MSA-DTWD | WA5534707 | 3 | Water2water Pty Ltd | C102 staircase foyer -CWDU low flow | Plumbing & Drainage | Water | 289.5525 | Pass | Pass | 0 | 0 | 0.66667 | 2022-06-16 13:21 | 2022-06-23 17:00 | 2022-06-20 12:00 | 2022-06-23 17:00 | 2022-06-20 12:40 |  |  | FILTER BLOCKED. REPLACED AND FLUSHED FILTER, ALL OKAY ON DEPARTURE.
MSA-DCA | WA5548891 | 2 | GPS Plumbing & Gas Services PtyLtd | Toilet Male north foyer - 2nd cubicle- Full Flush extremely hard to push & toilet seat coming off | Plumbing & Drainage | Toilets/Cisterns | 184.4975 | Pass | Pass | -1 | -1 | 0.66667 | 2022-06-17 10:35 | 2022-06-22 17:00 | 2022-06-17 15:20 | 2022-06-22 17:00 | 2022-06-17 16:00 |  |  | Replaced rubbers for the 2 buttons and greased it up, tightened toilet seat
MSA-DTWD | WA5565551 | 2 | Dormakaba Australia Pty Ltd | Ground - Main entrance - Automatic entrance door is faulty | Building | Automatic Doors | 180 | Pass | Pass | -1 | -1 | 0.66667 | 2022-06-22 08:57 | 2022-06-27 17:00 | 2022-06-22 10:43 | 2022-06-27 17:00 | 2022-06-22 11:23 |  |  | Attended site and found door to be operating correctly. Michael from facilities informed me the door was partly closing and opening again. On inspection found the external sensor to be full of dirt and cobwebs, also spider in sensor, removed dirt and cobwebs and adjusted sensor, cleaned and checked unit, tested and all working now.
MSA-DCA | WA5660764 | 0 | ADVANCED LOCK & KEY | Ground Floor - Disabled access Toilet - The latch on toilet door is broken - keeps spinning | Security | Locksmith | 307.5 | Pass | Pass | 0 | 0 | 0.66667 | 2022-07-19 12:23 | 2022-07-19 14:23 | 2022-07-19 14:15 | 2022-07-19 16:23 | 2022-07-19 14:55 |  |  | Replaced broken indicator bolt on disabled toilet on the ground floor of the blue room theatre with new Astra MIB lock
MSA-DFES | WA5832589 | 1 | ADVANCED LOCK & KEY | Ground Floor - Duty Room - Door remains locked from inside and cannot be opened | Security | Locksmith | 331.54 | Pass | Pass | 0 | 0 | 0.66667 | 2022-09-05 14:12 | 2022-09-06 17:00 | 2022-09-06 09:30 | 2022-09-06 17:00 | 2022-09-06 10:10 |  |  | replaced mortice lock with dead latching issue on key bag room with new lock
MSA-DCA | WA5838440 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground floor theatre foyer male toilet - urinal leaking to trough | Plumbing & Drainage | Toilets/Cisterns | 163.77 | Pass | Pass | 0 | 0 | 0.66667 | 2022-09-08 13:21 | 2022-09-15 17:00 | 2022-09-13 07:15 | 2022-09-15 17:00 | 2022-09-13 07:55 |  |  | Replaced outlet washer and inlet valve
MSA-MRWA | WA6108720 | 3 | Water2water Pty Ltd | RETROSPECTIVE - Ground - Eastern kitchen - Wilson boiler fail - see notes | Plumbing & Drainage | HWS/Units Electric & Gas | 150.355 | Pass | Pass | -1 | -1 | 0.66667 | 2022-10-20 10:28 | 2022-10-27 17:00 | 2022-10-20 15:20 | 2022-10-27 17:00 | 2022-10-20 16:00 | 1 |  | External plumber or tradesman has been fiddling with the unit. Tech reconnected everything all okay on departure.
MSA-DTAG | WA6108841 | 2 | Water2water Pty Ltd | RETROSPECTIVE WORK ORDER-technician completed repairs to Billi tap -DO NOT ATTEND | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 0.66667 | 2022-10-18 09:00 | 2022-10-21 17:00 | 2022-10-18 09:30 | 2022-10-21 17:00 | 2022-10-18 10:10 | 1 |  | CLEANED READER SWITCH ON TAP HEADS. ALL OKAY
MSA-DFES | WA6130781 | 2 | Dom's Total Grounds Maintenance | Ground - Verge reticulation - Broken sprinkler head Verge next to footpath | Landscaping & Gardening | Grounds Maintenance | 223 | Fail | Fail | 1 | 1 | 0.66667 | 2022-10-28 15:36 | 2022-11-02 17:00 | 2022-11-07 14:35 | 2022-11-02 17:00 | 2022-11-07 15:15 |  |  | Repair damaged retic & Supply Parts
MSA-DCA | WA6242038 | 0 | TK Elevator Australia Pty Ltd | PICA-Main Building-Ground Floor - Lift is not working - stuck on Ground floor - reoccurring fault | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.66667 | 2022-11-20 10:59 | 2022-11-20 12:59 | 2022-11-20 12:00 | 2022-11-20 14:59 | 2022-11-20 12:40 |  |  | Upon arrival I found the lift ooo at the ground floor through the bottom over travel limit i reset the lift by driving it up out of the over travel limit and tested all running correctly on departure it would not repeat the fault while i was on site.
MSA-DTWD | WA6401650 | 2 | ADVANCED LOCK & KEY | Ladies staff toilets - key lock barrel faulty - see notes | Security | Locksmith | 190.5 | Pass | Pass | -1 | -1 | 0.66667 | 2023-01-04 14:24 | 2023-01-09 17:00 | 2023-01-05 11:45 | 2023-01-09 17:00 | 2023-01-05 12:25
MSA-DCA | WA6408074 | 2 | ADVANCED LOCK & KEY | Level 5 - Door handle and lock broken See Notes Below | Security | Locksmith | 341.76 | Pass | Pass | 0 | 0 | 0.66667 | 2023-01-10 14:21 | 2023-01-13 17:00 | 2023-01-12 14:00 | 2023-01-13 17:00 | 2023-01-12 14:40
MSA-DTWD | WA6528663 | 2 | LIGHTHOUSE LOCKSMITHS | Q014 - The door key lock jams and difficult to turn the key to unlock | Security | Locksmith | 127.2 | Pass | Pass | -1 | -1 | 0.66667 | 2023-02-02 11:37 | 2023-02-07 17:00 | 2023-02-03 13:35 | 2023-02-07 17:00 | 2023-02-03 14:15
MSA-DTWD | WA6688230 | 2 | CONNECT SECURITY SYSTEMS | A/B/C/T/CAMERAS ARE NOT WORKING | Security | CCTV Surveillance | 165.45 | Pass | Pass | 0 | 0 | 0.66667 | 2023-03-07 12:48 | 2023-03-10 17:00 | 2023-03-10 09:41 | 2023-03-10 17:00 | 2023-03-10 10:21
MSA-DTWD | WA5107962 | 2 | AHS Services WA Pty Ltd (Anchor) | Q-Block, Pan Room, the maserator has a broken drain pipe | Plumbing & Drainage | Water | 139.7725 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-08 10:42 | 2022-02-11 17:00 | 2022-02-08 14:10 | 2022-02-11 17:00 | 2022-02-08 14:50 |  |  | Completed
MSA-MRWA | WA5142124 | 1 | Water2water Pty Ltd | Level 3 - kitchen - zip hot water unit - dripping water | Plumbing & Drainage | Water | 247.9125 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-16 13:34 | 2022-02-17 17:00 | 2022-02-17 12:40 | 2022-02-17 17:00 | 2022-02-17 13:20 |  |  | REPLACED TAP ON RHEEM BWU A402020423
MSA-DTAG | WA5199477 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Public Female Toilets - see notes below | Plumbing & Drainage | Toilets/Cisterns | 107.2725 | Pass | Pass | 0 | 0 | 0.66667 | 2022-03-01 09:45 | 2022-03-02 17:00 | 2022-03-01 10:40 | 2022-03-02 17:00 | 2022-03-01 11:20 |  |  | Completed
MSA-DTWD | WA5199498 | 1 | PEEL LOCK SERVICES PTY LTD | Key stuck in external office door lock | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.66667 | 2022-03-01 09:50 | 2022-03-02 17:00 | 2022-03-02 10:55 | 2022-03-02 17:00 | 2022-03-02 11:35 |  |  | Job Completed - replace lock
MSA-DTAG | WA5204936 | 2 | Water2water Pty Ltd | Level 12 - Kitchen - Cold water filter tap is running very slow(Left billi unit tap) | Plumbing & Drainage | Water | 291.27 | Pass | Pass | 0 | 0 | 0.66667 | 2022-03-04 15:27 | 2022-03-10 17:00 | 2022-03-10 12:10 | 2022-03-10 17:00 | 2022-03-10 12:50 |  | WACCES | Billi filter replaced due to slow flow issues.
MSA-DTWD | WA5481969 | 1 | ECO PLUMBING AND GAS PTY LTD | J121 - Water coming up from Floor drain | Plumbing & Drainage | Drainage | 116.425 | Pass | Pass | 0 | 0 | 0.66667 | 2022-05-31 08:13 | 2022-06-01 17:00 | 2022-05-31 15:40 | 2022-06-01 17:00 | 2022-05-31 16:20 |  |  | Clear blockage
MSA-DFES | WA5482033 | 1 | SONTEC WA PTY LTD | Kitchen - Main door - swipe access not working | Security | Access Control | 270 | Pass | Pass | 0 | 0 | 0.66667 | 2022-05-31 08:42 | 2022-06-01 17:00 | 2022-05-31 10:40 | 2022-06-01 17:00 | 2022-05-31 11:20 |  |  | 31/5/22 - Dylan ParslowFound card reader not receiving power.Reterminated in panel and tested, all working.
MSA-DTWD | WA5566651 | 2 | Water2water Pty Ltd | Block 10 - Ground - Staff room - Boiling Billy not delivering water | Plumbing & Drainage | Water | 258.0925 | Pass | Pass | -1 | -1 | 0.66667 | 2022-06-23 10:20 | 2022-06-28 17:00 | 2022-06-23 15:10 | 2022-06-28 17:00 | 2022-06-23 15:50 |  |  | Replaced broken tap
MSA-DFES | WA5588935 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Change room toilet - Toilet is clogged | Plumbing & Drainage | Toilets/Cisterns | 180.55 | Pass | Pass | 0 | 0 | 0.66667 | 2022-07-08 08:27 | 2022-07-11 17:00 | 2022-07-08 10:21 | 2022-07-11 17:00 | 2022-07-08 11:01 |  |  | Arrived on site and singed in went to Male toilets next to the gym on Ground floor got gave the toilet a flush blockage went away, flush the toilet numerous times with paper everything was fine. Someone used to much paper
MSA-DCA | WA5596768 | 2 | ADVANCED LOCK & KEY | HLT Foyer - Level 2 - Door 5 Lock issues - See notes below | Security | Locksmith | 172.5 | Pass | Pass | 0 | 0 | 0.66667 | 2022-07-11 10:23 | 2022-07-14 17:00 | 2022-07-13 12:25 | 2022-07-14 17:00 | 2022-07-13 13:05 |  |  | Service Lock cylinder
MSA-DCA | WA5677506 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Public ladies bathroom- last cubicle - Water leaking into bowl when cistern is full | Plumbing & Drainage | Toilets/Cisterns | 167.4775 | Pass | Pass | -1 | -1 | 0.66667 | 2022-07-25 14:54 | 2022-08-01 17:00 | 2022-07-26 15:14 | 2022-08-01 17:00 | 2022-07-26 15:54 |  |  | Replaced inlet valve to Female public toilet last cubicle
MSA-DFES | WA5691819 | 1 | Water2water Pty Ltd | Kitchen - Hot water unit is not functioning - Billie Unit under sink | Plumbing & Drainage | HWS/Units Electric & Gas | 150.355 | Pass | Pass | 0 | 0 | 0.66667 | 2022-08-03 08:20 | 2022-08-04 17:00 | 2022-08-03 09:40 | 2022-08-04 17:00 | 2022-08-03 10:20 |  |  | Lowered temperature and re calibration on system. Seems to have sorted issue with hot water delivery.
MSA-DTWD | WA5706936 | 3 | ADVANCED LOCK & KEY | Door lock faulty | Security | Locksmith | 172.5 | Pass | Pass | 0 | 0 | 0.66667 | 2022-08-11 14:39 | 2022-08-18 17:00 | 2022-08-15 11:40 | 2022-08-18 17:00 | 2022-08-15 12:20 |  |  | repinned cyl on A103 as bottom pins had worn flat
MSA-DCA | WA5838454 | 3 | GPS Plumbing & Gas Services PtyLtd | female toilet - first cubicle - cistern faulty, occasionally fails to flush | Plumbing & Drainage | Toilets/Cisterns | 100.98 | Pass | Pass | 0 | 0 | 0.66667 | 2022-09-08 13:27 | 2022-09-15 17:00 | 2022-09-13 07:55 | 2022-09-15 17:00 | 2022-09-13 08:35 |  |  | Replaced inlet valve
MSA-MRWA | WA5970460 | 0 | GPS Plumbing & Gas Services PtyLtd | Unknown Water leak come from level 1 to ground floor office . | Plumbing & Drainage | Materials | 188.7575 | Pass | Pass | 0 | 0 | 0.66667 | 2022-09-20 07:30 | 2022-09-20 09:30 | 2022-09-20 08:10 | 2022-09-20 11:30 | 2022-09-20 08:50 |  |  | Inspected burst fire service pipe. Different contractor needed.
MSA-DTWD | WA6040859 | 2 | LIGHTHOUSE LOCKSMITHS | P block-workshop-repair 2x locks | Security | Locksmith | 107.2 | Pass | Pass | 0 | 0 | 0.66667 | 2022-10-17 06:56 | 2022-10-19 17:00 | 2022-10-17 11:40 | 2022-10-19 17:00 | 2022-10-17 12:20 |  |  | service 2 x locks in P block
MSA-DTWD | WA6290971 | 2 | Swan Pest Control | Inspect and treat white ant infestation in Floor Boards A207 - See notes | Pest Control | General Pest | 295 | Pass | Pass | 0 | 0 | 0.66667 | 2022-11-28 11:12 | 2022-12-01 17:00 | 2022-12-01 09:10 | 2022-12-01 17:00 | 2022-12-01 09:50 |  |  | Treated active termites under sub floor of A207
MSA-DFES | WA6393473 | 3 | MR POTHOLE | Pothole in driveway - See Notes Below | Paving & Roadworks | Concreting |  | Fail | Fail | 1 | 1 | 0.66667 | 2022-12-28 15:39 | 2023-01-05 17:00 | 2023-01-12 13:55 | 2023-01-05 17:00 | 2023-01-12 14:35
MSA-DCA | WA6531393 | 0 | ADVANCED LOCK & KEY | external door cannot be locked | Security | Locksmith | 363.61 | Pass | Pass | 0 | 0 | 0.66667 | 2023-02-03 11:29 | 2023-02-03 13:29 | 2023-02-03 12:10 | 2023-02-03 15:29 | 2023-02-03 12:50
MSA-DTWD | WA6573208 | 2 | ADVANCED LOCK & KEY | A block and B block - room B201.1 and A135 -Key Barrel (see notes) | Security | Locksmith | 250 | Fail | Fail | 0 | 0 | 0.66667 | 2023-02-14 11:34 | 2023-02-17 17:00 | 2023-02-20 15:40 | 2023-02-17 17:00 | 2023-02-20 16:20
MSA-DCA | WA5053273 | 2 | GPS Plumbing & Gas Services PtyLtd | Mani Building -Ground Floor - Male toilet - urinal blocked | Plumbing & Drainage | Toilets/Cisterns | 128.4975 | Pass | Pass | 0 | 0 | 0.66667 | 2022-01-18 14:43 | 2022-01-21 17:00 | 2022-01-20 08:30 | 2022-01-21 17:00 | 2022-01-20 09:10 |  |  | Unblock urinal in male public toilet ground floor
MSA-DTWD | WA5085609 | 3 | ADVANCED LOCK & KEY | Pin Security Entry handle is not operating | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.66667 | 2022-01-21 09:17 | 2022-01-31 17:00 | 2022-01-24 10:20 | 2022-01-31 17:00 | 2022-01-24 11:00 |  |  | adjust to strike
MSA-DTAG | WA5087756 | 3 | Sapio Pty Ltd | Ground - Secuirty - Security computer control system have unlock and lock actions back to front | Security | Access Control | 130 | Pass | Pass | -1 | -1 | 0.66667 | 2022-01-24 12:31 | 2022-02-01 17:00 | 2022-01-25 08:30 | 2022-02-01 17:00 | 2022-01-25 09:10 |  |  | Updated site plans to match the rest of the site.
MSA-DTWD | WA5105209 | 1 | CONNECT SECURITY SYSTEMS | B block - alarm panel - Tamper alarm triggered unable to arm building | Security | Security Management System | 115 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-04 08:39 | 2022-02-07 17:00 | 2022-02-04 11:30 | 2022-02-07 17:00 | 2022-02-04 12:10 |  |  | reset tamper alarm caused by student touching security sensors
MSA-DTWD | WA5141947 | 1 | Complete Pest Management Services | Bad smell coming from roof space | Pest Control | General Pest | 240.91 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-16 12:41 | 2022-02-17 17:00 | 2022-02-17 07:20 | 2022-02-17 17:00 | 2022-02-17 08:00 |  |  | No access into roof void for inspection or treatment.Placed another 2 deodorisers in classroom.Advised staff not to use ceiling fans as they draw air down from the ceiling through the perforated slats.Use only air conditioning and natural ventilation from windows.Odour will naturally dissipate over time.
MSA-DTWD | WA5226722 | 2 | CONNECT SECURITY SYSTEMS | Alarm activation faults at both 40 Commerce Ave & 45 Commerce Armadale | Security | Monitoring | 172.5 | Pass | Pass | 0 | 0 | 0.66667 | 2022-03-14 11:53 | 2022-03-17 17:00 | 2022-03-14 13:18 | 2022-03-17 17:00 | 2022-03-14 13:58 |  |  | Removed Duress Function at 40 commerce as not allowed by DoE Monitoring. Replaced 1 x PIR at 45 commerce
MSA-DCA | WA5399191 | 1 | Automatic Fire Protection (ARA) | Spare Parts - Puppet Theatre - Zone 2 has been isolated on the fire panel due to multiple alarms | Fire Protection Services | Fire Protection - Monitor System | 410.19 | Pass | Pass | 0 | 0 | 0.66667 | 2022-05-09 17:14 | 2022-05-10 17:00 | 2022-05-10 11:50 | 2022-05-10 17:00 | 2022-05-10 12:30 |  |  | Attended site and found Az 2 in Alarm/isolated found faulty detector in lobby area.Fitted new detector and base and reset ok.Left system normal
MSA-DTWD | WA5460641 | 3 | Swan Pest Control | Ground Level - Room D07 - Termite activity in skirting boards ( column Nth West ) | Pest Control | General Pest | 125 | Pass | Pass | -1 | -1 | 0.66667 | 2022-05-18 16:00 | 2022-05-25 17:00 | 2022-05-19 13:45 | 2022-05-25 17:00 | 2022-05-19 14:25 |  |  | Broke open termite workings and applied 1 Litre Fipronil @ .6%
MSA-DCA | WA5497267 | 1 | GPS Plumbing & Gas Services PtyLtd | State Theatre Centre - Basement Level 2-Disabled Toilet - Blocked toilet and overflowing | Building | Materials | 111.025 | Pass | Pass | 0 | 0 | 0.66667 | 2022-06-09 21:40 | 2022-06-10 17:00 | 2022-06-10 08:05 | 2022-06-10 17:00 | 2022-06-10 08:45 |  |  | Cleared blocked disabled toilet basement level 2 caused by paper towels.
MSA-DTWD | WA5572688 | 2 | Water2water Pty Ltd | Library - Zip tap – no hot water | Plumbing & Drainage | Water | 248.995 | Pass | Pass | -1 | -1 | 0.66667 | 2022-06-30 09:31 | 2022-07-05 17:00 | 2022-07-01 14:30 | 2022-07-05 17:00 | 2022-07-01 15:10 |  |  | Replaced faulty hot pump
MSA-DFES | WA5596871 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - Kitchen - Kitchen sink blocked | Plumbing & Drainage | Drainage | 143.6 | Fail | Fail | 1 | 1 | 0.66667 | 2022-07-11 10:57 | 2022-07-14 17:00 | 2022-07-18 07:20 | 2022-07-14 17:00 | 2022-07-18 08:00 |  | WCAPPR | Arrived on site and singed in went to kitchen sink filled up sinks 4 times with hot water and released it every time water was running fine the fire guys took off the trap and cleaned it themselves. If happens again need to investigate further.
MSA-DFES | WA6001083 | 2 | SONTEC WA PTY LTD | Outside laundry area - Ground - Door next to laundry/oil separator not opening - see notes | Security | Access Control | 270 | Pass | Pass | 0 | 0 | 0.66667 | 2022-10-10 12:15 | 2022-10-13 17:00 | 2022-10-11 10:20 | 2022-10-13 17:00 | 2022-10-11 11:00 |  |  | 11/10/22 - Dylan ParslowFound build up of rust on locking pin preventing strike from working correctly.Cleaned and tested, all working.
MSA-DCA | WA6019917 | 1 | Dormakaba Australia Pty Ltd | door mechanism not working - see notes | Building | Automatic Doors | 351.95 | Pass | Pass | 0 | 0 | 0.66667 | 2022-10-13 09:18 | 2022-10-14 17:00 | 2022-10-13 10:20 | 2022-10-14 17:00 | 2022-10-13 11:00 |  |  | Attended site and found that door was a manual door controlled by electronic strike and not controlled by Dormakaba unit. Tested button is signalling but strike lock not releasing, client will need to contact there access control company to have a look at this. Left area clean and tidy there is no Dormakaba assert tag on this door as we do not look after this one.
MSA-DTWD | WA6088965 | 3 | ADVANCED LOCK & KEY | Artist in Residence - Rear Door - damaged door lock | Security | Locksmith | 245 | Pass | Pass | -1 | -1 | 0.66667 | 2022-10-19 11:48 | 2022-10-26 17:00 | 2022-10-20 10:00 | 2022-10-26 17:00 | 2022-10-20 10:40 |  |  | Replaced single cyl deadbolt on artist in residence rear door with new one 1x alb4010
MSA-DTWD | WA6380900 | 2 | SCAVENGER SUPPLIES PTY LTD | L1-male student toilet-Fire sensors need changing after alarm activation due to dust. see notes | Fire Protection Services | Fire Protection - Monitor System | 124.151 | Pass | Pass | 0 | 0 | 0.66667 | 2022-12-19 12:25 | 2022-12-22 17:00 | 2022-12-19 13:00 | 2022-12-22 17:00 | 2022-12-19 13:40 |  |  | Completed 19/12/2022Called to investigate sensor gone into alarm- T Block, First Floor West male toilet Sensor 70 Zone115.Confirmed with FIP location and sensor number is correct. Upon investigation it appears that thetoilet block is undergoing maintenance work and there is a considerable amount of plaster dust ect.It is believed this has set off the smoke detector as some dust came off sensor when I disconnectedit from the base.I cleaned out the sensor with mild air pressure, re connected to the base, de isolated and resetpanel. Waited for 15 minutes and no issues so left with management
MSA-DFES | WA6401499 | 3 | ADVANCED LOCK & KEY | Level 2 - Cleaners cupboard - Getting jammed / Faulty door closer | Security | Locksmith | 190.7 | Pass | Pass | -1 | -1 | 0.66667 | 2023-01-04 12:22 | 2023-01-11 17:00 | 2023-01-06 09:35 | 2023-01-11 17:00 | 2023-01-06 10:15
MSA-DTAG | WA6425924 | 2 | High Tech Pest Control | Ground - Staff Office Area & Female Toilets- Mosquitos | Pest Control | General Pest | 260.28 | Pass | Pass | 0 | 0 | 0.66667 | 2023-01-12 12:45 | 2023-01-17 17:00 | 2023-01-17 13:20 | 2023-01-17 17:00 | 2023-01-17 14:00
MSA-DTWD | WA6650960 | 2 | Water2water Pty Ltd | zippy water system not working in staff room | Plumbing & Drainage | HWS/Units Electric & Gas | 249.445 | Pass | Pass | 0 | 0 | 0.66667 | 2023-02-20 15:06 | 2023-02-23 17:00 | 2023-02-23 11:50 | 2023-02-23 17:00 | 2023-02-23 12:30
MSA-DCA | WA5674541 | 2 | GPS Plumbing & Gas Services PtyLtd | Basement (security level) - AHU Plant Room - Floor drain requires checking for efficiency & blockage | Plumbing & Drainage | Drainage | 95.77 | Pass | Pass | -1 | -1 | 0.65 | 2022-07-21 12:26 | 2022-07-26 17:00 | 2022-07-22 14:11 | 2022-07-26 17:00 | 2022-07-22 14:50 |  |  | Investigated down pipe and drain, checked drain for blockages
MSA-DTAG | WA6680762 | 1 | Dormakaba Australia Pty Ltd | Back Carpark - Censor to open gate from inside the carpark is intermittently not working(see notes) | Building | Steel Fencing & Gates | 206.95 | Pass | Pass | 0 | 0 | 0.65 | 2023-03-01 13:59 | 2023-03-02 17:00 | 2023-03-01 15:12 | 2023-03-02 17:00 | 2023-03-01 15:51
MSA-DFES | WA5199839 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | 2 taps are leaking and require fixing - see notes below | Plumbing & Drainage | Water | 158.2 | Pass | Pass | 0 | 0 | 0.65 | 2022-03-01 12:13 | 2022-03-09 17:00 | 2022-03-08 07:20 | 2022-03-09 17:00 | 2022-03-08 07:59 |  |  | Had to replaces 2 outside taps that were leaking
MSA-DTWD | WA5116475 | 2 | Dormakaba Australia Pty Ltd | T block Jennalup Street entry - Hair and beauty - Main entry auto Glass doors - loud noise | Building | Doors | 180 | Pass | Pass | 0 | 0 | 0.65 | 2022-02-11 15:43 | 2022-02-16 17:00 | 2022-02-14 09:04 | 2022-02-16 17:00 | 2022-02-14 09:43 |  |  | On inspection found track wheels to Rhys door looking out were making a sticking noise, lubricated, tested ok now. If problem reoccurs recommend replacing 8 x heavy duty track wheels to both doors, this will require 2 technicians for safety as this is a large heavy frameless glass door.
MSA-DFES | WA5151570 | 1 | Water2water Pty Ltd | 2nd floor kitchen - operation side - zip tap unit - not working | Plumbing & Drainage | Water | 489.4425 | Pass | Pass | 0 | 0 | 0.65 | 2022-02-17 13:59 | 2022-02-18 17:00 | 2022-02-18 11:10 | 2022-02-18 17:00 | 2022-02-18 11:49 |  |  | Replaced faulty tap head. Now operating as per normal.
MSA-DTWD | WA5307118 | 3 | CONNECT SECURITY SYSTEMS | Belt Spicing Shed - Security Alarm indicates low Battery | Security | Monitoring | 180.24 | Pass | Pass | -1 | -1 | 0.65 | 2022-04-07 10:15 | 2022-04-14 17:00 | 2022-04-07 12:51 | 2022-04-14 17:00 | 2022-04-07 13:30 |  |  | Replaced 2 x dead batteries
MSA-DCA | WA5660565 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground and First Floor - Conservation Labs and Wet Room - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 371.62 | Pass | Pass | 0 | 0 | 0.65 | 2022-07-19 10:35 | 2022-07-20 17:00 | 2022-07-19 15:04 | 2022-07-20 17:00 | 2022-07-19 15:43 |  |  | Attended site gained access and carried out inspection of water pump and flow of RO water to ground floor snd first floor labs. RO storage tank full. Confirmed RO field circulation pump was operating and making up pressure when RO tap turned on. On checking RO unit feed pump control switch was found in the off position. This has been turned back on. Clicking from RO plant unit could have been the solonids that control the flush and dump valves which may have been operating dependingon equipmentset up. During inspection confirmed normal plant operation. All switches have been left in auto. Confirmed all RO taps on ground floor and level 1 were work and providing RO water. No further action required on this job.
MSA-DCA | WA6019734 | 0 | Dormakaba Australia Pty Ltd | External plant room doors ground-water has damaged magnet lock on gate | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.65 | 2022-10-13 08:06 | 2022-10-13 10:06 | 2022-10-13 09:26 | 2022-10-13 12:06 | 2022-10-13 10:05 |  |  | Arrived onsite and spoke to the client and found the problem is the wooden double doors are so badly water damaged causing the doors to warp, preventing the magnet for the reed switchnot making which in turn can’t arm the doors. Forced door to properly close, fitted arm back on closer and packed out magnet so to switch the reed. These doors are in a very bad state andneed to be replaced by others. Pictures attached with asset number.
MSA-DCA | WA5568310 | 0 | GPS Plumbing & Gas Services PtyLtd | gas smell next to the front door area | Plumbing & Drainage | Gas | 213.9775 | Pass | Pass | 0 | 0 | 0.63333 | 2022-06-26 13:26 | 2022-06-26 15:26 | 2022-06-26 14:37 | 2022-06-26 17:26 | 2022-06-26 15:15 |  |  | Investigate gas smell to front of building.Checked round the building,no gas supply to building.No gas smell present at the time.
MSA-DCA | WA5688091 | 2 | Dormakaba Australia Pty Ltd | Ground Floor - Boardroom - Side access door, internal button is not responding when pushed | Building | Doors | 245.95 | Pass | Pass | 0 | 0 | 0.63333 | 2022-08-02 09:43 | 2022-08-05 17:00 | 2022-08-03 09:07 | 2022-08-05 17:00 | 2022-08-03 09:45 |  |  | Attended site and found large bell switch exit button was worn and would need a few pushes before it would activate door. Replaced bell switch, tested and all working fine now. Left area clean and tidy.
MSA-DCA | WA5793694 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Male Public Toilets - Basin Tap Leaking | Plumbing & Drainage | Water | 587.8175 | Pass | Pass | 0 | 0 | 0.63333 | 2022-08-24 09:28 | 2022-08-29 17:00 | 2022-08-26 15:09 | 2022-08-29 17:00 | 2022-08-26 15:47 |  |  | Replaced leaking push tap in level 1 male public toilet LHS
MSA-DTWD | WA6249479 | 3 | Dormakaba Australia Pty Ltd | Auto door has power but not responding to push buttons. | Building | Automatic Doors | 206.95 | Pass | Pass | -1 | -1 | 0.63333 | 2022-11-21 12:13 | 2022-11-28 17:00 | 2022-11-22 11:24 | 2022-11-28 17:00 | 2022-11-22 12:02 |  |  | Found that the door has gone into fault and requires reprogramming. Reset and reprogrammed. Adjusted spring tension, tested all ok.
MSA-DTWD | WA6531198 | 2 | Water2water Pty Ltd | Zip urn not heating water anymore | Plumbing & Drainage | HWS/Units Electric & Gas | 150.355 | Pass | Pass | 0 | 0 | 0.63333 | 2023-02-03 10:05 | 2023-02-08 17:00 | 2023-02-08 15:05 | 2023-02-08 17:00 | 2023-02-08 15:43
MSA-DTAG | WA5649203 | 0 | Automatic Fire Protection (ARA) | faulty smoke detector | Fire Protection Services | Fire Protection - Monitor System | 742.83 | Pass | Pass | 0 | 0 | 0.63333 | 2022-07-17 09:11 | 2022-07-17 11:11 | 2022-07-17 10:44 | 2022-07-17 13:11 | 2022-07-17 11:22 |  |  | On arrival, smoke detector L1 S59 z9 was isolated but not in alarm and code red was in alarm.Firies had been and isolated and reset fip.Logs showed the device had gone into alarm this morning.Avalues for the device were normal.Replaced head with new Xp95 opt smoke and deisolated device.
MSA-DFES | WA5491360 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - FF en suite Dorm 1 and 2 - Half flush button not working on toilet - Half flush button not | Plumbing & Drainage | Toilets/Cisterns | 133.45 | Fail | Fail | 0 | 0 | 0.61667 | 2022-06-03 14:51 | 2022-06-13 17:00 | 2022-06-14 07:22 | 2022-06-13 17:00 | 2022-06-14 07:59 |  |  | Had to adjust a screw to raise a flush button on toilet in Dorm 1 and 2
MSA-DCA | WA4990738 | 1 | GPS Plumbing & Gas Services PtyLtd | Entry Way - damaged pipe - see notes below | Plumbing & Drainage | Water | 88.9975 | Pass | Pass | 0 | 0 | 0.61667 | 2022-01-04 11:14 | 2022-01-05 17:00 | 2022-01-04 13:13 | 2022-01-05 17:00 | 2022-01-04 13:50 |  |  | The leaking pipe coming out of the wall is from the aircon, i have advised the admin desk that they need to get the aircon contractors to have a look
MSA-DTWD | WA5200981 | 1 | Dormakaba Australia Pty Ltd | North side main entrance - auto door sopped half way | Building | Doors | 180 | Pass | Pass | 0 | 0 | 0.61667 | 2022-03-02 10:43 | 2022-03-03 17:00 | 2022-03-02 12:32 | 2022-03-03 17:00 | 2022-03-02 13:09 |  |  | Found that the door was going into over current while closing, adjusted the current limits, cleaned and adjusted all sensors, tested all ok.
MSA-DTWD | WA6518678 | 2 | Water2water Pty Ltd | The urn in the staff lunchroom is not heating the water | Plumbing & Drainage | HWS/Units Electric & Gas | 150.355 | Pass | Pass | 0 | 0 | 0.61667 | 2023-01-25 10:25 | 2023-01-31 17:00 | 2023-01-31 11:29 | 2023-01-31 17:00 | 2023-01-31 12:06
MSA-DCA | WA6523248 | 0 | TK Elevator Australia Pty Ltd | Lift - Has dropped | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 0.61667 | 2023-01-31 13:40 | 2023-01-31 15:40 | 2023-01-31 16:06 | 2023-01-31 17:40 | 2023-01-31 16:43
MSA-DCA | WA6650274 | 1 | TK Elevator Australia Pty Ltd | Foyer - Person stuck in elevator earlier today | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.61667 | 2023-02-20 10:13 | 2023-02-21 17:00 | 2023-02-21 14:45 | 2023-02-21 17:00 | 2023-02-21 15:22
MSA-DTAG | WA5462537 | 3 | Dormakaba Australia Pty Ltd | Ground Floor - Building entrance - External ‘slow button’ on the revolving door is missing | Building | Automatic Doors | 361.5 | Pass | Pass | 0 | 0 | 0.61667 | 2022-05-19 16:04 | 2022-05-26 17:00 | 2022-05-25 13:39 | 2022-05-26 17:00 | 2022-05-25 14:16 |  |  | Supplied and fitted new push button as required, checked over and tested operation upon completion and left in good working order
MSA-MRWA | WA5151687 | 3 | GPS Plumbing & Gas Services PtyLtd | Basement kitchen -Replace HWS pressure release valve | Plumbing & Drainage | HWS/Units Electric & Gas | 263.3025 | Pass | Pass | -1 | -1 | 0.61667 | 2022-02-17 16:19 | 2022-02-24 17:00 | 2022-02-18 11:08 | 2022-02-24 17:00 | 2022-02-18 11:45 |  |  | Replaced corroded relief valve to hot water unit
MSA-DTWD | WA5191551 | 2 | Water2water Pty Ltd | Level 3 - D308 - Boiler Unit in Kitchen isnt working | Plumbing & Drainage | Water | 559.9225 | Pass | Pass | -1 | -1 | 0.61667 | 2022-02-25 07:17 | 2022-03-01 17:00 | 2022-02-25 14:30 | 2022-03-01 17:00 | 2022-02-25 15:07 |  |  | Replaced faulty solenoid and blocked filter and PLV.
MSA-MRWA | WA5679885 | 1 | Schindler Lifts Australia | Lift out of service | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.61667 | 2022-07-27 08:13 | 2022-07-28 17:00 | 2022-07-28 07:41 | 2022-07-28 17:00 | 2022-07-28 08:18 |  |  | Works completed - close out at $0
MSA-DFES | WA6534531 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Delivery driver has driven over the Western Power dome | Electrical | Distribution Board | 254.785 | Pass | Pass | 0 | 0 | 0.61667 | 2023-02-06 13:23 | 2023-02-06 15:23 | 2023-02-06 13:23 | 2023-02-06 17:23 | 2023-02-06 14:00
MSA-DCA | WA5092720 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Kitchen Lift – no. 2 - Lift on level 1 - lift is not responding | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.6 | 2022-01-28 09:15 | 2022-01-31 17:00 | 2022-01-28 12:16 | 2022-01-31 17:00 | 2022-01-28 12:52 |  |  | Lift 2 Art-Kitchen-Geared :Rope brake not resetting, manually reset, informed supervisor, tested and left lift running
MSA-DFES | WA5216287 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room - Broken power point in rear of engine room 2.4 bay | Electrical | General Electrical | 90.24 | Pass | Pass | 0 | 0 | 0.6 | 2022-03-11 09:10 | 2022-03-16 17:00 | 2022-03-16 08:09 | 2022-03-16 17:00 | 2022-03-16 08:45 |  |  | Arrive onsite 809 signed in and shown to GPO by staff. Spent time finding circet as no rcd or label. Replaced damaged mounting block and installed more fixings to prevent further damage. Completed and 845 and continued with other job on same site.
MSA-DCA | WA5382572 | 1 | TK Elevator Australia Pty Ltd | Long Bar - Dumb waiter is faulty | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.6 | 2022-04-27 07:51 | 2022-04-27 17:00 | 2022-04-27 09:05 | 2022-04-27 17:00 | 2022-04-27 09:41 |  |  | Lift out of order, found no voltage on return sode of safety circuit, found high resistance on bottom pit stop button. Cleaned and tested all ok left in service.Work order to be closed out at $0 cost
MSA-DTAG | WA5383263 | 1 | Gilmour & Jooste Electrical | Waiting area Courtroom building - Outside door in secure car park - see notes below | Electrical | General Electrical | 143.55 | Pass | Pass | 0 | 0 | 0.6 | 2022-04-27 13:37 | 2022-04-28 17:00 | 2022-04-27 14:30 | 2022-04-28 17:00 | 2022-04-27 15:06 |  |  | Replaced GPO and mounting block behind vending machine allegedly kicked in.Tested and working.
MSA-DTWD | WA5481630 | 2 | CAPS AUSTRALIA PTY LTD | Ground - Workshops - air pressure hose leaking form compressor to workshops | Equipment | Compressors, Generators | 82.2 | Fail | Fail | 1 | 1 | 0.6 | 2022-05-30 15:12 | 2022-06-02 17:00 | 2022-06-08 13:30 | 2022-06-02 17:00 | 2022-06-08 14:06 |  |  | Find and repair air leaks.
MSA-DFES | WA5563307 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Administration - Ground - Transportable Toilet Block - see details below | Plumbing & Drainage | Toilets/Cisterns | 133.45 | Pass | Pass | -1 | -1 | 0.6 | 2022-06-20 13:44 | 2022-06-27 17:00 | 2022-06-21 15:09 | 2022-06-27 17:00 | 2022-06-21 15:45 |  |  | Had to plung three basin tested everything running fine and toilet also
MSA-DCA | WA5677566 | 3 | GPS Plumbing & Gas Services PtyLtd | Zone 33 - Investigate the HWU next to fire detector, HWU is causing detector to go off. | Plumbing & Drainage | HWS/Units Electric & Gas | 153.375 | Pass | Pass | -1 | -1 | 0.6 | 2022-07-25 16:03 | 2022-08-01 17:00 | 2022-07-26 12:34 | 2022-08-01 17:00 | 2022-07-26 13:10 |  |  | No fault found with the hot water unit.Advised Denise form Programmed.
MSA-DFES | WA5696217 | 2 | Anvil Doors | ground - External gate keypad faulty | Building | Steel Fencing & Gates | 2270.8 | Fail | Fail | 0 | 0 | 0.6 | 2022-08-08 10:15 | 2022-08-11 17:00 | 2022-08-12 09:05 | 2022-08-11 17:00 | 2022-08-12 09:41 |  |  | Key Pads require replacing and gate motor. Please see attached BRAF, Braf Quote signature slip and site photos19/08/22 2x Keypad replaced by automation technician. Signature Slip, Service Report uploaded on completion.
MSA-DFES | WA5988494 | 2 | Water2water Pty Ltd | Ground Floor - Kitchen - Zip tap closest to the courtyard has no hot water | Plumbing & Drainage | Water | 248.995 | Pass | Pass | 0 | 0 | 0.6 | 2022-10-04 09:37 | 2022-10-07 17:00 | 2022-10-05 13:00 | 2022-10-07 17:00 | 2022-10-05 13:36 |  |  | Replaced faulty hot pulp
MSA-DTWD | WA6255837 | 1 | SCAVENGER SUPPLIES PTY LTD | RETROSPECTIVE JOB - DO NOT ATTEND WORK ORDER - SEE NOTES BELOW | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | 0 | 0 | 0.6 | 2022-11-17 14:24 | 2022-11-18 17:00 | 2022-11-17 14:24 | 2022-11-18 17:00 | 2022-11-17 15:00 | 1 |  | completed 17/11/2022-wb
MSA-DFES | WA6650743 | 2 | Australian HVAC Services Pty. Ltd. | Kats office - Aircon not working | Air Conditioning | Room Air Conditioners | 201.88 | Pass | Pass | 0 | 0 | 0.6 | 2023-02-20 12:59 | 2023-02-23 17:00 | 2023-02-20 14:00 | 2023-02-23 17:00 | 2023-02-20 14:36
MSA-DTWD | WA6680271 | 1 | Water2water Pty Ltd | Bad tasting water to drink fountain | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 0.6 | 2023-03-01 09:49 | 2023-03-02 17:00 | 2023-03-02 11:20 | 2023-03-02 17:00 | 2023-03-02 11:56
MSA-DCA | WA6704152 | 0 | GPS Plumbing & Gas Services PtyLtd | Van Dock GRND - Water coming from ground pipework | Plumbing & Drainage | Water | 230.255 | Pass | Pass | 0 | 0 | 0.6 | 2023-03-12 19:23 | 2023-03-12 21:23 | 2023-03-12 20:29 | 2023-03-12 23:23 | 2023-03-12 21:05
MSA-DTWD | WA5052507 | 2 | Swan Pest Control | Staff Kitchen - ants infestation | Pest Control | General Pest | 295 | Pass | Pass | 0 | 0 | 0.58333 | 2022-01-18 08:40 | 2022-01-21 17:00 | 2022-01-18 14:20 | 2022-01-21 17:00 | 2022-01-18 14:55 |  |  | Sprayed kitchen (staffroom) and courtyard with Fipronil @ 6.%
MSA-DFES | WA5164103 | 1 | Anvil Doors | Roller Door 3 - hinge that secures a roller has snapped - | Building | Roller Shutters | 378.91 | Pass | Pass | 0 | 0 | 0.58333 | 2022-02-18 16:21 | 2022-02-21 17:00 | 2022-02-21 14:20 | 2022-02-21 17:00 | 2022-02-21 14:55 |  |  | Attended Dalglish Fire Station and replaced damaged hinge to sectional door. Please see attached signature slip and service report.
MSA-DCA | WA5207393 | 2 | GPS Plumbing & Gas Services PtyLtd | Kitchenette between staff toilets -Spout to sink damaged, requires replacing | Plumbing & Drainage | Materials | 188.5025 | Pass | Pass | 0 | 0 | 0.58333 | 2022-03-08 12:52 | 2022-03-11 17:00 | 2022-03-11 11:20 | 2022-03-11 17:00 | 2022-03-11 11:55 |  |  | Replaced leaking spout to kitchen sink.
MSA-DTWD | WA5752794 | 3 | LIGHTHOUSE LOCKSMITHS | Kitchen area - cupboard locks Kitchen area not opening/sticking | Security | Locksmith | 116.8 | Pass | Pass | -1 | -1 | 0.58333 | 2022-08-17 12:06 | 2022-08-24 17:00 | 2022-08-19 09:05 | 2022-08-24 17:00 | 2022-08-19 09:40 |  |  | serviced key locks on kitchen cabinets and replaced 4 damaged keys for same locks
MSA-DCA | WA5792289 | 2 | Quality Pest & Weed Solutions PTY LTD | Geologist Building-L1-Locate and remove vermin remains from Escape stair area. -see notes | Pest Control | General Pest |  | Pass | Pass | 0 | 0 | 0.58333 | 2022-08-23 12:42 | 2022-08-26 17:00 | 2022-08-23 13:48 | 2022-08-26 17:00 | 2022-08-23 14:23 |  |  | Job is completed - No evidence of rodent activity or potential ingress points. Odor bag installed . No rodent to remove
MSA-DTAG | WA5797643 | 2 | Water2water Pty Ltd | Level 12 - Kitchen - No water coming out. Both red and green (replace filter) lights are flashing | Plumbing & Drainage | HWS/Units Electric & Gas | 150.355 | Pass | Pass | 0 | 0 | 0.58333 | 2022-08-29 09:36 | 2022-09-01 17:00 | 2022-08-29 11:20 | 2022-09-01 17:00 | 2022-08-29 11:55 |  |  | UNIT IN CHECK WATER SUPPLY FAULT ON ARRIVAL. RESET, CHECKED FLOW & LEVEL SENSORS - SLOW COLD CHILLING BUT ALL OKAY. UNIT IS 12 YEARS OLD, IF PLAYS UP AGAIN - HIGHLY RECOMMEND REPLACEMENT WITH WILSON, IC8 CHILLER & MAXISCALE SYSTEM.
MSA-DFES | WA5099892 | 2 | ADVANCED LOCK & KEY | External front door to Room 2 SO Office - Front door security screen lock defective | Security | Locksmith | 326.24 | Fail | Fail | 1 | 1 | 0.58333 | 2022-02-02 09:29 | 2022-02-07 17:00 | 2022-02-11 10:10 | 2022-02-07 17:00 | 2022-02-11 10:45 |  | WCAPPR | Completed11/2/88
MSA-DTWD | WA5140783 | 2 | Water2water Pty Ltd | ET10 Corridor - Leaking CW Drinking Fountain | Plumbing & Drainage | Water | 139.7325 | Fail | Fail | 1 | 1 | 0.58333 | 2022-02-16 07:13 | 2022-02-18 17:00 | 2022-02-22 14:00 | 2022-02-18 17:00 | 2022-02-22 14:35 |  | WCAPPR | BRAF FOR REPLACEMENT FOUNTAIN DECLINED. WORK ORDER CLOSED OUT.
MSA-DTWD | WA5207418 | 3 | Water2water Pty Ltd | West Block - W119 - Filter requires changing to Tap | Plumbing & Drainage | Water | 310.6625 | Pass | Pass | -1 | -1 | 0.58333 | 2022-03-08 13:01 | 2022-03-15 17:00 | 2022-03-09 12:25 | 2022-03-15 17:00 | 2022-03-09 13:00 |  |  | Filter blocked Zip Hydrotap A40191124B replaced filter reset checked ok
MSA-DTWD | WA5258094 | 3 | ADVANCED LOCK & KEY | West Block - Level 1 - W125 -Barrel cannot be opened on store door | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.58333 | 2022-03-17 15:00 | 2022-03-24 17:00 | 2022-03-21 13:15 | 2022-03-24 17:00 | 2022-03-21 13:50 |  |  | Sprayed dry 355 on w125 storeroom as it was hard to turn the key because it was that dry, tested GMK and w001 and both worked fine. Serviced lock.
MSA-DTWD | WA5279219 | 0 | ACTION GLASS & ALUMINIUM | C Block - Break in - Please secure broken window and clean glass | Building | Materials | 362.1 | Pass | Pass | 0 | 0 | 0.58333 | 2022-03-19 19:39 | 2022-03-19 21:39 | 2022-03-19 20:25 | 2022-03-19 23:39 | 2022-03-19 21:00 |  |  | ATTENDED SITE AFTER HOURSREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-992 X 795
MSA-DTWD | WA5285981 | 3 | Water2water Pty Ltd | B block - B21 - Chilled water cooler leaking | Plumbing & Drainage | Water | 154.5525 | Pass | Pass | 0 | 0 | 0.58333 | 2022-03-21 11:31 | 2022-03-28 17:00 | 2022-03-28 15:25 | 2022-03-28 17:00 | 2022-03-28 16:00 |  |  | REPLACED LEAKING JOHN GUEST TUBE JOINER ON FOUNTAIN. HAS TO REASSEMBLE COOLER AFTER HANDYMAN TOOK ALL PANELS OFF. TESTED & CHECKED - ALL OKAY ON DEPARTURE.
MSA-DCA | WA5287713 | 3 | ADVANCED LOCK & KEY | Main Building - Level 2 - Studio 1 - Lock broken to Studio 1 door. Lock just keeps turns not locking | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.58333 | 2022-03-22 14:49 | 2022-03-29 17:00 | 2022-03-23 14:25 | 2022-03-29 17:00 | 2022-03-23 15:00 |  |  | Reassembled 8221 cyl on studio 1 doors deadbolt as cap had undone and tailbar had fallen off
MSA-DTWD | WA5291106 | 2 | PEEL LOCK SERVICES PTY LTD | Lock and door handle damaged | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.58333 | 2022-03-25 15:12 | 2022-03-30 17:00 | 2022-03-29 11:25 | 2022-03-30 17:00 | 2022-03-29 12:00 |  |  | Lock and handle damaged J Block SET/HA set of handles set of spindles
MSA-DTWD | WA5301466 | 2 | PEEL LOCK SERVICES PTY LTD | Lock damaged not locking | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.58333 | 2022-04-01 09:15 | 2022-04-06 17:00 | 2022-04-04 10:30 | 2022-04-06 17:00 | 2022-04-04 11:05 |  |  | job completed - serviced lock
MSA-DFES | WA5301856 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Building - kitchen - tap difficult to swivel - may need replacement | Plumbing & Drainage | Water | 158.71 | Pass | Pass | 0 | 0 | 0.58333 | 2022-04-01 13:28 | 2022-04-06 17:00 | 2022-04-06 09:10 | 2022-04-06 17:00 | 2022-04-06 09:45 |  |  | Tap replacement
MSA-DTWD | WA5384166 | 3 | AWB Co. | Gutter at the end of covered walkway has come away from awning | Building | Awnings | 147.95 | Pass | Pass | 0 | 0 | 0.58333 | 2022-04-28 10:22 | 2022-05-05 17:00 | 2022-05-05 11:40 | 2022-05-05 17:00 | 2022-05-05 12:15 |  |  | Installed hanging gutter back into original position securely.
MSA-DTWD | WA5400444 | 1 | COMMERCIAL LAUNDRY SOLUTIONS | Room C45 - Commercial Washing Machine leaking from beneath | Equipment | Cleaning Equipment | 95 | Pass | Pass | 0 | 0 | 0.58333 | 2022-05-10 10:36 | 2022-05-11 17:00 | 2022-05-10 11:25 | 2022-05-11 17:00 | 2022-05-10 12:00 |  |  | 10/05 - AD attended site - Tested both machines and traced the issue to a backwashing problem from the drain. Advised maintenance on site as a plumber will be required.
MSA-DTWD | WA5470425 | 1 | Complete Pest Management Services | Cafeteria kitchen - Evidence of rodents in the kitchen | Pest Control | General Pest | 403.91 | Pass | Pass | 0 | 0 | 0.58333 | 2022-05-23 09:58 | 2022-05-24 17:00 | 2022-05-24 07:40 | 2022-05-24 17:00 | 2022-05-24 08:15 |  |  | Inspected kitchen cafeteria for rodent activity, found minimal droppings, used blocks in 2 x manholes and placedrodent bait stations in various areas of kitchen area for rodent control.
MSA-DTAG | WA5495701 | 2 | Water2water Pty Ltd | Level 10 - Kitchen - Billi quadra – water running slow | Plumbing & Drainage | Water | 289.5525 | Pass | Pass | 0 | 0 | 0.58333 | 2022-06-08 14:15 | 2022-06-13 17:00 | 2022-06-13 09:25 | 2022-06-13 17:00 | 2022-06-13 10:00 |  |  | TECH REPLACED FILTER. ALL OKAY ON DEPARTURE.
MSA-DTWD | WA5513599 | 3 | ADVANCED LOCK & KEY | Digital door lock faulty | Security | Locksmith | 485 | Pass | Pass | -1 | -1 | 0.58333 | 2022-06-14 11:47 | 2022-06-21 17:00 | 2022-06-15 14:25 | 2022-06-21 17:00 | 2022-06-15 15:00 |  |  | Replaced broken Lockwood digital keypad on E323
MSA-DFES | WA5565498 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Front of property - Northern side of engine room - 25mm PVC pipe leaking end cap is cracked | Plumbing & Drainage | Drainage | 143.61 | Pass | Pass | 0 | 0 | 0.58333 | 2022-06-22 08:29 | 2022-06-23 17:00 | 2022-06-22 09:10 | 2022-06-23 17:00 | 2022-06-22 09:45 |  |  | Had dig up ground and repair a 25mm pressure cap tested and running fine
MSA-DCA | WA5715176 | 2 | ADVANCED LOCK & KEY | Lower ground floor - Quarantine Room - double door latch is not latching shut | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.58333 | 2022-08-12 11:53 | 2022-08-17 17:00 | 2022-08-15 11:00 | 2022-08-17 17:00 | 2022-08-15 11:35 |  |  | installed escape latch on fixed site of double doors higher as it wasnt latching ( the kind of escape latch that has chain)
MSA-DCA | WA5887722 | 2 | Techworks Plumbing | Faulty Zip tap - Francis St Building Ground floor – behind the front desk | Plumbing & Drainage | Water | 326.58 | Pass | Pass | 0 | 0 | 0.58333 | 2022-09-16 09:29 | 2022-09-21 17:00 | 2022-09-19 08:45 | 2022-09-21 17:00 | 2022-09-19 09:20 |  |  | arrived to check the zip tap behind the front reception on ground floor, on arrival of the zip tap inspection we checked the operation of the zip tap it was working fine both nozzles were working and temperature was good, we then made our way to the basement to sign out and return key card.
MSA-DCA | WA5973524 | 2 | TK Elevator Australia Pty Ltd | HLT Grid Lift - Lift 5 - Error message to contact management as there's a fault- See notes below | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.58333 | 2022-09-21 14:01 | 2022-09-27 17:00 | 2022-09-21 14:24 | 2022-09-27 17:00 | 2022-09-21 14:59 |  |  | On arrival, opened the controller door, and found the 3G GSM unit flashing red.After about a minute, the unit started to flash green. Adjusted the angle of the aerial on the unit, and closed the controller door, waited a few minutes, then tested theemergency lift phone. The phone rang the to the call centre ok. Left the lift in service.
MSA-DTAG | WA5982661 | 2 | Water2water Pty Ltd | Ground - Robing Room - tap is leaking – loose seal around the fountain spout | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 0.58333 | 2022-09-30 13:18 | 2022-10-05 17:00 | 2022-10-03 08:00 | 2022-10-05 17:00 | 2022-10-03 08:35 |  |  | Tightened inserts in bubbler and tested. All ok
MSA-DCA | WA5985884 | 0 | GPS Plumbing & Gas Services PtyLtd | Art Gallery of WA - James St Level1 bad odour suspect gas leak | Building | Materials | 191.495 | Pass | Pass | 0 | 0 | 0.58333 | 2022-10-01 13:34 | 2022-10-01 15:34 | 2022-10-01 14:15 | 2022-10-01 17:34 | 2022-10-01 14:50 |  |  | No gas leaks detected-not bad odours smelt. Fualty forklift battery in basement
MSA-DFES | WA6156509 | 1 | ADVANCED LOCK & KEY | Stairway between carpark and main building - Door handle wont open from one side - Replace Lock | Security | Locksmith | 305.48 | Pass | Pass | 0 | 0 | 0.58333 | 2022-11-09 08:29 | 2022-11-10 17:00 | 2022-11-09 10:30 | 2022-11-10 17:00 | 2022-11-09 11:05 |  |  | Attend site and replace damaged internal handle 1x LW1905/70
MSA-DCA | WA6191402 | 3 | ADVANCED LOCK & KEY | Inner door latch to DG/18 (glass door by Control Room) - Door latch broken - see notes below | Security | Locksmith | 280 | Pass | Pass | -1 | -1 | 0.58333 | 2022-11-16 16:25 | 2022-11-23 17:00 | 2022-11-17 09:25 | 2022-11-23 17:00 | 2022-11-17 10:00 |  |  | 1xNSQ-13V-25-SCp Replaced in glass security door
MSA-DCA | WA6358747 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Francis Level - Basement - Control Room - CCTV camera 911 fault - See Notes Below | Security | CCTV Surveillance | 486.99 | Pass | Pass | 0 | 0 | 0.58333 | 2022-12-06 09:51 | 2022-12-09 17:00 | 2022-12-06 18:00 | 2022-12-09 17:00 | 2022-12-06 18:35 |  |  | Found camera not communicating SMS.Reinitialized camera in the field.Camera now tested and operating ok.
MSA-DCA | WA6360885 | 2 | ADVANCED LOCK & KEY | Ground Exterior - HV Power Recess - Lock requires new padlock - See Notes Below | Security | Locksmith | 235 | Pass | Pass | -1 | -1 | 0.58333 | 2022-12-07 16:39 | 2022-12-12 17:00 | 2022-12-08 15:00 | 2022-12-12 17:00 | 2022-12-08 15:35 |  |  | Workers Notes Supplied and put on padlock keyed to sample and WAS on high voltage gate 1x WAS 83/45 75mm SS shackle
MSA-DFES | WA6537686 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | ground yard area - Mains water tap (isolator) is leaking, requiring repair-see notes | Plumbing & Drainage | Water | 110.845 | Pass | Pass | 0 | 0 | 0.58333 | 2023-02-07 10:59 | 2023-02-10 17:00 | 2023-02-09 12:55 | 2023-02-10 17:00 | 2023-02-09 13:30
MSA-DTWD | WA6600717 | 2 | ADVANCED LOCK & KEY | Tumblers worn key struggles to turn - Photo Store loading dock nearest to Beauford st | Security | Locksmith | 240 | Pass | Pass | 0 | 0 | 0.58333 | 2023-02-17 09:48 | 2023-02-22 17:00 | 2023-02-21 12:25 | 2023-02-22 17:00 | 2023-02-21 13:00
MSA-DTAG | WA6680892 | 2 | GPS Plumbing & Gas Services PtyLtd | Staff Kitchen - Kitchen tap micer is spraying water erratically (see notes) | Plumbing & Drainage | Drainage | 196.4575 | Pass | Pass | -1 | -1 | 0.58333 | 2023-03-01 16:08 | 2023-03-07 17:00 | 2023-03-02 12:10 | 2023-03-07 17:00 | 2023-03-02 12:45
MSA-DTWD | WA5292723 | 0 | AHS Services WA Pty Ltd (Anchor) | Admin Building has no water - entire building | Plumbing & Drainage | Water | 107.2725 | Pass | Pass | 0 | 0 | 0.58333 | 2022-03-28 08:52 | 2022-03-28 10:52 | 2022-03-28 09:35 | 2022-03-28 12:52 | 2022-03-28 10:10 |  |  | Completed
MSA-DTWD | WA5296010 | 3 | Swan Pest Control | Unit G block - G block West - Automotive G Block Classrooms - mosquitos | Pest Control | General Pest | 295 | Fail | Fail | 0 | 0 | 0.58333 | 2022-03-30 08:34 | 2022-04-06 17:00 | 2022-04-07 05:50 | 2022-04-06 17:00 | 2022-04-07 06:25 |  |  | Sprayed all classrooms and undercover area with Bifrenthrin and Biflex Aqua
MSA-DTWD | WA5452867 | 2 | Swan Pest Control | b019 - dead rat smell in ceiling | Pest Control | General Pest | 95 | Pass | Pass | 0 | 0 | 0.58333 | 2022-05-17 09:24 | 2022-05-20 17:00 | 2022-05-19 10:20 | 2022-05-20 17:00 | 2022-05-19 10:55 |  |  | Dead rodent could not be located. Suggest that it may be in the wall which cannot be reached.
MSA-DTWD | WA5481068 | 2 | Water2water Pty Ltd | Room A018 - Zippy boil not heating water | Plumbing & Drainage | HWS/Units Electric & Gas | 405.835 | Pass | Pass | 0 | 0 | 0.58333 | 2022-05-30 10:46 | 2022-06-02 17:00 | 2022-06-02 11:50 | 2022-06-02 17:00 | 2022-06-02 12:25 |  |  | Replaced faulty Power pcb. All ok
MSA-DFES | WA5566648 | 2 | Water2water Pty Ltd | Kitchen - Zip Unit hot/cold not working (unit on right hand side) near the exit door | Plumbing & Drainage | HWS/Units Electric & Gas | 782.85 | Pass | Pass | -1 | -1 | 0.58333 | 2022-06-23 10:25 | 2022-06-28 17:00 | 2022-06-23 16:20 | 2022-06-28 17:00 | 2022-06-23 16:55 |  |  | Tester unit. No sign of water in unit even though in leak fault. Ran unit and no signs of leak. Customer to Monitor unit as was only a solitary fault logged and no sign of issue
MSA-DTAG | WA5585336 | 2 | Water2water Pty Ltd | Level 12-meeting room-Billi unit in meeting room. No hot water and cold is room temperature-see note | Plumbing & Drainage | Water | 300.175 | Pass | Pass | 0 | 0 | 0.58333 | 2022-07-05 14:58 | 2022-07-08 17:00 | 2022-07-06 12:20 | 2022-07-08 17:00 | 2022-07-06 12:55 |  |  | Replaced expired filter. Reconfigured setting as unit heads also been put into “locked off”
MSA-DCA | WA5686844 | 0 | Dormakaba Australia Pty Ltd | roller door and dock door-both stuck closed | Building | Doors | 220 | Pass | Pass | 0 | 0 | 0.58333 | 2022-08-01 11:15 | 2022-08-01 13:15 | 2022-08-01 12:44 | 2022-08-01 15:15 | 2022-08-01 13:19 |  |  | 1090991 - Inspection of gate found gates access control had no power but door was powered upAccess control require to find fault1068598 - Inspection of roller shutter found shutters access control had no power but door was powered upAccess control require to find fault
MSA-DCA | WA5838463 | 3 | GPS Plumbing & Gas Services PtyLtd | Staff female toilet - 1st cubicle - water leaking to pan | Plumbing & Drainage | Toilets/Cisterns | 72.98 | Pass | Pass | 0 | 0 | 0.58333 | 2022-09-08 13:34 | 2022-09-15 17:00 | 2022-09-13 08:35 | 2022-09-15 17:00 | 2022-09-13 09:10 |  |  | Replaced outlet washer
MSA-DTAG | WA6256732 | 2 | Bullant Security Pty Ltd | Level 1 - Switchboard room - Door lock is not engaging | Security | Security Management System | 155 | Pass | Pass | 0 | 0 | 0.58333 | 2022-11-24 08:36 | 2022-11-29 17:00 | 2022-11-29 08:50 | 2022-11-29 17:00 | 2022-11-29 09:25 |  |  | Attended site, repaired lock to allow door to be secured.Date on site: 29/11/2022Time on site: 08:50 - 09:25
MSA-DFES | WA6257264 | 2 | ADVANCED LOCK & KEY | Level 1 - Duty room - Door Lock/handle on duty room is broken to engine room | Security | Locksmith | 160 | Pass | Pass | -1 | -1 | 0.58333 | 2022-11-24 13:26 | 2022-11-29 17:00 | 2022-11-25 09:20 | 2022-11-29 17:00 | 2022-11-25 09:55 |  |  | Attend site to repair damaged lock on duty door Replaced broken screw and serviced lock
MSA-DTWD | WA6579084 | 2 | Dormakaba Australia Pty Ltd | Large roller door status /service light indicating | Building | Automatic Doors | 401.95 | Pass | Pass | -1 | -1 | 0.58333 | 2023-02-15 14:11 | 2023-02-20 17:00 | 2023-02-15 15:20 | 2023-02-20 17:00 | 2023-02-15 15:55
MSA-DTWD | WA5112035 | 2 | Dormakaba Australia Pty Ltd | - D-Block Ground Floor JSC the door closer has a bent arm and unpinned mechanism | Building | Automatic Doors | 180 | Pass | Pass | -1 | -1 | 0.58333 | 2022-02-10 12:34 | 2022-02-15 17:00 | 2022-02-11 09:40 | 2022-02-15 17:00 | 2022-02-11 10:15 |  |  | Manual screen door, the closer arm has broken off, and the bracket is bent, straightened bracket and refixed arm, tested all ok.
MSA-DTWD | WA5186585 | 1 | Water2water Pty Ltd | Block 9 - Staff kitchen - Boiling water unit has leaking tap | Plumbing & Drainage | Water | 247.9125 | Pass | Pass | 0 | 0 | 0.58333 | 2022-02-22 08:46 | 2022-02-23 17:00 | 2022-02-22 14:10 | 2022-02-23 17:00 | 2022-02-22 14:45 |  |  | REPLACED BROKEN RHEEM TAP CHECKED OK
MSA-DTWD | WA5193757 | 2 | Complete Pest Management Services | Student kitchen - rodent activity | Pest Control | General Pest | 210.23 | Pass | Pass | 0 | 0 | 0.58333 | 2022-02-25 13:52 | 2022-03-02 17:00 | 2022-03-01 13:25 | 2022-03-02 17:00 | 2022-03-01 14:00 |  |  | Inspected student kitchen area for rodent activity.Found some rat droppings near student fridge and Ed support fridge.Placed beta rodent bait stations next to both fridges for control of rodents.
MSA-DFES | WA5383824 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Shower head in female shower doom needs replacing | Plumbing & Drainage | Materials | 176.57 | Fail | Fail | 0 | 0 | 0.58333 | 2022-04-28 07:35 | 2022-05-02 17:00 | 2022-05-03 13:25 | 2022-05-02 17:00 | 2022-05-03 14:00 |  |  | Replaced shower head like for like in female showers tested and working
MSA-DTWD | WA5392215 | 1 | Swan Pest Control | D-Block - student services mouse issues needs baiting | Pest Control | General Pest | 207.5 | Pass | Pass | 0 | 0 | 0.58333 | 2022-05-03 08:37 | 2022-05-04 17:00 | 2022-05-04 11:10 | 2022-05-04 17:00 | 2022-05-04 11:45 |  |  | Installed 5 small lockable rodent stations and 10 Ditrac rodent blocks
MSA-DTAG | WA5488163 | 3 | Water2water Pty Ltd | Level 1 - DPP kitchen water filter light is flashing | Plumbing & Drainage | Water | 294.0925 | Pass | Pass | 0 | 0 | 0.58333 | 2022-06-02 10:45 | 2022-06-10 17:00 | 2022-06-07 15:15 | 2022-06-10 17:00 | 2022-06-07 15:50 |  |  | Replaced filter, flushed, reset timers and checked over unit
MSA-DTWD | WA5752509 | 2 | LIGHTHOUSE LOCKSMITHS | Interleading door - door handle broken on office door | Security | Locksmith | 117.8 | Pass | Pass | 0 | 0 | 0.58333 | 2022-08-17 11:53 | 2022-08-22 17:00 | 2022-08-19 08:30 | 2022-08-22 17:00 | 2022-08-19 09:05 |  |  | replaced broken spindles in lock on b block
MSA-DCA | WA6145783 | 1 | ADVANCED LOCK & KEY | Level 2 - HLT Sound Lock - Door handle has broken off | Security | Locksmith | 290 | Pass | Pass | 0 | 0 | 0.58333 | 2022-11-02 14:51 | 2022-11-03 17:00 | 2022-11-03 11:30 | 2022-11-03 17:00 | 2022-11-03 12:05 |  |  | Attend site to replace damaged lock on HLT level 12 1x CARPA8082SC
MSA-DFES | WA6393422 | 2 | Water2water Pty Ltd | Kitchen - Under sink filtered water system water tastes foul - See notes | Plumbing & Drainage | HWS/Units Electric & Gas | 303.255 | Pass | Pass | -1 | -1 | 0.58333 | 2022-12-28 14:16 | 2023-01-03 17:00 | 2022-12-28 15:40 | 2023-01-03 17:00 | 2022-12-28 16:15
MSA-DTWD | WA6465080 | 2 | Swan Pest Control | Block C- Room C107 & C120- pest spray | Pest Control | General Pest | 250 | Pass | Pass | 0 | 0 | 0.58333 | 2023-01-17 11:33 | 2023-01-20 17:00 | 2023-01-19 09:15 | 2023-01-20 17:00 | 2023-01-19 09:50
MSA-DFES | WA6540747 | 3 | ADVANCED LOCK & KEY | Ground level - Large lockers not working (see notes) | Security | Locksmith | 250 | Pass | Pass | 0 | 0 | 0.58333 | 2023-02-09 13:19 | 2023-02-16 17:00 | 2023-02-15 15:15 | 2023-02-16 17:00 | 2023-02-15 15:50
MSA-DCA | WA5676566 | 3 | Earth & Water Pty Ltd | Urban Orchard - Lawn Area - Missing sprinkler | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 0.56667 | 2022-07-25 09:24 | 2022-08-01 17:00 | 2022-07-25 12:01 | 2022-08-01 17:00 | 2022-07-25 12:35 |  |  | Job copmleted - Arrived on site; replaced sprinkler on lawn area.
MSA-DTAG | WA5294249 | 2 | Gilmour & Jooste Electrical | Custody - Mens Toilet - light has blown | Electrical | Lighting, Internal | 69.25 | Pass | Pass | 0 | 0 | 0.56667 | 2022-03-28 14:52 | 2022-03-31 17:00 | 2022-03-29 07:45 | 2022-03-31 17:00 | 2022-03-29 08:19 |  |  | Replaced faulty fluro tube and starter in men’s toilet
MSA-DTAG | WA5569581 | 0 | Dormakaba Australia Pty Ltd | Main revolving auto door is not securing. | Building | Doors | 450 | Pass | Pass | 0 | 0 | 0.56667 | 2022-06-27 17:12 | 2022-06-27 19:12 | 2022-06-27 19:00 | 2022-06-27 21:12 | 2022-06-27 19:34 |  |  | Found door locked and displaying no faults on arrival. Checked all modes and tested. No fault found. Security reported that the stop button had been pressed which may have been the cause.
MSA-MRWA | WA6190372 | 1 | Schindler Lifts Australia | Lift 3 is stuck open on level 5 | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0.56667 | 2022-11-16 07:53 | 2022-11-16 17:00 | 2022-11-18 15:23 | 2022-11-16 17:00 | 2022-11-18 15:57 |  |  | Works completed - close out at $0
MSA-DTWD | WA6373540 | 0 | Dormakaba Australia Pty Ltd | West auto door - Broken away from the track and cant be secured. | Building | Automatic Doors | 255.86 | Pass | Pass | 0 | 0 | 0.56667 | 2022-12-14 15:06 | 2022-12-14 17:06 | 2022-12-14 16:03 | 2022-12-14 19:06 | 2022-12-14 16:37 |  |  | Found doors have been struck and are out of alignment. L/H floor guide is broken. Replaced broken floor guide and adjusted doors. All ok.
MSA-DTWD | WA6517934 | 1 | Precise Air Group | M Block - BMS not turning on A/C to | Air Conditioning | Building HVAC Maintenance (Major Plant) | 570.43 | Pass | Pass | 0 | 0 | 0.56667 | 2023-01-24 14:31 | 2023-01-25 17:00 | 2023-01-25 10:29 | 2023-01-25 17:00 | 2023-01-25 11:03
MSA-DCA | WA6683377 | 0 | TK Elevator Australia Pty Ltd | Ground floor - Platform lift - Doors arent opening | Lifts | Lifts | 590 | Fail | Pass | 0 | 0 | 0.56667 | 2023-03-03 08:19 | 2023-03-03 10:19 | 2023-03-03 11:30 | 2023-03-03 12:19 | 2023-03-03 12:04
MSA-DTWD | WA6693430 | 3 | AWB Co. | 2 lights with broken diffusers | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 0.56667 | 2023-03-10 10:07 | 2023-03-17 17:00 | 2023-03-14 08:26 | 2023-03-17 17:00 | 2023-03-14 09:00
MSA-DTWD | WA5472948 | 2 | Dormakaba Australia Pty Ltd | B21 - Auto Doors have power but not operational | Building | Automatic Doors | 242.05 | Pass | Pass | 0 | 0 | 0.55 | 2022-05-24 11:52 | 2022-05-27 17:00 | 2022-05-24 15:41 | 2022-05-27 17:00 | 2022-05-24 16:14 |  |  | Found that the door has been switched off at the controller and the battery has gone flat, switched back on, replaced battery and tested, all ok.
MSA-DCA | WA5477511 | 1 | GPS Plumbing & Gas Services PtyLtd | Hot water unit fault. Dial showing 75, affecting labs on ground and first floor. | Plumbing & Drainage | HWS/Units Electric & Gas | 160.2625 | Pass | Pass | 0 | 0 | 0.55 | 2022-05-25 14:13 | 2022-05-26 17:00 | 2022-05-26 12:50 | 2022-05-26 17:00 | 2022-05-26 13:23 |  |  | Reset non potable hot water unit in plantroom level 1
MSA-DFES | WA5487689 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Bathroom - lack of water pressure to the whole bathroom - see notes below | Plumbing & Drainage | Water | 180.55 | Pass | Pass | 0 | 0 | 0.55 | 2022-06-02 07:56 | 2022-06-02 17:00 | 2022-06-02 09:48 | 2022-06-02 17:00 | 2022-06-02 10:21 |  |  | Flushed the shower heads out due to there was a bit of sand stuck in the shower head tested everything else and the staff are happy.
MSA-DCA | WA5649630 | 0 | TK Elevator Australia Pty Ltd | Lift out of order in building | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.55 | 2022-07-17 09:31 | 2022-07-17 11:31 | 2022-07-17 10:50 | 2022-07-17 13:31 | 2022-07-17 11:23 |  |  | Lift found 130mm below the bottom floor level with final limit switch activated on arrival and indicating 00 on display. Drove lift up off the bottom final limitswitch on inspection and indicator changed to 88 on display. Reset main board and all reset ok and lift started operating correctly.
MSA-DTAG | WA5513436 | 1 | Gilmour & Jooste Electrical | Admin - Front entrance/exit to Complex- automatic door has stopped working- see notes below | Building | Automatic Doors | 64.835 | Pass | Pass | 0 | 0 | 0.55 | 2022-06-14 10:33 | 2022-06-15 17:00 | 2022-06-14 11:15 | 2022-06-15 17:00 | 2022-06-14 11:48 |  |  | Inspected faulty to automatic door. Tripped RCD found. Reset RCD and tested door. All in good working order. No cause evident to tripped RCD.
MSA-MRWA | WA5194688 | 1 | GPS Plumbing & Gas Services PtyLtd | urinal not flushing | Plumbing & Drainage | Toilets/Cisterns | 160.2625 | Pass | Pass | 0 | 0 | 0.55 | 2022-02-28 08:27 | 2022-03-01 17:00 | 2022-03-01 11:23 | 2022-03-01 17:00 | 2022-03-01 11:56 |  |  | Inspected male urinal firstfloor no power to outlet at the back needs electrician to inspect
MSA-DCA | WA5879934 | 0 | Dormakaba Australia Pty Ltd | William street side entrance door - Door not locking | Building | Security Doors | 220 | Pass | Pass | 0 | 0 | 0.55 | 2022-09-15 10:11 | 2022-09-15 12:11 | 2022-09-15 12:08 | 2022-09-15 14:11 | 2022-09-15 12:41 |  |  | William street Side gate - Inspected gate and found that the electric strike is not locking, spoke with site and advised them to call out the access techs to investigate.
MSA-DTAG | WA5203750 | 1 | FSA (WA) Pty Ltd | Zone 3 fire alarm fault - see notes - | Fire Protection Services | Fire Protection - Monitor System | 99.37 | Pass | Pass | 0 | 0 | 0.53333 | 2022-03-03 16:27 | 2022-03-04 17:00 | 2022-03-04 06:55 | 2022-03-04 17:00 | 2022-03-04 07:27 |  |  | Attended site to investigate false alarm. Found that there had been a test conducted yesterday and the people conducting have called out fire brigade. Not sure what has happened but it looks like the code red has been turned on when there was still an alarm active on the code red. This has then called out fire brigade. When I arrived code red still had alarm on it and zone 3 isolated and sitting normal. Spoke with security and I have reset the system and taken the isolation off the panel. All back to normal.
MSA-DTAG | WA5462058 | 2 | Water2water Pty Ltd | Level 1 - Kitchen - Zip hydro tap change filter light flashing - Service required | Plumbing & Drainage | HWS/Units Electric & Gas | 264.925 | Pass | Pass | 0 | 0 | 0.53333 | 2022-05-19 10:55 | 2022-05-24 17:00 | 2022-05-23 12:30 | 2022-05-24 17:00 | 2022-05-23 13:02 |  |  | Asset captured.. filter change and operation check. All ok
MSA-MRWA | WA6111585 | 1 | Dormakaba Australia Pty Ltd | Main auto gate not opening | Building | Steel Fencing & Gates | 186.95 | Pass | Pass | 0 | 0 | 0.53333 | 2022-10-21 08:59 | 2022-10-24 17:00 | 2022-10-21 11:45 | 2022-10-24 17:00 | 2022-10-21 12:17 |  |  | Gate was in stopped fault. Reset unit. Tested. All good.
MSA-DTAG | WA4992385 | 3 | Sapio Pty Ltd | Request for swipe cards and return “broken” ones - see notes below | Security | Access Control | 239.26 | Fail | Fail | 1 | 1 | 0.53333 | 2022-01-06 10:56 | 2022-01-13 17:00 | 2022-01-21 11:28 | 2022-01-13 17:00 | 2022-01-21 12:00 |  | WACCES | Work performed by Ken Moore 21/01/2022:Delivered 2 x new Airkeys (270 & 271) to Louise Parkinson.Job completed.
MSA-DFES | WA5377686 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - External Toilet, Adjacent to rear entry door - Water ingress- water damage -mould on wall | Plumbing & Drainage | Water | 86.35 | Pass | Pass | 0 | 0 | 0.53333 | 2022-04-20 08:27 | 2022-04-28 17:00 | 2022-04-26 10:16 | 2022-04-28 17:00 | 2022-04-26 10:48 |  |  | Inspected possible water leak in toilet out side there is no water in that area
MSA-DTWD | WA5679774 | 1 | Dormakaba Australia Pty Ltd | Faulty door closer – hard to open once inside | Building | Doors | 180 | Pass | Pass | 0 | 0 | 0.53333 | 2022-07-27 07:09 | 2022-07-27 17:00 | 2022-07-27 08:46 | 2022-07-27 17:00 | 2022-07-27 09:18 |  |  | Door was working correctly on arrival, found external push button was loose, tightened loose button, checked all fixings and buttons, tested door operation a number of times, all working fine.
MSA-DCA | WA5689662 | 1 | Dormakaba Australia Pty Ltd | james st gate, electronic lock not operating-Gate is not opening or closing by the key currently, | Building | Steel Fencing & Gates | 220 | Pass | Pass | 0 | 0 | 0.53333 | 2022-08-02 12:50 | 2022-08-03 17:00 | 2022-08-03 15:43 | 2022-08-03 17:00 | 2022-08-03 16:15 |  |  | Tested gate motor. Found an issue with the power supply. But due to the corrosion all over. Recommend replacing the whole unit with a centsys D10 which will also require a new set of battery operated beams and possibly replacing the rack as well. Please quote
MSA-DCA | WA6292285 | 1 | Dormakaba Australia Pty Ltd | RETROSPECTIVE - South entry automatic door - External right side door is wobbling | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.53333 | 2022-08-23 11:31 | 2022-08-24 17:00 | 2022-08-23 12:11 | 2022-08-24 17:00 | 2022-08-23 12:43 | 1 |  | Attended site, refitted and adjusted both floor guides, tested door operation a number of times, all Ok.
MSA-DFES | WA6356693 | 3 | Dom's Total Grounds Maintenance | Yard - Weeds require spraying over entire property | Landscaping & Gardening | Grounds Maintenance | 193.68 | Pass | Pass | -1 | -1 | 0.53333 | 2022-12-05 08:55 | 2022-12-12 17:00 | 2022-12-06 08:38 | 2022-12-12 17:00 | 2022-12-06 09:10 |  |  | Dom Coniglio has completed a weedspray
MSA-DFES | WA5133856 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Car Park - The metal drain cover has moved and leaving a hole in the drain and is a | Plumbing & Drainage | Materials | 204.1 | Pass | Pass | 0 | 0 | 0.53333 | 2022-02-15 15:20 | 2022-02-22 17:00 | 2022-02-22 13:14 | 2022-02-22 17:00 | 2022-02-22 13:46 |  |  | Had to move great to cover a 40mm hole in a spoon drain and tighten 2 nuts to lock it in place.
MSA-MRWA | WA6231980 | 1 | Dormakaba Australia Pty Ltd | RNOC-Metal gate 1 doesn't open .gate 2 is stuck open | Building | Materials | 345 | Pass | Pass | 0 | 0 | 0.53333 | 2022-11-19 06:34 | 2022-11-21 17:00 | 2022-11-21 10:14 | 2022-11-21 17:00 | 2022-11-21 10:46 |  |  | Gate has been damaged. P.E beams cut and knocked off, mag lock cut, break glass smashed and cut.
MSA-MRWA | WA5238797 | 1 | Water2water Pty Ltd | Billi tap showing fault message | Plumbing & Drainage | Water | 117.925 | Pass | Pass | 0 | 0 | 0.51667 | 2022-03-16 09:09 | 2022-03-17 17:00 | 2022-03-16 13:50 | 2022-03-17 17:00 | 2022-03-16 14:21 |  |  | Unit logged one isolated “level fail” fault at 7.08am this morning. Unit has run without fault since and tested correctly whilst on site. No parts were changed. How ever if the issue does re occur I’d suggest changing the level sensors and loom. How ever for isolated fault and the unit testing correctly. I didn’t change at time.
MSA-DCA | WA5792444 | 0 | TK Elevator Australia Pty Ltd | RETROSPECTIVE WORK ORDER-Lift fault-DO NOT ATTEND | Lifts | Lifts | 1242 | Pass | Pass | 0 | 0 | 0.51667 | 2022-08-20 21:09 | 2022-08-20 23:09 | 2022-08-20 21:48 | 2022-08-21 01:09 | 2022-08-20 22:19 | 1 |  | Upon arrival I found the lift running and the passenger was no longer trapped, i tested the lift and it operatedcorrectly. The on site staff did mention the it was a self propelled mobility chair which may have tripped the safety pe beam during travel. The lift was running correctly ondeparture
MSA-DCA | WA6291467 | 1 | Dormakaba Australia Pty Ltd | Eastern roller door - Part fell from mechanism, roller door becomes stuck while closing - see notes | Building | Automatic Doors | 226.95 | Pass | Pass | 0 | 0 | 0.51667 | 2022-11-28 15:48 | 2022-11-29 17:00 | 2022-11-29 07:50 | 2022-11-29 17:00 | 2022-11-29 08:21 |  |  | Door had slat end clip jam and had come away from Curtin. Inspected door and tested, door is safe and working correctly
MSA-DTWD | WA5288912 | 1 | Dormakaba Australia Pty Ltd | Block1 - North auto door to foyer - Door not opening or closing fully again | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.51667 | 2022-03-23 15:33 | 2022-03-24 17:00 | 2022-03-23 16:19 | 2022-03-24 17:00 | 2022-03-23 16:50 |  |  | 1046630. Programmed barcode number A403131078.Arrived on-site and found door only closing halfway. Removed door and found floor guide was tight in bottom door rail causing door to obstruct, re positioned floor guide and re fixed door, reset and tested all ok. Advised campus manager that door is very old and is showing signs of wear on motor gearbox and electrical components and highly recommend upgrading door. Quote required to replace SL200 for NON locking ES200 operator with IXIO, microhead and M4 mode switch.
MSA-DTWD | WA5412967 | 2 | LIGHTHOUSE LOCKSMITHS | Kendrew- C-Block 1st Floor room C112 door lock faulty | Security | Locksmith | 170 | Pass | Pass | -1 | -1 | 0.51667 | 2022-05-12 08:06 | 2022-05-17 17:00 | 2022-05-12 12:13 | 2022-05-17 17:00 | 2022-05-12 12:44 |  |  | replaced cylinder keyed back to door 31 (c112) and tightened loose handles
MSA-MRWA | WA5480851 | 1 | Dormakaba Australia Pty Ltd | Front boom gate - not working - access reader is not working | Building | General Building | 180 | Pass | Pass | 0 | 0 | 0.51667 | 2022-05-30 08:30 | 2022-05-31 17:00 | 2022-05-30 10:17 | 2022-05-31 17:00 | 2022-05-30 10:48 |  |  | Immediately after arriving onsite Danika informed me that the job should have been sent to Siemens and not Dormakaba.Checked boom gate and found that it is being held open by access input.
MSA-MRWA | WA5679294 | 1 | GPS Plumbing & Gas Services PtyLtd | Two blocked toilets | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 0.51667 | 2022-07-26 12:36 | 2022-07-27 17:00 | 2022-07-26 13:25 | 2022-07-27 17:00 | 2022-07-26 13:56 |  |  | Cleared blocked toilets x 2 male toilets level 6
MSA-DTWD | WA5799689 | 3 | ACTION GLASS & ALUMINIUM | Room 219 - damaged window film | Glazing | Window Glass | 342.02 | Fail | Fail | 1 | 1 | 0.51667 | 2022-08-30 13:33 | 2022-09-06 17:00 | 2022-09-15 07:59 | 2022-09-06 17:00 | 2022-09-15 08:30 |  |  | ATTENDED SITE, REMOVED FROST TINT TO 2X DOORS
MSA-MRWA | WA6516734 | 1 | Dormakaba Australia Pty Ltd | Front reception sliding door failing to open/close | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.51667 | 2023-01-23 14:20 | 2023-01-24 17:00 | 2023-01-23 15:45 | 2023-01-24 17:00 | 2023-01-23 16:16
MSA-DCA | WA5497162 | 2 | Earth & Water Pty Ltd | Ground - External - Rectic sprinker leaking in garden bed in urban orchard - close to PICA Building | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 0.51667 | 2022-06-09 14:59 | 2022-06-14 17:00 | 2022-06-10 12:44 | 2022-06-14 17:00 | 2022-06-10 13:15 |  |  | water in the pipes will still be flowing down hill causing the sprinkler to look as if it is still turned on. Leaks identified on urban orchard, someone has cut the drip line. Repaired with drip fittings. water in the pipes will still be flowing down hill causing the sprinkler to look as if it is still turned on.Leaks identified on urban orchard, someone has cut the drip line. Repaired with drip fittings.
MSA-DFES | WA4986317 | 3 | Protek 24/7 Building & Maintenance | Main Administration - Carers Room - Air Conditioner outlet and ceiling panel out of place | Building | General Building | 113.73 | Pass | Pass | -1 | -1 | 0.5 | 2021-12-31 16:27 | 2022-01-10 17:00 | 2022-01-04 14:00 | 2022-01-10 17:00 | 2022-01-04 14:30 |  |  | Aircon vent and ceiling panel shifted Put it back in place
MSA-DFES | WA4991059 | 3 | SONTEC WA PTY LTD | Applied Training Ground - Cube - See notes below | Security | Monitoring | 230 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-04 14:45 | 2022-01-11 17:00 | 2022-01-06 13:15 | 2022-01-11 17:00 | 2022-01-06 13:45 |  |  | 6/1/21 - Dylan ParslowFaults on fire panel. Fire contractor required.
MSA-DTWD | WA4992619 | 3 | AWB Co. | S block - room S213 - damaged Wifi units - detaching from ceilings | Building | Ceiling | 119.66 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-06 14:34 | 2022-01-13 17:00 | 2022-01-13 12:30 | 2022-01-13 17:00 | 2022-01-13 13:00 |  |  | Attended site and signed in. Completed jsa. Met with IT guy on site and located wifi units and discussed where he wanted them, and what one was allocated to eat port on roof. Secured brackets to roof and connected cable from wifi box to port on roof. Took after pictures. Completed paperwork. Signed out.Job completed
MSA-DTWD | WA5009964 | 0 | FSA (WA) Pty Ltd | Admin building - lost power, please check fire panel faults - code red alarms | Fire Protection Services | Fire Protection - Monitor System | 99.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-12 08:50 | 2022-01-12 10:50 | 2022-01-12 09:30 | 2022-01-12 12:50 | 2022-01-12 10:00 |  | WCAPPR | Arrive to find Mains power turned off due to issues with switchboard. Fire panel is operating on batteries. We are unable to do anything until the power is back on and then we can come back and clear any faults present. Batteries could need replacing if they don’t charge back up once power goes back on. Received a call from Matt once power had been turned on and I was able to talk him through resetting the code red. The fire panel and EWIS had already cleared itself. All ok and system back online.
MSA-DTWD | WA5052976 | 2 | Securex Security Systems & Services | Ground - Block L - Creche - Double Door reader faulty | Security | Keys & Access | 329.27 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-18 11:29 | 2022-01-21 17:00 | 2022-01-20 08:00 | 2022-01-21 17:00 | 2022-01-20 08:30 |  |  | 20/1/2022No resistors in reed. Add resistors and cleared alarm
MSA-DTAG | WA5053140 | 3 | Total Security Systems Pty Ltd | Cell 2 out of action due to buzzer and intercom not working properly. (possible warranty) | Security | Monitoring |  | Pass | Pass | -1 | -1 | 0.5 | 2022-01-18 13:31 | 2022-01-25 17:00 | 2022-01-18 14:00 | 2022-01-25 17:00 | 2022-01-18 14:30 |  |  | Warranty job - completed prior to Christmas - NO CHARGE
MSA-DTWD | WA5069187 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 125.18 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-19 16:30 | 2022-01-27 17:00 | 2022-01-27 11:45 | 2022-01-27 17:00 | 2022-01-27 12:15 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B03 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box lcated in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DTWD | WA5069191 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 148.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-19 16:34 | 2022-01-27 17:00 | 2022-01-27 13:15 | 2022-01-27 17:00 | 2022-01-27 13:45 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B46 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box located in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DTWD | WA5081421 | 3 | ADVANCED LOCK & KEY | Repair locks to small cabinets in S109 | Security | Locksmith | 235 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-20 13:47 | 2022-01-28 17:00 | 2022-01-24 09:50 | 2022-01-28 17:00 | 2022-01-24 10:20 |  |  | Replace faulty cupboard lock.Install cupboard lock and make keys.
MSA-DCA | WA5087928 | 1 | Precise Air Group | Last Cubicle - aircon leaking into the cubicle | Air Conditioning | Building HVAC Maintenance (Major Plant) | 120.36 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-24 14:51 | 2022-01-25 17:00 | 2022-01-24 15:30 | 2022-01-25 17:00 | 2022-01-24 16:00 |  |  | Found plumbing drain from floor above leaking. Reported to customer
MSA-DTAG | WA5090216 | 2 | Bullant Security Pty Ltd | Staff only door across from Caffissimo - is not locking properly – the lock appears to get stuck out | Security | Locksmith | 258.64 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-25 10:23 | 2022-01-31 17:00 | 2022-01-27 14:00 | 2022-01-31 17:00 | 2022-01-27 14:30 |  |  | Attended site to replace faulty mortice lock on staff door adjacent to Caffissimo.Date on site: 27/01/2022Time on site: 02:00pm - 02:30pm
MSA-DFES | WA5100855 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Electric power point it is arking in the kitchen . | Electrical | General Electrical | 88.44 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-03 07:05 | 2022-02-03 17:00 | 2022-02-03 10:15 | 2022-02-03 17:00 | 2022-02-03 10:45 |  |  | Arrived on site. Replaced faulty GPO with new. Advised staff of work completed.
MSA-DCA | WA5101061 | 1 | Protek 24/7 Building & Maintenance | Substage / BOH corridor - Handle on fire door has broken | Building | Doors | 108.23 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-03 09:19 | 2022-02-04 17:00 | 2022-02-03 14:00 | 2022-02-04 17:00 | 2022-02-03 14:30 |  |  | Repair handle on fire door
MSA-DTAG | WA5101366 | 2 | Sapio Pty Ltd | Ground - Entrance desk - PA system not operational | Security | Security Management System | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-03 11:37 | 2022-02-08 17:00 | 2022-02-07 09:30 | 2022-02-08 17:00 | 2022-02-07 10:00 |  |  | PA system reset at desk and working all okay, tested good.
MSA-DCA | WA5101779 | 1 | Techworks Plumbing | Old Jail/Goal - External building surrounds - see details | Plumbing & Drainage | Water | 370.54 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-03 14:43 | 2022-02-04 17:00 | 2022-02-03 17:00 | 2022-02-04 17:00 | 2022-02-03 17:30 |  |  | Tundish around building blocked with pebble rocks Cleared drains and blockage
MSA-DFES | WA5108473 | 1 | Australian HVAC Services Pty. Ltd. | Dorm 3 (Room 20) - Aircon is not working with error code: CH67 | Air Conditioning | Room Air Conditioners | 99.42 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-08 14:22 | 2022-02-09 17:00 | 2022-02-09 08:00 | 2022-02-09 17:00 | 2022-02-09 08:30 |  |  | Attempted to access site at 8:15am & 10:30am (09/02/21), no fire-fighters onsite, returned to site 8am (10/02/21). Arrived onsite, signed in & spoke to onsite representative who directed me to dorms with faulty A/C units, began investigation & found that we already have a repair job open for this unit. We had been waiting on parts, although parts have now arrived as of late last week. Repairs will be carried out today.Ref work order - WA4958783
MSA-DTAG | WA5109520 | 1 | Sapio Pty Ltd | Lift C - Unlocked when it should be restricted | Security | CCTV Surveillance | 130 | Fail | Fail | 0 | 0 | 0.5 | 2022-02-09 11:01 | 2022-02-10 17:00 | 2022-02-11 15:30 | 2022-02-10 17:00 | 2022-02-11 16:00 |  |  | Organised Schindler to attend and rectify. tested lift functions after schindler completed works
MSA-DTWD | WA5112080 | 2 | BJ SYSTEMS | E Block - Ground - Main Entrance - door beeping from cardax system | Building | General Building | 80 | Pass | Pass | -1 | -1 | 0.5 | 2022-02-10 12:59 | 2022-02-15 17:00 | 2022-02-11 14:00 | 2022-02-15 17:00 | 2022-02-11 14:30 |  |  | E Block ground main entrance and loading bay keypads were beeping when door opened. Found area was still armed and going into entry and exit delay causing warnings on keypads. No siren outputs and unlatched alarms set to 1, so no external activations were on
MSA-DTWD | WA5116044 | 2 | ECO PLUMBING AND GAS PTY LTD | E Block - Ground - E58 Large Scale Kitchen - Cleaner’s tap is leaking | Plumbing & Drainage | Materials | 91.57 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-11 10:58 | 2022-02-16 17:00 | 2022-02-14 11:00 | 2022-02-16 17:00 | 2022-02-14 11:30 |  |  | Tightened nut on tap
MSA-DTWD | WA5133717 | 2 | Swan Pest Control | Ground - Staff lunch room - AT229 - Ant infestation | Pest Control | General Pest | 220 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-15 13:13 | 2022-02-18 17:00 | 2022-02-17 09:30 | 2022-02-18 17:00 | 2022-02-17 10:00 |  |  | Sprayed perimeter of lunch room and adjacent office with Fipronil @ .6%
MSA-DFES | WA5140735 | 2 | Australian HVAC Services Pty. Ltd. | Ground floor - Meeting Room - Air conditioning drain pipes still blocking | Air Conditioning | Room Air Conditioners | 173.66 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-16 07:02 | 2022-02-18 17:00 | 2022-02-16 14:00 | 2022-02-18 17:00 | 2022-02-16 14:30 |  |  | Investigated condensate drain blockage. Recommend plumber carry out further investigation.
MSA-DTWD | WA5141469 | 1 | Securex Security Systems & Services | Campus - Ground - Alarm power fail constant beeping sound around site | Security | Monitoring | 154.55 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-16 10:29 | 2022-02-17 17:00 | 2022-02-16 11:45 | 2022-02-17 17:00 | 2022-02-16 12:15 |  |  | Ian Fouche (16/02/2022, 1145-1215) - Work NoteElectricians disconnected the dgp and battery due to construction.They also cut the wires and planning on rejoining them later once demolition is finished.Disabled dgp4 and ras6. Area 6 is off-line. They will call once we can return to re connect
MSA-DTAG | WA5151229 | 1 | Schindler Lifts Australia | Basement, Level 1, Level 2 - Lift 2 - Lift is not leveling with the floor when stopping at each lev | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.5 | 2022-02-17 11:39 | 2022-02-18 17:00 | 2022-02-17 13:15 | 2022-02-18 17:00 | 2022-02-17 13:45 |  |  | to be closed out at $0 cost
MSA-DTAG | WA5201515 | 1 | Water2water Pty Ltd | Marriage reception/ duress alarm - Billy Tap in the staff café is not providing cold water | Plumbing & Drainage | Water | 184.745 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-02 16:01 | 2022-03-03 17:00 | 2022-03-03 11:00 | 2022-03-03 17:00 | 2022-03-03 11:30 |  |  | replaced solenoid
MSA-DFES | WA5206727 | 2 | Go Doors | Engine Room doors remote not working Fallen apart inside main housing - see notes below | Building | Automatic Doors | 380 | Fail | Fail | 1 | 1 | 0.5 | 2022-03-08 09:04 | 2022-03-11 17:00 | 2022-03-15 08:00 | 2022-03-11 17:00 | 2022-03-15 08:30 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5206794 | 2 | Anvil Doors | Engine Room - Door #4 – Guide roller has come off on one side | Building | Automatic Doors | 350 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-08 09:29 | 2022-03-11 17:00 | 2022-03-08 11:20 | 2022-03-11 17:00 | 2022-03-08 11:50 |  |  | Attended Claremont fire station. Right hand bearing that runs on the ramp has worn out. Technician tightened circlip and replaced bearing and washer. Technician ran through several cycles of the door and the door appears to be running fine again.Please note that no one was on site to sign off the signature slip
MSA-DFES | WA5216375 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Rear yard - power point located outside Gym wall facing east is not working - see notes | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-11 09:32 | 2022-03-18 17:00 | 2022-03-18 08:00 | 2022-03-18 17:00 | 2022-03-18 08:30 |  |  | Onsite 8am signed in and fault find power point. Slight water ingress cleaned out and resealed. Tested and all working informed staff and signed out 830.
MSA-MRWA | WA5238758 | 2 | AWB Co. | Asphalt lab hallway - Emergency light not working (LED) | Electrical | General Electrical | 122.21 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-16 08:49 | 2022-03-21 17:00 | 2022-03-21 11:00 | 2022-03-21 17:00 | 2022-03-21 11:30 |  |  | Attended site signed in completed jsa. Found reported fault by manager. EM light has been knocked off the base plate. Pushed back on and now works correctly. ***job completed***
MSA-DFES | WA5271252 | 1 | Anvil Doors | Engine Room - Front door for the pump - door wont open all to the top (bi-fold door) | Building | Automatic Doors | 490 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-18 09:24 | 2022-03-21 17:00 | 2022-03-18 10:15 | 2022-03-21 17:00 | 2022-03-18 10:45 |  |  | Attended Claremont fire station and adjusted door # 1. Technician found that the clutch was slipping. Technician re adjusted the clutch and tested door to be functioning all OK. Please see attached signature slip.Thank you
MSA-DTAG | WA5287740 | 2 | Midolo Building Services | Ground - male toilets - West wing (judicial Corridor) - door handle inside male toilets is broken | Building | Doors | 99.92 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-22 15:18 | 2022-03-25 17:00 | 2022-03-23 08:00 | 2022-03-25 17:00 | 2022-03-23 08:30 |  |  | door handle secured/repaired
MSA-DCA | WA5288314 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Gournd floor - Entry - revolving doors not working | Building | Automatic Doors | 358 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-23 09:23 | 2022-03-24 17:00 | 2022-03-23 11:45 | 2022-03-24 17:00 | 2022-03-23 12:15 |  | WCAPPR | Attended site and inspected revolving door. Noted from staff, door went into fault mode this morning. Note this will continue until quote is approvedand works can be completed. Staff on site are aware. Quoted previously on 09/09/2021
MSA-DTAG | WA5288793 | 3 | Gilmour & Jooste Electrical | Custody - Water is entering light fitting – fitting to be removed to allow plumbers access | Electrical | General Electrical | 64.835 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-23 13:31 | 2022-03-30 17:00 | 2022-03-29 07:15 | 2022-03-30 17:00 | 2022-03-29 07:45 |  |  | Met plumbers on-site and removed light fitting for access
MSA-DCA | WA5289893 | 0 | CONNECT SECURITY SYSTEMS | G block - Dis engage the alarms – blue strobe | Security | CCTV Surveillance | 153.18 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-24 14:01 | 2022-03-24 16:01 | 2022-03-24 15:55 | 2022-03-24 18:01 | 2022-03-24 16:25 |  |  | Disabled G Block Public Toilet Alarm System while Lead Paint being tested in E Block
MSA-DTAG | WA5291174 | 1 | Midolo Building Services | Court 1 - Custody door in Court 1 is not closing properly, gets caught - see notes below | Building | Doors | 92.52 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-25 16:09 | 2022-03-28 17:00 | 2022-03-28 08:45 | 2022-03-28 17:00 | 2022-03-28 09:15 |  |  | door and fixings repaired
MSA-DTAG | WA5297881 | 3 | Gilmour & Jooste Electrical | Ground - Cell 4 - 1 Fluorescent in cell 4 needs replacing | Electrical | General Electrical | 77.04 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-31 13:47 | 2022-04-07 17:00 | 2022-04-06 10:15 | 2022-04-07 17:00 | 2022-04-06 10:45 |  |  | Replaced blown fluro in cell 4
MSA-DTWD | WA5304108 | 2 | AWB Co. | Block 8 - Ground - 8G41 - Main light switch faulty | Electrical | General Electrical | 198.85 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-04 14:47 | 2022-04-07 17:00 | 2022-04-05 09:30 | 2022-04-07 17:00 | 2022-04-05 10:00 |  |  | Attended site signed in completed jsa. Spke with site FM about works on site. Got keys for access. found faulty light switches in building. Isolated two circuits and replaced with two new switch mechs. Tested ok now and works correctly.*** job completed ***
MSA-DTWD | WA5307411 | 2 | Critical Fire Protection & Training | Male toilets - Workshops fire alarm activation | Fire Protection Services | Fire Protection - Monitor System | 274.14 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-07 13:29 | 2022-04-12 17:00 | 2022-04-11 13:13 | 2022-04-12 17:00 | 2022-04-11 13:43 |  |  | Call-out to fire alarm activation. Found male toilets had an alarm on 7/4/22. No obvious reason for activation. Replaced detector.1 x addressable smoke detector used. 2 x techs on site. Time on site: 1.13time left site: 1.43
MSA-DTWD | WA5312053 | 2 | Securex Security Systems & Services | Slip Street - Wooden Boat works - Alarm not working - see notes | Security | Security Management System | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-11 10:37 | 2022-04-14 17:00 | 2022-04-12 11:00 | 2022-04-14 17:00 | 2022-04-12 11:30 |  |  | PIR (zone 9) false alarming.Cleaned PIR and moved cables which were dangling in front of PIR.
MSA-DTWD | WA5318151 | 1 | Critical Fire Protection & Training | Opp E- Cafe - Admin Fire panel in fault | Fire Protection Services | Fire Protection - Monitor System | 279.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-12 08:56 | 2022-04-13 17:00 | 2022-04-12 14:00 | 2022-04-13 17:00 | 2022-04-12 14:30 |  |  | Call out for fault to fire panel. Detector 64 loop 1 in maintenance fault on arrival .Located and replaced detector head with new addressable ampac detector. Fault cleared on panel after replacement and system reset.
MSA-DFES | WA5319248 | 2 | Protek 24/7 Building & Maintenance | DOSS OFFICE SOC - nternal door in between DOSS office and Com Cen | Building | Doors | 163 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-12 13:53 | 2022-04-19 17:00 | 2022-04-13 08:00 | 2022-04-19 17:00 | 2022-04-13 08:30 |  | WACCES | Repair Internal door
MSA-DCA | WA5335932 | 1 | Critical Fire Protection & Training | Electric wires above the fire panel making a distinct buzzing sound | Electrical | General Electrical | 125.52 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-16 09:55 | 2022-04-17 09:55 | 2022-04-16 11:00 | 2022-04-17 09:55 | 2022-04-16 11:30 |  |  | Determined buzzing sound IS NOT coming from fire panel or EWSGot ladder to determine if it’s from “Colt smoke curtain power unit” above panelSound does not get louder or softer upon opening and closing colt smoke unitDetermined it’s not coming from colt smoke unit but instead the “jet stream maestro” (with mic and phones plug)(pictures attached) Tightened cable on jet stream maestro and buzzing has stopped completely
MSA-DFES | WA5377671 | 2 | MALCO FLOORING PTY LTD | walkway - carpet tiles are lifting | Flooring | Carpet | 110 | Fail | Fail | 0 | 0 | 0.5 | 2022-04-20 08:26 | 2022-04-26 17:00 | 2022-04-29 08:00 | 2022-04-26 17:00 | 2022-04-29 08:30 |  |  | Report Walkway carpet tiles are liftingAction Restuck carpet tiles to walkway
MSA-DFES | WA5384850 | 3 | AWB Co. | Downpipe damaged outside station officers office | Roofing | Guttering | 127.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-28 16:46 | 2022-05-05 17:00 | 2022-05-05 09:30 | 2022-05-05 17:00 | 2022-05-05 10:00 |  |  | Attended, blocked downpipe, unblocked and flushed pipe. Job complete
MSA-DTWD | WA5393179 | 2 | PEEL LOCK SERVICES PTY LTD | Manual pin code lock on door not working | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.5 | 2022-05-03 15:43 | 2022-05-06 17:00 | 2022-05-05 08:45 | 2022-05-06 17:00 | 2022-05-05 09:15 |  |  | Repairs to door
MSA-DTAG | WA5399215 | 3 | Midolo Building Services | L4 Room/Office Male public bathroom on Hay St side, loose door latch | Building | Doors | 74.92 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-09 18:47 | 2022-05-16 17:00 | 2022-05-12 09:30 | 2022-05-16 17:00 | 2022-05-12 10:00 |  |  | REPAIRS MADE TO RESECURE DOOR LATCH
MSA-DTWD | WA5400644 | 2 | Critical Fire Protection & Training | ground replace discharged fire extinguishers and broken signage | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 47.07 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-10 09:02 | 2022-05-13 17:00 | 2022-05-13 15:30 | 2022-05-13 17:00 | 2022-05-13 16:00 |  |  | On arrival - technician spoke with Tracy (building management) and could not ascertain where the extinguisher/signage was required -Pressure Gauge on extinguisher not indicating discharged and no signs of brackets or signage for extinguisher-Advised by client to leave extinguisher as is, and client will follow up on any further required worksTime on site: .5hrsArrived: 15:30Depart: 16:00
MSA-DTWD | WA5417051 | 1 | AWB Co. | E200 Exposed wires on Lathe 6 ( Hazard ) | Electrical | General Electrical | 122.21 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-13 10:06 | 2022-05-16 17:00 | 2022-05-13 12:30 | 2022-05-16 17:00 | 2022-05-13 13:00 |  |  | Attended site signed in jsa completed. got keys from guard. located lathe with cables exposed. Found gland to be loose from pedestrians most likely. Tightened up and good now.*** job completed ***
MSA-DFES | WA5437316 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Power outage - running on generator at the moment | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-16 07:17 | 2022-05-16 17:00 | 2022-05-16 08:00 | 2022-05-16 17:00 | 2022-05-16 08:30 |  |  | Power had been restored to site
MSA-DFES | WA5460006 | 3 | Securex Security Systems & Services | Sim Centre - Ground Level - Tecom/Titan Monitored Alarm - Siren Monitor Fail | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-18 10:31 | 2022-05-25 17:00 | 2022-05-25 13:15 | 2022-05-25 17:00 | 2022-05-25 13:45 |  |  | 25/05/2022, 1315-1345Tested siren is working ok.No faults showing on system.
MSA-DFES | WA5460225 | 1 | Critical Fire Protection & Training | Fire Panel - disabled zone is being recorded - cant reset | Fire Protection Services | Fire Protection - Monitor System | 99.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-18 12:03 | 2022-05-19 17:00 | 2022-05-19 08:00 | 2022-05-19 17:00 | 2022-05-19 08:30 |  |  | De-isolated existing isolate on zone 6 of sub panel. Sub panel returned to all systems normal. Main panel has zones isolated (1-2-14) for current carpet/ re-flooring work being done Time of arrival: 8:00amTime of Departure: 8:30am
MSA-DTAG | WA5470469 | 2 | Midolo Building Services | Level 14 - Anteroom 14.6 - Missing roof tile | Roofing | Tiled Roofing | 85 | Fail | Fail | 0 | 0 | 0.5 | 2022-05-23 10:23 | 2022-05-26 17:00 | 2022-05-27 08:45 | 2022-05-26 17:00 | 2022-05-27 09:15 |  |  | TILE HAS BEEN REPLACED
MSA-DTWD | WA5476115 | 2 | AWB Co. | roof leak | Roofing | Metal Roofing | 127.5 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-25 11:01 | 2022-05-30 17:00 | 2022-05-26 14:00 | 2022-05-30 17:00 | 2022-05-26 14:30 |  |  | attended site advised of works to be completed - BRAF required
MSA-DTAG | WA5477398 | 1 | AAA Ability Locksmiths | Courtroom 2 entry door is slamming loudly - see more information | Security | Locksmith | 180 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-25 13:17 | 2022-05-26 17:00 | 2022-05-26 07:15 | 2022-05-26 17:00 | 2022-05-26 07:45 |  | WACCES | Attend site, door closer failed- requires parts.
MSA-DFES | WA5477602 | 3 | Australian HVAC Services Pty. Ltd. | Station Kitchen - GRD Floor - Station Dining Room - air conditioner fan is making a grating noise | Air Conditioning | Room Air Conditioners | 109.12 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-25 15:16 | 2022-06-01 17:00 | 2022-05-27 08:00 | 2022-06-01 17:00 | 2022-05-27 08:30 |  |  | Paul Veurink (27/05/2022) - Work NoteStarted on site. Signed in. Spoke with staff. Went to kitchen/living room AC. Turned on. Unit running quiet. Tested all Louvres. All good.Spoke with staff. The only service call they out in for this AC was 26/04. Which I had previously attended for and had repaired already. Staff checked they're list. No other service call for that AC.Spoke with the office. Let them know.Packed up and left site
MSA-DTAG | WA5477634 | 3 | Midolo Building Services | 2A - Ceiling in main office - Water patch near light fittings | Building | General Building | 45 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-25 16:00 | 2022-06-01 17:00 | 2022-05-30 08:45 | 2022-06-01 17:00 | 2022-05-30 09:15 |  |  | inspect ceiling only - plumbers issue
MSA-DTWD | WA5478023 | 2 | GRAFFITI FORCE PTY LTD | Automotive Center - Rear entrance door - Graffiti to be removed | Cleaning | Graffiti | 134.76 | Fail | Fail | 0 | 0 | 0.5 | 2022-05-26 07:57 | 2022-05-30 17:00 | 2022-06-01 11:00 | 2022-05-30 17:00 | 2022-06-01 11:30 |  |  | REMOVAL OF GRAFFITI FROM REAR ENTRANCE WINDOW
MSA-DTAG | WA5478647 | 3 | Total Security Systems Pty Ltd | Mimic panel LED stuck in ON state even after alarm is cleared (possible warranty) | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0.5 | 2022-05-26 12:45 | 2022-06-02 17:00 | 2022-05-30 08:00 | 2022-06-02 17:00 | 2022-05-30 08:30 |  |  | warranty jobfaulty cabling found behind duress, repaired and all working.
MSA-DTAG | WA5481098 | 1 | Sapio Pty Ltd | Ground Floor - Registry - Staff Back door wont unlock with swipe cards | Security | Access Control | 145 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-30 10:51 | 2022-05-31 17:00 | 2022-05-30 14:00 | 2022-05-31 17:00 | 2022-05-30 14:30 |  |  | found solenoid not releasing, removed fixed internal solenoid and secured lock in place. tested and confirmed full operation
MSA-DFES | WA5481972 | 2 | Protek 24/7 Building & Maintenance | Hanger - Main Building Hallway - broken self-closer on door | Building | Doors | 97.75 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-31 08:15 | 2022-06-03 17:00 | 2022-05-31 13:15 | 2022-06-03 17:00 | 2022-05-31 13:45 |  |  | repair self-closer on door , main building hallway
MSA-DTWD | WA5486486 | 2 | LIGHTHOUSE LOCKSMITHS | B-Block - East main door - the push button lock is faulty | Security | Locksmith | 80 | Pass | Pass | -1 | -1 | 0.5 | 2022-06-01 08:58 | 2022-06-07 17:00 | 2022-06-01 11:20 | 2022-06-07 17:00 | 2022-06-01 11:50 |  |  | change code to b block digital lock
MSA-DFES | WA5491425 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | SIMCEN Bunker - Underground - Meeting room outside COMCEN - Emergency light wont turn off | Electrical | Emergency & Exit Lighting | 110.98 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-03 16:16 | 2022-06-09 17:00 | 2022-06-09 12:30 | 2022-06-09 17:00 | 2022-06-09 13:00 |  |  | Arrived on site at 12:30. Was shown comcen bunker by security and unable to locate emergency light going off, checked all em fittings for charging lights top and bottom of bunker. Left site at 13:00
MSA-DFES | WA5495820 | 3 | AWB Co. | Level 1 - External roof line by engine room doors - Trims on fasica hanging down - See notes below | Roofing | Metal Roofing | 127.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-08 16:30 | 2022-06-15 17:00 | 2022-06-13 08:00 | 2022-06-15 17:00 | 2022-06-13 08:30 |  |  | BRAF declined - close costs to date
MSA-DCA | WA5511971 | 1 | Dormakaba Australia Pty Ltd | Level 1 - HLT dock – cable gate - Cable gate pin snapped - See notes | Building | Steel Fencing & Gates | 220 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 11:41 | 2022-06-14 17:00 | 2022-06-13 14:00 | 2022-06-14 17:00 | 2022-06-13 14:30 |  |  | Cable gate had been driven through by a truck breaking the bolt that holds the cable to the retracting mechanism, replaced nut and bolt to rectify issue. Tested and working.
MSA-DTWD | WA5513735 | 3 | AWB Co. | R013 - 2 x lights out in lunch area | Electrical | General Electrical | 487.3 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-14 12:48 | 2022-06-21 17:00 | 2022-06-20 11:45 | 2022-06-21 17:00 | 2022-06-20 12:15 |  | WACCES | Attended site and signed in. Completed JSA. re located faulty lights. Installed new globes. Working as intended, took pic, completed paperwork. Signed out,Job complete
MSA-DTAG | WA5522352 | 1 | Sapio Pty Ltd | Ground Floor - Registry - Back staff door - not unlocking with swipe card | Security | Access Control | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-15 14:42 | 2022-06-16 17:00 | 2022-06-16 09:30 | 2022-06-16 17:00 | 2022-06-16 10:00 |  |  | Found door operational at time of attending. Aware of issue reported and suggest replacing strike lockover to mortice lock.
MSA-DTWD | WA5534580 | 2 | Dormakaba Australia Pty Ltd | B/Block - west side - auto door glass panel - has slip down from the frame leaving a 10cm gap | Building | Automatic Doors | 180 | Pass | Pass | -1 | -1 | 0.5 | 2022-06-16 12:02 | 2022-06-21 17:00 | 2022-06-17 08:00 | 2022-06-21 17:00 | 2022-06-17 08:30 |  |  | Attended site and found that glass had moved down in frame leaving a gap at the top, see attached photo. Have informed facilities that this will need to be rectified by a glazier as We do not deal with the glass component of the door.
MSA-DTAG | WA5534599 | 1 | AWB Co. | Registry Manager Office - Flickering light | Electrical | General Electrical | 95.48 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-16 12:15 | 2022-06-17 17:00 | 2022-06-16 15:30 | 2022-06-17 17:00 | 2022-06-16 16:00 |  |  | Attended site and signed in. Completed JSA. Located manager office and found faulty light. Supply and replace lamp to fittings and tested all okay. Signed out. Job complete
MSA-DTAG | WA5563061 | 1 | AWB Co. | Ground - Courtroom 3 - network connection down, no power to rack - see notes below | Electrical | General Electrical | 91.58 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-20 11:39 | 2022-06-21 17:00 | 2022-06-20 15:30 | 2022-06-21 17:00 | 2022-06-20 16:00 |  |  | Job fixed by others. Job complete
MSA-DTWD | WA5567111 | 2 | Protek 24/7 Building & Maintenance | Ground Floor - Babys Bathroom - Door gets caught/jammed on the door frame | Building | Doors | 119.5 | Fail | Fail | 0 | 0 | 0.5 | 2022-06-23 14:57 | 2022-06-28 17:00 | 2022-06-29 12:30 | 2022-06-28 17:00 | 2022-06-29 13:00 |  |  | Repair Baby Bathroom Doors which were getting caught on the door frame
MSA-DCA | WA5567169 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Basement Level - Communications 01 (Server Room) - see details below | Equipment | Electrical Equipment | 110.975 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-23 15:58 | 2022-06-24 17:00 | 2022-06-24 15:30 | 2022-06-24 17:00 | 2022-06-24 16:00 |  |  | complete
MSA-DCA | WA5567452 | 0 | Wilson Security | RETROSPECTIVE WORK ORDER - E Block - EXTERNAL CHECK | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0.5 | 2022-06-19 13:45 | 2022-06-19 15:45 | 2022-06-19 14:00 | 2022-06-19 17:45 | 2022-06-19 14:30 | 1 |  | Completed
MSA-DCA | WA5568203 | 0 | Critical Fire Protection & Training | Fire alarm is going off - reset fire panel and detector needs to be replaced | Fire Protection Services | Smoke and Heat Detection | 219.66 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-25 12:19 | 2022-06-25 14:19 | 2022-06-25 14:00 | 2022-06-25 16:19 | 2022-06-25 14:30 |  |  | Start time: 2pmFinish time: 2:30pmInvestigated false alarm activation to zone 5 plant room/air handling room smoke detector. False activation likely caused due to excess dust in environment directly adjacent to detector. Replaced current smoke detector with thermal to eliminate false activations through dust ingress. Critical fire office to apply and confirm replacement of smoke to thermal detection suits environment and complies with AS/NZS standards and DFES monitoring requirements. Fire panel returned to normal operation with no faults, isolates or alarms present.
MSA-DTAG | WA5570789 | 1 | AAA Ability Locksmiths | Family Violence Lock - Issues with the lock, and the key not opening or locking the door | Security | Locksmith | 210 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-28 14:54 | 2022-06-29 17:00 | 2022-06-29 15:30 | 2022-06-29 17:00 | 2022-06-29 16:00 |  |  | Attend site, service and lubricate main door, adjust striker plate and loctite all fasteners.
MSA-DTWD | WA5571195 | 2 | AWB Co. | Faulty External Lights - See notes | Electrical | Lighting, External | 98.545 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-29 09:39 | 2022-07-04 17:00 | 2022-07-01 14:00 | 2022-07-04 17:00 | 2022-07-01 14:30 |  |  | Attended site and signed in. Completed JSA. Located all external lights and found to be older style flood lights. None of them work and can not see if they have power need ewp. Signed out. Job not complete. Submit brafBoom ewp to access 6 to 8mPick up either 250 or 400w lamps and ignitors.Replace the lamps if the fittings arnt corroded and seized.1 day labour 2 peopleIf fittings aren’t repairable we are not to replace them. The landlord has to repair them. Won’t know till we get up there.**BRAF SUBMITTED AND DECLINED NO FURTHER WORKS**
MSA-DFES | WA5571257 | 2 | Water2water Pty Ltd | Kitchen - Zip tap has a chemical taste | Plumbing & Drainage | Water | 126.89 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-29 10:17 | 2022-07-04 17:00 | 2022-07-04 09:50 | 2022-07-04 17:00 | 2022-07-04 10:20 |  |  | CHECKED OVER SYSTEM, NO FAULTS - SEEMS TO BE WORKING OKAY?
MSA-DCA | WA5572244 | 3 | Protek 24/7 Building & Maintenance | Ground Level - Loading Bay - Door has a fault - See notes below | Building | Doors | 103.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-29 15:01 | 2022-07-06 17:00 | 2022-07-05 11:00 | 2022-07-06 17:00 | 2022-07-05 11:30 |  |  | Replace missing rivets
MSA-DTWD | WA5583009 | 3 | AHS Services WA Pty Ltd (Anchor) | Toilet A110C - Female toilet floor drain blocked | Plumbing & Drainage | Drainage | 90.095 | Fail | Fail | 1 | 1 | 0.5 | 2022-07-04 09:44 | 2022-07-11 17:00 | 2022-07-18 08:00 | 2022-07-11 17:00 | 2022-07-18 08:30 |  |  | Cleared blocked floor waste drain
MSA-DCA | WA5583157 | 3 | Techworks Electrical | Level 1 - Courtyard - 4 strings of lights in courtyard not working | Electrical | Lighting, External | 135.15 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-04 10:43 | 2022-07-11 17:00 | 2022-07-04 14:00 | 2022-07-11 17:00 | 2022-07-04 14:30 |  |  | Found lights plug into gpos and when all gpos turned on all lights work. Ken was with us.
MSA-DTWD | WA5588084 | 2 | Protek 24/7 Building & Maintenance | Ground - E Block - Damaged brick wall, may need to be removed and re-laid | Building | External Walls | 122.38 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-07 13:01 | 2022-07-12 17:00 | 2022-07-08 13:15 | 2022-07-12 17:00 | 2022-07-08 13:45 |  | WACCES | BRAF Declined
MSA-DFES | WA5588400 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Numerous electrical items that have not been electrically tested and tagged. | Electrical | General Electrical | 80.97 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-07 15:52 | 2022-07-14 17:00 | 2022-07-12 07:15 | 2022-07-14 17:00 | 2022-07-12 07:45 |  |  | Arrived onsite at 7:15 to investigate various items needed to be tagged. Found entire station needs to be tested and tagged and will need to be done through normal testing and tagging process. Job doesn’t come under a breakdown and nothing is actually faulty. Will contact necessary people of interest to conduct testing and tagging for station but will need to come under standard process for testing. Continued onsite at 7:45
MSA-DFES | WA5596706 | 2 | AWB Co. | Ground Floor - Firefighters ensuite -Water coming in through light fitting in ensuite when it rains. | Roofing | Metal Roofing | 88.77 | Fail | Fail | 0 | 0 | 0.5 | 2022-07-11 09:57 | 2022-07-14 17:00 | 2022-07-15 12:30 | 2022-07-14 17:00 | 2022-07-15 13:00 |  |  | Works relate to another job that is active.will close jobClose job outDuplicate to: WA5416748Which works completed onBoth show on ProMAP as "Roof Fixtures"
MSA-DCA | WA5613697 | 1 | Critical Fire Protection & Training | Level 5 - Plant Room - investigate relocating sensor from AHU 2 to a less dust prone location | Fire Protection Services | Smoke and Heat Detection | 132.255 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-14 15:28 | 2022-07-15 17:00 | 2022-07-14 15:30 | 2022-07-15 17:00 | 2022-07-14 16:00 |  |  | Start time: 2:20pmFinish time: 3:05pmAttended site as a call-out. Loop 4 sensor 40 Zone 52 A/C 2 duct probe supply air in isolated alarm condition on arrival. Investigated duct probe and found same probe duct that had previously caused alarm 06/22 had activated again after replacement on 14/7/22 at 12:33pm. This device has been left in a isolated/reset normal condition until further action can be taken.
MSA-DCA | WA5661101 | 3 | Critical Fire Protection & Training | Fire Service Padlock needs replacing on roller door on pumphouse. | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 27.01 | Fail | Fail | 1 | 1 | 0.5 | 2022-07-19 15:56 | 2022-07-26 17:00 | 2022-08-05 08:00 | 2022-07-26 17:00 | 2022-08-05 08:30 |  | WACCES | New 003 lock requested to be install now the replacement roller door is on.
MSA-DTWD | WA5674847 | 2 | Protek 24/7 Building & Maintenance | Fault description Unsteady brick wall just outside FG37 needs to be removed. | Building | External Walls | 87.43 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-21 14:42 | 2022-07-26 17:00 | 2022-07-25 11:45 | 2022-07-26 17:00 | 2022-07-25 12:15 |  |  | BRAF Declined
MSA-DTWD | WA5677086 | 3 | Securex Security Systems & Services | Level 2 - Guest Services - fix and attach the security alarm switch underneath desk | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-25 12:29 | 2022-08-01 17:00 | 2022-07-29 08:00 | 2022-08-01 17:00 | 2022-07-29 08:30 |  |  | 29/07/2022, 800-830Refitted duress button to desk
MSA-DFES | WA5677417 | 1 | Go Doors | reception - door between the Reception and the workshop had a large delay and dose not close- notes | Building | Automatic Doors | 310 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-25 14:24 | 2022-07-26 17:00 | 2022-07-25 14:45 | 2022-07-26 17:00 | 2022-07-25 15:15 |  |  | Completed
MSA-DTWD | WA5687884 | 3 | Securex Security Systems & Services | Guest Services-Duress switch position 8 has come loose & needs to be moved slightly and resecured | Security | Security Management System | 160 | Pass | Pass | -1 | -1 | 0.5 | 2022-08-02 07:59 | 2022-08-08 17:00 | 2022-08-04 14:45 | 2022-08-08 17:00 | 2022-08-04 15:15 |  |  | 04/08/2022, 245-315Refitted duress button to desk
MSA-DFES | WA5699570 | 1 | Critical Fire Protection & Training | Fire Alarm Panel - has no power being supplied to it after the station lost power | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-10 10:30 | 2022-08-11 17:00 | 2022-08-10 14:20 | 2022-08-11 17:00 | 2022-08-10 14:50 |  |  | Attended site as a call-out to investigate fault to fire panel. On arrival found fire panel not operational with total blackout. The extended power outage has caused batteries to die and create total power down to fire panel. After conducting hard reset with batteries disconnected and panel mains switch turned off. Reset by turning fire panel main switch back on and reconnecting batteries after boot up process complete.All systems returned to normal operation with no faults alarms or isolates left on panel and remained on site to confirm code red wait for master no longer present and Monitoring is returned to normal operation. No further action required.
MSA-DTWD | WA5727733 | 1 | Securex Security Systems & Services | Electric gate does not operate - see notes | Electrical | General Electrical | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-15 11:44 | 2022-08-16 17:00 | 2022-08-15 15:30 | 2022-08-16 17:00 | 2022-08-15 16:00 |  |  | 15/08/2022, 1530-1600Gate motor may have blown.No response when release button pressed.Removed motor from gate to allow entry/exit until problem fixed.
MSA-DFES | WA5728126 | 3 | Securex Security Systems & Services | Reception - Exit Button has broken | Security | Access Control | 179.89 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-15 14:35 | 2022-08-22 17:00 | 2022-08-22 12:50 | 2022-08-22 17:00 | 2022-08-22 13:20 |  |  | 22/08/2022, 1250-1320Replaced broken Push to Exit button at admin. Tested OK.
MSA-DCA | WA5761492 | 2 | Earth & Water Pty Ltd | small garden bed-Broken retic in small garden bed by left hand side of AGWA rooftop bar lift. | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.5 | 2022-08-18 09:41 | 2022-08-23 17:00 | 2022-08-23 10:15 | 2022-08-23 17:00 | 2022-08-23 10:45 |  |  | Dig out valve box and undo system and replace broken fittings and fit flush valves and test as OK
MSA-DTAG | WA5763651 | 3 | Go Doors | Door 3 Magistrates Airlock and Door into custody interview rooms not working (could be a sensor issu | Building | Automatic Doors | 230 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-18 14:03 | 2022-08-25 17:00 | 2022-08-25 08:00 | 2022-08-25 17:00 | 2022-08-25 08:30 |  |  | Completed
MSA-DTAG | WA5790456 | 2 | OCS SERVICES PTY LTD | Level 3 - Judicial Support Office - Please see notes below | Cleaning | Cleaning |  | Pass | Fail | 0 | 0 | 0.5 | 2022-08-22 10:27 | 2022-08-25 17:00 | 2022-08-25 17:00 | 2022-08-25 17:00 | 2022-08-25 17:30 |  |  | Completed
MSA-DTAG | WA5793665 | 0 | Sapio Pty Ltd | Lift C – Judges lift All levels - Touch panels on lift not working - See notes below | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-24 09:15 | 2022-08-24 11:15 | 2022-08-24 09:30 | 2022-08-24 13:15 | 2022-08-24 10:00 |  |  | C lift call panels from 6 to 11 are not respondingLift people to fix not security
MSA-DTAG | WA5800443 | 3 | Midolo Building Services | Level 4 male disabled toilet - Soap dispenser fixings in disabled toilet are loose | Building | Internal Walls | 81.31 | Pass | Pass | -1 | -1 | 0.5 | 2022-08-31 10:01 | 2022-09-07 17:00 | 2022-09-02 09:30 | 2022-09-07 17:00 | 2022-09-02 10:00 |  |  | soap dispenser re secured
MSA-DTWD | WA5829346 | 0 | ADVANCED LOCK & KEY | The door is jammed - Lock has dropped inside door - Room is inaccessible | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-02 12:30 | 2022-09-02 14:30 | 2022-09-02 13:40 | 2022-09-02 16:30 | 2022-09-02 14:10 |  |  | removed debri from cylinder
MSA-DTWD | WA5836174 | 3 | Securex Security Systems & Services | DGP - 14 - Data Gathering Panel - battery Failed - L2 | Security | Security Management System | 210 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-07 10:31 | 2022-09-14 17:00 | 2022-09-07 14:00 | 2022-09-14 17:00 | 2022-09-07 14:30 |  |  | 07/09/2022, 1400-1430Replaced dgp 14 battery
MSA-DFES | WA5837770 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilet - Sink tap is leaking | Plumbing & Drainage | Water | 110.845 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-08 08:52 | 2022-09-15 17:00 | 2022-09-13 10:15 | 2022-09-15 17:00 | 2022-09-13 10:45 |  |  | I was unable to find leaking tap as I could not locate a male toilets in the volunteers building as reported and there was no leaking taps in the fire station
MSA-DTAG | WA5838340 | 3 | Midolo Building Services | Level 2 - Exec. Mgr’s office - Faulty Door handle - loose | Building | Doors | 48.42 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-08 12:31 | 2022-09-15 17:00 | 2022-09-09 08:00 | 2022-09-15 17:00 | 2022-09-09 08:30 |  |  | LOOSE SCREWS ON DOOR HANDLE TIGHTENED
MSA-DTWD | WA5853581 | 3 | PEEL LOCK SERVICES PTY LTD | Faulty lock plus require 3 addition keys for CL ST – Yellow/Grey | Security | Locksmith |  | Pass | Pass | -1 | -1 | 0.5 | 2022-09-12 09:40 | 2022-09-19 17:00 | 2022-09-13 11:00 | 2022-09-19 17:00 | 2022-09-13 11:30 |  |  | Keys cut
MSA-DFES | WA5853677 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Electrical fault light in duty room is lit – see notes | Electrical | General Electrical | 91.95 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-12 10:08 | 2022-09-19 17:00 | 2022-09-15 14:00 | 2022-09-19 17:00 | 2022-09-15 14:30 |  |  | Continued on site at 14:00 to investigate fault light on ehxaust fan, found that no power has tripped and fan running. Fault lights showing monitored mechanical system fault. Checked exhaust fan in laundry running as normal. Informed staff to contact mechanical services to investigate further. Continued on site at 14:30
MSA-DTAG | WA5861805 | 3 | Midolo Building Services | Prison review board side - leakage through one of windows - see notes below | Building | Windows | 48.42 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-13 11:29 | 2022-09-20 17:00 | 2022-09-15 11:00 | 2022-09-20 17:00 | 2022-09-15 11:30 |  |  | inspect only - no leak evident
MSA-DCA | WA5887740 | 2 | Techworks Plumbing | Faulty Zip tap - Jubilee kitchen | Plumbing & Drainage | Water | 230.86 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-16 09:39 | 2022-09-21 17:00 | 2022-09-19 07:15 | 2022-09-21 17:00 | 2022-09-19 07:45 |  |  | Checked for a faulty zip on arrival it was working as normal.
MSA-DCA | WA5888223 | 1 | Techworks Plumbing | Hackett hall ground male toilet - flush plate is broken and missing | Plumbing & Drainage | Toilets/Cisterns | 239.02 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-16 14:17 | 2022-09-19 17:00 | 2022-09-17 14:00 | 2022-09-19 17:00 | 2022-09-17 14:30 |  |  | Replaced Broken flush place
MSA-DCA | WA5993162 | 1 | Protek 24/7 Building & Maintenance | RETROSPECTIVE WO - Ground Floor - Discovery Lounge Male Toilet - HAND DYER -SEE NOTES | Building | Internal Walls | 83.26 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-04 09:40 | 2022-10-05 17:00 | 2022-10-04 11:00 | 2022-10-05 17:00 | 2022-10-04 11:30 | 1 |  | Unable to complete requires electrician
MSA-DTAG | WA5994217 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Sheriff’s Office - Toilet in gents dripping | Plumbing & Drainage | Toilets/Cisterns | 93.915 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-05 13:48 | 2022-10-10 17:00 | 2022-10-07 12:30 | 2022-10-10 17:00 | 2022-10-07 13:00 |  |  | No issue found.
MSA-DTWD | WA5995145 | 3 | Critical Fire Protection & Training | Fire Panel - Fire Panel in Alarm, Alarms now muted | Fire Protection Services | Fire Protection - Monitor System | 50.65 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-06 10:49 | 2022-10-13 17:00 | 2022-10-10 11:00 | 2022-10-13 17:00 | 2022-10-10 11:30 |  |  | Attended site to investigate abnormal condition of fire panel. On arrival found fire panel operating all systems normal however 1x intermittent EWIS fault latched and indicated as had occurred from zone 3 upper ground. After resetting and monitoring EWIS panel for 10 minutes found fault condition no longer present as did not re-occur on EWIS. To identify and rectify fault EWIS fault condition needs to be in fault constantly to begin investigations. No further action required at this time.
MSA-DTWD | WA6000949 | 2 | Securex Security Systems & Services | Ground Floor - Store Room - Faulty “Store room door” PIR - multiple false activations recorded | Security | Access Control | 160 | Fail | Fail | 1 | 1 | 0.5 | 2022-10-10 11:25 | 2022-10-13 17:00 | 2022-10-17 09:30 | 2022-10-13 17:00 | 2022-10-17 10:00 |  |  | 17/10/2022, 930-1000Edsec have no records of zone false alarming, assume it is zone 8. Checked device no fault found adjusted sensitivity.
MSA-DTAG | WA6007639 | 3 | Midolo Building Services | Ground - Judges chamber - Door stop broken | Building | Doors | 78.73 | Pass | Pass | -1 | -1 | 0.5 | 2022-10-11 09:25 | 2022-10-18 17:00 | 2022-10-11 13:15 | 2022-10-18 17:00 | 2022-10-11 13:45 |  |  | New door stop installed
MSA-DFES | WA6112928 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Room 16 - Toilet bowl cracked | Plumbing & Drainage | Toilets/Cisterns | 991.8675 | Pass | Pass | -1 | -1 | 0.5 | 2022-10-24 08:02 | 2022-10-31 17:00 | 2022-10-27 11:00 | 2022-10-31 17:00 | 2022-10-27 11:30 |  |  | Called before we left the last job, to let someone know we are on our way, they said that's fine. Upon arrival nobody was here.
MSA-DFES | WA6113874 | 3 | Protek 24/7 Building & Maintenance | Ground floor Cleaners cupboard broken broom holder | Carpentry | Timber (all types) | 188.3 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-24 16:18 | 2022-10-31 17:00 | 2022-10-28 09:30 | 2022-10-31 17:00 | 2022-10-28 10:00 |  | WACCES | Replaced with new broom holder
MSA-DTAG | WA6126453 | 1 | Midolo Building Services | Interview Rooms 1 & 4 Fault description Damage to walls (holes have been made)-see notes | Building | Internal Walls | 75.32 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-25 11:48 | 2022-10-26 17:00 | 2022-10-25 14:45 | 2022-10-26 17:00 | 2022-10-25 15:15 |  |  | inspect only - work to be completed on priority 0 work order # wa6126887
MSA-DTWD | WA6130687 | 1 | Complete Pest Management Services | Construction Office – does not have a room number-dead rodent-see notes | Pest Control | General Pest | 197.1 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-28 14:18 | 2022-10-31 17:00 | 2022-10-31 08:00 | 2022-10-31 17:00 | 2022-10-31 08:30 |  |  | Inspected the roof void as far as possible without gaining full body entry.Nothing visible and odour not strong enough to suggest a dead animal near to the access opening.Likely that a rodent has died in the office southern wall cavity.Placed 3 x deodoriser pots in the office to mask odour.
MSA-DCA | WA6132508 | 1 | Techworks Electrical | DB-GB/BK electrical riser-NE power 4 white and Kitchen 3 blue keep failing -see notes | Electrical | General Electrical | 135.15 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-31 14:36 | 2022-11-01 17:00 | 2022-11-01 12:30 | 2022-11-01 17:00 | 2022-11-01 13:00 |  |  | The dishwasher that is getting plugged into that circuit is the problem. Now the circuit itself.
MSA-DTWD | WA6157249 | 2 | Critical Fire Protection & Training | Continuous high pitched noise coming from ceiling mounted Fire Warning speaker - See notes | Fire Protection Services | Smoke and Heat Detection | 50.65 | Fail | Fail | 0 | 0 | 0.5 | 2022-11-09 14:17 | 2022-11-14 17:00 | 2022-11-15 13:15 | 2022-11-14 17:00 | 2022-11-15 13:45 |  | WACCES | Investigated the fault, the 2x speakers in A103 that were noted to be making a high pitched noise were not currently making any disruptive noises.
MSA-DCA | WA6178637 | 2 | Automatic Fire Protection (ARA) | Ground Floor - Male Toilet - Faulty smoke detector | Fire Protection Services | Smoke and Heat Detection | 320.78 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-14 12:38 | 2022-11-17 17:00 | 2022-11-15 10:15 | 2022-11-17 17:00 | 2022-11-15 10:45 |  |  | Replaced smoke detector zone 17 devices L6S48, L6S50 & L6S51 due to false alarms & high AV readings when a diagnostic test wasperformed.Checked new AV readings now OK.Left zone 17 isolated for maintenance to de-isolate once they have completed their works.
MSA-DTWD | WA6184496 | 2 | AWB Co. | A Block - Customer Service - Lights makes loud crackle noise - See notes below | Electrical | Lighting, Internal | 150.505 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-15 12:48 | 2022-11-18 17:00 | 2022-11-16 09:30 | 2022-11-18 17:00 | 2022-11-16 10:00 |  |  | Attended site signed in jsa completed. Found faulty burnt switch in panel. Replaced with new 20a mechTested operational.Job completed
MSA-DCA | WA6184673 | 1 | ADVANCED LOCK & KEY | Electrical Box by Pretzel & STC - Lock needs replacing - See Notes Below | Electrical | General Electrical | 210 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-15 14:29 | 2022-11-16 17:00 | 2022-11-16 11:00 | 2022-11-16 17:00 | 2022-11-16 11:30 |  |  | Attend site to cut 2x RBF keys by code to electrical box 2x RBF KEYS
MSA-DFES | WA6208318 | 2 | Go Doors | Automatic entrance gate to the station is extremely slow to open. | Building | Security Doors | 333.56 | Fail | Fail | 0 | 0 | 0.5 | 2022-11-17 16:50 | 2022-11-22 17:00 | 2022-11-25 15:30 | 2022-11-22 17:00 | 2022-11-25 16:00 |  |  | 25/11/2022 James GreenReprogrammed sliding gate to reduce creep distance.Controller had reverted back to default settings, if this keeps happening I would recommend replacing the motor.Antenna seems to have lost strength, still works ok but may also require replacing in future.
MSA-DFES | WA6249439 | 2 | Water2water Pty Ltd | Unit 21 -Under sink filtered water system not working. Water tastes foul request new filtration | Equipment | Catering Equipment | 126.89 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-21 11:57 | 2022-11-24 17:00 | 2022-11-22 12:50 | 2022-11-24 17:00 | 2022-11-22 13:20 |  |  | Flushed Tanks & Filter again, all okay on departure.
MSA-DFES | WA6249454 | 2 | Critical Fire Protection & Training | Fire pane in fault-Please attend Tuesday 22/11 | Fire Protection Services | Fire Protection - Monitor System | 50.65 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-21 12:08 | 2022-11-24 17:00 | 2022-11-22 15:30 | 2022-11-24 17:00 | 2022-11-22 16:00 |  |  | Start time: 3:30pmFinish time: 4pmAttended site to investigate fault to fire panel. On arrival found fault on fire panel indicating fault exists on external bell circuit. After investigating cable within fire panel found 1x loose connection on external bell output of fire panel brigade card. After re-terminating cable and conducting function test to external bell found all systems returned to normal. If fault re-occurs on the same output of the fire panel, further investigation will be required. All systems normal on departure including remaining fault free for 5 minutes after re-terminating cable, before departure from site.
MSA-DTAG | WA6253864 | 2 | Midolo Building Services | ground court 1-air lock door into court appears to have come off its hinge. Hard to open | Building | Doors | 48.42 | Fail | Fail | 1 | 1 | 0.5 | 2022-11-22 12:38 | 2022-11-25 17:00 | 2022-11-30 13:15 | 2022-11-25 17:00 | 2022-11-30 13:45 |  |  | Screws tightened
MSA-DFES | WA6292127 | 1 | Anvil Doors | Engine Room Door 4 - is faulty | Building | Automatic Doors | 602 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-29 08:11 | 2022-11-30 17:00 | 2022-11-29 17:00 | 2022-11-30 17:00 | 2022-11-29 17:30 |  |  | Recommend replacing PE Beams for a more sturdy option as the firemen play basketball and pickleball inside the engine bays and are constantly knocking the PE Beams around. Caught up with Peteron site and his recommendation was XP 30's PE beams
MSA-DFES | WA6360887 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Kitchen - Glass Kitchen cook top chipped & Broken - open glass and sharp edges | Building | General Building | 92.81 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-07 16:52 | 2022-12-08 17:00 | 2022-12-08 09:30 | 2022-12-08 17:00 | 2022-12-08 10:00 |  | WACCES | BRaf Declined Made good stove top with Duct tape
MSA-DTAG | WA6362363 | 1 | Midolo Building Services | Ground - Court 1 corridor to judicial side - Secure door is not automatically closing - See Notes | Building | Automatic Doors | 75.32 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-09 09:59 | 2022-12-12 17:00 | 2022-12-09 11:45 | 2022-12-12 17:00 | 2022-12-09 12:15 |  |  | inspect only. - Door/door closer seems to be in good working order
MSA-DTAG | WA6364774 | 1 | Sapio Pty Ltd | L4 patch room-not showing on monitor | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-12 14:48 | 2022-12-13 17:00 | 2022-12-13 11:00 | 2022-12-13 17:00 | 2022-12-13 11:30 |  |  | Reset camera and programmed streaming to Milestone
MSA-DTAG | WA6365714 | 1 | Schindler Lifts Australia | Ground-Lift 1 is showing “out of service” | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.5 | 2022-12-13 11:47 | 2022-12-14 17:00 | 2022-12-13 13:15 | 2022-12-14 17:00 | 2022-12-13 13:45 |  |  | to be closed out at $0 cost
MSA-DFES | WA6368181 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1- numerous lights out - see notes | Electrical | Lighting, Internal | 165.89 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-14 07:25 | 2022-12-16 17:00 | 2022-12-14 09:30 | 2022-12-16 17:00 | 2022-12-14 10:00 |  |  | Replaced faulty lights above bed heads and in the dry cleaning cupboard. Checked rest of the station for any lights not working. Everything was good
MSA-DFES | WA6376498 | 1 | Complete Pest Management Services | External - Near Close Line - Wasp nest | Pest Control | General Pest | 165.73 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-15 16:20 | 2022-12-16 17:00 | 2022-12-16 09:30 | 2022-12-16 17:00 | 2022-12-16 10:00 |  |  | Inspected next to clothes line for wasps nest found and treated and removed nest.
MSA-DTAG | WA6393031 | 0 | Sapio Pty Ltd | Control Room - Level 10 - monitors on the wall arent appearing | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-28 08:45 | 2022-12-28 10:45 | 2022-12-28 09:30 | 2022-12-28 12:45 | 2022-12-28 10:00 |  |  | Reconfigured Milestone to show SAT and DMJC views. All OK.
MSA-DTAG | WA6393867 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 14 - Toilets - Issues with toilet flushing | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Fail | Fail | 1 | 1 | 0.5 | 2022-12-29 11:09 | 2023-01-06 17:00 | 2023-01-11 09:30 | 2023-01-06 17:00 | 2023-01-11 10:00
MSA-DTWD | WA6400234 | 1 | Ballantyne Plumbing Gas & Electrical | Sewer alarm flashing - see note | Plumbing & Drainage | Sewer Drains & Septic Systems |  | Pass | Pass | 0 | 0 | 0.5 | 2023-01-03 10:38 | 2023-01-04 17:00 | 2023-01-04 07:15 | 2023-01-04 17:00 | 2023-01-04 07:45
MSA-DFES | WA6404803 | 3 | Water2water Pty Ltd | Bushfire risk management branch - Kitchen - Hot water tap not working | Plumbing & Drainage | Water | 126.89 | Pass | Pass | -1 | -1 | 0.5 | 2023-01-09 09:21 | 2023-01-16 17:00 | 2023-01-12 11:00 | 2023-01-16 17:00 | 2023-01-12 11:30
MSA-DTAG | WA6405070 | 0 | Sapio Pty Ltd | Level 10 - Security office - Cameras on wall need reconfiguring | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-09 11:16 | 2023-01-09 13:16 | 2023-01-09 12:30 | 2023-01-09 15:16 | 2023-01-09 13:00
MSA-DCA | WA6405501 | 2 | Techworks Plumbing | GEO Francis St - UAT Bathroom - Flush plate issues (see notes) | Plumbing & Drainage | Toilets/Cisterns | 303.51 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-09 14:40 | 2023-01-12 17:00 | 2023-01-11 11:00 | 2023-01-12 17:00 | 2023-01-11 11:30
MSA-MRWA | WA6408058 | 3 | AWB Co. | Ground - Rear kitchen -Failed light fitting, have changed tubes out | Electrical | Lighting, Internal | 128.76 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-10 14:12 | 2023-01-17 17:00 | 2023-01-16 14:00 | 2023-01-17 17:00 | 2023-01-16 14:30
MSA-DTWD | WA6415277 | 2 | AWB Co. | 2G1 staff room - Light unit on south side not working | Electrical | Lighting, Internal | 128.76 | Pass | Pass | -1 | -1 | 0.5 | 2023-01-11 15:01 | 2023-01-16 17:00 | 2023-01-12 14:00 | 2023-01-16 17:00 | 2023-01-12 14:30
MSA-MRWA | WA6509754 | 2 | Water2water Pty Ltd | Hot / Cold Billi Tap intermittently locking | Plumbing & Drainage | Water | 489.74 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-20 14:45 | 2023-01-25 17:00 | 2023-01-23 14:07 | 2023-01-25 17:00 | 2023-01-23 14:37
MSA-DFES | WA6509767 | 2 | Dom's Total Grounds Maintenance | Transportable toilets - Eastern end - Reception - Broken Retic (see notes) | Plumbing & Drainage | Water | 147 | Pass | Pass | -1 | -1 | 0.5 | 2023-01-20 15:02 | 2023-01-25 17:00 | 2023-01-21 08:00 | 2023-01-25 17:00 | 2023-01-21 08:30
MSA-DTAG | WA6516413 | 0 | AAA Ability Locksmiths | Underground carpark - pedestrian door - loose lock | Security | Locksmith | 199.08 | Fail | Pass | 0 | 0 | 0.5 | 2023-01-23 11:30 | 2023-01-23 13:30 | 2023-01-23 14:00 | 2023-01-23 15:30 | 2023-01-23 14:30
MSA-DFES | WA6517461 | 2 | Protek 24/7 Building & Maintenance | RETROSPECTIVE WORK ORDER - REF WA6516108 | Building | Doors | 122.4 | Pass | Pass | -1 | -1 | 0.5 | 2023-01-23 09:15 | 2023-01-27 17:00 | 2023-01-23 12:30 | 2023-01-27 17:00 | 2023-01-23 13:00 | 1
MSA-DTAG | WA6520200 | 3 | Sapio Pty Ltd | RETROSPECTIVE WORK ORDER-Power outage - DO NOT ATTEND-see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-25 07:00 | 2023-02-01 17:00 | 2023-01-31 15:30 | 2023-02-01 17:00 | 2023-01-31 16:00 | 1
MSA-DCA | WA6520476 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security Issue-DO NOT ATTEND-See notes | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.5 | 2023-01-18 14:45 | 2023-01-19 17:00 | 2023-01-18 15:30 | 2023-01-19 17:00 | 2023-01-18 16:00 | 1
MSA-DCA | WA6522729 | 3 | Techworks Plumbing | Ground floor- toilet behind info desk - broken hinges | Plumbing & Drainage | Toilets/Cisterns | 230.86 | Pass | Pass | -1 | -1 | 0.5 | 2023-01-31 09:50 | 2023-02-07 17:00 | 2023-02-01 14:00 | 2023-02-07 17:00 | 2023-02-01 14:30
MSA-DTWD | WA6523359 | 2 | Securex Security Systems & Services | Alarm sensor is faulty | Security | Security Management System | 267.85 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-31 15:05 | 2023-02-03 17:00 | 2023-02-01 14:45 | 2023-02-03 17:00 | 2023-02-01 15:15
MSA-DTWD | WA6526642 | 3 | Protek 24/7 Building & Maintenance | Small hole in Lino floor ( trip Hazard ) | Flooring | Vinyl | 963.25 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-01 09:26 | 2023-02-08 17:00 | 2023-02-02 11:00 | 2023-02-08 17:00 | 2023-02-02 11:30 |  | WACCES
MSA-DTWD | WA6537910 | 3 | ADVANCED LOCK & KEY | Tools stores 211 roller door-Unable to lock roller door due to broken key and no spares | Security | Locksmith | 190 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-07 12:54 | 2023-02-14 17:00 | 2023-02-09 10:35 | 2023-02-14 17:00 | 2023-02-09 11:05
MSA-DTWD | WA6538168 | 1 | COMMERCIAL PLUMBING AND GAS | Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 78.835 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-07 15:35 | 2023-02-08 17:00 | 2023-02-08 14:00 | 2023-02-08 17:00 | 2023-02-08 14:30
MSA-DTWD | WA6540429 | 3 | Protek 24/7 Building & Maintenance | Repair defective / worn carpet | Flooring | Carpet | 83.25 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-09 10:48 | 2023-02-16 17:00 | 2023-02-13 11:45 | 2023-02-16 17:00 | 2023-02-13 12:15
MSA-DTWD | WA6543859 | 2 | Water2water Pty Ltd | Zip tap not working- has no water | Plumbing & Drainage | Water | 126.89 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-10 08:56 | 2023-02-15 17:00 | 2023-02-10 14:00 | 2023-02-15 17:00 | 2023-02-10 14:30
MSA-DCA | WA6579132 | 2 | Techworks Electrical | Wardrobe - Extractor fan on window not functioning. | Electrical | General Electrical | 135.15 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-15 14:35 | 2023-02-20 17:00 | 2023-02-17 09:30 | 2023-02-20 17:00 | 2023-02-17 10:00
MSA-DFES | WA6586304 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Station Officers Dorm - Reading Light Broken (see notes) | Electrical | General Electrical | 139.43 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-16 15:40 | 2023-02-23 17:00 | 2023-02-20 11:45 | 2023-02-23 17:00 | 2023-02-20 12:15
MSA-DFES | WA6650847 | 3 | Dom's Total Grounds Maintenance | Lawn area – Western side – Mackie Street - repair a broken reticulation head. | Plumbing & Drainage | Water | 179 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-20 13:39 | 2023-02-27 17:00 | 2023-02-22 17:00 | 2023-02-27 17:00 | 2023-02-22 17:30
MSA-DTAG | WA6650914 | 1 | Sapio Pty Ltd | Registry security door still not locking on all occasions (see notes) | Security | Locksmith | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-20 14:31 | 2023-02-21 17:00 | 2023-02-21 09:30 | 2023-02-21 17:00 | 2023-02-21 10:00
MSA-DFES | WA6667834 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Metro Ops Executive Office - 4 x Flouro Lights not working | Electrical | Lighting, Internal | 119.425 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-21 15:21 | 2023-02-28 17:00 | 2023-02-22 14:00 | 2023-02-28 17:00 | 2023-02-22 14:30
MSA-DTWD | WA6669213 | 0 | Casa Security Pty Ltd | Alarm Panel beeping | Security | Security Management System | 180 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-22 15:32 | 2023-02-22 17:32 | 2023-02-22 16:15 | 2023-02-22 19:32 | 2023-02-22 16:45
MSA-DFES | WA6669245 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Room 21 - Male shower leaking | Plumbing & Drainage | Water | 114.92 | Fail | Fail | 0 | 0 | 0.5 | 2023-02-22 16:26 | 2023-02-27 17:00 | 2023-02-28 17:00 | 2023-02-27 17:00 | 2023-02-28 17:30
MSA-DFES | WA6674153 | 0 | Anvil Doors | Front door after locking is not secured- electronic door can be pushed and open. | Building | Doors | 716.75 | Fail | Pass | 0 | 0 | 0.5 | 2023-02-27 06:28 | 2023-02-27 08:28 | 2023-02-27 09:30 | 2023-02-27 10:28 | 2023-02-27 10:00
MSA-DTWD | WA6676066 | 3 | AWB Co. | Fluroescent lights not working out side room | Electrical | Lighting, Internal | 98.545 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-28 11:34 | 2023-03-08 17:00 | 2023-03-02 09:30 | 2023-03-08 17:00 | 2023-03-02 10:00
MSA-DCA | WA6690691 | 3 | SCAVENGER SUPPLIES PTY LTD | Old Gaol- Ground floor - CEO Admin Office - Smoke Detector has fallen off ceiling | Fire Protection Services | Smoke and Heat Detection | 50.65 | Pass | Pass | -1 | -1 | 0.5 | 2023-03-09 11:46 | 2023-03-16 17:00 | 2023-03-09 14:20 | 2023-03-16 17:00 | 2023-03-09 14:50
MSA-DFES | WA4985874 | 3 | Critical Fire Protection & Training | Yard - Ball vale on hydrant in yard needs to be rotated 90 degrees - see details below | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 94.14 | Pass | Pass | 0 | 0 | 0.5 | 2021-12-30 13:31 | 2022-01-07 17:00 | 2022-01-05 07:30 | 2022-01-07 17:00 | 2022-01-05 08:00 |  |  | Ball valve handle hitting lug collar of female BICAdjusted coupling to rectify issue
MSA-DTWD | WA4991122 | 2 | ACTION GLASS & ALUMINIUM | Main Glass door has dropped needs adjustment | Glazing | Door Glass | 87.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-04 15:27 | 2022-01-07 17:00 | 2022-01-05 13:30 | 2022-01-07 17:00 | 2022-01-05 14:00 |  |  | ATTENDED SITE AND ADJUSTED FLOOR PIVOT OF DOOR
MSA-MRWA | WA4991525 | 3 | SONTEC WA PTY LTD | Server Room - Replace two faulty air keys and program | Security | Keys & Access | 332.76 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-05 09:19 | 2022-01-12 17:00 | 2022-01-10 10:00 | 2022-01-12 17:00 | 2022-01-10 10:30 |  |  | 10/1/22 - Dylan ParslowSupplied and programmed 2 airkey remotes.
MSA-DTAG | WA4992352 | 2 | Midolo Building Services | Level 3 - Door to Kitchen at Admin - secure door is not auto closing after opening | Building | Doors | 117.52 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-06 10:41 | 2022-01-11 17:00 | 2022-01-10 09:15 | 2022-01-11 17:00 | 2022-01-10 09:45 |  |  | Adjusted door closer
MSA-DTWD | WA4992621 | 3 | AWB Co. | S block - room S216 - damaged Wifi units - detaching from ceilings | Building | Ceiling | 72.56 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-06 14:36 | 2022-01-13 17:00 | 2022-01-13 12:00 | 2022-01-13 17:00 | 2022-01-13 12:30 |  |  | Attended site and signed in. Completed jsa. Met with IT guy on site and located wifi units and discussed where he wanted them, and what one was allocated to eat port on roof. Secured brackets to roof and connected cable from wifi box to port on roof. Took after pictures. Completed paperwork. Signed out.Job completed
MSA-DFES | WA4992663 | 2 | Securex Security Systems & Services | Ground - Side gate - please see details below | Security | Keys & Access | 154.55 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-06 14:47 | 2022-01-11 17:00 | 2022-01-11 13:30 | 2022-01-11 17:00 | 2022-01-11 14:00 |  |  | Checked gate.Found technician from Go Doors came on the 10th to fix the gate but gate remains open.The gate is controlled by time relay in the motor housing.Gate programmed correctly but motor will not respond.Require technician from Go Doors to return to fix.
MSA-DFES | WA4993268 | 2 | Go Doors | 1st Floor - Bypass the door switch and connect to the button - Please see details below | Building | Doors | 716.25 | Fail | Fail | 1 | 1 | 0.5 | 2022-01-07 11:41 | 2022-01-12 17:00 | 2022-01-17 15:15 | 2022-01-12 17:00 | 2022-01-17 15:45 |  |  | completed works
MSA-DFES | WA4993513 | 1 | Critical Fire Protection & Training | Fire Alarm - unable to reset the alarm system | Fire Protection Services | Fire Protection - Monitor System | 125.52 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-07 16:51 | 2022-01-10 17:00 | 2022-01-07 18:00 | 2022-01-10 17:00 | 2022-01-07 18:30 |  |  | Callout to fault on fipfound 2x isolations on panelRemoved isolations, no sign of faultSystem normal on departure
MSA-DTWD | WA4994870 | 3 | ADVANCED LOCK & KEY | North Block - N427 - Key over-ride to digital lock will not release key | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-10 08:23 | 2022-01-17 17:00 | 2022-01-12 13:00 | 2022-01-17 17:00 | 2022-01-12 13:30 |  |  | Completed12/1/22Remounted key override cyl on 3572 dx530 lock as override plate screws had undone and the cam had fallen out of the spindle hub.
MSA-DFES | WA4995295 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Comcen - Men's toilet - light is faulty | Electrical | General Electrical | 110.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-10 11:40 | 2022-01-13 17:00 | 2022-01-12 14:15 | 2022-01-13 17:00 | 2022-01-12 14:45 |  |  | Continued on site at 1415 to investigate lights not working. Found faulty globes in comcen male toilet. Replaced globes, tested and all working ok. Continued on site at 1445
MSA-DTWD | WA5001272 | 2 | Falcetta Plumbing and Gas | Staff toilet - water leak | Plumbing & Drainage | Toilets/Cisterns | 41.86 | Fail | Fail | 1 | 1 | 0.5 | 2022-01-11 10:42 | 2022-01-14 17:00 | 2022-01-20 16:30 | 2022-01-14 17:00 | 2022-01-20 17:00 |  |  | inspected toilets ensured operation
MSA-DTAG | WA5001662 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Custody Cell 4 - spit on floor in copious amounts | Cleaning | Cleaning | 300 | Fail | Fail | 0 | 0 | 0.5 | 2022-01-11 14:21 | 2022-01-12 17:00 | 2022-01-12 18:00 | 2022-01-12 17:00 | 2022-01-12 18:30 |  |  | Job completed as per WO
MSA-DTAG | WA5001671 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Custody Cell 2 - spit on floor in copious amounts | Cleaning | Cleaning | 300 | Fail | Fail | 0 | 0 | 0.5 | 2022-01-11 14:35 | 2022-01-12 17:00 | 2022-01-12 17:30 | 2022-01-12 17:00 | 2022-01-12 18:00 |  |  | Job completed as per WO
MSA-DTAG | WA5009978 | 1 | Sapio Pty Ltd | Ground Floor - Staff Turnstile - not working/not accepting security cards | Security | Security Management System | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-12 08:48 | 2022-01-13 17:00 | 2022-01-12 10:30 | 2022-01-13 17:00 | 2022-01-12 11:00 |  |  | Work performed by Ken Moore (12/01/2022)Attended site. Reset staff turnstiles. Turned system off, powered back on, all OK.Job completed.
MSA-DTWD | WA5010172 | 3 | Securex Security Systems & Services | Possible alarm sensor fault continuous call out to security | Security | Monitoring | 277.27 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-12 10:55 | 2022-01-19 17:00 | 2022-01-12 11:30 | 2022-01-19 17:00 | 2022-01-12 12:00 |  |  | Replaced PIR (zone 39) in room AF30
MSA-DFES | WA5010289 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Field Analyst Lab - no power to the room | Electrical | General Electrical | 110.98 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-12 12:06 | 2022-01-13 17:00 | 2022-01-12 13:45 | 2022-01-13 17:00 | 2022-01-12 14:15 |  |  | Arrived on site at 1345. Went to field analysis lad and located effected lighting circuit with fan. Located tripped rcd in switchboard reset and tested curcit all okay. Next job on same site started at 14:15
MSA-DTWD | WA5010427 | 2 | SCAVENGER SUPPLIES PTY LTD | Ground - A Block - Fire panel - Fire panel reads: Fire panel fault sensor 1 Sultan Building C Block | Fire Protection Services | Fire Protection - Monitor System | 52.3 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-12 13:49 | 2022-01-17 17:00 | 2022-01-13 09:00 | 2022-01-17 17:00 | 2022-01-13 09:30 |  |  | COMPLETED 13/01/202213/01/2021START 9.00AM-9.30AM
MSA-DTWD | WA5017410 | 1 | Securex Security Systems & Services | B Block - Ground & 1st floor - see details below | Security | Monitoring | 154.55 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-13 13:54 | 2022-01-14 17:00 | 2022-01-14 10:00 | 2022-01-14 17:00 | 2022-01-14 10:30 |  |  | Smoke detectors are not on alarm system.Fire alarm technician already attended site prior to us coming.
MSA-DTWD | WA5017511 | 0 | Securex Security Systems & Services | Security panel has stopped working | Security | Access Control | 154.55 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-13 15:57 | 2022-01-13 17:57 | 2022-01-13 16:30 | 2022-01-13 19:57 | 2022-01-13 17:00 |  |  | GPO in Room S110 Facilities Office (where the security panel is) has no power.Used extension cord to restore power to expander.Require an electrician to fix GPO.
MSA-DTAG | WA5018087 | 1 | Sapio Pty Ltd | Level 19 - comms room - reader not working | Security | Access Control | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-14 08:41 | 2022-01-17 17:00 | 2022-01-14 14:30 | 2022-01-17 17:00 | 2022-01-14 15:00 |  |  | Work performed by Ken Moore (14/01/2022)Attended site. Reset Level 19 Patch Room Card Reader, tested, all OK.Job completed.
MSA-DCA | WA5018534 | 2 | Dormakaba Australia Pty Ltd | Breezeway - door not responding, see notes | Building | Automatic Doors | 70 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-14 12:35 | 2022-01-19 17:00 | 2022-01-14 13:30 | 2022-01-19 17:00 | 2022-01-14 14:00 |  |  | Inspected gate and found that the gate had failed from being badly corroded etc, please quote for 1x d5 motor and 2x remotes, site also need to clear all the soil to allow us acces around the gate motor.
MSA-DTWD | WA5052849 | 1 | Falcetta Plumbing and Gas | E Block - Ground - Canteen hot water system - Heater will not light | Plumbing & Drainage | Materials | 73.26 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-18 11:01 | 2022-01-19 17:00 | 2022-01-19 10:00 | 2022-01-19 17:00 | 2022-01-19 10:30 |  |  | purged and lit hot water unit
MSA-DTWD | WA5053246 | 3 | Falcetta Plumbing and Gas | Block 10 - First floor - Male toilets -R/H cistern on urinal not working | Plumbing & Drainage | Toilets/Cisterns | 83.26 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-18 14:29 | 2022-01-25 17:00 | 2022-01-25 15:00 | 2022-01-25 17:00 | 2022-01-25 15:30 |  |  | repaired invisi cistern
MSA-DTWD | WA5069185 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 122 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-19 16:28 | 2022-01-27 17:00 | 2022-01-27 11:15 | 2022-01-27 17:00 | 2022-01-27 11:45 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B02 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box located in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DTWD | WA5069188 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 125.66 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-19 16:31 | 2022-01-27 17:00 | 2022-01-27 12:15 | 2022-01-27 17:00 | 2022-01-27 12:45 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B10 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box located in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DTWD | WA5069189 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 119.66 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-19 16:32 | 2022-01-27 17:00 | 2022-01-27 12:45 | 2022-01-27 17:00 | 2022-01-27 13:15 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B40 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box lcated in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DFES | WA5085444 | 3 | ADVANCED LOCK & KEY | Administration building western exit door is not latching correctly when closing | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-21 07:55 | 2022-01-28 17:00 | 2022-01-27 10:20 | 2022-01-28 17:00 | 2022-01-27 10:50 |  |  | Adjust closer
MSA-DTWD | WA5086909 | 3 | Protek 24/7 Building & Maintenance | White board fallen off wall | Building | General Building | 119.5 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-21 15:56 | 2022-01-31 17:00 | 2022-01-25 15:00 | 2022-01-31 17:00 | 2022-01-25 15:30 |  |  | Work done by others
MSA-DTWD | WA5090077 | 1 | Precise Air Group | room V002, V003, staff room - bed smell admitting from vents or aircon *moldy noise | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-25 09:20 | 2022-01-27 17:00 | 2022-01-25 11:30 | 2022-01-27 17:00 | 2022-01-25 12:00 |  |  | Arrived on sites and signed in as necessary. Went to staffroom and investigated smell issue. Smell not present at time of service call. Smell potentially due to dried out drains over school holidays then condensation has rectified issue. Flushed drains anyway all OK.
MSA-DTWD | WA5090144 | 2 | AWB Co. | Level 1 - First Floor - 1F23 - Broken light switch | Electrical | Lighting, Internal | 91.58 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-25 09:56 | 2022-01-31 17:00 | 2022-01-31 10:00 | 2022-01-31 17:00 | 2022-01-31 10:30 |  |  | Attended site and signed in. Completed JSA. Located 1f23. Found light switch at main door to be pushed through plate. Removed panel and re fitted mech to switch plate. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5090249 | 2 | Sapio Pty Ltd | Detention Control Room - dvd player for the cells is not working | Security | CCTV Surveillance | 256.27 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-25 10:40 | 2022-01-31 17:00 | 2022-01-28 07:30 | 2022-01-31 17:00 | 2022-01-28 08:00 |  |  | Replaced DVD player
MSA-DTWD | WA5091669 | 3 | Falcetta Plumbing and Gas | Block 7 - Ground - Male toilets - Water splashing out of urinal | Plumbing & Drainage | Toilets/Cisterns | 73.26 | Pass | Pass | -1 | -1 | 0.5 | 2022-01-27 10:04 | 2022-02-03 17:00 | 2022-01-28 14:30 | 2022-02-03 17:00 | 2022-01-28 15:00 |  |  | repaired urinal sparge outlets
MSA-DFES | WA5092700 | 1 | Go Doors | Gate - code is not working for gate - has been kicked in | Building | Steel Fencing & Gates | 310 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-28 09:21 | 2022-01-31 17:00 | 2022-01-28 10:45 | 2022-01-31 17:00 | 2022-01-28 11:15 |  |  | Works completed.
MSA-DCA | WA5093314 | 0 | Critical Fire Protection & Training | Ground Floor - near stage door - fire panel - isolate zone 10 | Fire Protection Services | Fire Protection - Monitor System | 217.3 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-28 13:20 | 2022-01-28 15:20 | 2022-01-28 14:30 | 2022-01-28 17:20 | 2022-01-28 15:00 |  |  | Isolate zone 10 as requested by site.
MSA-DTWD | WA5094899 | 2 | Swan Pest Control | P Block - Ground - G01 - ants in the kitchen area | Pest Control | General Pest | 205 | Pass | Pass | 0 | 0 | 0.5 | 2022-01-31 15:14 | 2022-02-03 17:00 | 2022-02-01 13:20 | 2022-02-03 17:00 | 2022-02-01 13:50 |  |  | Gelled kitchen with advion ant gel and sprayed window sills with Fipronil @ .6%
MSA-DTWD | WA5100256 | 2 | LIGHTHOUSE LOCKSMITHS | F-SHED - external - external electrical node has a broken lock on door | Security | Locksmith | 80 | Pass | Pass | -1 | -1 | 0.5 | 2022-02-02 12:00 | 2022-02-07 17:00 | 2022-02-03 08:30 | 2022-02-07 17:00 | 2022-02-03 09:00 |  |  | refit and serviced lock at f shed
MSA-DTWD | WA5100263 | 2 | LIGHTHOUSE LOCKSMITHS | E-Block E18 the door lock is not locking/ unlocking at times | Security | Locksmith | 80 | Pass | Pass | -1 | -1 | 0.5 | 2022-02-02 12:12 | 2022-02-07 17:00 | 2022-02-03 09:00 | 2022-02-07 17:00 | 2022-02-03 09:30 |  |  | adjusted strike and serviced lock on E18 door
MSA-DFES | WA5101763 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Academy Facility - Entire Facility - see details | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-03 14:30 | 2022-02-10 17:00 | 2022-02-08 14:30 | 2022-02-10 17:00 | 2022-02-08 15:00 |  |  | Arrived on site and discussed with staff about the faulty lights. The lights reported are being fixed on another work order. The other work order is WA5090343. Staff advised there might of been a missed communication with Programed. They advised not to carry out in work on this work order.
MSA-DCA | WA5106314 | 1 | Critical Fire Protection & Training | Ground Floor - Foyer - Fault in area 18 - Fire panel fault | Fire Protection Services | Fire Protection - Monitor System | 99.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-07 07:24 | 2022-02-07 17:00 | 2022-02-07 07:30 | 2022-02-07 17:00 | 2022-02-07 08:00 |  |  | No fault on panel. No zone 18 . Security contacted before test. FIP clear.
MSA-DCA | WA5106814 | 1 | Earth & Water Pty Ltd | Ground - External - Museum Plaza -High flow alert on zone 13 | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.5 | 2022-02-07 11:51 | 2022-02-08 17:00 | 2022-02-07 12:00 | 2022-02-08 17:00 | 2022-02-07 12:30 |  |  | JOB COMPLETED - repaired broken sprinklers
MSA-DTAG | WA5108450 | 0 | AAA Ability Locksmiths | sally port door - Door leading into custody from carpark is faulty not securing through the system. | Security | Locksmith | 180 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-08 13:55 | 2022-02-08 15:55 | 2022-02-08 15:40 | 2022-02-08 17:55 | 2022-02-08 16:10 |  |  | Attend site, refit lock back onto sally port door.
MSA-DCA | WA5108528 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Studio - 1 - upper level - studio back wall broken double GPO | Electrical | General Electrical | 88.44 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-08 15:05 | 2022-02-11 17:00 | 2022-02-10 09:00 | 2022-02-11 17:00 | 2022-02-10 09:30 |  |  | Arrived onsite at 0900 to investigate broken gpo. Found gpo with damaged switch. Replaced damged gpo for new. Tested gpo and notified staff. Signed out at 930.
MSA-DTAG | WA5116480 | 2 | Bullant Security Pty Ltd | Registry - Ground - Front Registry waiting area - see details | Security | Locksmith | 164.09 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-11 15:51 | 2022-02-16 17:00 | 2022-02-15 11:35 | 2022-02-16 17:00 | 2022-02-15 12:05 |  |  | Attended site, repaired and re-attached locking mechanism to registry service area glass entry door using new fixing screws. Date on site: 15/02/2022 Time on site: 11:35 - 12:05
MSA-DFES | WA5126863 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Yard outside engine room - Broken PVC pipe under rear sink S trap | Plumbing & Drainage | Water | 92.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-14 10:16 | 2022-02-21 17:00 | 2022-02-21 10:45 | 2022-02-21 17:00 | 2022-02-21 11:15 |  |  | Upon inspection I found the 50 mil S&P trap was broken due to sun damage I have replaced it with a new S&P trap And tested that everything is working correctly
MSA-DTWD | WA5133282 | 1 | AWB Co. | C Block - Level 1 - C106 - Door and frame to C Block North End has been vandalised | Building | General Building | 86.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-15 09:13 | 2022-02-16 17:00 | 2022-02-15 11:30 | 2022-02-16 17:00 | 2022-02-15 12:00 |  |  | Attend site and reapair door lock
MSA-DTWD | WA5133863 | 2 | AWB Co. | J Block - Ground - J03 - Noisy ceiling fan | Electrical | General Electrical | 122.21 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-15 15:33 | 2022-02-18 17:00 | 2022-02-16 13:00 | 2022-02-18 17:00 | 2022-02-16 13:30 |  |  | Attended site and signed in. Completed JSA. Located faulty noisey fan, found loose coverings on fan. Made secured the covers and retested and adjusted fan to be super quiet. Staff in room were stoked that the noisey fan had been fixed. Signed out. Job complete
MSA-DTWD | WA5141494 | 1 | Equans Mechanical Services Australia | Staff room - Air con not cooling enough | Air Conditioning | Room Air Conditioners | 78.49 | Fail | Fail | 3 | 3 | 0.5 | 2022-02-16 10:40 | 2022-02-17 17:00 | 2022-03-11 12:00 | 2022-02-17 17:00 | 2022-03-11 12:30 |  |  | Attended site and carried out inspection of staff room A/C confirmed equipment operating normally. Checked air flow and found to be OK. Confirmed temps stable in office. Please note that there was a similar fault raised on WA5086695 which fixed all temps problems in office space. Confirmed equipment working. Work area left tidy.
MSA-DTWD | WA5163686 | 2 | Falcetta Plumbing and Gas | B5 - Level 1 - Male toilet - Urinal constantly leaking | Plumbing & Drainage | Toilets/Cisterns | 73.26 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-18 10:59 | 2022-02-23 17:00 | 2022-02-21 13:00 | 2022-02-23 17:00 | 2022-02-21 13:30 |  |  | inspected urinal sensor, site to monitor
MSA-DTWD | WA5163721 | 1 | Securex Security Systems & Services | H and G Block - Ground floor & Mezzanine Office - G1 & H6 - see details below | Security | Monitoring | 154.55 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-18 11:30 | 2022-02-21 17:00 | 2022-02-18 13:30 | 2022-02-21 17:00 | 2022-02-18 14:00 |  |  | (18/02/2022, 1330-1400) - Work NoteUser error for alot of the alarms. The zone Es they supplied are different to zone edsec said went off. We decided toleave it and if it happens again to get a report from edsec to check zones and times
MSA-DTWD | WA5163914 | 3 | Falcetta Plumbing and Gas | Staff Room Level 2 - Replace/repair faulty tap in kitchen | Plumbing & Drainage | Water | 73.26 | Pass | Pass | -1 | -1 | 0.5 | 2022-02-18 13:24 | 2022-02-25 17:00 | 2022-02-21 13:30 | 2022-02-25 17:00 | 2022-02-21 14:00 |  |  | inspected sink, lubricated filter faucet tap
MSA-DTWD | WA5187168 | 1 | Equans Mechanical Services Australia | AT - Ground - AT248 & AT253 - Air conditioners not working. | Air Conditioning | Room Air Conditioners | 78.49 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-22 11:49 | 2022-02-23 17:00 | 2022-02-23 11:15 | 2022-02-23 17:00 | 2022-02-23 11:45 |  |  | Arrived to wrong site completed paperwork accordingly.
MSA-DTAG | WA5187261 | 2 | Bullant Security Pty Ltd | Between Front Registry waiting area and Office entry - see notes below | Security | Locksmith | 155 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-22 12:13 | 2022-02-25 17:00 | 2022-02-22 14:40 | 2022-02-25 17:00 | 2022-02-22 15:10 |  |  | Attended site, viewed issue to door, requires different trade (Commercial glazier) to remove door and identify issue, I believe in transom closer, door not cantering to lock. Lock is working correctly when door manually centred.Date on site: 22/2/2022 Time on site: 14:40 - 15:10
MSA-DTAG | WA5188565 | 1 | Sapio Pty Ltd | Ground - Custody - Issue logging in to alarm programs | Security | Security Management System | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-23 09:51 | 2022-02-24 17:00 | 2022-02-24 09:00 | 2022-02-24 17:00 | 2022-02-24 09:30 |  |  | Attended site. Found account locked. Unlocked account and provided new password.Job completed
MSA-DFES | WA5188923 | 3 | Water2water Pty Ltd | Engine Room - Water cooler is not producing cold water | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 0.5 | 2022-02-23 12:39 | 2022-03-02 17:00 | 2022-03-01 10:00 | 2022-03-02 17:00 | 2022-03-01 10:30 |  |  | RENTAL UNIT - WATER BLOCK NEEDED RESETTING - NO CHARGE AS RENTAL UNIT
MSA-DTWD | WA5189016 | 2 | Water2water Pty Ltd | Urn handle broken off | Plumbing & Drainage | Water | 259.065 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-23 13:10 | 2022-02-28 17:00 | 2022-02-28 13:00 | 2022-02-28 17:00 | 2022-02-28 13:30 |  |  | A40421166D/A40421165C Zip BWU Replaced Tap
MSA-DTWD | WA5190753 | 2 | Swan Pest Control | Crèche and verandas - P Block - see details below | Pest Control | General Pest | 255 | Fail | Fail | 0 | 0 | 0.5 | 2022-02-24 14:13 | 2022-03-01 17:00 | 2022-03-04 06:00 | 2022-03-01 17:00 | 2022-03-04 06:30 |  |  | Sprayed all external with Bifrenthrin
MSA-DCA | WA5195633 | 1 | Automatic Fire Protection (ARA) | Store Room, Gallery 9 (behind lift) - Smoke detector in fault (& Isolated) – L3S70 | Fire Protection Services | Smoke and Heat Detection | 345.18 | Pass | Pass | 0 | 0 | 0.5 | 2022-02-28 13:49 | 2022-03-01 17:00 | 2022-02-28 15:00 | 2022-03-01 17:00 | 2022-02-28 15:30 |  |  | Replaced L3 D70 XP95 smoke detector in maintenance fault. Reset loop and Deisolated sensor all ok
MSA-DTWD | WA5195832 | 1 | Equans Mechanical Services Australia | All Building - Air conditioning not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 78.49 | Fail | Fail | 16 | 16 | 0.5 | 2022-02-28 16:43 | 2022-03-01 17:00 | 2022-06-21 16:00 | 2022-03-01 17:00 | 2022-06-21 16:30 |  |  | Attended site, signed in and accessed building 4. Checked operation of chillers and any faults / alarms. Found chillers working as per normal, recorded temperatures in building around 22.5degreese. Will monitor operation of chillers and building temperatures during routine maintenance.
MSA-DFES | WA5200110 | 2 | Seme Solutions Pty Ltd | Comms Cupboard 29 - Alarm panel room 22 - see notes below | Security | Security Management System | 180 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-01 14:05 | 2022-03-04 17:00 | 2022-03-02 07:00 | 2022-03-04 17:00 | 2022-03-02 07:30 |  |  | Located comms cabinet 29 - replaced 2 7AH batteries and checked fault had cleared
MSA-DTWD | WA5201388 | 1 | Critical Fire Protection & Training | Workshops - Zone 5 - fire alarm activation | Fire Protection Services | Fire Protection - Monitor System | 306.44 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-02 14:27 | 2022-03-03 17:00 | 2022-03-02 15:00 | 2022-03-03 17:00 | 2022-03-02 15:30 |  |  | Call out to fire panel in alarm on arrival found detector loop1 sensor 47 zone 5 corridor 2 east Located detector - appears to have activate due to dust.Replace detector system normal on departure 2 technicians on site for duration Use 1x ampac addressable smoke detector
MSA-DTWD | WA5203112 | 1 | Securex Security Systems & Services | G & H Blocks - Security alarm panel continually beeping, possible battery replacement needed. | Security | Monitoring | 379.27 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-03 10:49 | 2022-03-04 17:00 | 2022-03-03 13:30 | 2022-03-04 17:00 | 2022-03-03 14:00 |  |  | (03/03/2022, 1330-1400) - Work NoteReplaced battery in g block
MSA-DFES | WA5203751 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchenette - Kitchen cabinet shows extensive Mould growth - see notes below | Plumbing & Drainage | Water | 86.35 | Fail | Fail | 1 | 1 | 0.5 | 2022-03-03 16:30 | 2022-03-11 17:00 | 2022-03-16 09:00 | 2022-03-11 17:00 | 2022-03-16 09:30 |  |  | Attended site for kitchenette in volunteers Association building having extensive mould growth on inspection I have not found any signs of a leak it does appear there has been water left previously which has caused the mould to start growing I have spoke with Dwayne and he has advised me that they will be having the cupboards replaced
MSA-DFES | WA5203753 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Unisex Toilet - Near SimCen - Toilet continues to flush. Contractor to call prior to attending | Plumbing & Drainage | Toilets/Cisterns | 86.35 | Fail | Fail | 1 | 1 | 0.5 | 2022-03-03 16:33 | 2022-03-11 17:00 | 2022-03-16 10:30 | 2022-03-11 17:00 | 2022-03-16 11:00 |  |  | Attended site for uni sex toilet near Sim centre continuously flushing upon inspection I found the cistern lid was not fitted correctly and come away I have set the cistern lid down properly another system is functioning correctly cleaned up packed up
MSA-DTWD | WA5205400 | 0 | Total Security Systems Pty Ltd | Security system for whole of T block swipe access doors, have unlocked by themselves. | Building | Materials | 175 | Fail | Fail | 0 | 0 | 0.5 | 2022-03-07 07:14 | 2022-03-07 09:14 | 2022-03-08 13:45 | 2022-03-07 11:14 | 2022-03-08 14:15 |  |  | 8/3/2022 - Jose Pereira - 1.45pm to 2.15pmInvestigated the reason why door unlocked and found the public holidays weren't set
MSA-DTWD | WA5208357 | 1 | Critical Fire Protection & Training | Workshop - fire alarm activated | Fire Protection Services | Fire Protection - Monitor System | 326.44 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-09 08:14 | 2022-03-10 17:00 | 2022-03-09 11:30 | 2022-03-10 17:00 | 2022-03-09 12:00 |  |  | Call-out to fault on FIP. Found detector L2S61 zone 9 missing. Found detector, wasn’t missing but was faulty. Replaced detector with addressable Ampac. System normal on departure. 2 x technicians on site for works.
MSA-DTWD | WA5209111 | 2 | ADVANCED LOCK & KEY | B6 - B120 - Replace faulty door lock | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-09 13:38 | 2022-03-14 17:00 | 2022-03-11 11:35 | 2022-03-14 17:00 | 2022-03-11 12:05 |  |  | Serviced lock
MSA-DTWD | WA5215077 | 2 | ADVANCED LOCK & KEY | A Block - A338 - replace barrel as fallen out | Security | Locksmith | 145 | Fail | Fail | 0 | 0 | 0.5 | 2022-03-10 09:11 | 2022-03-15 17:00 | 2022-03-16 11:05 | 2022-03-15 17:00 | 2022-03-16 11:35 |  |  | Repair lock
MSA-DTWD | WA5215573 | 3 | ACTION GLASS & ALUMINIUM | Level 1 - B106 - repair Decal to glass door B106 | Glazing | Window Glass | 87.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-10 13:44 | 2022-03-17 17:00 | 2022-03-14 12:00 | 2022-03-17 17:00 | 2022-03-14 12:30 |  |  | ATTENDED SITE, INSTALLED CLIENT'S OWN DECAL ON DOOR
MSA-MRWA | WA5215734 | 0 | Automatic Fire Protection (ARA) | Fire Panel in fault and lose of communication | Fire Protection Services | Fire Protection - Monitor System | 491.62 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-10 16:36 | 2022-03-10 18:36 | 2022-03-10 18:00 | 2022-03-10 20:36 | 2022-03-10 18:30 |  |  | Checked FIP found zone in fault Z101 comms rm gas SIP. No fault on SIP when checked. No history log as SIP is old Inertia model. SIP has Vesda unit plugged in and checked airflow but both pipes sitting at 99%. Reset fault at main FIP panel clear. Called FAMS to check of code red had loss of communications and they advised their comms was ok and they didn’t have any record of loss of comms. Reset and deisolated panel all ok.
MSA-DTWD | WA5226362 | 1 | Complete Pest Management Services | U Block - Ground - U8 - Rodent smell please investigate to find origin | Pest Control | General Pest | 227.27 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-14 08:11 | 2022-03-15 17:00 | 2022-03-14 13:45 | 2022-03-15 17:00 | 2022-03-14 14:15 |  |  | Inspected roof void for bad smell - Deodorised
MSA-DTWD | WA5226550 | 1 | Complete Pest Management Services | Block U - U6 - Rodent smell please investigate to find origin | Pest Control | General Pest | 48 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-14 10:04 | 2022-03-15 17:00 | 2022-03-14 14:15 | 2022-03-15 17:00 | 2022-03-14 14:45 |  |  | Removed 1 rat and 1 mouse from for void
MSA-DTWD | WA5226626 | 1 | AWB Co. | A block - Level 2 - A220 - Male toilet - 3 Phase hot water unit is leaking | Electrical | General Electrical | 91.58 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-14 10:31 | 2022-03-15 17:00 | 2022-03-15 07:00 | 2022-03-15 17:00 | 2022-03-15 07:30 |  |  | Attended site and signed in, completed jsa, set up work area, fm arrived and informed me that plumber had completed job yesterday including electrical component as he had a restricted electrical license, packed up , completed paperwork, signed outJob completed
MSA-DFES | WA5231822 | 2 | Securex Security Systems & Services | Security alarm system in fault - please see the below for further notes | Security | Monitoring | 260 | Fail | Fail | 1 | 1 | 0.5 | 2022-03-15 15:28 | 2022-03-18 17:00 | 2022-03-24 09:00 | 2022-03-18 17:00 | 2022-03-24 09:30 |  |  | 24/03/2022, 900-930Main BuildingReplaced both batteries in main system.It's currently communicating and on 4gICV ShedThe icv shed is not our system and not monitored by us but not currently showing any faults on the display.
MSA-DTAG | WA5284421 | 0 | OCS SERVICES PTY LTD | Request covid19 disinfection clean to be performed for Level 14 today | Cleaning | Cleaning |  | Fail | Pass | 0 | 0 | 0.5 | 2022-03-20 15:13 | 2022-03-20 17:13 | 2022-03-20 17:30 | 2022-03-20 19:13 | 2022-03-20 18:00 |  |  | Covid clean
MSA-DTWD | WA5286422 | 3 | Swan Pest Control | Ground - Block M - room M05 - White ants are back in M Block | Pest Control | General Pest | 225 | Pass | Pass | -1 | -1 | 0.5 | 2022-03-21 16:00 | 2022-03-28 17:00 | 2022-03-22 12:15 | 2022-03-28 17:00 | 2022-03-22 12:45 |  |  | Injected skirting board in 2 places - one at back of class behind filing cabinet and the other under heater on opposite corner
MSA-DFES | WA5287600 | 0 | SONTEC WA PTY LTD | Rear Exit door - Kitchen to the courtyard - Egress Buttion is faulty | Security | Monitoring | 230 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-22 13:41 | 2022-03-22 15:41 | 2022-03-22 15:00 | 2022-03-22 17:41 | 2022-03-22 15:30 |  |  | 22/3/22 - Dylan ParslowFound door controller not responding.Reset controller and tested.All working.
MSA-DFES | WA5287812 | 3 | Securex Security Systems & Services | Communications Cabinet - security alarm backup battery is showing battery low | Security | Security Management System | 210 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-22 16:47 | 2022-03-29 17:00 | 2022-03-29 07:30 | 2022-03-29 17:00 | 2022-03-29 08:00 |  | WACCES | 29/03/2022, 730-800Replaced dgp1 battery
MSA-DTAG | WA5289546 | 1 | Schindler Lifts Australia | Lift 2 - Button 8 is missing in lift 2 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.5 | 2022-03-24 10:30 | 2022-03-25 17:00 | 2022-03-25 08:15 | 2022-03-25 17:00 | 2022-03-25 08:45 |  |  | to be closed out at $0 cost
MSA-DFES | WA5294241 | 2 | Dom's Total Grounds Maintenance | Front House - Ground - Lawn - see notes below | Landscaping & Gardening | Grounds Maintenance | 157 | Fail | Fail | 0 | 0 | 0.5 | 2022-03-28 14:41 | 2022-03-31 17:00 | 2022-03-31 17:30 | 2022-03-31 17:00 | 2022-03-31 18:00 |  |  | call Out & Repair Retic Supply Parts $17
MSA-DTAG | WA5295304 | 1 | AWB Co. | Ground - Clerk of the Court Office - Flickering fluoro | Electrical | General Electrical | 99.38 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-29 12:31 | 2022-03-30 17:00 | 2022-03-29 15:00 | 2022-03-30 17:00 | 2022-03-29 15:30 |  |  | Attended site and signed in. Completed JSA. Located clerks office in admin. Found lights to be switched off. Switched and found flickering fluro above the desk. Supply and replaced tube as required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5295546 | 1 | Protek 24/7 Building & Maintenance | Block 3 Heavy Auto – Truck Dyno area - Guard rail To be re-attached to concrete floor | Building | General Building | 81.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-29 15:17 | 2022-03-30 17:00 | 2022-03-30 12:15 | 2022-03-30 17:00 | 2022-03-30 12:45 |  |  | Guard rail re-attached
MSA-DTAG | WA5295583 | 3 | AWB Co. | Basement - Cell 6 - Wall paint peeled off in multiple locations - see notes below | Painting | Internal | 86.5 | Pass | Pass | -1 | -1 | 0.5 | 2022-03-29 16:03 | 2022-04-05 17:00 | 2022-03-30 13:00 | 2022-04-05 17:00 | 2022-03-30 13:30 |  |  | Attended site and inspected work that was required.BRAF submitted and declinedclose cost to date
MSA-DTAG | WA5297875 | 3 | Gilmour & Jooste Electrical | Level 1 - Court 2 - 2 Fluorescents (Side) in Court 2 needs replacing. Work to be completed by 9.30am | Electrical | General Electrical | 77.04 | Pass | Pass | 0 | 0 | 0.5 | 2022-03-31 13:40 | 2022-04-07 17:00 | 2022-04-06 09:15 | 2022-04-07 17:00 | 2022-04-06 09:45 |  |  | Replaced blown globes in court 2
MSA-DTAG | WA5303613 | 1 | Bullant Security Pty Ltd | Ground - Mazza JA Chambers – Balcony - see notes below | Security | Locksmith | 155 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-04 11:13 | 2022-04-05 17:00 | 2022-04-05 10:30 | 2022-04-05 17:00 | 2022-04-05 11:00 |  |  | Attended site to repair balcony door lock.Date on site: 05/04/2022Time on site: 10:30am - 11:00am
MSA-DTWD | WA5304157 | 2 | Critical Fire Protection & Training | E-Block - Restaurant Kitchen - fire extinguisher Faulty | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 187.23 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-04 15:14 | 2022-04-07 17:00 | 2022-04-07 15:00 | 2022-04-07 17:00 | 2022-04-07 15:30 |  |  | Identified the ‘faulty’ extinguisher, Found 3.5kg Co2 that had been used, replaced with new 3.5kg Co2Far part of restaurant kitchen
MSA-DTWD | WA5304739 | 2 | Total Security Systems Pty Ltd | T block ground level - Ground level - Alarm panel - Alarm battery showing fault | Security | Monitoring | 335 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-05 09:29 | 2022-04-08 17:00 | 2022-04-06 10:30 | 2022-04-08 17:00 | 2022-04-06 11:00 |  |  | 6/4/2022 - Michael Higginbotham - 10.30am to 11amReplaced 4 batteries in G-block ground west cabinet room T044, tested OK. job complete.
MSA-DTWD | WA5304753 | 2 | AWB Co. | T block Library - T014 staff office - Ceiling florescent lights x2 not working above office desk | Electrical | General Electrical | 136.71 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-05 09:35 | 2022-04-08 17:00 | 2022-04-05 13:00 | 2022-04-08 17:00 | 2022-04-05 13:30 |  |  | Attended site signed in completed jsa. Spoke with Susan about job in library. Located a light which had two tubes out. Reasoning for this is its connected in series so if one goes out they both go out. Replaced with new t5 tubes and works perfect now.Site contacts were not on site to get signiture slip signed it was emailed to kristy.raj@smtafe.wa.edu.au*** job completed ***
MSA-DFES | WA5304892 | 3 | Protek 24/7 Building & Maintenance | 3 - Ground - Station front - Blue flashing front station (front of gym) requires refixing - loose | Building | General Building | 121.7 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-05 10:33 | 2022-04-12 17:00 | 2022-04-06 10:00 | 2022-04-12 17:00 | 2022-04-06 10:30 |  |  | repair flashing
MSA-DFES | WA5306065 | 3 | Protek 24/7 Building & Maintenance | Main carpark electric gate -see details below | Building | Steel Fencing & Gates | 81.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-06 09:54 | 2022-04-13 17:00 | 2022-04-12 07:00 | 2022-04-13 17:00 | 2022-04-12 07:30 |  | WACCES | Replace battery on carpark electric Gate
MSA-DTWD | WA5307753 | 2 | Protek 24/7 Building & Maintenance | Building 1 - Level 1 - Entrance Door - Main door to walkway has dropped and catching on ground | Building | General Building | 691.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-07 15:47 | 2022-04-12 17:00 | 2022-04-11 10:30 | 2022-04-12 17:00 | 2022-04-11 11:00 |  | WACCES | Repair door to main walkway
MSA-DTAG | WA5308039 | 3 | Midolo Building Services | Ground - Male Female Public toilets - Soap dispensers are not securely screwed to wall and leaking | Building | General Building | 99.92 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-08 08:35 | 2022-04-19 17:00 | 2022-04-19 10:00 | 2022-04-19 17:00 | 2022-04-19 10:30 |  |  | SOAP DISPENSERS RE-SECURED TO WALL
MSA-DFES | WA5308105 | 1 | Go Doors | Front panel door - 1A - glass door - stuck in the up position and flashing fault | Building | General Building | 535 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-08 09:00 | 2022-04-11 17:00 | 2022-04-08 15:00 | 2022-04-11 17:00 | 2022-04-08 15:30 |  |  | Works completed
MSA-DCA | WA5308290 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Level 5 – Plant room - Behind chiller 4 - RO plant leaking | Air Conditioning | Room Air Conditioners | 83.725 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-08 10:23 | 2022-04-13 17:00 | 2022-04-08 11:30 | 2022-04-13 17:00 | 2022-04-08 12:00 |  |  | Leak repaired
MSA-DTAG | WA5308360 | 2 | Sapio Pty Ltd | Level 6 and Level 8 - Court room 606 and court room 809 - please see details below | Electrical | General Electrical | 130 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-08 11:03 | 2022-04-13 17:00 | 2022-04-08 13:30 | 2022-04-13 17:00 | 2022-04-08 14:00 |  |  | Work performed by Ken Moore (08/04/2022)Attended site. Checked in session buttons on Level 6 and 8, all working ok.
MSA-DFES | WA5308970 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | one light in SO dorm not working | Electrical | General Electrical | 111.36 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-09 14:12 | 2022-04-13 17:00 | 2022-04-12 13:30 | 2022-04-13 17:00 | 2022-04-12 14:00 |  |  | Located faulty light. Replaced faulty tubes and starters with new.
MSA-DFES | WA5311977 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Light in dry cleaning room not operating | Electrical | Lighting, Internal | 92.4 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-11 10:10 | 2022-04-14 17:00 | 2022-04-12 09:00 | 2022-04-14 17:00 | 2022-04-12 09:30 |  |  | Located faulty light. Replaced faulty tube and starter with new.
MSA-DTWD | WA5312065 | 1 | Critical Fire Protection & Training | E-Block - Restaurant kitchen - fire Alarm activation | Fire Protection Services | Fire Protection - Monitor System | 254.14 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-11 10:46 | 2022-04-12 17:00 | 2022-04-11 12:00 | 2022-04-12 17:00 | 2022-04-11 12:30 |  |  | Found smoke detector in alarm. No obvious reason for activation. Replaced detector.2 x technicians on site.1 x conventional Ampac detector.
MSA-DFES | WA5323430 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Lecture Room 10 - has no power | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-13 08:09 | 2022-04-14 17:00 | 2022-04-13 10:30 | 2022-04-14 17:00 | 2022-04-13 11:00 |  |  | Arrived on site at 1030 to investigate power outage in lecture room 10. Located relative db and discovered rcd switched off. Ensured power did not trip during visit. Left site at 1100.
MSA-DTAG | WA5323615 | 1 | AWB Co. | Hallway from Chambers to Registry - Flickering light | Electrical | Lighting, Internal | 137.01 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-13 09:36 | 2022-04-14 17:00 | 2022-04-14 07:30 | 2022-04-14 17:00 | 2022-04-14 08:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located lights out in corridor. Changed 2x 2ft fluros. Notified of works completed. **job complete**
MSA-DTAG | WA5325210 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Entire Facility - No water supply to entire facility | Plumbing & Drainage | Water | 83.725 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-14 08:28 | 2022-04-19 17:00 | 2022-04-14 10:50 | 2022-04-19 17:00 | 2022-04-14 11:20 |  |  | Completed
MSA-DCA | WA5325547 | 3 | Critical Fire Protection & Training | CRC - Ground Level - Leaking Fire Hose Reel - see notes | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 60 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-14 10:03 | 2022-04-26 17:00 | 2022-04-21 15:00 | 2022-04-26 17:00 | 2022-04-21 15:30 |  |  | FHR nozzle leaking - Removed old nozzleReplaced with new nozzleTightened clamps and ensured leak stopped
MSA-DFES | WA5377654 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Possible leak or may be the station hydrant - Water Corp bill seems unreasonable | Plumbing & Drainage | Water | 86.35 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-20 08:14 | 2022-04-26 17:00 | 2022-04-26 13:00 | 2022-04-26 17:00 | 2022-04-26 13:30 |  |  | Investigating high water bill
MSA-DFES | WA5377784 | 3 | Anvil Doors | Ground Level - Engine Room - Electric motor for engine room door 2 is leaking oil | Building | Automatic Doors | 350 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-20 08:56 | 2022-04-28 17:00 | 2022-04-20 12:00 | 2022-04-28 17:00 | 2022-04-20 12:30 |  |  | Attended Vincent Fire Station. Technician inspected report of oil leak coming from motor and determined that the oil has come from the drive chain only. no further action is required. Please refer to signature slip and service report.
MSA-DTWD | WA5377891 | 1 | CONNECT SECURITY SYSTEMS | Alarm code fault | Security | Monitoring | 153.18 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-20 09:47 | 2022-04-21 17:00 | 2022-04-21 10:16 | 2022-04-21 17:00 | 2022-04-21 10:46 |  |  | reprog guards code
MSA-DTWD | WA5380258 | 2 | AWB Co. | E58 Large Scale Kitchen - Damaged lead plug on mixer | Electrical | General Electrical | 122.21 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-22 09:52 | 2022-04-28 17:00 | 2022-04-26 16:00 | 2022-04-28 17:00 | 2022-04-26 16:30 |  |  | Attended site and signed in. Completed JSA. Located large kitchen. Found mixer plugged into wall to have a knick in the cable flex. To exposed copper. Repaired and fixed cabling and plug top. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5380459 | 3 | Water2water Pty Ltd | Rooms 8G45 & 8G46 - Boiling Billi showing filter needs replacing | Plumbing & Drainage | Water | 117.925 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-22 12:40 | 2022-05-02 17:00 | 2022-04-27 11:30 | 2022-05-02 17:00 | 2022-04-27 12:00 |  |  | Checked and cleared fault log, filter has been changed. Checked and tested, all ok
MSA-DTWD | WA5383539 | 0 | Assa Abloy Entrance Systems Aust P/L-WA | the main Auto door at 25 Aberdeen Street is not working properly it's opening and closing | Building | Doors | 675 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-27 18:32 | 2022-04-27 20:32 | 2022-04-27 20:15 | 2022-04-27 22:32 | 2022-04-27 20:45 |  |  | Attended site and inspected auto door. Noted door self actuating and not closing properly. Found outside sensor causing issues. Required to adjustand tested operations all OK.
MSA-DTWD | WA5384043 | 2 | AWB Co. | D016 - faulty fluro | Electrical | General Electrical | 91.58 | Pass | Pass | 0 | 0 | 0.5 | 2022-04-28 09:21 | 2022-05-03 17:00 | 2022-05-02 13:30 | 2022-05-03 17:00 | 2022-05-02 14:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located lighting,refixed fitting to ceiling, cleaned up, packed up, completed paperwork,signed out, ***job completed***
MSA-DTWD | WA5384320 | 2 | ECO PLUMBING AND GAS PTY LTD | E75 - Asian Kitchen - Flick Mixer Leaking at bench station #7 | Plumbing & Drainage | Water | 183.57 | Fail | Fail | 0 | 0 | 0.5 | 2022-04-28 11:50 | 2022-05-03 17:00 | 2022-05-05 07:30 | 2022-05-03 17:00 | 2022-05-05 08:00 |  |  | Replaced mixer and spout
MSA-DTWD | WA5385486 | 3 | AWB Co. | Carpark 2 - Faulty pole light near entrance | Electrical | Lighting, External | 91.58 | Pass | Pass | -1 | -1 | 0.5 | 2022-04-29 10:18 | 2022-05-06 17:00 | 2022-04-29 13:30 | 2022-05-06 17:00 | 2022-04-29 14:00 |  |  | Attended site signed in jsa completed. Found reported pole light not on. No cables connected to it as the cable between two of them is faulty and no way to run new one. New led light was fitted on corner of building facing that way. Re adjusted timer to turn on earlier. *** job completed ***
MSA-DTAG | WA5399210 | 3 | Midolo Building Services | L3 Court 37 Loose capping on public stairs in the back of the courtroom | Carpentry | Staircases, Balustrades and Handrails | 99.92 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-09 18:28 | 2022-05-16 17:00 | 2022-05-11 12:45 | 2022-05-16 17:00 | 2022-05-11 13:15 |  |  | re secured step & capping
MSA-DFES | WA5408014 | 3 | Complete Pest Management Services | Main Administration - SES/Marine Training Office -see details below | Pest Control | General Pest | 234.37 | Fail | Fail | 0 | 0 | 0.5 | 2022-05-11 16:20 | 2022-05-18 17:00 | 2022-05-19 11:30 | 2022-05-18 17:00 | 2022-05-19 12:00 |  |  | Installed 3 beta rodent bait station
MSA-DTWD | WA5438297 | 3 | ECO PLUMBING AND GAS PTY LTD | dripping tap in room C41,Hairdressing C Block | Plumbing & Drainage | Water | 98.57 | Fail | Fail | 4 | 4 | 0.5 | 2022-05-16 13:27 | 2022-05-23 17:00 | 2022-06-20 14:15 | 2022-05-23 17:00 | 2022-06-20 14:45 |  | WACCES | Serviced hot and cold taps
MSA-DTWD | WA5454546 | 3 | PEEL LOCK SERVICES PTY LTD | C Block - Ground Level - Rear Sliding door - Lock broken - needs replacement | Security | Locksmith |  | Pass | Pass | -1 | -1 | 0.5 | 2022-05-17 12:16 | 2022-05-24 17:00 | 2022-05-19 08:30 | 2022-05-24 17:00 | 2022-05-19 09:00 |  |  | Repairs to lock
MSA-DTAG | WA5460313 | 2 | MALCO FLOORING PTY LTD | Level 9 - Court 92 - Carpet skirting board panels not sticking to the wall behind witness stand | Flooring | Carpet | 90 | Fail | Fail | 0 | 0 | 0.5 | 2022-05-18 12:51 | 2022-05-23 17:00 | 2022-05-26 06:45 | 2022-05-23 17:00 | 2022-05-26 07:15 |  |  | LEVEL 9 COURT 92 CARPET SKIRTING BOARD PANELS NOT STICKING TO THE WALL BEHIND WITNESS STANDATTENDED SITE AND RESTUCK LOOSE CARPET TO WALL
MSA-DCA | WA5461710 | 1 | Critical Fire Protection & Training | Stage door - False fire alarm activation, requires a reset | Fire Protection Services | Fire Protection - Monitor System | 99.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-19 08:20 | 2022-05-20 17:00 | 2022-05-19 09:00 | 2022-05-20 17:00 | 2022-05-19 09:30 |  |  | Attended as a call-out to investigate/reset false activated fire alarm. On arrival system sitting all operations as normal. Investigated history log and found level 1 Chester building male toilet went into alarm at 17:36 (18/5/22) next log is a alarm acknowledgment at 17:38 and then system reset requested and successful at 17:49. If false alarm occurs from same device recommend replacing detector with thermal detector to eliminate false alarm risk from smoke/aerosolsArrived on site: 9:00amDeparted Site: 9:30am
MSA-DTWD | WA5461762 | 1 | Protek 24/7 Building & Maintenance | E30 Kitchen - Water leaking through ceiling and light fitting onto benches | Building | General Building | 81.25 | Fail | Fail | 0 | 0 | 0.5 | 2022-05-19 08:45 | 2022-05-20 17:00 | 2022-05-23 10:00 | 2022-05-20 17:00 | 2022-05-23 10:30 |  |  | Roof unable to be accessed This was unable to be looked at during the first attendance due to rain, but we found it to be associated with a different work order that was raised in the same area when we attended that one.Both have now been closed out as per the clients request, now that they have seen no further evidence of leaks
MSA-DCA | WA5462559 | 3 | ADVANCED LOCK & KEY | Substage - Street Level - Substage Door (Eastern End) - Faulty Lock - See notes below | Security | Locksmith | 149.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-19 16:55 | 2022-05-26 17:00 | 2022-05-26 13:50 | 2022-05-26 17:00 | 2022-05-26 14:20 |  |  | Service Lock
MSA-DTWD | WA5468318 | 0 | Securex Security Systems & Services | A Block - Level 3 - Duress alarm - remove faulty duress alarm | Security | Monitoring | 260 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-20 08:38 | 2022-05-20 10:38 | 2022-05-20 10:00 | 2022-05-20 12:38 | 2022-05-20 10:30 |  |  | 20/05/2022, 1000-1030Located duress and programmed zone 73 out
MSA-DTWD | WA5468667 | 2 | Swan Pest Control | Room A126 - Possible dead rat in celling of A126 staff room | Pest Control | General Pest | 185 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-20 11:35 | 2022-05-25 17:00 | 2022-05-24 10:45 | 2022-05-25 17:00 | 2022-05-24 11:15 |  |  | No dead rodent was found. Installed 5 large cardboard rodent stations and 10 Ditrac blocks
MSA-MRWA | WA5471808 | 2 | SONTEC WA PTY LTD | Reception - Site PA System is not working - lost power | Security | Monitoring | 276.75 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-23 13:22 | 2022-05-26 17:00 | 2022-05-26 14:15 | 2022-05-26 17:00 | 2022-05-26 14:45 |  |  | 26/5/22 - Dean SimpsonTested cable from amp to microphone, no fault with cable. reconnected microphone and power cycled equipment. tested operation, all working
MSA-DTAG | WA5473282 | 1 | Sapio Pty Ltd | ground - court 2 - Issue with the time delay locks on court 2 doors: see notes | Security | Security Management System | 162.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-24 13:19 | 2022-05-25 17:00 | 2022-05-25 09:00 | 2022-05-25 17:00 | 2022-05-25 09:30 |  | WACCES | Could not fault door as it opened eventide within the waiting period. Advised court manager and recommended to replaced exit buttons if occurs again.
MSA-DTWD | WA5475891 | 3 | Falcetta Plumbing and Gas | Level 3 - Male Student Toilet - Urinal not flushing | Plumbing & Drainage | Toilets/Cisterns | 78.835 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-25 09:17 | 2022-06-01 17:00 | 2022-05-26 15:00 | 2022-06-01 17:00 | 2022-05-26 15:30 |  |  | dislodged flush mechanism
MSA-DTWD | WA5477465 | 3 | Critical Fire Protection & Training | N223-Visual Line Fault" to L1N on EWIS panel | Fire Protection Services | Fire Protection - Monitor System | 141.21 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-25 13:51 | 2022-06-01 17:00 | 2022-05-26 12:00 | 2022-06-01 17:00 | 2022-05-26 12:30 |  |  | Attended site to investigate reported fault to EWIS system.On arrival found EWIS panel operating as all systems normal. No faults present during visit.Physically investigated area of reported fault in level 1 north block for issues with visual strobe devices. Found no apparent signs of damage or water ingress. Client to monitor for re-occurrence and requested client take photo of panel during fault condition
MSA-DTAG | WA5480035 | 1 | AHS Services WA Pty Ltd (Anchor) | Custody Area - Basement - Custody Male Toilets - Male Toilets – Urinal has a strong odour | Plumbing & Drainage | Toilets/Cisterns | 88.315 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-27 14:50 | 2022-05-30 17:00 | 2022-05-27 15:00 | 2022-05-30 17:00 | 2022-05-27 15:30 |  |  | Completed
MSA-DFES | WA5480042 | 3 | Protek 24/7 Building & Maintenance | Level 1 - Kitchen - Draw with the bin inside no longer closes | Building | General Building | 81.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-27 14:52 | 2022-06-03 17:00 | 2022-06-01 10:00 | 2022-06-03 17:00 | 2022-06-01 10:30 |  |  | Replace Bins back on sliding tracks
MSA-DTWD | WA5480948 | 3 | Critical Fire Protection & Training | North Block - N223 - Emergency control room - Line fault on EWIS Panel | Fire Protection Services | Fire Protection - Monitor System | 47.07 | Pass | Pass | -1 | -1 | 0.5 | 2022-05-30 09:36 | 2022-06-07 17:00 | 2022-05-31 10:30 | 2022-06-07 17:00 | 2022-05-31 11:00 |  |  | No faults on EWIS panel on arrival.Unable to investigate any further as faults not active during visit. Spoke to Dave Gaff for further action required. He requested to halt investigation until further notice/fault active.
MSA-MRWA | WA5481023 | 1 | Siemens Ltd | Front boom gate - not working - access reader is not working | Security | Access Control |  | Pass | Pass | 0 | 0 | 0.5 | 2022-05-30 10:24 | 2022-05-31 17:00 | 2022-05-30 10:30 | 2022-05-31 17:00 | 2022-05-30 11:00 |  |  | Repairs to gate
MSA-DTAG | WA5481111 | 1 | Sapio Pty Ltd | Ground Floor - Middle Custody Gate - wont latch | Security | Access Control | 75 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-30 10:58 | 2022-05-31 17:00 | 2022-05-30 14:30 | 2022-05-31 17:00 | 2022-05-30 15:00 |  |  | found lock tongue sense sticky, relocated with key and cleaned internals with WD40.tested and confirmed ok
MSA-DTWD | WA5482053 | 2 | Casa Security Pty Ltd | Zone 53 - faulty - cannot reset | Security | Monitoring | 292.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-31 08:48 | 2022-06-03 17:00 | 2022-06-03 09:00 | 2022-06-03 17:00 | 2022-06-03 09:30 |  |  | ZONE 53 - FAULTY - CANNOT RESETCHECKED DEVICE/REPLACED BATTERIESZONE WOULD NOT RESTORERECOMMENDED DEVICE BE REPLACED - AUTHORISED BY SILVIORETURNED SAME DAY TO REPLACE WIRELESS SENSORTESTED - ALL OKSYSTEM RESTORED TO NORMAL
MSA-DFES | WA5482798 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - change rooms - Blocked toilet in womens change rooms ground floor | Plumbing & Drainage | Toilets/Cisterns | 86.35 | Pass | Pass | 0 | 0 | 0.5 | 2022-05-31 15:37 | 2022-06-03 17:00 | 2022-06-02 07:45 | 2022-06-03 17:00 | 2022-06-02 08:15 |  |  | I attended site for block toilet in the female change rooms I have not been able to find the toilet affected I inspect the toilet in the change rooms as well as in the surrounding area tested them all several times and found no issues cleaned up packed up
MSA-DTWD | WA5487878 | 3 | ECO PLUMBING AND GAS PTY LTD | E313 - Vehicle wash Bay - Sump blocked causing bad smell | Plumbing & Drainage | Drainage | 91.57 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-02 09:10 | 2022-06-10 17:00 | 2022-06-07 16:30 | 2022-06-10 17:00 | 2022-06-07 17:00 |  |  | No issue found
MSA-DTAG | WA5491400 | 1 | Sapio Pty Ltd | Courtroom 3 - Magistrate entry/exit door - duress button the Magistrate entry/exit door isn’t lockin | Security | Access Control | 130 | Pass | Pass | -1 | -1 | 0.5 | 2022-06-03 15:28 | 2022-06-07 17:00 | 2022-06-03 16:00 | 2022-06-07 17:00 | 2022-06-03 16:30 |  |  | All working normally. Issue is relating to physical lock barrel not being locked and allows free handle when it should notbe. Staff will raise to locksmith.
MSA-DTWD | WA5496245 | 3 | AHS Services WA Pty Ltd (Anchor) | Gas Hot water booster fault code 65 not heating water | Plumbing & Drainage | HWS/Units Electric & Gas | 83.725 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-09 08:39 | 2022-06-16 17:00 | 2022-06-14 14:30 | 2022-06-16 17:00 | 2022-06-14 15:00 |  |  | Error code 65, attempted to clean filters on inlet however still isnt working . Reccomend rheem technician to have a look.
MSA-DTWD | WA5496568 | 2 | AWB Co. | T Block - Switch board - Blue 15 Circuit Breaker - faulty and will not reset | Electrical | General Electrical | 91.58 | Pass | Pass | -1 | -1 | 0.5 | 2022-06-09 11:20 | 2022-06-14 17:00 | 2022-06-10 07:00 | 2022-06-14 17:00 | 2022-06-10 07:30 |  | WCAPPR | Attended site signed in jsa completed. Spoke with rick about issue with b15. he had unplugged all vending machines and circuit would not reset. I came and reset it first try. consistantly kept tripping it manually to try see if it would jam and not reset and wouldnt kept staying on. rick said no rain had been but maybe vending machine company had done something as they came to restock supplies. have left the job open as rick had requested. Powerboard is used on b15 my guess is some water had got into it as its a little exposed. Left job open as requested for a week. **Email attached from site advising to close out job**
MSA-DTWD | WA5511738 | 2 | Critical Fire Protection & Training | N223 - Fire panel in alarm - Earth fault detected | Fire Protection Services | Fire Protection - Monitor System | 47.07 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 08:24 | 2022-06-16 17:00 | 2022-06-14 10:00 | 2022-06-16 17:00 | 2022-06-14 10:30 |  |  | On arrival found fire panel in alarm caused by water ingress into thermal detector on level 5 bathroom due to boiler leak on level 6 coming through roof. This is also the cause for a current earth fault to the system.System will require replacement of 2x thermal detectors in level 5 toilets after water damage and leaks have been repaired including roof repair works due to damaged ceiling.
MSA-DTWD | WA5511780 | 2 | AHS Services WA Pty Ltd (Anchor) | A123 - Female staff toilet not working | Plumbing & Drainage | Toilets/Cisterns | 47.095 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 08:59 | 2022-06-16 17:00 | 2022-06-14 11:30 | 2022-06-16 17:00 | 2022-06-14 12:00 |  |  | Readjusted toilet cistern
MSA-DTWD | WA5511961 | 2 | AHS Services WA Pty Ltd (Anchor) | Q-Block 1st Floor ladies toilets middle cubicle has a loose/broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 170.135 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 11:34 | 2022-06-16 17:00 | 2022-06-14 13:30 | 2022-06-16 17:00 | 2022-06-14 14:00 |  |  | Tightened toilet seat
MSA-DTAG | WA5512131 | 1 | Sapio Pty Ltd | Admin - Front entrance/exit to Complex- automatic door has stopped working- see notes below | Security | Access Control | 162.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 14:15 | 2022-06-14 17:00 | 2022-06-13 15:00 | 2022-06-14 17:00 | 2022-06-13 15:30 |  |  | Found no 240V at Auto Door, requires an Electrician to attend.
MSA-DTWD | WA5512177 | 3 | AWB Co. | C008 - 1 x lights out | Electrical | Lighting, Internal | 120.68 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 14:37 | 2022-06-20 17:00 | 2022-06-20 10:00 | 2022-06-20 17:00 | 2022-06-20 10:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located faulty lighting and made list of parts, replaced with new, tested all lights and they are working as intended , completed paperwork,packed up, signed out ***job complete**
MSA-DTWD | WA5512181 | 3 | AWB Co. | C009 - 2 x lights out | Electrical | Lighting, Internal | 126.37 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 14:38 | 2022-06-20 17:00 | 2022-06-20 10:30 | 2022-06-20 17:00 | 2022-06-20 11:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located faulty lighting and made list of parts, picked up materials from wholesaler, replaced with new, tested all lights and they are working as intended , completed paperwork,packed up, signed out ***job complete**
MSA-DTAG | WA5512220 | 1 | Sapio Pty Ltd | Mandurah Court front entry doors - possible warranty job - see notes below | Building | Security Doors | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-13 15:22 | 2022-06-14 17:00 | 2022-06-14 09:00 | 2022-06-14 17:00 | 2022-06-14 09:30 |  |  | Programmed Auto Door times to 08:30 to 16:30, extended Door Open Too Long time to 50 seconds
MSA-DTWD | WA5513156 | 2 | AWB Co. | The Lights in Classroom E603 have tripped the electrical circuit breaker twice in the past 4 days. | Electrical | Lighting, Internal | 91.58 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-14 08:12 | 2022-06-17 17:00 | 2022-06-17 14:30 | 2022-06-17 17:00 | 2022-06-17 15:00 |  |  | Attended site and signed in. Completed JSA. Located classroom lights to be reported tripping, found no lights out and not tripping. Tested circuit at switchboard and found no present faults. Was advised that when it rains it trips. Have told site to look into the roof leak and drainage to stop water coming into roof space where cabling is. No fault found at time of visit. Signed out. Job complete
MSA-DTAG | WA5513554 | 1 | Sapio Pty Ltd | Level 3 - Camera - out of focus | Security | CCTV Surveillance | 130 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-14 11:27 | 2022-06-15 17:00 | 2022-06-14 13:30 | 2022-06-15 17:00 | 2022-06-14 14:00 |  |  | Attended site, refocused camera C308, checked, OK.
MSA-DCA | WA5513964 | 0 | Kone Elevators Pty Ltd | Francis Street - Level 1 - Escalator 5 - handrail inlet fault | Lifts | Escalators or Moving Walk |  | Pass | Pass | 0 | 0 | 0.5 | 2022-06-14 14:34 | 2022-06-14 16:34 | 2022-06-14 16:30 | 2022-06-14 18:34 | 2022-06-14 17:00 |  |  | repairs to escalator
MSA-DTWD | WA5521331 | 2 | AWB Co. | Ground Floor - Customer Service - Faulty power point behind Carols desk | Electrical | General Electrical | 91.58 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-15 10:29 | 2022-06-20 17:00 | 2022-06-20 07:45 | 2022-06-20 17:00 | 2022-06-20 08:15 |  |  | Attended site and signed in. Completed JSA. Located reported faulty gpo. Tested and found power to both outlets. Used fan heater on gpo that usually is used and it works well. No fault found. Signed out. Job complete
MSA-DTWD | WA5534688 | 3 | AWB Co. | Outdoor Area - broken light fitting | Electrical | Lighting, External | 120.68 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-16 13:17 | 2022-06-23 17:00 | 2022-06-20 12:45 | 2022-06-23 17:00 | 2022-06-20 13:15 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located light fitting, discussed options with fm , explained that since fitting was so old we would either have to replace diffuser with custom made cover or replace light completely ( both roughly the same price to do ). Fm said to close off job as light fitting wasn’t posing a risk and he will discuss these options with Silvio. Completed paperwork , signed out **job completed**
MSA-DTAG | WA5565604 | 0 | Sapio Pty Ltd | Level 8 -803 - duress alarm - faulty not working | Security | Monitoring | 177.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-22 09:28 | 2022-06-22 11:28 | 2022-06-22 10:00 | 2022-06-22 13:28 | 2022-06-22 10:30 |  |  | Attended site. Replaced battery in Room 803 RF duress. Tested all OK.
MSA-DTWD | WA5565664 | 2 | BJ SYSTEMS | Security System - Ground - Swipe card access for semester break | Security | Access Control | 207.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-22 09:55 | 2022-06-27 17:00 | 2022-06-27 14:30 | 2022-06-27 17:00 | 2022-06-27 15:00 |  |  | Checked Gilmore lecturer access, they will have access to main doors during holidays. Dennis will set door schedules to Holiday calendar when it starts
MSA-DTWD | WA5565705 | 2 | Water2water Pty Ltd | K20 - Water cooler faulty | Plumbing & Drainage | Water | 117.925 | Pass | Pass | -1 | -1 | 0.5 | 2022-06-22 10:18 | 2022-06-27 17:00 | 2022-06-22 11:15 | 2022-06-27 17:00 | 2022-06-22 11:45 |  |  | New unit required - BRAF DECLINED.
MSA-DTAG | WA5566668 | 2 | Total Security Systems Pty Ltd | Door going into custody area - Swipe card door not closing automatically | Security | Access Control | 175 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-23 10:32 | 2022-06-28 17:00 | 2022-06-28 13:45 | 2022-06-28 17:00 | 2022-06-28 14:15 |  |  | 28/6/2022 - Jose Pereira - 1.45pm to 2.15pm (no travel as was already on site for another job)Adjusted the door closer no issues with access control. Door now closes.
MSA-DFES | WA5566750 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Main switchboard - protected power - B12 RCD needs replacing | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-23 10:37 | 2022-06-28 17:00 | 2022-06-27 13:30 | 2022-06-28 17:00 | 2022-06-27 14:00 |  | WACCES | Arrived onsite at 13:30 to investigate B12 RCD needs replacing. Found issue had already been resolved and job was in the process of being cancelled. Confirmed issue had definitely been resolved and left site at 14:00
MSA-DFES | WA5567045 | 2 | Protek 24/7 Building & Maintenance | Entrance to RO - Fire damage to front steps needs removal | Building | General Building | 81.25 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-23 14:07 | 2022-06-28 17:00 | 2022-06-27 10:30 | 2022-06-28 17:00 | 2022-06-27 11:00 |  |  | Inspect Damage in front of the steps to the office
MSA-DTWD | WA5570794 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block SK1 water filter leaking L/H rear sink water has been isolated | Plumbing & Drainage | Water | 91.225 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-28 14:58 | 2022-07-01 17:00 | 2022-06-29 07:00 | 2022-07-01 17:00 | 2022-06-29 07:30 |  |  | Job completed
MSA-DFES | WA5570861 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Kitchen - Faulty PowerPoint - See notes below | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-28 15:59 | 2022-07-01 17:00 | 2022-07-01 08:30 | 2022-07-01 17:00 | 2022-07-01 09:00 |  |  | Arrived onsite at 8:30am to investigate GPO loose located kitchen. Found GPO was loose in the kitchen area due to poor fixings. Re-fixed GPO tightly and notified staff. Left site at 9:00
MSA-DFES | WA5572055 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Female Toilets - Newly fitted door has become swollen and wont close | Building | Doors | 90.45 | Pass | Pass | 0 | 0 | 0.5 | 2022-06-29 13:26 | 2022-06-30 17:00 | 2022-06-30 15:15 | 2022-06-30 17:00 | 2022-06-30 15:45 |  |  | Repair Sticking Door
MSA-DFES | WA5578235 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Level - Engine Room - Door 3 SET rear door sensor cable broken | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-01 09:57 | 2022-07-06 17:00 | 2022-07-04 15:00 | 2022-07-06 17:00 | 2022-07-04 15:30 |  |  | Arrived on site at 1500 to investigate Ground Level - Engine Room - Door 3 SET rear door sensor cable broken. Discovered roller door cable pulled/disconnected from terminal enclosure. Reconnected and reenergised panel, confirmed operation and left site at 1530.
MSA-DCA | WA5583071 | 3 | Protek 24/7 Building & Maintenance | Level 3 - HLT Door 5 - Internal door 5 Foyer side sticks on the carpet and doesn’t shut properly | Building | Doors | 128.59 | Fail | Fail | 0 | 0 | 0.5 | 2022-07-04 10:04 | 2022-07-11 17:00 | 2022-07-12 10:00 | 2022-07-11 17:00 | 2022-07-12 10:30 |  |  | Site canceled order on attendance - ref Ryan Riddles
MSA-DCA | WA5583151 | 3 | Techworks Electrical | Level 2 - HLT Male Bathroom - Light under door 4 stairs near HLT male bathroom needs a new globe | Electrical | Lighting, Internal | 135.15 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-04 10:40 | 2022-07-11 17:00 | 2022-07-04 14:30 | 2022-07-11 17:00 | 2022-07-04 15:00 |  |  | With Ken found all lights working well.
MSA-DCA | WA5583164 | 3 | Techworks Electrical | Level 1 - HLT Door 4 - One of the Lights on the Barrel staircase above door 4 needs a new globe | Electrical | Lighting, Internal | 135.15 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-04 10:44 | 2022-07-11 17:00 | 2022-07-04 15:00 | 2022-07-11 17:00 | 2022-07-04 15:30 |  |  | looked at light not working. This would be a huge job for 1x light globe as it would need 15m tall scaffolding to reach as it is above the stair case. I tried to take a photo the best I could to be able to portray it. In my opinion it should wait till there is at least another one gone.
MSA-DTWD | WA5584657 | 2 | Critical Fire Protection & Training | Hallway - fire panel in fault | Fire Protection Services | Fire Protection - Monitor System | 47.07 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-05 09:32 | 2022-07-08 17:00 | 2022-07-07 13:55 | 2022-07-08 17:00 | 2022-07-07 14:25 |  |  | Attended site as a call-out for job raised to investigate fault to E-block fire panel. On arrival found no evidence existing of any faults occurring to system. Checked history log in panel (photographed) no faults recorded since 03/22 panel operating with all systems normal on arrival and departure. Also checked A-block/networked panels and found no history log records indicating faults.
MSA-DFES | WA5585119 | 1 | Securex Security Systems & Services | Entrance Hallway - Alarm Control Panel -Security Alarm reading Low battery- see notes | Security | Security Management System | 210 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-05 12:46 | 2022-07-06 17:00 | 2022-07-05 15:00 | 2022-07-06 17:00 | 2022-07-05 15:30 |  |  | 05/07/2022, 1500-1530Replaced old warped battery in expander.
MSA-DTWD | WA5586648 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire alarm panels need to be checked after an incident accrued - see notes below | Fire Protection Services | Fire Protection - Monitor System | 193.51 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-06 13:30 | 2022-07-06 15:30 | 2022-07-06 14:30 | 2022-07-06 17:30 | 2022-07-06 15:00 |  |  | Completed 06/07/2022
MSA-DTWD | WA5586652 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire alarm panels need to be checked after an incident accrued - see notes below | Fire Protection Services | Fire Protection - Monitor System | 193.51 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-06 13:34 | 2022-07-06 15:34 | 2022-07-06 14:30 | 2022-07-06 17:34 | 2022-07-06 15:00 |  |  | Completed 06/07/2022
MSA-DTWD | WA5586860 | 2 | PEEL LOCK SERVICES PTY LTD | Main workshop outside entry door - Lock box has been damaged needs removal and keys retrieved | Security | Locksmith |  | Pass | Pass | -1 | -1 | 0.5 | 2022-07-06 15:49 | 2022-07-11 17:00 | 2022-07-06 16:00 | 2022-07-11 17:00 | 2022-07-06 16:30 |  |  | Repairs to lock
MSA-DFES | WA5586867 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Front Foyer - Middle bollard located in front foyer of building is jammed - see notes | Building | Columns | 839.56 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-06 16:09 | 2022-07-13 17:00 | 2022-07-08 11:15 | 2022-07-13 17:00 | 2022-07-08 11:45 |  | WACCES | repair faulty Bollard
MSA-DTAG | WA5587871 | 1 | AAA Ability Locksmiths | Custody - Non Contact Interview Room – PIC side - The locking plate is coming loose (needs a screw) | Security | Locksmith | 193.68 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-07 11:22 | 2022-07-08 17:00 | 2022-07-08 07:30 | 2022-07-08 17:00 | 2022-07-08 08:00 |  |  | Attend site, refit strike.
MSA-DTAG | WA5588341 | 2 | Sapio Pty Ltd | Ground - Room one – Security Manager room - Camera 41 is now black and white - See notes below | Security | CCTV Surveillance | 139.88 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-07 14:55 | 2022-07-12 17:00 | 2022-07-08 13:00 | 2022-07-12 17:00 | 2022-07-08 13:30 |  | WACCES | Restored Camera 41 image as threshold on scene was too high and switched into night mode. Threshold lowered to suitable level and reset camera, came back on a d stayed on daylight scene confirming changes made with current light levels picked up by the camera. All okay now.
MSA-DFES | WA5589257 | 3 | Protek 24/7 Building & Maintenance | Admin Building - Ground Floor - Hall way - Kats Office - Broken door handle | Building | Doors | 82.13 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-08 11:20 | 2022-07-15 17:00 | 2022-07-13 11:30 | 2022-07-15 17:00 | 2022-07-13 12:00 |  |  | inspected loose door handle and refitted
MSA-DCA | WA5603292 | 0 | TK Elevator Australia Pty Ltd | Lift 1-No2 button has been pushed all the way though | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0.5 | 2022-07-12 09:31 | 2022-07-12 11:31 | 2022-07-14 15:00 | 2022-07-12 13:31 | 2022-07-14 15:30 |  |  | Lift1 SAC-Gearless :2nd floor button broken on left Car operating panel. Found button broken replaced button and tested all ok. Left in serviceto be closed out at $0 cost
MSA-DTAG | WA5661073 | 1 | Sapio Pty Ltd | Level 9 - The card reader to get into ROOM 908 from the public area isn’t reading. | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-19 15:40 | 2022-07-20 17:00 | 2022-07-20 08:30 | 2022-07-20 17:00 | 2022-07-20 09:00 |  |  | Inspected issue with Card Reader on Level 9 Room 5.08. Reset reader, tested, all OK
MSA-DTAG | WA5672886 | 1 | Midolo Building Services | Magistrates Entry to Courtroom 1 - Non slip lining on the top step is lifting | Building | General Building | 143.99 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-20 10:12 | 2022-07-21 17:00 | 2022-07-20 10:30 | 2022-07-21 17:00 | 2022-07-20 11:00 |  |  | re secured strip to stair
MSA-DFES | WA5674720 | 3 | Complete Pest Management Services | Level 1 - Side Entry Door - ICV Shed - Ants nest inside entry door | Pest Control | General Pest | 157.11 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-21 13:36 | 2022-07-28 17:00 | 2022-07-27 15:45 | 2022-07-28 17:00 | 2022-07-27 16:15 |  |  | Inspected the door for ants no visible sign of ants, sprayed a perimeter for crawling insects
MSA-DTWD | WA5675266 | 2 | AWB Co. | U022.4 - Machine room - roof leak - above the thicknesses machine | Roofing | Metal Roofing | 155.38 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-22 09:13 | 2022-07-27 17:00 | 2022-07-25 13:30 | 2022-07-27 17:00 | 2022-07-25 14:00 |  |  | Attended, sealed rusted holes t sheet ends
MSA-DFES | WA5676608 | 2 | Securex Security Systems & Services | Room 10 - Ground - CCTV camera STILL not working | Security | CCTV Surveillance | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-25 09:34 | 2022-07-28 17:00 | 2022-07-28 12:00 | 2022-07-28 17:00 | 2022-07-28 12:30 |  |  | 28/07/2022, 1200-1230Cameras 7,8,15 faulty but unknown which th why are due to lack of plans. Whole site requires walk test and mappingwith 2 techs. Cameras 4 and 14 in engine bay need a good clean possibly replaced if doesn’t improve view. EWPrequired to reach.***BRAF Declined 12/08/2022, therefore job completed and closed.***
MSA-DCA | WA5677476 | 1 | Critical Fire Protection & Training | L1 fire panel-FIP indicating 2 faults - see notes | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-25 14:42 | 2022-07-26 17:00 | 2022-07-25 15:00 | 2022-07-26 17:00 | 2022-07-25 15:30 |  |  | .
MSA-DTAG | WA5680373 | 3 | Midolo Building Services | door handle loose DOC legal office | Building | Doors | 81.31 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-27 11:49 | 2022-08-03 17:00 | 2022-07-29 14:15 | 2022-08-03 17:00 | 2022-07-29 14:45 |  |  | DOOR HANDLE RESECURED
MSA-DTAG | WA5680390 | 3 | Midolo Building Services | rubber strip (rear stairs level 1) is damaged | Flooring | Rubber | 81.31 | Pass | Pass | -1 | -1 | 0.5 | 2022-07-27 11:58 | 2022-08-03 17:00 | 2022-07-29 13:45 | 2022-08-03 17:00 | 2022-07-29 14:15 |  |  | RUBBER STRIP RESECURED
MSA-DFES | WA5680687 | 1 | TK Elevator Australia Pty Ltd | Lift 1 main lobby, lift jolted and did not open for 30 secs | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 0.5 | 2022-07-27 14:33 | 2022-07-28 17:00 | 2022-07-28 07:45 | 2022-07-28 17:00 | 2022-07-28 08:15 |  |  | 1ELE-Gearless :Lift running on arrival, spoke to security, they said someone reported that the lift had bounced at top floor and it took a long time for the doors to open this onlyhappened once. Checked relevant circuits all okay. No errors on both lifts. Tested lift to all floors couldn't reproducer fault. Left units in service
MSA-DCA | WA5694905 | 0 | GPS Plumbing & Gas Services PtyLtd | water leaking pipe under the sink | Plumbing & Drainage | Water | 128.035 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-05 14:33 | 2022-08-05 16:33 | 2022-08-05 14:50 | 2022-08-05 18:33 | 2022-08-05 15:20 |  |  | No leaks found
MSA-DTWD | WA5696840 | 2 | AWB Co. | west-northern gutter blocked | Roofing | Guttering | 166.69 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-08 15:17 | 2022-08-11 17:00 | 2022-08-11 13:00 | 2022-08-11 17:00 | 2022-08-11 13:30 |  |  | WORK COMPLETED:Leaking coming from upper roof vent, missing flashing fixings allowing water to ingress. Repaired fixings and over sealedon ribs to flashing. If returns further investigation will be needed.
MSA-DFES | WA5699744 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine rooom - Change room 2 drying room - dryer switch is falling into the wall cavity see notes | Electrical | General Electrical | 119.43 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-10 11:48 | 2022-08-15 17:00 | 2022-08-15 12:45 | 2022-08-15 17:00 | 2022-08-15 13:15 |  |  | Arrived on site at 1245 to investigate Engine rooom - Change room 2 drying room - dryer switch is falling into the wall cavity. Located damaged switch, reinstated switch mechanism, reenergised and informed staff of works. Left site at 1315.
MSA-DFES | WA5700081 | 1 | Critical Fire Protection & Training | Fire panel - in fault again | Fire Protection Services | Smoke and Heat Detection | 262.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-10 15:02 | 2022-08-11 17:00 | 2022-08-11 14:40 | 2022-08-11 17:00 | 2022-08-11 15:10 |  |  | Replaced 2x 12ah batteries as they ran dead due to extended power outage.
MSA-DTWD | WA5706943 | 3 | ADVANCED LOCK & KEY | D Block - D117 - Door will not lock | Security | Locksmith | 170 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-11 14:42 | 2022-08-18 17:00 | 2022-08-15 12:20 | 2022-08-18 17:00 | 2022-08-15 12:50 |  |  | cut replacement key for damaged one trying to lock D117, no power to electric mortice so electricians job
MSA-DTWD | WA5715400 | 2 | ADVANCED LOCK & KEY | PIN code to A403 from passage has broken | Security | Access Control | 485 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-12 14:50 | 2022-08-17 17:00 | 2022-08-15 10:05 | 2022-08-17 17:00 | 2022-08-15 10:35 |  |  | replaced broken digital with new one on A403
MSA-DTAG | WA5735019 | 1 | Sapio Pty Ltd | Lower custody - Unable to display all visual sites on security screens within the Ventia Secure area | Security | Access Control | 333.56 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-16 10:59 | 2022-08-17 17:00 | 2022-08-16 16:00 | 2022-08-17 17:00 | 2022-08-16 16:30 |  |  | One of the monitors for the cells cameras was blank, opened up the camera wall for cells custody and put it on the display for the blank monitor.Job completed.
MSA-DTAG | WA5735698 | 1 | Bullant Security Pty Ltd | Exit door that opens to Irwin St, near Magistrates Carpark-loose lock - see notes | Security | Locksmith | 155 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-16 14:29 | 2022-08-17 17:00 | 2022-08-17 13:00 | 2022-08-17 17:00 | 2022-08-17 13:30 |  |  | Attend site to tighten door furniture screws and lubricate lock.Date on site: 17/08/2022Time on site: 13:00 - 13:30
MSA-DTWD | WA5791011 | 1 | Critical Fire Protection & Training | Fire Panel/D109 - Fire Alarm, Detector checked and de isolate | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-22 14:11 | 2022-08-23 17:00 | 2022-08-22 14:30 | 2022-08-23 17:00 | 2022-08-22 15:00 |  |  | Upon arrival, the fire panel had been isolated as there was a fire.The smoke detector was checked and was fine.Deisolated detector and put panel back to normal.
MSA-DCA | WA5792398 | 0 | Protek 24/7 Building & Maintenance | Ground Floor - beaufort Street Building - Epoch Cafe - Bi fold doors are not locking - See notes | Building | Doors | 124.02 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-23 13:49 | 2022-08-23 15:49 | 2022-08-23 15:00 | 2022-08-23 17:49 | 2022-08-23 15:30 |  |  | Issue with door handles advised to use keys instead of finger lock on handle
MSA-DCA | WA5795188 | 1 | Techworks Plumbing | Hackett Hall - Ground Level - Male & Female Toilets - Blocked hand basins - See notes below | Plumbing & Drainage | Drainage | 143.3 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-25 10:00 | 2022-08-26 17:00 | 2022-08-25 15:00 | 2022-08-26 17:00 | 2022-08-25 15:30 |  |  | Removed trap and emptied waste into bin
MSA-DTAG | WA5795281 | 2 | Midolo Building Services | Level 2A - Quasi-Judicial Services - Door is not closing properly - See notes below | Building | Doors | 75.32 | Pass | Pass | -1 | -1 | 0.5 | 2022-08-25 10:48 | 2022-08-30 17:00 | 2022-08-26 07:45 | 2022-08-30 17:00 | 2022-08-26 08:15 |  |  | ASSESSED DOOR - APPEARS TO BE WORKING PROPERLY
MSA-DFES | WA5795408 | 1 | Protek 24/7 Building & Maintenance | Front - Staff Carpark - Staff electric steel gate - keeps breaking down and not opening correctly | Building | Steel Fencing & Gates | 87.43 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-25 12:05 | 2022-08-26 17:00 | 2022-08-26 07:00 | 2022-08-26 17:00 | 2022-08-26 07:30 |  | WACCES | Work order cancelled by client following First attendance From: Imogen Bull <imogen@weareliberty.com.au>Sent: Wednesday, 31 August 2022 3:15 PMTo: Protek247 Jobs & Quotes <jobs@protek247.com.au>Cc: Sunju Ruttun <sunju.ruttun@protek247.com.au>Subject: cancelled workorder WA5795408
MSA-DTAG | WA5797426 | 0 | Sapio Pty Ltd | Level 10 - monitor room - card reader not working | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-29 08:27 | 2022-08-29 10:27 | 2022-08-29 10:00 | 2022-08-29 12:27 | 2022-08-29 10:30 |  |  | Reset door controllerChecked all ok
MSA-DTAG | WA5797431 | 0 | Sapio Pty Ltd | ground floor - staff entry - card reader not working | Security | Access Control | 64.56 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-29 08:31 | 2022-08-29 10:31 | 2022-08-29 10:30 | 2022-08-29 12:31 | 2022-08-29 11:00 |  |  | Checked reader and door controllerFault with raceGun and blow to fix
MSA-DFES | WA5799203 | 3 | Water2water Pty Ltd | Ground-Heritage Shed-Water Cooler is not working, no water coming out. this has been since the last | Plumbing & Drainage | Water | 225.08 | Pass | Pass | 0 | 0 | 0.5 | 2022-08-30 10:17 | 2022-09-06 17:00 | 2022-09-05 07:45 | 2022-09-06 17:00 | 2022-09-05 08:15 |  |  | REPLACED BUBBLER INSERT. ALL OKAY ON DEPARTURE.
MSA-DTAG | WA5800603 | 3 | Midolo Building Services | Conference room table - The Beading needs to be restuck. I have the beading on my desk. | Furniture | Indoor Furniture | 69.65 | Pass | Pass | -1 | -1 | 0.5 | 2022-08-31 11:10 | 2022-09-07 17:00 | 2022-09-01 14:30 | 2022-09-07 17:00 | 2022-09-01 15:00 |  |  | EDGING STRIPS RE STUCK TO TABLE
MSA-DTWD | WA5827346 | 1 | AHS Services WA Pty Ltd (Anchor) | Urinal blocked | Plumbing & Drainage | Toilets/Cisterns | 198.3775 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-01 09:42 | 2022-09-02 17:00 | 2022-09-01 14:30 | 2022-09-02 17:00 | 2022-09-01 15:00 |  |  | Used momar to unblock urinal
MSA-DFES | WA5827930 | 2 | Protek 24/7 Building & Maintenance | First Floor - MOC meeting Room - table is faulty | Furniture | Office Furniture | 83.26 | Fail | Fail | 1 | 1 | 0.5 | 2022-09-01 14:18 | 2022-09-06 17:00 | 2022-09-12 07:00 | 2022-09-06 17:00 | 2022-09-12 07:30 |  |  | repair loose table
MSA-DTAG | WA5836408 | 2 | Midolo Building Services | fire door leading out to steps on Irwin Street is loose | Building | Fire Door | 48.42 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-07 11:55 | 2022-09-12 17:00 | 2022-09-09 08:30 | 2022-09-12 17:00 | 2022-09-09 09:00 |  |  | ON INSPECTION IT WAS FOUND THERE IS AN ELECTRONIC LATCH - NOT FOR MIDOLO
MSA-DFES | WA5837777 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Female Toilet - Cistern is leaking | Plumbing & Drainage | Toilets/Cisterns | 113.505 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-08 08:57 | 2022-09-15 17:00 | 2022-09-13 09:45 | 2022-09-15 17:00 | 2022-09-13 10:15 |  |  | I have repaired the leaking toilet by replacing the old outlet washer with a new outlet washer
MSA-DTAG | WA5838346 | 3 | Midolo Building Services | Front Reception (lvl 7) - Faulty door handle - loose | Building | Doors | 75.32 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-08 12:35 | 2022-09-15 17:00 | 2022-09-09 07:30 | 2022-09-15 17:00 | 2022-09-09 08:00 |  |  | LOOSE SCREWS TIGHTENED
MSA-DTAG | WA5838347 | 3 | Midolo Building Services | Level 3 - Server Room - Ceiling tiles damaged and sagging | Building | Ceiling | 48.42 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-08 12:36 | 2022-09-15 17:00 | 2022-09-09 09:00 | 2022-09-15 17:00 | 2022-09-09 09:30 |  | WACCES | closing ctd - requires a new ceiling but servers are in the way and making dust is an issue so we are unable to make repairs until servers can be relocated. Iain advised to close off - see email attached
MSA-DTAG | WA5854066 | 2 | Sapio Pty Ltd | L6-Room/Office - Business Support / Technology Team business area-new public holiday - see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-12 13:19 | 2022-09-15 17:00 | 2022-09-13 08:30 | 2022-09-15 17:00 | 2022-09-13 09:00 |  |  | Programmed 22nd September 2022 as Public Holiday.
MSA-DTAG | WA5862038 | 1 | Midolo Building Services | L1 DCP office - Metal slide has fallen down from the roof.- see notes | Building | Ceiling | 48.42 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-13 13:24 | 2022-09-14 17:00 | 2022-09-13 14:30 | 2022-09-14 17:00 | 2022-09-13 15:00 |  |  | re inserted air con blocker to ceiling
MSA-DCA | WA5888181 | 1 | Techworks Plumbing | Francis street - Level 2 - Female toilet - Toilet seat and lid missing | Plumbing & Drainage | Toilets/Cisterns | 239.02 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-16 13:53 | 2022-09-19 17:00 | 2022-09-17 13:30 | 2022-09-19 17:00 | 2022-09-17 14:00 |  |  | We attended to the broken toilet seat on level 2 we grabbed a spare toilet seat that they had in storage in the basement and we installed the toilet seat so people would be able to use the toilet again we cleaned up and left site completed paperwork
MSA-DCA | WA5888220 | 1 | Techworks Plumbing | Hackett hall ground-female toilet-flush mech is broken and missing | Plumbing & Drainage | Toilets/Cisterns | 239.02 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-16 14:15 | 2022-09-19 17:00 | 2022-09-16 14:30 | 2022-09-19 17:00 | 2022-09-16 15:00 |  |  | new push button cover plate and went to jacket hall toilets to find where they had a missing push button plate once there we installed it and tested.cleaned up and left site
MSA-DCA | WA5971904 | 0 | TK Elevator Australia Pty Ltd | Ground floor Lift - Not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.5 | 2022-09-20 16:22 | 2022-09-20 18:22 | 2022-09-20 17:15 | 2022-09-20 20:22 | 2022-09-20 17:45 |  |  | Lift1 PICA-Elevator > MRL > Gearless :Found lift stopped at lower floor with doors closed. Pushed the doors by hand, lift started running. Cleaned door lock contacts, sill ,gateswitch at bottom landing. Did couple of runs. Lift running ok, put lift back on service.Declaration/
MSA-DTAG | WA5974210 | 0 | Sapio Pty Ltd | Custody Control Centre - Due to power outage yesterday - Monitors for duress alarm cant be accesed | Security | Monitoring | 139.88 | Fail | Pass | 0 | 0 | 0.5 | 2022-09-23 09:17 | 2022-09-23 11:17 | 2022-09-23 11:30 | 2022-09-23 13:17 | 2022-09-23 12:00 |  |  | Logged into Workstation for Custody. Advised them of what their password is
MSA-DFES | WA5974591 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Mens Toilet - Toilet seat broken in mens toilet block | Plumbing & Drainage | Toilets/Cisterns | 92.92 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-23 13:28 | 2022-09-29 17:00 | 2022-09-28 09:45 | 2022-09-29 17:00 | 2022-09-28 10:15 |  |  | Upon inspection I have found the toilet seat release button was engaged causing the toilet seat to become loose I have reinstalled it correctly everything is now working correctly cleaned up packed up
MSA-DTWD | WA5976709 | 2 | Techworks Electrical | ground-JSC-light not working | Electrical | Lighting, Internal | 276.08 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-27 10:52 | 2022-09-30 17:00 | 2022-09-28 10:00 | 2022-09-30 17:00 | 2022-09-28 10:30 |  |  | Attended site found lights out in kitchen area Replaced tubes all working
MSA-DFES | WA5977147 | 2 | Protek 24/7 Building & Maintenance | ground-ladies toilet-Soap dispenser has fallen off wall in ladies toilet | Building | Internal Walls | 83.26 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-27 13:44 | 2022-09-30 17:00 | 2022-09-28 08:30 | 2022-09-30 17:00 | 2022-09-28 09:00 |  |  | Site had already refixed dispenser
MSA-DTWD | WA5977312 | 1 | AWB Co. | Team room - Power outlet not working | Electrical | General Electrical | 129.86 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-27 15:33 | 2022-09-28 17:00 | 2022-09-28 11:15 | 2022-09-28 17:00 | 2022-09-28 11:45 |  | WCAPPR | works attendedadvised to close off works
MSA-DTWD | WA5977318 | 3 | Water2water Pty Ltd | AF2.14-Fault description Billi unit has filter fault - see notes | Plumbing & Drainage | Water | 126.89 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-27 15:40 | 2022-10-04 17:00 | 2022-09-30 14:15 | 2022-10-04 17:00 | 2022-09-30 14:45 |  |  | REMOVED FILTER & SIMULATED FILTER CHANGE. ALL OKAY ON DEPARTURE
MSA-DTWD | WA5978017 | 3 | Australian Airconditioning Services Pty Ltd | Toilets - Fans not working | Air Conditioning | Materials | 150.64 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-28 08:21 | 2022-10-05 17:00 | 2022-09-28 14:30 | 2022-10-05 17:00 | 2022-09-28 15:00 |  |  | Found schedule timer had fallen out of sync due to power outage. Reprogrammed timer and tested fan. All ok
MSA-DFES | WA5978251 | 2 | ADVANCED LOCK & KEY | Engine Bay - Entrance door located at the rear of the engine bay faulty - See notes | Security | Locksmith | 160 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-28 09:46 | 2022-10-03 17:00 | 2022-09-28 12:00 | 2022-10-03 17:00 | 2022-09-28 12:30 |  |  | Assessed lock & could not fault, lubricated & tested lock multiple times. removed lock off door & assessed .
MSA-DFES | WA5978443 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | main admin-ground-Lecture room 6-Numerous floor and walls power points are not working | Electrical | Lighting, Internal | 80.97 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-28 10:48 | 2022-10-05 17:00 | 2022-09-29 11:30 | 2022-10-05 17:00 | 2022-09-29 12:00 |  |  | complete
MSA-DTAG | WA5979637 | 3 | Sapio Pty Ltd | Level 31: All doors gone into free handle and readers have no lights on - see notes below | Security | Security Management System | 139.88 | Pass | Pass | -1 | -1 | 0.5 | 2022-09-29 09:00 | 2022-10-06 17:00 | 2022-09-29 09:00 | 2022-10-06 17:00 | 2022-09-29 09:30 |  |  | No 240 volts going to panelCircuit breaker switch offReset and checked
MSA-DCA | WA5980215 | 0 | ADVANCED LOCK & KEY | Behind PICA and the Blue Room - Pool fencing - pool fencing lock is broken | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-29 13:32 | 2022-09-29 15:32 | 2022-09-29 14:10 | 2022-09-29 17:32 | 2022-09-29 14:40 |  |  | gate was unlocked but the gate & the pool lock were too close together that when you pull the pool gate lock knob upthe pin still gets caught in the lock strike/catch, so you have to push the post on the hinge side out to create enough of gap for gate to open. Denise advised that she will get installers of gate to fix everything as making keys will not solve the problem.
MSA-DCA | WA5994970 | 1 | Wilson Security | Retrospective breakdown, no need to send contractor - Security Callout – 01/10/2022 15.31 | Security | Monitoring |  | Fail | Fail | 0 | 0 | 0.5 | 2022-10-01 15:31 | 2022-10-03 17:00 | 2022-10-06 10:00 | 2022-10-03 17:00 | 2022-10-06 10:30 | 1 |  | Completed
MSA-DFES | WA5995740 | 2 | Anvil Doors | Rear Yard - Rear gate needs servicing as it not always closing | Building | Steel Fencing & Gates | 377 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-06 15:50 | 2022-10-11 17:00 | 2022-10-10 16:30 | 2022-10-11 17:00 | 2022-10-10 17:00 |  |  | Please see attached service report and signature slip
MSA-DCA | WA5998100 | 1 | Critical Fire Protection & Training | Foyer -Fire curtain closest to side entry door has partially descended - See notes below | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 157.57 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-07 12:00 | 2022-10-10 17:00 | 2022-10-08 06:45 | 2022-10-10 17:00 | 2022-10-08 07:15 |  |  | Returned fire curtain to normal position/recessed in roof surround cafe area.
MSA-DCA | WA5998113 | 1 | Critical Fire Protection & Training | FIP -Speaker/amplifier fault came up last night on the EWIS | Fire Protection Services | Fire Protection - Monitor System | 213.85 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-07 12:05 | 2022-10-10 17:00 | 2022-10-08 08:30 | 2022-10-10 17:00 | 2022-10-08 09:00 |  |  | Attended site as a call-out to investigate fault to EWIS system as reported by site.On arrival the EWIS was showing amplifier - speaker fault.However it was not identifying any zones in fault.After conducting a manual reset on the EWIS, the fault cleared and remained cleared for 10 minute of monitoring period before departure. All systems normal no further action on departure.
MSA-DTWD | WA6000967 | 2 | Swan Pest Control | Mice droppings evident in Beauty storeroom | Pest Control | General Pest | 207.5 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-10 11:30 | 2022-10-13 17:00 | 2022-10-11 08:55 | 2022-10-13 17:00 | 2022-10-11 09:25 |  |  | Installed 5 small lockable rodent stations and 10 Ditrac rodent blocks to toreroom in beauty salon
MSA-DTAG | WA6019879 | 2 | Midolo Building Services | Detention - Interview Room - Damage to the wall in the interview room -Wall has been punched | Building | Internal Walls | 75.32 | Fail | Fail | 0 | 0 | 0.5 | 2022-10-13 08:54 | 2022-10-18 17:00 | 2022-10-19 11:30 | 2022-10-18 17:00 | 2022-10-19 12:00 |  | WACCES | inspect only - work to be completed on priority 0 work order # wa6126887
MSA-DTWD | WA6019938 | 3 | Securex Security Systems & Services | DGP17 - Tamper alarm triggered unable to reset in panel | Security | Security Management System | 160 | Pass | Pass | -1 | -1 | 0.5 | 2022-10-13 09:19 | 2022-10-20 17:00 | 2022-10-14 11:15 | 2022-10-20 17:00 | 2022-10-14 11:45 |  |  | 14/10/2022, 1115-1145Refitted tamper reed switch
MSA-DTWD | WA6022853 | 3 | AWB Co. | light keeps turning off by itself | Electrical | Lighting, Internal | 134.255 | Pass | Pass | -1 | -1 | 0.5 | 2022-10-14 12:26 | 2022-10-21 17:00 | 2022-10-14 14:30 | 2022-10-21 17:00 | 2022-10-14 15:00 |  |  | Attended site signed in jsa completed. Found faulty driver in female staff toilets. Replaced with new one from johns office store. Works fine nowJob completed
MSA-DFES | WA6023080 | 1 | Critical Fire Protection & Training | Fire panel - lost communications | Fire Protection Services | Fire Protection - Monitor System | 135.065 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-14 16:33 | 2022-10-17 17:00 | 2022-10-14 18:00 | 2022-10-17 17:00 | 2022-10-14 18:30 |  |  | Upon arrival code red had a comms fault.After speaking to monitoring service, code red has come back on line, panel system normal, fault cleared.
MSA-DCA | WA6043804 | 3 | Techworks Electrical | Timer fault for exterior lights in urban orchard - Please see notes | Electrical | Lighting, External | 87.285 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-17 09:43 | 2022-10-24 17:00 | 2022-10-24 09:00 | 2022-10-24 17:00 | 2022-10-24 09:30 |  |  | This wasn’t a fault. Times where requested to change. Changed and all working well.
MSA-DTWD | WA6046717 | 2 | AWB Co. | Level 1 - B/block - Light switch faulty in room B010 D.C.S Control Room | Electrical | General Electrical | 114.795 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-17 11:57 | 2022-10-20 17:00 | 2022-10-20 15:00 | 2022-10-20 17:00 | 2022-10-20 15:30 |  |  | Attended site signed in jsa completed. Found class and lights not working due to broken switch. removed old and. Installed new 20a mech. lights now workingJob completed
MSA-DTWD | WA6050988 | 1 | AWB Co. | Metal Fabrication - Down button on electric motor for roller door faulty - See notes below | Equipment | Electrical Equipment | 134.255 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-17 15:47 | 2022-10-18 17:00 | 2022-10-18 12:00 | 2022-10-18 17:00 | 2022-10-18 12:30 |  |  | Attended site signed in jsa completed. Got called to check power to roller door as button was jamming. Power to gpo and power to controller advised site to call roller door contractor. Job completed
MSA-DTWD | WA6088934 | 2 | ADVANCED LOCK & KEY | Both access doors are required to be changed for access - see notes | Security | Locksmith | 320 | Pass | Pass | -1 | -1 | 0.5 | 2022-10-19 11:42 | 2022-10-24 17:00 | 2022-10-20 09:20 | 2022-10-24 17:00 | 2022-10-20 09:50 |  |  | Replaced 2 oval cyls on a block lvl 2 with 2 new 42886 oval cyl on entry doors and 6 42886 keys
MSA-DTWD | WA6111666 | 3 | AWB Co. | Metal Fab- 1st row of lights not working. Another faulty switch.-see notes | Electrical | Lighting, Internal | 178.745 | Pass | Pass | -1 | -1 | 0.5 | 2022-10-21 09:56 | 2022-10-28 17:00 | 2022-10-24 14:30 | 2022-10-28 17:00 | 2022-10-24 15:00 |  | WACCES | Attended site signed in jsa completed. Found 3 faulty light switches in workshop. Replaced with new ones and tested operation.Job completed
MSA-DTWD | WA6112026 | 2 | Equans Mechanical Services Australia | Air-conditioning AHU B2 showing fan fault | Air Conditioning | Room Air Conditioners | 84.465 | Fail | Fail | 1 | 1 | 0.5 | 2022-10-21 12:28 | 2022-10-26 17:00 | 2022-11-01 11:30 | 2022-10-26 17:00 | 2022-11-01 12:00 |  |  | Checked the operation of the AHU, found it working OK, no fault on bms.
MSA-DTWD | WA6112188 | 2 | AWB Co. | No power to 3 Phase power point for Metal Gouger | Electrical | General Electrical | 185.645 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-21 13:41 | 2022-10-26 17:00 | 2022-10-24 13:30 | 2022-10-26 17:00 | 2022-10-24 14:00 |  |  | attended site signed in jsa completed.Found 3 faulty fuses for workshop welder Replaced and tested and operationalJob completed
MSA-DFES | WA6113306 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Front garden - Light which illuminates flagpole does not work. Circuit breaker keeps tripping. | Electrical | Lighting, External |  | Pass | Pass | -1 | -1 | 0.5 | 2022-10-24 10:20 | 2022-10-31 17:00 | 2022-10-25 12:00 | 2022-10-31 17:00 | 2022-10-25 12:30 |  |  | cancelled duplicate of WA6113013
MSA-DTWD | WA6127945 | 1 | AWB Co. | Power circuit tripped | Electrical | General Electrical | 98.545 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-26 11:12 | 2022-10-27 17:00 | 2022-10-26 11:15 | 2022-10-27 17:00 | 2022-10-26 11:45 |  |  | Attended site and signed in. Completed JSA. Located L block and found compressor with no power. Checked for power and found to be off. Located switchboard and found main switch tripped from a E stop being activated. Reset control and retested to be all working. Signed out. Job complete
MSA-DCA | WA6129442 | 2 | Quality Pest & Weed Solutions PTY LTD | Ground Floor - L Block - Remove Beehive activity in L Block | Pest Control | General Pest |  | Pass | Pass | -1 | -1 | 0.5 | 2022-10-27 15:23 | 2022-11-01 17:00 | 2022-10-28 07:45 | 2022-11-01 17:00 | 2022-10-28 08:15 |  |  | Treatment of bee's
MSA-DFES | WA6131595 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | L2 west side - power outlets not working in 2 offices & Victor Zeng | Electrical | General Electrical | 53.49 | Pass | Pass | 0 | 0 | 0.5 | 2022-10-31 08:42 | 2022-11-01 17:00 | 2022-10-31 09:00 | 2022-11-01 17:00 | 2022-10-31 09:30 |  |  | Tyler Beard (31/10/2022) - Work NoteOn site already from another job at 0900, proceed to Level 2 West offices where DB-2.2 Circuit ID R13 was in an isolated state. According to staff, no power was present upon their arrival at site today. I unplugged all appliances from the circuit and reset the RCD. With the RCD reset, I reconnected all appliances and the circuit remained energised. The fault has not reoccurred and is no longer present. Informed relevant staff of works completed. Continued with other works on site at 0930.
MSA-DCA | WA6132546 | 1 | Protek 24/7 Building & Maintenance | Level GF-cloak room-Door furniture handle has come loose -see notes | Building | Doors | 114.51 | Fail | Fail | 0 | 0 | 0.5 | 2022-10-31 15:12 | 2022-11-01 17:00 | 2022-11-03 10:30 | 2022-11-01 17:00 | 2022-11-03 11:00 |  |  | Replaced door handle
MSA-DFES | WA6142549 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | ground-Ensuite bathroom firefighter dorm 1-toilet bowl cracked - see notes | Plumbing & Drainage | Toilets/Cisterns | 145.1475 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-01 07:36 | 2022-11-03 17:00 | 2022-11-03 12:15 | 2022-11-03 17:00 | 2022-11-03 12:45 |  |  | Arrived on site and singed in went to dorm 1 look at toilet bowl A new bowl that was cracked . Job has been already been raised and a new toilet had been ordered.
MSA-DTAG | WA6142832 | 1 | Midolo Building Services | Ground - Murphy JA chambers - Internal door handle has fallen off | Building | Doors | 126.2 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-01 09:14 | 2022-11-02 17:00 | 2022-11-02 11:30 | 2022-11-02 17:00 | 2022-11-02 12:00 |  |  | re secured handle to door
MSA-DCA | WA6149271 | 1 | Automatic Fire Protection (ARA) | Retrospective for call to ARA re fire panel alarm at 1.30am 4.11. -see notes | Fire Protection Services | Fire Protection - Monitor System | 236.355 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-04 01:30 | 2022-11-04 17:00 | 2022-11-04 01:30 | 2022-11-04 17:00 | 2022-11-04 02:00 | 1 |  | Received call from AH asking to phone site directly. Site did not wish for attendance, instead wanting assistance over the phone.Fire alarm was present on FIP and could not be reset. Worked with client to find resolution, resulting in FIP holding out vesda reset. Eventuallyreset detector and isolations were removed.
MSA-DTWD | WA6155941 | 2 | Swan Pest Control | Redbacks under windows and mice droppings and in area - See notes | Pest Control | General Pest | 175 | Fail | Fail | 1 | 1 | 0.5 | 2022-11-08 15:25 | 2022-11-11 17:00 | 2022-11-17 10:25 | 2022-11-11 17:00 | 2022-11-17 10:55 |  |  | Sprayed office for spiders and installed rodent baits
MSA-DFES | WA6158550 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - FF Dorm bathroom #1 (toilet) - Toilet is not flushing correctly and taking ages to refill. | Plumbing & Drainage | Toilets/Cisterns | 119.95 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-10 07:04 | 2022-11-14 17:00 | 2022-11-11 12:15 | 2022-11-14 17:00 | 2022-11-11 12:45 |  |  | Arrived on site and singed in went to drom bathroom 1 and looked at toilet had to replaces a inlet valve and put spring flush button tested everything and working fine.
MSA-DTWD | WA6158841 | 2 | MR POTHOLE | 2 x Pot holes in car park entrance Eddy Baron dve | Paving & Roadworks | Concreting |  | Fail | Fail | 1 | 1 | 0.5 | 2022-11-10 09:32 | 2022-11-15 17:00 | 2022-11-21 12:15 | 2022-11-15 17:00 | 2022-11-21 12:45 |  |  | Repairs to potholes
MSA-DTWD | WA6183989 | 2 | AWB Co. | V Block Staff Office - Faulty Ceiling Lights | Electrical | Lighting, Internal | 145.055 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-15 09:31 | 2022-11-18 17:00 | 2022-11-16 13:30 | 2022-11-18 17:00 | 2022-11-16 14:00 |  |  | Attended site signed in jsa completed. Found two tubes out in staff office. replaced x2 28w tubesChecked operational.Job completed.
MSA-DTAG | WA6184703 | 2 | AHS Services WA Pty Ltd (Anchor) | Basement - Toilet has been reported as being blocked. | Plumbing & Drainage | Toilets/Cisterns | 90.095 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-15 14:37 | 2022-11-18 17:00 | 2022-11-18 12:00 | 2022-11-18 17:00 | 2022-11-18 12:30 |  |  | Toilet wasn’t blocked but flushing mech is faulty so it my of been the day the flushing mech wasn’t working
MSA-DTWD | WA6190869 | 1 | SCAVENGER SUPPLIES PTY LTD | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - See notes | Fire Protection Services | Fire Protection - Monitor System | 236.355 | Pass | Pass | 0 | 0 | 0.5 | 2022-09-03 08:30 | 2022-09-05 17:00 | 2022-09-03 09:00 | 2022-09-05 17:00 | 2022-09-03 09:30 | 1 |  | COMPLETED 03/09/2022-CALL OUT-VIA PHONE
MSA-DTAG | WA6208259 | 2 | Sapio Pty Ltd | Court 3 - Magistrate Buzzer entrance into Court 3 is not working | Security | Access Control | 139.88 | Fail | Fail | 0 | 0 | 0.5 | 2022-11-17 15:13 | 2022-11-22 17:00 | 2022-11-23 09:00 | 2022-11-22 17:00 | 2022-11-23 09:30 |  |  | Checked reported fault. No fault present. Buzzer in Court 3 is working correctly.Job completed.
MSA-DTWD | WA6248913 | 1 | GRAFFITI FORCE PTY LTD | Fire Isolation Valve door (Oxford St.) has graffiti on it, please remove. | Cleaning | Graffiti | 153.28 | Fail | Fail | 1 | 1 | 0.5 | 2022-11-21 08:48 | 2022-11-22 17:00 | 2022-11-29 12:00 | 2022-11-22 17:00 | 2022-11-29 12:30 |  |  | REMOVAL OF GRAFFITI FROM FIRE ISOLATION VALVE DOOR
MSA-DCA | WA6253632 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - SEE NOTES | Security | Guards |  | Pass | Pass | 0 | 0 | 0.5 | 2022-11-13 10:55 | 2022-11-14 17:00 | 2022-11-13 12:00 | 2022-11-14 17:00 | 2022-11-13 12:30 | 1 |  | Completed
MSA-DFES | WA6254055 | 2 | Critical Fire Protection & Training | Intermittent fault on fire monitor | Fire Protection Services | Fire Protection - Monitor System | 50.65 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-22 14:12 | 2022-11-25 17:00 | 2022-11-23 14:15 | 2022-11-25 17:00 | 2022-11-23 14:45 |  |  | Attended site to investigate fault to fire panel. On arrival found fire panel operating with all systems normal and no faults present. Code red display reading system 1 FLT as display of code red is latching. Display of code red returned to normal after reset of ASE box. Contacted FAMs to track record of fault logs as this style of panel has no history log capability. After speaking with FAMS found fault occurred 22/11/22 at 11:26 and returned to normal at 12:02 and has remained fault free since. All systems operating as normal on departure. If fault re-occurs photo required of panel in fault to further identify. NOTE: potential power faults in area coinciding with time of fault or potential water ingress due to incline to weather could have caused fault.
MSA-DFES | WA6254056 | 2 | Critical Fire Protection & Training | Intermittent fault on fire monitor | Fire Protection Services | Fire Protection - Monitor System | 50.65 | Pass | Pass | 0 | 0 | 0.5 | 2022-11-22 14:48 | 2022-11-25 17:00 | 2022-11-25 15:00 | 2022-11-25 17:00 | 2022-11-25 15:30 |  |  | Whilst on site investigated fire panel fault history log as panel is operating all systems normal with no history of faults present on code red display box. After confirming with history log no faults re-occurred since visit on 22/11/22 panel has been operating all systems normal since.
MSA-DFES | WA6258039 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Offices bathroom - Tap is broken, water leaking in all directions from spout when turned on | Plumbing & Drainage | Water | 110.845 | Pass | Pass | -1 | -1 | 0.5 | 2022-11-25 09:47 | 2022-12-02 17:00 | 2022-11-28 08:30 | 2022-12-02 17:00 | 2022-11-28 09:00 |  |  | Attend to site to check out leaking tap. On arrival found aerator spraying water all over basin, removed cleaned and re fitted. All working correctly.
MSA-DFES | WA6291461 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Ground - Halogen lights (boom lift required) - See notes | Electrical | Lighting, Internal | 802.75 | Pass | Pass | -1 | -1 | 0.5 | 2022-11-28 15:43 | 2022-12-05 17:00 | 2022-11-30 07:00 | 2022-12-05 17:00 | 2022-11-30 07:30 |  |  | Tyler Beard (30/11/2022) - Work NoteAttended site at 0700, proceeded to investigate report of faulty lights in engine bay. Found all lights to be working correctly. Informed staff and moved onto next works at same site at 0730.
MSA-DCA | WA6293386 | 0 | TK Elevator Australia Pty Ltd | kitchen lift-not working again 3rd time this has been logged this week | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.5 | 2022-11-30 08:37 | 2022-11-30 10:37 | 2022-11-30 09:00 | 2022-11-30 12:37 | 2022-11-30 09:30 |  |  | Lift 2 Art-Kitchen-Elevator > MR > Geared :Gave access to client into motor room and took photos of main print. Lift left out of service.
MSA-DCA | WA6357156 | 1 | Earth & Water Pty Ltd | Broken Retic - See notes | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 0.5 | 2022-12-05 11:31 | 2022-12-06 17:00 | 2022-12-05 17:15 | 2022-12-06 17:00 | 2022-12-05 17:45 |  |  | Completed
MSA-DTWD | WA6358714 | 1 | Securex Security Systems & Services | Unable to Arm Area 1 Alarm panel showing CIS Panel tamper | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-06 09:35 | 2022-12-07 17:00 | 2022-12-06 14:30 | 2022-12-07 17:00 | 2022-12-06 15:00 |  |  | 06/12/2022, 1430-1500Adjusted tamper switch on electrical switch board. Tamper restored.
MSA-DFES | WA6364695 | 2 | Critical Fire Protection & Training | Fire alarm activating intermittently | Fire Protection Services | Fire Protection - Monitor System | 50.65 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-12 13:48 | 2022-12-15 17:00 | 2022-12-15 13:30 | 2022-12-15 17:00 | 2022-12-15 14:00 |  |  | Attended site to investigate fire panel not in normal operation. On arrival, the fire panel was operating all systems normal with no faults, alarms or isolates present. The code red monitoring box has latched system 1 fault displayed. After contacting monitoring centre found faults occurring intermittently only a few times throughout the day. Unable to determine cause of fault as there was no fault active during our visit and no facility to check history log (Ampac ZoneSense Plus).Prior to leaving, we checked and confirmed all terminals within the fire panel are tight.Further investigating will be required if the fault returns and remains in place.
MSA-DFES | WA6366134 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Dorm 1 - Bathroom - lights not working | Electrical | Lighting, Internal | 80.97 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-13 16:16 | 2022-12-16 17:00 | 2022-12-14 09:15 | 2022-12-16 17:00 | 2022-12-14 09:45 |  |  | Arrived onsite at 09:15 to investigate faulty light fitting in dorm 1 bathroom. Found that the starter was not engaged in the fitting properly. Turned starter so that it could ignite the globe properly and tested that all was working correctly. left site at 09:30.
MSA-DTWD | WA6376485 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire Panel - Fault with Store PIR - see notes below | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-15 16:01 | 2022-12-16 17:00 | 2022-12-16 08:50 | 2022-12-16 17:00 | 2022-12-16 09:20 |  |  | COMPLETED 16/12/22 - Attend site for a fault with store PIR. This call out was intended for the sercurity company and was a miscommunication between the Tafe and programmed.
MSA-DTWD | WA6376911 | 1 | Securex Security Systems & Services | Security Panel - Fault with Store PIR - see notes below | Security | Security Management System | 160 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-16 09:29 | 2022-12-19 17:00 | 2022-12-19 14:15 | 2022-12-19 17:00 | 2022-12-19 14:45 |  |  | 19/12/2022, 1415-1445Replaced reed magnet. Check sealed.
MSA-DFES | WA6377342 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Outside - Area 52 - Water tap that wont turn off. | Plumbing & Drainage | Water | 100.09 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-16 13:12 | 2022-12-19 17:00 | 2022-12-16 13:45 | 2022-12-19 17:00 | 2022-12-16 14:15 |  |  | Arrived on site went to tap that wont turn off located outside area 52, had turn off hot water unit and replaced a tap over a Cleaners sink.
MSA-DTWD | WA6379219 | 0 | Dormakaba Australia Pty Ltd | Entry door - Glass doors opening and closing continuously - see notes | Building | Automatic Doors | 186.95 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-19 10:08 | 2022-12-19 12:08 | 2022-12-19 11:21 | 2022-12-19 14:08 | 2022-12-19 11:51 |  |  | Arrived on site to attend Callout for door IP 1069983. Upon inspection door was being held open due to safety sensor picking up the door when closing. Parameters were adjusted and door was left operational again.
MSA-DTWD | WA6383976 | 2 | Equans Mechanical Services Australia | GYM AHU 9-Wall switch to on /off the AHU has broken and fallen into the switch plate | Air Conditioning | Room Air Conditioners | 106.44 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-20 16:11 | 2022-12-23 17:00 | 2022-12-22 15:00 | 2022-12-23 17:00 | 2022-12-22 15:30 |  |  | PULLED SWITCH APART AND REASEMBLED - OK
MSA-DFES | WA6384323 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Disabled toilet (o/s SO’s Office) - Not light in toilet at all | Electrical | General Electrical | 96.53 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-21 07:54 | 2022-12-23 17:00 | 2022-12-22 07:30 | 2022-12-23 17:00 | 2022-12-22 08:00 |  |  | Arrived onsite at 07:30 to repair/replace light fitting in disabled toilet outside S/O office. Repaired light fitting with new light tube and starter and left site at 08:00.
MSA-DTAG | WA6390650 | 1 | Seme Solutions Pty Ltd | Alter the automatic alarm activation - See Notes Below | Equipment | Security Equipment | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-22 11:12 | 2022-12-23 17:00 | 2022-12-22 16:00 | 2022-12-23 17:00 | 2022-12-22 16:30 |  |  | Attended site, changed auto arm time to 2200 hrs for every day.Synchronised all date and times on pacom hardware.
MSA-DTAG | WA6393873 | 3 | SCAVENGER SUPPLIES PTY LTD | Level 11 - Electrical cupboard near female staff toilet - Fire extinguisher (see notes) | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-29 11:15 | 2023-01-06 17:00 | 2023-01-06 10:30 | 2023-01-06 17:00 | 2023-01-06 11:00
MSA-DTAG | WA6393963 | 3 | SCAVENGER SUPPLIES PTY LTD | Level 12-electric cupboard-Unable to access fire extinguisher (lock mechanism not working) | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2022-12-29 13:33 | 2023-01-06 17:00 | 2023-01-06 10:00 | 2023-01-06 17:00 | 2023-01-06 10:30
MSA-DTAG | WA6400982 | 1 | SONTEC WA PTY LTD | Ground - Magistrate Chamber One – Disable duress alarm (see notes) | Security | Monitoring | 230 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-04 08:22 | 2023-01-05 17:00 | 2023-01-04 09:20 | 2023-01-05 17:00 | 2023-01-04 09:50
MSA-DTWD | WA6402713 | 2 | Securex Security Systems & Services | Throughout C block -The security PIR's throughout C block do not appear to be working | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-05 15:31 | 2023-01-10 17:00 | 2023-01-10 14:15 | 2023-01-10 17:00 | 2023-01-10 14:45
MSA-DTWD | WA6403630 | 1 | Securex Security Systems & Services | S Block - S110 - Facilities/security office - Replace the alarm battery (see notes) | Security | Monitoring | 210 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-06 12:54 | 2023-01-09 17:00 | 2023-01-09 11:15 | 2023-01-09 17:00 | 2023-01-09 11:45
MSA-DCA | WA6405495 | 2 | Techworks Plumbing | Levels 2 & 3 - Various plumbing issues (see notes) | Plumbing & Drainage | Toilets/Cisterns | 422.3 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-09 14:29 | 2023-01-12 17:00 | 2023-01-11 11:30 | 2023-01-12 17:00 | 2023-01-11 12:00
MSA-DFES | WA6405521 | 1 | Water2water Pty Ltd | Kitchen - Zip water unit flashing lights - No got or cold water coming out at all | Plumbing & Drainage | Water | 126.89 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-09 15:00 | 2023-01-10 17:00 | 2023-01-09 15:45 | 2023-01-10 17:00 | 2023-01-09 16:15
MSA-DFES | WA6407448 | 3 | Protek 24/7 Building & Maintenance | Retrospective Work Order - Radio Comms Store Roller door - see notes below | Building | Doors | 83.26 | Pass | Pass | -1 | -1 | 0.5 | 2022-12-20 06:00 | 2022-12-28 17:00 | 2022-12-20 12:00 | 2022-12-28 17:00 | 2022-12-20 12:30 | 1 |  | Tried to adjust the track but no advantage
MSA-DTAG | WA6407479 | 2 | Complete Pest Management Services | 1903 Building -cockroach infestation | Pest Control | General Pest | 269.82 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-10 09:10 | 2023-01-13 17:00 | 2023-01-10 13:00 | 2023-01-13 17:00 | 2023-01-10 13:30
MSA-DFES | WA6425741 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 2 - Payroll office - Light bulb out above desk | Electrical | Lighting, Internal | 133.75 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-12 11:25 | 2023-01-17 17:00 | 2023-01-16 09:45 | 2023-01-17 17:00 | 2023-01-16 10:15
MSA-DTWD | WA6430957 | 3 | Critical Fire Protection & Training | West Exit doors x 2- Fire door signs unreadable | Signage | General Signage | 140.65 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-13 10:35 | 2023-01-20 17:00 | 2023-01-17 10:00 | 2023-01-20 17:00 | 2023-01-17 10:30
MSA-DCA | WA6431505 | 0 | Automatic Fire Protection (ARA) | Ground floor - Fire panel - Constant Alarm fault | Fire Protection Services | Smoke and Heat Detection | 844.13 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-13 16:40 | 2023-01-13 18:40 | 2023-01-13 18:00 | 2023-01-13 20:40 | 2023-01-13 18:30
MSA-DCA | WA6450892 | 2 | Techworks Electrical | On Stage Lighting - Men’s Toilets - Globe holder above desk keeps tripping (see notes) | Electrical | Lighting, Internal | 87.285 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-16 16:08 | 2023-01-19 17:00 | 2023-01-18 10:30 | 2023-01-19 17:00 | 2023-01-18 11:00
MSA-DCA | WA6450903 | 1 | Protek 24/7 Building & Maintenance | Ground - Old Gaol - Door has come loose off hinges and will not align to close properly (see notes) | Building | Doors | 102.01 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-16 16:43 | 2023-01-17 17:00 | 2023-01-17 13:00 | 2023-01-17 17:00 | 2023-01-17 13:30
MSA-DTAG | WA6466286 | 1 | Sapio Pty Ltd | Ground floor - Courtoom 3 - Wide angle camera is not working | Security | Monitoring | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-17 13:08 | 2023-01-18 17:00 | 2023-01-18 08:30 | 2023-01-18 17:00 | 2023-01-18 09:00
MSA-DTAG | WA6466448 | 1 | Sapio Pty Ltd | Ground floor - Courtoom 3 - Second Monitor keeps dropping out/ connectivity (see notes) | Security | Monitoring | 64.56 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-17 13:23 | 2023-01-18 17:00 | 2023-01-18 09:00 | 2023-01-18 17:00 | 2023-01-18 09:30
MSA-DTAG | WA6503723 | 3 | Sapio Pty Ltd | L23- Irwin room not secure - cannot lock door | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-19 11:03 | 2023-01-27 17:00 | 2023-01-24 08:30 | 2023-01-27 17:00 | 2023-01-24 09:00
MSA-DFES | WA6504271 | 2 | Complete Pest Management Services | Level 1- Base Manager’s office and Sim Room - Smell coming from ceiling in hallway | Pest Control | General Pest | 142.56 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-19 14:14 | 2023-01-24 17:00 | 2023-01-23 15:00 | 2023-01-24 17:00 | 2023-01-23 15:30
MSA-DTAG | WA6504412 | 3 | EASTERN HILLS ELECTRICAL SERVICE | Level 1 - Court 2 - Flickering Light - See Notes | Electrical | Lighting, Internal | 167.03 | Fail | Fail | 2 | 2 | 0.5 | 2023-01-19 15:47 | 2023-01-27 17:00 | 2023-02-11 07:00 | 2023-01-27 17:00 | 2023-02-11 07:30
MSA-DTWD | WA6509634 | 3 | AWB Co. | Broken Power point | Electrical | General Electrical | 142.36 | Pass | Pass | -1 | -1 | 0.5 | 2023-01-20 13:05 | 2023-01-30 17:00 | 2023-01-20 16:00 | 2023-01-30 17:00 | 2023-01-20 16:30
MSA-DTAG | WA6517913 | 1 | Sapio Pty Ltd | Ground - Court room 3 - faulty buzzer- see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-24 14:14 | 2023-01-25 17:00 | 2023-01-25 11:30 | 2023-01-25 17:00 | 2023-01-25 12:00
MSA-DCA | WA6518539 | 1 | ADVANCED LOCK & KEY | Lock / Latch stuck leaving emergency stair case unsecure | Security | Locksmith | 369.99 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-25 09:13 | 2023-01-27 17:00 | 2023-01-25 11:30 | 2023-01-27 17:00 | 2023-01-25 12:00
MSA-DFES | WA6519207 | 2 | Dom's Total Grounds Maintenance | Access and remove any branches that are deemed unsafe | Landscaping & Gardening | Grounds Maintenance | 135 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-25 13:57 | 2023-01-31 17:00 | 2023-01-31 06:00 | 2023-01-31 17:00 | 2023-01-31 06:30
MSA-DFES | WA6519911 | 2 | Complete Pest Management Services | Office - Ant infestation | Pest Control | General Pest | 176.61 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-27 08:31 | 2023-02-01 17:00 | 2023-01-30 14:30 | 2023-02-01 17:00 | 2023-01-30 15:00
MSA-DFES | WA6520667 | 0 | Critical Fire Protection & Training | VESDA PANELS IN IT DATA CENTRE AND COMCEM CENTRE IN FAULTS=. | Fire Protection Services | Fire Protection - Monitor System | 236.355 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-28 15:30 | 2023-01-28 17:30 | 2023-01-28 17:15 | 2023-01-28 19:30 | 2023-01-28 17:45
MSA-DTWD | WA6521575 | 2 | PEEL LOCK SERVICES PTY LTD | Change door Bi lock to new key system with 3 new keys | Security | Keys & Access |  | Pass | Pass | 0 | 0 | 0.5 | 2023-01-30 11:47 | 2023-01-31 17:00 | 2023-01-31 11:30 | 2023-01-31 17:00 | 2023-01-31 12:00
MSA-DFES | WA6522055 | 1 | Critical Fire Protection & Training | Zone 7 detector fault - fire panel fault | Fire Protection Services | Fire Protection - Monitor System | 315.065 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-30 18:14 | 2023-01-31 17:00 | 2023-01-30 19:30 | 2023-01-31 17:00 | 2023-01-30 20:00
MSA-MRWA | WA6523402 | 2 | ADVANCED LOCK & KEY | Door handle is catching and likley to fail | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.5 | 2023-01-31 15:35 | 2023-02-03 17:00 | 2023-02-03 09:45 | 2023-02-03 17:00 | 2023-02-03 10:15
MSA-DTAG | WA6527033 | 1 | AWB Co. | Court 1 - Light above JSO desk is flickering | Electrical | Lighting, Internal | 102.885 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-01 13:02 | 2023-02-02 17:00 | 2023-02-01 15:45 | 2023-02-02 17:00 | 2023-02-01 16:15
MSA-DTAG | WA6527328 | 1 | Midolo Building Services | Level 5 - Court 55 - Door squeaks very loudly and bangs shut impeding on court function | Building | Doors | 95.12 | Fail | Fail | 0 | 0 | 0.5 | 2023-02-01 16:09 | 2023-02-02 17:00 | 2023-02-03 07:00 | 2023-02-02 17:00 | 2023-02-03 07:30
MSA-DCA | WA6528151 | 1 | TK Elevator Australia Pty Ltd | Lift 4 - doors making a noise that sounds like scraping metal | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.5 | 2023-02-02 08:59 | 2023-02-03 17:00 | 2023-02-02 16:00 | 2023-02-03 17:00 | 2023-02-02 16:30
MSA-DTAG | WA6528568 | 1 | AAA Ability Locksmiths | Custody lower - Cell 4 and surround - Cell 3 hatch not locking | Security | Keys & Access | 478.64 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-02 10:51 | 2023-02-03 17:00 | 2023-02-02 15:00 | 2023-02-03 17:00 | 2023-02-02 15:30
MSA-DFES | WA6534240 | 3 | Securex Security Systems & Services | Main Administration - Lecture Room 5 - Smoke detector cheeping | Fire Protection Services | Smoke and Heat Detection | 168.18 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-06 10:42 | 2023-02-13 17:00 | 2023-02-06 13:00 | 2023-02-13 17:00 | 2023-02-06 13:30
MSA-DFES | WA6537747 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Bay- Change room 2 - Button to activate the Drying Room is broken | Electrical | General Electrical | 80.97 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-07 10:55 | 2023-02-14 17:00 | 2023-02-10 11:15 | 2023-02-14 17:00 | 2023-02-10 11:45
MSA-DTWD | WA6537819 | 1 | COMMERCIAL PLUMBING AND GAS | Female staff toilet next to Lecture Theatre 229 - Pan does not flush | Plumbing & Drainage | Toilets/Cisterns | 78.835 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-07 11:58 | 2023-02-08 17:00 | 2023-02-08 14:30 | 2023-02-08 17:00 | 2023-02-08 15:00
MSA-DTAG | WA6539377 | 3 | Midolo Building Services | Basement - Glass sliding doors - Loud squeaking when opening and closing | Building | Doors | 95.12 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-08 12:16 | 2023-02-15 17:00 | 2023-02-13 07:30 | 2023-02-15 17:00 | 2023-02-13 08:00
MSA-DCA | WA6539732 | 1 | Protek 24/7 Building & Maintenance | Substage - Door on MPR side has lost pin from top door closure (see notes) | Building | Doors | 83.26 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-08 16:45 | 2023-02-09 17:00 | 2023-02-09 11:30 | 2023-02-09 17:00 | 2023-02-09 12:00
MSA-DTWD | WA6573162 | 3 | PEEL LOCK SERVICES PTY LTD | Ground - room B31 - Lock is faulty to electrical store | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.5 | 2023-02-14 11:16 | 2023-02-21 17:00 | 2023-02-20 11:30 | 2023-02-21 17:00 | 2023-02-20 12:00
MSA-MRWA | WA6578483 | 1 | Water2water Pty Ltd | Kitchenette - LHS Sink - Low pressure on cold Billi unit tap | Plumbing & Drainage | HWS/Units Electric & Gas | 225.9 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-15 09:59 | 2023-02-16 17:00 | 2023-02-15 13:05 | 2023-02-16 17:00 | 2023-02-15 13:35
MSA-DFES | WA6586219 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Lecture room 2B blinking light | Electrical | Lighting, Internal | 154.35 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-16 14:43 | 2023-02-23 17:00 | 2023-02-21 11:15 | 2023-02-23 17:00 | 2023-02-21 11:45
MSA-DTWD | WA6604026 | 1 | PEEL LOCK SERVICES PTY LTD | Bi lock not working / change to new ( B13 key system) with 10 keys | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.5 | 2023-02-17 14:49 | 2023-02-20 17:00 | 2023-02-20 12:45 | 2023-02-20 17:00 | 2023-02-20 13:15
MSA-DFES | WA6667719 | 1 | TK Elevator Australia Pty Ltd | Staff dropped keys down lift shaft - See notes | Lifts | Lifts | 381.82 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-21 14:06 | 2023-02-22 17:00 | 2023-02-22 06:45 | 2023-02-22 17:00 | 2023-02-22 07:15
MSA-DTWD | WA6668830 | 2 | Swan Pest Control | ant problem, please treat inside and outside area. | Pest Control | General Pest | 250 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-22 11:54 | 2023-02-27 17:00 | 2023-02-27 13:30 | 2023-02-27 17:00 | 2023-02-27 14:00
MSA-DFES | WA6672340 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Bathroom - Electrical switches faulty | Electrical | General Electrical | 184.46 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-23 15:21 | 2023-02-23 17:21 | 2023-02-23 16:30 | 2023-02-23 19:21 | 2023-02-23 17:00
MSA-DFES | WA6674288 | 1 | SONTEC WA PTY LTD | D O S S to Communcation Centre - No swipe access | Security | Keys & Access | 230 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-27 09:17 | 2023-02-28 17:00 | 2023-02-27 10:10 | 2023-02-28 17:00 | 2023-02-27 10:40
MSA-DFES | WA6674804 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Front yard- Pressure relief valve - Leaking | Plumbing & Drainage | Water | 118.26 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-27 11:47 | 2023-03-02 17:00 | 2023-02-28 07:00 | 2023-03-02 17:00 | 2023-02-28 07:30
MSA-DFES | WA6674823 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Light in WC for dorm 8 not working | Electrical | Lighting, Internal | 137.69 | Pass | Pass | 0 | 0 | 0.5 | 2023-02-27 12:20 | 2023-03-02 17:00 | 2023-03-02 07:00 | 2023-03-02 17:00 | 2023-03-02 07:30
MSA-DTAG | WA6675437 | 3 | Seme Solutions Pty Ltd | Unable to assign pin codes to users | Security | CCTV Surveillance | 139.88 | Pass | Pass | -1 | -1 | 0.5 | 2023-02-28 07:06 | 2023-03-07 17:00 | 2023-03-01 09:00 | 2023-03-07 17:00 | 2023-03-01 09:30
MSA-DFES | WA6680014 | 1 | Complete Pest Management Services | ground interligence services-ants nest under desk | Pest Control | General Pest | 171.36 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-01 07:57 | 2023-03-01 17:00 | 2023-03-01 10:30 | 2023-03-01 17:00 | 2023-03-01 11:00
MSA-DTAG | WA6680081 | 1 | Midolo Building Services | Rear Door to Main Hallway-Crack in the stairwell concrete which runs all the way underneath-notes | Carpentry | Staircases, Balustrades and Handrails | 75.32 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-01 08:26 | 2023-03-02 17:00 | 2023-03-01 11:30 | 2023-03-02 17:00 | 2023-03-01 12:00
MSA-DTAG | WA6682035 | 2 | AHS Services WA Pty Ltd (Anchor) | L3-North East Corner (Irwin Street side) single staff toilet-keeps running | Plumbing & Drainage | Toilets/Cisterns | 90.095 | Fail | Fail | 0 | 0 | 0.5 | 2023-03-02 14:21 | 2023-03-08 17:00 | 2023-03-09 12:00 | 2023-03-08 17:00 | 2023-03-09 12:30
MSA-DFES | WA6682153 | 0 | Securex Security Systems & Services | Front security gate wont close. | Security | Monitoring | 350 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-02 23:47 | 2023-03-03 01:47 | 2023-03-03 | 2023-03-03 03:47 | 2023-03-03 00:30
MSA-DTWD | WA6683647 | 2 | Australian Airconditioning Services Pty Ltd | Unit not cooling sufficiently | Air Conditioning | Ducted Split System | 320.11 | Pass | Pass | -1 | -1 | 0.5 | 2023-03-03 10:44 | 2023-03-09 17:00 | 2023-03-03 10:45 | 2023-03-09 17:00 | 2023-03-03 11:15
MSA-DTAG | WA6688365 | 0 | GPS Plumbing & Gas Services PtyLtd | Custody - Cell 1 - Piping ripped out - Require plumbing to be isolated | Plumbing & Drainage | Drainage | 394.54 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-07 13:57 | 2023-03-07 15:57 | 2023-03-07 14:30 | 2023-03-07 17:57 | 2023-03-07 15:00
MSA-DFES | WA6693464 | 1 | Complete Pest Management Services | Director TDSC Office & Lecture room 3 - Dead animal smell | Pest Control | General Pest | 191.16 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-10 10:30 | 2023-03-13 17:00 | 2023-03-10 12:45 | 2023-03-13 17:00 | 2023-03-10 13:15
MSA-DTWD | WA6707854 | 1 | SCAVENGER SUPPLIES PTY LTD | DG01 - Campus lost power over weekend. Alarm panel beeping this morning – Plant Isolate and Bell | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-13 09:15 | 2023-03-14 17:00 | 2023-03-13 10:30 | 2023-03-14 17:00 | 2023-03-13 11:00
MSA-DTWD | WA6721679 | 1 | ADVANCED LOCK & KEY | Ground Floor - Riser door under the stairs - lock loose - wont open | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.5 | 2023-03-14 10:48 | 2023-03-15 17:00 | 2023-03-15 10:25 | 2023-03-15 17:00 | 2023-03-15 10:55
MSA-DTAG | WA6721920 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Ladies toilet - Cubicle 2 toilet button pushed in | Plumbing & Drainage | Toilets/Cisterns | 172.4575 | Pass | Pass | 0 | 0 | 0.5 | 2023-03-14 13:04 | 2023-03-17 17:00 | 2023-03-15 10:30 | 2023-03-17 17:00 | 2023-03-15 11:00
MSA-DTWD | WA6727195 | 1 | Water2water Pty Ltd | Block B - Reception - Unit leaking/ not working | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 0.5 | 2023-03-15 11:06 | 2023-03-16 17:00 | 2023-03-15 14:40 | 2023-03-16 17:00 | 2023-03-15 15:10
MSA-DTWD | WA5190458 | 1 | SCAVENGER SUPPLIES PTY LTD | U Block - Ground - U6 - Fire/smoke alarm beeping | Fire Protection Services | Smoke and Heat Detection | 106.87 | Pass | Pass | 0 | 0 | 0.48333 | 2022-02-24 12:53 | 2022-02-25 17:00 | 2022-02-24 15:31 | 2022-02-25 17:00 | 2022-02-24 16:00 |  |  | COMPLETED 24/02/2022Smoke alarm had flat battery, replaced with new 9volt battery
MSA-DTWD | WA5308026 | 1 | AHS Services WA Pty Ltd (Anchor) | E-Block - Restaurant- Dish wash area the hot water has no pressure | Plumbing & Drainage | Water | 177.92 | Pass | Pass | 0 | 0 | 0.48333 | 2022-04-08 08:32 | 2022-04-11 17:00 | 2022-04-08 12:31 | 2022-04-11 17:00 | 2022-04-08 13:00 |  |  | Mini stop tap was turned down
MSA-DTAG | WA5482604 | 1 | Dormakaba Australia Pty Ltd | RETROSPCTIVE WORK ORDER - Court Room 1- Door - not closing properly - push button door | Building | Doors | 235 | Pass | Pass | 0 | 0 | 0.48333 | 2022-05-31 10:30 | 2022-06-01 17:00 | 2022-05-31 10:39 | 2022-06-01 17:00 | 2022-05-31 11:08 |  |  | Manual swing door that the arm is hitting the frame and not closing, it seems that the arm has moved around on the top of the door, there is no access to adjust, site will need to remove bulkhead before any works can proceed, see photos.
MSA-DTWD | WA5534634 | 2 | Falcetta Plumbing and Gas | A Block (1st Floor) - Low water flow - See notes below | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 0.48333 | 2022-06-16 12:33 | 2022-06-21 17:00 | 2022-06-21 16:30 | 2022-06-21 17:00 | 2022-06-21 16:59 |  |  | adjusted flush volume and cistern volume
MSA-DTAG | WA5628713 | 1 | OCS SERVICES PTY LTD | Ground floor- registryDesk in Registry-covid clean sign on desk - Covid Clean | Cleaning | Emergency Cleans |  | Fail | Fail | 0 | 0 | 0.48333 | 2022-07-15 15:54 | 2022-07-18 17:00 | 2022-07-18 17:01 | 2022-07-18 17:00 | 2022-07-18 17:30 |  |  | Covid clean complete
MSA-DTAG | WA5675538 | 2 | Dormakaba Australia Pty Ltd | Level 2 - Basement Car Park Internal door - Door is not auto closing | Building | Automatic Doors | 235 | Pass | Pass | -1 | -1 | 0.48333 | 2022-07-22 11:23 | 2022-07-27 17:00 | 2022-07-22 13:09 | 2022-07-27 17:00 | 2022-07-22 13:38 |  |  | On inspection found door lock was not latching, increased latching action, tested door operation a number of times, left door in good working condition.
MSA-DTWD | WA5978313 | 3 | COMMERCIAL PLUMBING AND GAS | Toilet not flushing properly - flows after flushing | Plumbing & Drainage | Toilets/Cisterns | 177.835 | Pass | Pass | 0 | 0 | 0.48333 | 2022-09-28 10:07 | 2022-10-05 17:00 | 2022-10-05 16:30 | 2022-10-05 17:00 | 2022-10-05 16:59 |  |  | repaired water wafer cistern
MSA-DTWD | WA6676307 | 2 | ECO PLUMBING AND GAS PTY LTD | South west corner under bridge saw - Blocked drain in L Block Stone Masonry (see notes) | Plumbing & Drainage | Drainage | 531.89 | Fail | Fail | 1 | 1 | 0.48333 | 2023-02-28 13:26 | 2023-03-03 17:00 | 2023-03-09 10:58 | 2023-03-03 17:00 | 2023-03-09 11:27
MSA-DCA | WA4991718 | 2 | GPS Plumbing & Gas Services PtyLtd | Male sick bay - The silver urinal is blocked | Plumbing & Drainage | Drainage | 159.595 | Pass | Pass | -1 | -1 | 0.48333 | 2022-01-05 11:21 | 2022-01-10 17:00 | 2022-01-05 12:51 | 2022-01-10 17:00 | 2022-01-05 13:20 |  |  | Unblock the urinal in male sick bay ground floor
MSA-DCA | WA4991990 | 2 | TK Elevator Australia Pty Ltd | Stalls Foyer - FOH lift -FOH lift doors screeching loudly when opening | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.46667 | 2022-01-05 16:06 | 2022-01-10 17:00 | 2022-01-06 10:10 | 2022-01-10 17:00 | 2022-01-06 10:38 |  |  | Lift as reported, found door shoes on car doors slightly out of alignment. Repaired shoes and cleaned out sills, could not fault, returned to service
MSA-DFES | WA6520599 | 2 | Critical Fire Protection & Training | Main Building-Ground Floor-Entrance - Fault on fire panel | Fire Protection Services | Fire Protection - Monitor System | 206.65 | Pass | Pass | 0 | 0 | 0.46667 | 2023-01-28 07:31 | 2023-02-01 17:00 | 2023-01-31 09:30 | 2023-02-01 17:00 | 2023-01-31 09:58
MSA-MRWA | WA6690688 | 3 | Dormakaba Australia Pty Ltd | Ground floor - Tuart room - Non functioning automatic door | Building | Automatic Doors | 395 | Pass | Pass | -1 | -1 | 0.46667 | 2023-03-09 11:44 | 2023-03-16 17:00 | 2023-03-09 13:28 | 2023-03-16 17:00 | 2023-03-09 13:56
MSA-DCA | WA5597069 | 2 | Techworks Electrical | Basement Level - Communications 01 (Server Room) - see details below | Equipment | Electrical Equipment | 230.88 | Pass | Pass | 0 | 0 | 0.46667 | 2022-07-11 12:10 | 2022-07-14 17:00 | 2022-07-11 14:46 | 2022-07-14 17:00 | 2022-07-11 15:14 |  |  | Work order was a retrospectively raised.Arrived on site, met up and spoke with Neil about fault, began investigation within server room. After looking through all switchboards and finding nothing wrong and nothing buzzing, I called Neil back up to have a look at the BMS computer to help narrow down fault. After looking on BMS fault appears to be with a server/server equipment and not even in the museum but somewhere within the PCC judging by the details given on the BMS. Different contractors will need to be engaged to identify fault with server.
MSA-DTWD | WA5390931 | 3 | Dormakaba Australia Pty Ltd | N231 - Disabled auto toilet door - faulty | Building | General Building | 180 | Pass | Pass | -1 | -1 | 0.46667 | 2022-05-02 15:17 | 2022-05-09 17:00 | 2022-05-03 10:56 | 2022-05-09 17:00 | 2022-05-03 11:24 |  |  | Inspected door and found emergency door release button was pressed, reset button, checked all fixings, checked all activation devices, checked operator and drive arm, tested door operation a number of times, all working fine.
MSA-MRWA | WA5396214 | 1 | Dormakaba Australia Pty Ltd | Ground Floor - Entrance Doors - Entrance sliding doors noisy on closing | Building | General Building | 180 | Pass | Pass | 0 | 0 | 0.46667 | 2022-05-06 09:09 | 2022-05-09 17:00 | 2022-05-06 10:20 | 2022-05-09 17:00 | 2022-05-06 10:48 |  |  | Found that the unit is running very rough, the track wheels are heavily worn, the motor gearbox is heavily worn, all of the control gear is showing signs of corrosion and the unit is 21 years old. I recommend that the unit has a full upgrade for reliable operation. Quotation required to replace the unit with an el301 locking unit, 4x heavy duty track wheels, pib kit and ixio. 2x technicians out of business hours required for safe working practices.
MSA-DTWD | WA5399148 | 1 | Water2water Pty Ltd | Kitchen Sink Tap - Water dispensing slowly out of filtered tap | Plumbing & Drainage | Water | 117.925 | Pass | Pass | 0 | 0 | 0.46667 | 2022-05-09 15:49 | 2022-05-10 17:00 | 2022-05-10 13:59 | 2022-05-10 17:00 | 2022-05-10 14:27 |  |  | Cold flow restricted. Removed restrict and now a bit better.
MSA-DTWD | WA5656537 | 2 | Water2water Pty Ltd | First Level - Staff Room - Boiling Billy tap has broken lever to release hot water has broken off | Plumbing & Drainage | Water | 298.545 | Pass | Pass | 0 | 0 | 0.46667 | 2022-07-18 14:37 | 2022-07-21 17:00 | 2022-07-20 11:42 | 2022-07-21 17:00 | 2022-07-20 12:10 |  |  | TECH REPLACED BROKEN TAP, ALL OKAY ON DEPARTURE
MSA-DTWD | WA5699286 | 2 | AWB Co. | Faulty GPO in staff kitchen | Electrical | General Electrical | 194.275 | Pass | Pass | -1 | -1 | 0.46667 | 2022-08-10 08:31 | 2022-08-15 17:00 | 2022-08-10 08:32 | 2022-08-15 17:00 | 2022-08-10 09:00 |  |  | Attended site signed in jsa completedspoke to site about job needed to be done. re screwed lighting diffuser in A block as site requested in high ceiling. Test and tagged air fryer in A block kitchen. Job completed
MSA-DTWD | WA6401104 | 1 | Australian Airconditioning Services Pty Ltd | Toilets - Exhaust fan not working in toilet block (see notes) | Air Conditioning | Room Air Conditioners | 333.56 | Pass | Pass | 0 | 0 | 0.46667 | 2023-01-04 09:02 | 2023-01-05 17:00 | 2023-01-04 09:02 | 2023-01-05 17:00 | 2023-01-04 09:30
MSA-DTAG | WA6560276 | 1 | Dormakaba Australia Pty Ltd | Ground-secure carpark-Electronic gate stuck open | Security | Access Control | 414 | Pass | Pass | 0 | 0 | 0.46667 | 2023-02-13 08:52 | 2023-02-14 17:00 | 2023-02-13 12:54 | 2023-02-14 17:00 | 2023-02-13 13:22
MSA-DTAG | WA4986078 | 1 | Sapio Pty Ltd | Outside door in secure carpark - Magistrates door entrance - Keypad cant activated for swipe card | Security | Keys & Access | 130 | Pass | Pass | -1 | -1 | 0.45 | 2021-12-31 09:02 | 2022-01-04 17:00 | 2021-12-31 10:30 | 2022-01-04 17:00 | 2021-12-31 10:57
MSA-DTAG | WA5163572 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground floor - Covid clean required (positive test) please contact Cherise 08 94215363 | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 1 | 0.45 | 2022-02-18 09:35 | 2022-02-18 11:35 | 2022-02-23 14:07 | 2022-02-18 13:35 | 2022-02-23 14:34 |  |  | WA5163572
MSA-DTWD | WA5481246 | 2 | Dormakaba Australia Pty Ltd | South Block - Level 1 - S 101 - Auto door not locking - REACH clinic auto door | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.45 | 2022-05-30 11:42 | 2022-06-02 17:00 | 2022-05-31 11:28 | 2022-06-02 17:00 | 2022-05-31 11:55 |  |  | Manual swing door, patch fitting has come loose and the door was not aligned when trying to lock, tightened patch fitting and tested, all ok.
MSA-MRWA | WA5518855 | 2 | Water2water Pty Ltd | Kitchen - The hot water urn is leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 279.9 | Pass | Pass | 0 | 0 | 0.45 | 2022-06-15 08:41 | 2022-06-20 17:00 | 2022-06-17 10:35 | 2022-06-20 17:00 | 2022-06-17 11:02 |  |  | replaced tap
MSA-DCA | WA5797165 | 0 | TK Elevator Australia Pty Ltd | PICA main lift is not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.45 | 2022-08-28 14:25 | 2022-08-28 16:25 | 2022-08-28 15:26 | 2022-08-28 18:25 | 2022-08-28 15:53 |  |  | Upob arrival it appears the the lift had lost its safety circuit in the lift car i reset and checked the switches and all appears to be runningcorrectly. I tested the lift and it was running correctly on departure
MSA-DCA | WA6132229 | 3 | ADVANCED LOCK & KEY | Door Lock on VMO is very stiff to open, needs replacing. -see notes | Security | Locksmith | 390.92 | Pass | Pass | -1 | -1 | 0.45 | 2022-10-31 12:34 | 2022-11-07 17:00 | 2022-11-03 12:03 | 2022-11-07 17:00 | 2022-11-03 12:30 |  |  | Attend site to replace damaged handles on VMO door 1x LW1360/1361/70SC
MSA-DCA | WA6366115 | 3 | TK Elevator Australia Pty Ltd | All - Elevator - verbal announcement as to which floor isnt working - see notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.45 | 2022-12-13 15:30 | 2022-12-20 17:00 | 2022-12-20 08:13 | 2022-12-20 17:00 | 2022-12-20 08:40 |  |  | On arrival found lift as reported, checked connections in speech pcb, recycled power to speech pcb, lift annunciation started working as normal, left the lift working.
MSA-DTWD | WA6578406 | 1 | Precise Air Group | A block North - Server Room 201 - Server air con (split system) not working | Air Conditioning | Ducted Split System | 656.755 | Fail | Fail | 3 | 3 | 0.45 | 2023-02-15 09:22 | 2023-02-16 17:00 | 2023-03-07 08:02 | 2023-02-16 17:00 | 2023-03-07 08:29
MSA-MRWA | WA5087983 | 2 | GPS Plumbing & Gas Services PtyLtd | failed back flow valve in the basement | Plumbing & Drainage | Materials | 87.27 | Pass | Pass | 0 | 0 | 0.45 | 2022-01-24 16:19 | 2022-01-28 17:00 | 2022-01-25 12:21 | 2022-01-28 17:00 | 2022-01-25 12:48 |  |  | nvestigate leaking RPZD.Valve to be replaced on a different work order.
MSA-DCA | WA5116007 | 1 | Dormakaba Australia Pty Ltd | Jubilee - Reflections Gallery - Main door will not close | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.45 | 2022-02-11 10:26 | 2022-02-14 17:00 | 2022-02-11 13:23 | 2022-02-14 17:00 | 2022-02-11 13:50 |  |  | Attended site to repair door, found that the door in question is a large 2.5m x 4m fire door with a marshall beatie box connected to it. This is not one of our doors and is out of our scope of works.
MSA-DTAG | WA5832329 | 1 | Codee Cleaning Services | Registry and Clerk of Court Office-Extensive Covid Clean required-see notes | Cleaning | Sanitary Services | 1400 | Pass | Pass | 0 | 0 | 0.43333 | 2022-09-05 12:20 | 2022-09-06 17:00 | 2022-09-06 15:51 | 2022-09-06 17:00 | 2022-09-06 16:17 |  |  | completed 6/09/2022
MSA-DFES | WA6145586 | 2 | SONTEC WA PTY LTD | Office/Warehouse - emergency release break glass is damaged | Fire Protection Services | Fire Protection - Monitor System | 234.65 | Pass | Pass | 0 | 0 | 0.43333 | 2022-11-02 12:59 | 2022-11-07 17:00 | 2022-11-07 09:04 | 2022-11-07 17:00 | 2022-11-07 09:30 |  |  | 7/11/22 - Dean SimpsonReplaced broken breakglass at main office entry door.
MSA-DTWD | WA6298378 | 2 | Precise Air Group | Check fresh air intake working. | Air Conditioning | Room Air Conditioners | 405.405 | Pass | Pass | -1 | -1 | 0.43333 | 2022-12-01 09:31 | 2022-12-06 17:00 | 2022-12-01 14:10 | 2022-12-06 17:00 | 2022-12-01 14:36 |  |  | All OAFs operatioanl and moving air as designed. All 4 filters are starting to become blocked recommend replacement but not a critical issue.All 4 OAF operational. unsure of design specifications for OAFs when installed. May need adjusting from installation parameters to operational needs of classrooms. All rooms are of a large volume room with 10foot to drop ceiling level plus roof space. One room is two rooms together creating a large double size classroom. All 4 room face west on the top level of west building and the cassette units maybe at there upper levels of designe parameters.
MSA-DCA | WA6518532 | 1 | Precise Air Group | Level 3 - Control room - Aircon faulty | Air Conditioning | Room Air Conditioners | 177.03 | Pass | Pass | 0 | 0 | 0.43333 | 2023-01-25 09:10 | 2023-01-27 17:00 | 2023-01-25 11:08 | 2023-01-27 17:00 | 2023-01-25 11:34
MSA-DFES | WA6650697 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Bedroom 1 - cracked toilet bowl - seat broken | Plumbing & Drainage | Toilets/Cisterns | 153.89 | Pass | Pass | 0 | 0 | 0.43333 | 2023-02-20 12:31 | 2023-02-23 17:00 | 2023-02-21 12:58 | 2023-02-23 17:00 | 2023-02-21 13:24
MSA-DTWD | WA5438224 | 2 | Swan Pest Control | V Block - 002 - Mice activity | Pest Control | General Pest | 203 | Pass | Pass | 0 | 0 | 0.41667 | 2022-05-16 13:16 | 2022-05-19 17:00 | 2022-05-18 12:10 | 2022-05-19 17:00 | 2022-05-18 12:35 |  |  | Installed 6 large cardboard rodent stations and 2 Ditrac blocks
MSA-DTWD | WA5496449 | 2 | Swan Pest Control | Marketing area - Kendrew- D-Block 2nd Floor marketing area mouse sightings | Pest Control | General Pest | 203 | Pass | Pass | 0 | 0 | 0.41667 | 2022-06-09 10:14 | 2022-06-14 17:00 | 2022-06-13 12:10 | 2022-06-14 17:00 | 2022-06-13 12:35 |  |  | Installed 6 large cardboard rodent stations and 12 Ditrac blocks
MSA-DTWD | WA5692196 | 1 | CONNECT SECURITY SYSTEMS | Entrance of side door-Unable to arm/disarm alarm system | Security | Security Management System | 82.4 | Pass | Pass | 0 | 0 | 0.41667 | 2022-08-03 11:16 | 2022-08-04 17:00 | 2022-08-03 11:25 | 2022-08-04 17:00 | 2022-08-03 11:50 |  |  | Replaced 1 x failed step down transformer
MSA-DCA | WA6000556 | 0 | ADVANCED LOCK & KEY | Opp Alex hotel-high voltage power recess-been broken into needs new lock-see note | Security | Locksmith | 250 | Pass | Pass | 0 | 0 | 0.41667 | 2022-10-10 08:53 | 2022-10-10 10:53 | 2022-10-10 09:10 | 2022-10-10 12:53 | 2022-10-10 09:35 |  |  | supplied new WAS 83/45 for high voltage entrance gate area & rekeyed another padlock to new padlocks keys & WAS key
MSA-DFES | WA6208136 | 1 | ADVANCED LOCK & KEY | external door into courtyard-to stair 4 door, it is not closing properly | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.41667 | 2022-11-17 13:29 | 2022-11-18 17:00 | 2022-11-18 11:25 | 2022-11-18 17:00 | 2022-11-18 11:50 |  |  | Adjusted door closer on door
MSA-MRWA | WA6519342 | 2 | Water2water Pty Ltd | kitchen-Billi Tap in kitchen continues to fault / lock-see notes | Plumbing & Drainage | Water | 479.64 | Pass | Pass | 0 | 0 | 0.41667 | 2023-01-25 15:57 | 2023-01-31 17:00 | 2023-01-30 15:55 | 2023-01-31 17:00 | 2023-01-30 16:20
MSA-DFES | WA5010029 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Admin - Male Toilets - leaking pipe from the cistern - see notes below | Plumbing & Drainage | Toilets/Cisterns | 75.9375 | Pass | Pass | -1 | -1 | 0.41667 | 2022-01-12 09:38 | 2022-01-17 17:00 | 2022-01-12 10:37 | 2022-01-17 17:00 | 2022-01-12 11:02 |  |  | Replaced Flexi hose.
MSA-DFES | WA5018120 | 2 | Water2water Pty Ltd | Hot water urn - tap is leaking | Equipment | Catering Equipment | 222.685 | Pass | Pass | 0 | 0 | 0.41667 | 2022-01-14 09:03 | 2022-01-19 17:00 | 2022-01-17 11:35 | 2022-01-19 17:00 | 2022-01-17 12:00 |  |  | Technician attended and replaced tap. All okay on departure.
MSA-DFES | WA5105544 | 2 | Water2water Pty Ltd | kitchen - faulty drinking water units - see notes | Plumbing & Drainage | Water | 392.025 | Pass | Pass | 0 | 0 | 0.41667 | 2022-02-04 11:51 | 2022-02-09 17:00 | 2022-02-08 12:15 | 2022-02-09 17:00 | 2022-02-08 12:40 |  |  | Replaced power board on Billi unit due to error message
MSA-DFES | WA5106637 | 3 | ADVANCED LOCK & KEY | Female bathroom - lock broken | Security | Locksmith | 195 | Pass | Pass | -1 | -1 | 0.41667 | 2022-02-07 09:57 | 2022-02-14 17:00 | 2022-02-10 13:35 | 2022-02-14 17:00 | 2022-02-10 14:00 |  |  | replace lock & adjust strike
MSA-DFES | WA5108478 | 2 | Water2water Pty Ltd | Level 1 - kitchen zip unit not working all the time, stop and start requires service | Plumbing & Drainage | Water | 117.925 | Pass | Pass | 0 | 0 | 0.41667 | 2022-02-08 14:19 | 2022-02-11 17:00 | 2022-02-10 14:35 | 2022-02-11 17:00 | 2022-02-10 15:00 |  |  | Checked all Zip Systems on Level 1 could not find any faults.
MSA-DTWD | WA5192758 | 1 | SENTINEL LOCK SERVICE PTY LTD | Fire Alarm Panel – Base of stair well - Key is stuck in Fire Alarm Panel lock | Security | Locksmith | 92.8 | Pass | Pass | 0 | 0 | 0.41667 | 2022-02-25 11:57 | 2022-02-28 17:00 | 2022-02-25 12:00 | 2022-02-28 17:00 | 2022-02-25 12:25 |  |  | Fire alarm panel - B Block - key stuck in lock.Key removed - lock repaired, worn key replaced.
MSA-DTWD | WA5209128 | 3 | ADVANCED LOCK & KEY | Level 1 - E102 Sliding gate - key stiff to turn barrel | Security | Locksmith | 145 | Fail | Fail | 1 | 1 | 0.41667 | 2022-03-09 13:51 | 2022-03-16 17:00 | 2022-03-21 12:50 | 2022-03-16 17:00 | 2022-03-21 13:15 |  |  | serviced lock.
MSA-DTWD | WA5209150 | 2 | ADVANCED LOCK & KEY | B6 - Level 3 - Fire exit door - replace broken door handle | Security | Keys & Access | 415.41 | Pass | Pass | 0 | 0 | 0.41667 | 2022-03-09 14:03 | 2022-03-14 17:00 | 2022-03-11 12:05 | 2022-03-14 17:00 | 2022-03-11 12:30 |  |  | Replaced broken mortice furniture
MSA-DTWD | WA5287171 | 2 | Swan Pest Control | B-Block - Play group area - mouse in play group area | Pest Control | General Pest | 200 | Pass | Pass | 0 | 0 | 0.41667 | 2022-03-22 10:46 | 2022-03-25 17:00 | 2022-03-24 09:45 | 2022-03-25 17:00 | 2022-03-24 10:10 |  |  | Installed 6 lockable rodent station and 6 ditrac blocks
MSA-DTWD | WA5289325 | 3 | Swan Pest Control | P block - Ground - play ground - Sand-flies in Playgroup Sandpit | Pest Control | General Pest | 195 | Pass | Pass | 0 | 0 | 0.41667 | 2022-03-24 08:31 | 2022-03-31 17:00 | 2022-03-29 06:00 | 2022-03-31 17:00 | 2022-03-29 06:25 |  |  | Sprayed both sandpits for sand flies with Biflex Aqua Max
MSA-DTWD | WA5290891 | 2 | AWB Co. | F & H Blocks - Security lights under verandah - Security lights on 24/7 | Electrical | Lighting, External | 131.58 | Pass | Pass | -1 | -1 | 0.41667 | 2022-03-25 12:35 | 2022-03-30 17:00 | 2022-03-25 12:35 | 2022-03-30 17:00 | 2022-03-25 13:00 |  |  | Attended site signed in completed jsa. Spoke to dennis about lights staying on. Found overide on and also pe cell was faulty as overide in the off was still keeping lights on. Replaced pe cell and problem was solved.**job completed**
MSA-DCA | WA5380292 | 2 | GPS Plumbing & Gas Services PtyLtd | Theatre Foyer - public male toilet - 2nd Cubicle blocked | Plumbing & Drainage | Toilets/Cisterns | 87.27 | Pass | Pass | 0 | 0 | 0.41667 | 2022-04-22 10:17 | 2022-04-28 17:00 | 2022-04-26 13:30 | 2022-04-28 17:00 | 2022-04-26 13:55 |  |  | Cleared blocked ground floor male public toilet 2nd cubicle
MSA-DTWD | WA5380629 | 2 | ADVANCED LOCK & KEY | Skip Compound - Exterior Compound - Replace broken Padlock to Skip Compund | Security | Locksmith | 245 | Pass | Pass | 0 | 0 | 0.41667 | 2022-04-22 14:18 | 2022-04-28 17:00 | 2022-04-27 15:30 | 2022-04-28 17:00 | 2022-04-27 15:55 |  |  | Supplied new 83/45 on status 6 ST keyed to GGMK only for skip compound1x ST status 6 83/45
MSA-MRWA | WA5383168 | 2 | Water2water Pty Ltd | Basement Corridor - Water fountain not cool | Plumbing & Drainage | Water | 117.925 | Pass | Pass | 0 | 0 | 0.41667 | 2022-04-27 13:03 | 2022-05-02 17:00 | 2022-05-02 09:45 | 2022-05-02 17:00 | 2022-05-02 10:10 |  |  | Arcus fountain not chilling. Will organise arcus to come out and look at the unit
MSA-DTWD | WA5493794 | 3 | ADVANCED LOCK & KEY | Lift Lobby - Door handle broken - Access to roof | Security | Locksmith | 154.5 | Pass | Pass | -1 | -1 | 0.41667 | 2022-06-07 10:18 | 2022-06-14 17:00 | 2022-06-08 09:35 | 2022-06-14 17:00 | 2022-06-08 10:00 |  |  | Replaced spindle that had been forced on roof access door next to lift with new spindle9:35-10:001x Lockwood 3572 spindle
MSA-DTWD | WA5496504 | 2 | Swan Pest Control | Block 8 - Roof space near 8G1- storeroom - possible dead possum | Pest Control | General Pest | 95 | Pass | Pass | -1 | -1 | 0.41667 | 2022-06-09 10:39 | 2022-06-14 17:00 | 2022-06-10 11:30 | 2022-06-14 17:00 | 2022-06-10 11:55 |  |  | No possum found
MSA-DTWD | WA5497185 | 2 | Swan Pest Control | Rat infestation in Q Shed in the insulation | Pest Control | General Pest | 227 | Pass | Pass | 0 | 0 | 0.41667 | 2022-06-09 15:27 | 2022-06-14 17:00 | 2022-06-14 09:15 | 2022-06-14 17:00 | 2022-06-14 09:40 |  |  | Installed 4 large cardboard stations and 20 Ditrac blocks to rafters in shed
MSA-DTAG | WA5513206 | 1 | OCS SERVICES PTY LTD | Ground Floor - Registry - Counter 5 - Covid Clean | Cleaning | Emergency Cleans |  | Pass | Pass | 0 | 0 | 0.41667 | 2022-06-14 08:40 | 2022-06-15 17:00 | 2022-06-15 11:05 | 2022-06-15 17:00 | 2022-06-15 11:30 |  |  | Completed covid clean
MSA-DTAG | WA5613500 | 1 | Dormakaba Australia Pty Ltd | ground sliding door-not working-see notes | Building | Automatic Doors | 235 | Pass | Pass | 0 | 0 | 0.41667 | 2022-07-14 13:00 | 2022-07-15 17:00 | 2022-07-14 14:30 | 2022-07-15 17:00 | 2022-07-14 14:55 |  |  | Found that the door was staying open due to dirty pe sensors, cleaned sensors and tested, all ok.
MSA-DTWD | WA5706958 | 2 | ADVANCED LOCK & KEY | Faulty lock on main door - keycode is B2 - see notes below | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.41667 | 2022-08-11 14:56 | 2022-08-16 17:00 | 2022-08-12 11:45 | 2022-08-16 17:00 | 2022-08-12 12:10 |  |  | not our system so could not pull lock apart or cut keys they wanted, James asked if I could complete the job & they will use Armadale lock & key direct.
MSA-DFES | WA5839046 | 2 | ADVANCED LOCK & KEY | Dormitory 9 - door lock broken away from door | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.41667 | 2022-09-09 08:42 | 2022-09-14 17:00 | 2022-09-12 13:20 | 2022-09-14 17:00 | 2022-09-12 13:45 |  |  | installed thumb turn on dorm 9 ensuite door in new position
MSA-DCA | WA5887731 | 2 | Techworks Plumbing | Faulty Zip tap - Francis st Level 1 - East zip (SEG exit) | Plumbing & Drainage | Water | 230.86 | Pass | Pass | 0 | 0 | 0.41667 | 2022-09-16 09:36 | 2022-09-21 17:00 | 2022-09-19 08:20 | 2022-09-21 17:00 | 2022-09-19 08:45 |  |  | On arrival to check level 1 Francis st zip tap, we checked the zip tap for operation but at first nothing was coming out, so we done a reset and flush, we flushed out roughly a quarter of a bucket of water, once we finished the flush we tested the zip tap for operation and it was working fine besides one side of the zip tap button wasn’t working, other then that it was operating, we then packed up and made our way to the next zip tap.
MSA-DFES | WA5973099 | 2 | ADVANCED LOCK & KEY | Dorm 6 - Ground - Lock mechanism on the sliding door between locker room and dorm 6 toilet is U/S | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.41667 | 2022-09-21 10:32 | 2022-09-27 17:00 | 2022-09-27 11:35 | 2022-09-27 17:00 | 2022-09-27 12:00 |  |  | serviced 3573 on dorm 6 bathroom door
MSA-DCA | WA5998312 | 1 | ADVANCED LOCK & KEY | Ground - Baby Change Room - Lock is jammed | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.41667 | 2022-10-07 14:02 | 2022-10-10 17:00 | 2022-10-07 14:35 | 2022-10-10 17:00 | 2022-10-07 15:00 |  |  | service lock on baby change room as snib binded up, 3573 with Astra indicator going through thumb turn adapter with square drive
MSA-DCA | WA6131937 | 2 | ADVANCED LOCK & KEY | Front doors-Fault description Auto door needing new lock barrels. New key to match existing master s | Security | Locksmith | 320 | Pass | Pass | 0 | 0 | 0.41667 | 2022-10-31 10:41 | 2022-11-03 17:00 | 2022-11-03 12:35 | 2022-11-03 17:00 | 2022-11-03 13:00 |  |  | Attend site to replace 2xLIW switches on front door and key alike 2x LIW switches MK LW4
MSA-DTWD | WA6154585 | 2 | ECO PLUMBING AND GAS PTY LTD | Toilet flusher not working properly, toilet is continuously flushing. | Plumbing & Drainage | Toilets/Cisterns | 103.191 | Pass | Pass | 0 | 0 | 0.41667 | 2022-11-07 13:49 | 2022-11-10 17:00 | 2022-11-10 13:07 | 2022-11-10 17:00 | 2022-11-10 13:32 |  |  | Replaced washer in 2nd cubicle
MSA-DTWD | WA6231239 | 2 | ADVANCED LOCK & KEY | A366 - Exit door requires a handle fitted | Building | Doors | 353.5 | Pass | Pass | 0 | 0 | 0.41667 | 2022-11-18 15:28 | 2022-11-23 17:00 | 2022-11-21 09:30 | 2022-11-23 17:00 | 2022-11-21 09:55 |  |  | A336 had a mag lock only on it, John said they will need to get the access control people out as it’s an issue for them not us, asked if he could get 3x 42886 padlocks since he got us out and call Kate and she said it would be ok since it’s programmed 3x 42886 83/45
MSA-DFES | WA6292793 | 1 | ADVANCED LOCK & KEY | Second Floor - Office of the Commissioner - cabinet wont open | Security | Locksmith | 170 | Pass | Pass | 0 | 0 | 0.41667 | 2022-11-29 13:12 | 2022-11-30 17:00 | 2022-11-30 14:35 | 2022-11-30 17:00 | 2022-11-30 15:00 |  |  | Cut 1 BMB3 to code a026 for pedestal filing draw in lvl 2 commissioner’s reception area 1x BMB3 to code
MSA-DTWD | WA6415291 | 1 | Casa Security Pty Ltd | Zone 69 - Alarm Fault | Security | Monitoring | 180 | Pass | Pass | 0 | 0 | 0.41667 | 2023-01-11 15:38 | 2023-01-12 17:00 | 2023-01-11 16:00 | 2023-01-12 17:00 | 2023-01-11 16:25
MSA-DTAG | WA6579148 | 2 | Bullant Security Pty Ltd | Detention - Male staff toilet - Faulty lock | Security | Locksmith | 165 | Pass | Pass | 0 | 0 | 0.41667 | 2023-02-15 15:06 | 2023-02-20 17:00 | 2023-02-17 13:45 | 2023-02-20 17:00 | 2023-02-17 14:10
MSA-DTWD | WA6680543 | 2 | ADVANCED LOCK & KEY | Replace cabinet lock to office A135 | Security | Locksmith |  | Pass | Pass | -1 | -1 | 0.41667 | 2023-03-01 12:17 | 2023-03-07 17:00 | 2023-03-03 10:00 | 2023-03-07 17:00 | 2023-03-03 10:25
MSA-DTWD | WA6708134 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire alarm was set off in male toilets next to lift. Cause not known. (see notes) | Fire Protection Services | Fire Protection - Monitor System | 98.826 | Pass | Pass | 0 | 0 | 0.41667 | 2023-03-13 13:19 | 2023-03-14 17:00 | 2023-03-13 14:50 | 2023-03-14 17:00 | 2023-03-13 15:15
MSA-DCA | WA4992331 | 3 | ADVANCED LOCK & KEY | Theatre Foyer- ladies toilets - cubicle 4 - Lock faulty, would not open. Lock taken off. | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.41667 | 2022-01-06 10:05 | 2022-01-13 17:00 | 2022-01-12 11:55 | 2022-01-13 17:00 | 2022-01-12 12:20 |  |  | Completed12/1/22Straighten mounting plate and reassembled indicator bolt on female toilet in foyer
MSA-DTWD | WA5106330 | 0 | ADVANCED LOCK & KEY | Door Handle - fallen to bits and faulty - need access ASAP | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.41667 | 2022-02-07 07:33 | 2022-02-07 09:33 | 2022-02-07 08:40 | 2022-02-07 11:33 | 2022-02-07 09:05 |  |  | Completed 7/2/22
MSA-DCA | WA5112008 | 3 | TK Elevator Australia Pty Ltd | ** Retrospective Work Order ** Lift 1 - reset the lift after a power outage | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.41667 | 2021-12-27 09:00 | 2022-01-05 17:00 | 2021-12-27 10:42 | 2022-01-05 17:00 | 2021-12-27 11:07 | 1 |  | Lift stopped due to power outage yesterday reset and tested all okay left running
MSA-DFES | WA5215713 | 1 | Facilities First Australia Pty Ltd | Commcen general area - clean required | Cleaning | Cleaning | 190 | Pass | Pass | 0 | 0 | 0.41667 | 2022-03-10 15:36 | 2022-03-11 17:00 | 2022-03-11 11:51 | 2022-03-11 17:00 | 2022-03-11 12:16 |  |  | Clean completed within the timeframe, as requested
MSA-DTWD | WA6113212 | 2 | ADVANCED LOCK & KEY | Door lock does not match maintenance door locking system - see notes below | Security | Locksmith | 274.5 | Pass | Pass | 0 | 0 | 0.41667 | 2022-10-24 09:38 | 2022-10-27 17:00 | 2022-10-25 08:40 | 2022-10-27 17:00 | 2022-10-25 09:05 |  |  | Replaced oval cyl on A block plant room with new 42886 oval cyl and supplied a 42886 padlock 8:40-9:05 1x 42886 570 cyl 1x 42886 83/45 padlock
MSA-DCA | WA6642396 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Air con is not working for the whole building | Air Conditioning | Materials | 546.18 | Pass | Pass | 0 | 0 | 0.41667 | 2023-02-19 14:57 | 2023-02-20 14:57 | 2023-02-20 08:40 | 2023-02-20 14:57 | 2023-02-20 09:05
MSA-MRWA | WA5437362 | 1 | TK Elevator Australia Pty Ltd | Lift 2 - out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.4 | 2022-05-16 07:47 | 2022-05-16 17:00 | 2022-05-16 11:24 | 2022-05-16 17:00 | 2022-05-16 11:48 |  |  | Lift2 DAC-Geared :Checked operation of lift as per customer request. Noticed some noise from door closer weight but most likely rubber O ring. Will check for replacement.to be closed out at $0 cost
MSA-DTWD | WA5491112 | 2 | Casa Security Pty Ltd | Faulty Sensor in zone 54 of O Block | Security | Monitoring | 42.76 | Pass | Pass | -1 | -1 | 0.4 | 2022-06-03 12:20 | 2022-06-09 17:00 | 2022-06-03 12:21 | 2022-06-09 17:00 | 2022-06-03 12:45 |  |  | FAULTY SENSOR IN 54 O BLOCKCHECKED/REPLACED LOW BATTERIES ON ZONE 54 SENSORCLEARED FAULTRESTORED TO NORMAL
MSA-DTWD | WA5603152 | 1 | CONNECT SECURITY SYSTEMS | Level 1 - T Block in Alarm - want to disarm | Security | Monitoring | 153.18 | Pass | Pass | 0 | 0 | 0.4 | 2022-07-12 08:20 | 2022-07-13 17:00 | 2022-07-12 11:36 | 2022-07-13 17:00 | 2022-07-12 12:00 |  |  | COMPLETED 12/7/22
MSA-DCA | WA5680464 | 0 | Kone Elevators Pty Ltd | Escalator 4 - is faulty | Lifts | Escalators or Moving Walk |  | Pass | Pass | 0 | 0 | 0.4 | 2022-07-27 12:36 | 2022-07-27 14:36 | 2022-07-27 13:55 | 2022-07-27 16:36 | 2022-07-27 14:19 |  |  | RUBBER TOY CAUGHT IN BOTTOM COMB PLATE,REMOVED, CONFIRM OPERATION AND RETURNTO SERVICE.
MSA-DFES | WA5596917 | 2 | Anvil Doors | Driveway - Entrance to yard - Auto gate not working automatically - See notes below | Building | Automatic Doors | 528 | Pass | Pass | 0 | 0 | 0.4 | 2022-07-11 11:16 | 2022-07-14 17:00 | 2022-07-12 13:56 | 2022-07-14 17:00 | 2022-07-12 14:20 |  |  | Due to impact front of gate track wheel bent. Removed track wheel straighten it and placed it back on,move motor, adjust limit and test operation all ok
MSA-DCA | WA5323554 | 1 | CONNECT SECURITY SYSTEMS | G block - Reinstate the dis-engaged alarms – blue strobe | Security | Monitoring | 153.18 | Fail | Fail | 0 | 0 | 0.38333 | 2022-04-13 09:15 | 2022-04-13 11:15 | 2022-04-13 13:09 | 2022-04-13 13:15 | 2022-04-13 13:32 |  |  | Re-enabled siren for G Block Public Toilet Alarm System
MSA-DTWD | WA5676817 | 1 | CONNECT SECURITY SYSTEMS | Alarm system showing low battery. | Security | Security Management System | 185.8 | Pass | Pass | 0 | 0 | 0.38333 | 2022-07-25 10:44 | 2022-07-26 17:00 | 2022-07-25 14:17 | 2022-07-26 17:00 | 2022-07-25 14:40 |  |  | Replaced 12V battery as the system was in low battery
MSA-DTWD | WA6539440 | 2 | Australian Airconditioning Services Pty Ltd | Split AC is not running | Air Conditioning | Room Air Conditioners | 333.56 | Pass | Pass | -1 | -1 | 0.38333 | 2023-02-08 13:06 | 2023-02-13 17:00 | 2023-02-08 13:07 | 2023-02-13 17:00 | 2023-02-08 13:30
MSA-DCA | WA6516069 | 0 | TK Elevator Australia Pty Ltd | Lift stuck in-between floors | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 0.38333 | 2023-01-23 08:52 | 2023-01-23 10:52 | 2023-01-23 11:10 | 2023-01-23 12:52 | 2023-01-23 11:33
MSA-DTWD | WA5216628 | 2 | AHS Services WA Pty Ltd (Anchor) | Kendrew- E-Block SK2 3rd sink on right has a broken flick mixer | Plumbing & Drainage | Materials | 83.725 | Pass | Pass | 0 | 0 | 0.36667 | 2022-03-11 11:46 | 2022-03-16 17:00 | 2022-03-15 07:53 | 2022-03-16 17:00 | 2022-03-15 08:15 |  |  | Completed
MSA-DTWD | WA6509480 | 2 | Dormakaba Australia Pty Ltd | Main Entrance - Security gate stuck open – require key to override | Security | Security Management System | 345 | Pass | Pass | 0 | 0 | 0.36667 | 2023-01-20 11:12 | 2023-01-25 17:00 | 2023-01-23 07:44 | 2023-01-25 17:00 | 2023-01-23 08:06
MSA-DTWD | WA5697991 | 3 | AWB Co. | Replace damaged 150 AMP plug to muffle furnace | Equipment | Electrical Equipment | 165.05 | Pass | Pass | 0 | 0 | 0.36667 | 2022-08-09 13:33 | 2022-08-16 17:00 | 2022-08-15 15:08 | 2022-08-16 17:00 | 2022-08-15 15:30 |  |  | Replaced damaged 20A 3pin plug
MSA-DCA | WA6129900 | 1 | Dormakaba Australia Pty Ltd | Geology building - ground floor - Epoch Cafe/NKBW - Door having issues please see notes | Building | Automatic Doors | 345 | Pass | Pass | 0 | 0 | 0.35 | 2022-10-28 08:13 | 2022-10-31 17:00 | 2022-10-28 11:54 | 2022-10-31 17:00 | 2022-10-28 12:15 |  |  | (Manual cafe doors) Called to site. Accessed doors with on-site contact Neil. Discussed likely access control scenarios. Doors okay.
MSA-DCA | WA6642306 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidity Alarm in Collection Store | Air Conditioning | Building HVAC Maintenance (Major Plant) | 546.18 | Fail | Fail | 0 | 0 | 0.35 | 2023-02-19 02:15 | 2023-02-19 04:15 | 2023-02-20 08:39 | 2023-02-19 06:15 | 2023-02-20 09:00
MSA-DCA | WA6377385 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - See notes | Security | Security Management System |  | Fail | Fail | 1 | 1 | 0.34 | 2022-12-12 07:30 | 2022-12-12 17:00 | 2022-12-16 13:40 | 2022-12-12 17:00 | 2022-12-16 14:00 | 1 |  | Conducted internal and external inspection of u block, no signs of forced EntryNo cause for alarm found. Significant damage found to site in area, In particular the collapsed roof is a hazard. Cleared from site by david from CMC
MSA-DTWD | WA5018673 | 1 | SCAVENGER SUPPLIES PTY LTD | B Block - Ground & 1st Floor - All staff rooms - see details below | Fire Protection Services | Fire Protection - Monitor System | 99.37 | Pass | Pass | 0 | 0 | 0.33333 | 2022-01-14 14:26 | 2022-01-17 17:00 | 2022-01-17 07:50 | 2022-01-17 17:00 | 2022-01-17 08:10 |  |  | COMPLETED 17/01/2021NO RETURN TO SITE ON OR BEFORE 19T-/01/2022 NEEDED
MSA-DFES | WA5099386 | 2 | Complete Pest Management Services | Ground - Rear yard -Active wasp nest in rear yard above clothesline | Pest Control | General Pest | 162.08 | Pass | Pass | 0 | 0 | 0.33333 | 2022-02-01 17:27 | 2022-02-04 17:00 | 2022-02-03 13:50 | 2022-02-04 17:00 | 2022-02-03 14:10 |  |  | Treated wasp nest in rear yard
MSA-DFES | WA5105836 | 2 | ADVANCED LOCK & KEY | side gate - faulty lock (Lockey Digital) - see notes | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.33333 | 2022-02-04 14:56 | 2022-02-09 17:00 | 2022-02-07 10:35 | 2022-02-09 17:00 | 2022-02-07 10:55 |  |  | Completed Serviced lock and reset code.
MSA-DFES | WA5126309 | 2 | ADVANCED LOCK & KEY | Shed - Lockable door to shed at rear of station is not locking - Lock wont engage the cutout | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.33333 | 2022-02-14 07:30 | 2022-02-16 17:00 | 2022-02-16 12:50 | 2022-02-16 17:00 | 2022-02-16 13:10 |  |  | Filed strike and tighten hinges on shed entry door
MSA-DTWD | WA5393503 | 2 | PEEL LOCK SERVICES PTY LTD | LG12b - Faulty door lock - See notes | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.33333 | 2022-05-04 08:22 | 2022-05-09 17:00 | 2022-05-06 10:50 | 2022-05-09 17:00 | 2022-05-06 11:10 |  |  | job compelted - repaired faulty lock
MSA-DTWD | WA6256955 | 2 | AHS Services WA Pty Ltd (Anchor) | Male staff toilet urinal overflowing before draining away - see notes below | Plumbing & Drainage | Toilets/Cisterns | 191.445 | Pass | Pass | 0 | 0 | 0.33333 | 2022-11-24 10:34 | 2022-11-29 17:00 | 2022-11-28 08:35 | 2022-11-29 17:00 | 2022-11-28 08:55 |  |  | Used hot water and plunger on both urinals
MSA-DFES | WA6360247 | 3 | ADVANCED LOCK & KEY | Ground Floor - Ant Sadler’s Office - Door not latching - See Notes Below | Building | Doors | 160 | Pass | Pass | 0 | 0 | 0.33333 | 2022-12-07 09:50 | 2022-12-14 17:00 | 2022-12-12 13:35 | 2022-12-14 17:00 | 2022-12-12 13:55 |  |  | File strike and cut strike box on superintendents office door on ground floor
MSA-DFES | WA6408078 | 2 | ADVANCED LOCK & KEY | Level 1 - Door lock is not engaging into the frame latch - See Notes Below | Security | Locksmith | 220 | Pass | Pass | 0 | 0 | 0.33333 | 2023-01-10 14:25 | 2023-01-13 17:00 | 2023-01-13 11:20 | 2023-01-13 17:00 | 2023-01-13 11:40
MSA-DTAG | WA6426128 | 1 | Water2water Pty Ltd | Retrospective work order - DO NOT ATTEND - Change filter & flush (see notes) | Plumbing & Drainage | Water | 142.38 | Pass | Pass | 0 | 0 | 0.33333 | 2023-01-11 15:50 | 2023-01-12 17:00 | 2023-01-11 15:50 | 2023-01-12 17:00 | 2023-01-11 16:10 | 1
MSA-DFES | WA4990905 | 2 | Dom's Total Grounds Maintenance | Ground - Courtyard - Pond Water sensor is broken | Landscaping & Gardening | Grounds Maintenance | 106.5 | Pass | Pass | 0 | 0 | 0.33333 | 2022-01-04 12:57 | 2022-01-07 17:00 | 2022-01-06 08:30 | 2022-01-07 17:00 | 2022-01-06 08:50 |  |  | Call Out & LabourSupply Parts
MSA-DTAG | WA5018593 | 2 | Water2water Pty Ltd | Level 11 - Kitchen - Cold water filter tap is running slow | Plumbing & Drainage | Water | 243.045 | Pass | Pass | 0 | 0 | 0.33333 | 2022-01-14 13:17 | 2022-01-19 17:00 | 2022-01-17 16:30 | 2022-01-19 17:00 | 2022-01-17 16:50 |  |  | Replaced filter. Flow not satisfactory for client
MSA-DTWD | WA5092223 | 0 | Dormakaba Australia Pty Ltd | Main Entrance - Door is opening and closing on it's own. | Building | Automatic Doors | 450 | Pass | Pass | 0 | 0 | 0.33333 | 2022-01-27 17:36 | 2022-01-27 19:36 | 2022-01-27 18:10 | 2022-01-27 21:36 | 2022-01-27 18:30 |  |  | Inspected door and found that the external safety sensor was self actuating, adjusted and reset sensor as necessary, checked over and tested operationupon completion and left in good working order.
MSA-DTWD | WA5094837 | 0 | Casa Security Pty Ltd | R Block - security not responding | Security | Monitoring | 157.5 | Fail | Fail | 1 | 1 | 0.33333 | 2022-01-31 14:27 | 2022-01-31 16:27 | 2022-02-07 15:51 | 2022-01-31 18:27 | 2022-02-07 16:11 |  |  | 31/01 INITIALLY ABLE TO CALL SITE AND PROGRAM OUT FAULTY ZONE OVER THE PHONE UNTIL WE COULD ATTENDATTENDED SITE 07/02LOCATED FAULTY ZONE NOT SEALING TO ALLOW ARMING OF THE SYSTEMFIXED TAMPER SWITCH ON THE DEVICEPROGRAMMED ZONE BACK INCLEARED FAULTSTESTED - ALL OK
MSA-DFES | WA5201384 | 2 | Anvil Doors | engine room - Warning Hazard lights on southern side front door are working intermittingly and pulle | Building | Automatic Doors | 2000 | Pass | Pass | -1 | -1 | 0.33333 | 2022-03-02 14:25 | 2022-03-08 17:00 | 2022-03-03 09:15 | 2022-03-08 17:00 | 2022-03-03 09:35 |  |  | Attended Dalglish Fire station and checked Traffic light operation to Door 1. It appears that the red warning light is not coming on while door is closing. Dispatch electrician to fix the issue. Please see attached service report and signature slip.Electrician has attended and found the the door requires a new TS971 controller. Please see attached BRAF and Quote.Thank you
MSA-DFES | WA5206884 | 2 | Dom's Total Grounds Maintenance | Front Yard (Near appliance driveway/apron) - Sprinkler broken | Plumbing & Drainage | Water | 222 | Pass | Pass | 0 | 0 | 0.33333 | 2022-03-08 09:58 | 2022-03-11 17:00 | 2022-03-10 08:00 | 2022-03-11 17:00 | 2022-03-10 08:20 |  |  | Replace Broken Sprinkler
MSA-DTAG | WA5274789 | 2 | Dormakaba Australia Pty Ltd | Armadale Court - Custody - Sallyport - Electronic lock faulty. Key barrel loose | Security | Access Control | 235 | Pass | Pass | -1 | -1 | 0.33333 | 2022-03-17 11:45 | 2022-03-22 17:00 | 2022-03-18 08:25 | 2022-03-22 17:00 | 2022-03-18 08:45 |  |  | Attended site and inspected door, and found that site have an issue with the electric strike not releasing, advised to site to call out access tech to rectify.
MSA-DTAG | WA5303852 | 1 | SONTEC WA PTY LTD | Security Office - CCTV screens not displaying - see notes below | Security | CCTV Surveillance | 230 | Fail | Fail | 0 | 0 | 0.33333 | 2022-04-04 12:56 | 2022-04-05 17:00 | 2022-04-06 15:40 | 2022-04-05 17:00 | 2022-04-06 16:00 |  |  | 6/4/22 - Dylan ParslowChecked CCTV operation of computers.All CCTV displays and PC's working correctly.
MSA-DTWD | WA5323667 | 2 | Casa Security Pty Ltd | Horticulture Shed - Camera Hard Drive system has an alarm sounding | Security | CCTV Surveillance | 180 | Pass | Pass | -1 | -1 | 0.33333 | 2022-04-13 10:07 | 2022-04-20 17:00 | 2022-04-13 13:10 | 2022-04-20 17:00 | 2022-04-13 13:30 |  |  | HORTICULTURE SHED -CAMERA HARD DRIVE SYSTEM HAS AN ALARM SOUNDINGTECHNICIAN REPLACED BACK UP BATTERY IN UPS (UNINTERRUPTED POWER SUPPLY)SYSTEM RESTORED TO NORMAL
MSA-DTWD | WA5368800 | 2 | Swan Pest Control | D-Block - Level 2 - Lift Lobby area - mouse sighting | Pest Control | General Pest | 207.5 | Pass | Pass | 0 | 0 | 0.33333 | 2022-04-19 12:58 | 2022-04-22 17:00 | 2022-04-21 07:15 | 2022-04-22 17:00 | 2022-04-21 07:35 |  |  | Installed 5 lockable mouse stations and 10Ditrac Blocks
MSA-DFES | WA5382194 | 2 | Complete Pest Management Services | Lecture Room 9 - Bad smell, possibly a dead rodent in the roof | Pest Control | General Pest | 122.59 | Pass | Pass | 0 | 0 | 0.33333 | 2022-04-26 15:14 | 2022-04-29 17:00 | 2022-04-29 13:25 | 2022-04-29 17:00 | 2022-04-29 13:45 |  |  | Inspected lecture room 9 and located deceased rodent in roof and removed.
MSA-DTAG | WA5491114 | 1 | AWB Co. | Ground - Registry/Customer Service Side - Counter 1 and Filing room - lights faulty | Electrical | General Electrical | 152.56 | Pass | Pass | 0 | 0 | 0.33333 | 2022-06-03 12:13 | 2022-06-07 17:00 | 2022-06-07 07:40 | 2022-06-07 17:00 | 2022-06-07 08:00 |  |  | Attended site and signed in. Completed JSA. Got escorted through site to locations of faulty light fittings. Supply and replace with new tubes and starters to faulty lights. Tested all okay. Signed out. Job complete
MSA-DFES | WA5514083 | 2 | SONTEC WA PTY LTD | Car Park - Boom Gate - Issues with carpark boom gate - See notes below | Security | Access Control | 230 | Pass | Pass | 0 | 0 | 0.33333 | 2022-06-14 15:36 | 2022-06-17 17:00 | 2022-06-17 16:00 | 2022-06-17 17:00 | 2022-06-17 16:20 |  |  | 17/6/22 - Dylan Parslow, Joshua ParkAdjusted relay unlock time for Go Doors.Boom gate working.
MSA-DFES | WA5522196 | 2 | Complete Pest Management Services | Ground Level - Kitchen - Cockroaches in cupboards - in pots and pans | Pest Control | General Pest | 254.55 | Pass | Pass | 0 | 0 | 0.33333 | 2022-06-15 13:20 | 2022-06-20 17:00 | 2022-06-20 14:40 | 2022-06-20 17:00 | 2022-06-20 15:00 |  |  | Inspected and treated for cockroaches
MSA-DTAG | WA5565218 | 1 | Bullant Security Pty Ltd | Custody – Control Room - Control room door handle is broken | Security | Locksmith | 264 | Pass | Pass | 0 | 0 | 0.33333 | 2022-06-21 15:01 | 2022-06-22 17:00 | 2022-06-21 15:55 | 2022-06-22 17:00 | 2022-06-21 16:15 |  |  | Attended site, replaced internal lever on control room door.Date on site: 21/06/2022Time on site: 15:55 - 16:15
MSA-DFES | WA5583597 | 1 | ADVANCED LOCK & KEY | ICV Shed - code lock on external door has failed | Security | Locksmith | 485 | Pass | Pass | 0 | 0 | 0.33333 | 2022-07-04 13:21 | 2022-07-05 17:00 | 2022-07-05 11:55 | 2022-07-05 17:00 | 2022-07-05 12:15 |  |  | Replaced broken/weather/ant damaged digital 530 on icv shed
MSA-DTAG | WA5585364 | 2 | Water2water Pty Ltd | L12 kitchen-Lights flashing on billi unit on the right side | Plumbing & Drainage | Water | 276.72 | Pass | Pass | 0 | 0 | 0.33333 | 2022-07-05 15:28 | 2022-07-08 17:00 | 2022-07-06 12:55 | 2022-07-08 17:00 | 2022-07-06 13:15 |  |  | Replaced expired filter.
MSA-DTWD | WA5675853 | 3 | ADVANCED LOCK & KEY | E204 - Door lock broken | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.33333 | 2022-07-22 14:38 | 2022-07-29 17:00 | 2022-07-25 09:40 | 2022-07-29 17:00 | 2022-07-25 10:00 |  |  | Lock working correctly - could be a key problem
MSA-DTWD | WA5780549 | 2 | Complete Pest Management Services | Multiple rodent droppings throughout workshop | Pest Control | General Pest | 339.09 | Pass | Pass | 0 | 0 | 0.33333 | 2022-08-19 11:32 | 2022-08-24 17:00 | 2022-08-24 14:00 | 2022-08-24 17:00 | 2022-08-24 14:20 |  |  | Inspected for rodents found evidence rodents installed 6 beta rodent bait stations
MSA-DCA | WA6046959 | 0 | TK Elevator Australia Pty Ltd | Linkway - Lift 3 - out of order, not opening | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 0.33333 | 2022-10-17 12:16 | 2022-10-17 14:16 | 2022-10-17 15:42 | 2022-10-17 16:16 | 2022-10-17 16:02 |  |  | Against door Spring without airport attached Further investigation required lift shut down And tagged out.
MSA-DTWD | WA6149366 | 2 | Swan Pest Control | A221a under roller service counter-It appears to be old white ant damage, please check | Pest Control | Specialist Pest | 95 | Pass | Pass | 0 | 0 | 0.33333 | 2022-11-04 14:32 | 2022-11-09 17:00 | 2022-11-08 08:00 | 2022-11-09 17:00 | 2022-11-08 08:20 |  |  | No activity was found only old damage
MSA-DFES | WA6383312 | 1 | Water2water Pty Ltd | Level 2 - Kitchen - 2 Zip taps not working. | Plumbing & Drainage | Water | 126.89 | Pass | Pass | 0 | 0 | 0.33333 | 2022-12-20 09:19 | 2022-12-21 17:00 | 2022-12-20 11:40 | 2022-12-21 17:00 | 2022-12-20 12:00 |  |  | Switch above bench had be isolated
MSA-DFES | WA6504011 | 3 | SONTEC WA PTY LTD | CCTV - C7 Camera - Garden - Feed blurry, please rectify | Security | Monitoring | 230 | Pass | Pass | 0 | 0 | 0.33333 | 2023-01-19 12:47 | 2023-01-27 17:00 | 2023-01-24 12:40 | 2023-01-27 17:00 | 2023-01-24 13:00
MSA-DFES | WA6516514 | 2 | Dom's Total Grounds Maintenance | Change room - Lawn sprinkler - not working properly | Landscaping & Gardening | Grounds Maintenance | 168 | Pass | Pass | 0 | 0 | 0.33333 | 2023-01-23 12:18 | 2023-01-27 17:00 | 2023-01-24 06:00 | 2023-01-27 17:00 | 2023-01-24 06:20
MSA-DTWD | WA6523029 | 2 | Swan Pest Control | Cockroach baits required | Pest Control | General Pest | 200 | Pass | Pass | 0 | 0 | 0.33333 | 2023-01-31 11:54 | 2023-02-03 17:00 | 2023-02-02 11:00 | 2023-02-03 17:00 | 2023-02-02 11:20
MSA-DTWD | WA6526591 | 2 | Swan Pest Control | Students kitchen - Rodents in cupboards and evidence of activity in the kitchen area | Pest Control | General Pest | 180 | Pass | Pass | -1 | -1 | 0.33333 | 2023-02-01 09:06 | 2023-02-06 17:00 | 2023-02-02 11:25 | 2023-02-06 17:00 | 2023-02-02 11:45
MSA-DFES | WA6601939 | 2 | ADVANCED LOCK & KEY | DOSS office - Comcen Training Room - Door latch connecting office and training room requires repair | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.33333 | 2023-02-17 10:47 | 2023-02-22 17:00 | 2023-02-21 10:45 | 2023-02-22 17:00 | 2023-02-21 11:05
MSA-DFES | WA6676142 | 2 | Securex Security Systems & Services | Engline Room Door - Pump sude strobe flashes red when door open not changing to green | Security | Monitoring | 160 | Fail | Fail | 1 | 1 | 0.33333 | 2023-02-28 11:53 | 2023-03-03 17:00 | 2023-03-09 08:10 | 2023-03-03 17:00 | 2023-03-09 08:30
MSA-DCA | WA5010465 | 2 | ADVANCED LOCK & KEY | Ground - Comms riser by stair 4 - Comms riser cannot be locked | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.33333 | 2022-01-12 14:48 | 2022-01-17 17:00 | 2022-01-14 12:35 | 2022-01-17 17:00 | 2022-01-14 12:55 |  |  | Open lock and service lock on comms riser. Completed.
MSA-DTWD | WA5209119 | 2 | Swan Pest Control | S Block - Level 1 - S109 - cockroach infestation in office | Pest Control | General Pest | 170 | Pass | Pass | 0 | 0 | 0.33333 | 2022-03-09 13:46 | 2022-03-14 17:00 | 2022-03-11 07:20 | 2022-03-14 17:00 | 2022-03-11 07:40 |  |  | Sprayed all office with 5 Litres Biflex Aqua
MSA-MRWA | WA5239834 | 0 | Dormakaba Australia Pty Ltd | EXT Rear sliding door in basement doesnt close. | Building | Materials | 320 | Fail | Pass | 0 | 0 | 0.33333 | 2022-03-16 21:45 | 2022-03-16 23:45 | 2022-03-16 23:50 | 2022-03-17 01:45 | 2022-03-17 00:10 |  |  | Inspected door and found that the access control was keeping the door open, removed connection to allow site to be secured and advised Brendan of the issue; we will possibly need to come back and terminate the cable once the access fault has been rectified.
MSA-DTWD | WA5394851 | 3 | Swan Pest Control | Creche Yard - Mosquito Issue - Staff have noticed more than usual mosquitos at P Block childcare | Pest Control | General Pest | 275 | Pass | Pass | 0 | 0 | 0.33333 | 2022-05-05 09:29 | 2022-05-12 17:00 | 2022-05-11 05:50 | 2022-05-12 17:00 | 2022-05-11 06:10 |  |  | Creche - sprayed all walls, ceilings and gazebo's with 60 Litres Bifrenthrin
MSA-DFES | WA5583717 | 2 | ADVANCED LOCK & KEY | Gym (out building) - security door will not latch or lock | Security | Locksmith | 215 | Pass | Pass | 0 | 0 | 0.33333 | 2022-07-04 14:15 | 2022-07-07 17:00 | 2022-07-07 15:35 | 2022-07-07 17:00 | 2022-07-07 15:55 |  |  | Replaced broken lock with new sd7 on gym sliding screen door
MSA-DCA | WA5611858 | 3 | ADVANCED LOCK & KEY | Ground - Security Office (rear loading dock entrance) - Fire door needs locked changed to master key | Security | Keys & Access | 180 | Pass | Pass | 0 | 0 | 0.33333 | 2022-07-14 09:56 | 2022-07-21 17:00 | 2022-07-18 11:50 | 2022-07-21 17:00 | 2022-07-18 12:10 |  |  | Rekeyed c4 oval cyl on fire control room door to their FD1 key
MSA-DFES | WA5974736 | 2 | Securex Security Systems & Services | Engine Bay - Entrance door located at the rear of the engine bay - See notes | Security | Keys & Access | 160 | Pass | Pass | 0 | 0 | 0.33333 | 2022-09-23 15:57 | 2022-09-29 17:00 | 2022-09-28 08:50 | 2022-09-29 17:00 | 2022-09-28 09:10 |  |  | 28/09/2022, 850-910Located door, push button type that no longer opens. Most likely that push button lock needs replacing and dooradjustment. Requires Locksmiths28/09/2022received confirmation to close job as it has been allocated to another trade
MSA-DTAG | WA6048902 | 2 | MALCO FLOORING PTY LTD | Ground-Registry-Loose carpet tile in registry entry threshold | Flooring | Carpet | 88.87 | Fail | Fail | 0 | 0 | 0.33333 | 2022-10-17 13:55 | 2022-10-20 17:00 | 2022-10-21 10:20 | 2022-10-20 17:00 | 2022-10-21 10:40 |  |  | REFIXED LOOSE CARPET TILE.
MSA-DFES | WA6207472 | 3 | ADVANCED LOCK & KEY | Ground - Male Staff Locker Room - Two lockers have broken locks. Locker #124 and #132 | Security | Locksmith | 220 | Pass | Pass | -1 | -1 | 0.33333 | 2022-11-17 11:53 | 2022-11-24 17:00 | 2022-11-18 14:05 | 2022-11-24 17:00 | 2022-11-18 14:25 |  |  | 14:05-14:25 Replaced two hafele cupboard locks
MSA-DFES | WA5287285 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Data Centre - Level 1 - see details below | Electrical | General Electrical | 68.255 | Pass | Pass | 0 | 0 | 0.31667 | 2022-03-22 11:34 | 2022-03-25 17:00 | 2022-03-25 12:32 | 2022-03-25 17:00 | 2022-03-25 12:51 |  |  | Onsite 1232 tested 2 off circuits that had tripped in sub board all test passed no faults found. signed out 1251
MSA-DCA | WA6130981 | 0 | Dormakaba Australia Pty Ltd | PICA-Main Building-Ground Floor - Glass auto doors stuck in the open position. | Building | Doors | 226.95 | Fail | Fail | 0 | 0 | 0.31667 | 2022-10-29 14:19 | 2022-10-29 16:19 | 2022-10-31 09:11 | 2022-10-29 18:19 | 2022-10-31 09:30 |  |  | Door working on arrival. On inspection, found that both external and internal key switch barrels are worn and very loose causing door to not be in selected mode.
MSA-MRWA | WA5295208 | 1 | Dormakaba Australia Pty Ltd | front admin - front auto door does not work | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.3 | 2022-03-29 11:49 | 2022-03-30 17:00 | 2022-03-29 13:07 | 2022-03-30 17:00 | 2022-03-29 13:25 |  |  | Found that the controller has completely failed, urgent quotation required to replace the old besam unit with an es200 locking unit, use all existing sensors and switches. Urgent
MSA-DCA | WA5791771 | 1 | Dormakaba Australia Pty Ltd | Epoch Café -ground-Glass doors both sides have faults-see notes | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.3 | 2022-08-23 09:26 | 2022-08-24 17:00 | 2022-08-23 13:41 | 2022-08-24 17:00 | 2022-08-23 13:59 |  |  | Doors had access control fault. Referred back to Noel.
MSA-DTWD | WA5534671 | 2 | Water2water Pty Ltd | zippy boil flashing showing no water | Plumbing & Drainage | HWS/Units Electric & Gas | 117.925 | Pass | Pass | 0 | 0 | 0.3 | 2022-06-16 13:03 | 2022-06-21 17:00 | 2022-06-20 09:00 | 2022-06-21 17:00 | 2022-06-20 09:18 |  |  | Water was turned off to property causing a fault on unit. Restarted and all ok.
MSA-DFES | WA5010359 | 3 | ADVANCED LOCK & KEY | Ground - Corridor - Admin building western exit door is not latching correctly when closing | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.28333 | 2022-01-12 12:57 | 2022-01-19 17:00 | 2022-01-14 14:18 | 2022-01-19 17:00 | 2022-01-14 14:35 |  |  | Tightened loose screw on exit door.
MSA-DTWD | WA5151006 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, Internal | 754.38 | Pass | Pass | -1 | -1 | 0.28333 | 2022-02-17 10:08 | 2022-02-22 17:00 | 2022-02-18 11:49 | 2022-02-22 17:00 | 2022-02-18 12:06 |  |  | Inspected lights out, sourced LED light fitting replacement to fit into ceiling grid. Returned to site, removed surface mount fluro light fittings and installed new LED panels into ceiling grid.
MSA-DFES | WA5305041 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Front admin building - Female toilets - fan had been tagged out and is not working | Electrical | General Electrical | 50.385 | Pass | Pass | 0 | 0 | 0.28333 | 2022-04-05 11:27 | 2022-04-08 17:00 | 2022-04-08 12:18 | 2022-04-08 17:00 | 2022-04-08 12:35 |  |  | Aos 1218 signed in and tested power point for fan all working OK informed by staff that hvac company already sourcing replacement fan. Signed out 1235
MSA-DTAG | WA5459814 | 0 | OCS SERVICES PTY LTD | Ground Floor - Registry - 2x areas – compliance & front counter supervisor - Covid Clean | Cleaning | Cleaning |  | Fail | Pass | 0 | 0 | 0.28333 | 2022-05-18 09:02 | 2022-05-18 11:02 | 2022-05-18 11:43 | 2022-05-18 13:02 | 2022-05-18 12:00 |  |  | Covid clean
MSA-MRWA | WA5487247 | 1 | TK Elevator Australia Pty Ltd | Elevator - Lift 4 - out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.28333 | 2022-06-01 13:32 | 2022-06-02 17:00 | 2022-06-01 15:45 | 2022-06-02 17:00 | 2022-06-01 16:02 |  |  | Car at level 6 with doors closed. Safety circuit open, found rope brake controller in fault state, 10 x led flash. Required 3 second reset operation to clear fault.Reset controller and checked operation. Unable to ascertain cause of rope brake controller fault.to be closed out at $0 cost
MSA-DTAG | WA5565776 | 3 | Sapio Pty Ltd | Level 6 - Room 609 - duress alarm is faulty | Security | Access Control | 200 | Pass | Pass | -1 | -1 | 0.28333 | 2022-06-22 11:12 | 2022-06-29 17:00 | 2022-06-22 11:13 | 2022-06-29 17:00 | 2022-06-22 11:30 |  |  | Replaced battery in Level 6, Room 609 duress alarm.
MSA-DTWD | WA5801385 | 1 | ECO PLUMBING AND GAS PTY LTD | Cleaners tap is leaking at compression fitting -See notes below | Plumbing & Drainage | Water | 186.98 | Fail | Fail | 0 | 0 | 0.28333 | 2022-08-31 16:06 | 2022-09-01 17:00 | 2022-09-02 17:00 | 2022-09-01 17:00 | 2022-09-02 17:17 |  |  | Installed new crimp back plated elbow
MSA-MRWA | WA6147754 | 2 | GPS Plumbing & Gas Services PtyLtd | Kitchenette-Hot Water unit leaking | Plumbing & Drainage | Water | 93.915 | Pass | Pass | -1 | -1 | 0.28333 | 2022-11-03 09:43 | 2022-11-08 17:00 | 2022-11-04 09:43 | 2022-11-08 17:00 | 2022-11-04 10:00 |  |  | Job assigned to the wrong contractor. Danika advised
MSA-DTWD | WA6158881 | 0 | Precise Air Group | AHU5 has stopped working | Air Conditioning | Room Air Conditioners | 152.03 | Pass | Pass | 0 | 0 | 0.28333 | 2022-11-10 09:47 | 2022-11-10 11:47 | 2022-11-10 10:46 | 2022-11-10 13:47 | 2022-11-10 11:03 |  |  | Attended site and signed in, spoke to facility manager about issue. Checked BMS system and found AHU5 in fault. Checked parameters of fan motor and found that the control system/VSD was providing abnormal Running Hz much higher than the set limit. Adjusted parameters and reset VSD for motor and ran back up. Found motor now stayed bellow the maximum Hz limit and was operating correctly. Recommend having controls contractors check operation of their system and see why problem occurred.
MSA-DFES | WA6249563 | 1 | Water2water Pty Ltd | second floor kitchen corporate service side -zip tap not working | Plumbing & Drainage | Water | 126.89 | Pass | Pass | 0 | 0 | 0.28333 | 2022-11-21 12:54 | 2022-11-22 17:00 | 2022-11-22 16:33 | 2022-11-22 17:00 | 2022-11-22 16:50 |  |  | Checked all units on level 2 as no faults, all working okay on depature
MSA-DTAG | WA5888343 | 1 | MARSHALL BEATTIE AUTOMATION | Basement - Magistrates Carpark - Entry Mechanical Sliding Gate - See notes below | Building | Steel Fencing & Gates | 130 | Pass | Pass | 0 | 0 | 0.28333 | 2022-09-16 16:10 | 2022-09-19 17:00 | 2022-09-19 07:16 | 2022-09-19 17:00 | 2022-09-19 07:33 |  |  | Paul Cullu.m (19/09/2022) - Work NoteInspection/test, gate operational, no faults found. Catch bracket ok
MSA-DTWD | WA6112320 | 1 | ECO PLUMBING AND GAS PTY LTD | E58 Large Scale Kitchen-Fault description Water leaking from faucet at restaurant dishwashing area | Plumbing & Drainage | Water | 168.03 | Pass | Pass | 0 | 0 | 0.28333 | 2022-10-21 16:20 | 2022-10-24 17:00 | 2022-10-24 13:11 | 2022-10-24 17:00 | 2022-10-24 13:28 |  |  | to cancel as incorrect site
MSA-DTAG | WA6379968 | 1 | Dormakaba Australia Pty Ltd | Ground - Courtroom 1 - public exit door into main area – green button release not responding | Building | Automatic Doors | 345 | Pass | Pass | 0 | 0 | 0.28333 | 2022-12-19 11:43 | 2022-12-20 17:00 | 2022-12-19 12:40 | 2022-12-20 17:00 | 2022-12-19 12:57 |  |  | On arrival, have been advised that this job has been allocated to Dormakaba by mistake. Job is intended for SAPIO. No works required.
MSA-DTAG | WA6383985 | 1 | Codee Cleaning Services | Ground custody-- Holding cell 2 (spit on camera, urine on walls/floor/door | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0.28333 | 2022-12-20 16:27 | 2022-12-21 17:00 | 2022-12-22 13:34 | 2022-12-21 17:00 | 2022-12-22 13:51 |  |  | completed 20/12/2022
MSA-DTWD | WA6527209 | 3 | LD TOTAL | External area - near B block - broken retic controller for pond | Plumbing & Drainage | Water | 434.47 | Pass | Pass | 0 | 0 | 0.28333 | 2023-02-01 09:05 | 2023-02-08 17:00 | 2023-02-07 10:09 | 2023-02-08 17:00 | 2023-02-07 10:26
MSA-DTAG | WA5207500 | 1 | Seme Solutions Pty Ltd | Keypads unresponsive upon code entry. Ongoing issue. (Possible warranty) - see note below | Security | Access Control | 130 | Fail | Fail | 0 | 0 | 0.26667 | 2022-03-08 13:27 | 2022-03-09 17:00 | 2022-03-10 11:56 | 2022-03-09 17:00 | 2022-03-10 12:12 |  |  | Contacted Site - Spoke to Veronica Fuller.Provided direction and assessed system status - noted alarm viewer had in excess of 150 un processed alarms. All of which were in active except 1 x door open too long which has been active since 3 March. Once all other alarms were cleared, tested keypad operation with client - Keypad responding and functioning correctly (no lag).Advised client that the un processed alarms were likely the cause of the lag. Advised site to contact me at end of the day when arming the system to confirm system was functioning as required.Advised client that alarms should be checked and cleared daily to avoid build up of issues.Advised client to log new job with PFM for the active door open too long alarm.Provided further phone support investigating cards that were "randomly" not working. Identified that access was being denied due to incorrect pin entry when cards were used - Veronica will follow up with cardholders.**all of the above information is pres
MSA-DCA | WA5301937 | 0 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Fail | Fail | 0 | 0 | 0.26667 | 2022-03-28 04:30 | 2022-03-28 06:30 | 2022-03-28 09:54 | 2022-03-28 08:30 | 2022-03-28 10:10 | 1 |  | EXTERNAL CHECK, ALL APPEARS SECURE, SECURITY COULD NOT GO INSIDE BASEMENTAREA BECAUSE KEY DID NOT WORK, CLEARED BY CRAIG FROM MONITORING.
MSA-DTAG | WA5324382 | 3 | Seme Solutions Pty Ltd | Multiple duress alarms unable to reset via Gallagher - see notes below | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.26667 | 2022-04-13 14:28 | 2022-04-22 17:00 | 2022-04-22 12:44 | 2022-04-22 17:00 | 2022-04-22 13:00 |  |  | The duress key had been wound past the stop pin so disassembled and removed key and reset the stop pin and reassembled and tested all perfect
MSA-DCA | WA5392641 | 2 | Dormakaba Australia Pty Ltd | HBRC Building - Ground Level - Reception - issues with self closing door - See notes below | Building | Automatic Doors | 235 | Pass | Pass | 0 | 0 | 0.26667 | 2022-05-03 11:06 | 2022-05-06 17:00 | 2022-05-04 07:48 | 2022-05-06 17:00 | 2022-05-04 08:04 |  |  | Found door closer plate connecting arm to frame had fallen off due to stripped fixing holes, re positioned arm plate and re fixed with new fixings, re fixed loose arm bolt and loose mag lock fixings, adjusted door speeds. Tested all ok
MSA-DCA | WA5018264 | 1 | Dormakaba Australia Pty Ltd | Ground - Stage Door/Roe Street Door - Internal stage door button release not working | Building | Automatic Doors | 35 | Pass | Pass | 0 | 0 | 0.26667 | 2022-01-14 10:25 | 2022-01-17 17:00 | 2022-01-14 12:29 | 2022-01-17 17:00 | 2022-01-14 12:45 |  |  | Inspected door and found that site are having issues with the release button behind the desk, inspected and found switch working fine, site had access tech out yesterday replacing a switch and so I guess they’ve disconnected something somewhere along the line. Advised site to call out access tech to rectify.
MSA-DCA | WA5417546 | 1 | ADVANCED LOCK & KEY | Disabled Toilet North Foyer - Lock Release mechanism has come loose from door - Is in FM Office | Security | Locksmith | 275 | Pass | Pass | 0 | 0 | 0.26667 | 2022-05-13 13:48 | 2022-05-16 17:00 | 2022-05-13 14:08 | 2022-05-16 17:00 | 2022-05-13 14:24 |  |  | Replaced lock missing parts with new austra mib lock on disable toilet 1x austra mib
MSA-DTWD | WA6249043 | 0 | Dormakaba Australia Pty Ltd | Level 1 - North Block - Garage door is going up and down -Car has driven into it | Building | Automatic Doors | 206.95 | Pass | Pass | 0 | 0 | 0.26667 | 2022-11-21 09:32 | 2022-11-21 11:32 | 2022-11-21 10:59 | 2022-11-21 13:32 | 2022-11-21 11:15 |  |  | Bottom rail had been hit by car bending it causing it to interfere with PE beams. Straightened Curtin and rectifed issue. All OK
MSA-DCA | WA6531279 | 0 | TK Elevator Australia Pty Ltd | Lift 5 - Button not working on Mezzanine Floor | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.26667 | 2023-02-03 10:50 | 2023-02-03 12:50 | 2023-02-03 12:25 | 2023-02-03 14:50 | 2023-02-03 12:41
MSA-DFES | WA5001236 | 2 | Water2water Pty Ltd | FRIST FLOOR - KITCHEN - Zip unit - no power to unit | Plumbing & Drainage | Water | 280.3775 | Pass | Pass | 0 | 0 | 0.25 | 2022-01-11 10:27 | 2022-01-14 17:00 | 2022-01-13 15:30 | 2022-01-14 17:00 | 2022-01-13 15:45 |  |  | Diagnosed and replaced faulty LCD Screen (error with time slip job took longer!) Promap not working on day. recalibrated unit tested working well A40189194P
MSA-DTWD | WA5069184 | 3 | AWB Co. | Spotlight out | Electrical | Lighting, External | 83.38 | Pass | Pass | 0 | 0 | 0.25 | 2022-01-19 16:26 | 2022-01-27 17:00 | 2022-01-27 14:45 | 2022-01-27 17:00 | 2022-01-27 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to lady at desk in C block about faulty spotlight. She took me to area. Turned all spotlights on. None appeared to be out/failed. Woman said she hadn’t noticed one out. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5080649 | 3 | Securex Security Systems & Services | Building 2 - Level 1 - Carpark Gate - Gate remote controls failed | Security | Access Control | 154.55 | Pass | Pass | -1 | -1 | 0.25 | 2022-01-20 08:20 | 2022-01-28 17:00 | 2022-01-21 10:15 | 2022-01-28 17:00 | 2022-01-21 10:30 |  |  | 21/01/2022, 1015-1030Issue resolved upon arrival apparently the power was turned off.
MSA-DTWD | WA5081125 | 2 | Schindler Lifts Australia | Lift not working | Lifts | Lifts |  | Fail | Fail | 4 | 4 | 0.25 | 2022-01-20 11:08 | 2022-01-25 17:00 | 2022-02-21 09:30 | 2022-01-25 17:00 | 2022-02-21 09:45 |  |  | to be closed out at $0 cost
MSA-DFES | WA5087357 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Fire Fighter Study - light has been tagged out and dont know why would like someone to check | Electrical | Lighting, Internal | 68.255 | Pass | Pass | 0 | 0 | 0.25 | 2022-01-24 08:46 | 2022-01-25 17:00 | 2022-01-24 09:45 | 2022-01-25 17:00 | 2022-01-24 10:00 |  |  | Attended site to investigate light switch that has been tagged out of service. Found light switch was tagged out as part of another job that is waiting on parts. Will need to return with parts to finish job. Notified staff and signed out.
MSA-DFES | WA5093938 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - damaged antenna lead or point and the television isn’t working. see notes | ICT/Audiovisual | General AV works | 50.385 | Pass | Pass | -1 | -1 | 0.25 | 2022-01-31 07:08 | 2022-02-04 17:00 | 2022-01-31 14:15 | 2022-02-04 17:00 | 2022-01-31 14:30 |  |  | Attended site 1415 to i estimate a faulty antenna outlet. Upon being shown the outlet, it was already changed last Friday 19/01/22, and was working as should. Staff on shift had not communicated that it had already been completed. Left site 1430.
MSA-DCA | WA5133094 | 2 | Wilson Security | RETROSPECTIVE WO - Jewellery shop - Request for security attendance | Security | Guards |  | Fail | Fail | 1 | 1 | 0.25 | 2022-02-05 08:00 | 2022-02-09 17:00 | 2022-02-15 14:15 | 2022-02-09 17:00 | 2022-02-15 14:30 | 1 |  | Completed
MSA-DFES | WA5151666 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen and officer’s toilet - Level 1 - See details below | Plumbing & Drainage | Drainage | 331.07 | Pass | Pass | 0 | 0 | 0.25 | 2022-02-17 15:36 | 2022-02-22 17:00 | 2022-02-22 08:45 | 2022-02-22 17:00 | 2022-02-22 09:00 |  |  | Replaced a mixer in kitchen and inlet valve in toilet and a new min stop and flexi hose
MSA-DTWD | WA5193730 | 3 | Swan Pest Control | D13 - Lots of red back spiders | Pest Control | General Pest | 200 | Pass | Pass | 0 | 0 | 0.25 | 2022-02-25 13:35 | 2022-03-04 17:00 | 2022-03-01 10:30 | 2022-03-04 17:00 | 2022-03-01 10:45 |  |  | Sprayed all plant room with Bifrenthrin @ .5%
MSA-DTWD | WA5204713 | 2 | M Construction (WA) | Paint House - faulty wooden door frame | Carpentry | Timber (all types) | 853.58 | Pass | Pass | -1 | -1 | 0.25 | 2022-03-04 12:44 | 2022-03-10 17:00 | 2022-03-04 12:45 | 2022-03-10 17:00 | 2022-03-04 13:00 |  |  | Attended site and inspected damaged frame. Spoke to Silvio and was told to remove damaged area and repair with a hardwood. Removed damaged area and installed Jarrah to frame. Painter requested to paint.
MSA-DTWD | WA5215408 | 1 | Equans Mechanical Services Australia | H-Block - HG01 - Compressor has stopped working – power supply seems to be OK | Equipment | Compressors, Generators | 57.56 | Pass | Pass | 0 | 0 | 0.25 | 2022-03-10 11:43 | 2022-03-11 17:00 | 2022-03-11 12:30 | 2022-03-11 17:00 | 2022-03-11 12:45 |  |  | JOB CANCELLED BY KELLY
MSA-MRWA | WA5239431 | 1 | SONTEC WA PTY LTD | Safety shower alarm is not turning off | Security | Security Management System | 230 | Pass | Pass | 0 | 0 | 0.25 | 2022-03-16 12:00 | 2022-03-17 17:00 | 2022-03-16 12:45 | 2022-03-17 17:00 | 2022-03-16 13:00 |  |  | 16/3/22 - Dylan ParslowShower alarm restored on arrival.
MSA-DFES | WA5287754 | 2 | Complete Pest Management Services | Ground - Information Resources Mail Area - Cockroaches - see notes | Pest Control | General Pest | 241.36 | Pass | Pass | 0 | 0 | 0.25 | 2022-03-22 15:33 | 2022-03-25 17:00 | 2022-03-24 12:30 | 2022-03-25 17:00 | 2022-03-24 12:45 |  |  | Inspected and treated envelopes cupboards with Rega slims am Chaindrite
MSA-DFES | WA5288791 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main Adminstration - Operational Delivery Office - see details below | Electrical | General Electrical | 68.255 | Pass | Pass | 0 | 0 | 0.25 | 2022-03-23 13:26 | 2022-03-30 17:00 | 2022-03-30 09:00 | 2022-03-30 17:00 | 2022-03-30 09:15 |  |  | Onsite 0900, signed in and shown to area. No flickering lights found at this time. Havementioned and suggest to staff onsite we can quote to replace the last 15 lights in thisarea to LED panels 1200x300, continued with other jobs onsite 0915.
MSA-DCA | WA5289602 | 1 | Earth & Water Pty Ltd | Urban Orchard - Ground – external - see details below | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 1 | 1 | 0.25 | 2022-03-24 11:09 | 2022-03-25 17:00 | 2022-03-30 16:50 | 2022-03-25 17:00 | 2022-03-30 17:05 |  |  | Retic leak in garden bed - Southside middle garden bed, to right of table
MSA-DCA | WA5306664 | 2 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2022-03-27 13:00 | 2022-03-30 17:00 | 2022-03-27 14:15 | 2022-03-30 17:00 | 2022-03-27 14:30 | 1 |  | Completed
MSA-DCA | WA5382175 | 1 | TK Elevator Australia Pty Ltd | Main building - Level 1 - Lift 1 - makes a rubbing noise between L1 and L2 | Lifts | Lifts |  | Fail | Fail | 4 | 4 | 0.25 | 2022-04-26 14:50 | 2022-04-27 17:00 | 2022-05-24 11:00 | 2022-04-27 17:00 | 2022-05-24 11:15 |  | WACCES | Lift 1 Art (large)-Geared :Call logged previously. Onsite technician (michael) did not allow entry to unit.As guide shoes have been identified as the cause of noise. Informed manager(Mark Rear). Left unit in service.to be closed out at no charges
MSA-DFES | WA5393982 | 2 | Securex Security Systems & Services | Entrance Hallway - Alarm Control Panel -Security Alarm reading Low battery | Security | Monitoring | 210 | Pass | Pass | -1 | -1 | 0.25 | 2022-05-04 11:34 | 2022-05-09 17:00 | 2022-05-05 11:15 | 2022-05-09 17:00 | 2022-05-05 11:30 |  |  | 05/05/2022, 1115-1130System is a Tecom v8 showing Ras fail and low battery.Replaced main battery and cleared Ras fail and battery fail all ok
MSA-DTWD | WA5394188 | 2 | OTIS ELEVATOR COMPANY PTY LTD | Kendrew- D-Block lift announcement telephone fault | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.25 | 2022-05-04 13:47 | 2022-05-09 17:00 | 2022-05-06 09:00 | 2022-05-09 17:00 | 2022-05-06 09:15 |  |  | TELEPHONE - LEAD - RUNNING ON ARRIVAL
MSA-DTAG | WA5394795 | 3 | Midolo Building Services | Level 5 - Court 51 - Faulty Chair - see notes below | Furniture | Office Furniture | 70.02 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-05 09:12 | 2022-05-12 17:00 | 2022-05-11 13:30 | 2022-05-12 17:00 | 2022-05-11 13:45 |  |  | re fixed chair to secure it & stopped the squeek
MSA-DTWD | WA5396322 | 1 | Critical Fire Protection & Training | Ground Level - Entrance - U-Block Fire pannel sounding, not in alarm but beeping continuously | Fire Protection Services | Fire Protection - Monitor System | 75.835 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-06 09:24 | 2022-05-09 17:00 | 2022-05-06 14:45 | 2022-05-09 17:00 | 2022-05-06 15:00 |  |  | Attended site to investigate fault/buzzer sounding on fire alarm sub panel in u-block on arrival found panel operating all systems normal however external bell and warning systems isolated. Viewed history log and found power fault logged 5/5/22. After speaking with security guard and confirming he had pushed buttons on fire panel. Concluded panel isolate reminder buzzer had initiated from isolates being inadvertently put on while on-site staff were acknowledging the power fault.
MSA-DTAG | WA5396631 | 1 | SONTEC WA PTY LTD | Ground Level - Security Office - Security CCTV cameras continue to buffer - See notes below | Security | CCTV Surveillance | 230 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-06 10:32 | 2022-05-09 17:00 | 2022-05-06 14:15 | 2022-05-09 17:00 | 2022-05-06 14:30 |  |  | 6/5/22 - Dylan ParslowFound camera images still displaying with the screens lost displaying.Reset displays.Cameras working correctly.
MSA-DTAG | WA5399224 | 3 | Midolo Building Services | L5 Court 57 jury room - Door latch is broken | Building | Doors | 52.42 | Pass | Pass | -1 | -1 | 0.25 | 2022-05-09 19:17 | 2022-05-16 17:00 | 2022-05-11 13:15 | 2022-05-16 17:00 | 2022-05-11 13:30 |  |  | latch re fixed & repaired
MSA-DFES | WA5454799 | 2 | Go Doors | Ground Floor - lunch Room - see details below | Building | General Building | 310 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-17 14:42 | 2022-05-20 17:00 | 2022-05-20 14:00 | 2022-05-20 17:00 | 2022-05-20 14:15 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5460466 | 2 | Go Doors | Ground Floor - Training Room 1 - Auto Door showing error and not closing. | Building | Automatic Doors | 375 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-18 14:22 | 2022-05-23 17:00 | 2022-05-20 14:15 | 2022-05-23 17:00 | 2022-05-20 14:30 |  |  | Please see attachments.
MSA-DTAG | WA5473510 | 2 | Bullant Security Pty Ltd | Custody - Sallyport - Lock on gunsafe faulty - Lock keeps jamming when trying to lock/unlock | Security | Locksmith | 125 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-24 16:11 | 2022-05-27 17:00 | 2022-05-25 12:20 | 2022-05-27 17:00 | 2022-05-25 12:35 |  |  | Attended site, viewed door and locking mechanism is working fine. Door is bent and have recommended it gets replace. To be forwared onto another trade.Date on site: 25/2/2022Time on site: 12:20 - 12:35
MSA-DTWD | WA5478271 | 2 | Water2water Pty Ltd | Room AT228 - Chilled/boiling water unit needs maintenance/filter change warning lights flashing | Plumbing & Drainage | HWS/Units Electric & Gas | 245.9375 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-26 10:34 | 2022-05-31 17:00 | 2022-05-31 09:55 | 2022-05-31 17:00 | 2022-05-31 10:10 |  |  | Filter replacement required only. Changed and all ok.
MSA-DFES | WA5488747 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | RETROSPECTIVE WORK ORDER - Ground - Mens change rooms - lights faulty - locations below | Electrical | General Electrical | 24.855 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-30 15:45 | 2022-06-02 17:00 | 2022-06-02 08:00 | 2022-06-02 17:00 | 2022-06-02 08:15 | 1 |  | Attended site and replaced blown light
MSA-DTWD | WA5493489 | 1 | Securex Security Systems & Services | Ground - A Block - Alarm panels beeping DGP tamper Code 1 | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 0.25 | 2022-06-07 08:40 | 2022-06-08 17:00 | 2022-06-07 11:15 | 2022-06-08 17:00 | 2022-06-07 11:30 |  |  | Iain McGillemhaoil (07/06/2022, 1115-1130) - Work NoteDgp 16 showing tamper, refitted lid and cleared alarm
MSA-DCA | WA5493875 | 1 | Wilson Security | Retrospective WO for security call out for 21/05/2022 07:26 | Security | Guards |  | Pass | Pass | 0 | 0 | 0.25 | 2022-05-21 07:15 | 2022-05-23 17:00 | 2022-05-21 07:30 | 2022-05-23 17:00 | 2022-05-21 07:45 | 1 |  | Completed
MSA-DFES | WA5511848 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Workshop - Reception - Fluro lights in the reception in faulty | Electrical | Lighting, Internal | 86.315 | Pass | Pass | 0 | 0 | 0.25 | 2022-06-13 09:52 | 2022-06-16 17:00 | 2022-06-16 13:30 | 2022-06-16 17:00 | 2022-06-16 13:45 |  |  | Located faulty lights. Staff advised they would not like it to bright and only fix one tube. Replaced faulty tube and starter with new.
MSA-DFES | WA5513440 | 3 | Seme Solutions Pty Ltd | GROUND - Front Entrance - External gates - see notes below | Security | Access Control | 130 | Pass | Pass | -1 | -1 | 0.25 | 2022-06-14 10:22 | 2022-06-21 17:00 | 2022-06-15 08:13 | 2022-06-21 17:00 | 2022-06-15 08:28 |  |  | Keypad is operational and not beeping
MSA-DTWD | WA5562754 | 1 | Protek 24/7 Building & Maintenance | A Block courtyard area (between room A12 and A40) - roof leak | Roofing | Metal Roofing | 81.25 | Pass | Pass | 0 | 0 | 0.25 | 2022-06-20 09:31 | 2022-06-21 17:00 | 2022-06-20 11:45 | 2022-06-21 17:00 | 2022-06-20 12:00 |  |  | Braf submitted to complete required work Braf Declined
MSA-DFES | WA5569531 | 3 | Protek 24/7 Building & Maintenance | Radio Comms near male toilet - Skirting boards have termite damage - termites have been treated | Building | Internal Walls | 62.125 | Pass | Pass | -1 | -1 | 0.25 | 2022-06-27 15:32 | 2022-07-04 17:00 | 2022-06-30 14:15 | 2022-07-04 17:00 | 2022-06-30 14:30 |  |  | Inspect for termite damage to Skirting Board
MSA-DTWD | WA5574134 | 2 | Protek 24/7 Building & Maintenance | 1G20 roof - Water not draining from gutter | Roofing | Guttering | 62.125 | Fail | Fail | 0 | 0 | 0.25 | 2022-06-30 15:26 | 2022-07-05 17:00 | 2022-07-07 15:45 | 2022-07-05 17:00 | 2022-07-07 16:00 |  |  | BRAF Declined
MSA-DFES | WA5585430 | 3 | Seme Solutions Pty Ltd | Appliance Bay - Appliance bay alarm panel - see notes below | Security | Monitoring | 399.1 | Fail | Fail | 4 | 4 | 0.25 | 2022-07-05 17:01 | 2022-07-12 17:00 | 2022-08-11 13:15 | 2022-07-12 17:00 | 2022-08-11 13:30 |  | WACCES | Attended site, replaced Tecom V8 Challenger keypad (SEME stock).Tested operation of all buttons, operating correctly.
MSA-DTWD | WA5677361 | 1 | Casa Security Pty Ltd | M block - security panel showing no power in A block | Security | Security Management System | 164.56 | Pass | Pass | 0 | 0 | 0.25 | 2022-07-25 13:45 | 2022-07-26 17:00 | 2022-07-26 11:00 | 2022-07-26 17:00 | 2022-07-26 11:15 |  |  | M BLOCK - SECURITY PANEL SHOWING NO POWER IN A BLOCKMet Darren on site - advised job was for keypad in AdminThis keypad has been disconnected for months due to cable damage in the pits.Job was lodged without knowingAll ok
MSA-DCA | WA5677448 | 1 | GPS Plumbing & Gas Services PtyLtd | Level B2 - SU BOH accessible bathroom - Access toilet not emptying when flushed- bowl very full | Plumbing & Drainage | Toilets/Cisterns | 93.915 | Pass | Pass | 0 | 0 | 0.25 | 2022-07-25 14:36 | 2022-07-26 17:00 | 2022-07-26 12:20 | 2022-07-26 17:00 | 2022-07-26 12:35 |  |  | On arrival client said the toilet in now cleared.Checked and tested no fault found.
MSA-DFES | WA5677886 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Dorm 1 Room - Bed light repair - Bed nearest to window) Transformer to be replaced | Electrical | Lighting, Internal | 54.225 | Fail | Fail | 0 | 0 | 0.25 | 2022-07-26 08:14 | 2022-08-02 17:00 | 2022-08-05 14:15 | 2022-08-02 17:00 | 2022-08-05 14:30 |  |  | Arrived on site at 1415 to investigate faulty bedroom light. Located light in dorm 1 and discovered faulty Fluro.Replaced/reenergised and left site at 1430.
MSA-DFES | WA5682303 | 1 | Go Doors | ground floor - traning room passege - training passage door not opening or closing - auto | Building | Doors | 310 | Pass | Pass | 0 | 0 | 0.25 | 2022-07-29 08:11 | 2022-08-01 17:00 | 2022-07-29 13:15 | 2022-08-01 17:00 | 2022-07-29 13:30 |  |  | 29/07/2022 Keith KingFault Found: Attended site as per work request and found A106468 unresponsive due to UPS failureWork Completed: bypassed UPS as they have back up generator as per FM acknowledgement, tested all good
MSA-DTAG | WA5693049 | 1 | SONTEC WA PTY LTD | ground security office-Duress Alarm ongoing | Security | Security Management System | 230 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-04 08:55 | 2022-08-05 17:00 | 2022-08-04 10:15 | 2022-08-05 17:00 | 2022-08-04 10:30 |  |  | 4/8/22 - Dylan ParslowDuress fault fixed on arrival.
MSA-DTWD | WA5706910 | 0 | Securex Security Systems & Services | Security System - audio unable to turn off due to power outage - see notes below | Security | Security Management System | 260 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-11 14:23 | 2022-08-11 16:23 | 2022-08-11 15:50 | 2022-08-11 18:23 | 2022-08-11 16:05 |  |  | Time onsite 11/08/2022 350pm to 405pmAlarm sounding onsite.Found this is NOT the security alarm system, this is an alarm indicating that the emergency egress doors have beenopened and left open.Once door was closed alarm stopped ok
MSA-DFES | WA5715349 | 3 | Go Doors | Level 1 - SOC/MOC - Auto door on level 1 door seal coming away need to be reattached or replaced | Building | Automatic Doors | 310 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-12 13:55 | 2022-08-19 17:00 | 2022-08-17 11:45 | 2022-08-19 17:00 | 2022-08-17 12:00 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5749231 | 1 | ADVANCED LOCK & KEY | Career drop off door - lock is faulty, will not lock - station unsecured | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-17 08:44 | 2022-08-18 17:00 | 2022-08-17 15:45 | 2022-08-18 17:00 | 2022-08-17 16:00 |  |  | adjust strike plate on drop off
MSA-DTWD | WA5753069 | 2 | PEEL LOCK SERVICES PTY LTD | Level 1 - Fabrication area - Room b12 Door handle is broken, requires reparing/replacing | Security | Keys & Access |  | Pass | Pass | 0 | 0 | 0.25 | 2022-08-17 13:29 | 2022-08-22 17:00 | 2022-08-22 11:45 | 2022-08-22 17:00 | 2022-08-22 12:00 |  |  | Repairs to damaged locks
MSA-DFES | WA5761280 | 1 | Securex Security Systems & Services | Security Gate - Security auto gate not shutting correctly | Building | Steel Fencing & Gates | 160 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-18 07:50 | 2022-08-18 17:00 | 2022-08-18 15:45 | 2022-08-18 17:00 | 2022-08-18 16:00 |  |  | 18/08/2022, 1545-1600Gate issue, tried resetting it but no success. Gate is over closing and hitting pole on other side forcing it to move back.Needs movement adjusted by gate contractors.
MSA-DFES | WA5790655 | 1 | Securex Security Systems & Services | Back door to the radio comms building -Its not opening and no acess | Building | Doors | 160 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-22 09:46 | 2022-08-23 17:00 | 2022-08-22 13:30 | 2022-08-23 17:00 | 2022-08-22 13:45 |  |  | 22/08/2022, 1330-1345Door reader working ok. Door strike sticking and not releasing.Replacement required. Separate Locksmith attending.
MSA-DTWD | WA5793445 | 0 | Securex Security Systems & Services | duress alarm activated,- contact steve regarding process | Security | Security Management System | 210 | Fail | Fail | 0 | 0 | 0.25 | 2022-08-24 07:59 | 2022-08-24 09:59 | 2022-08-24 11:45 | 2022-08-24 11:59 | 2022-08-24 12:00 |  |  | 24/08/2022, 1145-1200System showing low battery not a duress alarm. Replaced battery and cleared ok.
MSA-DTAG | WA5795228 | 1 | Bullant Security Pty Ltd | Ground floor - Detention corridor door near echo chamber - Please see notes below | Security | Access Control | 125 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-25 09:53 | 2022-08-26 17:00 | 2022-08-25 11:20 | 2022-08-26 17:00 | 2022-08-25 11:35 |  |  | Attended site, electric strike has failed so will require a electrician to repair or replace. Lock is working fine.Date on site: 25/8/2022Time on site: 11:20 - 11:35
MSA-DTWD | WA5797587 | 3 | Water2water Pty Ltd | Billi not cooling water | Plumbing & Drainage | HWS/Units Electric & Gas | 103.425 | Pass | Pass | -1 | -1 | 0.25 | 2022-08-29 09:20 | 2022-09-05 17:00 | 2022-08-29 13:10 | 2022-09-05 17:00 | 2022-08-29 13:25 |  |  | Run water through system & checked - All okay.
MSA-DFES | WA5839225 | 2 | MALCO FLOORING PTY LTD | Kitchen - Lino lifting in two areas - water damage to skirting under AC | Flooring | Vinyl | 107.6 | Fail | Fail | 18 | 18 | 0.25 | 2022-09-09 10:31 | 2022-09-14 17:00 | 2023-01-17 09:45 | 2022-09-14 17:00 | 2023-01-17 10:00 |  |  | SITE VISITED AND INSPECTED WITH PERSON ON DUTY 17/01/2023. WORKS WERE COMPLETED PREVIOUSLY UNDER DIFFERENT WORK ORDER NUMBER AND NO WORKS WERE REQUIRED TO BE CARRIED OUT.
MSA-DTAG | WA5839737 | 3 | Midolo Building Services | Ground - Disabled Toilet - dial on the door handle says engaged even when the toilet is not in use | Building | Doors | 51.11 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-09 15:25 | 2022-09-16 17:00 | 2022-09-13 14:15 | 2022-09-16 17:00 | 2022-09-13 14:30 |  |  | lock adjusted to working order
MSA-DCA | WA5861462 | 3 | Critical Fire Protection & Training | Level 1 - Fire Panel - Fire Panel fault - System Power Supply - Negative earth ground - See notes | Fire Protection Services | Fire Protection - Monitor System | 25.325 | Pass | Pass | -1 | -1 | 0.25 | 2022-09-13 09:38 | 2022-09-20 17:00 | 2022-09-15 12:45 | 2022-09-20 17:00 | 2022-09-15 13:00 |  |  | On arrival to site found system operating normal. No faults, alarms or isolates present. Checked history logs and found 1x occurrence of earth fault from Friday 9/9/22 is most recent fault in log. Due to the nature of earth faults recommend site to monitor and confirm if earth fault re-occurs during wet weather and is identifying a potential leak. Unable to conduct any further fault finding as no faults on system during visit
MSA-DTWD | WA5887653 | 3 | AWB Co. | West Balcony -Investigate & Repair Leak from Library Balcony | Building | Ceiling | 92.805 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-16 09:05 | 2022-09-23 17:00 | 2022-09-20 12:45 | 2022-09-23 17:00 | 2022-09-20 13:00 |  |  | Will pass to appropriate trade, to be re allocated to water proofing company
MSA-DTAG | WA5970802 | 1 | Bullant Security Pty Ltd | L3-court 34-lock on entry door is loose | Security | Locksmith | 150.77 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-20 09:23 | 2022-09-21 17:00 | 2022-09-20 10:10 | 2022-09-21 17:00 | 2022-09-20 10:25 |  |  | Attended site, tightened court 34 cylinder retaining screw and serviced lock.Date on site: 20/9/2022Time on site: 10:10 - 10:25
MSA-DFES | WA5974697 | 2 | ADVANCED LOCK & KEY | Ground - Dining Area - Latch on the sliding door to the dining room is U/S. | Security | Locksmith | 262.58 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-23 15:18 | 2022-09-29 17:00 | 2022-09-27 11:20 | 2022-09-29 17:00 | 2022-09-27 11:35 |  |  | replaced broken 590 strike with new
MSA-DCA | WA5993361 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - Security Call out 27/09/2022 due to unsecure door. -DO NOT ATTEND | Security | Security Management System |  | Fail | Fail | 1 | 1 | 0.25 | 2022-09-27 05:00 | 2022-09-27 17:00 | 2022-10-05 10:15 | 2022-09-27 17:00 | 2022-10-05 10:30 | 1 |  | Completed
MSA-DCA | WA5994020 | 1 | Wilson Security | Retrospective WO – no need to send contractor - See notes below | Security | Monitoring |  | Fail | Fail | 2 | 2 | 0.25 | 2022-10-01 11:55 | 2022-10-03 17:00 | 2022-10-15 12:45 | 2022-10-03 17:00 | 2022-10-15 13:00 | 1 |  | Completed
MSA-DTWD | WA5998020 | 2 | MR POTHOLE | There are 3 potholes on the road leading up to car parks 5, 6 & 7 | Paving & Roadworks | Concreting |  | Fail | Fail | 2 | 2 | 0.25 | 2022-10-07 11:28 | 2022-10-12 17:00 | 2022-10-24 14:15 | 2022-10-12 17:00 | 2022-10-24 14:30 |  |  | Potholes repairs
MSA-DCA | WA6001151 | 1 | TK Elevator Australia Pty Ltd | RETROSPECTIVE WORK ORDER - Lift 2 stopped-INV ONLY DO NOT ATTEND | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0.25 | 2022-10-07 07:00 | 2022-10-07 17:00 | 2022-10-10 13:15 | 2022-10-07 17:00 | 2022-10-10 13:30 | 1 |  | to be closed out at no charge as inv 8067165262 was generated and has been credited
MSA-DTWD | WA6007405 | 3 | ADVANCED LOCK & KEY | Key getting stuck in lock | Security | Locksmith | 160 | Pass | Pass | -1 | -1 | 0.25 | 2022-10-11 07:50 | 2022-10-17 17:00 | 2022-10-12 10:15 | 2022-10-17 17:00 | 2022-10-12 10:30 |  |  | tighten loose cam screws on oval cyl on A121 West entry door
MSA-DTWD | WA6020512 | 2 | AHS Services WA Pty Ltd (Anchor) | L2-Hand basin flick mixer tap loose on basin, tap rotates.- see notes | Plumbing & Drainage | Water | 126.6875 | Pass | Pass | -1 | -1 | 0.25 | 2022-10-13 13:26 | 2022-10-18 17:00 | 2022-10-14 12:30 | 2022-10-18 17:00 | 2022-10-14 12:45 |  |  | Located locking nut and tightened
MSA-DCA | WA6021852 | 2 | TK Elevator Australia Pty Ltd | Lift in Assembly Area-Button is getting progressively harder to push in and a bit stuck-see notes | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.25 | 2022-10-14 11:13 | 2022-10-19 17:00 | 2022-10-14 11:45 | 2022-10-19 17:00 | 2022-10-14 12:00 |  |  | Lift1 HMT-Elevator > MR > Geared :Ground floor landing call button has deteriorated and backing module broken. Able to make temp repair but has to be handled gently until replaced. Require Dewhurst C3 UP button with silver face.To be closed out at $0 cost
MSA-DCA | WA6109212 | 1 | Quality Pest & Weed Solutions PTY LTD | Rear of State Library-Bees on tree, please remove. | Pest Control | General Pest |  | Pass | Pass | 0 | 0 | 0.25 | 2022-10-20 15:19 | 2022-10-21 17:00 | 2022-10-20 17:00 | 2022-10-21 17:00 | 2022-10-20 17:15 |  |  | Treatment of bee's
MSA-DTWD | WA6113462 | 3 | Critical Fire Protection & Training | D214-Reset smoke detector and de isolate zone - after fire alarm triggered | Fire Protection Services | Smoke and Heat Detection | 25.325 | Pass | Pass | -1 | -1 | 0.25 | 2022-10-24 11:49 | 2022-10-31 17:00 | 2022-10-24 12:00 | 2022-10-31 17:00 | 2022-10-24 12:15 |  |  | Whilst onsite, Dave advised that on Friday students were making popcorn and set a smoke detector off.They isolated the panel and needed the smoke detector reset and deisolation of the zone.
MSA-DCA | WA6157385 | 1 | Wilson Security | Retrospective Work Order - INTERNAL AND EXTERNAL CHECK ALL APPEARS SECURE | Security | Guards |  | Pass | Pass | 0 | 0 | 0.25 | 2022-10-22 14:00 | 2022-10-24 17:00 | 2022-10-22 15:30 | 2022-10-24 17:00 | 2022-10-22 15:45 | 1 |  | Completed
MSA-DCA | WA6159272 | 1 | Wilson Security | RETROSPECTIVE no need to send contractor - U Block - see notes | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2022-10-30 12:15 | 2022-10-31 17:00 | 2022-10-30 12:30 | 2022-10-31 17:00 | 2022-10-30 12:45 | 1 |  | Completed
MSA-DTWD | WA6231126 | 2 | AWB Co. | B2204-Fault description See attached photos Fluorescents x 2 units. Not switching on. Tubes replace | Electrical | Lighting, Internal | 74.6125 | Pass | Pass | 0 | 0 | 0.25 | 2022-11-18 13:45 | 2022-11-23 17:00 | 2022-11-23 10:15 | 2022-11-23 17:00 | 2022-11-23 10:30 |  |  | Wrong work order do not bill Murdoch tafeworks attended - advised on site work order should of been cancelled as per work note
MSA-DCA | WA6293862 | 1 | Wilson Security | Retrospective Work Order - security call out for 26/11/2022 08:12 - see notes below | Security | Guards |  | Pass | Pass | 0 | 0 | 0.25 | 2022-11-26 08:00 | 2022-11-28 17:00 | 2022-11-26 08:15 | 2022-11-28 17:00 | 2022-11-26 08:30 | 1 |  | Completed
MSA-DCA | WA6360207 | 2 | TK Elevator Australia Pty Ltd | Level 1 - Lift 7 - Light in lift machine room requires new fluorescent tube and guarding on the unit | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.25 | 2022-12-07 09:34 | 2022-12-12 17:00 | 2022-12-07 11:15 | 2022-12-12 17:00 | 2022-12-07 11:30 |  |  | Lift7 Greem Rm-Elevator > MR > Hydraulic :Lift room lights: 1 led light working and has cover.Fluro fitting, 1 fluro missing and the other fluro tube blown. Replaced 2x fluro t5 4 foot.Tried to loction gaurding/cover in motor room, couldn't find it.Suggest to replaced the fluro fitting as it is starting to crumble and disintergrate.Closed at $0 cost.
MSA-DCA | WA6364108 | 2 | Property Fire Maintenance | Fire Escape Door between BOH & FOH near stairs - hinge falling off the door | Building | Fire Door |  | Pass | Pass | 0 | 0 | 0.25 | 2022-12-12 09:40 | 2022-12-15 17:00 | 2022-12-12 12:30 | 2022-12-15 17:00 | 2022-12-12 12:45 |  |  | Closed out at $0
MSA-DTWD | WA6365482 | 2 | Australian Airconditioning Services Pty Ltd | Aircon - not working | Air Conditioning | Ducted Split System | 88.77 | Pass | Pass | 0 | 0 | 0.25 | 2022-12-13 09:54 | 2022-12-16 17:00 | 2022-12-15 08:00 | 2022-12-16 17:00 | 2022-12-15 08:15 |  |  | Waiting on parts. Refer to WA6360823
MSA-DTWD | WA6366133 | 0 | Casa Security Pty Ltd | Alarm Panel is in fault | Security | Monitoring | 342.5 | Pass | Pass | 0 | 0 | 0.25 | 2022-12-13 16:07 | 2022-12-13 18:07 | 2022-12-13 17:15 | 2022-12-13 20:07 | 2022-12-13 17:30 |  |  | TECHNICIAN IDENTIFED BLOCKED ZONES IN "CHECK" CONDITIONDELETED ZONES TO ENABLE ARMING OF PARTITIONSWILL NEED TO RETURN FOR FOLLOW UP MAINTENANCETO IDENTIFY THE LOCATION OF ZONES 54 & 68, PARTITION 1THESE ZONES NEED TO BE SORTED OUT AS ONE OR MORE HAVE AN RF FAULT** HAVE ATTACHED A BREAKDOWN REPAIR AUTHORISATION REQUEST FOR US TO RETURN FOR FURTHER TESTING REQUIRED RE THE RF FAULT - WILL CHECK THE WIRELESS RANGE FOR THE DEVICES THAT WERE IN FAULT
MSA-DTAG | WA6376484 | 3 | Midolo Building Services | Level 3 - Male public toilets (st georges terrace) - Yellow staining on wall & ceiling | Building | Internal Walls | 24.21 | Fail | Fail | 3 | 3 | 0.25 | 2022-12-15 15:58 | 2022-12-22 17:00 | 2023-01-09 14:15 | 2022-12-22 17:00 | 2023-01-09 14:30 |  |  | INSPECTED STAINING - SITE TO PAINT
MSA-DCA | WA6381704 | 1 | Wilson Security | RETROSPECTIVE - no attendance required - Security fault | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2022-11-19 13:11 | 2022-11-21 17:00 | 2022-11-19 13:15 | 2022-11-21 17:00 | 2022-11-19 13:30 | 1 |  | Completed
MSA-DTAG | WA6393833 | 3 | Midolo Building Services | Level 9-Interview room 9.3-Very squeaky door | Building | Doors | 51.25 | Fail | Fail | 0 | 0 | 0.25 | 2022-12-29 10:42 | 2023-01-06 17:00 | 2023-01-09 11:45 | 2023-01-06 17:00 | 2023-01-09 12:00
MSA-DCA | WA6400610 | 1 | Wilson Security | Retrospective Work Order - Security alarm activated - see notes below | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0.25 | 2023-01-01 12:00 | 2023-01-03 17:00 | 2023-01-01 13:15 | 2023-01-03 17:00 | 2023-01-01 13:30 | 1
MSA-DCA | WA6400612 | 1 | Wilson Security | Retrospective Work Order - Security alarm activated - see notes below | Security | Monitoring |  | Fail | Fail | 0 | 0 | 0.25 | 2023-01-02 12:00 | 2023-01-03 17:00 | 2023-01-04 11:00 | 2023-01-03 17:00 | 2023-01-04 11:15 | 1
MSA-DCA | WA6401488 | 1 | Wilson Security | Retrospective Work Order - Security alarm activated - see notes below | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0.25 | 2023-01-02 15:00 | 2023-01-03 17:00 | 2023-01-02 16:30 | 2023-01-03 17:00 | 2023-01-02 16:45 | 1
MSA-DTAG | WA6403776 | 2 | Bullant Security Pty Ltd | Ground - Mitchell JA chambers - Lock broken | Security | Locksmith | 129.09 | Pass | Pass | 0 | 0 | 0.25 | 2023-01-06 16:11 | 2023-01-11 17:00 | 2023-01-09 12:45 | 2023-01-11 17:00 | 2023-01-09 13:00
MSA-DTWD | WA6404629 | 2 | Securex Security Systems & Services | Block G - Arming Panel - Low Battery Alarm G Block Zone 027 | Security | Security Management System | 229.09 | Pass | Pass | 0 | 0 | 0.25 | 2023-01-09 07:43 | 2023-01-11 17:00 | 2023-01-10 14:45 | 2023-01-11 17:00 | 2023-01-10 15:00
MSA-DFES | WA6517720 | 0 | Go Doors | rear of the FS-door is not latching into frame-keypad door | Building | Automatic Doors | 343.56 | Fail | Fail | 0 | 0 | 0.25 | 2023-01-24 11:56 | 2023-01-24 13:56 | 2023-01-26 14:15 | 2023-01-24 15:56 | 2023-01-26 14:30
MSA-DCA | WA6520433 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security - ATTENDED ON THE 7/1 | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2023-01-07 07:00 | 2023-01-09 17:00 | 2023-01-07 07:15 | 2023-01-09 17:00 | 2023-01-07 07:30 | 1
MSA-DTWD | WA6520455 | 1 | Complete Pest Management Services | External - Wasp nest in ceiling space outside door of room N14 | Pest Control | General Pest | 165.73 | Pass | Pass | 0 | 0 | 0.25 | 2023-01-27 14:48 | 2023-01-30 17:00 | 2023-01-30 11:00 | 2023-01-30 17:00 | 2023-01-30 11:15
MSA-DCA | WA6520466 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security Issue-DO NOT ATTEDN-see notes | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2023-01-17 12:15 | 2023-01-18 17:00 | 2023-01-17 17:00 | 2023-01-18 17:00 | 2023-01-17 17:15 | 1
MSA-DCA | WA6520507 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - See notes | Security | Guards |  | Pass | Pass | 0 | 0 | 0.25 | 2023-01-22 00:36 | 2023-01-23 17:00 | 2023-01-22 00:45 | 2023-01-23 17:00 | 2023-01-22 01:00 | 1
MSA-DFES | WA6537271 | 2 | Go Doors | Level 1 - State operation centre- media call centre- door fault | Building | Automatic Doors | 333.56 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-07 08:22 | 2023-02-10 17:00 | 2023-02-09 08:45 | 2023-02-10 17:00 | 2023-02-09 09:00
MSA-DFES | WA6579175 | 3 | Protek 24/7 Building & Maintenance | Bay 3 - vehicle electric charger cable - Jamming in track - see notes | Building | General Building | 63.69 | Pass | Pass | -1 | -1 | 0.25 | 2023-02-15 15:22 | 2023-02-22 17:00 | 2023-02-16 12:30 | 2023-02-22 17:00 | 2023-02-16 12:45
MSA-DFES | WA6654056 | 1 | ADVANCED LOCK & KEY | Bushfire Mitigation - External Door - Lock coming loose | Security | Locksmith | 160.7 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-21 09:19 | 2023-02-22 17:00 | 2023-02-21 10:05 | 2023-02-22 17:00 | 2023-02-21 10:20
MSA-DTAG | WA6668240 | 3 | Sapio Pty Ltd | Custody - Technician to attend 27/2/23 from 06:00am – reset monitors & cameras due to RCD testing | Security | Monitoring | 139.88 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-22 07:47 | 2023-02-28 17:00 | 2023-02-27 06:00 | 2023-02-28 17:00 | 2023-02-27 06:15
MSA-DTWD | WA6675922 | 1 | SCAVENGER SUPPLIES PTY LTD | Zone 4 - EWIS alarm beeping intermittently | Fire Protection Services | Fire Protection - Monitor System | 360.18 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-28 10:27 | 2023-03-01 17:00 | 2023-02-28 16:17 | 2023-03-01 17:00 | 2023-02-28 16:32
MSA-DFES | WA5001421 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Main Engine Bay - door number 2 red light is faulty | Electrical | General Electrical | 90.255 | Pass | Pass | 0 | 0 | 0.25 | 2022-01-11 12:05 | 2022-01-14 17:00 | 2022-01-11 13:45 | 2022-01-14 17:00 | 2022-01-11 14:00 |  |  | Arrived on site at 1345, Replaced globe in engine room door 2 light, left site at 1400
MSA-DTAG | WA5017397 | 1 | Bullant Security Pty Ltd | Ground - Courtroom 3 - door not locking | Building | Security Doors | 125 | Pass | Pass | 0 | 0 | 0.25 | 2022-01-13 13:46 | 2022-01-14 17:00 | 2022-01-14 08:30 | 2022-01-14 17:00 | 2022-01-14 08:45 |  |  | Attended site, lubricated lock and cylinder and made sure latch latches correctly.Date on site: 14/01/2022Time on site: 08:40am - 08:45am
MSA-DCA | WA5190841 | 0 | TK Elevator Australia Pty Ltd | Cafe Kitchen - dumb waiter is stuck with the fault light flashing | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.25 | 2022-02-24 15:17 | 2022-02-24 17:17 | 2022-02-24 16:09 | 2022-02-24 19:17 | 2022-02-24 16:24 |  |  | Back door hit by box when loading, causing lift to stop,opened door removed box,made back door switch,tested and left lift running
MSA-DFES | WA5203725 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Outside - HWS cold water relief valve is leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 202.03 | Pass | Pass | 0 | 0 | 0.25 | 2022-03-03 15:57 | 2022-03-09 17:00 | 2022-03-08 15:15 | 2022-03-09 17:00 | 2022-03-08 15:30 |  |  | Attended site for faulty cold water relief valve located the back of Fire Station on the left-hand side near the gym I have replaced the faulty cold water relief with new one after testing everything is working correctly cleaned up packed up
MSA-DCA | WA5306662 | 2 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2022-03-27 06:00 | 2022-03-30 17:00 | 2022-03-27 07:00 | 2022-03-30 17:00 | 2022-03-27 07:15 | 1 |  | Completed
MSA-DTAG | WA5307768 | 2 | SONTEC WA PTY LTD | Registry Counter - Plastic forked key snapped off in duress alarm unit | Security | Security Management System | 40 | Fail | Fail | 0 | 0 | 0.25 | 2022-04-07 16:20 | 2022-04-12 17:00 | 2022-04-14 12:15 | 2022-04-12 17:00 | 2022-04-14 12:30 |  |  | 14/4/22 - Dylan ParslowFixed registry duress and tested.No call out fee as already onsite.
MSA-DCA | WA5312245 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.25 | 2022-03-01 15:00 | 2022-03-02 17:00 | 2022-03-01 15:15 | 2022-03-02 17:00 | 2022-03-01 15:30 | 1 |  | Completed
MSA-DTAG | WA5379822 | 1 | SONTEC WA PTY LTD | Ground - Fire Door to Exterior Near Security Office - Faulty Electronic Lock | Security | Access Control | 225 | Pass | Pass | 0 | 0 | 0.25 | 2022-04-21 15:29 | 2022-04-22 17:00 | 2022-04-22 14:30 | 2022-04-22 17:00 | 2022-04-22 14:45 |  |  | 22/4/22 - Dylan ParslowFound input for keyswitch isolated in system.Deisolated and tested all ok.
MSA-DCA | WA5395575 | 1 | TK Elevator Australia Pty Ltd | DSATM Lift - LED safety strip in DSATM Lift is not working. Requires replacement for shows this week | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.25 | 2022-05-05 14:17 | 2022-05-06 17:00 | 2022-05-06 09:15 | 2022-05-06 17:00 | 2022-05-06 09:30 |  | WACCES | Strip requires replacementClosed out at $0 cost
MSA-DTAG | WA5399226 | 3 | Midolo Building Services | L9 Court 92 Door doesn’t close properly | Building | Doors | 70.02 | Pass | Pass | -1 | -1 | 0.25 | 2022-05-09 19:27 | 2022-05-16 17:00 | 2022-05-11 13:45 | 2022-05-16 17:00 | 2022-05-11 14:00 |  |  | eased & repaired door
MSA-DFES | WA5416777 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Dorm Ensuite -Firefighter Dorm 1 ensuite exhaust fan does not activate when sensor triggered | Equipment | Electrical Equipment | 24.855 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-13 08:15 | 2022-05-18 17:00 | 2022-05-18 14:30 | 2022-05-18 17:00 | 2022-05-18 14:45 |  |  | Works being completed under different work order
MSA-DTWD | WA5454590 | 2 | PEEL LOCK SERVICES PTY LTD | Admin Gate & Student Carpark Gate - Padlocks faulty | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.25 | 2022-05-17 12:33 | 2022-05-20 17:00 | 2022-05-19 12:15 | 2022-05-20 17:00 | 2022-05-19 12:30 |  |  | Repairs to lock
MSA-MRWA | WA5482304 | 1 | Automatic Fire Protection (ARA) | Basement - Fault on fire panel - See notes below | Fire Protection Services | Fire Protection - Monitor System | 75.835 | Pass | Pass | 0 | 0 | 0.25 | 2022-05-31 10:57 | 2022-06-01 17:00 | 2022-05-31 16:00 | 2022-06-01 17:00 | 2022-05-31 16:15 |  |  | Attended site and found zone 41 in alarm but was isolated. Reset alarm and deisolated zone as per Danika (programmed) advice. FIP normal
MSA-DCA | WA5493887 | 1 | Wilson Security | Retrospective WO for security call out for 21/05/2022 15:13 | Security | Guards |  | Pass | Pass | 0 | 0 | 0.25 | 2022-05-21 15:00 | 2022-05-23 17:00 | 2022-05-21 15:15 | 2022-05-23 17:00 | 2022-05-21 15:30 | 1 |  | Completed
MSA-DCA | WA5563342 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Track lighting is faulty and not working | Electrical | Lighting, Internal | 24.855 | Pass | Pass | 0 | 0 | 0.25 | 2022-06-20 14:04 | 2022-06-21 17:00 | 2022-06-21 09:15 | 2022-06-21 17:00 | 2022-06-21 09:30 |  | WACCES | Arrived on site at 07:00 to investigate track lighting on level 1 above function room entrance not working, found that Dali lighting feed comes from level 2 plant room controller. All parts of track have power tested these connections, removed 1 x fitting for bench testing at workshop as fittings faulty. Continued on site at 09:15
MSA-DCA | WA5567465 | 0 | Wilson Security | Retrospective WO - security call out | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0.25 | 2022-06-05 13:15 | 2022-06-05 15:15 | 2022-06-05 13:45 | 2022-06-05 17:15 | 2022-06-05 14:00 | 1 |  | PART INTERNAL CHECK, NO SIGN OF FORCED ENTRY COULD BE SEEN. SEAL CONFIRMEDBY MONITORING CARRY
MSA-DTWD | WA5585210 | 3 | Falcetta Plumbing and Gas | L1 male toilet-toilet bowl broken | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | -1 | -1 | 0.25 | 2022-07-05 13:30 | 2022-07-12 17:00 | 2022-07-07 13:45 | 2022-07-12 17:00 | 2022-07-07 14:00 |  | WACCES | inspect toilet, complete on different wo
MSA-DTWD | WA5585668 | 2 | Securex Security Systems & Services | Entry foyer-Duress Alarm button damaged | Security | Security Management System | 160 | Pass | Pass | 0 | 0 | 0.25 | 2022-07-06 07:14 | 2022-07-08 17:00 | 2022-07-08 13:00 | 2022-07-08 17:00 | 2022-07-08 13:15 |  |  | 08/07/2022, 1300-1315Refitted and deisolated zone 263
MSA-DFES | WA5727748 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Mens Toilet - light entry into toilet is faulty | Electrical | Lighting, Internal | 88.295 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-15 11:48 | 2022-08-16 17:00 | 2022-08-15 13:45 | 2022-08-16 17:00 | 2022-08-15 14:00 |  |  | Arrived on site at 1345 to attend Ground Floor - Mens Toilet - light entry into toilet is faulty. Located/replaced 1 x fluro, informed staff and left site at 1400.
MSA-DTAG | WA5794213 | 1 | AHS Services WA Pty Ltd (Anchor) | ACC Kitchen - Water leaking from Billi unit valve in staff kitchen | Plumbing & Drainage | HWS/Units Electric & Gas | 64.7575 | Pass | Pass | 0 | 0 | 0.25 | 2022-08-24 12:53 | 2022-08-25 17:00 | 2022-08-25 11:30 | 2022-08-25 17:00 | 2022-08-25 11:45 |  |  | .
MSA-DTAG | WA5838329 | 3 | MALCO FLOORING PTY LTD | Level 3-Drug Court lawyer room-Fault description Patch of carpet missing | Flooring | Carpet | 60.35 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-08 12:26 | 2022-09-15 17:00 | 2022-09-13 07:00 | 2022-09-15 17:00 | 2022-09-13 07:15 |  |  | LEVEL 3 DRUG COURT LAWYER OFFICE REFIXED CARPET TILE
MSA-DFES | WA5854217 | 2 | Securex Security Systems & Services | Watchroom - faulty security system - see notes below | Security | Monitoring | 210 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-12 14:31 | 2022-09-15 17:00 | 2022-09-13 16:45 | 2022-09-15 17:00 | 2022-09-13 17:00 |  |  | 13/09/2022, 1645-1700Replaced system back up battery. Reset low battery.
MSA-DFES | WA5978398 | 1 | Securex Security Systems & Services | Low battery alarm keeps activating every 5-10 minutes | Security | Security Management System | 210 | Pass | Pass | 0 | 0 | 0.25 | 2022-09-28 10:33 | 2022-09-29 17:00 | 2022-09-28 14:50 | 2022-09-29 17:00 | 2022-09-28 15:05 |  |  | 28/09/2022, 1450-1505Replaced system backup battery
MSA-DCA | WA5994965 | 1 | Wilson Security | Retrospective breakdown, no need to send contractor - Security Callout – 01/10/2022 16.50 | Security | Monitoring |  | Fail | Fail | 5 | 5 | 0.25 | 2022-10-01 16:50 | 2022-10-03 17:00 | 2022-11-06 14:30 | 2022-10-03 17:00 | 2022-11-06 14:45 | 1 |  | Completed
MSA-DTAG | WA6145480 | 1 | Sapio Pty Ltd | Custody Area - Basement - Control Area - Workstation is offline - See notes | Security | Monitoring | 64.56 | Pass | Pass | 0 | 0 | 0.25 | 2022-11-02 12:14 | 2022-11-03 17:00 | 2022-11-02 12:15 | 2022-11-03 17:00 | 2022-11-02 12:30 |  |  | Rectified Jacques Workstation for Cell Calls. All okay.
MSA-DTWD | WA6231129 | 2 | AWB Co. | B2209-Fault description See attached photos Fluorescents x 2 units. Not switching on. Tubes replace | Electrical | Lighting, Internal | 23.9325 | Pass | Pass | 0 | 0 | 0.25 | 2022-11-18 14:03 | 2022-11-23 17:00 | 2022-11-23 10:00 | 2022-11-23 17:00 | 2022-11-23 10:15 |  |  | Wrong work order do not bill Murdoch tafeworks attended - advised on site work order should of been cancelled as per work note
MSA-DTWD | WA6257165 | 2 | LIGHTHOUSE LOCKSMITHS | Large Creche room - broken door mechanism | Building | Doors |  | Pass | Pass | -1 | -1 | 0.25 | 2022-11-24 12:28 | 2022-11-29 17:00 | 2022-11-24 14:30 | 2022-11-29 17:00 | 2022-11-24 14:45 |  |  | Repairs to lock
MSA-DTAG | WA6291489 | 1 | Seme Solutions Pty Ltd | Custody Sally Port -Sally Port Garage Door needs repairing - See Notes Below | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 0.25 | 2022-11-28 16:11 | 2022-11-29 17:00 | 2022-11-29 10:45 | 2022-11-29 17:00 | 2022-11-29 11:00 |  |  | Checked and found customer complaints about the roller gate of the sally port safety sensor problem. Wrong job to SEME. Should be Dorma or Marshall Beattie job.
MSA-DTAG | WA6292907 | 3 | Midolo Building Services | Magistrate Dewsbury Chamber-Reattach nameplate to the door | Building | Doors | 84 | Pass | Pass | -1 | -1 | 0.25 | 2022-11-29 14:17 | 2022-12-06 17:00 | 2022-11-30 10:00 | 2022-12-06 17:00 | 2022-11-30 10:15 |  |  | name plate re attached as requested
MSA-DTAG | WA6392140 | 2 | Midolo Building Services | Court 55 - Squeaky Door | Building | Doors | 51.25 | Fail | Fail | 1 | 1 | 0.25 | 2022-12-23 09:59 | 2022-12-30 17:00 | 2023-01-09 11:30 | 2022-12-30 17:00 | 2023-01-09 11:45 |  |  | DOOR LUBRICATED
MSA-DFES | WA6407390 | 2 | ADVANCED LOCK & KEY | Front Door - latch is falling out of the door, 1 screw has fallen out and doors jams | Building | Doors | 161 | Pass | Pass | 0 | 0 | 0.25 | 2023-01-10 08:37 | 2023-01-13 17:00 | 2023-01-12 10:45 | 2023-01-13 17:00 | 2023-01-12 11:00
MSA-DTWD | WA6504411 | 0 | ADVANCED LOCK & KEY | A Block West - Ground Floor - Fire Door cant be locked | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 0.25 | 2023-01-19 15:45 | 2023-01-19 17:45 | 2023-01-19 16:00 | 2023-01-19 19:45 | 2023-01-19 16:15
MSA-DCA | WA6527282 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - See notes | Security | Guards |  | Pass | Pass | 0 | 0 | 0.25 | 2023-01-31 17:32 | 2023-02-01 17:00 | 2023-01-31 18:15 | 2023-02-01 17:00 | 2023-01-31 18:30 | 1
MSA-DFES | WA6540735 | 2 | Dom's Total Grounds Maintenance | Solenoid leaking Doms - Grounds | Plumbing & Drainage | Water | 120 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-09 13:22 | 2023-02-14 17:00 | 2023-02-11 15:35 | 2023-02-14 17:00 | 2023-02-11 15:50
MSA-DTWD | WA6650420 | 1 | Critical Fire Protection & Training | main fire panel showing fault - Power Failure | Fire Protection Services | Fire Protection - Monitor System | 81.605 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-20 11:17 | 2023-02-21 17:00 | 2023-02-20 16:45 | 2023-02-21 17:00 | 2023-02-20 17:00
MSA-DTAG | WA6669023 | 1 | Bullant Security Pty Ltd | Irwin Street - External - Gas box - Barrell lock on gas box is loose | Security | Locksmith | 138.01 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-22 13:30 | 2023-02-23 17:00 | 2023-02-23 11:55 | 2023-02-23 17:00 | 2023-02-23 12:10
MSA-DTAG | WA6672385 | 2 | Bullant Security Pty Ltd | Old Court House Law Museum - Lock bent and unable to open | Security | Locksmith | 132.5 | Pass | Pass | 0 | 0 | 0.25 | 2023-02-23 16:11 | 2023-02-28 17:00 | 2023-02-27 12:15 | 2023-02-28 17:00 | 2023-02-27 12:30
MSA-DTAG | WA6693828 | 3 | AWB Co. | L5-court 51-Magistrates door bell in court 51 is not working | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 0.25 | 2023-03-10 15:14 | 2023-03-17 17:00 | 2023-03-15 07:45 | 2023-03-17 17:00 | 2023-03-15 08:00
MSA-DTWD | WA6106048 | 2 | ECO PLUMBING AND GAS PTY LTD | Toilet is blocked and water is overflowing from the toilet | Plumbing & Drainage | Toilets/Cisterns | 414.131 | Pass | Pass | 0 | 0 | 0.23333 | 2022-10-20 07:45 | 2022-10-24 17:00 | 2022-10-24 13:13 | 2022-10-24 17:00 | 2022-10-24 13:27 |  |  | Unblocked drain with jetter and put camera down drain to find 1.7m section of pipe holding water
MSA-DTWD | WA5682145 | 0 | SCAVENGER SUPPLIES PTY LTD | T Block fire pump alarm sounding | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Fail | Pass | 0 | 0 | 0.23333 | 2022-07-29 07:18 | 2022-07-29 09:18 | 2022-07-29 09:55 | 2022-07-29 11:18 | 2022-07-29 10:09 |  |  | Call out to fault 29/7/22. Arrived to find electric pump fault on panel and pump shed alarms activated. Cause seems to be due to a power failure form a storm cell in the early hours of the morning. The pump shed alarms reset and FIP reset and brought back online
MSA-DFES | WA5151686 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Recirculation Valve on hot water system not working efficiently - see details below | Plumbing & Drainage | HWS/Units Electric & Gas | 180.55 | Pass | Pass | 0 | 0 | 0.23333 | 2022-02-17 15:58 | 2022-02-22 17:00 | 2022-02-22 10:16 | 2022-02-22 17:00 | 2022-02-22 10:30 |  |  | Had to pull the circulating pump apart because something was blocking it
MSA-DCA | WA5308607 | 0 | Automatic Fire Protection (ARA) | First floor - Studio 2 - Fire alarms needs isolation to avoid setting them off to complete works ons | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 0.23333 | 2022-04-08 13:46 | 2022-04-08 15:46 | 2022-04-08 13:46 | 2022-04-08 17:46 | 2022-04-08 14:00 |  |  | Attended site at 7.30am 8/4/2022 to isolateReturned 1.30pm to deisolateIsolated zones 1 to 20 as per requestTarget start and Target finish are incorrectTarget Start:08-Apr-2022 15:45Target Finish:08-Apr-2022 17:45
MSA-DTAG | WA5093414 | 1 | GPS Plumbing & Gas Services PtyLtd | ground - Staff male toilet, first cubicle leaking on floor | Plumbing & Drainage | Water | 23.755 | Pass | Pass | 0 | 0 | 0.23333 | 2022-01-28 14:17 | 2022-01-31 17:00 | 2022-01-31 08:06 | 2022-01-31 17:00 | 2022-01-31 08:20 |  |  | Flushed toilets in female and male’s toilets several times. No issues found
MSA-DCA | WA5488726 | 3 | ADVANCED LOCK & KEY | Level 3 - Next to kitchenette, DBO -Key has snapped off and remains stuck inside the lock | Security | Locksmith | 218 | Pass | Pass | 0 | 0 | 0.23333 | 2022-06-02 15:24 | 2022-06-10 17:00 | 2022-06-07 13:10 | 2022-06-10 17:00 | 2022-06-07 13:24 |  |  | Removed broken key and cut a replacement LF31R1:10-2:201x LF31R
MSA-MRWA | WA6165640 | 1 | Schindler Lifts Australia | Basement - Lift 2 - Display is screen is showing loading sign and lift is beeping | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.23333 | 2022-11-11 08:11 | 2022-11-14 17:00 | 2022-11-11 13:19 | 2022-11-14 17:00 | 2022-11-11 13:33 |  |  | Works completed - close out at $0
MSA-DCA | WA6727480 | 1 | TK Elevator Australia Pty Ltd | Ground - Dumb waiter - not operational | Equipment | Catering Equipment |  | Pass | Pass | 0 | 0 | 0.23333 | 2023-03-15 13:25 | 2023-03-16 17:00 | 2023-03-15 14:10 | 2023-03-16 17:00 | 2023-03-15 14:24
MSA-DFES | WA5656169 | 3 | Anvil Doors | Engine Room - Retractable cord on engine room door 4 has been cut and not operable | Building | Automatic Doors | 2609 | Fail | Fail | 2 | 2 | 0.21667 | 2022-07-18 11:56 | 2022-07-25 17:00 | 2022-08-08 08:17 | 2022-07-25 17:00 | 2022-08-08 08:30 |  |  | Reel was replace by electrical technician. Technician determined Door 3 Motor needs to be replaced. Please see attached Quotation, signature slip BRAF and service reports for Replacement motor to bifold door # 3Bifold Door #3 Motor replaced, Please see Signature Slip, Service Report and 2x Images.
MSA-DCA | WA5177179 | 1 | TK Elevator Australia Pty Ltd | BAR - Dun waiter stuck stuck on level 1 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.2 | 2022-02-21 15:39 | 2022-02-22 17:00 | 2022-02-21 16:45 | 2022-02-22 17:00 | 2022-02-21 16:57 |  |  | L4 DW (Bar-Kitchen)-Dumbwaiter :Vfm fault arrived on site 16.30.Sign in at stage doir and get keys as Restaurant is closed until tomorrow morning.DW on bottom level with back inside door half open .Closed door and tested.Left at bottom floor.Return keys and sign out.
MSA-DCA | WA5253918 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.2 | 2022-01-15 15:00 | 2022-01-17 17:00 | 2022-01-16 13:34 | 2022-01-17 17:00 | 2022-01-16 13:46 | 1 |  | CONDUCTED PATROL OF THE AREAS IN ALARM, THIS IS A REPEAT ISSUE WITH THIS SITEHOWEVER I CAN SEE NO NOTICEABLE CAUSE FOR THE ALARM IN THESE AREAS,EXTERNAL PATROLS HAVE BEEN CONDUCTED DUE TO THE DERELICT NATURE OF THISSITE HOWEVER THERE APPEARS TO BE NO DAMAGE TO THE FENCELINES. THE SYSTEMHAS BEEN RESET HOWEVER IT IS LIKELY TO GO BACK INTO ALARM. EVERYTHING ELSELOOKS GREAT CLEARED OFFSITE BY JAMES
MSA-DCA | WA5572835 | 1 | OTIS ELEVATOR COMPANY PTY LTD | Public lift - Display arrows and floor numbers inside the lift are not displaying | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.2 | 2022-06-30 11:22 | 2022-07-01 17:00 | 2022-06-30 12:42 | 2022-07-01 17:00 | 2022-06-30 12:54 |  |  | On 30/06/2022 at 11:26 AM, Angelika - Programmed requested service on F12140 (Pass #1) at WA Maritime Museum Shipwreck Galleries, 47 Cliff Street. An Otis technician was dispatched at 30/06/2022 12:02 PM and arrived onsite at 30/06/2022 12:42 PM.The equipment returned to service by 30/06/2022 12:54 PM.The call-back was requested because: DISPLAY SCREEN NOT WORKING with call ID number 2846040. Customer Reference: WA5572835Upon arrival at site, the technician performed the following:HALL LANTERN FIXTURES - PRINTED CIRCUIT BOARD - COMPONENT COLLAPSED
MSA-DFES | WA5190113 | 1 | Water2water Pty Ltd | Second Floor - Zip tap unit is faulty | Plumbing & Drainage | Water | 96.1175 | Pass | Pass | 0 | 0 | 0.18333 | 2022-02-24 11:04 | 2022-02-25 17:00 | 2022-02-24 14:35 | 2022-02-25 17:00 | 2022-02-24 14:46 |  |  | There is an isolation switch above cupboard. Re set and all working ok?
MSA-DTWD | WA5215662 | 3 | AHS Services WA Pty Ltd (Anchor) | A block - Level 2 - Male Toilet - Male shower leaking | Plumbing & Drainage | Materials | 83.725 | Pass | Pass | -1 | -1 | 0.18333 | 2022-03-10 14:49 | 2022-03-17 17:00 | 2022-03-10 14:49 | 2022-03-17 17:00 | 2022-03-10 15:00 |  |  | Isolated water removed tapware to shower reseated and replaced washers.
MSA-DCA | WA5564785 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Retrospective Work Order - FCU8 Humidity alarm - value - 44.375 | Air Conditioning | Room Air Conditioners | 334.9 | Fail | Fail | 17 | 17 | 0.18333 | 2022-02-20 12:03 | 2022-02-20 14:03 | 2022-06-21 12:19 | 2022-02-20 16:03 | 2022-06-21 12:30 | 1 |  | Completed
MSA-DTWD | WA5693682 | 3 | AWB Co. | Passageway lights outside not working | Electrical | Lighting, External | 835.53 | Fail | Fail | 1 | 1 | 0.18333 | 2022-08-04 14:26 | 2022-08-11 17:00 | 2022-08-18 13:36 | 2022-08-11 17:00 | 2022-08-18 13:47 |  |  | Attended site and signed in. Completed JSA. Located lights outside office at block 10 not working. Found to be old light fittings and controlled by timer. Lights asked to be on a sensor so that the ladies and cleaners can see when the arrive in the dark. Supply and replace 3 x ceiling lights with 20w downlights. Supply and install 1 x sensor above switchboard to light up walkway area. Tested all okay. Signed out. Job complete
MSA-DTWD | WA6463498 | 1 | ECO PLUMBING AND GAS PTY LTD | H Block - Evap A/C have blocked water delivery pipe | Plumbing & Drainage | Drainage | 296.67 | Pass | Pass | 0 | 0 | 0.18333 | 2023-01-17 10:06 | 2023-01-18 17:00 | 2023-01-18 15:37 | 2023-01-18 17:00 | 2023-01-18 15:48
MSA-DCA | WA5217075 | 1 | Wilson Security | Retrospective WO - Already attended - DUNBAR CLEANERS ACCIDENTLY ACTIVATED ALARM | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.16667 | 2022-03-11 07:45 | 2022-03-11 17:00 | 2022-03-11 08:09 | 2022-03-11 17:00 | 2022-03-11 08:19 | 1 |  | EXTERNAL AND INTERNAL ALL APPEARS TO BE SECURES AND CORRECT ALL SITEFOUND OPEN OFFICES ARE OPEN STAFF WORKING AND ONE CONTRACTORS WORKINGBON 2 FLOOR UPDATE MONITORING, CLERED BY CRAIG
MSA-DCA | WA5286173 | 0 | ADVANCED LOCK & KEY | Office front door lock isn't latching and no power to the striker | Security | Locksmith | 172.5 | Pass | Pass | 0 | 0 | 0.16667 | 2022-03-21 13:06 | 2022-03-21 15:06 | 2022-03-21 14:45 | 2022-03-21 17:06 | 2022-03-21 14:55 |  |  | Changed electric strike to fail secure but there was no reading with the multimeter so believe it’s a power supply issue and told them they need to get their security people out.
MSA-DFES | WA5481568 | 3 | ADVANCED LOCK & KEY | Admin Building - Plant Room - Door not locking - seems to be jamming | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.16667 | 2022-05-30 14:31 | 2022-06-07 17:00 | 2022-05-31 12:50 | 2022-06-07 17:00 | 2022-05-31 13:00 |  |  | Checked out the door, lock was fine, hinges tighten up ever so slightly, serviced the lock but the door is rubbing badly on the frame and requires plaining.
MSA-DTWD | WA5570804 | 2 | AHS Services WA Pty Ltd (Anchor) | - E-Block SK1 R/H sink 4 leaking tap | Plumbing & Drainage | Water | 126.49 | Pass | Pass | 0 | 0 | 0.16667 | 2022-06-28 15:05 | 2022-07-01 17:00 | 2022-06-29 08:20 | 2022-07-01 17:00 | 2022-06-29 08:30 |  |  | Job completed
MSA-DTWD | WA5692193 | 1 | CAPS AUSTRALIA PTY LTD | U Block - C&J Workshop - Air compressor is not working - Compressor is required for classes | Equipment | Compressors, Generators |  | Pass | Pass | 0 | 0 | 0.16667 | 2022-08-03 11:13 | 2022-08-04 17:00 | 2022-08-03 13:04 | 2022-08-04 17:00 | 2022-08-03 13:14 |  |  | Darren called back to cancel job. Compressor started working again.
MSA-DTAG | WA6129174 | 1 | Sapio Pty Ltd | Card reader faulty lv21 lift lobby | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 0.16667 | 2022-10-27 11:57 | 2022-10-28 17:00 | 2022-10-27 14:00 | 2022-10-28 17:00 | 2022-10-27 14:10 |  |  | WA - Michael Tomlinson (27/10/2022) - Work NoteMet with Sue and attended to faulty card reader on Level 21. Replaced and all working okay.
MSA-DTWD | WA5287183 | 1 | PEEL LOCK SERVICES PTY LTD | Security gates padlocks - Padlocks damaged need replacing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.16667 | 2022-03-22 10:50 | 2022-03-23 17:00 | 2022-03-23 08:25 | 2022-03-23 17:00 | 2022-03-23 08:35 |  |  | Padlocks damaged on security gates
MSA-DFES | WA5294553 | 3 | ADVANCED LOCK & KEY | Sliding door from patio area - Sliding door lock mechanism is missing screws and falling out of door | Building | Doors | 146 | Pass | Pass | -1 | -1 | 0.16667 | 2022-03-29 07:24 | 2022-04-04 17:00 | 2022-03-30 08:40 | 2022-04-04 17:00 | 2022-03-30 08:50 |  |  | Replace missing screws to sliding door
MSA-DTWD | WA5105162 | 1 | ECO PLUMBING AND GAS PTY LTD | F block yard East - Water coming up through pavers from broken water pipe | Plumbing & Drainage | Water | 355.41 | Pass | Pass | 0 | 0 | 0.16667 | 2022-02-04 08:21 | 2022-02-07 17:00 | 2022-02-07 08:35 | 2022-02-07 17:00 | 2022-02-07 08:45 |  |  | Repaired burst pipe in F Block on 4/2/2022 and returned on 7/2/2022 to turn back water on, test pipe and backfill
MSA-DTWD | WA5174212 | 1 | PEEL LOCK SERVICES PTY LTD | B1 - Ground - B1 Classroom - The main entry door lock is Brocken and will not lock | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.16667 | 2022-02-21 07:38 | 2022-02-21 17:00 | 2022-02-21 13:30 | 2022-02-21 17:00 | 2022-02-21 13:40 |  |  | Job completed - replaced lock
MSA-DTWD | WA5287178 | 1 | PEEL LOCK SERVICES PTY LTD | Security gates padlocks - Padlocks damaged need replacing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.16667 | 2022-03-22 10:45 | 2022-03-23 17:00 | 2022-03-23 08:15 | 2022-03-23 17:00 | 2022-03-23 08:25 |  |  | Damaged padlock
MSA-DTAG | WA5308457 | 3 | O'Brien Glass With Care | Registry - Ground - Between Front Registry waiting area and Office entry - see details | Building | Doors |  | Pass | Pass | -1 | -1 | 0.16667 | 2022-04-08 12:12 | 2022-04-19 17:00 | 2022-04-13 09:00 | 2022-04-19 17:00 | 2022-04-13 09:10 |  |  | job completed - Site attendance onlyDoor was operational and not in need of maintenance
MSA-DTWD | WA5377870 | 1 | CONNECT SECURITY SYSTEMS | Alarm code fault | Security | Monitoring | 153.18 | Pass | Pass | 0 | 0 | 0.16667 | 2022-04-20 09:37 | 2022-04-21 17:00 | 2022-04-21 10:05 | 2022-04-21 17:00 | 2022-04-21 10:15 |  |  | Attended to re-enter in guards code
MSA-DTWD | WA5827588 | 3 | TW - Programmed Facility Management | TEST | Building | Internal Walls |  | Pass | Pass | -1 | -1 | 0.16667 | 2022-09-01 11:30 | 2022-09-08 17:00 | 2022-09-01 11:30 | 2022-09-08 17:00 | 2022-09-01 11:40 |  |  | Job completed
MSA-DTWD | WA5976888 | 3 | CONNECT SECURITY SYSTEMS | C5 Aroma Café Entrance-Faulty alarm key pad - see notes | Security | Security Management System | 255.97 | Pass | Pass | -1 | -1 | 0.16667 | 2022-09-27 12:03 | 2022-10-04 17:00 | 2022-09-30 14:05 | 2022-10-04 17:00 | 2022-09-30 14:15 |  |  | Replaced faulty RAS to C Block Cafe
MSA-DCA | WA6518017 | 1 | Precise Air Group | Air con leaking water causing hazard | Air Conditioning | Room Air Conditioners | 456.08 | Pass | Pass | 0 | 0 | 0.15 | 2023-01-24 15:34 | 2023-01-25 17:00 | 2023-01-25 10:03 | 2023-01-25 17:00 | 2023-01-25 10:12
MSA-DCA | WA4995700 | 2 | TK Elevator Australia Pty Ltd | Lift - Key selection switch does not operate correctly | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.15 | 2022-01-10 15:18 | 2022-01-13 17:00 | 2022-01-11 08:43 | 2022-01-13 17:00 | 2022-01-11 08:52 |  |  | Key switch operation working correctly, tried several times but could not fault.No charges
MSA-DCA | WA5116319 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 5 - Plantroom - ETS - Investigate heat reclaim VSD | Air Conditioning | Room Air Conditioners | 1798.5 | Fail | Fail | 7 | 7 | 0.15 | 2022-02-11 13:42 | 2022-02-14 17:00 | 2022-04-01 10:49 | 2022-02-14 17:00 | 2022-04-01 10:58 |  |  | Various works carried out by subcontractors to prevent further faults with chiller 4. Unable to run the chiller in heat reclaim mode at this stage until further works are carried out.
MSA-DTWD | WA5303966 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire Pump Shed - Contactors on jacking pump require replacement | Fire Protection Services | Fire Protection - Monitor System | 523 | Pass | Pass | 0 | 0 | 0.15 | 2022-04-04 13:36 | 2022-04-05 17:00 | 2022-04-05 15:10 | 2022-04-05 17:00 | 2022-04-05 15:19 |  |  | Main switchboard tripped and started pump. Attended 5/4/22
MSA-DTWD | WA5796312 | 2 | NEYLOR | 1st window right hand side blind is broken | Building | Curtains & Blinds | 150 | Fail | Fail | 4 | 4 | 0.15 | 2022-08-26 10:05 | 2022-08-31 17:00 | 2022-09-27 10:52 | 2022-08-31 17:00 | 2022-09-27 11:01 |  |  | Completed & invoiced
MSA-DFES | WA6383943 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - FF Toilet - Blocked sink and drain on FF Sink, Bathroom, Overflowing, not draining | Plumbing & Drainage | Drainage | 158.35 | Pass | Pass | 0 | 0 | 0.15 | 2022-12-20 15:35 | 2022-12-20 17:35 | 2022-12-20 16:21 | 2022-12-20 19:35 | 2022-12-20 16:30 |  |  | Attend site to investigate blocked basin drain in toilet room, on arrival found water not draining out of basin, removed trap and found trap to be clear but missing trap rubbers. Installed new trap rubbersand re filled sink, used hand plunger to clear blockage in drain line from basin to floor waste gully. Checked DG out side and found water running in to dig all good. Ran several loads of water down sinkto test, all, working correctly
MSA-DTWD | WA6401062 | 1 | ECO PLUMBING AND GAS PTY LTD | L Block - East wall - External upholstery - Water pipe next to external compressor (see notes) | Plumbing & Drainage | Water | 1196.69 | Fail | Fail | 2 | 2 | 0.15 | 2023-01-04 08:48 | 2023-01-05 17:00 | 2023-01-16 12:17 | 2023-01-05 17:00 | 2023-01-16 12:26
MSA-DCA | WA5215789 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidity alarm on Level 4 and the Centenary Galley | Building | Materials | 209 | Fail | Fail | 3 | 3 | 0.13333 | 2022-03-11 04:11 | 2022-03-11 06:11 | 2022-04-01 13:04 | 2022-03-11 08:11 | 2022-04-01 13:12 |  |  | Various works carried out by subcontractors to prevent further faults with the ETS. Unable to run the chiller 4 - state library in heat reclaim mode at this stage until further works are carried out. Various other contractor works are waiting to be carried out until WA Art Gallery can run in local mode.
MSA-DTWD | WA5838535 | 2 | ECO PLUMBING AND GAS PTY LTD | Toilet is possibly leaking | Plumbing & Drainage | Toilets/Cisterns | 265.584 | Pass | Pass | 0 | 0 | 0.13333 | 2022-09-08 14:25 | 2022-09-13 17:00 | 2022-09-13 08:09 | 2022-09-13 17:00 | 2022-09-13 08:17 |  |  | Put new washer in toilet in M block Unblocked drain in H block as instructed by Silvio whilst on site
MSA-DCA | WA5888138 | 1 | Techworks Plumbing | Geology building - Ground floor - Male Toilets - toilet constantly running | Plumbing & Drainage | Toilets/Cisterns | 239.02 | Pass | Pass | 0 | 0 | 0.13333 | 2022-09-16 13:21 | 2022-09-19 17:00 | 2022-09-16 13:22 | 2022-09-19 17:00 | 2022-09-16 13:30 |  |  | arrived on site and signed in at the security office.then we called and spoke to Neil he had a few things he wanted to show us, then we attended to the toilet to see why it was running we took the push button plate off the wall and removed the plastic flush button assembly straight away we could see that flush valve was getting jammed and not closing all the way so we loosened it up and applied grease to it so it could move freely without getting caught We reinstalled the cover plate and push button assembly and tested it a few times to make sure it was workingtoilet is working normally again and can be used cleaned up and left sitecompleted paperwork
MSA-DCA | WA5481615 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Lift no. 2 (Kitchen Lift) -Kitchen lift is not working, stopped on level 1 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.13333 | 2022-05-30 14:55 | 2022-05-31 17:00 | 2022-05-30 15:57 | 2022-05-31 17:00 | 2022-05-30 16:05 |  |  | Onsite at 1515, lift out of order on top floor with doors open and rope brake engaged, found uncontrolled movement device tripped, reset uncontrolled movement and rope brake. Tested operation, unable to reproduce fault. Left in service.
MSA-DTAG | WA5396728 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground - Various locations - covid clean - please see details below | Cleaning | Emergency Cleans | 500 | Fail | Fail | 2 | 2 | 0.13333 | 2022-05-06 11:08 | 2022-05-06 13:08 | 2022-05-23 12:02 | 2022-05-06 15:08 | 2022-05-23 12:10 |  |  | As per work order no# WA5396728.
MSA-DTWD | WA6394106 | 0 | Water2water Pty Ltd | Water fountain between Green skills and Main Building - D&E Block - Significant Water Leak | Plumbing & Drainage | Water | 150.355 | Fail | Fail | 0 | 0 | 0.13333 | 2022-12-28 13:03 | 2022-12-28 15:03 | 2022-12-30 08:03 | 2022-12-28 17:03 | 2022-12-30 08:11 |  |  | Retrospective work order we attended on 28.12.22 and on investigation these works require leak to be fixed on the Mains Water Line (not work we do) the original work order was then cancelled and 2 more reissued.
MSA-DCA | WA6522637 | 3 | SCAVENGER SUPPLIES PTY LTD | Ground floor - FIP - MSSB General Fire Alarm Parameters – the Control Room Computer shows a fault | Fire Protection Services | Fire Protection - Monitor System | 56.28 | Pass | Pass | -1 | -1 | 0.13333 | 2023-01-31 09:14 | 2023-02-07 17:00 | 2023-02-01 15:51 | 2023-02-07 17:00 | 2023-02-01 15:59
MSA-DCA | WA5099202 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - Level 4 - central evergy plant ETS system - fault - going into local mode | Air Conditioning | Building HVAC Maintenance (Major Plant) | 550 | Fail | Fail | 8 | 8 | 0.11667 | 2022-02-01 16:18 | 2022-02-02 17:00 | 2022-04-01 13:13 | 2022-02-02 17:00 | 2022-04-01 13:20 |  |  | Various works carried out by subcontractors to prevent further faults with the ETS. Unable to run the chiller 4 - state library in heat reclaim mode at this stage until further works are carried out. Further investigation is required into Chiller 4 heat recovery mode faults.Various other contractor works are waiting to be carried out until WA Art Gallery can run in local mode.
MSA-DTWD | WA5453273 | 3 | ADVANCED LOCK & KEY | South Block - Level 2 - Creche - Key snapped off in lock - cannot open door | Security | Locksmith | 175 | Pass | Pass | -1 | -1 | 0.11667 | 2022-05-17 09:42 | 2022-05-24 17:00 | 2022-05-18 13:24 | 2022-05-24 17:00 | 2022-05-18 13:31 |  |  | Removed broken key and cut 3x copies 3x lw10
MSA-DTAG | WA5511837 | 1 | Dormakaba Australia Pty Ltd | ground front entry doors incorrect opening times on doors, see notes | Building | Automatic Doors | 200 | Pass | Pass | 0 | 0 | 0.11667 | 2022-06-13 09:38 | 2022-06-14 17:00 | 2022-06-13 12:50 | 2022-06-14 17:00 | 2022-06-13 12:57 |  |  | Attended site and was informed by the clerk of courts Michelle that she requested Sapio as this is an access control issue and not a DormakabaWe are still charging call out as we were called to site, however no CBRA was done as we didn't perform any work.
MSA-DTAG | WA4993108 | 1 | Sapio Pty Ltd | ground - custody - Errors showing on CCTV cameras - see notes | Security | CCTV Surveillance | 130 | Pass | Pass | 0 | 0 | 0.11667 | 2022-01-07 09:33 | 2022-01-10 17:00 | 2022-01-07 14:40 | 2022-01-10 17:00 | 2022-01-07 14:47 |  |  | Found that one camera had dropped off line but had now come back. All cameras are online.
MSA-DTWD | WA5175138 | 1 | Precise Air Group | B106 -BMS is offline for AHUs 1, 2, 3 and 4 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 597.1 | Pass | Pass | 0 | 0 | 0.11667 | 2022-02-21 10:34 | 2022-02-22 17:00 | 2022-02-22 11:26 | 2022-02-22 17:00 | 2022-02-22 11:33 |  |  | Found that device 1- Genesis controller was ofline on the BMS (AHU 1-4).Reset the IG03 which communicates with the database.Device did not come back online.Attended Plantroom 1 and found Genesis controller in BMS Panel 1. Disconnectedpower from the VAV gateway and foundthat the controller re-built (very slowly).When the Gateway's power was reinstated and subsequently rebuilt the Genesis controller again dropped out.Iwas able to download logic out of the Genesis controller, though the net/global plug, at a good speed. I discovered that whereturned the Genesis' Controller net/global plug the device was able to re-build along side a connected Gateway.All devices are now connected through iComm and the BMS is healthy.Noting that while looking at this switchboard I found that the 160VA transformer is not supplying correct voltage to thecontrollers. I measured only about 22.1VAC. Advise replacement - controller issues can arise at low voltage levels.Likely issue with the Gateway
MSA-DTWD | WA5191900 | 1 | SCAVENGER SUPPLIES PTY LTD | Pump 1 jacking pump fault lights it showing. Alarm has been muted. Water/fuel on ground under pump. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) |  | Pass | Pass | 0 | 0 | 0.11667 | 2022-02-25 10:15 | 2022-02-28 17:00 | 2022-02-25 13:25 | 2022-02-28 17:00 | 2022-02-25 13:32 |  |  | Completed - 25/2/22 - Checking pump hose has slow leak tightened up hose leak has stopped covered under warranty """NO CHARGE-CLAIM SUBMITTED $0.00"
MSA-DTWD | WA5799847 | 2 | ECO PLUMBING AND GAS PTY LTD | 2nd cubicle toilet pan leaking | Plumbing & Drainage | Water | 106.57 | Pass | Pass | 0 | 0 | 0.11667 | 2022-08-30 15:02 | 2022-09-02 17:00 | 2022-09-02 15:59 | 2022-09-02 17:00 | 2022-09-02 16:06 |  |  | Installed new 50mm flush cone rubber
MSA-DTWD | WA5827815 | 2 | ECO PLUMBING AND GAS PTY LTD | No hot water at the sink & blocked drain at the same sink | Plumbing & Drainage | Water | 930.768 | Fail | Fail | 0 | 0 | 0.11667 | 2022-09-01 13:14 | 2022-09-06 17:00 | 2022-09-07 14:17 | 2022-09-06 17:00 | 2022-09-07 14:24 |  |  | Investigated hot water system found that tank has split and braf to be sent for new one Used drain machine to unblock sewer
MSA-DTWD | WA5862276 | 1 | ECO PLUMBING AND GAS PTY LTD | D Block - Female Staff Toilets - Both Toilets are blocked | Plumbing & Drainage | Toilets/Cisterns | 240.7 | Pass | Pass | 0 | 0 | 0.11667 | 2022-09-13 15:32 | 2022-09-14 17:00 | 2022-09-14 09:26 | 2022-09-14 17:00 | 2022-09-14 09:33 |  |  | Ran jetter down IO outside disbaled toilet and camera inspected after all is clear
MSA-DTWD | WA6377470 | 0 | ECO PLUMBING AND GAS PTY LTD | Leaking Pipe on the Roof of H Block - possible Evap Aircon | Plumbing & Drainage | Water | 152.03 | Fail | Fail | 1 | 1 | 0.11667 | 2022-12-16 16:27 | 2022-12-16 18:27 | 2022-12-22 07:47 | 2022-12-16 20:27 | 2022-12-22 07:54 |  |  | Investigated leak on roof, issue was box gutter full of leaves, cleaned and all draining away
MSA-DTWD | WA4992330 | 2 | ECO PLUMBING AND GAS PTY LTD | 2 x cisterns are leaking | Plumbing & Drainage | Toilets/Cisterns | 196.28 | Fail | Fail | 3 | 3 | 0.1 | 2022-01-06 10:14 | 2022-01-11 17:00 | 2022-02-01 10:35 | 2022-01-11 17:00 | 2022-02-01 10:41 |  |  | Serviced one toilet by replacing washer and inlet valve and inlet valve on other cistern
MSA-DTWD | WA5569018 | 2 | ECO PLUMBING AND GAS PTY LTD | A9 Male Toilets - Cubicle cistern - Faulty flush valve - Toilet not flushing at all | Plumbing & Drainage | Toilets/Cisterns | 385.51 | Pass | Pass | 0 | 0 | 0.1 | 2022-06-27 11:24 | 2022-06-30 17:00 | 2022-06-29 16:13 | 2022-06-30 17:00 | 2022-06-29 16:19 |  |  | Replaced cistern in A block male toilets
MSA-DTWD | WA5691942 | 1 | ECO PLUMBING AND GAS PTY LTD | Cleaners store water leaking from wall near the sink | Plumbing & Drainage | Water | 141.28 | Pass | Pass | 0 | 0 | 0.1 | 2022-08-03 09:12 | 2022-08-04 17:00 | 2022-08-03 13:53 | 2022-08-04 17:00 | 2022-08-03 13:59 |  |  | Investigated pooling water
MSA-DTWD | WA6109114 | 2 | ECO PLUMBING AND GAS PTY LTD | Room J100 - Low water pressure at wash trough taps in Workshop | Plumbing & Drainage | Water | 1244.23 | Pass | Pass | 0 | 0 | 0.1 | 2022-10-20 13:56 | 2022-10-25 17:00 | 2022-10-25 16:24 | 2022-10-25 17:00 | 2022-10-25 16:30 |  |  | Investigated hwu found low water pressure to be related to isolation need to send braf for new isolation for block and HWU
MSA-DTWD | WA6360724 | 1 | ECO PLUMBING AND GAS PTY LTD | Gated court yard near door U015 -repair or replace faulty water ball valve | Plumbing & Drainage | Water | 693.69 | Fail | Fail | 0 | 0 | 0.1 | 2022-12-07 13:32 | 2022-12-08 17:00 | 2022-12-08 18:19 | 2022-12-08 17:00 | 2022-12-08 18:25 |  |  | Installed new 25mm isolation valve
MSA-DFES | WA5462474 | 3 | Seme Solutions Pty Ltd | Duty Room - Swipe card access to key room is not working - access only possible by phone co | Security | Access Control | 130 | Fail | Fail | 1 | 1 | 0.1 | 2022-05-19 15:14 | 2022-05-26 17:00 | 2022-06-01 14:53 | 2022-05-26 17:00 | 2022-06-01 14:59 |  |  | Couldn’t resolve issue
MSA-DCA | WA6019846 | 2 | TK Elevator Australia Pty Ltd | Lift 4 – out of service – displaying overloaded | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.1 | 2022-10-13 08:46 | 2022-10-18 17:00 | 2022-10-13 13:14 | 2022-10-18 17:00 | 2022-10-13 13:20 |  |  | Lift stuck on ground floor doors closed. Power cycled controller, lift running.
MSA-DCA | WA6364047 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 - is into alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 600.53 | Fail | Fail | 1 | 1 | 0.1 | 2022-12-12 09:12 | 2022-12-12 11:12 | 2022-12-22 10:44 | 2022-12-12 13:12 | 2022-12-22 10:50 |  |  | Airvision to Attend site to investigate and repair chiller with intermittent fault.
MSA-DTWD | WA6539613 | 3 | AWB Co. | Toilets - Powerpoint in accessible toilet keeps tripping - contractor on site | Electrical | Lighting, Internal | 284.92 | Pass | Pass | -1 | -1 | 0.1 | 2023-02-08 14:44 | 2023-02-15 17:00 | 2023-02-08 14:44 | 2023-02-15 17:00 | 2023-02-08 14:50
MSA-DTWD | WA5128045 | 2 | SCAVENGER SUPPLIES PTY LTD | Room B8 - fire panel showing battery fault and smoke fault | Fire Protection Services | Fire Protection - Monitor System | 259.37 | Pass | Pass | 0 | 0 | 0.1 | 2022-02-14 15:35 | 2022-02-17 17:00 | 2022-02-17 08:48 | 2022-02-17 17:00 | 2022-02-17 08:54 |  |  | COMPLETED 16/02/2022
MSA-DTWD | WA5833404 | 3 | Australian Airconditioning Services Pty Ltd | heating cycle will not working | Air Conditioning | Room Air Conditioners | 392.74 | Fail | Fail | 2 | 2 | 0.094167 | 2022-09-06 08:00 | 2022-09-12 17:00 | 2022-09-29 10:31 | 2022-09-12 17:00 | 2022-09-29 10:37 |  |  | Reset unit and ran. Unit running ok, will monitor.Ran and tested unit and all ok.
MSA-DTWD | WA5454494 | 1 | ECO PLUMBING AND GAS PTY LTD | G13 Female Toilets - Toilets are blocked - Water overflowing | Plumbing & Drainage | Toilets/Cisterns | 190.99 | Pass | Pass | 0 | 0 | 0.083333 | 2022-05-17 11:50 | 2022-05-18 17:00 | 2022-05-17 15:39 | 2022-05-18 17:00 | 2022-05-17 15:44 |  |  | Used jetter to unblock female toilets in G block
MSA-DTWD | WA5793874 | 2 | ECO PLUMBING AND GAS PTY LTD | A12-blocked kitchen sink | Plumbing & Drainage | Drainage | 406.43 | Pass | Pass | -1 | -1 | 0.083333 | 2022-08-24 10:42 | 2022-08-29 17:00 | 2022-08-25 12:30 | 2022-08-29 17:00 | 2022-08-25 12:35 |  |  | Unblock drain in A12 and supply new air admittance valve
MSA-DTWD | WA5307221 | 3 | Equans Mechanical Services Australia | Block 7 - Ground - Freezer - Door seal faulty | Air Conditioning | Room Air Conditioners | 225 | Pass | Pass | -1 | -1 | 0.083333 | 2022-04-07 11:25 | 2022-04-14 17:00 | 2022-04-07 12:18 | 2022-04-14 17:00 | 2022-04-07 12:23 |  |  | Job raised as client raised a recall on previous job to repair hinge. Found lower part of adhesive sealing strip on door frame has worn out. Picked up parts from suppliers and returned to site. Removed old seal and installed new seal. Checked and found door now sealing correctly. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5377898 | 1 | CONNECT SECURITY SYSTEMS | Alarm code fault | Security | Monitoring | 153.18 | Pass | Pass | 0 | 0 | 0.083333 | 2022-04-20 09:54 | 2022-04-21 17:00 | 2022-04-21 09:52 | 2022-04-21 17:00 | 2022-04-21 09:57 |  |  | Reprog guard code
MSA-DCA | WA5495258 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - Ground Floor - Massive noise coming from plant room - See notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 188.375 | Fail | Fail | 1 | 1 | 0.083333 | 2022-06-08 10:25 | 2022-06-08 12:25 | 2022-06-13 14:05 | 2022-06-08 14:25 | 2022-06-13 14:10 |  |  | Investigated squeaky noise reported as coming from plant room. Checked all of plant and found no reported noises. Hot water pump on landing did start up and make a very quick squeak sound but stopped immediately. Suspect pump may have been cause but appears to have cleared itself. Stopped and started pump several times but no further unusual sounds found.
MSA-DTWD | WA5675571 | 0 | ECO PLUMBING AND GAS PTY LTD | toilets are blocked | Plumbing & Drainage | Toilets/Cisterns | 420.12 | Fail | Fail | 0 | 0 | 0.083333 | 2022-07-22 11:56 | 2022-07-22 13:56 | 2022-07-22 16:16 | 2022-07-22 15:56 | 2022-07-22 16:21 |  |  | Attempted using plunger to unblock no success Used drain machine to unblock female and disabled toilets
MSA-DFES | WA5827706 | 2 | AWB Co. | Door on Duty Room to Engine Room - Kickboard on door has come off - Needs re attachment | Building | General Building | 92.805 | Fail | Fail | 0 | 0 | 0.083333 | 2022-09-01 12:26 | 2022-09-06 17:00 | 2022-09-07 09:35 | 2022-09-06 17:00 | 2022-09-07 09:40 |  |  | Refix drop seal to door
MSA-DTAG | WA6020605 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Basement - Custody Area - Cell 2 - Require bio clean to cell 2 as PIC has urinated throughout cell | Cleaning | Emergency Cleans | 300 | Fail | Fail | 1 | 1 | 0.083333 | 2022-10-13 14:39 | 2022-10-13 16:39 | 2022-10-17 14:31 | 2022-10-13 18:39 | 2022-10-17 14:36 |  |  | As per Work Order No# WA6020605
MSA-DTWD | WA6155864 | 2 | ECO PLUMBING AND GAS PTY LTD | External area - Tap at low level in rose garden is leaking | Plumbing & Drainage | Water | 164.03 | Pass | Pass | 0 | 0 | 0.083333 | 2022-11-08 14:24 | 2022-11-11 17:00 | 2022-11-10 13:26 | 2022-11-11 17:00 | 2022-11-10 13:31 |  |  | Serviced hose tap
MSA-DCA | WA6294019 | 1 | Site Environmental & Remediation Services Pty Ltd | Removal of Asbestos | Waste Management | Asbestos removal | 200 | Fail | Fail | 9 | 9 | 0.083333 | 2022-11-30 11:49 | 2022-12-01 17:00 | 2023-02-01 14:20 | 2022-12-01 17:00 | 2023-02-01 14:25 |  |  | Called by Reese in regards to some possible asbestos material that had fallen off the building. Went to collect the material and confirmed it was not asbestos material.
MSA-DFES | WA4993259 | 2 | SONTEC WA PTY LTD | 1st Floor - Bypass the door switch and connect to the button - Please see details below | Security | Access Control |  | Pass | Pass | 0 | 0 | 0.083333 | 2022-01-07 11:19 | 2022-01-12 17:00 | 2022-01-12 15:00 | 2022-01-12 17:00 | 2022-01-12 15:05 |  |  | Showed Go Doors the relay contacts for the door. Tech already onsite for another job.No Charge.
MSA-DCA | WA5092015 | 1 | EQUANS Mechanical Services (WA) Pty Limited | spotted a slow water leak in the boiler room coming from above the cable tray | Air Conditioning | Room Air Conditioners | 1076.4 | Fail | Fail | 0 | 0 | 0.083333 | 2022-01-27 13:13 | 2022-01-28 17:00 | 2022-01-31 12:00 | 2022-01-28 17:00 | 2022-01-31 12:05 |  |  | Carried out isolations and drain down of heating water system. Leaking pipework was repaired by the contractor. Reinstated water, pumps and boiler. Ran system and checked for leaks - no leaks present.
MSA-DTWD | WA5468531 | 1 | ECO PLUMBING AND GAS PTY LTD | Room C45 - Drains overflowing for washing machines | Plumbing & Drainage | Drainage | 161.164 | Fail | Fail | 0 | 0 | 0.083333 | 2022-05-20 10:18 | 2022-05-23 17:00 | 2022-05-23 17:04 | 2022-05-23 17:00 | 2022-05-23 17:09 |  |  | Investigated blockage found that you can only run washing machine at once as there is too great a volume of water therefore causing a blockage, lady in reception has knowledge of this as is a reoccurring issue, Dave is to tell cleaners not to use both washing machines at once
MSA-DTWD | WA5675273 | 2 | ECO PLUMBING AND GAS PTY LTD | Blocked sink | Plumbing & Drainage | Drainage | 141.28 | Pass | Pass | 0 | 0 | 0.083333 | 2022-07-22 09:17 | 2022-07-27 17:00 | 2022-07-27 13:23 | 2022-07-27 17:00 | 2022-07-27 13:28 |  |  | Used plunger to unblock sink
MSA-DTAG | WA5679602 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Custody Cell - Cell 1 - bio clean of blood after prisoner cut himself in cell | Cleaning | Sanitary Services | 300 | Fail | Fail | 0 | 0 | 0.083333 | 2022-07-26 15:43 | 2022-07-26 17:43 | 2022-07-27 16:38 | 2022-07-26 19:43 | 2022-07-27 16:43 |  |  | As per Work Order no# WA5679602
MSA-DTWD | WA5693348 | 2 | ECO PLUMBING AND GAS PTY LTD | Blocked Floor Drain - Near water cooler | Plumbing & Drainage | Drainage | 500.54 | Fail | Fail | 0 | 0 | 0.083333 | 2022-08-04 11:37 | 2022-08-09 17:00 | 2022-08-10 15:25 | 2022-08-09 17:00 | 2022-08-10 15:30 |  | WCAPPR | Unblock drain in G block G101
MSA-DTWD | WA5795609 | 2 | ECO PLUMBING AND GAS PTY LTD | basin taps leaking | Plumbing & Drainage | Water | 157.28 | Pass | Pass | 0 | 0 | 0.083333 | 2022-08-25 13:48 | 2022-08-30 17:00 | 2022-08-30 08:58 | 2022-08-30 17:00 | 2022-08-30 09:03 |  |  | Serviced 4x sets of taps in C59
MSA-DCA | WA5974428 | 0 | Site Environmental & Remediation Services Pty Ltd | Level 4 - Potential asbestos - Please investigate | Building | Foundations | 925 | Fail | Fail | 5 | 5 | 0.083333 | 2022-09-23 11:34 | 2022-09-23 13:34 | 2022-10-30 13:30 | 2022-09-23 15:34 | 2022-10-30 13:35 |  |  | Requested by Reece to collect bulk sample for asbestos analysis and also air monitoring after asbestos material was found in the roof space
MSA-DTWD | WA5978624 | 2 | ECO PLUMBING AND GAS PTY LTD | 3x faulty taps | Plumbing & Drainage | Water | 515.93 | Fail | Fail | 0 | 0 | 0.083333 | 2022-09-28 11:54 | 2022-10-03 17:00 | 2022-10-04 10:17 | 2022-10-03 17:00 | 2022-10-04 10:22 |  |  | Serviced taps Replaced spouts Replaced trap
MSA-DTWD | WA6145328 | 2 | ECO PLUMBING AND GAS PTY LTD | Female staff toilet in D block has water continually flowing and does not flush-see notes | Plumbing & Drainage | Toilets/Cisterns | 561.9 | Pass | Pass | 0 | 0 | 0.083333 | 2022-11-02 11:36 | 2022-11-07 17:00 | 2022-11-04 17:21 | 2022-11-07 17:00 | 2022-11-04 17:26 |  |  | Serviced leaking toilet
MSA-DCA | WA6523204 | 3 | Commercial Aquatics Australia | City room - Ground floor - external area - Several misters not spraying correctly - see notes | Plumbing & Drainage | Water | 190 | Pass | Pass | 0 | 0 | 0.083333 | 2023-01-31 13:15 | 2023-02-07 17:00 | 2023-02-07 12:51 | 2023-02-07 17:00 | 2023-02-07 12:56
MSA-DTWD | WA6537267 | 2 | ECO PLUMBING AND GAS PTY LTD | S Block - gas leak. see notes | Plumbing & Drainage | Gas | 217.787 | Pass | Pass | 0 | 0 | 0.083333 | 2023-02-07 08:14 | 2023-02-10 17:00 | 2023-02-10 08:15 | 2023-02-10 17:00 | 2023-02-10 08:20
MSA-DTWD | WA5017316 | 3 | ECO PLUMBING AND GAS PTY LTD | Unit Z - East Wall - Damaged External Tap | Plumbing & Drainage | Water | 300.7 | Fail | Fail | 1 | 1 | 0.066667 | 2022-01-13 12:38 | 2022-01-20 17:00 | 2022-01-27 11:15 | 2022-01-20 17:00 | 2022-01-27 11:19 |  |  | Replaced 2x external hose taps in N Block
MSA-DTWD | WA5091555 | 1 | ECO PLUMBING AND GAS PTY LTD | J Block toilets - J008.1 - J008.2 - J008.3 - J008.4 - multiple taps leaking | Plumbing & Drainage | Materials | 437.62 | Pass | Pass | 0 | 0 | 0.066667 | 2022-01-27 09:33 | 2022-01-28 17:00 | 2022-01-27 14:53 | 2022-01-28 17:00 | 2022-01-27 14:57 |  |  | Serviced 10x taps, tightened mixer tap in bathroom and serviced urinal
MSA-DCA | WA5105998 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Air conditioning leaking water in curators office | Air Conditioning | Room Air Conditioners | 905.25 | Fail | Fail | 2 | 2 | 0.066667 | 2022-02-05 16:48 | 2022-02-06 16:48 | 2022-02-17 08:13 | 2022-02-06 16:48 | 2022-02-17 08:17 |  |  | Job attended as AH call Sunday 6/2/22. Equipment isolated due to water leakage. Returned Monday 7/2/22 found condensate pump to have failed. Replacement sourced and brought to site. Installed on unit. Confirmed no further leakage. Work area left tidy. BRAF submitted to PFM
MSA-DTWD | WA5270503 | 3 | NEYLOR | N100 -Replace broken blinds | Building | Curtains & Blinds | 966.07 | Fail | Fail | 5 | 5 | 0.066667 | 2022-03-18 08:15 | 2022-03-25 17:00 | 2022-04-27 13:49 | 2022-03-25 17:00 | 2022-04-27 13:53 |  |  | Completed & invoiced
MSA-DTAG | WA5379519 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground/ Level 1 - Various locations - see below for details - COVID Clean required | Cleaning | Emergency Cleans | 500 | Fail | Fail | 1 | 1 | 0.066667 | 2022-04-21 12:00 | 2022-04-21 14:00 | 2022-04-27 14:46 | 2022-04-21 16:00 | 2022-04-27 14:50 |  |  | As per Work Order No# WA5379519
MSA-DTWD | WA5384052 | 2 | NEYLOR | P002.4 - faulty blinds | Building | Curtains & Blinds | 529.59 | Fail | Fail | 3 | 3 | 0.066667 | 2022-04-28 09:28 | 2022-05-03 17:00 | 2022-05-27 12:28 | 2022-05-03 17:00 | 2022-05-27 12:32 |  |  | Completed & invoiced
MSA-DTWD | WA5400838 | 1 | ECO PLUMBING AND GAS PTY LTD | E401 Unable to get water to wash troughs URGENT | Plumbing & Drainage | Water | 141.28 | Fail | Fail | 0 | 0 | 0.066667 | 2022-05-10 13:22 | 2022-05-11 17:00 | 2022-05-12 16:26 | 2022-05-11 17:00 | 2022-05-12 16:30 |  |  | Investigated no water due up hot water system being isolated there is no water to the trough
MSA-DTWD | WA5687152 | 2 | ECO PLUMBING AND GAS PTY LTD | Tap next to dishwasher has come off the wall - Hoping tap just need a couple of O rings to repair | Plumbing & Drainage | Water | 154.28 | Pass | Pass | 0 | 0 | 0.066667 | 2022-08-01 13:41 | 2022-08-04 17:00 | 2022-08-04 15:56 | 2022-08-04 17:00 | 2022-08-04 16:00 |  |  | Replaced orings
MSA-DTWD | WA5699995 | 2 | ECO PLUMBING AND GAS PTY LTD | FG02 - Male toilets - Left hand side urinal not filling/flushing properly | Plumbing & Drainage | Toilets/Cisterns | 132.66 | Fail | Fail | 0 | 0 | 0.066667 | 2022-08-10 13:53 | 2022-08-15 17:00 | 2022-08-18 16:03 | 2022-08-15 17:00 | 2022-08-18 16:07 |  |  | Installed new bellows inside urinal cistern
MSA-DTWD | WA5761443 | 3 | ECO PLUMBING AND GAS PTY LTD | Disabled toilet Hot tap unable to turn off - C16 | Plumbing & Drainage | Water | 101.57 | Pass | Pass | -1 | -1 | 0.066667 | 2022-08-18 09:03 | 2022-08-25 17:00 | 2022-08-18 15:54 | 2022-08-25 17:00 | 2022-08-18 15:58 |  |  | Serviced hot spindle
MSA-DTWD | WA5798836 | 1 | Precise Air Group | Hallway-ceiling tiles not put back after routine maintenance | Air Conditioning | Room Air Conditioners | 366 | Pass | Pass | 0 | 0 | 0.066667 | 2022-08-30 07:42 | 2022-08-30 17:00 | 2022-08-30 13:28 | 2022-08-30 17:00 | 2022-08-30 13:32 |  |  | Arrived at site ceiling panel had been left out by another contractor doing works in building re installed ceiling panel also adjust thermostat in kids daycare area was to hot adjusted thermostat for spring conditions
MSA-DCA | WA6014700 | 0 | Commercial Aquatics Australia | Courtyard next to pond - Pond is leaking underneath to the pump room | Recreation | General | 190 | Fail | Pass | 0 | 0 | 0.066667 | 2022-10-12 11:13 | 2022-10-12 13:13 | 2022-10-12 13:58 | 2022-10-12 15:13 | 2022-10-12 14:02 |  |  | Water feature found to be leaking down wall inside the state theatre. Make up water was not shutting off as it should due to a sensor issue. This has been shut off. Elliot from site has made the decision to drain the pond to further investigate continuous leaks into the building.
MSA-DTWD | WA6301042 | 2 | ECO PLUMBING AND GAS PTY LTD | Blocked Drain | Plumbing & Drainage | Drainage | 217.03 | Fail | Fail | 5 | 5 | 0.066667 | 2022-12-02 12:55 | 2022-12-07 17:00 | 2023-01-10 16:28 | 2022-12-07 17:00 | 2023-01-10 16:32 |  |  | Unblocked sink in FT 17
MSA-DTWD | WA6402440 | 2 | Precise Air Group | Evaporative A/C 8 and 9 appear to have no water running through (see notes) | Air Conditioning | Ducted Split System | 999.48 | Pass | Pass | 0 | 0 | 0.066667 | 2023-01-05 11:35 | 2023-01-10 17:00 | 2023-01-09 08:02 | 2023-01-10 17:00 | 2023-01-09 08:06
MSA-DTWD | WA6523299 | 2 | ECO PLUMBING AND GAS PTY LTD | Water leak from pan when flushed | Plumbing & Drainage | Toilets/Cisterns | 202.26 | Pass | Pass | 0 | 0 | 0.066667 | 2023-01-31 14:12 | 2023-02-03 17:00 | 2023-02-03 14:09 | 2023-02-03 17:00 | 2023-02-03 14:13
MSA-DTWD | WA6674741 | 1 | ECO PLUMBING AND GAS PTY LTD | Urinal at far end is completely blocked | Plumbing & Drainage | Toilets/Cisterns | 178.96 | Pass | Pass | 0 | 0 | 0.066667 | 2023-02-27 11:31 | 2023-02-28 17:00 | 2023-02-28 15:55 | 2023-02-28 17:00 | 2023-02-28 15:59
MSA-DTWD | WA4993422 | 1 | ECO PLUMBING AND GAS PTY LTD | tile cutting room - leak in the room from ceiling | Plumbing & Drainage | Water | 220.99 | Fail | Fail | 3 | 3 | 0.066667 | 2022-01-07 13:44 | 2022-01-10 17:00 | 2022-02-01 10:25 | 2022-01-10 17:00 | 2022-02-01 10:29 |  |  | Completed job on day but ProMAP was down so couldn’t complete notes Cut out old section of 20mm copper water pipe where there was a burst and replaced with new copper
MSA-DCA | WA5106411 | 1 | Programmed Property Services | remove tree and make safe - see notes below | Landscaping & Gardening | Grounds Maintenance | 662 | Pass | Pass | 0 | 0 | 0.066667 | 2022-02-07 08:12 | 2022-02-08 17:00 | 2022-02-07 13:31 | 2022-02-08 17:00 | 2022-02-07 13:35 |  |  | Work completed 07/02/2022
MSA-DTAG | WA5193934 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Bio Clean - Court cells 3 and 4 - bio clean body fluids | Cleaning | Sanitary Services | 300 | Pass | Pass | 0 | 0 | 0.066667 | 2022-02-25 16:35 | 2022-02-28 17:00 | 2022-02-28 15:57 | 2022-02-28 17:00 | 2022-02-28 16:01 |  |  | WA5193934
MSA-DTWD | WA5319187 | 3 | ECO PLUMBING AND GAS PTY LTD | 2 x taps faulty | Plumbing & Drainage | Water | 165.28 | Pass | Pass | 0 | 0 | 0.066667 | 2022-04-12 12:59 | 2022-04-21 17:00 | 2022-04-21 13:42 | 2022-04-21 17:00 | 2022-04-21 13:46 |  |  | Serviced 2x tap sets in female toilets
MSA-DTWD | WA5401062 | 2 | ECO PLUMBING AND GAS PTY LTD | ground C45 Drains in laundry for washing machines blocked and backing up | Plumbing & Drainage | Drainage | 141.28 | Pass | Pass | 0 | 0 | 0.066667 | 2022-05-10 15:29 | 2022-05-13 17:00 | 2022-05-12 16:31 | 2022-05-13 17:00 | 2022-05-12 16:35 |  |  | Removed trap on trough and pulled out hair in pipe, put trap back on and plunged trough which unblocked the drain
MSA-DTWD | WA5674775 | 3 | ECO PLUMBING AND GAS PTY LTD | MID - A08 Leaking Pan seal first cubicle | Plumbing & Drainage | Water | 141.28 | Pass | Pass | 0 | 0 | 0.066667 | 2022-07-21 13:54 | 2022-07-28 17:00 | 2022-07-28 08:55 | 2022-07-28 17:00 | 2022-07-28 08:59 |  |  | Replaced flush cone rubber and pan seal
MSA-DTWD | WA5683089 | 3 | Equans Mechanical Services Australia | Replace faulty chiller anodes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 281.42 | Pass | Pass | 0 | 0 | 0.066667 | 2022-07-29 16:14 | 2022-08-05 17:00 | 2022-08-05 10:42 | 2022-08-05 17:00 | 2022-08-05 10:46 |  |  | anodes replaced
MSA-DTWD | WA5706812 | 3 | Equans Mechanical Services Australia | Faulty CRAC unit set points/ Server room | Air Conditioning | Room Air Conditioners | 945.945 | Pass | Pass | 0 | 0 | 0.066667 | 2022-08-11 14:07 | 2022-08-18 17:00 | 2022-08-18 15:59 | 2022-08-18 17:00 | 2022-08-18 16:03 |  |  | INVESTIAGTED LAG ISSUES WITH CRAC UNITS OVER SEVERAL DAYS AS FAULTS WITH CHILLERS HAD POTENTIAL TO CAUSE ISSUES.DX SYSTEM TAKES OVER WHEN CHILLER WATER FAILS OR IS OFF. ALL OK
MSA-DCA | WA6672090 | 1 | Precise Air Group | Old office - Rehearsal room - Aircon is leaking while turned on | Air Conditioning | Room Air Conditioners | 202.705 | Fail | Fail | 1 | 1 | 0.066667 | 2023-02-23 12:40 | 2023-02-24 17:00 | 2023-02-28 08:10 | 2023-02-24 17:00 | 2023-02-28 08:14
MSA-DTWD | WA6675123 | 2 | ECO PLUMBING AND GAS PTY LTD | Faulty taps on bench 6/7 | Plumbing & Drainage | Drainage | 159.53 | Pass | Pass | 0 | 0 | 0.066667 | 2023-02-27 15:40 | 2023-03-02 17:00 | 2023-02-28 15:59 | 2023-03-02 17:00 | 2023-02-28 16:03
MSA-DTWD | WA5319192 | 3 | ECO PLUMBING AND GAS PTY LTD | Faulty Cistern - Constantly running | Plumbing & Drainage | Water | 175.87 | Pass | Pass | 0 | 0 | 0.066667 | 2022-04-12 13:11 | 2022-04-21 17:00 | 2022-04-21 13:47 | 2022-04-21 17:00 | 2022-04-21 13:51 |  |  | Serviced toilet that was leaking in first floor female bathroom
MSA-DTWD | WA5413665 | 1 | ECO PLUMBING AND GAS PTY LTD | B2347 Male Toilets - Basin Taps Leaking Badly | Plumbing & Drainage | Materials | 111.57 | Pass | Pass | 0 | 0 | 0.066667 | 2022-05-12 12:45 | 2022-05-13 17:00 | 2022-05-12 16:36 | 2022-05-13 17:00 | 2022-05-12 16:40 |  |  | Serviced 2x taps in male bathroom in top floor of B block
MSA-DTWD | WA5417029 | 1 | ECO PLUMBING AND GAS PTY LTD | E30 Kitchen - Lecturers Tap is loose and leaking | Plumbing & Drainage | Water | 127.125 | Fail | Fail | 0 | 0 | 0.066667 | 2022-05-13 09:59 | 2022-05-16 17:00 | 2022-05-17 15:44 | 2022-05-16 17:00 | 2022-05-17 15:48 |  |  | Installed new bracket underneath kitchen mixer
MSA-DTWD | WA6154703 | 1 | Dormakaba Australia Pty Ltd | Block main auto door - F Block - Slow to open and close | Building | Automatic Doors | 180 | Fail | Fail | 8 | 8 | 0.066667 | 2022-11-07 16:15 | 2022-11-08 17:00 | 2023-01-06 07:02 | 2022-11-08 17:00 | 2023-01-06 07:06 |  |  | Attended site and found door to be working fine on arrival. Checked history and found there where numerous opening and closing faults, door jammed closed faults and loose mechanism. Due to age this is more than likely caused by wear and tear on the motor and controller. Checked for any current obstructions but there where no one. If problem reoccurs this unit will need to be upgraded. Spoke to Dennis from facilities and he has said just to leave as is for now and if door breaks down we will look at doing a quote.left area clean and tidy.
MSA-DFES | WA6166053 | 2 | Facilities First Australia Pty Ltd | SES Volunteer Association Building - Ground Floor - Kitchen - Mold Issue - See notes below | Cleaning | Hazardous Materials | 98.64 | Fail | Fail | 5 | 5 | 0.05 | 2022-11-11 11:49 | 2022-11-16 17:00 | 2022-12-21 15:03 | 2022-11-16 17:00 | 2022-12-21 15:06 |  |  | When client services manager met with DFES site representative there was no mould to be found - invoice claimed against this work order is for a call out fee as discussed between Fiona Hermsen (Serco FM) and Tania Cook (Programmed)
MSA-DFES | WA6356683 | 2 | Facilities First Australia Pty Ltd | Under cover area - Washing machine area - Patio roof covering has mold growing on inside roof sheet | Cleaning | Cleaning | 780 | Fail | Fail | 2 | 2 | 0.05 | 2022-12-05 08:48 | 2022-12-08 17:00 | 2022-12-20 15:48 | 2022-12-08 17:00 | 2022-12-20 15:51 |  |  | Mould removed from patio as requested
MSA-DTAG | WA6373552 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Level 1-Custody Cell 2 - PIC in custody yesterday that has now tested positive for COVID-see notes | Cleaning | Emergency Cleans | 300 | Fail | Fail | 3 | 3 | 0.05 | 2022-12-14 15:15 | 2022-12-15 17:00 | 2023-01-06 14:09 | 2022-12-15 17:00 | 2023-01-06 14:12 |  |  | As per work order no# WA6373552
MSA-DTWD | WA6523226 | 3 | ECO PLUMBING AND GAS PTY LTD | Leaking tap at hand basin | Plumbing & Drainage | Water | 102.84 | Pass | Pass | 0 | 0 | 0.05 | 2023-01-31 13:33 | 2023-02-07 17:00 | 2023-02-07 08:52 | 2023-02-07 17:00 | 2023-02-07 08:55
MSA-DTWD | WA5383301 | 3 | AWB Co. | U Block - Ground - Lights turn off after 5 minutes – faulty switch - see notes below | Electrical | General Electrical | 1000 | Pass | Pass | -1 | -1 | 0.05 | 2022-04-27 14:09 | 2022-05-04 17:00 | 2022-04-28 08:25 | 2022-05-04 17:00 | 2022-04-28 08:28 |  |  | supply only of materialswork relates to previous WA that was closed out early
MSA-DTAG | WA5454296 | 3 | NEYLOR | Registry -Roller blind needs to be refitted after window being fixed | Building | Curtains & Blinds | 280 | Fail | Fail | 1 | 1 | 0.05 | 2022-05-17 10:33 | 2022-05-24 17:00 | 2022-05-30 09:28 | 2022-05-24 17:00 | 2022-05-30 09:31 |  |  | Completed & invoiced
MSA-DTWD | WA5679023 | 3 | ECO PLUMBING AND GAS PTY LTD | Cleaners sink is leaking from waste | Plumbing & Drainage | Drainage | 44.739 | Pass | Pass | -1 | -1 | 0.05 | 2022-07-26 10:04 | 2022-08-02 17:00 | 2022-07-29 14:27 | 2022-08-02 17:00 | 2022-07-29 14:30 |  |  | Replaced trap washers on 50mm trap
MSA-DTWD | WA5796980 | 1 | ECO PLUMBING AND GAS PTY LTD | 1st Cubicle Toilet Cistern Damaged | Plumbing & Drainage | Toilets/Cisterns | 388.72 | Pass | Pass | 0 | 0 | 0.05 | 2022-08-26 15:53 | 2022-08-29 17:00 | 2022-08-29 11:27 | 2022-08-29 17:00 | 2022-08-29 11:30 |  |  | Replaced broken cistern
MSA-DCA | WA5832110 | 1 | Commercial Aquatics Australia | External Grounds - Wetlands - Wetlands pump is not operating as it should | Landscaping & Gardening | Grounds Maintenance | 1000 | Pass | Pass | 0 | 0 | 0.05 | 2022-09-05 11:13 | 2022-09-06 17:00 | 2022-09-06 07:53 | 2022-09-06 17:00 | 2022-09-06 07:56 |  |  | .
MSA-DTWD | WA6111580 | 2 | ECO PLUMBING AND GAS PTY LTD | Rec room - 2 x leaking taps | Plumbing & Drainage | Water | 157.18 | Pass | Pass | 0 | 0 | 0.05 | 2022-10-21 08:48 | 2022-10-26 17:00 | 2022-10-26 13:04 | 2022-10-26 17:00 | 2022-10-26 13:07 |  |  | Replaced basin taps with new ones
MSA-DTWD | WA6361747 | 1 | ECO PLUMBING AND GAS PTY LTD | Student male/female toilets - Blocked toilets | Plumbing & Drainage | Toilets/Cisterns | 16.047 | Pass | Pass | 0 | 0 | 0.05 | 2022-12-08 12:40 | 2022-12-09 17:00 | 2022-12-09 11:11 | 2022-12-09 17:00 | 2022-12-09 11:14 |  |  | Toilets were not blocked tested on site, facilities manager tested to confirm
MSA-DTWD | WA6650000 | 0 | Precise Air Group | Aircon not working - A block | Air Conditioning | Room Air Conditioners | 253.38 | Fail | Fail | 0 | 0 | 0.05 | 2023-02-20 08:48 | 2023-02-20 10:48 | 2023-02-22 10:49 | 2023-02-20 12:48 | 2023-02-22 10:52
MSA-DTWD | WA6675962 | 1 | ECO PLUMBING AND GAS PTY LTD | student urinal constantly running - Faulty flush button | Plumbing & Drainage | Toilets/Cisterns | 214.33 | Fail | Fail | 0 | 0 | 0.05 | 2023-02-28 10:41 | 2023-03-01 17:00 | 2023-03-02 10:51 | 2023-03-01 17:00 | 2023-03-02 10:54
MSA-DTWD | WA6681409 | 0 | Precise Air Group | AHU2 has stopped working | Air Conditioning | Room Air Conditioners | 152.03 | Fail | Fail | 0 | 0 | 0.05 | 2023-03-02 08:37 | 2023-03-02 10:37 | 2023-03-02 15:21 | 2023-03-02 12:37 | 2023-03-02 15:24
MSA-DTWD | WA6693419 | 2 | Equans Mechanical Services Australia | Jewellery Workshop - Extraction fan coming on and air flow only on one side (see notes) | Air Conditioning | Evaporative Coolers | 444.825 | Pass | Pass | 0 | 0 | 0.05 | 2023-03-10 10:00 | 2023-03-15 17:00 | 2023-03-14 20:27 | 2023-03-15 17:00 | 2023-03-14 20:30
MSA-DTAG | WA5017203 | 1 | Codee Cleaning Services | Ground and 1 - custody cells - cell 2 lower custody - transit cell 2 upper custody - see details | Cleaning | Emergency Cleans | 500 | Fail | Fail | 1 | 1 | 0.05 | 2022-01-13 11:26 | 2022-01-14 17:00 | 2022-01-19 18:22 | 2022-01-14 17:00 | 2022-01-19 18:25 |  |  | complete
MSA-DTWD | WA5413241 | 1 | ECO PLUMBING AND GAS PTY LTD | D16 - Bakery Kitchen - Tap is leaking | Plumbing & Drainage | Water | 69.71 | Pass | Pass | 0 | 0 | 0.05 | 2022-05-12 09:55 | 2022-05-13 17:00 | 2022-05-12 16:41 | 2022-05-13 17:00 | 2022-05-12 16:44 |  |  | Isolated water and serviced taps in bakery kitchen
MSA-DTWD | WA5686226 | 2 | ECO PLUMBING AND GAS PTY LTD | disable toilet-Hand basin waste pipe in the Disabled toilet in F block is leaking | Plumbing & Drainage | Water | 64.71 | Pass | Pass | 0 | 0 | 0.05 | 2022-08-01 06:25 | 2022-08-03 17:00 | 2022-08-03 14:01 | 2022-08-03 17:00 | 2022-08-03 14:04 |  |  | Installed new trap washers
MSA-DTWD | WA6072182 | 1 | ECO PLUMBING AND GAS PTY LTD | toilets/store - Disconnect 2 x Hot water systems and make safe. | Plumbing & Drainage | HWS/Units Electric & Gas | 152.03 | Pass | Pass | 0 | 0 | 0.05 | 2022-10-18 08:38 | 2022-10-19 17:00 | 2022-10-19 10:50 | 2022-10-19 17:00 | 2022-10-19 10:53 |  |  | Isolated hot water unit
MSA-DFES | WA6393918 | 2 | Anvil Doors | Ground Floor - Tunic Room - Automatic door not functioning (see notes) | Building | Automatic Doors | 685.5 | Pass | Pass | -1 | -1 | 0.05 | 2022-12-29 12:00 | 2023-01-04 17:00 | 2022-12-30 16:52 | 2023-01-04 17:00 | 2022-12-30 16:55
MSA-DTWD | WA6526951 | 3 | ECO PLUMBING AND GAS PTY LTD | E16 - Female toilets - Faulty flush button on cubicle toilet | Plumbing & Drainage | Toilets/Cisterns | 48.141 | Pass | Pass | 0 | 0 | 0.05 | 2023-02-01 12:16 | 2023-02-08 17:00 | 2023-02-07 08:59 | 2023-02-08 17:00 | 2023-02-07 09:02
MSA-DTWD | WA5571603 | 2 | ECO PLUMBING AND GAS PTY LTD | Ground floor - M6 staff kitchen - Faulty tap spout | Plumbing & Drainage | Water | 129.89 | Pass | Pass | -1 | -1 | 0.05 | 2022-06-29 10:28 | 2022-07-04 17:00 | 2022-06-29 16:21 | 2022-07-04 17:00 | 2022-06-29 16:24 |  |  | Replaced hob outlet in kitchenette
MSA-DTWD | WA5694418 | 2 | ECO PLUMBING AND GAS PTY LTD | Female staff toilets are blocked | Plumbing & Drainage | Toilets/Cisterns | 330.7 | Pass | Pass | 0 | 0 | 0.05 | 2022-08-05 09:58 | 2022-08-10 17:00 | 2022-08-09 17:04 | 2022-08-10 17:00 | 2022-08-09 17:07 |  |  | Ran drain machine down drain
MSA-DTWD | WA5761449 | 3 | ECO PLUMBING AND GAS PTY LTD | Leaking tap ladies toilet | Plumbing & Drainage | Water | 84.565 | Pass | Pass | -1 | -1 | 0.05 | 2022-08-18 09:16 | 2022-08-25 17:00 | 2022-08-18 15:58 | 2022-08-25 17:00 | 2022-08-18 16:01 |  |  | Drilled out crack in brass seat for tap set
MSA-DTWD | WA5981405 | 2 | ECO PLUMBING AND GAS PTY LTD | No hot water at the sink - see notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 1052.695 | Pass | Pass | 0 | 0 | 0.05 | 2022-09-29 15:56 | 2022-10-04 17:00 | 2022-10-04 10:14 | 2022-10-04 17:00 | 2022-10-04 10:17 |  |  | Took photos to send braf
MSA-DTWD | WA6294234 | 2 | ECO PLUMBING AND GAS PTY LTD | Faulty hot water system | Plumbing & Drainage | HWS/Units Electric & Gas | 303.89 | Fail | Fail | 5 | 5 | 0.05 | 2022-11-30 13:57 | 2022-12-05 17:00 | 2023-01-10 16:34 | 2022-12-05 17:00 | 2023-01-10 16:37 |  |  | Replaced element and thermostat on hot water system
MSA-DTWD | WA6298748 | 2 | Boilertronics | B25 - Plant Room (inside B24) - Boiler not reaching appropriate temp. (see notes) | Plumbing & Drainage | HWS/Units Electric & Gas | 426.25 | Fail | Fail | 1 | 1 | 0.05 | 2022-12-01 12:50 | 2022-12-06 17:00 | 2022-12-12 11:49 | 2022-12-06 17:00 | 2022-12-12 11:52 |  |  | Attend site and sign inGet keys and acces to steam boilerTurned boiler on and watched it get to pressure with no issuesCustomer was getting correct tempreture he requiredRecommend boiler to to get serviced as it has not been serviced for a long timeDetails off boiler have been attached to the job
MSA-DTWD | WA6361633 | 2 | ECO PLUMBING AND GAS PTY LTD | Roof plumbing structure - leak in copper pipe | Plumbing & Drainage | Drainage | 203.13 | Pass | Pass | -1 | -1 | 0.05 | 2022-12-08 11:37 | 2022-12-13 17:00 | 2022-12-09 11:15 | 2022-12-13 17:00 | 2022-12-09 11:18 |  |  | Repair burst pipe
MSA-DTWD | WA6493811 | 2 | ECO PLUMBING AND GAS PTY LTD | toilet cisterns - continually flowing | Plumbing & Drainage | Toilets/Cisterns | 129.542 | Pass | Pass | 0 | 0 | 0.05 | 2023-01-18 15:52 | 2023-01-23 17:00 | 2023-01-23 16:27 | 2023-01-23 17:00 | 2023-01-23 16:30
MSA-DTAG | WA6520502 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Bio Clean – Cell 3 – Prisoner bled throughout cell after head injury | Cleaning | Hazardous Materials | 300 | Fail | Fail | 0 | 0 | 0.05 | 2023-01-27 15:24 | 2023-01-30 17:00 | 2023-02-01 12:27 | 2023-01-30 17:00 | 2023-02-01 12:30
MSA-DTWD | WA6693516 | 2 | ECO PLUMBING AND GAS PTY LTD | Leaking toilet pan | Plumbing & Drainage | Toilets/Cisterns | 283.095 | Pass | Pass | 0 | 0 | 0.05 | 2023-03-10 11:08 | 2023-03-15 17:00 | 2023-03-13 13:21 | 2023-03-15 17:00 | 2023-03-13 13:24
MSA-DTWD | WA6707815 | 0 | Precise Air Group | Cool room is faulty | Refrigeration | Coolroom |  | Fail | Fail | 0 | 0 | 0.05 | 2023-03-13 09:28 | 2023-03-13 11:28 | 2023-03-14 07:45 | 2023-03-13 13:28 | 2023-03-14 07:48
MSA-DTAG | WA5053129 | 3 | Total Security Systems Pty Ltd | Level 2 interview rooms no alarm sound or anything on computer (alarm viewer) in control room | Security | Monitoring |  | Pass | Pass | -1 | -1 | 0.033333 | 2022-01-18 13:22 | 2022-01-25 17:00 | 2022-01-21 11:39 | 2022-01-25 17:00 | 2022-01-21 11:41 |  |  | Repaired prior to Christmas 2021 - warranty - NO CHARGE
MSA-DTAG | WA5065608 | 1 | Codee Cleaning Services | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Cleaning | Emergency Cleans | 280 | Fail | Fail | 0 | 0 | 0.033333 | 2022-01-14 16:00 | 2022-01-17 17:00 | 2022-01-19 18:36 | 2022-01-17 17:00 | 2022-01-19 18:38 | 1 |  | complete
MSA-DTWD | WA5101762 | 2 | ECO PLUMBING AND GAS PTY LTD | Toilet cistern broken. Water keeps running | Plumbing & Drainage | Toilets/Cisterns | 191.28 | Pass | Pass | 0 | 0 | 0.033333 | 2022-02-03 14:32 | 2022-02-08 17:00 | 2022-02-07 11:31 | 2022-02-08 17:00 | 2022-02-07 11:33 |  |  | Serviced toilet in E Block
MSA-DTAG | WA5200218 | 1 | Codee Cleaning Services | Custody - Bio-Clean - Cell 4 - PIC picking scabs and blood | Cleaning | Sanitary Services | 280 | Fail | Fail | 0 | 0 | 0.033333 | 2022-03-01 15:57 | 2022-03-02 17:00 | 2022-03-03 17:39 | 2022-03-02 17:00 | 2022-03-03 17:41 |  |  | Clean completed 01/03/2022
MSA-DTWD | WA5209181 | 1 | Precise Air Group | BLD 833 - Kitchen - Cool room Freezer not Working | Refrigeration | Coolroom | 992.24 | Pass | Pass | 0 | 0 | 0.033333 | 2022-03-09 14:54 | 2022-03-10 17:00 | 2022-03-10 16:32 | 2022-03-10 17:00 | 2022-03-10 16:34 |  |  | SUBCONTRACTOR ATTENDED AND FIXED
MSA-DTWD | WA5231172 | 2 | NEYLOR | Clarkson - Conference room auto blinds broken and new remote required | Building | Curtains & Blinds | 140 | Fail | Fail | 2 | 2 | 0.033333 | 2022-03-15 09:38 | 2022-03-18 17:00 | 2022-03-30 09:02 | 2022-03-18 17:00 | 2022-03-30 09:04 |  |  | Completed & invoiced
MSA-DTWD | WA5368731 | 2 | CAPS AUSTRALIA PTY LTD | (EADV) Solenoid Valve on compressed air holding tank not working | Equipment | Compressors, Generators | 728.4 | Fail | Fail | 11 | 11 | 0.033333 | 2022-04-19 12:34 | 2022-04-22 17:00 | 2022-07-08 14:28 | 2022-04-22 17:00 | 2022-07-08 14:30 |  | WACCES | Replaced Solenoid Valve and Corrected Timer
MSA-DTWD | WA5368767 | 3 | ECO PLUMBING AND GAS PTY LTD | Hot water tap leaking in cleaners room | Plumbing & Drainage | Water | 906.8 | Pass | Pass | -1 | -1 | 0.033333 | 2022-04-19 12:47 | 2022-04-27 17:00 | 2022-04-21 13:55 | 2022-04-27 17:00 | 2022-04-21 13:57 |  |  | serviced hot tap
MSA-DTWD | WA5369083 | 2 | ECO PLUMBING AND GAS PTY LTD | The hot water system in E409 workshop has sprung a leak - see notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 66.715 | Pass | Pass | 0 | 0 | 0.033333 | 2022-04-19 16:14 | 2022-04-22 17:00 | 2022-04-21 13:58 | 2022-04-22 17:00 | 2022-04-21 14:00 |  |  | Quote for new tank
MSA-DTWD | WA5454669 | 2 | Precise Air Group | Roof Plant Room - Repair one Air compressor with parts salvaged from decomissioned unit | Air Conditioning | Room Air Conditioners | 894.32 | Pass | Pass | 0 | 0 | 0.033333 | 2022-05-17 13:18 | 2022-05-20 17:00 | 2022-05-20 15:39 | 2022-05-20 17:00 | 2022-05-20 15:41 |  |  | Sub contractor completed work
MSA-DCA | WA5462549 | 1 | ADVANCED LOCK & KEY | Electrical Pass Room, Level 1 - The door cannot be locked - See notes below | Security | Locksmith | 172.5 | Pass | Pass | 0 | 0 | 0.033333 | 2022-05-19 16:23 | 2022-05-20 17:00 | 2022-05-20 15:05 | 2022-05-20 17:00 | 2022-05-20 15:07 |  |  | Repair lock
MSA-DTWD | WA5478862 | 2 | NEYLOR | T012 classroom - Blind Wall up/ down touch button - Broken needs replacement | Building | Curtains & Blinds | 140 | Fail | Fail | 4 | 4 | 0.033333 | 2022-05-26 14:14 | 2022-05-31 17:00 | 2022-06-30 14:54 | 2022-05-31 17:00 | 2022-06-30 14:56 |  |  | Completed & InvoicedReplaced Batteries in Remote
MSA-DTWD | WA5488738 | 3 | NEYLOR | C48 - repair damaged vertical drapes - 3 drapes have snapped off upper end | Building | Curtains & Blinds | 2503.95 | Fail | Fail | 9 | 9 | 0.033333 | 2022-06-02 15:36 | 2022-06-10 17:00 | 2022-08-09 09:36 | 2022-06-10 17:00 | 2022-08-09 09:38 |  |  | Completed & invoiced
MSA-DTWD | WA5493490 | 0 | AHS Services WA Pty Ltd (Anchor) | A Block External - Burst Water pipe | Plumbing & Drainage | Water | 356.71 | Fail | Fail | 0 | 0 | 0.033333 | 2022-06-07 08:40 | 2022-06-07 10:40 | 2022-06-07 14:47 | 2022-06-07 12:40 | 2022-06-07 14:49 |  |  | Hose cock was kicked and snapped
MSA-DTWD | WA5495230 | 2 | AHS Services WA Pty Ltd (Anchor) | Tap to basin wont stop running male toilet | Plumbing & Drainage | Water | 133.32 | Pass | Pass | -1 | -1 | 0.033333 | 2022-06-08 10:23 | 2022-06-13 17:00 | 2022-06-08 14:19 | 2022-06-13 17:00 | 2022-06-08 14:21 |  |  | Job done
MSA-DTAG | WA5499626 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Female Public Toilets - blocked | Plumbing & Drainage | Toilets/Cisterns | 107.275 | Pass | Pass | 0 | 0 | 0.033333 | 2022-06-10 13:47 | 2022-06-13 17:00 | 2022-06-10 15:20 | 2022-06-13 17:00 | 2022-06-10 15:22 |  |  | Job done unblocked
MSA-DTAG | WA5565209 | 1 | Codee Cleaning Services | Custody – Cell 4 & Holding Cell 1 - Bio Clean (blood in the cell and holding cell) | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 1 | 0.033333 | 2022-06-21 14:57 | 2022-06-22 17:00 | 2022-06-30 13:25 | 2022-06-22 17:00 | 2022-06-30 13:27 |  |  | COMPLETED 21/06/2022
MSA-DTWD | WA5569014 | 2 | ECO PLUMBING AND GAS PTY LTD | Leaking sink taps - Tap seats are damaged. See facilities staff for location | Plumbing & Drainage | Water | 63.71 | Pass | Pass | 0 | 0 | 0.033333 | 2022-06-27 11:21 | 2022-06-30 17:00 | 2022-06-29 16:19 | 2022-06-30 17:00 | 2022-06-29 16:21 |  |  | Service taps in small scale kitchen
MSA-DTAG | WA5586052 | 2 | NEYLOR | ground registry-Bottom rail on Counters 5 & 9 roller blinds have become detached | Building | Windows | 160 | Fail | Fail | 2 | 2 | 0.033333 | 2022-07-06 07:44 | 2022-07-08 17:00 | 2022-07-25 12:25 | 2022-07-08 17:00 | 2022-07-25 12:27 |  |  | Completed & invoiced
MSA-DTAG | WA5674357 | 1 | Codee Cleaning Services | Ground - Custody - Bio Clean – Cell 2, interview room 1, holding cell 1- See notes below | Cleaning | Emergency Cleans | 500 | Fail | Fail | 0 | 0 | 0.033333 | 2022-07-21 11:15 | 2022-07-22 17:00 | 2022-07-24 11:51 | 2022-07-22 17:00 | 2022-07-24 11:53 |  |  | Completed 21/07/2022
MSA-DTWD | WA5680596 | 3 | Techworks Electrical | Replace multiple flickering lights in P008 | Electrical | Lighting, Internal | 567.185 | Pass | Pass | 0 | 0 | 0.033333 | 2022-07-27 13:40 | 2022-08-03 17:00 | 2022-08-01 14:01 | 2022-08-03 17:00 | 2022-08-01 14:03 |  |  | Replaced fluro tubes and starters at mclarty campus room P008, Q101 and kendrew campus D block level 2.used;8x 4ft fluro tubes and starters10 2ft fluro tubes and starters
MSA-DTWD | WA5781097 | 1 | Precise Air Group | plant room - AHU 7 - is supplying excessive heat to B306, B310.2 | Air Conditioning | Room Air Conditioners | 523.66 | Fail | Fail | 4 | 4 | 0.033333 | 2022-08-19 12:49 | 2022-08-22 17:00 | 2022-09-22 12:21 | 2022-08-22 17:00 | 2022-09-22 12:23 |  |  | Attended site and signed in, spoke to facility manager on si te about issue. Checked equipment and found AHU and boiler o perating correctly on inspection. Check heating coil actuato r for AHU and found that it was staying open at 100% regardl ess of what the BMS and setpoint was set too. We were able t o manually move the actuator it would return to fully open. Controls contractors will need to attend site to check actua tor controls are operating correctly. We have shut off the h eating valves to prevent area overheating.
MSA-DTWD | WA5795959 | 2 | Precise Air Group | coffee room aircon has bird feathers blowing out of the vent into the room | Air Conditioning | Room Air Conditioners | 208.34 | Pass | Pass | 0 | 0 | 0.033333 | 2022-08-26 07:56 | 2022-08-30 17:00 | 2022-08-30 13:34 | 2022-08-30 17:00 | 2022-08-30 13:36 |  |  | Found dead bird in fan assembly some feathers going through duct removed dead bird and cleaned out and run unit all good
MSA-DTWD | WA5797653 | 2 | Precise Air Group | S-Block - S006 - the aircon is not responding to temp setting running too cold | Air Conditioning | Room Air Conditioners | 660.89 | Pass | Pass | 0 | 0 | 0.033333 | 2022-08-29 09:44 | 2022-09-01 17:00 | 2022-08-30 09:21 | 2022-09-01 17:00 | 2022-08-30 09:23 |  |  | Traveled to kendrew campus signed in and received keys for m clarty. Traveled to mclarty and located reported area. Teste d unit and checked through field setting and lock options. S witched with another control to test and found cintrol to be faulty. Traveled to supplier to get a new wall control. Tra veled back to site and fitted new wall control. Test ran uni t and checked that controller responded to the inputs. Unit back in ormal operation.
MSA-DTWD | WA5799817 | 2 | ECO PLUMBING AND GAS PTY LTD | Blocked sink in B009 | Plumbing & Drainage | Water | 614.54 | Pass | Pass | 0 | 0 | 0.033333 | 2022-08-30 14:42 | 2022-09-02 17:00 | 2022-09-02 15:02 | 2022-09-02 17:00 | 2022-09-02 15:04 |  |  | Unblock drain in B block
MSA-DTWD | WA5827507 | 2 | Precise Air Group | Restaurant demo kitchen - Blast chiller not working | Refrigeration | Refrigerators | 366 | Pass | Pass | 0 | 0 | 0.033333 | 2022-09-01 10:54 | 2022-09-06 17:00 | 2022-09-06 09:24 | 2022-09-06 17:00 | 2022-09-06 09:26 |  |  | attended site signed in and located blast chiller. Restored power and ran unit. Test ran unit and observed it come down to -32 degrees in an hour will all components operational. u nable to find a fault with the unit. will monitor and may ne ed more info from occupants on site
MSA-DTWD | WA5830121 | 3 | Boilertronics | Level 5 - Boiler room - Boiler going into fault and Hot Water Pump #1 going into overcurrent | Mechanical Services | Boilers | 664 | Fail | Fail | 0 | 0 | 0.033333 | 2022-09-02 15:45 | 2022-09-09 17:00 | 2022-09-12 07:08 | 2022-09-09 17:00 | 2022-09-12 07:10 |  |  | Travelled to site and signed in.Went to the boiler room and the client was outside.Spoke to the client and they mentioned that the boiler is faulting regularly.They had a picture of the LFL faulted on “1”.It faults in the early mornings when the system starts up.I mentioned to the client that this is a common issue in cold conditions.Let the client know that I may be able to make slight adjustments but can’t simulate the cold conditions.Isolated the burner.Made changes to run the pilot only.Deisolated and ran the burner.Checked the pilot combustion and adjusted slightly to get a better reading.Put the burner back in to normal operating condition.Checked the combustion in low fire to make sure the pilot adjustments did not change low fire combustion.Ran the burner up to temperature and it cycled on and off as normal.We won’t know until another cold morning if the adjustments reduce the faults.If the faults still occur, we will need to make major adjustments that will affe
MSA-DTWD | WA5838646 | 2 | ECO PLUMBING AND GAS PTY LTD | Ground - eg16 - male toilet - toilet is blocked in the third cubicle | Plumbing & Drainage | Toilets/Cisterns | 61.744 | Pass | Pass | 0 | 0 | 0.033333 | 2022-09-08 16:55 | 2022-09-13 17:00 | 2022-09-13 08:18 | 2022-09-13 17:00 | 2022-09-13 08:20 |  |  | Used plunger to unblock toilet in EG 16
MSA-DTWD | WA5973504 | 3 | Water2water Pty Ltd | T Block - First Floor - Landing - Water cooler compressor very noisy | Plumbing & Drainage | Water | 173.82 | Fail | Fail | 1 | 1 | 0.033333 | 2022-09-21 13:51 | 2022-09-29 17:00 | 2022-10-04 11:43 | 2022-09-29 17:00 | 2022-10-04 11:45 |  | WCAPPR | All operating correctly. All noise just standard. Both taps chilled water. All ok
MSA-DCA | WA5976843 | 1 | Techworks Plumbing | Geology Building - Ground - Epoch Cafe - Male urinal blocked | Plumbing & Drainage | Toilets/Cisterns | 135.14 | Pass | Pass | 0 | 0 | 0.033333 | 2022-09-27 11:42 | 2022-09-28 17:00 | 2022-09-27 13:36 | 2022-09-28 17:00 | 2022-09-27 13:38 |  |  | Cleared blocking urinal - tested okCleaned grate and reinstated
MSA-DTWD | WA6008384 | 3 | AWB Co. | Ground and security lights not turning off | Electrical | Lighting, External | 134.255 | Pass | Pass | 0 | 0 | 0.033333 | 2022-10-11 13:57 | 2022-10-18 17:00 | 2022-10-18 16:52 | 2022-10-18 17:00 | 2022-10-18 16:54 |  |  | Attended site signed in jsa completed. went for a walk with john to show us lights staying on. Couldnt find them. Looked in board everything seemed fine. possible that someone had turned block 7 on for some reason but now off. Advised john naylor and he asked us to close job off.Job completed
MSA-DTWD | WA6129217 | 3 | AWB Co. | ground-Lecturers office 6F43-Power point won’t turn off | Electrical | General Electrical | 231.43 | Pass | Pass | -1 | -1 | 0.033333 | 2022-10-27 12:21 | 2022-11-03 17:00 | 2022-10-27 12:22 | 2022-11-03 17:00 | 2022-10-27 12:24 |  |  | Attended site signed in jsa completed. Found gpo in on position and wont turn off. replaced with new double 10a gpo.Tested and operational.Job completed
MSA-DTWD | WA6148334 | 1 | Precise Air Group | Air-conditioning not working - see notes | Air Conditioning | Room Air Conditioners | 1103.72 | Pass | Pass | 0 | 0 | 0.033333 | 2022-11-03 14:55 | 2022-11-04 17:00 | 2022-11-04 10:33 | 2022-11-04 17:00 | 2022-11-04 10:35 |  |  | was informed by facilities Manager Dave no cool air in deli section of E Block ,got ladder out and got on roof and checked evap cooler found diaphragm in water solenoid had broken and feeding through dump valve line and blocked it up ,checked pump as well kept on starting and stopping, so told facilities and they said to change all 3 components, dump valve ,pump and solenoid flow switch.works completed on the 4/11/2022
MSA-DTAG | WA6156564 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Level 1 - Custody area transit cell - BIO clean - see notes | Cleaning | Hazardous Materials | 300 | Fail | Fail | 1 | 1 | 0.033333 | 2022-11-09 08:54 | 2022-11-10 17:00 | 2022-11-15 12:09 | 2022-11-10 17:00 | 2022-11-15 12:11 |  |  | Job completed on 09/11/2022 6.00pm as per work order
MSA-DTWD | WA6249084 | 2 | ECO PLUMBING AND GAS PTY LTD | Opposite Room J120 - Leaking Tap | Plumbing & Drainage | Water | 102.54 | Pass | Pass | 0 | 0 | 0.033333 | 2022-11-21 09:50 | 2022-11-24 17:00 | 2022-11-24 16:46 | 2022-11-24 17:00 | 2022-11-24 16:48 |  |  | Replaced washer in tap
MSA-DTWD | WA6293878 | 1 | Precise Air Group | W block 207 - 211 - Central air con not working | Air Conditioning | Evaporative Coolers | 287.17 | Pass | Pass | 0 | 0 | 0.033333 | 2022-11-30 10:53 | 2022-12-01 17:00 | 2022-11-30 17:15 | 2022-12-01 17:00 | 2022-11-30 17:17 |  |  | Attended site, signed in and spoke to staff about issue with aircon. Checked aircon operation and found that the master controller do the VRV system was set to heating only allowing the slave units to run in heat or fan modes. Changed master to cooling and check slaves again found cooling mode available. Ran system and found it operational. Ran a staff member that worked in the area through how to use the master controller.
MSA-DTAG | WA6360866 | 0 | Codee Cleaning Services | Ground - Court Custody center - Bio Clean – 4 & interview room 2 – signage displayed - See Notes | Cleaning | Emergency Cleans | 301.28 | Pass | Pass | 0 | 0 | 0.033333 | 2022-12-07 16:05 | 2022-12-07 18:05 | 2022-12-07 16:34 | 2022-12-07 20:05 | 2022-12-07 16:36 |  |  | Completed 07/12/2022
MSA-MRWA | WA6363967 | 2 | Automatic Fire Protection (ARA) | UAT - Investigate sensitivity of detector - see notes below | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | 0 | 0 | 0.033333 | 2022-12-12 08:36 | 2022-12-15 17:00 | 2022-12-13 09:28 | 2022-12-15 17:00 | 2022-12-13 09:30 |  |  | Fire alarm level 7 UAT due to excessive spray in area.Checked location and unable to move or change device.Site has no put signage in area re excessive spays.
MSA-DCA | WA6365162 | 0 | Dormakaba Australia Pty Ltd | Retrospective Work Order- Roller door was accidently hit by a truck. Needs realignment. | Building | Automatic Doors | 350 | Fail | Fail | 1 | 1 | 0.033333 | 2022-12-10 13:30 | 2022-12-10 15:30 | 2022-12-19 18:31 | 2022-12-10 17:30 | 2022-12-19 18:33 | 1 |  | Found bottom steal bar and first slat bent outward. Straight out both items and got door operating. Requires additional works to strengthen lower steel bar at the ends where it enters the guides. The impact of the truck has cracked this piece. Pictures attached.This job was not sent via programmed. Michael Hewitt 0418672823 sent the job through.
MSA-DTWD | WA6403095 | 2 | Precise Air Group | Canteen roof - Evaporative AC constantly leaking - see notes | Air Conditioning | Evaporative Coolers | 725.33 | Pass | Pass | 0 | 0 | 0.033333 | 2023-01-06 08:35 | 2023-01-11 17:00 | 2023-01-09 08:07 | 2023-01-11 17:00 | 2023-01-09 08:09
MSA-DTWD | WA6526941 | 3 | ECO PLUMBING AND GAS PTY LTD | Cleaners Hot Water Tap is Leaking | Plumbing & Drainage | Water | 102.84 | Pass | Pass | 0 | 0 | 0.033333 | 2023-02-01 12:10 | 2023-02-08 17:00 | 2023-02-07 08:56 | 2023-02-08 17:00 | 2023-02-07 08:58
MSA-DTWD | WA6535250 | 2 | ECO PLUMBING AND GAS PTY LTD | Repair leaking tap and cistern | Plumbing & Drainage | Drainage | 167.03 | Pass | Pass | 0 | 0 | 0.033333 | 2023-02-06 16:39 | 2023-02-09 17:00 | 2023-02-08 15:57 | 2023-02-09 17:00 | 2023-02-08 15:59
MSA-DTWD | WA6579038 | 1 | Equans Mechanical Services Australia | Reset Aircon in computer room OH & S issue - see notes | Air Conditioning | Room Air Conditioners |  | Fail | Fail | 2 | 2 | 0.033333 | 2023-02-15 13:44 | 2023-02-16 17:00 | 2023-02-27 15:18 | 2023-02-16 17:00 | 2023-02-27 15:20
MSA-DTWD | WA6667771 | 2 | ECO PLUMBING AND GAS PTY LTD | Taps Leaking - Repair | Plumbing & Drainage | Water | 136.98 | Pass | Pass | 0 | 0 | 0.033333 | 2023-02-21 14:43 | 2023-02-24 17:00 | 2023-02-24 15:31 | 2023-02-24 17:00 | 2023-02-24 15:33
MSA-DFES | WA6668462 | 2 | Anvil Doors | Rear Daglish 1st light tanker roller door, close to the station entrance is mulfunctioning | Building | Automatic Doors | 377 | Pass | Pass | -1 | -1 | 0.033333 | 2023-02-22 09:30 | 2023-02-27 17:00 | 2023-02-22 11:47 | 2023-02-27 17:00 | 2023-02-22 11:49
MSA-DTAG | WA6674411 | 1 | AHS Services WA Pty Ltd (Anchor) | Custody - Toilet and drink fountains not flushing | Plumbing & Drainage | Toilets/Cisterns | 290.005 | Pass | Pass | 0 | 0 | 0.033333 | 2023-02-27 09:48 | 2023-02-28 17:00 | 2023-02-28 12:00 | 2023-02-28 17:00 | 2023-02-28 12:02
MSA-DTWD | WA6681768 | 2 | SCAVENGER SUPPLIES PTY LTD | Faulty CO2 fire extinguisher | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 207.1 | Pass | Pass | -1 | -1 | 0.033333 | 2023-03-02 11:57 | 2023-03-08 17:00 | 2023-03-02 12:51 | 2023-03-08 17:00 | 2023-03-02 12:53
MSA-DTWD | WA6689132 | 1 | ECO PLUMBING AND GAS PTY LTD | toilet wont flush properly and broken seat and covers (see notes) | Plumbing & Drainage | Toilets/Cisterns | 295.38 | Pass | Pass | 0 | 0 | 0.033333 | 2023-03-08 09:44 | 2023-03-09 17:00 | 2023-03-09 11:28 | 2023-03-09 17:00 | 2023-03-09 11:30
MSA-DTWD | WA6689789 | 2 | Australian Airconditioning Services Pty Ltd | AC not cooling - Room temp is 4 degrees above set point | Air Conditioning | Ducted Split System |  | Pass | Pass | 0 | 0 | 0.033333 | 2023-03-08 16:43 | 2023-03-13 17:00 | 2023-03-10 15:51 | 2023-03-13 17:00 | 2023-03-10 15:53
MSA-DTWD | WA4993482 | 2 | Equans Mechanical Services Australia | E60 Plant Room - Possible VSD fault with Extraction hood in E58 Large Scale Kitchen | Air Conditioning | Room Air Conditioners | 586.63 | Fail | Fail | 15 | 15 | 0.033333 | 2022-01-07 14:54 | 2022-01-12 17:00 | 2022-04-26 15:46 | 2022-01-12 17:00 | 2022-04-26 15:48 |  |  | ARRIVED ON SITE AND WAS INFORMED JOB WAS RAISED FOR PERTH AIR AND POWER TO ATTEND CALL. completed by sub contractor
MSA-DTAG | WA5231820 | 1 | Codee Cleaning Services | Ground - Custody cells - Bio Clean - see details | Cleaning | Emergency Cleans | 500 | Pass | Pass | 0 | 0 | 0.033333 | 2022-03-15 15:23 | 2022-03-16 17:00 | 2022-03-16 15:59 | 2022-03-16 17:00 | 2022-03-16 16:01 |  |  | COMPLETED 15/03/2022
MSA-DCA | WA5679033 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Air-conditioning is very noisy in one areas of the boardroom. Dampers may need adjusting | Air Conditioning | Room Air Conditioners | 653.145 | Pass | Pass | 0 | 0 | 0.033333 | 2022-07-26 10:10 | 2022-07-27 17:00 | 2022-07-26 15:29 | 2022-07-27 17:00 | 2022-07-26 15:31 |  |  | VQ Board Room Arrived on site as per client request 7am. Attended site as requested. Please note this job is for AC 10 and VAVs 10.2 , 10.3 in level 1 boardroom. As per discussion with site FM Pey-Sue. Adjustment have been made to temperature settings on VAV as setting was found to be set up for summer. Confirmed heating active and no fault with Electric duct heater zones. Confirmed air flow decrease on area achieving set point. Monitored operation and a few more minor adjustments were made for occupants comfort. Work area left tidy. No further action required on this job. Please note the VSD on this equipment is having issues with comms loss and is very old. Quote will be submitted for replacement. Note. Original work order was cancelled due to wrong fault notes. WA5677567
MSA-DTWD | WA6020293 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet flush button broken/missing from cistern | Plumbing & Drainage | Toilets/Cisterns | 241.115 | Pass | Pass | 0 | 0 | 0.033333 | 2022-10-13 11:58 | 2022-10-18 17:00 | 2022-10-17 12:42 | 2022-10-18 17:00 | 2022-10-17 12:44 |  |  | Picked up and replaced broken button7.00-8.30
MSA-DTWD | WA6661067 | 2 | ECO PLUMBING AND GAS PTY LTD | Leaking S bends | Plumbing & Drainage | Toilets/Cisterns | 249.68 | Pass | Pass | 0 | 0 | 0.033333 | 2023-02-21 12:23 | 2023-02-24 17:00 | 2023-02-24 15:29 | 2023-02-24 17:00 | 2023-02-24 15:31
MSA-DTWD | WA6666232 | 1 | Australian Airconditioning Services Pty Ltd | Fourth Floor - Ceiling Cassette Split System Leaking Water | Air Conditioning | Ducted Split System | 236.72 | Pass | Pass | 0 | 0 | 0.033333 | 2023-02-21 13:36 | 2023-02-22 17:00 | 2023-02-22 12:29 | 2023-02-22 17:00 | 2023-02-22 12:31
MSA-DTWD | WA6681745 | 2 | Boilertronics | Boiler with outlet low pressure | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 0.033333 | 2023-03-02 11:33 | 2023-03-08 17:00 | 2023-03-08 13:59 | 2023-03-08 17:00 | 2023-03-08 14:01
MSA-DTWD | WA5303944 | 0 | SCAVENGER SUPPLIES PTY LTD | Hallway - Break glass broken | Fire Protection Services | Fire Protection - Monitor System | 206.44 | Fail | Pass | 0 | 0 | 0.033333 | 2022-04-04 13:27 | 2022-04-04 15:27 | 2022-04-04 15:44 | 2022-04-04 17:27 | 2022-04-04 15:46 |  |  | COMPLETED - 4/4/22 - B block first floor manual call point was activated by a student and has since been replaced, system is normal.
MSA-DCA | WA5106839 | 1 | Automatic Fire Protection (ARA) | level 2 - concourse - AMPAC unit is in fault | Fire Protection Services | Fire Protection - Monitor System | 533.46 | Pass | Pass | 0 | 0 | 0.033333 | 2022-02-07 12:01 | 2022-02-08 17:00 | 2022-02-08 11:41 | 2022-02-08 17:00 | 2022-02-08 11:43 |  |  | Replaced L2 D15 XP95 smoke detector in maintenance fault. Reset loop and deisolated, all ok. 3x existing isolates due to ongoing works.
MSA-DTAG | WA5188535 | 3 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | attended on 22/02/22 - Bio Clean Cell 5 - blood found during afternoon clean | Cleaning | Cleaning | 300 | Fail | Fail | 1 | 1 | 0.033333 | 2022-02-22 09:36 | 2022-03-01 17:00 | 2022-03-11 15:53 | 2022-03-01 17:00 | 2022-03-11 15:55 |  |  | attended on 22/02/2022 Bio Clean Cell 5 - blood found during afternoon clean.
MSA-DTWD | WA5491095 | 3 | AHS Services WA Pty Ltd (Anchor) | A126 - Urinal isn't working | Plumbing & Drainage | Toilets/Cisterns | 283.8875 | Pass | Pass | -1 | -1 | 0.033333 | 2022-06-03 12:15 | 2022-06-13 17:00 | 2022-06-07 14:50 | 2022-06-13 17:00 | 2022-06-07 14:52 |  |  | Job done
MSA-DCA | WA6688294 | 3 | Precise Air Group | Uncle Joes Barbers - Air con leaking | Air Conditioning | Ducted Split System | 366 | Pass | Pass | 0 | 0 | 0.033333 | 2023-03-07 13:17 | 2023-03-14 17:00 | 2023-03-13 07:47 | 2023-03-14 17:00 | 2023-03-13 07:49
MSA-DCA | WA5016983 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main Building - Plant room (BMS system location) - BMS alarms not being reported | Security | Monitoring | 188.375 | Pass | Pass | 0 | 0 | 0.016667 | 2022-01-13 09:25 | 2022-01-14 17:00 | 2022-01-14 15:05 | 2022-01-14 17:00 | 2022-01-14 15:06 |  |  | Completed
MSA-DTAG | WA5204746 | 3 | Sapio Pty Ltd | Ground south hallway door fault | Security | Access Control | 643.12 | Pass | Pass | -1 | -1 | 0.016667 | 2022-03-04 13:01 | 2022-03-14 17:00 | 2022-03-10 15:03 | 2022-03-14 17:00 | 2022-03-10 15:04 |  |  | Installed new cable and checked system
MSA-DCA | WA5208622 | 1 | Programmed Property Services | Opposite 89 Birdwood Pde and 3 Beatrice Rd Dalkeith - see details below | Landscaping & Gardening | Tree Lopping | 875 | Pass | Pass | 0 | 0 | 0.016667 | 2022-03-09 09:39 | 2022-03-10 17:00 | 2022-03-09 12:52 | 2022-03-10 17:00 | 2022-03-09 12:53 |  |  | Fallen branch removed
MSA-DTWD | WA5297703 | 2 | NEYLOR | Admin building - Conference room - repair broken cords on blinds | Building | General Building | 140 | Fail | Fail | 1 | 1 | 0.016667 | 2022-03-31 12:12 | 2022-04-05 17:00 | 2022-04-12 14:11 | 2022-04-05 17:00 | 2022-04-12 14:12 |  |  | Completed & invoiced
MSA-DTWD | WA5472906 | 2 | NEYLOR | Ground Level - S/Services - Blinds not working by Sheryl's desk | Building | Curtains & Blinds | 691.22 | Fail | Fail | 8 | 8 | 0.016667 | 2022-05-24 11:32 | 2022-05-27 17:00 | 2022-07-25 12:39 | 2022-05-27 17:00 | 2022-07-25 12:40 |  |  | Completed & invoiced
MSA-DTWD | WA5493913 | 1 | Precise Air Group | Kendrew- E-Block Deli the display freezer not working | Refrigeration | Freezers | 1790.2 | Fail | Fail | 25 | 25 | 0.016667 | 2022-06-07 11:19 | 2022-06-08 17:00 | 2022-11-28 15:05 | 2022-06-08 17:00 | 2022-11-28 15:06 |  | WACCES | Fan completed notes for compressor are from a differant job , I have been to site and checked the freezer it is working and fan has been fitted.job ready to invoice
MSA-DTAG | WA5512079 | 1 | Codee Cleaning Services | Ground - Custody - Cell 1 & 3 - Bio Clean - See notes below | Cleaning | Emergency Cleans | 500 | Fail | Fail | 1 | 1 | 0.016667 | 2022-06-13 13:09 | 2022-06-14 17:00 | 2022-06-21 19:22 | 2022-06-14 17:00 | 2022-06-21 19:23 |  |  | completed 13/06/2022
MSA-DCA | WA5567101 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Security Control Room - please see details below | Security | CCTV Surveillance | 1184.2 | Fail | Fail | 13 | 13 | 0.016667 | 2022-06-23 14:29 | 2022-06-24 17:00 | 2022-09-23 11:20 | 2022-06-24 17:00 | 2022-09-23 11:21 |  |  | Completed
MSA-DTWD | WA5569222 | 3 | Precise Air Group | Music staff-room - AC not working | Air Conditioning | Room Air Conditioners | 486.66 | Pass | Pass | -1 | -1 | 0.016667 | 2022-06-27 12:49 | 2022-07-04 17:00 | 2022-06-28 17:11 | 2022-07-04 17:00 | 2022-06-28 17:12 |  |  | Found thermostat showing E3 fault on Daikin unit. Went up to the roofwhere the two split ducted systems located. ResetCondencing unit, turned switch breaker off, checked for leaks. All good. Found mother board fuze blown. replaced both fuzes on Condencing units. checked all ELECTRICALworks all good. Both units working on cooling andheating.
MSA-DTWD | WA5700091 | 2 | ECO PLUMBING AND GAS PTY LTD | Hot mixer tap constantly running | Plumbing & Drainage | Water |  | Fail | Fail | 0 | 0 | 0.016667 | 2022-08-10 15:09 | 2022-08-15 17:00 | 2022-08-18 16:01 | 2022-08-15 17:00 | 2022-08-18 16:02 |  |  | Spoke to Tao on site job to be cancelled as double up
MSA-DCA | WA5748503 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 heating water plant boiler fault - value 100 | Air Conditioning | Room Air Conditioners | 636.27 | Fail | Fail | 1 | 1 | 0.016667 | 2022-08-17 08:11 | 2022-08-18 17:00 | 2022-08-23 14:07 | 2022-08-18 17:00 | 2022-08-23 14:08 |  |  | Completed
MSA-DTAG | WA5796556 | 1 | Codee Cleaning Services | ground custody area-Extensive COVID clean required - see notes | Cleaning | Emergency Cleans | 1400 | Fail | Fail | 1 | 1 | 0.016667 | 2022-08-26 12:08 | 2022-08-29 17:00 | 2022-09-06 15:41 | 2022-08-29 17:00 | 2022-09-06 15:42 |  |  | completed 27/08/2022
MSA-DCA | WA5829497 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Basement - AHU Humidifier No2 Alarm fault | Equipment | Electrical Equipment | 371.62 | Fail | Fail | 0 | 0 | 0.016667 | 2022-09-02 14:13 | 2022-09-05 17:00 | 2022-09-06 09:37 | 2022-09-05 17:00 | 2022-09-06 09:38 |  |  | Completed
MSA-DTWD | WA5988446 | 0 | Dormakaba Australia Pty Ltd | Brick Laying Area - Room 6C - Main roller door has been damaged - Cant close - Stuck 2 meters | Building | Automatic Doors | 280 | Fail | Fail | 13 | 13 | 0.016667 | 2022-10-04 09:18 | 2022-10-04 11:18 | 2023-01-06 06:50 | 2022-10-04 13:18 | 2023-01-06 06:51 |  |  | Door sustained damage on RH side bottom section of slats,Managed to return slats into guides and straighten out enough for operation,Door now requires x8 100mm slatsCan reuse existing bottom railColour is PAPERBARKSLAT CUT LENGTH 4770mm (not including clips)X2 techsSee attached images.
MSA-DTAG | WA6015163 | 1 | Codee Cleaning Services | Public Disabled Toilet – Level 1 - Bio Clean - Blood on toilet seat | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 1 | 1 | 0.016667 | 2022-10-12 16:36 | 2022-10-13 17:00 | 2022-10-19 12:39 | 2022-10-13 17:00 | 2022-10-19 12:40 |  |  | Completed 12/10/2022
MSA-DCA | WA6151691 | 1 | Precise Air Group | Stage door - No 3 phase power to BMS system. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 523.66 | Pass | Pass | 0 | 0 | 0.016667 | 2022-11-07 08:22 | 2022-11-08 17:00 | 2022-11-08 11:54 | 2022-11-08 17:00 | 2022-11-08 11:55 |  |  | equipment is beyond repair, required to remove and replace
MSA-DTAG | WA6377198 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - 1987 Plant room - Water is leaking from the square tundish due to corrosion | Air Conditioning | Building HVAC Maintenance (Major Plant) | 460.88 | Pass | Pass | -1 | -1 | 0.016667 | 2022-12-16 11:52 | 2022-12-23 17:00 | 2022-12-16 11:52 | 2022-12-23 17:00 | 2022-12-16 11:53 |  |  | Attend site. Access level 4 plantroom. Check water leaking from cooling tower. Check over whole tower and found no leaks. Found water on floor. Found water at the back of the new cooling tower. While monitoring tower I found the chilled water make-up tank to start overflowing. Overflow goes into a steel tundish that is leaking. Found tundish leaking on the floor. Western Air advise they are fixing up the tundish and pipework. The only water tap in the plantroom is also located behind the old cooling tower. Any time this tap is turned on the water goes under the old tower cooling tower. Monitor operation of tower and found no leaks
MSA-DFES | WA6392942 | 2 | NEYLOR | Blinds in gym broken and missing on both windows and door | Building | Curtains & Blinds | 1219.82 | Fail | Fail | 8 | 8 | 0.016667 | 2022-12-28 07:25 | 2022-12-30 17:00 | 2023-02-22 14:20 | 2022-12-30 17:00 | 2023-02-22 14:21 |  |  | Completed
MSA-DFES | WA6467779 | 2 | Dom's Total Grounds Maintenance | Ground- Garden- Retic controller see notes | Landscaping & Gardening | Grounds Maintenance | 135 | Pass | Pass | 0 | 0 | 0.016667 | 2023-01-17 15:32 | 2023-01-20 17:00 | 2023-01-18 12:28 | 2023-01-20 17:00 | 2023-01-18 12:29
MSA-DFES | WA4983910 | 3 | NEYLOR | External Roller blinds outside the Training Dining Room & Staff Dining Room not working | Building | Curtains & Blinds | 230 | Fail | Fail | 2 | 2 | 0.016667 | 2021-12-23 14:28 | 2022-01-04 17:00 | 2022-01-19 13:06 | 2022-01-04 17:00 | 2022-01-19 13:07 |  |  | Completed & invoiced
MSA-DTAG | WA4994889 | 2 | Sapio Pty Ltd | SAT - Level 4 Room 4.05 - Duress alarm is faulty (no response ) | Security | Security Management System | 254.67 | Pass | Pass | 0 | 0 | 0.016667 | 2022-01-10 08:26 | 2022-01-13 17:00 | 2022-01-10 11:00 | 2022-01-13 17:00 | 2022-01-10 11:01 |  |  | Tested and found the Duress Transmitter battery completely dead after numerous failed activations. Replaced CR123A battery and transmitter powered back on. Tested and duress working all OK.Job completed.
MSA-DTWD | WA5094771 | 1 | Precise Air Group | EVAPS 1,3,4 & 5 not working will not turn | Air Conditioning | Room Air Conditioners | 1311 | Fail | Fail | 38 | 38 | 0.016667 | 2022-01-31 13:46 | 2022-02-01 17:00 | 2022-10-26 10:04 | 2022-02-01 17:00 | 2022-10-26 10:05 |  |  | Arrived on site and signed in as necessary. Investigated evaporative coolers in areas of complaint. Found faultyfan motor capacitors and sump dumps. Went to suppliersand purchased necessary parts. Returned to site andfitted. Tested operation. All OK.
MSA-DTAG | WA5108692 | 1 | Codee Cleaning Services | Custody - Cell 1 - Bio clean - blood noted on cell floor and half wall near toilet | Cleaning | Cleaning | 280 | Pass | Pass | 0 | 0 | 0.016667 | 2022-02-08 16:45 | 2022-02-09 17:00 | 2022-02-09 12:14 | 2022-02-09 17:00 | 2022-02-09 12:15 |  |  | Clean complete
MSA-DCA | WA5173268 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS communications failure | Air Conditioning | Room Air Conditioners | 410.775 | Fail | Fail | 0 | 0 | 0.016667 | 2022-02-20 20:17 | 2022-02-20 22:17 | 2022-02-22 09:10 | 2022-02-21 00:17 | 2022-02-22 09:11 |  |  | Completed
MSA-DCA | WA5308260 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Steam common equipment SP header presser alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 507.58 | Fail | Fail | 4 | 4 | 0.016667 | 2022-04-08 01:59 | 2022-04-08 03:59 | 2022-05-04 11:34 | 2022-04-08 05:59 | 2022-05-04 11:35 |  |  | Completed
MSA-DTAG | WA5368842 | 1 | Codee Cleaning Services | Ground - Custody cells - cell 4 - Bio clean - human waste on wall | Cleaning | Hazardous Materials | 280 | Pass | Pass | 0 | 0 | 0.016667 | 2022-04-19 13:27 | 2022-04-20 17:00 | 2022-04-20 16:49 | 2022-04-20 17:00 | 2022-04-20 16:50 |  |  | complete
MSA-DTAG | WA5379547 | 1 | Codee Cleaning Services | Ground & Level 1 - Custody Cell 3 & Interview Room - Bio Clean - see details | Cleaning | Emergency Cleans | 280 | Fail | Fail | 1 | 1 | 0.016667 | 2022-04-21 12:14 | 2022-04-22 17:00 | 2022-04-26 17:49 | 2022-04-22 17:00 | 2022-04-26 17:50 |  |  | completed 21/04/2022
MSA-DTAG | WA5462458 | 1 | Sapio Pty Ltd | Level 7 - Court 712 - swipe panel on public entrance is not working | Security | Access Control | 130 | Pass | Pass | 0 | 0 | 0.016667 | 2022-05-19 15:14 | 2022-05-20 17:00 | 2022-05-20 08:27 | 2022-05-20 17:00 | 2022-05-20 08:28 |  |  | found Pacom system had locked up causing reader not to work.reset and tested ok
MSA-DTWD | WA5565261 | 3 | Equans Mechanical Services Australia | E601 Boiler Room - Boiler 2 has intermittent fault - will not run | Mechanical Services | Boilers | 245.93 | Pass | Pass | -1 | -1 | 0.016667 | 2022-06-21 16:51 | 2022-06-28 17:00 | 2022-06-21 16:55 | 2022-06-28 17:00 | 2022-06-21 16:56 |  |  | Attended site, signed in and accessed building 1 boiler plantroom. Changed lead / lag for boiler 2 to run. Investigated and found the boiler low flame switch intermittently faulty causing the boiler to trip out. Reset the alarm and adjusted the switch. If Fault reoccurs it is recommended changing out the switch.
MSA-DTAG | WA5569572 | 1 | Codee Cleaning Services | Custody – Cell 2 - Urine and spit on the floor | Cleaning | Emergency Cleans | 280 | Fail | Fail | 0 | 0 | 0.016667 | 2022-06-27 16:37 | 2022-06-28 17:00 | 2022-06-30 13:31 | 2022-06-28 17:00 | 2022-06-30 13:32 |  |  | completed 27/06/2022
MSA-DCA | WA5694258 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - AC9 - Honeywell BMS alarm - RA fan in fault - note EF29 alarm has cleared | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Fail | Fail | 6 | 6 | 0.016667 | 2022-08-05 08:49 | 2022-08-08 17:00 | 2022-09-21 11:45 | 2022-08-08 17:00 | 2022-09-21 11:46 |  |  | Completed
MSA-DTWD | WA5793385 | 3 | Precise Air Group | A314..A327-Fume Hoods 7 and 12 not running 7 is on manual on BMS | Air Conditioning | Room Air Conditioners | 456.08 | Pass | Pass | -1 | -1 | 0.016667 | 2022-08-24 07:35 | 2022-08-30 17:00 | 2022-08-26 16:06 | 2022-08-30 17:00 | 2022-08-26 16:07 |  |  | Attended site and signed out keys. Gained access to BMS to c heck fume fan 7 and 12 status. Both fans show that they have stopped status but when we physically checked the fan motor s and fume hoods we found that they are mechanically fine an d running, suspect there is an issue with the controls syste m/ signal to these hoods. Room A314 has no control in the cl assroom to operate hood. Room A327 the hood can be switched on/off in the classroom via it's own controls but isn't reco gnised on the BMS.
MSA-DTWD | WA5800329 | 3 | NEYLOR | broken chain on roller blind | Building | Curtains & Blinds | 180 | Fail | Fail | 3 | 3 | 0.016667 | 2022-08-31 09:11 | 2022-09-07 17:00 | 2022-09-27 13:15 | 2022-09-07 17:00 | 2022-09-27 13:16 |  |  | Completed & invoiced
MSA-DTAG | WA5838605 | 1 | Codee Cleaning Services | Custody - Cell 1, spit floor around the toilet area | Cleaning | Cleaning | 301.28 | Fail | Fail | 0 | 0 | 0.016667 | 2022-09-08 15:25 | 2022-09-09 17:00 | 2022-09-12 13:49 | 2022-09-09 17:00 | 2022-09-12 13:50 |  |  | Completed 08/09/2022
MSA-DTWD | WA5861825 | 2 | Workzone Pty Ltd | Horticultural area - Tunnel Green house - Green house cover/glass required - see notes below | Landscaping & Gardening | Materials |  | Pass | Pass | 0 | 0 | 0.016667 | 2022-09-13 11:31 | 2022-09-16 17:00 | 2022-09-15 09:14 | 2022-09-16 17:00 | 2022-09-15 09:15 |  |  | BRAF submitted 15th Sept 2022This work order was for us to supply a quote only which was completed on 15th sept 2022. Work order raised under WA5861825
MSA-DTWD | WA5878214 | 1 | Equans Mechanical Services Australia | frayed & cracked Drive Belts to AHU 1 - see notes | Air Conditioning | Room Air Conditioners | 995.19 | Fail | Fail | 1 | 1 | 0.016667 | 2022-09-15 07:25 | 2022-09-15 17:00 | 2022-09-19 10:31 | 2022-09-15 17:00 | 2022-09-19 10:32 |  |  | COLLECTED PARTS, REPLACED - MADE ADJUSTMENTS
MSA-DTWD | WA5994412 | 1 | Dormakaba Australia Pty Ltd | Main carpark auto gate motor is not working. | Building | Automatic Doors | 270 | Fail | Fail | 13 | 13 | 0.016667 | 2022-10-05 17:03 | 2022-10-06 17:00 | 2023-01-06 06:57 | 2022-10-06 17:00 | 2023-01-06 06:58 |  |  | Inspection of gate found gate has no powerChecked all switch board but couldn’t find rcd for gateElectrician to attend site to find out where gates rcd is and find out why there’s no power
MSA-DTAG | WA6128216 | 3 | Australian HVAC Services Pty. Ltd. | Roof - AC3 V Belt is noisy | Air Conditioning | Building HVAC Maintenance (Major Plant) | 376.94 | Pass | Pass | -1 | -1 | 0.016667 | 2022-10-26 13:22 | 2022-11-02 17:00 | 2022-10-26 14:00 | 2022-11-02 17:00 | 2022-10-26 14:01 |  |  | Check noise from AC 3. Found belt to be making noise. Belt is almost ready for replacement. Leave site and pick up new belt. Return to site and access roof. Isolate unit and remove old belt. Install new belt, allign and tighten. Deisolate and test operation. Unit is now running quietly.
MSA-DTWD | WA6249313 | 2 | ECO PLUMBING AND GAS PTY LTD | Block C - 38 - Blocked drain | Plumbing & Drainage | Water | 53.49 | Pass | Pass | 0 | 0 | 0.016667 | 2022-11-21 11:18 | 2022-11-24 17:00 | 2022-11-24 16:49 | 2022-11-24 17:00 | 2022-11-24 16:50 |  |  | Opened up trap and removed 2x pens and glove from trap
MSA-DTAG | WA6255818 | 0 | Codee Cleaning Services | Custody Area - Non-contact interview room - BIO CLEAN - Cell 1 | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0.016667 | 2022-11-23 14:10 | 2022-11-23 16:10 | 2022-11-25 16:31 | 2022-11-23 18:10 | 2022-11-25 16:32 |  |  | Completed
MSA-DTWD | WA6293608 | 1 | Precise Air Group | Aircon isnt working properly - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 253.38 | Pass | Pass | 0 | 0 | 0.016667 | 2022-11-30 09:56 | 2022-12-01 17:00 | 2022-12-01 12:30 | 2022-12-01 17:00 | 2022-12-01 12:31 |  |  | Attended site and signed in. Spoke with facility manager about temperature issues for block A and C on hot days. Accessed BMS to check system operation. Made adjustments to settings and checked operation, system all operational on completion.
MSA-DTAG | WA6388316 | 1 | Gilmour & Jooste Electrical | ground-custody area-2 x Fluro lights need replacing in the Women’s Toilet in the custody area -notes | Electrical | Lighting, Internal | 139.54 | Pass | Pass | 0 | 0 | 0.016667 | 2022-12-21 12:10 | 2022-12-22 17:00 | 2022-12-22 15:46 | 2022-12-22 17:00 | 2022-12-22 15:47 |  |  | Repair lights to custody
MSA-DCA | WA6438863 | 0 | Dormakaba Australia Pty Ltd | Entry door Eastern outer airlock door is not responding to command | Building | Doors | 436.19 | Fail | Fail | 0 | 0 | 0.016667 | 2023-01-14 08:48 | 2023-01-14 10:48 | 2023-01-16 16:44 | 2023-01-14 12:48 | 2023-01-16 16:45
MSA-DTAG | WA6520414 | 1 | Codee Cleaning Services | Ground custody-Additional Comments Bio Clean – Holding Cell 1 (upstairs) – Spit on floor | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0.016667 | 2023-01-27 14:14 | 2023-01-30 17:00 | 2023-01-30 17:38 | 2023-01-30 17:00 | 2023-01-30 17:39
MSA-DTWD | WA6560326 | 0 | Precise Air Group | A Block - AH2 stopped working - roof | Air Conditioning | Room Air Conditioners | 202.705 | Fail | Fail | 0 | 0 | 0.016667 | 2023-02-13 09:24 | 2023-02-13 11:24 | 2023-02-14 08:13 | 2023-02-13 13:24 | 2023-02-14 08:14
MSA-DTAG | WA6667791 | 3 | Australian HVAC Services Pty. Ltd. | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Court 7 too warm | Air Conditioning | Package | 392.14 | Pass | Pass | -1 | -1 | 0.016667 | 2023-02-21 14:53 | 2023-02-28 17:00 | 2023-02-21 15:30 | 2023-02-28 17:00 | 2023-02-21 15:31 | 1
MSA-DTAG | WA6681615 | 1 | Codee Cleaning Services | Ground - Cell 4 - Staph Infection requiring bio cleaning (see notes) | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 1 | 1 | 0.016667 | 2023-03-02 10:22 | 2023-03-03 17:00 | 2023-03-07 14:49 | 2023-03-03 17:00 | 2023-03-07 14:50
MSA-DTWD | WA6682119 | 1 | SCAVENGER SUPPLIES PTY LTD | Ampac fire panel in fault - Zone 3 | Fire Protection Services | Fire Protection - Monitor System | 233.555 | Pass | Pass | 0 | 0 | 0.016667 | 2023-03-02 16:09 | 2023-03-03 17:00 | 2023-03-03 09:19 | 2023-03-03 17:00 | 2023-03-03 09:20
MSA-DTWD | WA6690897 | 0 | Precise Air Group | Plant room - Air compresser - Not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 366 | Fail | Fail | 1 | 1 | 0.016667 | 2023-03-09 13:35 | 2023-03-09 15:35 | 2023-03-13 09:32 | 2023-03-09 17:35 | 2023-03-13 09:33
MSA-DTWD | WA5163939 | 3 | Equans Mechanical Services Australia | Level 1 - Server room - Electrical heating fail | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 0.016667 | 2022-02-18 13:35 | 2022-02-25 17:00 | 2022-02-22 15:58 | 2022-02-25 17:00 | 2022-02-22 15:59 |  |  | GAINED ACCESS TO SERVER ROOM AND CARRIED OUT INVESTIGATIONS OF FAULT ON CRAC UNIT LG-2. ELECTRIC REHEAT FOUND TO HAVE TRIPPED. CARRIED OUT ISOLATION AND RESET. CHECKED OPERATION AND NO FURTHER ISSUE WAS NOTED. WORK AREA HAS BEEN LEFT TIDY.
MSA-DFES | WA5417366 | 1 | ADVANCED LOCK & KEY | Training Dining room - External Door - not latching and locking | Security | Locksmith | 145 | Pass | Pass | 0 | 0 | 0.016667 | 2022-05-13 12:20 | 2022-05-16 17:00 | 2022-05-13 14:15 | 2022-05-16 17:00 | 2022-05-13 14:16 |  |  | Tighten hinge on dining room door.
MSA-DTAG | WA5438544 | 1 | OCS SERVICES PTY LTD | Ground Floor, Registry - Covid Clean required at front counters 9 & 10 | Cleaning | Cleaning |  | Fail | Fail | 1 | 1 | 0.016667 | 2022-05-16 15:09 | 2022-05-17 17:00 | 2022-05-24 11:46 | 2022-05-17 17:00 | 2022-05-24 11:47 |  |  | Covid clean
MSA-DTWD | WA5511799 | 2 | Precise Air Group | S213 - cannot adjust Temp of controller | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | 0 | 0 | 0.016667 | 2022-06-13 09:15 | 2022-06-16 17:00 | 2022-06-14 14:50 | 2022-06-16 17:00 | 2022-06-14 14:51 |  |  | Attended site and located reported office space. Loggedinto centralised controls and adjusted temps to occupants request.
MSA-DTAG | WA5549228 | 1 | Codee Cleaning Services | Custody – Cell 2 - Accused had staff infection | Cleaning | Emergency Cleans | 280 | Fail | Fail | 0 | 0 | 0.016667 | 2022-06-17 14:55 | 2022-06-20 17:00 | 2022-06-21 19:50 | 2022-06-20 17:00 | 2022-06-21 19:51 |  |  | completed 19/06/2022
MSA-DTAG | WA5549260 | 1 | Codee Cleaning Services | Retrospective Work Order - Bio Clean - Custody Various locations - see notes below do not attend | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 1 | 0.016667 | 2022-06-16 12:00 | 2022-06-17 17:00 | 2022-06-21 19:41 | 2022-06-17 17:00 | 2022-06-21 19:42 | 1 |  | COMPLETED 16/06/2022
MSA-DTWD | WA5572727 | 1 | Precise Air Group | G/1/2 - BMS System FCU's not turning off | Air Conditioning | Building HVAC Maintenance (Major Plant) | 459.6 | Pass | Pass | 0 | 0 | 0.016667 | 2022-06-30 09:54 | 2022-07-01 17:00 | 2022-07-01 10:50 | 2022-07-01 17:00 | 2022-07-01 10:51 |  |  | NRP attended 01/07 - service report to follow
MSA-DCA | WA5603701 | 0 | Precise Air Group | Level 4 - Plant room - Leaks coming from cooling towers | Air Conditioning | Cooling Tower | 1446.79 | Fail | Fail | 15 | 15 | 0.016667 | 2022-07-12 12:13 | 2022-07-12 12:43 | 2022-10-25 17:48 | 2022-07-12 14:13 | 2022-10-25 17:49 |  |  | Attended site and found pipe work for dosing pump failed. Picked up new parts from supplier and returned to fix.
MSA-DTAG | WA5613665 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Cell 2-Accused in custody has spread faeces around the water basin and toilet & surrounding areas | Cleaning | Emergency Cleans | 300 | Fail | Fail | 1 | 1 | 0.016667 | 2022-07-14 14:49 | 2022-07-14 16:49 | 2022-07-19 13:52 | 2022-07-14 18:49 | 2022-07-19 13:53 |  |  | As per WO WA5613665
MSA-DTAG | WA5748046 | 1 | Codee Cleaning Services | Retrospective work order required for a bio-clean – 30 July 2022 from 17:00pm to 19:30pm (2.5hrs) | Cleaning | Cleaning | 280 | Fail | Fail | 3 | 3 | 0.016667 | 2022-07-30 07:34 | 2022-08-01 17:00 | 2022-08-19 22:20 | 2022-08-01 17:00 | 2022-08-19 22:21 | 1 |  | completed 30/07/2022
MSA-DTAG | WA5800231 | 1 | Sapio Pty Ltd | Ground floor-Registry-Back door not locking- Don't need scan to get in.Please see notes below | Security | Keys & Access | 473.44 | Pass | Pass | 0 | 0 | 0.016667 | 2022-08-31 08:21 | 2022-09-01 17:00 | 2022-08-31 17:46 | 2022-09-01 17:00 | 2022-08-31 17:47 |  |  | Attended site. Checked reported fault. Found lock feature inappropriate for purpose and may keep door unlocked. Unable to fix the issue. Advised client and changed REX to the door in order to reset lock when exit.client error
MSA-DCA | WA5831425 | 1 | EQUANS Mechanical Services (WA) Pty Limited | the A/C on 16 degree it's very cold for the customers need to be adjust ASAP | Air Conditioning | Materials | 523.66 | Fail | Fail | 3 | 3 | 0.016667 | 2022-09-04 11:50 | 2022-09-05 17:00 | 2022-09-27 11:35 | 2022-09-05 17:00 | 2022-09-27 11:36 |  |  | Completed
MSA-DTAG | WA5974718 | 1 | Codee Cleaning Services | Ground - Custody - Cell 2 & 3 - Bio clean - see toes | Cleaning | Cleaning | 301.28 | Fail | Fail | 0 | 0 | 0.016667 | 2022-09-23 15:46 | 2022-09-27 17:00 | 2022-09-30 00:18 | 2022-09-27 17:00 | 2022-09-30 00:19 |  |  | Completed 23/09/2022
MSA-DCA | WA5995699 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Building | Automatic Doors | 506.05 | Fail | Fail | 1 | 1 | 0.016667 | 2022-10-06 08:00 | 2022-10-06 17:00 | 2022-10-13 07:50 | 2022-10-06 17:00 | 2022-10-13 07:51 | 1 |  | Attended site and inspected auto door. Found lhs door self actuating via inside sensor unit. Required to adjust sensor to improve performance. Alsoadjusted Rh door inside sensor to match. Tested operations all OKunable to input actual time:06/10/2022 07:30 AM 06/10/2022 08:45 AM
MSA-DTWD | WA6080434 | 2 | Dormakaba Australia Pty Ltd | Metal Fab-Down button on electric motor for roller door faulty (Intermittent) | Building | Doors | 220 | Fail | Fail | 11 | 11 | 0.016667 | 2022-10-18 13:47 | 2022-10-21 17:00 | 2023-01-06 06:44 | 2022-10-21 17:00 | 2023-01-06 06:45 |  |  | 1053192, Programmed asset number A40213728G. Arrived onsite and signed in, tested door and found the down switch faulty, isolated power andreplaced switch. Restored power and tested operation at least twenty times and could not fault.
MSA-DTWD | WA6148113 | 1 | Precise Air Group | Room J100 - Air conditioning is not working at all. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 208.34 | Fail | Fail | 1 | 1 | 0.016667 | 2022-11-03 12:12 | 2022-11-04 17:00 | 2022-11-08 11:50 | 2022-11-04 17:00 | 2022-11-08 11:51 |  |  | equipment decommissioned
MSA-DTWD | WA6184780 | 1 | Precise Air Group | Culinary Art School-Walk-in Refrigerator/Freezer not working | Refrigeration | Freezers | 1115.42 | Fail | Fail | 0 | 0 | 0.016667 | 2022-11-15 15:50 | 2022-11-16 17:00 | 2022-11-17 14:48 | 2022-11-16 17:00 | 2022-11-17 14:49 |  |  | 16/11/22Attended site and signed in. Gained access to E block to check freezer. Found controls unresponsive. Checked circuits in mech board and all were energised. Found breaker behind controller was off. Energised breaker and system started running, found evap fan was faulty in freezer room. Tracked down a replacement and went to pick up. Returned to site and swapped out faulty fan. Will need to return to de ice system and take readings.17/11/22Returned to site, signed in. Gained access to freezer room and proceeded to de ice evaporator unit. Once de ice ran system and took readings. Found system operating within desired parameters, monitored room getting down to setpoint and cycling off/ on again. System operational on completion of works. System is becoming quite aged, recommend budgeting for replacement.
MSA-DTWD | WA6253878 | 2 | M Construction (WA) | E Block - Deli - faulty stainless steel adjustable leg on counter table | Building | Steel Work | 193.68 | Pass | Pass | 0 | 0 | 0.016667 | 2022-11-22 12:50 | 2022-11-25 17:00 | 2022-11-25 15:18 | 2022-11-25 17:00 | 2022-11-25 15:19 |  |  | RE Thread Legs on Counters to suit. Reinstall Legs and Level Counter
MSA-DCA | WA6392293 | 0 | ADVANCED LOCK & KEY | Basement Level 2, Firepump Room - door lock broken | Building | Doors | 400 | Fail | Fail | 2 | 2 | 0.016667 | 2022-12-23 12:23 | 2022-12-23 14:23 | 2023-01-04 13:56 | 2022-12-23 16:23 | 2023-01-04 13:57 |  |  | work order complete.
MSA-DTWD | WA6523053 | 2 | AHS Services WA Pty Ltd (Anchor) | Water running non stop in toilet | Plumbing & Drainage | Toilets/Cisterns | 337.7525 | Pass | Pass | 0 | 0 | 0.016667 | 2023-01-31 12:04 | 2023-02-03 17:00 | 2023-02-02 12:54 | 2023-02-03 17:00 | 2023-02-02 12:55
MSA-DTWD | WA6529128 | 3 | SCAVENGER SUPPLIES PTY LTD | Discharged fire extinguisher needs replacing | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 106.93 | Pass | Pass | 0 | 0 | 0.016667 | 2023-02-02 15:06 | 2023-02-09 17:00 | 2023-02-07 15:44 | 2023-02-09 17:00 | 2023-02-07 15:45
MSA-DCA | WA6721603 | 3 | Techworks Plumbing | Basement - Security Control Room - loose tap leaking | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 0.016667 | 2023-03-14 10:14 | 2023-03-21 17:00 | 2023-03-15 11:59 | 2023-03-21 17:00 | 2023-03-15 12:00
MSA-DTAG | WA5053103 | 3 | Total Security Systems Pty Ltd | Court 1 and 2 dock alarm working but no light displayed on panel in control room (possible warranty) | Security | Monitoring |  | Pass | Pass | -1 | -1 | 0.016667 | 2022-01-18 13:07 | 2022-01-25 17:00 | 2022-01-21 11:42 | 2022-01-25 17:00 | 2022-01-21 11:43 |  |  | Repaired prior to Christmas 2021 - warranty - NO CHARGE
MSA-DTWD | WA5094339 | 2 | Precise Air Group | Could we get the temperature changed in room J128 I believe it is centrally controlled | Air Conditioning | Room Air Conditioners | 282.575 | Pass | Pass | 0 | 0 | 0.016667 | 2022-01-31 10:14 | 2022-02-03 17:00 | 2022-02-01 14:44 | 2022-02-03 17:00 | 2022-02-01 14:45 |  |  | Investigated J128 unit under central control. Contacted daikin for tech support. Scheduled access into room.Rewired and tested. Reset B block chiller throughout dayand assisted airvision
MSA-DTAG | WA5116462 | 1 | Codee Cleaning Services | Custody - Cell 4 - Bio-Clean - Cell 4 - Spittle on the floor, windows and walls. | Cleaning | Cleaning | 280 | Fail | Fail | 0 | 0 | 0.016667 | 2022-02-11 15:31 | 2022-02-14 17:00 | 2022-02-17 16:23 | 2022-02-14 17:00 | 2022-02-17 16:24 |  |  | complete
MSA-DTAG | WA5204963 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Court Room 3 - Covid clean in public gallery | Cleaning | Sanitary Services | 500 | Fail | Fail | 1 | 1 | 0.016667 | 2022-03-04 16:29 | 2022-03-08 17:00 | 2022-03-14 15:49 | 2022-03-08 17:00 | 2022-03-14 15:50 |  |  | Works completed as per work order no# WA5204963
MSA-DTAG | WA5255531 | 1 | Sapio Pty Ltd | Ground - Custody - 'Receiver 5 Alarm' active on our systems | Security | CCTV Surveillance | 250 | Pass | Pass | 0 | 0 | 0.016667 | 2022-03-17 10:20 | 2022-03-18 17:00 | 2022-03-18 09:36 | 2022-03-18 17:00 | 2022-03-18 09:37 |  |  | Attended site. Investigated issue and found it came from fault relay on Inovonics controller 5. Fault was due to tamper alarm on Museum Kitchen duress. Inspected duress and found that Inovonics receiver cover had been knocked loose. Resecured cover and alarm cleared.Job completed.
MSA-DCA | WA5278439 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Basement Level - Security Control Room - CCTV camera repairs –see notes for list of cameras & faults | Security | CCTV Surveillance | 2279.2 | Fail | Fail | 8 | 8 | 0.016667 | 2022-03-18 14:57 | 2022-03-25 17:00 | 2022-05-18 11:12 | 2022-03-25 17:00 | 2022-05-18 11:13 |  |  | Works carried out by Honeywell
MSA-DCA | WA5288859 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Francis ST - Basement Level - CCTV camera faulty require repair - 5211, 5206, 1212, 1213, 1216, 5209 | Security | CCTV Surveillance | 427.35 | Fail | Fail | 7 | 7 | 0.016667 | 2022-03-23 14:27 | 2022-03-28 17:00 | 2022-05-18 11:10 | 2022-03-28 17:00 | 2022-05-18 11:11 |  |  | Works carried out by Honeywell
MSA-DTAG | WA5413820 | 1 | Codee Cleaning Services | Ground - Custody - Cell 2 - Bio Clean - Spit in cell 2 from an accused in custody | Cleaning | Cleaning | 280 | Fail | Fail | 1 | 1 | 0.016667 | 2022-05-12 13:53 | 2022-05-13 17:00 | 2022-05-19 17:57 | 2022-05-13 17:00 | 2022-05-19 17:58 |  |  | clean completed 12/05/2022
MSA-DCA | WA5416631 | 1 | SCAVENGER SUPPLIES PTY LTD | Level 1-Reflections Gallery, Eastern Entry-repair wiring to magnetic door catch box- see notes below | Building | Fire Door | 193.51 | Pass | Pass | 0 | 0 | 0.016667 | 2022-05-13 07:14 | 2022-05-13 17:00 | 2022-05-13 11:44 | 2022-05-13 17:00 | 2022-05-13 11:45 |  |  | Completed 13/5/22
MSA-DTAG | WA5417721 | 1 | Codee Cleaning Services | Custody – Cell 3 - Bio Clean - Spit on floors and benches | Cleaning | Hazardous Materials | 280 | Fail | Fail | 0 | 0 | 0.016667 | 2022-05-13 15:51 | 2022-05-16 17:00 | 2022-05-19 18:02 | 2022-05-16 17:00 | 2022-05-19 18:03 |  |  | Clean completed 13/05/2022
MSA-DCA | WA5422660 | 0 | ADVANCED LOCK & KEY | External door to ground floor external box office - is not locking unsecured. | Building | Doors | 270 | Fail | Fail | 1 | 1 | 0.016667 | 2022-05-13 20:58 | 2022-05-13 22:58 | 2022-05-20 14:55 | 2022-05-14 00:58 | 2022-05-20 14:56 |  |  | Completed afterhours
MSA-DTWD | WA5481621 | 2 | AHS Services WA Pty Ltd (Anchor) | ground - E-Block - Ladies staff toilet - blocked | Plumbing & Drainage | Toilets/Cisterns | 203.88 | Pass | Pass | 0 | 0 | 0.016667 | 2022-05-30 15:02 | 2022-06-02 17:00 | 2022-06-02 10:32 | 2022-06-02 17:00 | 2022-06-02 10:33 |  |  | Job done
MSA-DCA | WA5628376 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Ground - Lift 5 Lobby - Card reader inside lift 5 is loose, needs securing- See notes below | Lifts | Lifts | 610.19 | Fail | Fail | 8 | 8 | 0.016667 | 2022-07-15 13:59 | 2022-07-20 17:00 | 2022-09-15 08:44 | 2022-07-20 17:00 | 2022-09-15 08:45 |  |  | Completed
MSA-DTWD | WA5693320 | 3 | AWB Co. | Grounds light on pole rear block 3 on driveway - Pole connection has been knocked exposing wires | Electrical | Lighting, External | 199.525 | Pass | Pass | -1 | -1 | 0.016667 | 2022-08-04 11:23 | 2022-08-11 17:00 | 2022-08-04 11:53 | 2022-08-11 17:00 | 2022-08-04 11:54 |  |  | Attended site signed in jsa completed. Found exposed wiring in lightpole near driveway 2. Dug down and exposed conduits. Sleeved with 20mm conduit and put new one way 20mm box on.Job completed
MSA-DCA | WA5735710 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Earth and Planetary Sciences Lab ground fume cupboard issues-see notes | Electrical | General Electrical | 146.4 | Fail | Fail | 1 | 1 | 0.016667 | 2022-08-16 14:43 | 2022-08-19 17:00 | 2022-08-23 13:38 | 2022-08-19 17:00 | 2022-08-23 13:39 |  |  | Completed
MSA-DTAG | WA5854272 | 1 | Codee Cleaning Services | Ground - Custody - Cell 1 - Bodily fluids around intercom button | Cleaning | Emergency Cleans | 301.28 | Pass | Pass | 0 | 0 | 0.016667 | 2022-09-12 15:14 | 2022-09-13 17:00 | 2022-09-13 12:27 | 2022-09-13 17:00 | 2022-09-13 12:28 |  |  | Completed 12/09/2022
MSA-DTAG | WA5869687 | 1 | Codee Cleaning Services | Bio Clean - Custody cell 3 - Spit on floor | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0.016667 | 2022-09-14 16:00 | 2022-09-15 17:00 | 2022-09-16 14:06 | 2022-09-15 17:00 | 2022-09-16 14:07 |  |  | Completed 14/09/2022
MSA-DFES | WA5887452 | 3 | AWB Co. | Ground floor - Radio communications store - Front of boat shed - Broken Ashpalt causing issues | Paving & Roadworks | Asphalt | 48.42 | Pass | Pass | 0 | 0 | 0.016667 | 2022-09-16 07:47 | 2022-09-22 17:00 | 2022-09-22 09:17 | 2022-09-22 17:00 | 2022-09-22 09:18 |  |  | attended site and submitted quote to make repairsquote and BRAF declined, close costs to date, only call out fee to attend and quote
MSA-DTAG | WA5977261 | 1 | Codee Cleaning Services | ground custody-Bio Clean – Ladies public toilets upstairs-see notes | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0.016667 | 2022-09-27 15:10 | 2022-09-28 17:00 | 2022-09-30 00:27 | 2022-09-28 17:00 | 2022-09-30 00:28 |  |  | completed 27/09/2022
MSA-DTWD | WA6022823 | 1 | Dormakaba Australia Pty Ltd | Auto locking system not working | Building | Automatic Doors | 240 | Fail | Fail | 12 | 12 | 0.016667 | 2022-10-14 12:08 | 2022-10-17 17:00 | 2023-01-06 06:47 | 2022-10-17 17:00 | 2023-01-06 06:48 |  |  | Attended site and found push to lock was not working on unit, after inspecting and testing linked out read connection, tested and now locking, explained to John and he is happy with this outcome. Left area clean and tidy.
MSA-DTWD | WA6088441 | 2 | Dormakaba Australia Pty Ltd | Doorway In B2127-2112The green exit button is failing to open the door.-see notes | Building | Automatic Doors | 312.26 | Fail | Fail | 11 | 11 | 0.016667 | 2022-10-19 08:41 | 2022-10-24 17:00 | 2023-01-06 06:53 | 2022-10-24 17:00 | 2023-01-06 06:54 |  |  | Note incorrect door number should be 1104087, Programmed asset number A403134318, arrived onsite and signed in, located door and problem to be a faulty mode connection board, fitted new mode board and tested operation all correct
MSA-DTAG | WA6149445 | 1 | Codee Cleaning Services | Ground Floor - Custody - Cell 1 - Bio Clean, see note | Cleaning | Emergency Cleans | 301.28 | Pass | Pass | 0 | 0 | 0.016667 | 2022-11-04 16:22 | 2022-11-07 17:00 | 2022-11-07 12:15 | 2022-11-07 17:00 | 2022-11-07 12:16 |  |  | completed 4/11/2022
MSA-DCA | WA6155918 | 2 | Precise Air Group | Fan Coil units x 2 not working in Technical Office | Air Conditioning | Materials | 253.38 | Fail | Fail | 17 | 17 | 0.016667 | 2022-11-08 14:56 | 2022-11-11 17:00 | 2023-03-13 18:38 | 2022-11-11 17:00 | 2023-03-13 18:39 |  |  | Completed - Attended site and signed in. Checked the two FCU on level one technical office, found one with loose electrical fitting stopping operation, repaired and ran, FCU now operational. Checked second FCU and found it had been removed from site, further investigation required and have notified manager.
MSA-DTWD | WA6190872 | 1 | SCAVENGER SUPPLIES PTY LTD | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - See notes | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Fail | Fail | 10 | 10 | 0.016667 | 2022-09-05 09:30 | 2022-09-06 17:00 | 2022-11-16 11:42 | 2022-09-06 17:00 | 2022-11-16 11:43 | 1 |  | Completed 05/09/2022
MSA-DTWD | WA6372014 | 3 | NEYLOR | Blind rollers broken, unable to open and close the blinds.-see notes | Building | Curtains & Blinds | 1912.54 | Fail | Fail | 5 | 5 | 0.016667 | 2022-12-14 10:57 | 2022-12-21 17:00 | 2023-01-25 11:12 | 2022-12-21 17:00 | 2023-01-25 11:13 |  |  | Completed & invoiced
MSA-DTWD | WA6517880 | 1 | Precise Air Group | Library Foyer - AHU 3 not working - no cold air | Air Conditioning | Building HVAC Maintenance (Major Plant) | 253.38 | Pass | Pass | 0 | 0 | 0.016667 | 2023-01-24 13:53 | 2023-01-25 17:00 | 2023-01-25 09:29 | 2023-01-25 17:00 | 2023-01-25 09:30
MSA-DTWD | WA6531827 | 1 | ECO PLUMBING AND GAS PTY LTD | one Female staff toilet is leaking from behind pan after flush | Plumbing & Drainage | Water |  | Fail | Fail | 1 | 1 | 0.016667 | 2023-02-03 15:28 | 2023-02-06 17:00 | 2023-02-10 08:21 | 2023-02-06 17:00 | 2023-02-10 08:22
MSA-DTAG | WA6681930 | 1 | Codee Cleaning Services | Bio – Clean Holding cell 2 (upstairs custody), urine on floor | Cleaning | Cleaning | 301.28 | Fail | Fail | 1 | 1 | 0.016667 | 2023-03-02 12:55 | 2023-03-03 17:00 | 2023-03-07 14:55 | 2023-03-03 17:00 | 2023-03-07 14:56
MSA-DCA | WA4991408 | 1 | Earth & Water Pty Ltd | Retic sprinkler 40 - zone 12 - faulty sprinkler, leaking water | Plumbing & Drainage | Water |  | Fail | Fail | 0 | 0 | 0 | 2022-01-05 07:59 | 2022-01-05 17:00 | 2022-01-06 | 2022-01-05 17:00 | 2022-01-06 |  |  | Arrived on site and identified issue-Replaced Hunter sprinkler ectra vtall pop body and fitted a new Hunter MP 1000 90-210' head-Tested and adjusted sprinkler-Left area clean and tidy
MSA-DTAG | WA4992423 | 1 | Sapio Pty Ltd | Ground - Custody - Door from sally port to custody not locking | Security | Keys & Access | 130 | Pass | Pass | 0 | 0 | 0 | 2022-01-06 11:35 | 2022-01-07 17:00 | 2022-01-06 15:30 | 2022-01-07 17:00 | 2022-01-06 15:30 |  |  | arrived onsite and found door hardware is loose. tightened and tested.
MSA-DTAG | WA5001713 | 2 | AWB Co. | Level 3 - Staff (JSO) Female Toilet - light not working | Electrical | Lighting, Internal |  | Fail | Fail | 0 | 0 | 0 | 2022-01-11 16:10 | 2022-01-14 17:00 | 2022-01-14 20:02 | 2022-01-14 17:00 | 2022-01-14 20:02 |  | WACCES
MSA-DTAG | WA5053120 | 3 | Total Security Systems Pty Ltd | Family counselling room 3 not working at all (possible warranty) | Security | Monitoring |  | Pass | Pass | -1 | -1 | 0 | 2022-01-18 13:17 | 2022-01-25 17:00 | 2022-01-21 11:42 | 2022-01-25 17:00 | 2022-01-21 11:42 |  |  | Repaired prior to Christmas 2021 - warranty - NO CHARGE
MSA-DTAG | WA5065623 | 1 | Codee Cleaning Services | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Cleaning | Emergency Cleans | 280 | Fail | Fail | 0 | 0 | 0 | 2022-01-14 18:00 | 2022-01-17 17:00 | 2022-01-19 18:43 | 2022-01-17 17:00 | 2022-01-19 18:43 | 1 |  | complete
MSA-DTAG | WA5069116 | 2 | Sapio Pty Ltd | Admin - Low Battery prompt from the security service monitoring company outlining a flag to the DGP | Security | Monitoring | 596.56 | Pass | Pass | -1 | -1 | 0 | 2022-01-19 15:06 | 2022-01-24 17:00 | 2022-01-20 12:44 | 2022-01-24 17:00 | 2022-01-20 12:44 |  |  | Attended site. Conducted battery testing on all DGPs due to recent power troubles. Replaced batteries on 4 x panels reporting issues. Cleared faults and reset 1 x Duress in alarm. Job completed.
MSA-DTWD | WA5092045 | 3 | NEYLOR | E Block - Level 1 - E209 - blinds damaged | Building | Curtains & Blinds | 978.72 | Fail | Fail | 9 | 9 | 0 | 2022-01-27 13:28 | 2022-02-03 17:00 | 2022-04-04 10:26 | 2022-02-03 17:00 | 2022-04-04 10:26 |  |  | Completed & invoiced
MSA-DTWD | WA5101761 | 1 | Precise Air Group | Between J and F - Industrial Gas Hut - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 777.72 | Pass | Pass | 0 | 0 | 0 | 2022-02-03 14:32 | 2022-02-04 17:00 | 2022-02-04 11:27 | 2022-02-04 17:00 | 2022-02-04 11:27 |  |  | Found unit had failed sump dump and faulty solenoid. Replaced parts with sump dump kit from van stock. Unitleft operational
MSA-DTWD | WA5101863 | 1 | Damian Rak Electrical Pty Ltd | faulty RCD x2 | Electrical | General Electrical |  | Fail | Fail | 25 | 25 | 0 | 2022-02-03 15:53 | 2022-02-04 17:00 | 2022-07-29 20:04 | 2022-02-04 17:00 | 2022-07-29 20:04
MSA-DTAG | WA5116471 | 1 | Codee Cleaning Services | Custody - upper custody transit cell 2 - Spittle on the floor, windows and walls. | Cleaning | Cleaning | 280 | Fail | Fail | 0 | 0 | 0 | 2022-02-11 15:41 | 2022-02-14 17:00 | 2022-02-17 16:34 | 2022-02-14 17:00 | 2022-02-17 16:34 |  |  | complete
MSA-MRWA | WA5128419 | 0 | EQUANS Mechanical Services (WA) Pty Limited | A/C unit flooding plant room | Air Conditioning | Room Air Conditioners | 279.955 | Fail | Fail | 1 | 1 | 0 | 2022-02-14 20:25 | 2022-02-14 22:25 | 2022-02-21 11:38 | 2022-02-15 00:25 | 2022-02-21 11:38 |  |  | Completed
MSA-DTAG | WA5133226 | 1 | AHS Services WA Pty Ltd (Anchor) | **DO NOT ATTEND** Level 10 - Admin kitchen - read details below | Plumbing & Drainage | Water |  | Fail | Fail | 2 | 2 | 0 | 2022-02-15 08:18 | 2022-02-16 17:00 | 2022-02-28 20:16 | 2022-02-16 17:00 | 2022-02-28 20:16
MSA-DTWD | WA5163665 | 2 | PEEL LOCK SERVICES PTY LTD | A7 - Damaged door lock | Security | Locksmith |  | Fail | Fail | 45 | 45 | 0 | 2022-02-18 10:55 | 2022-02-23 17:00 | 2023-01-03 20:08 | 2022-02-23 17:00 | 2023-01-03 20:08
MSA-DTAG | WA5186976 | 3 | Sapio Pty Ltd | Level B01 - Comms Room - assist in power transfer to UPS backup | Electrical | UPS System Maintenance | 130 | Pass | Pass | -1 | -1 | 0 | 2022-02-22 10:16 | 2022-03-01 17:00 | 2022-02-22 10:17 | 2022-03-01 17:00 | 2022-02-22 10:17 |  |  | attended site while electrician onsite.all systems operational
MSA-DTAG | WA5187623 | 3 | Sapio Pty Ltd | **DO NOT ATTEND** Indigo and Gallagher admin access not working- see notes below | Security | Access Control |  | Pass | Pass | 0 | 0 | 0 | 2022-02-22 13:47 | 2022-03-01 17:00 | 2022-02-28 20:16 | 2022-03-01 17:00 | 2022-02-28 20:16
MSA-DFES | WA5188507 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Belmont Bunker - Female Toilets - Black mould present in female toilets | Plumbing & Drainage | Water | 133.45 | Pass | Pass | 0 | 0 | 0 | 2022-02-23 09:16 | 2022-02-28 17:00 | 2022-02-28 11:00 | 2022-02-28 17:00 | 2022-02-28 11:00 |  |  | Located to female toilets in bunker to find black mold couldn’t see any but have seen holes in the grout would need a tiler to do the job.
MSA-DTWD | WA5189619 | 2 | AHS Services WA Pty Ltd (Anchor) | N115A - sink has lost pressure to taps | Plumbing & Drainage | Water | 133.32 | Pass | Pass | 0 | 0 | 0 | 2022-02-24 07:16 | 2022-02-28 17:00 | 2022-02-25 14:00 | 2022-02-28 17:00 | 2022-02-25 14:00 |  |  | Replaced washer to cold tap in n115 lab
MSA-DTWD | WA5191622 | 2 | Precise Air Group | J005 - Air con is not cooling | Air Conditioning | Room Air Conditioners | 486.66 | Pass | Pass | 0 | 0 | 0 | 2022-02-25 08:03 | 2022-03-02 17:00 | 2022-02-28 14:59 | 2022-03-02 17:00 | 2022-02-28 14:59 |  |  | Inspected system for airflow inside, found ac on and fan running but cooling not as effective as required. Package unit ducting checked and wiring to fan blower set tohigh speed. Newer barrell appears to have been installed. Airflow very strong at unit and loss through duct within expectation. Test run of unit shows compressor ok.Discharge pressure a little high. Found 1 x condenser fan very slow running. Other fan mtr not at full rotationspeed also.Capacitor check shows run caps at 0.67 and 1.65uf.New parts obtained from suppliers and fitted. Unit now discharging condenser air much stronger and unit coolernot to go out on hp.Unit monitored and cooling in rooms much better
MSA-DCA | WA5253785 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Fail | Fail | 22 | 22 | 0 | 2022-02-10 10:00 | 2022-02-11 17:00 | 2022-07-15 20:07 | 2022-02-11 17:00 | 2022-07-15 20:07 | 1
MSA-DTWD | WA5278438 | 1 | CLEVELAND COMPRESSED AIR SERVICES | External - Air dryer - C block - keeps over loading | Equipment | Compressors, Generators | 236.25 | Pass | Pass | 0 | 0 | 0 | 2022-03-18 14:50 | 2022-03-21 17:00 | 2022-03-21 15:00 | 2022-03-21 17:00 | 2022-03-21 15:00 |  |  | Attended site and assessed dryerfound it very dirty and the filters were blockedCleaned them out and tested, all ol
MSA-DFES | WA5287350 | 0 | Allpest WA | Ceiling space - above station offiicers office - they have criiters in the ceiling | Pest Control | General Pest |  | Fail | Fail | 5 | 5 | 0 | 2022-03-22 11:59 | 2022-03-22 13:59 | 2022-04-29 20:05 | 2022-03-22 15:59 | 2022-04-29 20:05
MSA-DCA | WA5297616 | 2 | EQUANS Mechanical Services (WA) Pty Limited | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2068 | Fail | Fail | 12 | 12 | 0 | 2022-02-27 16:00 | 2022-03-02 17:00 | 2022-05-24 09:18 | 2022-03-02 17:00 | 2022-05-24 09:18 | 1 |  | Completed
MSA-DTAG | WA5301517 | 2 | Schindler Lifts Australia | Lift 2 - lift intermittently showing out of service | Lifts | Lifts |  | Fail | Fail | 27 | 27 | 0 | 2022-04-01 09:51 | 2022-04-06 17:00 | 2022-10-13 20:02 | 2022-04-06 17:00 | 2022-10-13 20:02
MSA-DTWD | WA5301881 | 2 | NEYLOR | D108 - faulty blinds - high on the wall | Building | Curtains & Blinds | 1498.1 | Fail | Fail | 16 | 16 | 0 | 2022-04-01 13:54 | 2022-04-06 17:00 | 2022-07-25 12:59 | 2022-04-06 17:00 | 2022-07-25 12:59 |  |  | Completed & invoiced
MSA-DTAG | WA5303278 | 1 | Schindler Lifts Australia | Ground - Lift 4 – Judge’s Lift - Lift is out of service | Lifts | Lifts |  | Fail | Fail | 27 | 27 | 0 | 2022-04-04 09:15 | 2022-04-05 17:00 | 2022-10-13 20:02 | 2022-04-05 17:00 | 2022-10-13 20:02
MSA-DTWD | WA5305882 | 1 | ECO PLUMBING AND GAS PTY LTD | Store room - U009 - Leaking hot water system | Plumbing & Drainage | HWS/Units Electric & Gas | 960.25 | Pass | Pass | 0 | 0 | 0 | 2022-04-06 08:28 | 2022-04-07 17:00 | 2022-04-07 07:00 | 2022-04-07 17:00 | 2022-04-07 07:00 |  |  | Replaced split hot water system
MSA-DTWD | WA5306005 | 3 | Equans Mechanical Services Australia | Level 6 - Boiler room - Overpressure or bypass valve continuously dumping water PRIORITY: 3 | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | -1 | -1 | 0 | 2022-04-06 09:30 | 2022-04-13 17:00 | 2022-04-06 10:00 | 2022-04-13 17:00 | 2022-04-06 10:00 |  |  | ATTENDED SITE, SIGNED IN AND ACCESSED BUILDING 1 BOILER PLANTROOM. DISCOVERED THEPLANTROOM FLOOR FULL OF WATER. TRACED BACK A PIPE FROM THE PLANTROOM ANDDISCOVERED THE LEAK WAS COMING FROM A DOMESTIC HOT WATER PIPE OVER FLOW. IT ISRECOMMENDED INSTALLING A TUNDISH TO ALLOW ANY OVERFLOW OF WATER TO GO DIRECTLYINTO THE DRAIN.
MSA-DTAG | WA5307645 | 1 | Schindler Lifts Australia | 1987 - Level 2 - Lift out of service | Lifts | Lifts |  | Fail | Fail | 27 | 27 | 0 | 2022-04-07 14:30 | 2022-04-08 17:00 | 2022-10-13 20:02 | 2022-04-08 17:00 | 2022-10-13 20:02
MSA-DFES | WA5308971 | 1 | AHS Services WA Pty Ltd (Anchor) | sewage pump alarm has activated | Plumbing & Drainage | Toilets/Cisterns | 200.02 | Fail | Fail | 8 | 8 | 0 | 2022-04-09 14:08 | 2022-04-11 17:00 | 2022-06-06 10:00 | 2022-04-11 17:00 | 2022-06-06 10:00 |  |  | Works complete
MSA-DTWD | WA5311868 | 1 | Schindler Lifts Australia | Left lift not operating and showing fault on the control panel | Lifts | Lifts |  | Fail | Fail | 26 | 26 | 0 | 2022-04-11 09:37 | 2022-04-12 17:00 | 2022-10-13 20:02 | 2022-04-12 17:00 | 2022-10-13 20:02
MSA-DCA | WA5325378 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Basement Level-Control Room-Issues with CCTV cameras-1203,1220 -Server unable to connect to camerasr | Security | Access Control | 3102 | Fail | Fail | 12 | 12 | 0 | 2022-04-14 08:50 | 2022-04-21 17:00 | 2022-07-14 09:08 | 2022-04-21 17:00 | 2022-07-14 09:08 |  |  | Completed
MSA-DCA | WA5380600 | 0 | Dormakaba Australia Pty Ltd | Breeze way gate not closing | Building | Steel Fencing & Gates | 220 | Fail | Pass | 0 | 0 | 0 | 2022-04-22 13:58 | 2022-04-22 15:58 | 2022-04-22 16:16 | 2022-04-22 17:58 | 2022-04-22 16:16 |  |  | Removed fencing that had been placed in front of gate and looked for faults with motor. Unable to find any fault. Found gate in open position with the controller reading as closed. This means that someone must have manually slid the gate open and forgotten to close it again before reengaging he gearbox. Tested operation, all ok.
MSA-DTAG | WA5390366 | 1 | Schindler Lifts Australia | Lift 1 is showing “out of service” | Lifts | Lifts |  | Fail | Fail | 23 | 23 | 0 | 2022-05-02 12:19 | 2022-05-03 17:00 | 2022-10-13 20:02 | 2022-05-03 17:00 | 2022-10-13 20:02
MSA-DTAG | WA5393721 | 2 | Schindler Lifts Australia | Level 15 - waiter service door is very stiff to open & close, light on level 15 not illuminating | Lifts | Lifts |  | Fail | Fail | 22 | 22 | 0 | 2022-05-04 09:50 | 2022-05-09 17:00 | 2022-10-13 20:02 | 2022-05-09 17:00 | 2022-10-13 20:02
MSA-DTWD | WA5399054 | 1 | Complete Pest Management Services | Ant infestation needs some baits | Pest Control | General Pest | 275.25 | Pass | Pass | 0 | 0 | 0 | 2022-05-09 14:24 | 2022-05-10 17:00 | 2022-05-10 06:45 | 2022-05-10 17:00 | 2022-05-10 06:45 |  |  | Inspected and treated for Coastal Brown Ants reported in G19Ants found tracking in from all surrounding areas.Recommend that all harbourage areas be treated to break the breeding cycle and prevent ongoing infestation ofbuildings.There is an extremely large population of ants at this campus the complete grounds need to be sprayed
MSA-DCA | WA5399194 | 2 | FCT SURFACE CLEANING | External Area - removal of graffiti on front hoarding including windows | Cleaning | Graffiti |  | Fail | Fail | 5 | 5 | 0 | 2022-05-09 17:26 | 2022-05-12 17:00 | 2022-06-15 20:09 | 2022-05-12 17:00 | 2022-06-15 20:09
MSA-DTWD | WA5454597 | 1 | Equans Mechanical Services Australia | Staff Room B16 - Air conditioner not working | Air Conditioning | Room Air Conditioners | 769.52 | Pass | Pass | 0 | 0 | 0 | 2022-05-17 12:38 | 2022-05-18 17:00 | 2022-05-18 15:00 | 2022-05-18 17:00 | 2022-05-18 15:00 |  |  | Attended site, investigated staff room B16 Apac AC unit, found time clock battery have failed. Left site, went to suppliers and picked up new batteries, returned back to site. Fitted new battery and tested AC. All OK. Filled out paperwork
MSA-DTAG | WA5454900 | 1 | Codee Cleaning Services | Ground - Custody - Cell 3 - Bio Clean - Urine on floor from accused in custody | Cleaning | Cleaning | 280 | Fail | Fail | 0 | 0 | 0 | 2022-05-17 16:13 | 2022-05-18 17:00 | 2022-05-19 18:09 | 2022-05-18 17:00 | 2022-05-19 18:09 |  |  | clean completed 17/05/2022
MSA-DTAG | WA5459737 | 3 | Schindler Lifts Australia | Level 4 - Public lifts on side of building - Plastic cover for lift buttons missing | Lifts | Lifts |  | Fail | Fail | 20 | 20 | 0 | 2022-05-18 08:31 | 2022-05-25 17:00 | 2022-10-13 20:02 | 2022-05-25 17:00 | 2022-10-13 20:02
MSA-DCA | WA5462039 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis Street -Basement Level - Security Control Room - Broken Faulty Security screen to video wall | Security | Monitoring | 550 | Fail | Fail | 8 | 8 | 0 | 2022-05-19 10:51 | 2022-05-20 17:00 | 2022-07-14 09:23 | 2022-05-20 17:00 | 2022-07-14 09:23 |  |  | Completed
MSA-DCA | WA5472236 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Controller 7 - failed - level cameras not working | Security | Access Control | 2374.9 | Fail | Fail | 7 | 7 | 0 | 2022-05-23 16:19 | 2022-05-23 18:19 | 2022-07-14 09:50 | 2022-05-23 20:19 | 2022-07-14 09:50 |  |  | Completed
MSA-DTWD | WA5478080 | 1 | Schindler Lifts Australia | L block Lift not working | Lifts | Lifts |  | Fail | Fail | 20 | 20 | 0 | 2022-05-26 08:45 | 2022-05-27 17:00 | 2022-10-13 20:02 | 2022-05-27 17:00 | 2022-10-13 20:02
MSA-DTWD | WA5481346 | 1 | Equans Mechanical Services Australia | Air con BMS - Ground - Rooms AT201 to AT209 in alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 78.49 | Pass | Pass | 0 | 0 | 0 | 2022-05-30 12:25 | 2022-05-31 17:00 | 2022-05-31 08:30 | 2022-05-31 17:00 | 2022-05-31 08:30 |  |  | Checked system, found it was the vrv requiring a new capillaries, parts arriving in the next few days REFER WA5378559
MSA-DFES | WA5511900 | 2 | Precise Air Group | Ground Floor - FF Dorm 2 - New A/C unit displays error code and not working - see notes below | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 0 | 2022-06-13 10:55 | 2022-06-16 17:00 | 2022-06-16 09:19 | 2022-06-16 17:00 | 2022-06-16 09:19 |  |  | Equipment is working as per spec
MSA-DCA | WA5564887 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Retrospective Work Order - Humidity Alarms for Galllery 1 | Air Conditioning | Room Air Conditioners | 183.15 | Fail | Fail | 18 | 18 | 0 | 2022-02-16 03:29 | 2022-02-16 05:29 | 2022-06-21 12:43 | 2022-02-16 07:29 | 2022-06-21 12:43 | 1 |  | Completed
MSA-DCA | WA5565233 | 1 | TK Elevator Australia Pty Ltd | Lift 7 broken down again - displaying Out of Order | Lifts | Lifts |  | Fail | Fail | 2 | 2 | 0 | 2022-06-21 15:21 | 2022-06-22 17:00 | 2022-07-04 20:06 | 2022-06-22 17:00 | 2022-07-04 20:06
MSA-DTWD | WA5565386 | 3 | NEYLOR | B314.2 - blinds wont close | Building | Internal Screens | 140 | Fail | Fail | 4 | 4 | 0 | 2022-06-22 07:19 | 2022-06-28 17:00 | 2022-07-28 09:33 | 2022-06-28 17:00 | 2022-07-28 09:33 |  |  | Completed & invoiced
MSA-DFES | WA5569526 | 3 | MR POTHOLE | Driveway- Pot holes needing to be fixed - See notes below | Building | General Building |  | Fail | Fail | 4 | 4 | 0 | 2022-06-27 15:27 | 2022-07-04 17:00 | 2022-07-29 20:02 | 2022-07-04 17:00 | 2022-07-29 20:02
MSA-DTWD | WA5589512 | 3 | AWB Co. | Water leaking from gutter down window into duct work to office below | Roofing | Guttering | 460.25 | Pass | Pass | -1 | -1 | 0 | 2022-07-08 13:41 | 2022-07-15 17:00 | 2022-07-11 02:00 | 2022-07-15 17:00 | 2022-07-11 02:00 |  |  | Investigated leak - found perish silicon on window seal and cladding. Found hole in sheet and unsealed join on flashings. Cleaned all old silicon and resealed all
MSA-DFES | WA5596761 | 3 | AWB Co. | 22 (Station Officer’s locker room) - Sliding door is stuck open and requires force to close | Building | Doors |  | Pass | Pass | 0 | 0 | 0 | 2022-07-11 10:14 | 2022-07-18 17:00 | 2022-07-15 20:08 | 2022-07-18 17:00 | 2022-07-15 20:08
MSA-DCA | WA5675973 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Centenary Gallery - 2 and 3 - FCU 2 - humidity alarm. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 627.825 | Fail | Fail | 2 | 2 | 0 | 2022-07-23 08:06 | 2022-07-23 10:06 | 2022-08-09 11:07 | 2022-07-23 12:06 | 2022-08-09 11:07 |  |  | Completed
MSA-DTAG | WA5677290 | 1 | Codee Cleaning Services | Ground custody-Bio Clean – Cell 3, Holding cell 2 and interview room 1-see notes | Cleaning | Emergency Cleans | 500 | Fail | Fail | 1 | 1 | 0 | 2022-07-25 13:42 | 2022-07-26 17:00 | 2022-08-01 16:55 | 2022-07-26 17:00 | 2022-08-01 16:55 |  |  | completed 25/07/2022
MSA-DTWD | WA5680713 | 3 | Boilertronics | Boiler 1 in fault | Mechanical Services | Boilers | 317.75 | Pass | Pass | 0 | 0 | 0 | 2022-07-27 14:58 | 2022-08-03 17:00 | 2022-08-03 16:29 | 2022-08-03 17:00 | 2022-08-03 16:29 |  |  | Travel to site. Sign in gain access. Both boilers not running in plant room. Boiler 1 had no power to controller. Check through circuit and find and had power at terminal 2 not terminal 3. Between terminal 2 and 3 there was a BMS relay. On the drawing looks to be a pump interlock relay. Go down to first floor BMS room with Theo and investigate. Boiler 1 pump although was running in plant room was displaying as an alarm on BMS. Neither of us could figure out how to clear alarm. Believe this alarm is probably holding out the boiler and the pump interlock. We decided it’s best that we get a controls professional to come out and have a look at the BMS setup as it appears there are issues present and it’s what is holding out the boiler.
MSA-DCA | WA5687270 | 1 | EQUANS Mechanical Services (WA) Pty Limited | basment-security control room-Interlock entry points failures following server updates-see notes | Air Conditioning | Room Air Conditioners | 1597.2 | Fail | Fail | 7 | 7 | 0 | 2022-08-01 14:56 | 2022-08-02 17:00 | 2022-09-23 11:28 | 2022-08-02 17:00 | 2022-09-23 11:28 |  |  | Completed
MSA-DTWD | WA5687275 | 3 | Schneider Electric Australia Pty Ltd | N223 - Door not securing | Security | Access Control |  | Pass | Pass | 0 | 0 | 0 | 2022-08-01 15:02 | 2022-08-08 17:00 | 2022-08-08 17:00 | 2022-08-08 17:00 | 2022-08-08 17:00 |  |  | SV22011485/5200415770replace faulty Lock on Control Room Door
MSA-DCA | WA5696948 | 0 | EQUANS Mechanical Services (WA) Pty Limited | SCU 7 Humidifier alarm galleries 10 - 13 | Air Conditioning | Room Air Conditioners | 546.18 | Fail | Fail | 2 | 2 | 0 | 2022-08-09 00:04 | 2022-08-09 02:04 | 2022-08-22 10:49 | 2022-08-09 04:04 | 2022-08-22 10:49 |  |  | Completed
MSA-MRWA | WA5699767 | 2 | EQUANS Mechanical Services (WA) Pty Limited | fume cupboard - failed | Air Conditioning | Room Air Conditioners | 484.23 | Pass | Pass | -1 | -1 | 0 | 2022-08-10 12:14 | 2022-08-15 17:00 | 2022-08-10 13:00 | 2022-08-15 17:00 | 2022-08-10 13:00 |  |  | Investigation complete see notes.
MSA-DTAG | WA5747774 | 1 | Codee Cleaning Services | Retrospective work order for a bio-clean – 15 July 2022 from 19:30pm - 22:00pm (2.5hrs) | Cleaning | Cleaning | 280 | Fail | Fail | 1 | 1 | 0 | 2022-08-15 07:21 | 2022-08-15 17:00 | 2022-08-19 22:27 | 2022-08-15 17:00 | 2022-08-19 22:27 | 1 |  | Completed 15/07/2022
MSA-DTWD | WA5829568 | 2 | Precise Air Group | Air con not working, please investigate | Air Conditioning | Room Air Conditioners | 152.03 | Pass | Pass | 0 | 0 | 0 | 2022-09-02 14:24 | 2022-09-07 17:00 | 2022-09-07 09:27 | 2022-09-07 17:00 | 2022-09-07 09:27 |  |  | Attended site signed in and located reported area. Carried o ut tests and found breaker for unit had tripped. Restored po wer and tested unit. Ac returned to normal operation. Unit a ppears to be nearing end of life reccomend budgeting to repl ace.
MSA-DCA | WA5830225 | 0 | EQUANS Mechanical Services (WA) Pty Limited | P1 Alarm Humidifier | Air Conditioning | Building HVAC Maintenance (Major Plant) | 337.835 | Fail | Fail | 1 | 0 | 0 | 2022-09-02 21:14 | 2022-09-02 23:14 | 2022-09-06 09:47 | 2022-09-03 01:14 | 2022-09-06 09:47 |  |  | Completed
MSA-DFES | WA5833657 | 3 | Critical Fire Protection & Training | Engine Room/ Duty Room - Fire door closer has failed | Building | Fire Door | 581.3 | Pass | Pass | -1 | -1 | 0 | 2022-09-06 11:04 | 2022-09-13 17:00 | 2022-09-07 09:04 | 2022-09-13 17:00 | 2022-09-07 09:04 |  |  | replaced door closer
MSA-DCA | WA5836792 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Vault - The air con vent is falling from the ceiling | Air Conditioning | Materials | 259.01 | Fail | Fail | 2 | 2 | 0 | 2022-09-07 14:28 | 2022-09-07 16:28 | 2022-09-19 12:32 | 2022-09-07 18:28 | 2022-09-19 12:32 |  |  | Completed
MSA-DTAG | WA5977079 | 1 | Codee Cleaning Services | ground custody-Bio Clean – Cell 3-see notes | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0 | 2022-09-27 13:33 | 2022-09-28 17:00 | 2022-09-30 00:22 | 2022-09-28 17:00 | 2022-09-30 00:22 |  |  | completed 27/09/2022
MSA-DTAG | WA5977338 | 1 | OCS SERVICES PTY LTD | Cell 4 - Fault description Require bio clean to cell 4 as blood is on wall/window | Cleaning | Emergency Cleans | 1 | Pass | Pass | 0 | 0 | 0 | 2022-09-27 16:22 | 2022-09-28 17:00 | 2022-09-28 09:30 | 2022-09-28 17:00 | 2022-09-28 09:30 |  |  | When OCS arrived they were notified the job had been completed the night before by onsite cleaners this is a call out fee onlyNo signature slip as no works were completed Bernie SAlderson spoke to the Programmed hotline who is aware the works were done before we arrived onsite
MSA-DTWD | WA6014557 | 1 | PEEL LOCK SERVICES PTY LTD | Room D09 - Fault description Door latch forced off frame / Latch repair & door frame reinforcing | Security | Locksmith |  | Fail | Fail | 12 | 12 | 0 | 2022-10-12 10:06 | 2022-10-13 17:00 | 2023-01-03 20:09 | 2022-10-13 17:00 | 2023-01-03 20:09 |  |  | Cancelled as not a locksmith issue - New work order number WA6014616
MSA-DFES | WA6088852 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Restrospective WO - lost power to lights on level 2 | Electrical | Lighting, Internal | 119.43 | Pass | Pass | -1 | -1 | 0 | 2022-10-19 10:31 | 2022-10-24 17:00 | 2022-10-19 10:31 | 2022-10-24 17:00 | 2022-10-19 10:31 |  |  | Onsite 900 checked and tested power to tripped circuit. Power was in separate area to where we were working and Adam how completed work said no other breakers were off. Have tested and check rcvo and appliances and all seem fine. Signed out 930
MSA-DCA | WA6127773 | 1 | Techworks Electrical | Retrospective WO – Do not attend - RCD tripped - 13/10/2022 | Electrical | General Electrical | 71.7975 | Pass | Pass | 0 | 0 | 0 | 2022-10-13 07:00 | 2022-10-13 17:00 | 2022-10-13 17:00 | 2022-10-13 17:00 | 2022-10-13 17:00 | 1 |  | Turned off the breaker and turned it back on hoping the curtain would come back up after the Power reset, this did not work. I suggested that the issue will be either at the FIP or up in the ceiling above one of the manholes next to the curtain. To access the manholes you would need a scissor, so not knowing at this stage there was a fire tech on site at the FIP, I said I would go look at it to see if there was anything obvious on the screen, as I got down to the FIP I met up with the fire tech, who I believe was called Jake but I may be mistaken, who said he couldn’t see anything on the FIP either. We both went back up to the curtain and he had a brief look around, then said that the curtain was not as high a priority as the window, the curtain can have Bollards around it and be left for now. The window was also on level 1 around the other side of the building, I checked the DB and found all power was on to it. The door was stuck open, it would begin to close and then immediately op
MSA-DTWD | WA6128090 | 2 | Techworks Electrical | E Block Hallway - the high bay lights are not working | Electrical | Lighting, Internal | 1706.535 | Pass | Pass | 0 | 0 | 0 | 2022-10-26 12:16 | 2022-10-31 17:00 | 2022-10-28 12:30 | 2022-10-31 17:00 | 2022-10-28 12:30 |  |  | Hallway-4 lights replaced in the walk way ceiling that are not working
MSA-DTWD | WA6130283 | 2 | AWB Co. | Library above MFD (printer)-light is faulty after changing the starter and tube.-see notes | Electrical | Lighting, Internal | 209.04 | Pass | Pass | 0 | 0 | 0 | 2022-10-28 11:04 | 2022-11-02 17:00 | 2022-10-31 10:45 | 2022-11-02 17:00 | 2022-10-31 10:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Went to library and located faulty light fitting above printer. Spoke to librarians in area and they said that someone from the tafe had fixed it. Only 1 tube was working. Librarians said that they are happy with the light fitting and will get it replaced when the other one fails. Spoke to Steve and he said Allgood to close off the job. Took picture. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6144780 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Gallery 1 - FCU1 - Humidity Alarm activated | Air Conditioning | Room Air Conditioners | 202.705 | Pass | Pass | 0 | 0 | 0 | 2022-11-02 09:02 | 2022-11-03 17:00 | 2022-11-02 09:03 | 2022-11-03 17:00 | 2022-11-02 09:03 |  |  | Checked out high humidity alarms on FCU 1 and 3 in centenary. Checked outside air dampers, valves and bms. System rummimg fine, alarms cleared on their own.
MSA-DTAG | WA6145489 | 1 | Schindler Lifts Australia | Ground - Lift 9 - Lift door not opening. Faulty | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0 | 2022-11-02 12:20 | 2022-11-03 17:00 | 2022-11-04 20:03 | 2022-11-03 17:00 | 2022-11-04 20:03
MSA-DTWD | WA6147854 | 1 | WESTERN IRRIGATION PTY LTD | J Block campus Bore pump not working | Plumbing & Drainage | Water | 287.5 | Pass | Pass | 0 | 0 | 0 | 2022-11-03 10:29 | 2022-11-04 17:00 | 2022-11-03 15:00 | 2022-11-04 17:00 | 2022-11-03 15:00 |  |  | Apparently Gefri 0418 914 327 the site maintenance manager is still waiting for the old tank floats to be replaced as part of the recent tank upgrade works.
MSA-DCA | WA6154409 | 3 | TK Elevator Australia Pty Ltd | Ground Floor - Lift – Fault Message on broadcast - See notes below | Lifts | Lifts |  | Fail | Fail | 2 | 2 | 0 | 2022-11-07 12:28 | 2022-11-14 17:00 | 2022-12-01 20:04 | 2022-11-14 17:00 | 2022-12-01 20:04
MSA-DTWD | WA6166063 | 3 | M Construction (WA) | Block E - Level 1 - Room E21 - Door hinge broken - Broken hinge is in Facilities Office | Building | Doors | 979.35 | Pass | Pass | 0 | 0 | 0 | 2022-11-11 11:53 | 2022-11-18 17:00 | 2022-11-16 10:00 | 2022-11-18 17:00 | 2022-11-16 10:00 |  |  | 16/11/2022:1. Door Hinges broken2. Closer not working3. Temporarily secured door4. Sourced non-standard door hinges and fitted5. Door damaged as well and requires repair17/11/20221. Repaired damage door and painted as required2. Fit door closer
MSA-DTWD | WA6184272 | 3 | AWB Co. | Ground - staff room/store room - Light out | Electrical | Lighting, Internal | 225.19 | Pass | Pass | -1 | -1 | 0 | 2022-11-15 11:13 | 2022-11-22 17:00 | 2022-11-17 12:00 | 2022-11-22 17:00 | 2022-11-17 12:00 |  |  | Attended site signed in jsa completed. Found faulty tubes in light fitting. Replaced with new tubes and two new starters. Tested operational.Job completed
MSA-DTWD | WA6249774 | 2 | AWB Co. | Light fitting fallen from ceiling in Transmission workshop 3D17 | Electrical | General Electrical | 301.405 | Pass | Pass | 0 | 0 | 0 | 2022-11-21 14:37 | 2022-11-24 17:00 | 2022-11-23 12:00 | 2022-11-24 17:00 | 2022-11-23 12:00 |  |  | Attended site and signed in. Completed JSA. Liasied with site about works going ahead. Located 3D17 and light hanging. Terminated cables. Secured light back up to railing. Notified relevant personnel of works completed. **job complete**
MSA-DFES | WA6257129 | 2 | Go Doors | Gate 007 speed is too slow and needs adjusting - see notes | Building | Steel Fencing & Gates | 333.56 | Pass | Pass | -1 | -1 | 0 | 2022-11-24 12:10 | 2022-11-29 17:00 | 2022-11-24 12:10 | 2022-11-29 17:00 | 2022-11-24 12:10 |  |  | complete
MSA-DTWD | WA6257243 | 1 | Techworks Electrical | Admin office - A section of the office area has no power to the GPOs - see notes | Electrical | General Electrical | 326.61 | Pass | Pass | 0 | 0 | 0 | 2022-11-24 13:16 | 2022-11-25 17:00 | 2022-11-24 17:00 | 2022-11-25 17:00 | 2022-11-24 17:00 |  |  | Located DB’s throughout building, tested load side of RCD’s due to no labelling on outlets, found issue with lead which was damaged causing RCD to trip. Re set no issues.
MSA-DTAG | WA6301161 | 1 | Codee Cleaning Services | Registry/ Building - Bio Clean – Cell 3 - see notes below | Cleaning | Emergency Cleans | 301.28 | Fail | Fail | 0 | 0 | 0 | 2022-12-02 14:30 | 2022-12-05 17:00 | 2022-12-06 10:19 | 2022-12-05 17:00 | 2022-12-06 10:19 |  |  | Completed
MSA-DTWD | WA6361523 | 2 | NEYLOR | Repair defective vertical blinds | Building | Curtains & Blinds | 1184.48 | Fail | Fail | 8 | 8 | 0 | 2022-12-08 10:20 | 2022-12-13 17:00 | 2023-02-07 13:19 | 2022-12-13 17:00 | 2023-02-07 13:19 |  |  | Completed on Tuesday 23/1/23
MSA-MRWA | WA6362252 | 1 | Schindler Lifts Australia | Lift cart 3-stuck on level 1 with doors open | Lifts | Lifts |  | Fail | Fail | 1 | 1 | 0 | 2022-12-09 09:06 | 2022-12-12 17:00 | 2022-12-20 20:14 | 2022-12-12 17:00 | 2022-12-20 20:14
MSA-DCA | WA6376152 | 2 | FCT SURFACE CLEANING | Graffiti in various locations - see notes | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 0 | 2022-12-15 12:55 | 2022-12-20 17:00 | 2022-12-15 13:00 | 2022-12-20 17:00 | 2022-12-15 13:00 |  |  | Cleaned graffiti
MSA-DTAG | WA6379427 | 2 | Water2water Pty Ltd | 1987 Level 2 - Sheriff's Office - Billi Tap not working | Plumbing & Drainage | Water | 679.92 | Pass | Pass | 0 | 0 | 0 | 2022-12-19 11:17 | 2022-12-22 17:00 | 2022-12-21 10:25 | 2022-12-22 17:00 | 2022-12-21 10:25 |  |  | Replaced faulty element. Calibrated all ok.
MSA-DCA | WA6393323 | 3 | Precise Air Group | Level 1 - Office 5 -Sensorium - Air Con Fault | Air Conditioning | Room Air Conditioners | 617.935 | Pass | Pass | 0 | 0 | 0 | 2022-12-28 12:19 | 2023-01-05 17:00 | 2023-01-05 07:58 | 2023-01-05 17:00 | 2023-01-05 07:58
MSA-DTAG | WA6403716 | 1 | Codee Cleaning Services | Ground - Custody - Bio Clean – Cell 1 (spit on window and floor) | Cleaning | Cleaning | 301.28 | Fail | Fail | 0 | 0 | 0 | 2023-01-06 14:20 | 2023-01-09 17:00 | 2023-01-10 16:12 | 2023-01-09 17:00 | 2023-01-10 16:12
MSA-DTWD | WA6405505 | 2 | Techworks Electrical | Ethernet port not working No PP7-P7-18 | Electrical | General Electrical | 183.015 | Pass | Pass | 0 | 0 | 0 | 2023-01-09 14:49 | 2023-01-12 17:00 | 2023-01-10 14:00 | 2023-01-12 17:00 | 2023-01-10 14:00
MSA-DTWD | WA6482178 | 3 | NEYLOR | Repair Blinds to A321 | Building | Curtains & Blinds | 711 | Fail | Fail | 6 | 6 | 0 | 2023-01-18 07:58 | 2023-01-24 17:00 | 2023-03-07 13:50 | 2023-01-24 17:00 | 2023-03-07 13:50
MSA-DTWD | WA6482410 | 3 | AWB Co. | Faulty 15AMP - plug on high temp | Electrical | General Electrical | 325.03 | Pass | Pass | 0 | 0 | 0 | 2023-01-18 10:10 | 2023-01-25 17:00 | 2023-01-25 12:00 | 2023-01-25 17:00 | 2023-01-25 12:00
MSA-DTAG | WA6504431 | 1 | Sapio Pty Ltd | Levels 4, 5, 6, 9 & 10 - Alarms in fault - See notes | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0 | 2023-01-19 16:37 | 2023-01-20 17:00 | 2023-01-20 11:47 | 2023-01-20 17:00 | 2023-01-20 11:47
MSA-DTWD | WA6544497 | 3 | AHS Services WA Pty Ltd (Anchor) | Missing tap handles to sink | Plumbing & Drainage | Water | 293.7075 | Fail | Fail | 1 | 1 | 0 | 2023-02-10 13:19 | 2023-02-17 17:00 | 2023-02-21 11:30 | 2023-02-17 17:00 | 2023-02-21 11:30
MSA-DTWD | WA6650967 | 2 | WESTERN IRRIGATION PTY LTD | Re-tic pump keeps going out - No flow | Plumbing & Drainage | Water | 860.47 | Pass | Pass | 0 | 0 | 0 | 2023-02-20 15:13 | 2023-02-23 17:00 | 2023-02-22 14:00 | 2023-02-23 17:00 | 2023-02-22 14:00
MSA-DTWD | WA6674274 | 2 | LIGHTHOUSE LOCKSMITHS | Admin - Gate - Faultylock on gate - Cleaners store room - Faulty lock | Security | Locksmith | 200 | Pass | Pass | 0 | 0 | 0 | 2023-02-27 09:13 | 2023-03-02 17:00 | 2023-02-27 12:50 | 2023-03-02 17:00 | 2023-02-27 12:50