## Export
Contract | Work Order | Prio | Vendor | Work Description | Service Type | Service Sub type | Claim Amount | Response SLA Compliance | Completion SLA Compliance | Weeks from Target Response | Weeks from Target Rectification | Time to Complete (hrs) | Service Request Creation Date | Target Start | Actual Start | Target Finish | Actual Finish | Retrospective | Status | Completion Notes
MSA-DTWD | WA5009967 | 2 | Techworks Plumbing | U Block - Compressor - Water leak in compressor room | Plumbing & Drainage | Materials | 2970.79 | Pass | Fail | -1 | 52 | 8898.5 | 2022-01-12 08:53 | 2022-01-17 17:00 | 2022-01-12 14:30 | 2022-01-17 17:00 | 2023-01-18 09:00 |  | WACCES | Attended site to find leak on unit light,
MSA-DTWD | WA5133309 | 1 | Precise Air Group | A Block - Ground - A52 - see details below | Air Conditioning | Room Air Conditioners | 813.275 | Pass | Fail | 0 | 49 | 8186.3833 | 2022-02-15 09:28 | 2022-02-16 17:00 | 2022-02-16 07:30 | 2022-02-16 17:00 | 2023-01-23 09:53 |  |  | Refitted covering as instructed. works complete
MSA-DTWD | WA5189195 | 1 | Precise Air Group | chiller not working to whole building | Air Conditioning | Building HVAC Maintenance (Major Plant) | 16626.005 | Pass | Fail | 0 | 47 | 7924.4167 | 2022-02-23 15:18 | 2022-02-24 17:00 | 2022-02-24 07:30 | 2022-02-24 17:00 | 2023-01-20 11:55 |  |  | Travelled to kendrew picked up required keys, headed to Mclarty campus, gained access to chiller compound found chiller system not in fault and being held out externally, gained access to BMS in Q block, found no faults on system, checked all set points, found DP on chiller one set point at 30kpa, but water pressure only sitting at 20kpa, which maybe be causing chiller to be helped out, when and isolated inlet valve to DP switch to check operation then switched to the outlet side, found no issues, unable to determine what the chiller status requires for water flow on system. Gained access back to BMS, attempted to switch chillers over from cchiller 1 lead to chiller 2 lead. Once system was reset was able to have chiller 2 change over and start over. Further investigation is required to have system running at 100%
MSA-DTWD | WA5085605 | 1 | Precise Air Group | B Block - Ground - B45 - Chiller in Fault | Refrigeration | Chiller | 1213.32 | Pass | Fail | 0 | 39 | 6671.25 | 2022-01-21 09:15 | 2022-01-24 17:00 | 2022-01-21 10:30 | 2022-01-24 17:00 | 2022-10-26 09:45 |  |  | Further works completed on WA5203039 B block - B45 - PLC Labratory - System 1 in fault due to motor overcurrent air vision on site to repair SYS 2 found fuse holders and wiring burned on system 1
MSA-DTWD | WA5295025 | 2 | Precise Air Group | Kendrew- E-Block Restaurant Kitchen service fridge not working | Air Conditioning | Room Air Conditioners | 2943.61 | Pass | Fail | 0 | 39 | 6525 | 2022-03-29 10:41 | 2022-04-01 17:00 | 2022-03-30 12:00 | 2022-04-01 17:00 | 2022-12-27 09:00 |  |  | Arrived on site and signed in as necessary. Went tofridge and confirmed isolation. Removed existingcontroller and replaced with new. Comfired wiring with manufacture. Signed out.
MSA-DCA | WA5186708 | 1 | Precise Air Group | A/C - 5.4 - unit not operating | Air Conditioning | Room Air Conditioners | 2554.5 | Pass | Fail | 0 | 38 | 6430.3 | 2022-02-22 08:55 | 2022-02-23 17:00 | 2022-02-22 11:39 | 2022-02-23 17:00 | 2022-11-17 09:57 |  | WACCES | Found Fan motor and PCB burn out, requires replacing. BRAF submitted Picked up parts from office, attended site and signed in. Spoke to supervisor about what unit required repairs. Isolated unit and tested. Removed fan motor and board from unit the installed new ones. Once system was energised found a communication fault showing up. Spoke to Fujitsu and went through their checks and was advised a Fujitsu tech may need to attend site to commission the new board and readdress the units for the multi system. Email sent to supervisor.Boards and parts swapped out and units re addressed, units operating
MSA-DCA | WA5133732 | 1 | Precise Air Group | Basement - Downstairs at the Maj theatre (DSATM) - APAC AC unit starting ok, but no compressors run | Air Conditioning | Room Air Conditioners | 7788.62 | Fail | Fail | 0 | 38 | 6384 | 2022-02-15 13:26 | 2022-02-16 17:00 | 2022-02-17 09:14 | 2022-02-16 17:00 | 2022-11-10 09:14 |  | WACCES | Attended site, found basemanrt unit stage 1 compressor tripped, began fault finding through system found stage 1 compressor down to earth. Tool required information to submit BRAfDue to the leaking heat exchanger, these works have stopped, the recommendation would be to replace the exchanger or the entire unit as the unit would be over 30 years old.will submit an invoice for works to date. quote to follow for repairs and replacing
MSA-DTWD | WA5068962 | 1 | Precise Air Group | Room - M008 & M009 - air con is faulty | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1414.72 | Pass | Fail | 0 | 38 | 6308.5 | 2022-01-19 13:07 | 2022-01-20 17:00 | 2022-01-20 11:30 | 2022-01-20 17:00 | 2022-10-10 08:00 |  |  | Attended site and ran after letting de ice overnight. Unit ran in cooling in both stages unable to confirm pressures due to service valves being seized shut. Due to age Unit appears to be less efficient and I would recommend upgrading.
MSA-DTWD | WA5151159 | 1 | Precise Air Group | M021 - air con is blowing hot air | Air Conditioning | Room Air Conditioners | 796.215 | Pass | Fail | 0 | 36 | 6118.55 | 2022-02-17 11:14 | 2022-02-18 17:00 | 2022-02-18 12:00 | 2022-02-18 17:00 | 2022-10-31 10:33 |  |  | Attended site signed in and gained access to reported area. Carried out possible checks but unable to control unit properly as BMS has become obsolete and no longer accessible. With this I suspect the board and overload may be faultyTravelled to site checked operation of AC 5 that services MO 21 traced all circuits,checked BMS ,and checked thermostat control, found burnt out PC BOARD and faulty control relay both need replacing no switching to cooling cycle.
MSA-DTWD | WA5151625 | 2 | Precise Air Group | B Block - B205 - AirCon not working - Control panel flashing | Air Conditioning | Room Air Conditioners | 2008.85 | Pass | Fail | 0 | 36 | 6047.5 | 2022-02-17 14:55 | 2022-02-22 17:00 | 2022-02-21 12:00 | 2022-02-22 17:00 | 2022-10-31 11:30 |  | WACCES | Picked up parts for Daikin ac 2 cond fan motor's 1 PCboard, travelled to site,removed old motor's and PC board installed new parts and test run unit running very welljob completed
MSA-DTWD | WA5053109 | 1 | Precise Air Group | Air con not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 366 | Pass | Fail | 0 | 35 | 5857 | 2022-01-18 13:15 | 2022-01-19 17:00 | 2022-01-19 07:00 | 2022-01-19 17:00 | 2022-09-20 08:00 |  |  | Attended service call went over checks for mechanical equipment and Refrigeration charges nothing seemed to have majorly failed. I suspect due to units age, ambient conditions and area needed to serve the unit was operating out of spec and no longer as efficient as it once was. I recommend replacing unit or adding additional cooling to area. Sub contractor to attendcto quote
MSA-DCA | WA5142353 | 1 | Precise Air Group | Air con faulty | Air Conditioning | Room Air Conditioners | 7277.45 | Fail | Fail | 2 | 37 | 5831 | 2022-02-16 14:37 | 2022-02-17 17:00 | 2022-03-02 09:00 | 2022-02-17 17:00 | 2022-10-31 08:00 |  |  | Unable to assess unit due to height. Will contact sub contractor to provide options for relocation
MSA-DTWD | WA5115818 | 2 | Precise Air Group | S Block - Level 2 - S203..S200 - Aircon temp setting is too high , cannot be adjusted | Air Conditioning | Room Air Conditioners | 734.29 | Fail | Fail | 1 | 34 | 5542.5 | 2022-02-11 09:30 | 2022-02-16 17:00 | 2022-02-21 10:00 | 2022-02-16 17:00 | 2022-10-10 08:30 |  |  | Adjusted ac settings
MSA-DTWD | WA5187401 | 2 | Equans Mechanical Services Australia | Investigate fault on stage 2 and 3 on chiller 2 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 5721.82 | Pass | Fail | 0 | 33 | 5542.1 | 2022-02-22 13:06 | 2022-02-25 17:00 | 2022-02-22 14:30 | 2022-02-25 17:00 | 2022-10-11 12:36 |  |  | Returned to site and rechecked. Valve water noise found to be present when valve are opening and allowing flow between 0-20% operation. BMS tech will be contacted to come up with an operation strategy that can be implemented when they attend site for a PM. Please note that the units are working as per design and have previously had auto air relief points fitted to water lines to assist in reducing noise. Work area left tidy.
MSA-DTAG | WA5175828 | 2 | Schindler Lifts Australia | Lift three - Out of service – no longer working | Lifts | Lifts |  | Pass | Fail | 0 | 32 | 5449.1667 | 2022-02-21 13:11 | 2022-02-24 17:00 | 2022-02-22 08:50 | 2022-02-24 17:00 | 2022-10-07 10:00 |  |  | Lift attempting to complete sync run on arrival, T5 missing. Lift 200mm below top floor. Inspected car doors & found front RHhanger roller failed causing KTC to not make. Replaced with spare on site. Tested. All ok. Lift in serviceto be closed out at $0 cost
MSA-DTWD | WA5567977 | 3 | AHS Services WA Pty Ltd (Anchor) | Zip Boiler not working | Plumbing & Drainage | HWS/Units Electric & Gas | 680.93 | Fail | Fail | 1 | 33 | 5354.0333 | 2022-06-24 14:09 | 2022-07-01 17:00 | 2022-07-08 07:47 | 2022-07-01 17:00 | 2023-02-16 09:49 |  |  | Replaced faulty tap loom cable.
MSA-DCA | WA5319243 | 2 | Precise Air Group | Meeting Room- Air con not working -Timer light flashes - See notes | Air Conditioning | Room Air Conditioners | 329.67 | Pass | Fail | -1 | 31 | 5334.2333 | 2022-04-12 13:37 | 2022-04-19 17:00 | 2022-04-13 08:00 | 2022-04-19 17:00 | 2022-11-21 14:14 |  |  | works complete, unable to get replacement parts
MSA-DTWD | WA5688060 | 3 | Protek 24/7 Building & Maintenance | Shade sail and all large umbrellas damaged in storm | Building | General Building | 11760.41 | Fail | Fail | 1 | 31 | 5061.5 | 2022-08-02 09:31 | 2022-08-09 17:00 | 2022-08-15 13:45 | 2022-08-09 17:00 | 2023-03-14 11:15 |  | WACCES | Sail 1 - Remove sail for repair, Install new mount in steel beam & reinstall repaired sail Cable has rubbed through pocket on beam when sail came down in stormUmbrella 1 - Remove and dispose of storm damaged umbrella, Supply and install new Heavy Duty 4.0m Square Umbrella, Frame Colour: White, Canopy Colour: White PVCUmbrella 2 - Remove umbrella for assessment, carry out minor repairs & re-installUmbrella 3 - Remove and dispose of storm damaged umbrella, Supply and install new Heavy Duty 4.0m Square Umbrella, Frame Colour: White, Canopy Colour: White PVCUmbrella 4 - Remove umbrella for assessment, carry out minor repairs & re-install
MSA-DTWD | WA5481627 | 2 | Precise Air Group | ground - E-Block - staff office E40 - aircon not working | Air Conditioning | Room Air Conditioners | 13353.755 | Pass | Fail | 0 | 30 | 5035.5833 | 2022-05-30 15:09 | 2022-06-02 17:00 | 2022-05-31 13:30 | 2022-06-02 17:00 | 2022-12-27 09:05 |  |  | Replaced failed AC unit. Operating correctly now
MSA-DTWD | WA5706228 | 0 | Precise Air Group | AC2 and AC3 in M Block are tripping out | Air Conditioning | Room Air Conditioners | 3676.84 | Fail | Fail | 0 | 30 | 4994.4833 | 2022-08-11 09:39 | 2022-08-11 11:39 | 2022-08-11 14:30 | 2022-08-11 13:39 | 2023-03-07 16:59 |  | WACCES | after completing the controls issue with old redundant Mizco AC control pannels, time was taken to get Mizco wiring diagrams (none on site) controls tech returned and resolved controls issues.Site requested this job was left open should their be any more intermittent faults, units left in heating all ok.later while tech was completing PM on site, Silvio asked tech to look at these two units again apparently, they are not cooling as efficiently as before, tech l;ater found R22 refrigerant levels low, BRAF 2 submitted to cover this.PLEASE NOTE THESE UNITS ARE 26YEARS OLD AND SHOULD BE REPLACED I HAVE FLAGGED THIS TO SILVIO SITE MANAGER AND ERIC PFMrepairs completed on AC unit as per BRAF but new coil required for AC3 this unit is beyond economical repair, we recommend a replacement unit.BRAF 3 Ordered new Condenser motor and blade eta 4 weeks Picked up parts travelled to site set up to get roof access,removed old burnt out condenser fan motor and replace with new one ,wired all u
MSA-DTWD | WA5290023 | 1 | Precise Air Group | A009 / chiller compound - chiller not working | Air Conditioning | Room Air Conditioners | 329.67 | Pass | Fail | 0 | 29 | 4805.1333 | 2022-03-24 15:28 | 2022-03-25 17:00 | 2022-03-25 07:00 | 2022-03-25 17:00 | 2022-10-11 12:08 |  |  | Checked the operation of the system and found the chiller operating to specs. monitored operation
MSA-DTWD | WA5481629 | 3 | Protek 24/7 Building & Maintenance | Old Hopper door - Door needs repair/replacing | Building | Doors | 3690.95 | Pass | Fail | -1 | 27 | 4703 | 2022-05-30 15:10 | 2022-06-07 17:00 | 2022-06-01 14:00 | 2022-06-07 17:00 | 2022-12-14 13:00 |  | WACCES | Perform make safe, make good or repair as instructed to prevent further damage or harm to persons and property? Remove and dispose of 2x Doors + Door Frame? Prepare site for install of new Door frame (cleanup of wall where frame to be installed)? Supply and install new Wooden Door Frame? Apply undercoat and paint (2 coats) both new doors to suit colour selection (Colourbond Terrain)? Supply and install 2x Rebated solid core doors to suit new door frame (2040mm x 720mm)? Supply and install new Door Hardware including: Lockwood Dead-latch, Chains, Barrel Bolts 600mm High kick plates
MSA-DTWD | WA4993428 | 1 | Precise Air Group | room B29 - leak in the room from ceiling | Air Conditioning | Room Air Conditioners | 749.9 | Pass | Fail | 0 | 27 | 4674.05 | 2022-01-07 13:48 | 2022-01-10 17:00 | 2022-01-07 13:48 | 2022-01-10 17:00 | 2022-07-21 07:51 |  |  | Picked up new filters, pull old filters out & replaced with new ones. Complete.
MSA-DTWD | WA5570735 | 2 | Precise Air Group | 3 door under bench fridge not working | Refrigeration | Refrigerators | 2444.42 | Pass | Fail | 0 | 28 | 4632 | 2022-06-28 14:05 | 2022-07-01 17:00 | 2022-07-01 08:00 | 2022-07-01 17:00 | 2023-01-10 08:00 |  |  | Found unit has already been looked at and parts been ordered. Will follow up with office
MSA-DCA | WA5312175 | 2 | Precise Air Group | Administration Office 2 - Control panel for AC in Admin 2 is flashing error message | Air Conditioning | Room Air Conditioners | 1246.75 | Pass | Fail | 0 | 27 | 4534.4833 | 2022-04-11 11:45 | 2022-04-14 17:00 | 2022-04-13 10:00 | 2022-04-14 17:00 | 2022-10-19 08:29 |  |  | Attended site, signed in and completed all pre start requirements. Gained access to unit on the roof and carried out functional checks on all refrig and mechanical components. No negative results found. Suspect as unit will only fault on low speed fan possible dirty indoor coil. Unit does appear close to end of life and showing signs of deterioration dur to age and weather conditions
MSA-DTWD | WA5609143 | 1 | Protek 24/7 Building & Maintenance | Ceiling next to stove and deep fryer dropped and distorted | Building | Ceiling | 3171.81 | Pass | Fail | 0 | 27 | 4472.75 | 2022-07-13 14:20 | 2022-07-14 17:00 | 2022-07-14 07:00 | 2022-07-14 17:00 | 2023-01-16 15:45 |  |  | Repairs to ceiling as per approved BRAF
MSA-DTWD | WA5001487 | 3 | Precise Air Group | A308 - commercial fridge stopped working A40299247Q | Refrigeration | Refrigerators | 1301.345 | Pass | Fail | -1 | 25 | 4397.05 | 2022-01-11 12:45 | 2022-01-18 17:00 | 2022-01-12 11:00 | 2022-01-18 17:00 | 2022-07-14 16:03 |  | WACCES | Required additional information for controllers as supplier was unable to match
MSA-DTWD | WA5290357 | 2 | Precise Air Group | E-Block - Restaurant - the ice machine not making ice | Refrigeration | Ice machine | 5005.505 | Pass | Fail | -1 | 25 | 4397 | 2022-03-25 08:18 | 2022-03-30 17:00 | 2022-03-25 10:00 | 2022-03-30 17:00 | 2022-09-24 15:00 |  | WACCES | Ice machine parts coming from South America, completed 24/10/22Returned back to site checked pressure test all good, charged up unit with 500 grams of R404A ,FOUND waterinlet wires were burnt out had to rewire all control circuits and then tested operation unit was then running well and producing ice put all covers back on and checked operation again all running well cleaned up site and completed job.
MSA-DCA | WA5838207 | 2 | Precise Air Group | Chugging noise from Air con - when on low or high setting - see notes below | Air Conditioning | Room Air Conditioners | 1931.58 | Pass | Fail | 0 | 26 | 4376.5167 | 2022-09-08 11:26 | 2022-09-13 17:00 | 2022-09-12 10:00 | 2022-09-13 17:00 | 2023-03-13 18:31 |  | WACCES | 18/10/22Returned to site, isolated FCU and removed from ceiling space. Took motor for repairs.2/2/23motor and shaft no longer made , have taken to specialist to source and machine parts waiting on price.27/2/23Attended site and signed in. Accessed roof space and proceeded to install new fan motor and align blowers to suit new shaft size. Unable to wired new fan motor as the wiring information is not available, will need to source info and return to site.2/3/23Returned to site with wiring information. Connected fan motor and energised. Tested and found fan operating correctly.
MSA-DFES | WA5478205 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Whole Site - Various Lights out - see notes below | Electrical | Lighting, Internal | 3077.965 | Pass | Fail | 0 | 26 | 4371.5 | 2022-05-26 10:08 | 2022-06-02 17:00 | 2022-06-02 10:30 | 2022-06-02 17:00 | 2022-12-01 14:00 |  | WACCES | Sebastian Pino (02/06/2022) - Work NoteArrived on site at 1030 located 10 x fluros requiring replacement across tdsc office, fac store, flag pole lts and toilet block in front of reception. Replaced all faulty fluros located and continued on site at 1330 to attend next job. While on site 1 x light was identified in bat building with damaged tombstones and faulty ballast. Will need to return to site with parts to replace lt fitting and 2 x fluros for flag pole lights.Jacob Prendergast (09/06/2022) - Work NoteContinued on site at 15:45 to replace blown tube in open office area, replaced 2 x 36w tubes and starters. Tested all okay. Left site at 16:15Sebastian Pino (21/06/2022) - Work NoteArrived on site at 0700 and awaited to be granted access into areas of site required for works. Began dismantling flag pole light fittings to replace globes. Globes acquired for replacement were faulty and could not replace existing globes. Will need to return to site to replace components f
MSA-DTWD | WA5780601 | 3 | Precise Air Group | Remote not working on Aircon | Air Conditioning | Room Air Conditioners | 6351.1 | Pass | Fail | 0 | 24 | 4181.9 | 2022-08-19 11:58 | 2022-08-26 17:00 | 2022-08-23 10:00 | 2022-08-26 17:00 | 2023-02-13 15:54 |  |  | Attended site signed in and located room s113. Found power circuit breaker for unit had tripped. Restored power and carried out functional checks of the unit. Unit went out on a fault. Led light indicate potential issues with compressor, main pcb and a secondary pcb or all the above. Carried out insulation test on compressor although passed was not perfect and could not get to run and my have potential mechanical issues. PCB housing showed signs of infestation including lizards and mice with some burn marks. Replaced covers and cage and tagged out at isolator. Reccomend replacing unit due to age and physical conditionunit has been removed and replaced
MSA-DFES | WA5522084 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Training Tower - flood light is fault and needs to be re-attached to wall | Electrical | Lighting, External | 547.645 | Pass | Fail | 0 | 25 | 4129.25 | 2022-06-15 12:30 | 2022-06-20 17:00 | 2022-06-20 07:15 | 2022-06-20 17:00 | 2022-12-09 08:30 |  | WACCES | Arrived on site at 0715 to investigate Training Tower - fallen flood light. Discovered 1 x water damaged floodlight. Will need to return to site to replaced damaged flood light. Reinstated fitting and informed staff. Left site at 0815.Sebastian Pino (20/06/2022) - Work NoteArrived on site at 0715 to investigate Training Tower - fallen flood light. Discovered 1 x water damaged floodlight. Will need to return to site to replaced damaged flood light. Reinstated fitting and informed staff. Left site at 0815.Adam Back (12/07/2022) - Work NoteArrived onsite at 14:15 to install LED floodlight to training tower. Found light is supplied by low voltage control panel located in equipment room. Light is not a standard fitting and is powered by low voltage control rather than standard 240v. Will need to return to site with qualified personnel to investigate intelligent lighting system to determine if light fitting is broken. Upon investigate it will be determined if light can be moved upon
MSA-DCA | WA5190070 | 3 | Assa Abloy Entrance Systems Aust P/L-WA | External Grounds - Cable gate chain has snapped | Building | Steel Fencing & Gates | 1371 | Pass | Fail | 0 | 24 | 4100.6833 | 2022-02-24 10:35 | 2022-03-03 17:00 | 2022-02-28 15:19 | 2022-03-03 17:00 | 2022-08-18 12:00 |  |  | 24/02/2022 -Noted cable gate had severed cable, batteries flat and out of date, and no power to unit. Quote to follow.18/8/2022: Attended site and inspected rope gate. Noted gate operational on arrival. Noted from staff on site, gate not raising intermittently. Inspected and suspectsafety beam may be cause during the poor wet storms over the past few days. Required to adjust beam, cleaned reflectors and glass, and testedoperations all OK. Staff will monitor operations. This callout is not warranty.
MSA-DTWD | WA5572197 | 3 | Precise Air Group | Chilled Water Actuator for AHU3 not working | Refrigeration | Chiller | 152.03 | Pass | Fail | 0 | 24 | 4051.3167 | 2022-06-29 14:31 | 2022-07-06 17:00 | 2022-07-05 13:47 | 2022-07-06 17:00 | 2022-12-21 09:06 |  |  | Spoke to Micheal otter who does chiller maintenance he is organising quote to rectify faulty valve and actuator and spoke to Tao to inform him the facility manager .Was advised by office job has been completed by contractor
MSA-DTWD | WA5068751 | 1 | Equans Mechanical Services Australia | C Block - Ground - AHUC1 – All of C that AHUC1 covers - AHUC1 is not cooling | Air Conditioning | Room Air Conditioners | 1934.28 | Pass | Fail | 0 | 24 | 4014.5 | 2022-01-19 12:21 | 2022-01-20 17:00 | 2022-01-20 08:00 | 2022-01-20 17:00 | 2022-07-06 14:30 |  | WACCES | .
MSA-DTWD | WA5727828 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 4 - Staff Kitchen - Zip boiler to staff kitchen not working | Plumbing & Drainage | Water | 239.33 | Fail | Fail | 0 | 24 | 3983.3 | 2022-08-15 12:07 | 2022-08-18 17:00 | 2022-08-19 11:42 | 2022-08-18 17:00 | 2023-02-01 11:00 |  |  | nil
MSA-DTWD | WA5794259 | 3 | Equans Mechanical Services Australia | Air con isn’t working on heating cycle | Air Conditioning | Ducted Split System | 6667.635 | Pass | Fail | -1 | 22 | 3796.4167 | 2022-08-24 13:19 | 2022-08-31 17:00 | 2022-08-26 12:30 | 2022-08-31 17:00 | 2023-01-31 16:55 |  | WACCES | Decommissioned and Removed Existing SystemInstalled New High Wall Split AC Indoor Unit
MSA-DCA | WA5271645 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Boiler room - high pressure outlet fault - please investigate | Mechanical Services | Boilers | 371.62 | Pass | Fail | 0 | 22 | 3774.2 | 2022-03-18 09:41 | 2022-03-21 17:00 | 2022-03-18 10:29 | 2022-03-21 17:00 | 2022-08-22 16:41 |  | WACCES | Repairs to equipment have been completed under WA5693681
MSA-DTWD | WA5106712 | 1 | Equans Mechanical Services Australia | Ground - D31 - Aircon turns on then goes off after a few minutes | Air Conditioning | Room Air Conditioners | 2000.59 | Pass | Fail | 0 | 22 | 3765 | 2022-02-07 10:44 | 2022-02-08 17:00 | 2022-02-08 13:00 | 2022-02-08 17:00 | 2022-07-15 10:00 |  | WACCES | Checked the high wall split not cooling , evap fan runs and the compressor doesn't start. Had to find remote control, used remote to try and get fault code , found problem with indoor unit , need to call technical support but they have close for the day will ring tomorrow. BRAF submitted, awaiting approval. (9/2/22)
MSA-DFES | WA5697612 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Volunteers side - water leak in training room - coming in threw light fitting | Electrical | Lighting, Internal | 399.7425 | Pass | Fail | 0 | 22 | 3745.25 | 2022-08-09 10:43 | 2022-08-10 17:00 | 2022-08-09 12:00 | 2022-08-10 17:00 | 2023-01-12 13:15 |  | WCAPPR | Sebastian Pino (09/08/2022) - Work NoteArrived on site at 1200 to investigate Volunteers side - water leak in training room - coming in through light fitting. Identified light. Isolated, disconnected, made safe, tagged out and sealed. Informed staff of works and left site at 1315.Matthew Kenney (12/01/2023) - Work NoteArrived onsite at 12:30 to reconnect light affected by water in volunteer training room, reconnected light and tested, light is now working in training room. Advised staff of works and left site at 13:15.
MSA-DTWD | WA5188556 | 1 | Precise Air Group | Air Con not cooling | Air Conditioning | Room Air Conditioners | 2415.35 | Pass | Fail | 0 | 22 | 3724.5 | 2022-02-23 09:47 | 2022-02-24 17:00 | 2022-02-23 11:30 | 2022-02-24 17:00 | 2022-07-28 16:00 |  |  | Fixed leaking flare nut on Indoor fan coil pressure tested ,vaced out charged unit checked full operating all running efficiently on heating and cooling cycles
MSA-DFES | WA5564173 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | APPLIANCE ROOM - 24V CHARGING CABLE BAY 5 NEEDS REPAIR | Electrical | General Electrical | 1700 | Pass | Fail | 0 | 21 | 3602.5 | 2022-06-21 08:44 | 2022-06-24 17:00 | 2022-06-24 12:00 | 2022-06-24 17:00 | 2022-11-21 14:30 |  | WCAPPR | Arrived onsite at 12:00 to investigate 24v vehicle trickle charger damaged. Found 1 x trickle charger had been snapped off its supply from a sliding breakaway curtain cable system. Further investigation is required with height acess to investigate how to repair cable damage. Most likely will need to return with large EWP and roof access gear to get under ceiling and onto roof to carry out repair. Will return to site to investigate further. Left site at 13:15 Matthew Kenney (21/11/2022) - Work NoteArrived on site at 7:45 to investigate issue with cable break away system in engine bay. Used scissor to replace existing charging leads and installed pendant GPOs at bays 2 & 5. Left site at 14:30.
MSA-DTWD | WA5438482 | 2 | Precise Air Group | Level one - Room A 145 - Extraction system not working | Air Conditioning | Evaporative Coolers | 1826.18 | Pass | Fail | 0 | 21 | 3579 | 2022-05-16 14:36 | 2022-05-19 17:00 | 2022-05-17 13:00 | 2022-05-19 17:00 | 2022-10-13 16:00 |  |  | Attended site and replaced fan. Unable to find power to isolator. Electrical contractor will need to be engaged as is falls out of our scope
MSA-DTWD | WA5612012 | 3 | AWB Co. | Francis street entry round LED light out | Electrical | Lighting, Internal | 829.08 | Pass | Fail | 0 | 21 | 3549.9 | 2022-07-14 11:17 | 2022-07-21 17:00 | 2022-07-20 11:06 | 2022-07-21 17:00 | 2022-12-15 09:00 |  | WACCES | Located faulty light fitting. Isolated circuit. Supplied and replaced with new LED fitting. Energised and tested.packed up site. **job complete**
MSA-DTWD | WA5100292 | 2 | Precise Air Group | P block. Facilities office. BMS software on facilities PC not functioning correctly | Air Conditioning | Building HVAC Maintenance (Major Plant) | 5252.1 | Pass | Fail | 0 | 20 | 3504.0667 | 2022-02-02 12:15 | 2022-02-07 17:00 | 2022-02-04 10:42 | 2022-02-07 17:00 | 2022-06-30 10:46 |  |  | 4/1 NRP atteneded - attended site and was advised that the staff want to access the BMCS PC in the attic from the Office at McLarty and and also the from the office at Kendrew campus. To do this we have several option but the 2 most cost affective are:Option 1To carry out the requested works this will require the TAFE IT to create a VPN account and set it up on the TAFE networkso the PC can be viewed from anywhere on the campus network, provided the IT structure is capable.This only allow one user at a time and the if technicians attend wanting to use the BMCS they will need to make surethe no else one is logged inOption 2Another option is to upgrade the BMCS graphics to the latest platform Magellan Server and Innotech Magellan app. This will allow multiple users to access the BMCS from any where on the network. Again TAFE IT will need to be consultedto ensure this can be implemented.
MSA-DFES | WA5128285 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - SOC - Repair to 10 Lights not working in the SOC and nearby office- SEE DETAILS | Electrical | Lighting, Internal | 997.735 | Pass | Fail | 0 | 21 | 3463 | 2022-02-14 16:53 | 2022-02-17 17:00 | 2022-02-17 08:15 | 2022-02-17 17:00 | 2022-07-11 15:15 |  | WACCES & WCAPPR | Continued onsite at 13:15 to investigate last remaining light not working. Found 1 x faulty electronic ballast. Collected parts from nearest wholesaler and returned to site. Installed and tested new ballast and notified staff of works completed. Left site at 15:15
MSA-DTWD | WA5175115 | 1 | Equans Mechanical Services Australia | C101 - Aircon temperature sensor in C101 faulty | Air Conditioning | Room Air Conditioners | 8600 | Fail | Fail | 1 | 21 | 3451.95 | 2022-02-21 10:28 | 2022-02-22 17:00 | 2022-02-28 12:30 | 2022-02-22 17:00 | 2022-07-22 08:27 |  |  | REQUIRES INVERTER PCB.REQUIRES FURTHER INVESTIGATION.REQUIRES REPLACEMENT INVERTER BOARD.
MSA-DTWD | WA5067095 | 3 | Precise Air Group | N Block - Level 1 - N117 - Replace broken Remotes to N117 Daikin Units | Air Conditioning | Room Air Conditioners | 1082.58 | Pass | Fail | -1 | 20 | 3449.5 | 2022-01-19 10:10 | 2022-01-27 17:00 | 2022-01-20 13:30 | 2022-01-27 17:00 | 2022-06-13 07:00 |  | WACCES | Quote to replace sent
MSA-DTWD | WA5472936 | 3 | AWB Co. | Level 3 - Corridor outside room 3-15 - Water leak from roof | Roofing | Metal Roofing | 1808.74 | Pass | Fail | 0 | 20 | 3406.9667 | 2022-05-24 11:46 | 2022-05-31 17:00 | 2022-05-30 14:47 | 2022-05-31 17:00 | 2022-10-19 13:45 |  |  | Works completed as per braf
MSA-DFES | WA5295278 | 3 | AWB Co. | Roof - Plant Room - Please see details below: | Building | General Building | 6573.5 | Pass | Fail | -1 | 19 | 3389 | 2022-03-29 12:09 | 2022-04-05 17:00 | 2022-03-31 07:00 | 2022-04-05 17:00 | 2022-08-19 12:00 |  |  | See drawings in attachments for current measurements of barge and door flashing.Inspected leak above door in plant room. Took appropriate pictures and measurements to increase barge flashing. And to increase width of door flashing. Will return to install and make watertight.Completed installing new apron flashing and waterproofing wall.works completedBRAF attached
MSA-DTWD | WA5982678 | 2 | Australian Airconditioning Services Pty Ltd | Block A - Cafeteria - AG10B -The display fridge is only cooling on the bottom half. | Refrigeration | Refrigerators | 688.26 | Pass | Fail | 0 | 19 | 3268.5 | 2022-09-30 13:26 | 2022-10-05 17:00 | 2022-10-04 08:00 | 2022-10-05 17:00 | 2023-02-17 12:30 |  |  | Checked works carried out by sub contractor. All ok.
MSA-DTWD | WA5308759 | 3 | Protek 24/7 Building & Maintenance | D Block (South side of North section of D block) - Gutters rusted through | Roofing | Metal Roofing | 3385.01 | Pass | Fail | -1 | 18 | 3242 | 2022-04-08 15:48 | 2022-04-19 17:00 | 2022-04-12 13:00 | 2022-04-19 17:00 | 2022-08-25 15:00 |  | WACCES | Remove dispose of and replace Gutter
MSA-DTWD | WA5325940 | 2 | Precise Air Group | Room C44 - Chiller in fault and not running - Main plant | Air Conditioning | Building HVAC Maintenance (Major Plant) | 13245.73 | Pass | Fail | 0 | 19 | 3200.2167 | 2022-04-14 14:12 | 2022-04-21 17:00 | 2022-04-20 07:30 | 2022-04-21 17:00 | 2022-08-31 15:43 |  |  | Subcontractor Completed.
MSA-DFES | WA5567519 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Ground - Engine Room Exhaust Fan tripping RCD | Electrical | General Electrical | 923.995 | Pass | Fail | 0 | 19 | 3193.1667 | 2022-06-24 10:08 | 2022-06-29 17:00 | 2022-06-29 12:15 | 2022-06-29 17:00 | 2022-11-09 13:25 |  | WCAPPR | Mechanical door company needs to be contacted, issue is with the door not electrical
MSA-DTAG | WA5081076 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Court 9 - Air-conditioning not working, light is on but no cold air coming out | Air Conditioning | Room Air Conditioners | 17953.325 | Pass | Fail | 0 | 19 | 3189.5833 | 2022-01-20 10:48 | 2022-01-21 17:00 | 2022-01-20 11:00 | 2022-01-21 17:00 | 2022-06-02 08:35 |  | WCAPPR | #40405
MSA-DTAG | WA5312138 | 0 | Midolo Building Services | Near door 6 (emergency exit door) - Significant flooding from roof/wall | Building | General Building | 4021.31 | Pass | Fail | 0 | 19 | 3188.25 | 2022-04-11 11:25 | 2022-04-11 13:25 | 2022-04-11 12:15 | 2022-04-11 15:25 | 2022-08-22 08:30 |  | WACCES | repaired ceiling, cleaned gutters, painted.
MSA-DCA | WA5100460 | 3 | Precise Air Group | roof - Western Plant Room - Toilet Vent Fan has burnt out winding | Electrical | General Electrical | 3973.285 | Pass | Fail | -1 | 18 | 3172.5833 | 2022-02-02 13:13 | 2022-02-09 17:00 | 2022-02-03 10:00 | 2022-02-09 17:00 | 2022-06-15 14:35 |  | WACCES | Travelled to supplier, picked up required parts,travelled to sote, gained access, installed new flexible connected between duct work sealed all connections, test operated fan motor alll running to specs cleared debrisfrom site.
MSA-DTWD | WA5832041 | 2 | AWB Co. | roof leak from aircon penetration | Roofing | Tiled Roofing | 3475.0625 | Pass | Fail | 0 | 19 | 3168 | 2022-09-05 10:34 | 2022-09-08 17:00 | 2022-09-07 08:45 | 2022-09-08 17:00 | 2023-01-17 08:45 |  | WACCES | Attended site and signed in. Completed JSA. Gained access to room. Isolated circuit. Reinstalled light which was isolated on the 10/01. Energised and tested. Light working correctly. **job complete**
MSA-DTWD | WA5017313 | 2 | Equans Mechanical Services Australia | Ground - F16 - Air con not working | Air Conditioning | Room Air Conditioners | 1285.73 | Fail | Fail | 0 | 19 | 3139.5 | 2022-01-13 12:47 | 2022-01-18 17:00 | 2022-01-21 14:30 | 2022-01-18 17:00 | 2022-06-01 10:00 |  | WACCES | Arrived on site signed in. Gathered tools and equipment assisted by Dave with working at heights installed new parts tested all ok. Cleaner up and completed paperwork.
MSA-DCA | WA5853631 | 0 | Protek 24/7 Building & Maintenance | outside Hackett hall ground - broken steps need to be cleaned up-safety issue | Paving & Roadworks | Paving | 906.92 | Pass | Fail | 0 | 19 | 3117 | 2022-09-12 09:56 | 2022-09-12 11:56 | 2022-09-12 11:00 | 2022-09-12 13:56 | 2023-01-20 08:00 |  | WACCES | ? Setup temporary fencing onsite to prevent access to staircase? Carried out site measure to confirm materials required? Leave temporary fencing for staircase onsite until early January 2023? Confirm pickup date with site contact before booking pickup time? Attend site and remove temporary fencing once confirmation has been received? Clean site & DemobiliseRepairs to staircase to be carried out by others
MSA-DTWD | WA5312196 | 1 | Protek 24/7 Building & Maintenance | A Block - Near room A4 - roof leaking | Building | General Building | 7822.56 | Pass | Fail | 0 | 18 | 3081.25 | 2022-04-11 11:54 | 2022-04-12 17:00 | 2022-04-12 07:00 | 2022-04-12 17:00 | 2022-08-18 16:15 |  | WACCES | Install flashings, new sheets, drypans and ridge capping
MSA-DFES | WA4992528 | 1 | Australian HVAC Services Pty. Ltd. | Double Dorm - Original part of building - A/C is dripping water | Air Conditioning | Room Air Conditioners | 585.29 | Pass | Fail | 0 | 18 | 3027 | 2022-01-06 13:00 | 2022-01-07 17:00 | 2022-01-07 06:00 | 2022-01-07 17:00 | 2022-05-13 09:00 |  |  | Traveled to site, located ac that was leaking water. Removed covers and tested drain found drain blocked and two other split systems feed into same drain Cleared out drains and tested. Found that the backing plate wall anchors are pulling out and unit is starting to fall off the wall.Returned 07/02 - Reattached unit to wall securely.Reattended 13/05/2022 to get details to quote on new unit
MSA-DCA | WA5175180 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - chiller 1 in fault | Air Conditioning | Room Air Conditioners | 659.3 | Fail | Fail | 0 | 18 | 3024.3667 | 2022-02-21 10:53 | 2022-02-21 12:53 | 2022-02-21 16:13 | 2022-02-21 14:53 | 2022-06-27 16:35 |  |  | Attended site gained access and carried out investigations into fault. Stage A starter guard fault found active. Water flow interlock fault found active. Flushed water flow DP switchsnd lines. Carried out hard reset of chiller and restored power. Confirmed equipment alarms reset. Accessed BMS and placed chiller 1 into lead unit. On change over it was noted chiller 2 went into alarm. On inspection of alarm water flow interlock fault found to have activated. Water pump stage down timer was check and found to be set for 10min. Plant changed within about 2min. CH 2 fault reset. Schneider BMS tech contacted and asked to check and confirm stage down timer operation. Work area left tidy. Chiller 1 currently operating and maintaining the building load. Work area left tidy.
MSA-DTWD | WA5674892 | 3 | Australian Airconditioning Services Pty Ltd | Staff room 2G1/2 - A/C Not working | Air Conditioning | Room Air Conditioners | 6513.5 | Pass | Fail | -1 | 17 | 3024.1667 | 2022-07-21 15:06 | 2022-07-28 17:00 | 2022-07-22 08:00 | 2022-07-28 17:00 | 2022-11-25 08:10 |  | WACCES | Replaced parts but further works required. BRAF declined.
MSA-DCA | WA5285975 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room Back Car Park - Ground floor - Plant room - Chiller 1 in fault | Air Conditioning | Room Air Conditioners | 450 | Pass | Fail | 0 | 18 | 2978.3833 | 2022-03-21 11:34 | 2022-03-24 17:00 | 2022-03-23 13:43 | 2022-03-24 17:00 | 2022-07-25 16:06 |  |  | Returned to sote and rechecked equipment operation. No further fault has occured on equipment. Confirmed chiller change over and no fault occured. Chiller running normally in auto mode. Work area left tidy.
MSA-DTWD | WA5141408 | 1 | Falcetta Plumbing and Gas | external d blocks - mains water leak under the bitumen | Plumbing & Drainage | Water | 23964.5175 | Pass | Fail | 0 | 17 | 2956 | 2022-02-16 09:54 | 2022-02-17 17:00 | 2022-02-16 12:00 | 2022-02-17 17:00 | 2022-06-19 16:00 |  |  | repaired 2x leaks inc access pits etc
MSA-DTWD | WA5692121 | 2 | Protek 24/7 Building & Maintenance | Water leak above Spray Booth door | Roofing | Metal Roofing | 1934.43 | Pass | Fail | -1 | 17 | 2952.75 | 2022-08-03 10:42 | 2022-08-08 17:00 | 2022-08-04 12:30 | 2022-08-08 17:00 | 2022-12-05 13:15 |  | WACCES & WCAPPR | •Remove and dispose of rusted box gutter•Supply and install custom box gutter & connect to rainhead•Reinstate the following once works complete•Roof sheets using new screws to to make good•Ladder access and anchor point•Parapet Capping•Water-test roof to confirm watertight once works complete and all materials reinstatedClean site & Demobilise
MSA-DTWD | WA5596618 | 3 | AWB Co. | Level 5 East disabled toilets with water damage needs repair and paint | Building | Internal Walls | 5663.92 | Pass | Fail | -1 | 16 | 2907.7 | 2022-07-11 09:27 | 2022-07-18 17:00 | 2022-07-11 12:18 | 2022-07-18 17:00 | 2022-11-09 16:00 |  |  | Works completed
MSA-DTWD | WA5094607 | 1 | Equans Mechanical Services Australia | A Block - Ground Floor - AG10B Café Kitchen - Freezer Room not working. Temp at approx. 0* | Refrigeration | Freezers | 1470.14 | Pass | Fail | 0 | 17 | 2886 | 2022-01-31 12:25 | 2022-02-01 17:00 | 2022-02-01 10:30 | 2022-02-01 17:00 | 2022-06-01 16:30 |  |  | Travelled to site and signed in. Located freezer room andnfound evaporator fan not running and door switch arm had come loose. Fixed door switch and tested switch works bit fan is faulty. Travelled off site to supplier to pick up parts. Removed fan and replaced and tested. Temps began to decrease.checked gas pressures all ok.
MSA-DTWD | WA5133870 | 2 | Equans Mechanical Services Australia | G Block - Ground - Rooms on western side of block not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1156.79 | Pass | Fail | 0 | 17 | 2858.75 | 2022-02-15 16:05 | 2022-02-18 17:00 | 2022-02-16 13:00 | 2022-02-18 17:00 | 2022-06-15 15:45 |  | WCAPPR | SEE REPORT
MSA-DCA | WA5112206 | 0 | Dormakaba Australia Pty Ltd | Main Building -GND -Loading Dock -Roller door Stuck in close position | Building | Doors | 810 | Fail | Fail | 0 | 17 | 2852.2 | 2022-02-10 09:09 | 2022-02-10 11:09 | 2022-02-10 16:36 | 2022-02-10 13:09 | 2022-06-09 12:48 |  |  | 10/2/22 - Assessed door and found multiple broken slat clips which have caused the slats shift and get caught on top of the guides. Door is back to normal operation but will require new slat clips to prevent further issues.Please return to replace 20 x 3 pin slat clips for 100mm slats9/6/22 - Completed works as per required. Tested all good
MSA-DTWD | WA5481498 | 3 | Equans Mechanical Services Australia | External G Block North -GG 13 exterior - Dust extractor not working. | Air Conditioning | Materials | 3100.72 | Pass | Fail | -1 | 16 | 2836.25 | 2022-05-30 13:46 | 2022-06-07 17:00 | 2022-06-03 08:00 | 2022-06-07 17:00 | 2022-09-29 12:15 |  |  | Arrived on site signed in checked in with Sharyn. Assisted by Dave. Reinstalled motor and accessories. Tested operation, cleaned up and completed paperwork and signed out.
MSA-DFES | WA5677045 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Station Yard - The storm water drains in the top part of the yard are close to full poorly draining | Plumbing & Drainage | Drainage | 2764.4 | Pass | Fail | -1 | 16 | 2835 | 2022-07-25 12:13 | 2022-08-01 17:00 | 2022-07-28 08:30 | 2022-08-01 17:00 | 2022-11-23 11:30 |  | WACCES | Where the trucks are parked there are 5 soakwall the 2 soakwall closest to the trucks are empty and the other three are full of water need to get job raised so we can suck them out to get them working again. Arrived on site with Terra vac and cleaned out 5 soakwall on top part of yard
MSA-DTWD | WA5296423 | 1 | AHS Services WA Pty Ltd (Anchor) | A-Block - External east end of building - A-Block East end external blocked sewer drain | Plumbing & Drainage | Drainage | 8260.5025 | Pass | Fail | 0 | 17 | 2808.75 | 2022-03-30 12:19 | 2022-03-31 17:00 | 2022-03-30 13:15 | 2022-03-31 17:00 | 2022-07-25 14:00 |  |  | Replace 6m of 100mm sewer infested with roots as per qoute
MSA-DCA | WA5413073 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | leading to maritime history area - Manual Chain roller door not coming down even to the ground | Building | Doors | 6683.7 | Pass | Fail | 0 | 16 | 2789.5 | 2022-05-12 08:43 | 2022-05-13 17:00 | 2022-05-12 11:30 | 2022-05-13 17:00 | 2022-09-05 17:00 |  |  | Found door sticking in guides. Inspection shows left hand track bent. Lubricated guides,realigned curtain.Carried out full test of operation ok.Door working ok but recommend rewelding left hand side guide and motorising the door as it is hard to operate and could be a safety issue.Quote to follow.Picked up parts and scissorlift from Belmont.Removed existing manual chain hoist. S&I new Grifco meastro operator with fitting plate kit. Straightened guide, set limits, carried out full test ofoperation ok.Returned scissorlift to Belmont.
MSA-DFES | WA5163294 | 1 | Australian HVAC Services Pty. Ltd. | Plant room - aircons not working | Air Conditioning | Room Air Conditioners | 3159.08 | Pass | Fail | 0 | 16 | 2788 | 2022-02-18 08:39 | 2022-02-21 17:00 | 2022-02-18 09:00 | 2022-02-21 17:00 | 2022-06-14 13:00 |  |  | 40706Attend site and go through BMS operation and confirm all issues have now been sorted out as requested. Liaise with mizco and go over reports.
MSA-DTWD | WA5706119 | 2 | AWB Co. | S Block - Roof - S100 Passage - Downpipe leak into S100 passage from South Block- See notes below | Roofing | Guttering | 2854.93 | Pass | Fail | 0 | 16 | 2787.0833 | 2022-08-11 08:49 | 2022-08-16 17:00 | 2022-08-13 10:55 | 2022-08-16 17:00 | 2022-12-07 14:00 |  |  | Works completed
MSA-DFES | WA5477656 | 2 | Protek 24/7 Building & Maintenance | Corridor/Lunchroom - please see details below | Building | General Building | 803.585 | Pass | Fail | 0 | 16 | 2783.5 | 2022-05-25 16:38 | 2022-05-30 17:00 | 2022-05-27 11:30 | 2022-05-30 17:00 | 2022-09-20 11:00 |  | WACCES | Upgrade 1x downpipe to 100mm PVC & add junction? Remove and dispose of inadequate downpipe and fixings? Supply and install new 100mm PVC downpipe? Connect new PVC downpipe to gutter using Y Junction to allow better drainage? Replace connection to downpipe at other end of gutter to ensure adequate drainage
MSA-DTAG | WA5390351 | 1 | Midolo Building Services | Level 4 - Cubicle door hinge in male public toilet has detached from the partition | Building | Doors | 1108.04 | Pass | Fail | 0 | 16 | 2761.25 | 2022-05-02 12:08 | 2022-05-03 17:00 | 2022-05-02 14:15 | 2022-05-03 17:00 | 2022-08-25 15:30 |  | WACCES | hang door, modified door stop
MSA-DFES | WA5734987 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Stormwater drains in training yard appear to be blocked and are not draining excess water. | Plumbing & Drainage | Drainage | 8688.665 | Pass | Fail | 0 | 16 | 2735.5 | 2022-08-16 10:47 | 2022-08-23 17:00 | 2022-08-22 12:00 | 2022-08-23 17:00 | 2022-12-14 11:30 |  | WCAPPR | logged into wrong job 12.00 22/8/22 22/8/22 1:15 attend site to check out car park drain in training area
MSA-DTWD | WA5627980 | 3 | AWB Co. | Carpark light #1 at entrance to Carpark 2 is badly rusted and may fall - see notes below | Electrical | Lighting, External | 5960.035 | Pass | Fail | -1 | 16 | 2717.5 | 2022-07-15 09:45 | 2022-07-22 17:00 | 2022-07-18 09:30 | 2022-07-22 17:00 | 2022-11-08 15:00 |  | WACCES | Attended site signed in jsa completed. Disconnected pole cabling and removed pole. Excavator removed footing and dug new pole depth, installed pit as cables too short and junctioned in pit. Installed pole with led head. Tested snd confirmed operational.Job completed
MSA-DTAG | WA5018517 | 2 | Australian HVAC Services Pty. Ltd. | Level 2 - Office - Air conditioning temperature is very cold. | Air Conditioning | Room Air Conditioners | 672.44 | Pass | Fail | 0 | 16 | 2713 | 2022-01-14 12:25 | 2022-01-19 17:00 | 2022-01-17 08:00 | 2022-01-19 17:00 | 2022-05-10 09:00 |  | WACCES | Job number 40146
MSA-DCA | WA5383835 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Main building - External lights that illuminate balcony stairs not working | Electrical | General Electrical | 680.675 | Pass | Fail | 0 | 16 | 2706.75 | 2022-04-28 07:45 | 2022-05-02 17:00 | 2022-05-02 14:45 | 2022-05-02 17:00 | 2022-08-23 09:30 |  | WCAPPR | Arrived onsite at 14:45 to investigate lights not working located staircase up to balcony outside function room inside main building. Found lights worked with the override switch and that the PE cell is faulty controlling the circuit. Will need to return to site with parts to fix PE cell and access to reach it. Left site at 15:45Arrived on site at 0700 to attend faulty pe cell feeding ramp lights of Museum. Gained access to site scissor lift and located relevant sunset switch. Replaced pe cell and ensured operation. Continued on site at 0930
MSA-DTWD | WA5487399 | 2 | AWB Co. | 2 rows of lights tripping RCD | Electrical | Lighting, Internal | 3211.1425 | Pass | Fail | 0 | 16 | 2691.75 | 2022-06-01 14:50 | 2022-06-07 17:00 | 2022-06-07 08:30 | 2022-06-07 17:00 | 2022-09-27 12:15 |  | WACCES & WCAPPR | Attended site and signed in. Located faulty lights in classroom. Removed old suspended light fittings. Supply and install new panel lights and surface kits. Tested all okay. Signed out. Job complete
MSA-DTWD | WA6000910 | 3 | Critical Fire Protection & Training | Central Plant room - 25Ab Diesel Fire pump - Fuel leak | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 869 | Pass | Fail | -1 | 15 | 2686 | 2022-10-10 11:11 | 2022-10-17 17:00 | 2022-10-11 12:00 | 2022-10-17 17:00 | 2023-01-31 10:00 |  | WACCES | Identified that the leak is from the coolant pump for the motor. I also found that thecoolant cistern is not working correctly. The 20mm float valve in the tank is blocked andneeds replacement. The coolant pump packing gland has deteriorated and needs to berepaired. This motor is very old and repair may not be easy, recommend removing andsending to pump specialists or mechanic to repair.
MSA-DTWD | WA5567042 | 3 | AWB Co. | sth block creche - Dryer wont turn on | Equipment | Electrical Equipment | 962.77 | Pass | Fail | 0 | 16 | 2670.5833 | 2022-06-23 14:04 | 2022-06-30 17:00 | 2022-06-28 08:00 | 2022-06-30 17:00 | 2022-10-17 14:35 |  | WACCES | 1st Attendance (28/06/2022)Attended site and signed inspoke with fm about job,located dryer and spoke with manager of crèche, she has said dryer has been playing up for about a year.tested circuit and all goodpulled cover off and tested all connections were tighttested limit switch on door and it is operationalspun tumbler and is a bit tightcalled fm and discussed options going forwardfm wants us to engage contractor for servicing (sticker on machine) dependable laundry solutions.**follow up required**2nd Attendance (11/07/2022)Dryer specialist attended to investigate the issueIssue found and parts requiredBRAF submitted to ProgrammedBRAF approvedParts ordered3rd Attendance (13/09/2022)Attended siteReplaced idler AssyReplaced Belt, tumbler and driveReplaced Drum SealReplaced Lint FilterTested and passed.Clean AreaJob completed.
MSA-DTWD | WA6184675 | 2 | Equans Mechanical Services Australia | T-Block - Male/Female/and Disable toilets - level 1 - exhaust fans are not turning on | Air Conditioning | Building HVAC Maintenance (Major Plant) | 5057.94 | Pass | Fail | 0 | 16 | 2669.5 | 2022-11-15 14:24 | 2022-11-18 17:00 | 2022-11-17 08:00 | 2022-11-18 17:00 | 2023-03-08 13:30 |  |  | As per BRAF
MSA-DTWD | WA5204251 | 3 | AWB Co. | Level 6 - Plant Room - Boiler flue repair | Building | General Building | 2892.21 | Pass | Fail | 0 | 15 | 2666.2 | 2022-03-04 09:15 | 2022-03-14 17:00 | 2022-03-11 09:30 | 2022-03-14 17:00 | 2022-06-30 11:42 |  | WCAPPR | Works completed
MSA-DTWD | WA6255474 | 2 | Precise Air Group | Chiller showing Cooler flow switch fault. I have re set this several times | Air Conditioning | Room Air Conditioners | 1231.32 | Pass | Fail | -1 | 15 | 2662.65 | 2022-11-23 10:59 | 2022-11-28 17:00 | 2022-11-24 10:00 | 2022-11-28 17:00 | 2023-03-15 08:39 |  |  | Attended site with Justin to investigate why the chiller keeps shutting off with a flow fault. I have ran the chiller and tested the flow switch. Unit is operating correctly and the flow switch is complete fine. This would be more of a parameter issue with the BMS system that is causing this to fault. We will need to get NRP out to adjust the parameters on the BMS .Promap won’t work, won’t let me sync details to fill out for the job.Works completed by BMS tech at NRP on system to keep it running however chilled water bypass actuator has been ordered for system and this is due in ioion the 2nd May 23
MSA-DTWD | WA5417118 | 2 | Protek 24/7 Building & Maintenance | Verandah outside AT09 - Concrete is lifting and has become a trip hazard | Flooring | Concrete | 3026.47 | Pass | Fail | 0 | 16 | 2658.25 | 2022-05-13 10:25 | 2022-05-18 17:00 | 2022-05-18 15:00 | 2022-05-18 17:00 | 2022-09-06 09:15 |  | WACCES | • Clean exposed reinforcing bar of all surface corrosion with a stiff wire brush.• Treat exposed and cleaned bar with a suitable anti corrosion product.• Reinstate concrete which has been cut away.• Apply non slip textured paint to match existing (as close as possible)
MSA-DTWD | WA5105467 | 2 | Equans Mechanical Services Australia | Level 2 - 240 IT - Low air conditioning air flow | Air Conditioning | Room Air Conditioners | 1638.65 | Fail | Fail | 1 | 17 | 2657 | 2022-02-04 10:56 | 2022-02-09 17:00 | 2022-02-18 16:00 | 2022-02-09 17:00 | 2022-06-09 09:00 |  |  | FAULTS RELATE TO CHILLER
MSA-DTWD | WA5827472 | 1 | Protek 24/7 Building & Maintenance | Footpath outside TM159 - Concrete has lifted up - Tripping hazard | Flooring | Concrete | 1672.63 | Pass | Fail | 0 | 16 | 2639.25 | 2022-09-01 10:39 | 2022-09-02 17:00 | 2022-09-01 14:30 | 2022-09-02 17:00 | 2022-12-20 13:45 |  |  | Grind concrete back until level
MSA-DCA | WA6155925 | 3 | Protek 24/7 Building & Maintenance | Ground - Rear Exit Doors - Exit doors are letting in water when it rains- See notes | Building | Doors | 1471.26 | Pass | Fail | -1 | 15 | 2635.75 | 2022-11-08 15:04 | 2022-11-15 17:00 | 2022-11-09 13:30 | 2022-11-15 17:00 | 2023-02-27 09:15 |  | WACCES | ? Remove and dispose damaged door seals to exit doors? Supply and install new fire seal to vertical section of doors to suit existing? Supply and install new door seals to bottom of both doors to prevent water ingress
MSA-DTWD | WA5413378 | 2 | AWB Co. | Roof Water leak outside shed area brick laying section where extension has been added | Roofing | Metal Roofing | 3010.25 | Pass | Fail | -1 | 15 | 2616.75 | 2022-05-12 10:30 | 2022-05-17 17:00 | 2022-05-12 12:30 | 2022-05-17 17:00 | 2022-08-29 13:15 |  | WACCES & WCAPPR | Attended as per signature slip attached, BRAF required and has now been submitted.Removed flashing installed tape over join of twinwall and sealed, reinstalled flashing
MSA-DTWD | WA6129261 | 2 | Ronley Holdings Pty Ltd | light fab Plasma cutter Extraction unit faulty - see notes | Electrical | Lighting, Internal | 6800 | Fail | Fail | 1 | 17 | 2615 | 2022-10-27 12:59 | 2022-11-01 17:00 | 2022-11-11 08:00 | 2022-11-01 17:00 | 2023-02-28 07:00 |  | WACCES | The filter cartridges were beyond their service life and required replacing. There was also evidence of water ingress on the roof of the extractor.
MSA-DCA | WA5307162 | 0 | Precise Air Group | Level 4 - Plant Room - cooling tower fan motor 1 is squeeking | Air Conditioning | Room Air Conditioners | 2397.67 | Pass | Fail | 0 | 16 | 2612.75 | 2022-04-07 10:48 | 2022-04-07 11:18 | 2022-04-07 11:15 | 2022-04-07 12:48 | 2022-07-25 08:00 |  |  | Attended site and gained access to plantroom, found cooling tower 1 noisy. Lubricated pulley to stop the noise for the time being. FM met me on site and discussed a permanent solution. due to the adjustment bracket being seized and the noise coming from motor miss alignment we will need to get the motor bracket refurbished. Organised contractor to meet on site to provide a quote to refurbish bracket.
MSA-DTWD | WA5994283 | 3 | AWB Co. | The air shaft that feeds to AC ducts has a wooden lid that has peeled away - See notes below | Building | General Building | 2629.5425 | Pass | Fail | -1 | 15 | 2591.75 | 2022-10-05 14:34 | 2022-10-12 17:00 | 2022-10-07 11:45 | 2022-10-12 17:00 | 2023-01-23 11:30 |  |  | Works completed
MSA-DTWD | WA5674319 | 2 | Protek 24/7 Building & Maintenance | Roof leak in center of room - Possible skylight roof sheet deterioration | Roofing | Metal Roofing | 1229.82 | Pass | Fail | 0 | 15 | 2566.5 | 2022-07-21 10:33 | 2022-07-26 17:00 | 2022-07-25 12:00 | 2022-07-26 17:00 | 2022-11-09 10:30 |  | WACCES | ? Remove and dispose of damaged skylight sheet? Supply and install Fibreglass skylight sheet and fixings? Supply and install Compriband supa-seal under flashing? Complete water-test once works complete
MSA-DTWD | WA5481632 | 2 | BAKE-QUIP PTY LTD | E-Block - Restaurant Kitchen - the large soup kettle is not connecting at times | Equipment | Catering Equipment | 1628.3 | Pass | Fail | 0 | 15 | 2566 | 2022-05-30 15:14 | 2022-06-02 17:00 | 2022-05-31 15:45 | 2022-06-02 17:00 | 2022-09-15 13:45 |  | WACCES | Refer to service report
MSA-DFES | WA5869050 | 2 | Protek 24/7 Building & Maintenance | Workshop - Conference room - Roof leak in the ceiling | Roofing | Tiled Roofing | 8148.47 | Fail | Fail | 1 | 16 | 2564 | 2022-09-14 11:36 | 2022-09-19 17:00 | 2022-09-27 14:00 | 2022-09-19 17:00 | 2023-01-12 10:00 |  | WACCES | ? Applied silicone to area to attempt to provide temporary fix? Carried out site measure to confirm materials required? Remove and dispose of entire dilapidated roof mounted vent unit? Supply and install new 300mm Throat Ridge Vent to roof? Supply and install new tray flashing to ridge vent and seal? Remove and dispose of 2x damaged ceiling boards? Supply and install 2x new ceiling boards
MSA-DTWD | WA5216846 | 2 | Ronley Holdings Pty Ltd | 4x hoods in the welding bays for extract toxic fumes - falling apart & are no longer work correctly | Electrical | General Electrical | 6275 | Pass | Fail | 0 | 15 | 2562.25 | 2022-03-11 13:26 | 2022-03-16 17:00 | 2022-03-16 15:15 | 2022-03-16 17:00 | 2022-07-01 09:30 |  |  | Replace 4 hoods in the welding bay with 4 x Plymoth hoods with arms.
MSA-DTAG | WA5869138 | 3 | Australian HVAC Services Pty. Ltd. | Chiller 1 in fault | Air Conditioning | Evaporative Coolers | 7436.05 | Pass | Fail | -1 | 14 | 2546.5 | 2022-09-14 11:48 | 2022-09-21 17:00 | 2022-09-14 13:30 | 2022-09-21 17:00 | 2022-12-29 16:00 |  | WACCES | After actuator fitted by controls tech, cover was made, we accessed site & fitted weather cover to actuator.tested actuator to check operation is not hindered by cover
MSA-DFES | WA5686583 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | 2 x Fluro lights blinking 1 in the change room, 1 in the engine room | Electrical | Lighting, Internal | 642.095 | Pass | Fail | 0 | 15 | 2524.75 | 2022-08-01 09:32 | 2022-08-04 17:00 | 2022-08-03 09:15 | 2022-08-04 17:00 | 2022-11-16 14:00 |  | WACCES | Located faulty lights. The light in the change room needed replacement. Replaced faulty light with new. There are two faulty lights in the engine bay that need replacement. They are 4.6 meters high will need to return with a taller ladder to change out there lights. Matthew Kenney (16/11/2022) - Work NoteArrived onsite at 13:00 to replace 2x faulty fluro fittings in engine bay, replaced faulty fittings with 2x new LED batons, all engine bay lights now working, advised staff of works and left site 14:00
MSA-DTAG | WA5107878 | 3 | Seme Solutions Pty Ltd | Rockingham Court - Family Violence Office -Security Panel is faulty - no display | Security | Monitoring | 880.99 | Fail | Fail | 0 | 15 | 2521.1 | 2022-02-08 10:02 | 2022-02-15 17:00 | 2022-02-16 13:00 | 2022-02-15 17:00 | 2022-06-01 14:06 |  | WACCES | Decommission old unit and remove programming, reinstate new device with old programming, install and test all okay.
MSA-DTWD | WA6008487 | 3 | Critical Fire Protection & Training | Diesel Pump coolant issue - see notes below | Fire Protection Services | Sprinkler Systems | 688.6 | Pass | Fail | 0 | 15 | 2515 | 2022-10-11 15:29 | 2022-10-18 17:00 | 2022-10-18 14:00 | 2022-10-18 17:00 | 2023-01-31 09:00 |  | WACCES | Replace 20mm float valve in the tank.Repair coolant pump packing gland.
MSA-DTWD | WA6207743 | 1 | Equans Mechanical Services Australia | Chiller for distillation unit not cooling enough-see notes | Refrigeration | Chiller | 1999.995 | Pass | Fail | 0 | 15 | 2501.5 | 2022-11-17 12:10 | 2022-11-18 17:00 | 2022-11-18 08:00 | 2022-11-18 17:00 | 2023-03-02 13:30 |  |  | Attended call, unit not coping with warm temperatures. Appeared short of gas. Also appeared too small for task, however has been in place for a considerable time. Reclaimed and weighed refrigerant. System slightly short of gas. Sourced refrigerant, drier and fittings. Fitted and pressure tested with nitrogen. Passed. Evacuated and tested Passed. Added refrigerant noted that controller was damaged and required replacement - raised separate job. Could not charge until controller replaced.Controller replaced. Charge unit. Tested operation. Tested operation with distillation plant and controls.
MSA-DTWD | WA5141712 | 1 | WESTERN IRRIGATION PTY LTD | O Greenhouse Water Recycling Plant -The main filter is leaking. see notes | Plumbing & Drainage | Water | 7106.42 | Pass | Fail | 0 | 15 | 2497.9 | 2022-02-16 11:46 | 2022-02-17 17:00 | 2022-02-16 14:15 | 2022-02-17 17:00 | 2022-05-31 16:09 |  | WACCES | Check leak on filter, sourcing replacement filter.16 -5 -2022 Installed replacement filter.31-5-2022 Installed additional valves, tested and commissioned.
MSA-DTWD | WA5111296 | 3 | Precise Air Group | A Block - Level 1 - A107 - Cafe Cool Room -Compressor water waste leaking into cool room | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Fail | -1 | 14 | 2497.5333 | 2022-02-10 07:29 | 2022-02-16 17:00 | 2022-02-10 11:30 | 2022-02-16 17:00 | 2022-05-25 13:02 |  |  | System no longer leaking from wall penetration
MSA-DFES | WA5216355 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Firefighter Dorm 1 (3 man dorm) ensuite exhaust fan does not activate when sensor triggered | Electrical | General Electrical | 1459.795 | Pass | Fail | 0 | 15 | 2495.5 | 2022-03-11 09:27 | 2022-03-16 17:00 | 2022-03-15 10:30 | 2022-03-16 17:00 | 2022-06-27 10:00 |  | WACCES | Attended site and signed in, located faulty fan on roof. Isolated and replaced fan unit. Tested and commissioned. Fan working correctly. Informed staff of job completion.
MSA-DTWD | WA5208801 | 3 | Precise Air Group | A block - Roof - Exhaust Fan 16 has loud bearing noise | Air Conditioning | Room Air Conditioners | 193.62 | Pass | Fail | -1 | 14 | 2492.1 | 2022-03-09 11:02 | 2022-03-16 17:00 | 2022-03-10 13:00 | 2022-03-16 17:00 | 2022-06-22 09:06 |  |  | Braf declined - closing out work order
MSA-DCA | WA5491344 | 2 | Precise Air Group | Level 1 - Main Theatre - AC Units not heating - See notes below | Air Conditioning | Room Air Conditioners | 4821.19 | Pass | Fail | 0 | 15 | 2490 | 2022-06-03 14:38 | 2022-06-09 17:00 | 2022-06-08 14:00 | 2022-06-09 17:00 | 2022-09-20 08:00 |  |  | Found AC-G16 stuck in cooling due to faulty wall sensors that will need replacing. Found AC-G17 stage 2 cutting out on low pressure, system will need a gas leak and repair. Due to age and condition of units recommended budgeting for replacement
MSA-DCA | WA5660333 | 1 | Precise Air Group | boilers not operating, | Mechanical Services | Boilers | 699.425 | Pass | Fail | 0 | 15 | 2474.9 | 2022-07-19 09:02 | 2022-07-20 17:00 | 2022-07-19 11:46 | 2022-07-20 17:00 | 2022-10-30 14:40 |  | WACCES | Travelled to site gained access, spoke with site contact regarding issues with boiler, fault finding through system found hot water pump 1 contractor requires replacing. Order new contractor from supplier, will be in next few days. Also checked operation, found boilers operating. Require pump 1 to carry out full inspection. Will return with partsReturned with parts, isolated board, removed failed contract or, installed new contractor, run pump, checked operation, f ound boiler 1 not switching on, has a request from BMS but n ot running, a BRAF to be submitted to have boiler tech atten ded and rectify. Boiler 2 is currently operating to specsBoiler tech has returned to site during maintenance and conf irmed correct operation of system. Job to be closed off
MSA-DTAG | WA5187643 | 2 | Midolo Building Services | Basement - Cell 4 - Rubber strips to dull door banging noise have been removed by detainee | Building | Doors | 299.3 | Pass | Fail | 0 | 15 | 2472.25 | 2022-02-22 14:16 | 2022-02-25 17:00 | 2022-02-25 08:00 | 2022-02-25 17:00 | 2022-06-08 08:15 |  | WACCES | door repaired & new seal installed
MSA-DTWD | WA5696799 | 3 | AWB Co. | A308 leaking near window into room | Building | Windows | 3470.86 | Pass | Fail | 0 | 15 | 2472 | 2022-08-08 14:43 | 2022-08-15 17:00 | 2022-08-15 11:30 | 2022-08-15 17:00 | 2022-11-26 11:30 |  | WACCES | works completed as per sign slips
MSA-DTWD | WA6129432 | 3 | Schneider Electric Australia Pty Ltd | Control room - Repair Fault on File master to Access Control data base | Equipment | Building Equipment |  | Pass | Fail | -1 | 14 | 2470.25 | 2022-10-27 14:52 | 2022-11-03 17:00 | 2022-10-27 15:15 | 2022-11-03 17:00 | 2023-02-07 13:30 |  |  | Completed
MSA-DTWD | WA5973671 | 1 | SCAVENGER SUPPLIES PTY LTD | Back of Heavy Auto Workshop - Leaking fire hydrant | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 3931.28 | Fail | Fail | 0 | 15 | 2452 | 2022-09-21 16:38 | 2022-09-22 17:00 | 2022-09-23 07:00 | 2022-09-22 17:00 | 2023-01-03 11:00 |  | WACCES | SC-6867-First visit completed 23/09/2022 will require more time on site30/10/2022 Braf submitted for approval 02/11/2022 Braf-checked -not yet approved08/11/2022-Braf-checked-not yet approved22/11/2022 Braf approved- Paul advised AND WORK TO BE SCHEDULED WITH MATT & DPH 12/12/223/01/2023 - Works completed.
MSA-DTWD | WA6249737 | 3 | Equans Mechanical Services Australia | Oil and gas plant Level 1 - Faulty temperature controller on distillation unit chiller | Refrigeration | Chiller | 1962.22 | Pass | Fail | -1 | 13 | 2424.5 | 2022-11-21 14:16 | 2022-11-28 17:00 | 2022-11-21 14:30 | 2022-11-28 17:00 | 2023-03-02 15:00 |  |  | Whilst working on other issue with chiller noted was unable to read screen of controller to check settings and status. Recommended replacement. Controller obsolete was able to source replacement controller. Arranged access with site scheduler next week.Received new controller, however the new controller was not a direct replacement for the old controller. It had been upgraded significantly to a blue tooth model with different wiring requirements. Sourced original chiller wiring diagrams and control drawings. Mapped old and new wiring and controllers. Made requires with control manufacturer advised new wiring harness also required. Mapped new harness and transposed wiring numbers from old wiring to new and rewired system. Set up system, configured parameters tested system. Refined setting to suit and tested. Tested with distillation process controller. Left operational.
MSA-DFES | WA5564128 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Outside on veranda and up lights in mall - lights are out | Electrical | General Electrical | 428.055 | Pass | Fail | 0 | 14 | 2402.8833 | 2022-06-21 08:34 | 2022-06-22 17:00 | 2022-06-21 11:45 | 2022-06-22 17:00 | 2022-09-29 14:38 |  |  | Arrived onsite at 12:45 to disconnect ground lights and install galvanised metal plates over ground lights upon client request. Half way into disconnecting lights and investigating client advised that they didn’t want ground lights disconnected anymore as they needed to have them connected for security purposes. Put lights back together and kept reconnected exactly as they were. Liased with site to confirm that’s what they wanted and left site at 14:30
MSA-DCA | WA5797665 | 1 | Automatic Fire Protection (ARA) | Basement security office-Fault description False alarm on fire system. Fault showing -see notes | Fire Protection Services | Fire Protection - Monitor System | 613.43 | Pass | Fail | 0 | 14 | 2399.45 | 2022-08-29 09:15 | 2022-08-30 17:00 | 2022-08-29 12:33 | 2022-08-30 17:00 | 2022-12-07 12:00 |  | WCAPPR | Attended site and found device 4029 Az 32 in maintenance fault traced through area but unable to locate exactly where device is but are confident it’s in the roof space outside the lift.Will require an access panel cut to reach detector.Attended site and worked with builder to work our panel location.10/10/2022 Denise has advised that they may be asbestos in the area and works are on hold until further notice07/12/2022Currently we are waiting on the Dept to approve one of the quotes to remove the asbestos.I have just spoken with Reese and he requested to close off the breakdown, “unable to access due to limitations”.
MSA-DTWD | WA5597501 | 2 | WESTERN IRRIGATION PTY LTD | Bore system / lake - Bore system showing fault on panel low water, and lake fountain not working | Equipment | Electrical Equipment | 22244.48 | Fail | Fail | 1 | 15 | 2374 | 2022-07-11 13:33 | 2022-07-14 17:00 | 2022-07-21 11:00 | 2022-07-14 17:00 | 2022-10-28 09:00 |  |  | Report in the form of a BRAF with cost to remove pump and aerator for further investigation work was provided 22 July 2022.
MSA-DTWD | WA5151023 | 1 | Equans Mechanical Services Australia | D Block - Ground - D29 - A/C not working | Air Conditioning | Room Air Conditioners | 2764.97 | Fail | Fail | 1 | 15 | 2367 | 2022-02-17 10:13 | 2022-02-18 17:00 | 2022-02-23 08:00 | 2022-02-18 17:00 | 2022-06-01 23:00 |  | WACCES | FOUND ONE CEILING CASSETTE ON AUTO , THE OTHER ONE WAS ON COOLING AND ONCE THE TEMPERATURE GETS DOWN THE FIRST ONE SWITCHES TO HEATING. ASSISTED BY DAVE WITH WORKING AT HEIGHTS INSTALLED NEW PARTS TESTED ALL OK. CLEANED UP AND COMPLETED PAPERWORK.SET BOTH ON COOLING AND TEST RAN ALL OK
MSA-DTAG | WA6143349 | 1 | Sapio Pty Ltd | Zone 138 – Reception Clerk - Duress Alarm is faulty | Security | Security Management System | 3992.22 | Pass | Fail | 0 | 14 | 2361.5 | 2022-11-01 11:46 | 2022-11-02 17:00 | 2022-11-02 10:30 | 2022-11-02 17:00 | 2023-02-08 20:00 |  | WACCES | Work performed by Dirk Malan, Mitchell Watt & Chris Kelleher AFTER HOURS 14/01/2023 & 08/02/2023:Recabled and replaced duress. Job completed.
MSA-DTWD | WA5479940 | 1 | Equans Mechanical Services Australia | Block 3 Toilets - Faulty Toilet Exhaust Fan | Equipment | Building Equipment | 6865.87 | Fail | Fail | 0 | 14 | 2355.8833 | 2022-05-27 13:21 | 2022-05-30 17:00 | 2022-06-02 10:45 | 2022-05-30 17:00 | 2022-09-08 14:38 |  |  | Unable to gain access due to rain.Fan blade broken off shaft. Email sent to Perth air and power to quote replacing unit. Braf to be submitted.
MSA-DTWD | WA5151347 | 3 | Equans Mechanical Services Australia | Block 8 - AC4 air con unit tripping | Air Conditioning | Room Air Conditioners | 1849.5 | Pass | Fail | -1 | 13 | 2354.5 | 2022-02-17 12:30 | 2022-02-24 17:00 | 2022-02-17 13:00 | 2022-02-24 17:00 | 2022-05-26 15:30 |  |  | Located Frigopol unit in Block 8 upstairs plantroom and found that stage 2 was cutting in and out. Investigated and found that stage 2 had lost its gas and gas a leak somewhere in the system. Temporarily isolated stage 2 so stage 1 will still run. Braf to be created for repairs.
MSA-DFES | WA5572583 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | TV Room/Lounge - TV will not receive channel 2/ABC - please check the antenna | Electrical | General Electrical | 991.8 | Pass | Fail | 0 | 14 | 2348.5 | 2022-06-30 08:52 | 2022-07-07 17:00 | 2022-07-07 13:30 | 2022-07-07 17:00 | 2022-10-13 10:00 |  | WACCES | Arrived on site at 07:00 to replace digital Tv antenna for TV room/lounge. Left to collect gear from wholesaler. Found splitter in roof and cabling to main tv point from splitter to be old, replaced splitter and cabling. Replaced tv antenna on roof and tested. All working, notified staff of outcome and continued to Volunteer side of site at 10:00.
MSA-DTWD | WA6166311 | 2 | AWB Co. | The fire proof Gyprock above the distribution box has collapsed | Building | General Building | 48.42 | Pass | Fail | 0 | 14 | 2333.8667 | 2022-11-11 13:53 | 2022-11-16 17:00 | 2022-11-15 08:00 | 2022-11-16 17:00 | 2023-02-20 13:52 |  |  | Works completed
MSA-DTWD | WA5476110 | 2 | AWB Co. | Roof leak into C001 | Roofing | Metal Roofing | 5640.43 | Pass | Fail | -1 | 13 | 2328 | 2022-05-25 10:56 | 2022-05-30 17:00 | 2022-05-26 14:30 | 2022-05-30 17:00 | 2022-08-31 14:30 |  | WACCES | Attended as per signature slip attached, BRAF required.Installed new boards and pipe as per BRAF
MSA-DTWD | WA5109613 | 2 | M Construction (WA) | Dry Cure Room - Moisture damaged sagging ceiling | Building | General Building | 5232.51 | Pass | Fail | -1 | 13 | 2327.75 | 2022-02-09 11:48 | 2022-02-14 17:00 | 2022-02-10 12:00 | 2022-02-14 17:00 | 2022-05-18 11:45 |  |  | Attended site and replaced ceiling.
MSA-DFES | WA5472650 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Stores Warehouse Section - Ceiling - faulty overhead lighting | Electrical | Lighting, Internal | 958.21 | Pass | Fail | 0 | 14 | 2304.25 | 2022-05-24 09:24 | 2022-05-27 17:00 | 2022-05-27 12:15 | 2022-05-27 17:00 | 2022-08-31 12:30 |  | WACCES | Arrived on site at 1015am to replace light in high bay. Unloaded scissor lift, replaced highbay light, tested/reenergised circuit. Notified staff and left site at 1230pm.
MSA-DTAG | WA5141550 | 1 | Australian HVAC Services Pty. Ltd. | All areas - Court 1, Magistrate Chambers - see details below | Air Conditioning | Room Air Conditioners | 3319.845 | Pass | Fail | 0 | 14 | 2302 | 2022-02-16 11:00 | 2022-02-17 17:00 | 2022-02-16 12:00 | 2022-02-17 17:00 | 2022-05-23 10:00 |  |  | Attend site. Access court 1 FCU 2. Drain water from system. Remove old isolation valves from pipework and install new. Disconnect electrical wiring to actuator. Cut out existing pipework and chilled water valve. Modify pipework and install new chilled water valve. Insulate pipework and connect actuator to valve. Connect electrical wiring and test operation, working ok. Fill system with water and bleed air. Run pumps and test operation, working ok. Clean up area.
MSA-DFES | WA5681732 | 1 | Go Doors | Yard - Gate D007 (Gate#2) - Security Gate D007 motor is defective and inoperable | Building | Automatic Doors | 3518.94 | Pass | Fail | 0 | 13 | 2279.25 | 2022-07-28 14:36 | 2022-07-29 17:00 | 2022-07-28 15:45 | 2022-07-29 17:00 | 2022-10-31 15:00 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5301853 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Comcen - Level 1 - Multiple lights faulty -Work to be carried out after 6pm - see notes | Electrical | General Electrical | 675.275 | Pass | Fail | 0 | 13 | 2275 | 2022-04-01 13:16 | 2022-04-08 17:00 | 2022-04-07 18:15 | 2022-04-08 17:00 | 2022-07-11 13:15 |  | WACCES | Continued onsite at 11:45 to install remaining globes and tubes to fix all lights in COMCEN. Found lights in kitchen and COMCEN had been replaced under another job since last visit. Was able to replace 2 x tubes in COMCEN office that had gone since last trip and 4 x globes in COMCEN kitchen. Tested lights and continued onsite at 13:15
MSA-DTAG | WA5499172 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - Plantroom - Cooling tower water leak – adjust float level | Air Conditioning | Cooling Tower | 3289.75 | Pass | Fail | -1 | 13 | 2255.4333 | 2022-06-10 10:53 | 2022-06-17 17:00 | 2022-06-13 12:00 | 2022-06-17 17:00 | 2022-09-15 11:26 |  | WACCES | Return to site. Access level 4 plantroom and fill cooling tower with water. Check for leaks. No leaks found. Deisolate all valves. Reinstate water treatment station. Access BMS and remove all pump overrides. Remove plastic from to pf tower. Manually run condenser water pump and check operation of tower and monitor float level. Tower working as normal.
MSA-DFES | WA6107778 | 1 | Protek 24/7 Building & Maintenance | Fence Line - Front Gate - Electrical Fence is broken - Wire has come off | Building | Steel Fencing & Gates | 1426.67 | Pass | Fail | 0 | 13 | 2254.5 | 2022-10-20 09:12 | 2022-10-21 17:00 | 2022-10-21 13:00 | 2022-10-21 17:00 | 2023-01-23 11:30 |  |  | specialist fencing contractor was required for repair
MSA-DTWD | WA6231161 | 2 | Australian Airconditioning Services Pty Ltd | D18.1 cool room-Fault description Walk in Cool room is running warm (3-5 degrees above set point) | Refrigeration | Coolroom | 1176.39 | Pass | Fail | 0 | 13 | 2236.25 | 2022-11-18 14:18 | 2022-11-23 17:00 | 2022-11-21 11:45 | 2022-11-23 17:00 | 2023-02-22 16:00 |  | WACCES | complete
MSA-DTWD | WA5477613 | 3 | AWB Co. | C109 - Rear doors are badly weathered and damaged - see details below | Electrical | General Electrical | 2326.84 | Pass | Fail | 0 | 13 | 2234.8667 | 2022-05-25 15:26 | 2022-06-01 17:00 | 2022-05-31 07:10 | 2022-06-01 17:00 | 2022-09-01 10:02 |  |  | works completedreplace and paint double doors and hardware
MSA-DTWD | WA5735639 | 3 | Protek 24/7 Building & Maintenance | Outside eastern side of building - replace stolen rain head from gutters | Roofing | Guttering | 834.315 | Pass | Fail | -1 | 12 | 2234 | 2022-08-16 14:04 | 2022-08-23 17:00 | 2022-08-17 07:00 | 2022-08-23 17:00 | 2022-11-18 09:00 |  | WACCES | Located missing rain-heads onsite, causing spillage onto pathwaysDocumented scope of works and carried out site measure to confirm materials? Setup mobile scaffold onsite? Remove and dispose of left over materials from rain-heads? Supply and install 2x Rain-heads and fixings
MSA-DTWD | WA5478410 | 2 | Falcetta Plumbing and Gas | Engineering Courtyard - please see details below | Plumbing & Drainage | Drainage |  | Pass | Fail | -1 | 13 | 2232 | 2022-05-26 11:29 | 2022-05-31 17:00 | 2022-05-26 16:00 | 2022-05-31 17:00 | 2022-08-27 16:00 |  | WACCES | replaced ball and check valves by removing manifold
MSA-DTWD | WA5749051 | 3 | Protek 24/7 Building & Maintenance | Courtyard - Replace stolen rain head from gutters - See notes below | Roofing | Guttering | 658.23 | Pass | Fail | -1 | 12 | 2231.5 | 2022-08-17 08:36 | 2022-08-24 17:00 | 2022-08-17 10:30 | 2022-08-24 17:00 | 2022-11-18 10:00 |  | WACCES | ? Setup mobile scaffold onsite? Remove and dispose of left over materials from rain-heads? Supply and install 2x Rain-heads and fixings
MSA-DTWD | WA5567751 | 2 | BAKE-QUIP PTY LTD | Combi Oven closest to coolrooms – temp probe not reading correct temps | Equipment | Catering Equipment | 999 | Fail | Fail | 1 | 14 | 2218.5 | 2022-06-24 11:59 | 2022-06-29 17:00 | 2022-07-04 08:00 | 2022-06-29 17:00 | 2022-10-04 18:30 |  | WACCES | REFER TO SERVICE REPORT.
MSA-DFES | WA5687897 | 1 | Protek 24/7 Building & Maintenance | Above Laundry Stairs - Significant Roof Leak - See notes below | Roofing | Metal Roofing | 2344.85 | Pass | Fail | 0 | 13 | 2208.75 | 2022-08-02 08:13 | 2022-08-03 17:00 | 2022-08-02 13:45 | 2022-08-03 17:00 | 2022-11-02 14:30 |  | WACCES | ? Supply and install new colorbond flashing to top of gym balcony wall ? Clean and reseal along base of balcony floor tiles and edge trim tile? Seal edges to 3x flow outlets from balcony? Carry out water-test after works complete
MSA-DTWD | WA5834266 | 2 | Protek 24/7 Building & Maintenance | 3x small roof leaks in welding bays - See notes below | Roofing | Metal Roofing | 3634.41 | Pass | Fail | 0 | 13 | 2208.5 | 2022-09-06 14:42 | 2022-09-09 17:00 | 2022-09-08 14:30 | 2022-09-09 17:00 | 2022-12-09 15:00 |  | WACCES | ? Remove and dispose of damaged roof sheet & dilapidated dek-tite? Supply and install new roof sheet and fixings? Supply and install new tray flashing to length of new roof sheet and seal? Supply and install new dek-tite and seal
MSA-DTWD | WA5676448 | 2 | Precise Air Group | Problem with heating on AHU8 for Level 4 classrooms. Rooms not reaching temperature - See notes belo | Air Conditioning | Room Air Conditioners | 325.68 | Pass | Fail | 0 | 13 | 2207.55 | 2022-07-25 08:38 | 2022-07-28 17:00 | 2022-07-25 14:51 | 2022-07-28 17:00 | 2022-10-25 14:24 |  | WACCES | Organised subcontractor to attend site
MSA-DTAG | WA5294160 | 1 | Australian HVAC Services Pty. Ltd. | Roof - AC plant - Crt 3 FCU 5 s/Air temp 13C. HW valve 100% open- Airconditioning very cold Court 3 | Air Conditioning | Room Air Conditioners | 5524.01 | Pass | Fail | 0 | 13 | 2191 | 2022-03-28 13:28 | 2022-03-29 17:00 | 2022-03-29 07:30 | 2022-03-29 17:00 | 2022-06-28 14:30 |  |  | Hire compression to from supplier. Pick up all gear required for works. Attend site and access plantroom. Isolate all valves and heating water system. Drain water out of system. Cut old valves off and compress new fittings to pipework. Install new valves and connect. Deisolate water supply and check for leaks. Clean off all surface corrosion from pot and paint. Clean up area.
MSA-DTWD | WA5682694 | 3 | AWB Co. | CBUS PC has an invalid disk error showing | Electrical | General Electrical | 7758.17 | Pass | Fail | 0 | 13 | 2186.5 | 2022-07-29 10:41 | 2022-08-05 17:00 | 2022-08-05 10:00 | 2022-08-05 17:00 | 2022-11-04 12:30 |  | WACCES | works ocmpleted
MSA-DTWD | WA5318131 | 1 | AWB Co. | Room E110 -Plant Room - GPOS and lights do not work | Electrical | General Electrical | 1952.115 | Pass | Fail | 0 | 13 | 2183 | 2022-04-12 08:33 | 2022-04-13 17:00 | 2022-04-12 12:30 | 2022-04-13 17:00 | 2022-07-12 11:30 |  | WCAPPR | Attended site signed in jsa completed. Ran two feeds one for lights one for power from grey box. Conduit into the bottom of mechanical board. All tested and now lights power switches and pe cell with two lights are working.Job completed.
MSA-DTWD | WA5285986 | 1 | Precise Air Group | B block - B05 - Squealing noise coming from Plant room ( appears belt from Fan motor slipping ) | Air Conditioning | Room Air Conditioners | 2812.66 | Pass | Fail | 0 | 13 | 2160 | 2022-03-21 11:43 | 2022-03-22 17:00 | 2022-03-22 08:00 | 2022-03-22 17:00 | 2022-06-20 08:00 |  |  | Attended site and completed pre start paperwork and signed in. Acessed air handler and found belts worn. Attended supplier and collected new belts. Returned to site and fitted. Braf pending for replacement motor. Left system operating.
MSA-DTWD | WA5089790 | 2 | Precise Air Group | P-Block room P006 connect BMS to Q-Block | Air Conditioning | Building HVAC Maintenance (Major Plant) | 235.48 | Fail | Fail | 19 | 32 | 2157.3167 | 2022-01-25 06:26 | 2022-01-28 17:00 | 2022-06-08 14:16 | 2022-01-28 17:00 | 2022-09-06 11:35 |  |  | Please have IT department set up BMS onto computer, as this is out of PAGS scope of works this WO is now closed
MSA-DTAG | WA5115945 | 2 | Australian HVAC Services Pty. Ltd. | Level 10 - Coroner’s office - Air does not seem to be circulating on level 10 | Air Conditioning | Room Air Conditioners | 2585.99 | Pass | Fail | -1 | 12 | 2157 | 2022-02-11 10:16 | 2022-02-16 17:00 | 2022-02-11 11:00 | 2022-02-16 17:00 | 2022-05-12 08:00 |  |  | Check temps on BMS and found VAV 10.08 working as normal
MSA-DTWD | WA5680577 | 1 | Precise Air Group | FCU 44 in fault. Requires repair | Air Conditioning | Room Air Conditioners | 354.73 | Pass | Fail | 0 | 13 | 2140.1167 | 2022-07-27 13:28 | 2022-07-28 17:00 | 2022-07-28 10:30 | 2022-07-28 17:00 | 2022-10-25 14:37 |  |  | attended site signed and inspected site bms. found unit is i n fault but could not gain access to classroom as it was cur rently occupied. Will need to re book for a 7am start.reattended and attemptedcto fault find. unable to diagnose f ault properly. Suspect it could be a controls issue. We will need to engage NRP and organise a time to attend siteworks has been completed on seprate WO, issue has now bee re solved and works can be closed as a result. system operating correctly
MSA-DTWD | WA5564290 | 2 | Water2water Pty Ltd | F100 - Water Cooler tripping power circuit | Plumbing & Drainage | Water | 3950.465 | Pass | Fail | 0 | 12 | 2138.3333 | 2022-06-21 09:30 | 2022-06-24 17:00 | 2022-06-22 10:40 | 2022-06-24 17:00 | 2022-09-19 13:00 |  | WACCES | Requires new unit Replaced unit
MSA-DTAG | WA5682372 | 1 | Midolo Building Services | whole of building- major flood needs to be made safe | Roofing | Metal Roofing | 3567.63 | Pass | Fail | 0 | 12 | 2138 | 2022-07-29 08:51 | 2022-08-01 17:00 | 2022-07-29 09:30 | 2022-08-01 17:00 | 2022-10-26 11:30 |  | WACCES | cleaned and dried out carpet, repaired ceiling and painted
MSA-DFES | WA5126328 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Multiple faulty lights - see notes for locations | Electrical | Lighting, Internal | 1061.285 | Pass | Fail | 0 | 13 | 2135.75 | 2022-02-14 07:34 | 2022-02-18 17:00 | 2022-02-18 10:00 | 2022-02-18 17:00 | 2022-05-18 09:45 |  | WACCES | Arrived onsite at 10:00 to investigate lights not working in mentioned locations. Found 3 x downlight a not working due to faulty drivers, 1 x light not working in courtyard due to no voltage (fault) and and 5 x fluros with faulty tubes. Will need to return to site with parts to fix as parts are special order and are not readily available. Left site at 11:30
MSA-DTWD | WA5570622 | 1 | Equans Mechanical Services Australia | Room D01 - AHUD1 not heating | Air Conditioning | Building HVAC Maintenance (Major Plant) | 4127.46 | Fail | Fail | 0 | 13 | 2134.5 | 2022-06-28 13:02 | 2022-06-29 17:00 | 2022-06-30 12:30 | 2022-06-29 17:00 | 2022-09-27 11:00 |  | WACCES | Picked up required parts refitted fan deck, replaced motor bearings. Tested all ok cleaned up and completed paperwork assisted by Dave Dos.
MSA-DCA | WA5656411 | 1 | Precise Air Group | ground-Ducted units are non responsive. Please investigate. | Air Conditioning | Room Air Conditioners | 1253.84 | Fail | Fail | 1 | 14 | 2120.2167 | 2022-07-18 13:48 | 2022-07-19 17:00 | 2022-07-29 09:34 | 2022-07-19 17:00 | 2022-10-25 17:47 |  |  | Attended site and checked ducted units found multiple issues with stages. Repair quote to follow. Units extremely poor condition and past life expectancy recommended replacing
MSA-DTAG | WA5116485 | 2 | Midolo Building Services | Registry - Ground - Wall near safe in registry - see details below | Building | General Building | 1722 | Pass | Fail | 0 | 12 | 2114 | 2022-02-11 15:57 | 2022-02-16 17:00 | 2022-02-14 11:00 | 2022-02-16 17:00 | 2022-05-13 13:00 |  | WACCES | Window re glazed & tinted
MSA-DTAG | WA5116155 | 1 | Sapio Pty Ltd | 2 x PTZ cameras faulty – connection lost to the server. | Security | CCTV Surveillance | 2263.1 | Pass | Fail | 0 | 12 | 2094 | 2022-02-11 11:47 | 2022-02-14 17:00 | 2022-02-14 10:00 | 2022-02-14 17:00 | 2022-05-12 16:00 |  | WACCES | Replaced camera in Staff Entrance Lift Lobby, confirmed working correctly.
MSA-DTWD | WA5674443 | 2 | AWB Co. | Foyer-Series of lights inoperative throughout building-see notes | Electrical | Lighting, Internal | 2264.185 | Pass | Fail | 0 | 12 | 2089.5 | 2022-07-21 11:54 | 2022-07-26 17:00 | 2022-07-26 10:00 | 2022-07-26 17:00 | 2022-10-21 11:30 |  | WACCES & WCAPPR | Attended site signed in jsa completed.Replaced various drivers for lights on site. Replaced one g12 globe in ground.Job completed
MSA-DTWD | WA5887698 | 2 | Dormakaba Australia Pty Ltd | Restaurant Kitchen - interleading auto sliding door not working | Building | Automatic Doors |  | Pass | Fail | -1 | 12 | 2086.1167 | 2022-09-16 09:23 | 2022-09-21 17:00 | 2022-09-16 14:47 | 2022-09-21 17:00 | 2022-12-12 12:54 |  |  | Found that the door was in fault, failtime, reset controller, checked and adjusted settings, tested operation, disc condition was 6, operating correctly at time of test. Refer WO-03263795 - No charge for this order.Return to site. Removed existing faulty door equipment and replaced with new ES200 upgrade kit complete with new sensor and mode switch as per quotation. Setup and tested operation upon completion and left in good working order.
MSA-DTAG | WA5675443 | 3 | Seme Solutions Pty Ltd | CCTV2 Camera 46 Assesmbly Area (3) not working + other cameras not working need investigating. | Security | CCTV Surveillance | 2781.32 | Pass | Fail | -1 | 12 | 2071.5 | 2022-07-22 10:46 | 2022-07-29 17:00 | 2022-07-25 08:00 | 2022-07-29 17:00 | 2022-10-19 15:30 |  | WACCES | 6 - Front entrance (1) replaced POE injector and neatened cabling at pole base. PTZ back online and operational.21 - tried resetting camera and reprogramming - keeps dropping off intermittently - separate job already open for cam.44 - BRAF'ed to replace on separate job45 - removed from software on separate work order as been removed from system.46 - Waiting (3) (Located above custodial control room door) black and white screen - camera has failed and requires upgrade to IP - separate job raised. WA6128228
MSA-DTAG | WA5318343 | 1 | Australian HVAC Services Pty. Ltd. | Custody - Lower - Custody air conditioning unit AC12 is making loud noises | Air Conditioning | Room Air Conditioners | 874.34 | Pass | Fail | 0 | 12 | 2066 | 2022-04-12 10:38 | 2022-04-13 17:00 | 2022-04-12 12:00 | 2022-04-13 17:00 | 2022-07-07 14:00 |  | WACCES | Picked up parts, attended site & isolated power to ac12. Removed old evap fan motor & fitted new motor. Rewired & reinstated power. Tested system operation, ok disposed of old parts
MSA-DTWD | WA5481635 | 3 | Protek 24/7 Building & Maintenance | Old auto service bay door- Door needs repair/replacing | Building | Doors | 1322.545 | Pass | Fail | -1 | 11 | 2064.25 | 2022-05-30 15:14 | 2022-06-07 17:00 | 2022-06-01 13:15 | 2022-06-07 17:00 | 2022-08-26 13:30 |  |  | • Remove door from frame and remove hardware• Sand back door completely and prepare for painting• Apply undercoat and 2 coats of paint (repaint to suit colour match)• Once dry, reinstall door hardware and hang back onto frame
MSA-DTWD | WA5962239 | 2 | Protek 24/7 Building & Maintenance | Roof leak - outside of J17 | Roofing | Tiled Roofing | 2781.215 | Pass | Fail | 0 | 12 | 2064 | 2022-09-19 12:53 | 2022-09-22 17:00 | 2022-09-20 12:30 | 2022-09-22 17:00 | 2022-12-15 12:30 |  | WACCES | ? Remove and dispose of damaged box gutter? Supply and install new zinc box gutter and connect to existing outlets? Patch eaves with filler and make flush? Apply undercoat and paint eaves once dry to match existin
MSA-DTWD | WA6080014 | 1 | Equans Mechanical Services Australia | Air conditioner fault, not working | Air Conditioning | Room Air Conditioners | 5115.12 | Pass | Fail | 0 | 12 | 2063 | 2022-10-18 13:22 | 2022-10-19 17:00 | 2022-10-18 13:30 | 2022-10-19 17:00 | 2023-01-12 12:30 |  | WACCES | 11/1/2023: Accessed the roof working at heights, carried tools and parts up. Reclaimed the gas , removed all the wiring to access the compressor, unsweated the compressor and fitted the new one, put under nitrogen pressure, removed equipment from the roof. 12/1/2023: accessed the roof again , removed the nitrogen charge, put onto vac pump. Released the gas, test ran all OK , removed the tools and rubbish off the roof.
MSA-DTWD | WA6047875 | 2 | Equans Mechanical Services Australia | Classroom D26 - Aircon not working | Air Conditioning | Room Air Conditioners | 3694.875 | Pass | Fail | 0 | 12 | 2062.5 | 2022-10-17 13:06 | 2022-10-20 17:00 | 2022-10-18 13:30 | 2022-10-20 17:00 | 2023-01-12 12:00 |  | WACCES | Completed removal of old split and installed new tested all ok cleaned up and completed paperwork.
MSA-DFES | WA5677340 | 1 | Protek 24/7 Building & Maintenance | L1 Workshop Bay 3 - Roof Leaking from the roof at Bay 3. | Roofing | Metal Roofing | 798.13 | Pass | Fail | 0 | 12 | 2048.75 | 2022-07-25 14:04 | 2022-07-26 17:00 | 2022-07-26 07:00 | 2022-07-26 17:00 | 2022-10-19 15:45 |  | WACCES | Replace 125 roof screws
MSA-DTAG | WA5128257 | 3 | Australian HVAC Services Pty. Ltd. | Level 5 - Court 56 - Air con making loud humming noise | Air Conditioning | Room Air Conditioners | 1846.15 | Pass | Fail | -1 | 11 | 2044 | 2022-02-14 16:45 | 2022-02-21 17:00 | 2022-02-16 08:00 | 2022-02-21 17:00 | 2022-05-12 12:00 |  |  | 40647
MSA-DFES | WA5677896 | 1 | AWB Co. | Engine Room - Roof leak in engine room near exhaust fans- See notes below | Roofing | Metal Roofing | 3478.12 | Pass | Fail | 0 | 12 | 2043.7 | 2022-07-26 08:19 | 2022-07-27 17:00 | 2022-07-27 11:18 | 2022-07-27 17:00 | 2022-10-20 15:00 |  | WACCES | Works completed
MSA-DCA | WA5494030 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 2 - Main Auditorium Bio Box - Breaker panel - See notes below | Electrical | General Electrical | 393.955 | Pass | Fail | 0 | 12 | 2043 | 2022-06-07 12:15 | 2022-06-10 17:00 | 2022-06-09 12:00 | 2022-06-10 17:00 | 2022-09-02 15:00 |  | WACCES | Continued onsite at 12:00 to investigate breaker tripping located bio box. Found 2 x circuit breakers for grid audio power had been used as isolation switches for grid audio power instead of intended use of circuit protection only. Repeated switching has damaged breakers and both need to be replaced. Will need to upgrade to a physical isolation switch for the power to it unit to be easily isolated and upgrade to RCD due to changing of the circuit. Will return to site with parts to upgrade to isolation switch and RCD. Left site at 12:45Removed faulty circuit breakers, circuit fed from RCBO W19 so rcds are not required.Mounted and wired two isolation switches below the board
MSA-DFES | WA6143757 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Training Dam - Pipe is leaking into dam - See notes below | Plumbing & Drainage | Water | 15386.88 | Pass | Fail | 0 | 12 | 2043 | 2022-11-01 14:11 | 2022-11-04 17:00 | 2022-11-03 07:30 | 2022-11-04 17:00 | 2023-01-27 10:30 |  | WACCES | Arrived on site had to and had assist Tunnel vision in repairing a pipe leakining into a dam.
MSA-DFES | WA5677388 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Stores tool shop - Roof Leaking from the roof at the back of the stores along the back wal | Roofing | Metal Roofing | 998.51 | Pass | Fail | 0 | 12 | 2040 | 2022-07-25 14:19 | 2022-07-26 17:00 | 2022-07-26 14:00 | 2022-07-26 17:00 | 2022-10-19 14:00 |  | WACCES | Remove and replace 400 roof screws
MSA-DFES | WA5677408 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Former FAP Bay (workshop) - Roof leak from the gutter back of the north end of workshop | Roofing | Metal Roofing | 1406.09 | Pass | Fail | 0 | 12 | 2034.25 | 2022-07-25 14:24 | 2022-07-26 17:00 | 2022-07-26 14:45 | 2022-07-26 17:00 | 2022-10-19 09:00 |  | WACCES | Clean and seal 2 gutter sumpsReplace 250 roof screws
MSA-DFES | WA5494299 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | VFRS Personnel Entrance - Rear - Issues with external light - See notes below | Electrical | General Electrical | 178.44 | Pass | Fail | 0 | 12 | 2033.5 | 2022-06-07 13:53 | 2022-06-08 17:00 | 2022-06-07 16:15 | 2022-06-08 17:00 | 2022-08-31 09:45 |  | WCAPPR | Arrived onsite at 9:15 to reconnect security lighting. Found security lighting had already been reconnected by another technician presumably under a different job. Found over ride switch had been changed and RCD reconnected. Confirmed security lights worked and left site at 9:45
MSA-DTAG | WA6191393 | 2 | Sapio Pty Ltd | Resource & Admin Desk - Computer for Gallagher card system not working | Security | Access Control | 3768.13 | Pass | Fail | -1 | 11 | 2024 | 2022-11-16 16:21 | 2022-11-21 17:00 | 2022-11-17 13:00 | 2022-11-21 17:00 | 2023-02-09 21:00 |  |  | Attended after hours and removed faulty workstation.installed new workstation and programmed into network
MSA-DFES | WA5326003 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | External Security Lights and Southern Boundary Fence Light not working - see notes | Electrical | Lighting, External | 1453.085 | Pass | Fail | -1 | 11 | 2022.25 | 2022-04-14 14:53 | 2022-04-26 17:00 | 2022-04-19 10:45 | 2022-04-26 17:00 | 2022-07-12 17:00 |  | WACCES | complete
MSA-DFES | WA5127444 | 3 | Protek 24/7 Building & Maintenance | Ground outside - Training pad wall - Damaged brick wall near training pad. Several bricks fallen | Building | General Building | 1525.25 | Pass | Fail | -1 | 11 | 2020.5 | 2022-02-14 13:02 | 2022-02-21 17:00 | 2022-02-15 07:30 | 2022-02-21 17:00 | 2022-05-10 12:00 |  | WACCES | Repair damaged brick wall
MSA-DFES | WA5585637 | 3 | Australian HVAC Services Pty. Ltd. | ground dorm 10-air con heat not working | Air Conditioning | Room Air Conditioners | 1769.16 | Pass | Fail | 0 | 12 | 2016 | 2022-07-06 06:50 | 2022-07-12 17:00 | 2022-07-11 13:00 | 2022-07-12 17:00 | 2022-10-03 13:00 |  | WACCES | Rhys Hall (03/10/2022) - Work NoteArrived on site and signed in etc.Located ac ac 2.9 and ac 2.10Isolated power and then proceeded to take off the facia of the ac and other components to access area needed.Replaced louver motors and indoor boards on both units.Re assembled both units then ran for testing, both working well.Packed up and cleaned area.
MSA-DTWD | WA6082389 | 3 | Equans Mechanical Services Australia | Level 2-splitting beans-Canteen display refrigerator not maintaining temperature | Refrigeration | Refrigerators | 129.51 | Pass | Fail | -1 | 11 | 2015.5667 | 2022-10-18 15:25 | 2022-10-25 17:00 | 2022-10-20 13:51 | 2022-10-25 17:00 | 2023-01-12 13:25 |  | WACCES | 20/10/2022: Found the tx valve sticking on the right hand display fridge, previously the system was topped up with gas and sealant put in. The sealant causes the tx valve to jam, parts on order .parts not available for this fridgeClosed job down
MSA-DFES | WA5597024 | 3 | AWB Co. | Engine Room - Asses and repair room ceiling | Building | Ceiling | 12408.46 | Fail | Fail | 0 | 12 | 1999.6167 | 2022-07-11 11:52 | 2022-07-18 17:00 | 2022-07-21 08:23 | 2022-07-18 17:00 | 2022-10-12 16:00 |  | WCAPPR | work completed as per quoted
MSA-DTWD | WA5400170 | 2 | AWB Co. | Leaking roof and sky light | Roofing | Rooflights and Skylights | 3282.3 | Pass | Fail | 0 | 12 | 1964.3167 | 2022-05-10 08:17 | 2022-05-13 17:00 | 2022-05-13 11:41 | 2022-05-13 17:00 | 2022-08-03 08:00 |  |  | Realigned section of tilesInstalled new flashings along wall and around skylightReplaced missing sarking under skylightRepointed ridge capping x 2 tilesPicked up tiles and delivered to site.Installed new roof tiles where missing from bottom row.
MSA-DTWD | WA6128403 | 1 | AWB Co. | Replace damage door to the canteen delivery entrance. | Building | Doors |  | Pass | Fail | 0 | 12 | 1949.4333 | 2022-10-26 15:56 | 2022-10-27 17:00 | 2022-10-27 07:00 | 2022-10-27 17:00 | 2023-01-16 12:26 |  |  | Works completed
MSA-DFES | WA5679223 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | L2-Two power sockets not working in Media and Corporate Communications-see notes | Electrical | General Electrical | 638.755 | Pass | Fail | -1 | 11 | 1947 | 2022-07-26 11:51 | 2022-08-02 17:00 | 2022-07-29 14:15 | 2022-08-02 17:00 | 2022-10-18 17:15 |  | WACCES | Jacob Prendergast (29/07/2022) - Work NoteArrived on site at 14:15 to investigate power points not working in public information area level 2, found that soft wiring has been disconnected and desks moved. We will need to return to install a new soft wiring point on will need to be installed and some wiring from point to desks. Left site at 14:30Sebastian Pino (04/08/2022) - Work NoteArrived on site at 1100. Left at 1130 and Picked up equipment for next job.Joel Harvey (10/10/2022) - Work NoteArrived on site at 11:15. Got measurements for duct lid to mount soft start onto. Will have to wait for parts to be ordered. Notified staff of works performed and left site at 12:00Will need a duct GPO mounting Kit with L- 125mm W- 150mm duct lid GPO mount plate in BLACK.Preferably need soft start to be black as well.Adam Back (18/10/2022) - Work NoteArrived onsite at 14:00 to install 1 x soft wiring socket outlet for connection of desktop outlets. Isolated power and wired in
MSA-DTAG | WA4990814 | 1 | Australian HVAC Services Pty. Ltd. | Courtside - All areas - Air con is not operating correctly - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 3381.185 | Pass | Fail | 0 | 11 | 1945.5 | 2022-01-04 12:01 | 2022-01-05 17:00 | 2022-01-04 12:30 | 2022-01-05 17:00 | 2022-03-26 14:00 |  | WACCES | Job number #40031Picked up fan motor and fan barrel for the job. Arrived on site and spoke to site representative about the works taking place. Gained access to the work area and accessed the Unit. Found the related switchboard for the unit and pulled out the fuse for the unit. Transported necessary equipment, tools and materials for the job into the work area. Started to dismantle the unit and remove the old fan motor + fan barrel. Once old fan barrel + motor had been removed, installed new fan motor and fan barrel assembly. Wired up the fan motor and reassemble the unit. Tested unit for operation by turning it on the BMS. After a period of operation, found that the unit seems to be operating correctly. Packed up and removed all debris from site.
MSA-DTWD | WA5312016 | 1 | AWB Co. | A52 - Water leaking down pipes into plant room from roof | Building | General Building | 3468.65 | Pass | Fail | 0 | 11 | 1939.5 | 2022-04-11 10:27 | 2022-04-12 17:00 | 2022-04-11 12:30 | 2022-04-12 17:00 | 2022-07-01 08:00 |  |  | Attended site and completed PFM roof access and JSA, found the leak and re sealed the Water chiller pipes, stopped the leak but slab still leaking due to poor water proofing and it being very old. Leak reported is fixed but Noel to follow up water proofing the slab.Bailey McKenzie (30/06/2022) - Work NoteReattended site with waterproofing membrane. Applied multiple coats to concrete slab. Cleaned and packed up site.
MSA-DTWD | WA6256820 | 1 | Australian Airconditioning Services Pty Ltd | Display Fridge keeps tripping again | Refrigeration | Refrigerators | 704.1 | Pass | Fail | 0 | 11 | 1922.25 | 2022-11-24 09:10 | 2022-11-25 17:00 | 2022-11-25 08:00 | 2022-11-25 17:00 | 2023-02-13 10:15 |  |  | Job complete
MSA-DFES | WA5053007 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Applied Training Ground - Tower 6 - Leak at valve and flanges at the base of tower 6 | Plumbing & Drainage | Water | 2754 | Pass | Fail | -1 | 10 | 1916.55 | 2022-01-18 11:53 | 2022-01-25 17:00 | 2022-01-18 13:57 | 2022-01-25 17:00 | 2022-04-08 10:30 |  | WACCES & WCAPPR | Located to look at a leak on fire line found the leak was coming from a weld on 100mm steel pipe will have to get a welder to do a quote to see if it can be fixed or will have to redo the hole thing.8/4/22Returned back to site with niche welding and redid the burst pipe work tested and working
MSA-DTWD | WA5414050 | 3 | AWB Co. | Room 2-13 - C-Bus light switch faulty | Electrical | General Electrical | 973.66 | Pass | Fail | 0 | 11 | 1894 | 2022-05-12 16:14 | 2022-05-19 17:00 | 2022-05-18 12:00 | 2022-05-19 17:00 | 2022-08-05 10:00 |  | WACCES | Attended site and signed in. Completed JSA. Located cbus control and switch. Downloaded current program on switch and saved. Replaced switch to room and reprogrammed. Tested to find lights staying on now permanently. Carried out testing to find that wiring has been altered wrongly to make lights all work together. Set up program for switching to work correctly. Lights turn on and off as 1. Advised site to get the issue fixed separately. Signed out. Job complete
MSA-DTAG | WA5792469 | 3 | Seme Solutions Pty Ltd | CCTV2 (21) Outside jury waiting PTZ Not working | Security | CCTV Surveillance | 6901.15 | Pass | Fail | -1 | 10 | 1893 | 2022-08-23 14:35 | 2022-08-30 17:00 | 2022-08-24 14:00 | 2022-08-30 17:00 | 2022-11-11 11:00 |  | WCAPPR | Reattended site, rectified existing PTZ camera operations on system.Only POE injector installed.
MSA-DTWD | WA5694252 | 3 | M Construction (WA) | ground-3B5 Hydraulics class room-Water leak South East corner | Roofing | Metal Roofing | 2082.48 | Pass | Fail | -1 | 11 | 1873 | 2022-08-05 08:46 | 2022-08-12 17:00 | 2022-08-08 11:00 | 2022-08-12 17:00 | 2022-10-25 12:00 |  | WCAPPR | Dekite Leaked and ingress through skylights. Seald Dektite and replaced x2 Roof Sheets
MSA-DTAG | WA6294334 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - Custody - Air flow in and around custody cell 7 is very poor | Air Conditioning | Materials | 5730.86 | Pass | Fail | -1 | 10 | 1871.9667 | 2022-11-30 14:51 | 2022-12-07 17:00 | 2022-11-30 15:00 | 2022-12-07 17:00 | 2023-02-16 14:58 |  | WACCES | Pick up new motor and lifter from workshop. Attend site. Access fire control room and carry isolation of level 4. Access level 4 and isolate exhaust fan. Disconnect electrical wiring. Modify mounting brackets and move from fan to ductwork. Unbolt mounting bolts and lower fan out of ceiling. Remove fan blade and wiring. Remove motor from mount platform. Install new motor and bolt into position. Fit fan blade and secure. Lift fan back ceiling and bolt inti position. Reseal joints. Connect electrical wiring and deisolate. Manual fan on and commission operation. Working ok. Clean exhaust grills in cells. Clean up area.
MSA-DTWD | WA5795618 | 1 | Protek 24/7 Building & Maintenance | Entrance door damaged/ split | Building | Doors | 1140.51 | Pass | Fail | 0 | 11 | 1853.5 | 2022-08-25 13:29 | 2022-08-26 17:00 | 2022-08-26 08:00 | 2022-08-26 17:00 | 2022-11-11 13:30 |  | WACCES | Replaced door, fitted digital lock and painted door
MSA-DTWD | WA5696794 | 2 | Precise Air Group | G102 heating not working | Air Conditioning | Room Air Conditioners | 456.08 | Pass | Fail | 0 | 11 | 1851.7 | 2022-08-08 14:40 | 2022-08-11 17:00 | 2022-08-09 11:23 | 2022-08-11 17:00 | 2022-10-25 15:05 |  |  | Unable to gain access into roof due to weatherAttended site, gained access to equipment, required apprentice for roof access, checked operations of condenser unit fou nd indoor board and fan motor has failed and required replacing. BRAF to be submitted.BRAF has been submitted, and are not proceeding with the works, job is to be closed off.
MSA-DTWD | WA5660665 | 3 | AWB Co. | Ground Floor - Main Carpark - Light pole has been hit buy car and leaning over | Electrical | Lighting, External | 2553.725 | Pass | Fail | -1 | 10 | 1851 | 2022-07-19 11:40 | 2022-07-26 17:00 | 2022-07-22 11:00 | 2022-07-26 17:00 | 2022-10-07 14:00 |  | WCAPPR | Attended site signed in jsa completed. Exposed rag bolts and put new washers to align pole. Reused two fittings as per sites request. One fitting works other one does not. Told site about this they said they will contact techworks to warranty job. Job completed
MSA-DTWD | WA5862091 | 3 | AWB Co. | multiple leaks in the classroom | Roofing | Metal Roofing | 8514.695 | Pass | Fail | -1 | 10 | 1850 | 2022-09-13 13:42 | 2022-09-20 17:00 | 2022-09-15 12:30 | 2022-09-20 17:00 | 2022-12-01 14:30 |  | WACCES | Stripped and resheeted section of roof as per approved BRAF
MSA-MRWA | WA5437963 | 2 | SONTEC WA PTY LTD | Camera 52 – Front Door Camera - Front Door Camera not clear / faulty | Security | CCTV Surveillance | 820 | Pass | Fail | 0 | 11 | 1845.1667 | 2022-05-16 11:49 | 2022-05-19 17:00 | 2022-05-16 14:20 | 2022-05-19 17:00 | 2022-08-01 11:30 |  |  | 16/5/22 - Dylan ParslowCamera 52 working currently.Image not clear due to age, requires replacement.BRAF submitted.1/8/22 - Dylan ParslowInstalled replacement camera.Tested all working.
MSA-DTWD | WA5673011 | 1 | BAKE-QUIP PTY LTD | D19 Baking Lab - Left hand deck on Hengel Prover isn’t working - water is leaking internally | Equipment | Catering Equipment | 1000 | Pass | Fail | 0 | 11 | 1842.5 | 2022-07-20 11:28 | 2022-07-21 17:00 | 2022-07-20 14:00 | 2022-07-21 17:00 | 2022-10-05 08:30 |  | WACCES | Refer to service report
MSA-DTWD | WA5696858 | 2 | AWB Co. | Roof Leak - Leaking onto AV control panel - right hand side of the white board | Roofing | Metal Roofing | 2440.315 | Fail | Fail | 0 | 11 | 1830.5167 | 2022-08-08 15:46 | 2022-08-11 17:00 | 2022-08-12 07:59 | 2022-08-11 17:00 | 2022-10-27 14:30 |  |  | works completedBRAF approval attached
MSA-DTWD | WA5571161 | 0 | Precise Air Group | Entire ground floor air cons not working - Making large banging sound on roof | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1869.32 | Pass | Fail | 0 | 11 | 1822 | 2022-06-29 09:22 | 2022-06-29 11:22 | 2022-06-29 10:00 | 2022-06-29 13:22 | 2022-09-13 08:00 |  |  | Attended site signed in and filled out nessesary paperwork. Gained access to the unit on m block. Assessed the mechanical components and traced wiring back to mssb. Foundvthst the issue is related to controls and will need a controls tech to attend to assess the system operation
MSA-DTWD | WA6044711 | 2 | BAKE-QUIP PTY LTD | Oven in the canteen kitchen is leaking water. | Electrical | General Electrical | 1153.45 | Fail | Fail | 2 | 13 | 1821.75 | 2022-10-17 10:46 | 2022-10-20 17:00 | 2022-11-04 11:00 | 2022-10-20 17:00 | 2023-01-19 08:45 |  | WACCES | Refer to service report
MSA-DFES | WA5513537 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Level - Various Lights needing replacement - See notes below | Electrical | Lighting, Internal | 749.305 | Pass | Fail | 0 | 11 | 1821 | 2022-06-14 11:16 | 2022-06-21 17:00 | 2022-06-21 15:00 | 2022-06-21 17:00 | 2022-09-05 12:00 |  | WACCES | Arrived on site at 1500 to replace fluorescent lighting around station. Located 1 x fluorescent globe in kitchen requiring replacement 1 x fluorescent globe in double dorm reading light requiring replacement 1 x fluorescent globe in Fire Station sign in front of building requiring replacement. Replaced 2 x fluros in kitchen and 1 x fluro in study area. Will need to return to site to replace fluros in double dorm reading and fire sign. Will also need to replace entire light fitting in rear office/study room as light contains faulty ballast/tombstone. Left site at 1715. Arrived on site at 0800 to replace remaining faulty fluros around station. Replaced/reenergised 1 x reading light, continued on site to replace fluros within station sign replaced 2 starters, 2 x fluros and 2 x ballasts. Informed staff of works and left site at 0930.Arrived onsite and signed in for 1130Located faulty light in kitchen. Replaced starters and fluro tubes.Informed staff of completed works and signed out
MSA-DTWD | WA5696841 | 2 | AWB Co. | Room G122 - East-water coming down internal wall | Roofing | Guttering | 1074.27 | Pass | Fail | 0 | 11 | 1818.0833 | 2022-08-08 15:19 | 2022-08-11 17:00 | 2022-08-09 15:25 | 2022-08-11 17:00 | 2022-10-24 09:30 |  | WACCES | 1. Strip and remove 4 x spandek roof sheets2. Supply and install new sheets to match existing with new fixings3. Remove waste from site
MSA-DTWD | WA5512114 | 2 | AWB Co. | Door frame Damaged and 2 of 3 hinges have come away from frame | Building | Doors | 3182.69 | Pass | Fail | 0 | 11 | 1808 | 2022-06-13 13:55 | 2022-06-16 17:00 | 2022-06-16 07:00 | 2022-06-16 17:00 | 2022-08-30 15:00 |  |  | works completed BRAF attached
MSA-DTWD | WA5385489 | 2 | Protek 24/7 Building & Maintenance | Block 7 - Cafetaria - investigate roof leak | Building | General Building | 2207.16 | Pass | Fail | 0 | 11 | 1804.5 | 2022-04-29 10:18 | 2022-05-04 17:00 | 2022-05-04 10:45 | 2022-05-04 17:00 | 2022-07-18 15:15 |  | WACCES | Replaced roof valley
MSA-DTWD | WA6255481 | 2 | Precise Air Group | chiller showing Cooler flow switch fault. This fault has been re set multiple times but keeps return | Air Conditioning | Room Air Conditioners | 956.32 | Pass | Fail | -1 | 10 | 1797.9667 | 2022-11-23 11:03 | 2022-11-28 17:00 | 2022-11-24 12:00 | 2022-11-28 17:00 | 2023-02-07 09:58 |  |  | Attended site with Justin to investigate why the chiller keeps shutting off with a flow fault. I have ran the chiller and tested the flow switch. Unit is operating correctly and the flow switch is complete fine. This would be more of a parameter issue with the BMS system that is causing this to fault. I have contacted BMS contractor to come out to site and check all the parameters. Completed same issue as WA6403048, should be closed off and works to continue on WA640304813/2/23 emailed update for todayHi Dave,Airvision are on site installing the new card and NRP should be with you in the next 30minutes.Kind regards
MSA-DTWD | WA5460480 | 1 | Precise Air Group | Chiller compound -chiller in alarm | Air Conditioning | Room Air Conditioners | 2713.31 | Pass | Fail | 0 | 11 | 1793.3333 | 2022-05-18 14:28 | 2022-05-19 17:00 | 2022-05-18 14:40 | 2022-05-19 17:00 | 2022-08-01 08:00 |  |  | Attended site and completed pre start paperwork and signed in. Acessed bms and inspected alarms. Found alarms on bms to have cleared. Acessed chiller plant and inspected chiller c alarm history. Found alarm "cooler flow switch alarm". Inspected pump operation and water flow and found all ok. Contacted nrp as I suspect it's a control fault. Nrp informed me that this is an ongoing issue that they are having Due to a demand/ load issue and that they have made recommendations. Chiller has no major faults. If issue gets worse suggest nrp attend to reprogram operation.
MSA-DCA | WA5392619 | 3 | Protek 24/7 Building & Maintenance | Maritime Conservation Workshop - Front Carpark - Roof Leak, right hand side corner - See notes | Roofing | Concrete Roof Construction | 2286.79 | Pass | Fail | -1 | 10 | 1778.25 | 2022-05-03 11:02 | 2022-05-10 17:00 | 2022-05-05 12:45 | 2022-05-10 17:00 | 2022-07-18 15:00 |  |  | repair leaking roof
MSA-DTAG | WA5189818 | 1 | AHS Services WA Pty Ltd (Anchor) | Roof membrane leaking | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 10 | 1777.65 | 2022-02-24 08:51 | 2022-02-25 17:00 | 2022-02-24 08:51 | 2022-02-25 17:00 | 2022-05-09 10:30 |  |  | Completed. Cancelled per Andrews request. Works have been completed and claimed under the following;?WA6824869?WA6824861
MSA-DTAG | WA5997837 | 1 | Sapio Pty Ltd | Sally port and car park gates interlock not working | Security | Keys & Access | 2990.35 | Pass | Fail | 0 | 10 | 1775.9167 | 2022-10-07 10:05 | 2022-10-10 17:00 | 2022-10-07 10:05 | 2022-10-10 17:00 | 2022-12-20 10:00 |  | WACCES | Work performed by Dirk Malan (20/12/2022):Work completed as per scope.Job completed.
MSA-DTWD | WA5715417 | 2 | BJ SYSTEMS | Repair damaged main reception door exit button | Security | Access Control | 2307.87 | Pass | Fail | 0 | 10 | 1774.5 | 2022-08-12 15:06 | 2022-08-17 17:00 | 2022-08-15 14:30 | 2022-08-17 17:00 | 2022-10-28 13:00 |  |  | Andrew Bradley (15/08/2022) - No fault with PTE button. New PTE button required for reception desk. No spare cables in area sealed ceilings, quote required Mark Power & Sean Gibbs (27/10/2022 & 28/10/2022) - Installation of additional exit button for admin main entry auto door under reception desk
MSA-DFES | WA5473514 | 2 | Protek 24/7 Building & Maintenance | Bay 1 and inside the stores area - Workshop - see details | Building | General Building | 1192.84 | Pass | Fail | 0 | 10 | 1772.75 | 2022-05-24 16:16 | 2022-05-27 17:00 | 2022-05-26 14:00 | 2022-05-27 17:00 | 2022-08-08 10:45 |  |  | Remove loose installation
MSA-DTWD | WA5693477 | 1 | M Construction (WA) | Store room - Investigate water dripping from ceiling and down wall -see notes | Building | Ceiling | 583.89 | Pass | Fail | 0 | 10 | 1755.1667 | 2022-08-04 12:43 | 2022-08-05 17:00 | 2022-08-05 11:45 | 2022-08-05 17:00 | 2022-10-17 14:55 |  | WACCES | Resealed perished silicon. Liquid sealed seam-2 coats
MSA-DTAG | WA5038288 | 1 | Midolo Building Services | Police hallway -custody entrance water leaking from the roof. Water still dripping off light fitting | Building | Ceiling | 1153.52 | Pass | Fail | 0 | 10 | 1754 | 2022-01-17 11:38 | 2022-01-18 17:00 | 2022-01-17 13:00 | 2022-01-18 17:00 | 2022-03-31 15:00 |  | WACCES | source of leak detected and sealed.
MSA-DCA | WA5295351 | 1 | Precise Air Group | PLANT ROOM - Various issues with AC plant, faults on BMS. Please investigate | Air Conditioning | Room Air Conditioners | 778.45 | Pass | Fail | 0 | 10 | 1753 | 2022-03-29 13:04 | 2022-03-30 17:00 | 2022-03-29 14:00 | 2022-03-30 17:00 | 2022-06-10 15:00 |  | WACCES | Ongoing issue with chiller 1 that is being monitored, found air compressor 1 contactor faulty and will need replacing.Replaced contractor on air pump 1
MSA-DTAG | WA5699473 | 1 | Australian HVAC Services Pty. Ltd. | Magistrates Wing - Airconditioning in Magistrates Wing is too cool. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2922.76 | Pass | Fail | 0 | 10 | 1734.5 | 2022-08-10 09:46 | 2022-08-11 17:00 | 2022-08-11 08:00 | 2022-08-11 17:00 | 2022-10-22 14:30 |  |  | Attend site. Access stairwell. Set up ladder and access ceiling space. Check operation of FCU 10. Drive valves and found 3 out of 4 valves working. Found fail valve to be heating water isolation valve. Test controls and found to be failed DC relay. Pick up new relay and install. Found actuator to start and work as normal. Access second stairwell and check FCU 11 test operation of actuators and found to work as normal.
MSA-DTWD | WA5583346 | 3 | Boilertronics | Boiler cuts out and restarts intermittently | Mechanical Services | Boilers | 2769.54 | Pass | Fail | -1 | 9 | 1734.2833 | 2022-07-04 11:56 | 2022-07-11 17:00 | 2022-07-05 06:46 | 2022-07-11 17:00 | 2022-09-15 13:03 |  |  | Change out Gas Valve & Test operation
MSA-DTAG | WA5494309 | 1 | Sapio Pty Ltd | Control Room - Cameras #92,93, 94, 95 located on Pole 1 have dropped out | Security | CCTV Surveillance | 3724.28 | Pass | Fail | 0 | 10 | 1733.5 | 2022-06-07 14:01 | 2022-06-08 17:00 | 2022-06-08 11:30 | 2022-06-08 17:00 | 2022-08-19 17:00 |  |  | 19/08/2022Technician attended site and tested fibre, Pole 1 has faulty fibre patch lead, replaced patch lead in basementcommunications rooms, cameras restored but intermittently dropping off, replaced SFP and cameras restored. Tested fibreson Pole 2, found no issues, replaced SFP and restored cameras. Check all cameras on IndigoVision system and confirmedall online and recording
MSA-DFES | WA5312018 | 0 | AWB Co. | Back of Station - Under cover truck port - panel is cracked and may fall (2.5 x 3.5) | Building | General Building | 1728.45 | Fail | Fail | 0 | 10 | 1728.75 | 2022-04-11 08:03 | 2022-04-11 10:03 | 2022-04-11 10:30 | 2022-04-11 12:03 | 2022-06-22 11:15 |  |  | Mason Burdon (11/04/2022) - Work NoteAttended site and completed roof access and JSA, inspected engine room veranda. Flashings on to the dampalon sheets were sealed but not water tight. EWP required as cannot walk along the polycarbonate roof sheets. Follow up soon.
MSA-DFES | WA5477964 | 2 | Protek 24/7 Building & Maintenance | Engine Room - 2x doors need repair, see notes below | Building | Doors | 1646.825 | Pass | Fail | 0 | 10 | 1724.75 | 2022-05-26 07:26 | 2022-05-30 17:00 | 2022-05-30 12:15 | 2022-05-30 17:00 | 2022-08-10 09:00 |  | WACCES | Remove and replace damaged doors including kick plates - paint and seals
MSA-DFES | WA5694834 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Outside & Inside Station - Lights not working - See notes below | Electrical | Lighting, Internal | 898.475 | Pass | Fail | 0 | 10 | 1723.25 | 2022-08-05 13:46 | 2022-08-10 17:00 | 2022-08-09 13:45 | 2022-08-10 17:00 | 2022-10-20 09:00 |  | WACCES | Arrived on site at 07:00 to investigate outside lights not working. Accessed roof with roof access kit and tested pe cell bringing on light above rear door, located switch for flood lights between roller doors and lights working. Checked all other security lights all working. Left site at 09:00No signature available as no one on site.
MSA-DTAG | WA5564424 | 3 | Australian HVAC Services Pty. Ltd. | Ground - Custody upstairs interview room - Square ceiling air vent has fallen away from the ceiling | Air Conditioning | Room Air Conditioners | 615.2 | Fail | Fail | 1 | 11 | 1711.5 | 2022-06-21 10:27 | 2022-06-28 17:00 | 2022-07-07 08:00 | 2022-06-28 17:00 | 2022-09-16 15:30 |  | WACCES | Attended service call, found diffuser for cushion head supplying interview room damaged & mounts in head broken. Checked with suppliers for replacement & found these no longer available. Sized parts & priced for replacement. Braf will be required Gary McAndrew (16/09/2022) - Work NotePicked up parts from suppliers, accessed site, replaced supply air outlet in interview room .
MSA-DTWD | WA5693334 | 2 | M Construction (WA) | Roof leak over metal guillotine | Roofing | Metal Roofing | 354.62 | Fail | Fail | 3 | 13 | 1704.5 | 2022-08-04 11:32 | 2022-08-09 17:00 | 2022-08-28 14:30 | 2022-08-09 17:00 | 2022-11-07 15:00 |  | WACCES & WCAPPR | Waterproofed upstand and fan hat over guillotine. Works Completed on 7 November
MSA-DTWD | WA5290601 | 1 | Dormakaba Australia Pty Ltd | Workshops carpentry section - the Bi Fold doors has a dislodged guide, loose pin in wheel | Building | Doors | 4605.76 | Fail | Fail | 8 | 18 | 1704 | 2022-03-25 09:56 | 2022-03-28 17:00 | 2022-05-25 13:00 | 2022-03-28 17:00 | 2022-08-04 13:00 |  |  | 25/3/22 - Door has twisted guide away from wall at both end, door is too large and will require 2 technicians and electrical technicians to strip door so faults can be rectifiedScissor lift is required4/8/22 - Strip down door for you so we could locate and rectify faults within the door faults were found ,guides have been modified and are now secure? .Door limits and parameters have been adjusted door has been tested and is working well
MSA-DTWD | WA6131991 | 3 | ACTION GLASS & ALUMINIUM | AMP Staff room - Cracked windows | Glazing | Window Glass | 3775.9084 | Pass | Fail | -1 | 9 | 1703.3333 | 2022-10-31 10:58 | 2022-11-07 17:00 | 2022-11-01 14:15 | 2022-11-07 17:00 | 2023-01-11 13:35 |  |  | ATTENDED SITE TO MEASURE & ASSESSRETURNED LATER DATE TO MEET WITH SCAFFOLDER TO GO OVER JOB REQUIREMENTSRETURNED LATER DATE WITH 4 MEN AND SCAFFOLD TO REGLAZE 2 ROOF PANELS6.38 TRANSLUCENT LAMINATED SAFETY GLASS1-1413 X 11691-1407 X 1169PLUS SILICONE
MSA-DTWD | WA5832373 | 1 | Precise Air Group | Main display fridge faulty - not cooling | Refrigeration | Refrigerators | 3267.04 | Pass | Fail | 0 | 10 | 1703.1 | 2022-09-05 12:35 | 2022-09-06 17:00 | 2022-09-05 14:00 | 2022-09-06 17:00 | 2022-11-15 13:06 |  |  | 15/11/2022 Completion of the Supply and Installation of a ReplacementEvaporator Coil to the FD1500 Display Cabinet at NorthMetropolitan TAFE as per approved quotation.
MSA-DCA | WA5569368 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Main Building - First Floor - Katies Office - Ramp Light Fuse tripped and fuse for upstairs area | Electrical | General Electrical | 535.45 | Pass | Fail | 0 | 10 | 1699.75 | 2022-06-27 13:50 | 2022-06-28 17:00 | 2022-06-27 16:00 | 2022-06-28 17:00 | 2022-09-06 11:45 |  | WACCES | Arrived on site at 1015 to replace 1 x faulty fluro batten. Installed new led batten, reenergised, Informed staff and left site at 1145.
MSA-DFES | WA5416748 | 2 | AWB Co. | Dorm 5 Bathroom - Water leaking from the roof through the lightfitting | Roofing | Metal Roofing | 740.59 | Pass | Fail | 0 | 10 | 1699 | 2022-05-13 08:09 | 2022-05-18 17:00 | 2022-05-16 14:00 | 2022-05-18 17:00 | 2022-07-26 09:00 |  | WACCES | Attended and investigated, requires BRAFFitted custom drypan flashings around extraction unit
MSA-DTWD | WA5472135 | 1 | Protek 24/7 Building & Maintenance | G200 - Roof Leak - See notes below | Roofing | Metal Roofing | 2762.61 | Pass | Fail | 0 | 10 | 1685.75 | 2022-05-23 14:38 | 2022-05-24 17:00 | 2022-05-24 07:00 | 2022-05-24 17:00 | 2022-08-02 12:45 |  | WACCES | Remove and replace damaged roof piping Remove and replace cupboard kickboards as required
MSA-DCA | WA5216552 | 1 | Precise Air Group | Cooling tower overflow leak - Leak is flowing out to the ground floor external fire escape | Air Conditioning | Room Air Conditioners | 4944.695 | Pass | Fail | 0 | 10 | 1679.5167 | 2022-03-11 11:08 | 2022-03-14 17:00 | 2022-03-11 13:44 | 2022-03-14 17:00 | 2022-05-20 13:15 |  | WACCES | Attended site, located water leak, adjusted water float valves on cooling towers? Due to water pressure float valves are sticking open. Required to replace valves and install new restriction valves to get to 250kpa water pressure
MSA-DTWD | WA5672900 | 1 | Protek 24/7 Building & Maintenance | K3 - Clear roof sheets are damaged causing rain water leak | Roofing | Metal Roofing | 1492.63 | Pass | Fail | 0 | 10 | 1678.75 | 2022-07-20 10:20 | 2022-07-21 17:00 | 2022-07-21 11:45 | 2022-07-21 17:00 | 2022-09-29 10:30 |  | WACCES | Replace 4 x skylight sheets to K Block shed
MSA-DTWD | WA5216800 | 1 | CLEVELAND COMPRESSED AIR SERVICES | H-Block - HG01 - Compressor has stopped working – power supply seems to be OK | Equipment | Compressors, Generators | 9154.1 | Pass | Fail | 0 | 10 | 1677.7333 | 2022-03-11 12:51 | 2022-03-14 17:00 | 2022-03-11 15:01 | 2022-03-14 17:00 | 2022-05-20 12:45 |  |  | Motor has failedClient requested quote to replace unit20/05/22 Installed new unit to site
MSA-DTWD | WA5686561 | 2 | AWB Co. | Car Park - Second Light pole fallen in car park - See notes below | Electrical | Lighting, External | 3697.465 | Pass | Fail | 0 | 10 | 1665.5 | 2022-08-01 09:21 | 2022-08-04 17:00 | 2022-08-03 06:00 | 2022-08-04 17:00 | 2022-10-11 15:30 |  |  | Attended site signed in jsa completed. Used quick cut saw to cut roadbase to expose pole bolts. Removed bumper stopper and put to side. removed old pole and put new one on. used blue metal as advised by nick mezzino to cover hole. Tested lights and confirmed operational. disposed of light poles. Job completed
MSA-DCA | WA6255876 | 2 | Protek 24/7 Building & Maintenance | External ground - Livingstones Cafe - Door is jamming - see notes | Building | Doors | 1419.38 | Pass | Fail | 0 | 9 | 1661.75 | 2022-11-23 14:50 | 2022-11-28 17:00 | 2022-11-25 07:15 | 2022-11-28 17:00 | 2023-02-02 13:00 |  | WACCES | Pop riveted the edge trims to 2 x doorsRe-fit door interlock to aluminum mullion style by using countersunk screws.Remove old door rollers from bottom of door and match replacement.
MSA-DTWD | WA6372987 | 1 | Precise Air Group | Canteen - Freezer not working Icing up | Refrigeration | Freezers | 2759.61 | Pass | Fail | 0 | 10 | 1661.5 | 2022-12-14 13:07 | 2022-12-15 17:00 | 2022-12-15 09:30 | 2022-12-15 17:00 | 2023-02-22 15:00 |  | WACCES | Attended 15/12/22 Tech unable to update PromapDefrost time clock and Klixon have failed, clock not available until 20/1/23, as soon as we have it we will attend and install. still awaiting parts due in by 10/2/23Parts have been delayed, confirmed to arrive 17/2/23 as soon as they arrive tech will be on site installing them, please note freezer room still in operation and working.15/2/23asked by Silvio to attend and defrost freezer, kitchen staff threatening to close the kitchen unless fixed. tech took 6 hours to defrost i have extended our BRAF hours and submitted.17/2/23 time clock has not been delivered yet, supplier chasing manufacturer for eta, no response as yet, will follow up again Monday.Supplier pushed back date for time clock to May 23, PAG have managed to source a timeclock from another supplier and canceled the other order. Will be installing time clock Wednesday 22/2/23Site FM Silvio 22/2/23 picked up new defrost clock and clipson heater switch ,travelled to s
MSA-DFES | WA5068940 | 1 | Australian HVAC Services Pty. Ltd. | Ground - LR 1 & 2 Administration - Air conditioning Control Unit in Lecture Room 1 & 2 constantly go | Air Conditioning | Building HVAC Maintenance (Major Plant) | 5019.76 | Pass | Fail | 0 | 10 | 1661.3667 | 2022-01-19 12:57 | 2022-01-20 17:00 | 2022-01-20 07:30 | 2022-01-20 17:00 | 2022-03-30 12:52 |  | WACCES | Temp units were installed and collected by supplier
MSA-DTWD | WA5514103 | 2 | Protek 24/7 Building & Maintenance | BG09 - Gutters on B-Block above BG09 have rusted & need replacing - see notes below | Roofing | Metal Roofing | 8368.03 | Pass | Fail | 0 | 10 | 1661 | 2022-06-14 16:06 | 2022-06-17 17:00 | 2022-06-16 07:00 | 2022-06-17 17:00 | 2022-08-24 12:00 |  | WACCES | • Receive portable scaffolding onsite and setup for access to roof• Remove and dispose of existing Box gutter full length of wall• Remove and dispose of Fascia Capping along Box Gutter• Remove and dispose of Top Barge capping from Roof into Box Gutter• Supply and Install New .55 Zinc Box Gutter and reconnect into existing Rain heads• Supply and Install New .55 C/B Shal Grey Fascia capping• Supply and Install New .55 Zinc Top Barge capping from Roof into Box Gutter
MSA-DTWD | WA5734910 | 3 | Ronley Holdings Pty Ltd | Outside N42 - Severe bearing noise in Dust extractor hopper | Electrical | General Electrical | 400 | Pass | Fail | -1 | 9 | 1656.5 | 2022-08-16 10:15 | 2022-08-23 17:00 | 2022-08-19 09:30 | 2022-08-23 17:00 | 2022-10-27 10:00 |  | WACCES | Disconnect electrics, remove fan motor assembly, transport motor to rewind company, strip and replace bearings and check windings. Transport back to site, reassemble fan and motor, reinstall, reconnect electrics, test run.
MSA-DFES | WA6376919 | 0 | Protek 24/7 Building & Maintenance | Hangar - flashing is damaged | Roofing | Metal Roofing | 1526.45 | Pass | Fail | 0 | 10 | 1655.5 | 2022-12-16 09:32 | 2022-12-16 11:32 | 2022-12-16 10:00 | 2022-12-16 13:32 | 2023-02-23 09:30 |  | WACCES | ? Installed temporary fixings to secure flashing back on wall? Carried out site measure to confirm materials required? Attend site, sign in & establish work zone? Setup scissor lift within work zone? Remove and dispose of damaged shed flashing? Supply and install new shed flashing to match existing? Clean site & Demobilise
MSA-DTWD | WA5397285 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire sensors and speakers not working - see notes below | Fire Protection Services | Fire Protection - Monitor System | 2179.845 | Pass | Fail | 0 | 10 | 1655.4167 | 2022-05-06 14:29 | 2022-05-11 17:00 | 2022-05-10 13:45 | 2022-05-11 17:00 | 2022-07-18 13:10 |  | WACCES | 10/5/22 - Our technician has attended however requires more time on site, please can you extend the completion date? Regards.23/05/2022-TECHNICIAN HAS RE-ATTENDED AND HAS SYSTEM WORKING HOWEVER 1 SPEAKER NEEDS TO BE REPLACED-TO BE ORDERED24/06/2022 SPEAKER NOW IN STOCK TO BE COMPLETED 24/06/2022-BEN COWDRAY/BEAU WYLLIE28/06/2022 FURTHER WOK STILL REQUIREDTO COMPLETE-BRAF TO BE SUBMITTED04/07/2022-BRAF TO BE SUBMITTED05/07/2022-braf emailed and attached
MSA-DTWD | WA5413410 | 1 | Protek 24/7 Building & Maintenance | E34 Loading Dock/Laundry Passage -Roof leak near light fitting | Building | General Building | 3178.98 | Pass | Fail | 0 | 10 | 1653.25 | 2022-05-12 10:50 | 2022-05-13 17:00 | 2022-05-12 12:45 | 2022-05-13 17:00 | 2022-07-20 10:00 |  | WACCES | repair leaking roof
MSA-DTAG | WA5142550 | 2 | AWB Co. | Replace light switch in Staff Café as top light switch has broken off and not safe for staff to tu | Electrical | General Electrical | 677.52 | Pass | Fail | -1 | 9 | 1651 | 2022-02-16 15:09 | 2022-02-21 17:00 | 2022-02-17 14:30 | 2022-02-21 17:00 | 2022-04-27 09:30 |  | WACCES | Attended site and signed in, completed jsa, spoke with client about job, located switch, replaced switch, tested switch and it is working as intended, cleaned up,packed up, completed paperwork,signed out , job completed
MSA-DTAG | WA5053028 | 2 | Sapio Pty Ltd | Ground Floor - Camera C008 Gnd Hay St PTZ (172.21.254.202) has lost server connection | Security | CCTV Surveillance | 3339.05 | Pass | Fail | 0 | 9 | 1640.5 | 2022-01-18 12:14 | 2022-01-21 17:00 | 2022-01-19 08:00 | 2022-01-21 17:00 | 2022-03-28 16:30 |  |  | Replaced PTZ and reconfigured to Milestone.
MSA-DFES | WA5201112 | 1 | AWB Co. | Tunic Room - roof leak | Roofing | Metal Roofing | 6328.31 | Pass | Fail | 0 | 10 | 1631.5 | 2022-03-02 11:40 | 2022-03-03 17:00 | 2022-03-02 12:45 | 2022-03-03 17:00 | 2022-05-09 12:15 |  |  | Attended and investigated cause of leak, sealed box gutter joins, will need return to apply box gutter sealer. Once worksare completed a chippie and electrician to attend to complete repairs to ceiling.Prepped and applied waterproof membrane to boxgutter
MSA-DTWD | WA6130608 | 2 | M Construction (WA) | Stores Area - Replace broken wall tiles in store area | Building | Internal Walls | 467.7372 | Pass | Fail | 0 | 10 | 1630 | 2022-10-28 13:18 | 2022-11-02 17:00 | 2022-11-02 11:00 | 2022-11-02 17:00 | 2023-01-09 09:00 |  | WCAPPR | Removed Broken wall tiles and installed new tiles from store room
MSA-DTWD | WA5471580 | 2 | Protek 24/7 Building & Maintenance | C2 Café Dining - Roof Leak - see notes | Roofing | Metal Roofing | 2259.77 | Pass | Fail | 0 | 10 | 1629.25 | 2022-05-23 13:05 | 2022-05-26 17:00 | 2022-05-26 13:15 | 2022-05-26 17:00 | 2022-08-02 10:30 |  | WACCES | Repair Roof leak
MSA-DFES | WA5200941 | 1 | Protek 24/7 Building & Maintenance | Exhibition area - leaking ceiling | Building | Ceiling | 1959.735 | Pass | Fail | 0 | 10 | 1608.25 | 2022-03-02 10:30 | 2022-03-03 17:00 | 2022-03-03 10:00 | 2022-03-03 17:00 | 2022-05-09 10:15 |  | WACCES | Repair leaking ceiling
MSA-DTWD | WA5978927 | 1 | Precise Air Group | faulty analog temp Gurage to freezer | Refrigeration | Freezers | 2448.02 | Fail | Fail | 7 | 17 | 1608.1 | 2022-09-28 14:15 | 2022-09-29 17:00 | 2022-11-17 08:33 | 2022-09-29 17:00 | 2023-01-23 08:39 |  | WACCES | Picked up new digital thermometer,cut out existing electrical box to install,pulled out old thermocouple and replaced calibrated controller and checked operation all good .
MSA-DTWD | WA5301837 | 3 | Protek 24/7 Building & Maintenance | Ground - B Block - walkway skylight section 1, 2 & 4 damaged / replacement/repair required | Roofing | Rooflights and Skylights | 2345.27 | Pass | Fail | -1 | 9 | 1606 | 2022-04-01 13:07 | 2022-04-08 17:00 | 2022-04-04 11:30 | 2022-04-08 17:00 | 2022-06-10 09:30 |  | WACCES & WCAPPR | Replace Damaged skylight
MSA-DTWD | WA5238850 | 1 | Equans Mechanical Services Australia | Air con in fault and not cooling room | Air Conditioning | Room Air Conditioners | 2984.27 | Pass | Fail | 0 | 9 | 1605.5 | 2022-03-16 09:36 | 2022-03-17 17:00 | 2022-03-16 13:30 | 2022-03-17 17:00 | 2022-05-22 11:00 |  |  | Arrived on site signed in, rechecked operation all ok. Checked individual rooms, found lunchroom temp at 16 degrees, phoned Dennis had temp reset from BMS. Returned equipment to supplier, cleaned up work area completed paperwork.
MSA-DFES | WA5795479 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Roof exhaust fan in engine room has noisy belt drive | Electrical | General Electrical | 231.2 | Pass | Fail | 0 | 9 | 1604.25 | 2022-08-25 12:42 | 2022-08-30 17:00 | 2022-08-29 14:00 | 2022-08-30 17:00 | 2022-11-04 10:15 |  | WCAPPR | Tasz Cumming (04/11/2022) - Work NoteArrived on site and spoke to staffLocated fan controls and roof access pointIsolated fanApplied lubricant to both fan belt and spindleTested for operation .
MSA-DTWD | WA5689818 | 2 | Protek 24/7 Building & Maintenance | ground - Roof leak in northwest corner of room | Roofing | Metal Roofing | 1132.06 | Pass | Fail | 0 | 9 | 1584.25 | 2022-08-02 14:02 | 2022-08-05 17:00 | 2022-08-05 11:15 | 2022-08-05 17:00 | 2022-10-10 11:30 |  | WACCES | remove and replace damaged skylight
MSA-DFES | WA5307133 | 3 | Protek 24/7 Building & Maintenance | Main Administration - Ground - Administration Building LR7 & 6 - see details below | Building | General Building | 866.8 | Pass | Fail | 0 | 9 | 1583.5 | 2022-04-07 10:25 | 2022-04-14 17:00 | 2022-04-12 09:00 | 2022-04-14 17:00 | 2022-06-17 08:30 |  | WACCES | Repair crack to wall in Admin building LR7 & 6
MSA-DFES | WA5988355 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Applied training ground - Near briefing room transportable - 2 x spotlights not working | Electrical | Lighting, External | 2366.3775 | Pass | Fail | 0 | 9 | 1578 | 2022-10-04 08:37 | 2022-10-07 17:00 | 2022-10-04 14:00 | 2022-10-07 17:00 | 2022-12-09 08:00 |  | WACCES | Joel Harvey (04/10/2022) - Work NoteArrived on site and signed in at 14:00pm to investigate faulty spot lights on light pole #2 and found there to be 1x light out and 1x isolation switch is faulty too as it goes further than the ON position. Will need to return with EWP (recommend boom lift) to change the globe. Notified staff and left site atUnable to test ballast functionality due to it being too deep inside light pole to test for correct voltages. If problem persists the lights will have to be retrofit with LEDs to allow the whole circuit to be accessible in the future.Light pole is 15m high and will need an EWP to change the globe. I have recommended we do both light globes whilst up there so that the other globe doesn’t blow in the upcoming months.Materials needed:- 1x 20A Clipsal isolation switch- 2x 1500W Sylvania brite line metal halide lampsMatthew Kenney (31/10/2022) - Work NoteContinued onsite at 8:20 to investigate faulty spot lights on pole #2. Was not able
MSA-DTWD | WA5715394 | 2 | AWB Co. | LSK ceiling leaks from the roof light near the passageway | Building | Ceiling | 2880.84 | Pass | Fail | 0 | 9 | 1565.2333 | 2022-08-12 14:47 | 2022-08-17 17:00 | 2022-08-15 09:01 | 2022-08-17 17:00 | 2022-10-19 14:15 |  | WACCES | Installed flashing system to the rear large evap system. Job complete
MSA-DTWD | WA5674131 | 2 | Protek 24/7 Building & Maintenance | Roof leak in rooms A008/A009 | Building | Ceiling | 4279.245 | Pass | Fail | 0 | 9 | 1565 | 2022-07-21 09:07 | 2022-07-26 17:00 | 2022-07-25 08:00 | 2022-07-26 17:00 | 2022-09-28 13:00 |  | WCAPPR | Patch walls with top coat, sand and paint both damaged walls 2 x coats of matched paint, re enstate furniture, clean up site
MSA-DTWD | WA5513696 | 1 | Protek 24/7 Building & Maintenance | Roof leak along western wall - Box gutter is possible source of leak | Roofing | Metal Roofing | 8167.565 | Pass | Fail | 0 | 9 | 1563.75 | 2022-06-14 12:33 | 2022-06-15 17:00 | 2022-06-15 08:30 | 2022-06-15 17:00 | 2022-08-19 12:15 |  | WACCES | Remove and dispose of damaged box gutter & sumpsClean up roof and install new roof plumbingSupply and install new box gutters & sumps onsite (Roughly 32m of Box gutter & 4 sumps)
MSA-DTWD | WA5306200 | 1 | Dormakaba Australia Pty Ltd | Block 2 - 2G19 - Roller door to workshop wont open | Building | Roller Shutters | 2670 | Pass | Fail | 0 | 9 | 1561.9333 | 2022-04-06 10:56 | 2022-04-07 17:00 | 2022-04-06 13:09 | 2022-04-07 17:00 | 2022-06-10 15:05 |  |  | 6/4/22 - Assessed door and found motor has been tagged out by customer due to limits been lost, motor is beyond repair due to age and requires new motor, applied manual haul so customer can open and close doorPlease quote for new 3 phase motor R/h10/6/22 - Completed works as per quote. Tested all good. Please quote to instal a pb008 safety beam as the nature of the room it’s more practical to press the down button and walk out than to use double bolted doors which will require keys to secure at night.
MSA-DTWD | WA5127175 | 3 | Protek 24/7 Building & Maintenance | Walkway between Buildings 4 & 5 - Floor tiles broken | Flooring | Tiling | 2192.75 | Pass | Fail | -1 | 9 | 1561.5 | 2022-02-14 11:29 | 2022-02-21 17:00 | 2022-02-16 10:30 | 2022-02-21 17:00 | 2022-04-22 12:00 |  | WACCES | Repair broken Floor tiles
MSA-DTAG | WA5176945 | 3 | Australian HVAC Services Pty. Ltd. | Level 6 - Plant Room - Power to Chiller 3 has tripped | Refrigeration | Chiller | 17992.48 | Pass | Fail | -1 | 8 | 1561.5 | 2022-02-21 14:45 | 2022-02-28 17:00 | 2022-02-21 15:00 | 2022-02-28 17:00 | 2022-04-27 16:30 |  |  | Attend site with new coated chiller ends. Install new anodes and gaskets to ends. Install ends and tighten up. Reconnect pipework and sensors. Deisolate water valves and check for leaks. Deisolate all water valves and water pump. Deisolate chiller and test operation, working as normal.
MSA-DCA | WA5687314 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Plant room - Isolate AHU’s to gallaries 2,3,4 to avoid humidity alarms - See notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 371.62 | Pass | Fail | 0 | 9 | 1560 | 2022-08-01 15:32 | 2022-08-02 17:00 | 2022-08-02 08:00 | 2022-08-02 17:00 | 2022-10-06 08:00 |  | WACCES | Works completed in centenary gallery. Reinstated humidifiers and fcus. Completed paperwork.
MSA-DTWD | WA5396040 | 3 | Equans Mechanical Services Australia | Room D113 - Jewelry Workshop - Compressed Air leak from regulator | Equipment | Compressors, Generators | 419.15 | Pass | Fail | -1 | 8 | 1558.5 | 2022-05-06 07:58 | 2022-05-12 17:00 | 2022-05-06 11:30 | 2022-05-12 17:00 | 2022-07-10 10:00 |  |  | PARTS REPLACED AS PER INVOICE
MSA-DTWD | WA5479943 | 1 | BAKE-QUIP PTY LTD | E58 Large Scale Kitchen - Combi Oven is leaking water again - see details below | Equipment | Catering Equipment | 1580.1 | Pass | Fail | 0 | 9 | 1557.25 | 2022-05-27 13:24 | 2022-05-30 17:00 | 2022-05-30 11:45 | 2022-05-30 17:00 | 2022-08-03 09:00 |  | WACCES | REFER TO SERVICE REPORT.
MSA-DTAG | WA5395396 | 1 | Midolo Building Services | Perth Children’s Court - Basement - Cell 2 & 6 - Custody - please check details below | Building | General Building | 3651.96 | Pass | Fail | 0 | 9 | 1541.75 | 2022-05-05 12:44 | 2022-05-06 17:00 | 2022-05-06 07:00 | 2022-05-06 17:00 | 2022-07-09 12:45 |  | WACCES | WALL PATCHED & PAINTED- SEE PHOTOS ATTACHED OF WORKS COMPLETED
MSA-DTWD | WA5478736 | 3 | AWB Co. | gutter that runs along the roof of the work shop (3B36) two classrooms come off 3B36 - see details | Building | General Building | 3278.895 | Pass | Fail | 0 | 9 | 1540.75 | 2022-05-26 13:21 | 2022-06-02 17:00 | 2022-06-02 10:00 | 2022-06-02 17:00 | 2022-08-05 14:45 |  | WACCES | Cut back roof sheets on the upper roof approximately 24 linear metresEnsured all sheet end tuned up on new roof sheetsSupplied and install new crank line flashing to match new lower roof sheet colour (Basalt)Supplied all fixings and accessories required for installationRemoved all waste from site on completion of work
MSA-DFES | WA5562632 | 2 | Protek 24/7 Building & Maintenance | Applied training donga - between table and training officers desk - roof leak | Roofing | Tiled Roofing | 1478.4 | Pass | Fail | 0 | 9 | 1538 | 2022-06-20 08:43 | 2022-06-23 17:00 | 2022-06-21 09:30 | 2022-06-23 17:00 | 2022-08-24 11:30 |  | WACCES | ? Temporarily remove top ridge corner flashing? Clear away all old silicone and foam seals? Bend up ends of sheets, Install new foam and reinstate flashings? Undo all sheet laps to lower end of roof and cut away underlap to stop capillary action? Water test once works completed to confirm roof is watertight
MSA-DTWD | WA6361328 | 2 | Protek 24/7 Building & Maintenance | Roof leak - water ingress near window | Roofing | Tiled Roofing | 1962.65 | Pass | Fail | 0 | 9 | 1538 | 2022-12-08 09:05 | 2022-12-13 17:00 | 2022-12-12 11:30 | 2022-12-13 17:00 | 2023-02-14 13:30 |  | WACCES | Install new rain heads on gblock (Southside)
MSA-DTWD | WA5098635 | 3 | AWB Co. | replace sound proofing a(coustic panels) as faulty/ falling apart - see notes | Building | Internal Walls | 8322.5 | Pass | Fail | -1 | 8 | 1537 | 2022-02-01 10:25 | 2022-02-08 17:00 | 2022-02-01 13:00 | 2022-02-08 17:00 | 2022-04-06 14:00 |  | WACCES | Completed installation of acoustic panels to two rooms as per BRAF
MSA-DTWD | WA5887719 | 3 | AWB Co. | Level 3 - Roof ( Alfresco ) - L3 Roof ( Alfresco ) shade netting storm damaged | Building | General Building | 3034.205 | Pass | Fail | 0 | 9 | 1536.5 | 2022-09-16 09:28 | 2022-09-23 17:00 | 2022-09-20 12:15 | 2022-09-23 17:00 | 2022-11-23 12:45 |  |  | Repair of the shade structure SS wire and discs
MSA-DFES | WA5239171 | 2 | Protek 24/7 Building & Maintenance | Please see details below - | Building | General Building | 2398.59 | Pass | Fail | -1 | 9 | 1536.25 | 2022-03-16 10:19 | 2022-03-21 17:00 | 2022-03-17 12:45 | 2022-03-21 17:00 | 2022-05-20 13:00 |  | WACCES | Remove and replace old, damaged door
MSA-DCA | WA5473378 | 1 | EQUANS Mechanical Services (WA) Pty Limited | AC9 Alarms for AC9 not clearing. Temperature much too low – refer to photos | Air Conditioning | Room Air Conditioners | 240.7 | Pass | Fail | 0 | 9 | 1536.1833 | 2022-05-24 14:24 | 2022-05-25 17:00 | 2022-05-25 08:00 | 2022-05-25 17:00 | 2022-07-28 08:11 |  |  | Attended site, signed in and accessed
MSA-DTWD | WA6364161 | 1 | AWB Co. | External - Driveway Southside - damaged retaining wall | Building | External Walls |  | Pass | Fail | 0 | 9 | 1536.15 | 2022-12-12 09:53 | 2022-12-13 17:00 | 2022-12-12 13:45 | 2022-12-13 17:00 | 2023-02-14 13:54 |  |  | Works completed
MSA-DTAG | WA5682686 | 2 | Midolo Building Services | ground-1. Door stop is broken near Courts 3 & 4. - 2. Tiles on corner of wall -see notes | Building | Internal Walls | 498.18 | Pass | Fail | 0 | 9 | 1535 | 2022-07-29 10:56 | 2022-08-03 17:00 | 2022-08-02 12:30 | 2022-08-03 17:00 | 2022-10-05 11:30 |  | WACCES | DOOR STOP REPLACED - CORNER WALL RENDERED AS TILES COULD NOT BE SOURCED
MSA-DTWD | WA5098966 | 3 | NEYLOR | Level 2 - B251 -Repair broken curtains | Building | Curtains & Blinds | 140 | Fail | Fail | 6 | 15 | 1534.55 | 2022-02-01 12:52 | 2022-02-08 17:00 | 2022-03-21 14:15 | 2022-02-08 17:00 | 2022-05-24 12:48 |  |  | Completed & invoiced
MSA-DTWD | WA5099141 | 2 | BAKE-QUIP PTY LTD | Deep fryer not working | Equipment | Catering Equipment | 2184.2 | Fail | Fail | 0 | 10 | 1531.75 | 2022-02-01 15:05 | 2022-02-04 17:00 | 2022-02-07 14:45 | 2022-02-04 17:00 | 2022-04-12 10:30 |  | WCAPPR | REFER TO SERVICE REPORT.
MSA-DTWD | WA5216829 | 2 | Precise Air Group | L block - room L101 - spilt system AC only blowing warm air | Air Conditioning | Room Air Conditioners | 2208.1 | Pass | Fail | 0 | 9 | 1520.0333 | 2022-03-11 13:12 | 2022-03-16 17:00 | 2022-03-14 07:30 | 2022-03-16 17:00 | 2022-05-16 15:32 |  |  | Attended site and completed pre start paperwork and signed in. Accessed unit in classroom set up work equipment and inspected flare. Repaired flare and accessed condenser, pressure tested system and checked for any further leaks. Once satisfied released nitrogen and placed system on evacuation. Evacuated unit to 500microns. Charged system with 3.7kg of 410a. Test ran/commisoned unit. Found system to start an run with out fault. Checked air on and off and found all ok. Packed up work equipment and completed paperwork. Left all ok.
MSA-DTWD | WA5676717 | 3 | AWB Co. | Level 2 men’s toilet rain damaged ceiling - repair patch and paint | Building | Ceiling | 1973.42 | Fail | Fail | 11 | 20 | 1520 | 2022-07-25 10:14 | 2022-08-01 17:00 | 2022-10-20 07:00 | 2022-08-01 17:00 | 2022-12-22 15:00 |  |  | works completedBRAF approval attached
MSA-DTWD | WA5188339 | 3 | Protek 24/7 Building & Maintenance | G block - roof - inspect the roof for any holes or penetrations where animals are accessing (possums | Building | Ceiling | 3466.555 | Pass | Fail | 0 | 9 | 1519.25 | 2022-02-23 08:19 | 2022-03-02 17:00 | 2022-03-02 07:00 | 2022-03-02 17:00 | 2022-05-04 14:15 |  | WACCES | repair roof following damage caused by possums entering
MSA-DCA | WA5438495 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Main Museum - Ground floor - Visitor Services Supervisors Office - see details below | Air Conditioning | Room Air Conditioners | 293.025 | Pass | Fail | 0 | 9 | 1515.2667 | 2022-05-16 14:41 | 2022-05-19 17:00 | 2022-05-19 12:04 | 2022-05-19 17:00 | 2022-07-21 15:20 |  | WCAPPR | Works completed. Quote submitted to PFM for equipment replacement. Ref. WA5569112
MSA-DTWD | WA6292783 | 3 | AWB Co. | West End - Visitor Carpark - Fault with carpark lighting – Continually trips break | Electrical | Lighting, External | 3322.52 | Pass | Fail | -1 | 8 | 1515 | 2022-11-29 13:08 | 2022-12-06 17:00 | 2022-12-02 09:00 | 2022-12-06 17:00 | 2023-02-03 12:00 |  | WCAPPR | Attended site signed in jsa complete. Replaced pole head in West Carpark. Ran cable from restaurant bunker light to bollard at front of restaurant. Powered up. Tested operational. x4 bollards working. x2 streetlights working.Job complete
MSA-DTWD | WA5481637 | 2 | BAKE-QUIP PTY LTD | E-Block - restaurant kitchen - the blast chiller, faulty cord on the probe | Equipment | Catering Equipment | 1837 | Pass | Fail | 0 | 9 | 1514.75 | 2022-05-30 15:17 | 2022-06-02 17:00 | 2022-05-31 14:45 | 2022-06-02 17:00 | 2022-08-02 17:30 |  | WACCES | Refer to service report
MSA-DTWD | WA5698076 | 2 | AWB Co. | Exit door - . East end ground floor exit door major leak from ceiling/roof | Roofing | Metal Roofing | 2282.37 | Pass | Fail | 0 | 9 | 1513.75 | 2022-08-09 14:19 | 2022-08-12 17:00 | 2022-08-12 13:00 | 2022-08-12 17:00 | 2022-10-14 14:45 |  |  | Removed large double storey downpipe from cavity and replaced in PVC. Job complete
MSA-DTWD | WA5682666 | 1 | SENTINEL LOCK SERVICE PTY LTD | 10G69-Faulty pin pad to computer room | Security | Locksmith | 975.24 | Pass | Fail | 0 | 9 | 1511.8333 | 2022-07-29 10:46 | 2022-08-01 17:00 | 2022-07-29 12:25 | 2022-08-01 17:00 | 2022-09-30 12:15 |  | WACCES | 10G69 - Faulty pin pad lock to computer room.Lock and keypad replaced.
MSA-DFES | WA5462462 | 1 | Seme Solutions Pty Ltd | Main Entrance Door - automatic night/day mode activation on card swipe is not working | Security | Access Control | 292.5 | Pass | Fail | 0 | 9 | 1510.6833 | 2022-05-19 15:15 | 2022-05-20 17:00 | 2022-05-20 12:34 | 2022-05-20 17:00 | 2022-07-22 11:15 |  |  | Job not complete, needs further investigation from workstation at Cockburn
MSA-DCA | WA4992584 | 1 | ADVANCED LOCK & KEY | Epoch Café, Terrace - Café terrace door GF_080 hardware has failed, see notes | Building | Doors | 413.35 | Pass | Fail | 0 | 9 | 1508.25 | 2022-01-06 13:51 | 2022-01-07 17:00 | 2022-01-07 15:15 | 2022-01-07 17:00 | 2022-03-11 11:30 |  | WACCES | Require black 590 escape handles. Currently on order from 10/1/22Takes 3 weeks for stock to come in. Replaced broken escape lever on cafe 590 with new SP3540-L1PC 11/3/22
MSA-DTWD | WA5460456 | 3 | Equans Mechanical Services Australia | Student Services - Ticking from ceiling / Air con actuator | Air Conditioning | Building HVAC Maintenance (Major Plant) | 690.54 | Pass | Fail | -1 | 8 | 1506.75 | 2022-05-18 14:19 | 2022-05-25 17:00 | 2022-05-18 14:45 | 2022-05-25 17:00 | 2022-07-20 09:30 |  | WACCES | Found damper actuator in ceiling is faulty. Located suppliers and ordered parts. Travelled to suppliers and picked up parts. Returned to site and gained access to unit in ceiling. Found suppliers supplied similar part but wiring is different. Ordered and picked up correct part. Returned to site. Gained access to site. Replaced faulty damper actuator and wired accordingly. Checked operation. All ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5828461 | 3 | AWB Co. | Verandah paint bubbled and peeling | Painting | External | 5165.46 | Pass | Fail | 0 | 9 | 1495 | 2022-09-02 08:32 | 2022-09-09 17:00 | 2022-09-09 07:00 | 2022-09-09 17:00 | 2022-11-10 14:00 |  |  | painting works completed
MSA-DCA | WA5879810 | 0 | Protek 24/7 Building & Maintenance | Light above internal entrance door dripping - electrician has made safe for work | Roofing | Tiled Roofing | 2940.93 | Pass | Fail | 0 | 9 | 1489.5 | 2022-09-15 09:18 | 2022-09-15 11:18 | 2022-09-15 11:00 | 2022-09-15 13:18 | 2022-11-16 12:30 |  | WACCES | ? Electrician to attend site, disconnect light fitting and internet modem and remove. Reinstate once works complete? Install zip walls and drops sheets to area for duration of works? Remove and dispose of damaged ceiling sheet & any fixings present? Supply and install new ceiling sheets and make flush? Undercoat and paint ceiling once dry to suit 'ceiling white' colour
MSA-DTWD | WA5413676 | 3 | Protek 24/7 Building & Maintenance | Block 7 - Ground - Staff toilet in kitchen - Water leak from exhaust fan in kitchen staff toilet | Building | General Building | 1666.81 | Pass | Fail | -1 | 8 | 1468 | 2022-05-12 12:50 | 2022-05-19 17:00 | 2022-05-13 10:00 | 2022-05-19 17:00 | 2022-07-13 14:00 |  | WACCES | Install new dry pans
MSA-DTWD | WA5827474 | 3 | Equans Mechanical Services Australia | Room N114 - Chiller 3 interlock fault | Refrigeration | Chiller | 776.42 | Pass | Fail | -1 | 8 | 1466.3667 | 2022-09-01 10:33 | 2022-09-08 17:00 | 2022-09-01 10:57 | 2022-09-08 17:00 | 2022-11-01 13:19 |  |  | SEE REPORT
MSA-DTWD | WA6253659 | 2 | M Construction (WA) | The ceiling in E40 has been damaged - see notes | Building | Ceiling | 1629.34 | Pass | Fail | 0 | 9 | 1466 | 2022-11-22 11:10 | 2022-11-25 17:00 | 2022-11-25 08:30 | 2022-11-25 17:00 | 2023-01-25 10:30 |  |  | First Attendance:1. Removed damaged area of ceiling.2. Discovered structural issue in ceiling space. Informed school and PFM of the issue and advised structural issue would need ot be resolved before ceiling could be repaired. School stated they would engage a structural engineer and let me know when the ceiling would be ready to be repaired.3. Removed debris and cleaned up area.Second Attendance (two Tradesmen):1. Fit ceiling supports2. Re-fixed gyprock ceiling3. Sanded and painted ceiling to match existing color.
MSA-DTWD | WA5001498 | 2 | AWB Co. | light constantly on | Electrical | Lighting, Internal | 919.275 | Pass | Fail | 0 | 9 | 1465.75 | 2022-01-11 12:55 | 2022-01-14 17:00 | 2022-01-14 13:45 | 2022-01-14 17:00 | 2022-03-16 15:30 |  | WACCES | Attended site and signed in. Completed JSA. Located faulty lights in toilets. Met with program guy to download all info. Assisted in setting and re programming the controls. Set to 25 mins as per rest of site. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4993483 | 3 | ACTION GLASS & ALUMINIUM | Window Broken to D106 | Glazing | Window Glass | 1327.49 | Pass | Fail | 0 | 8 | 1465.4167 | 2022-01-07 14:59 | 2022-01-14 17:00 | 2022-01-12 10:35 | 2022-01-14 17:00 | 2022-03-14 12:00 |  |  | ATTENDED SITE TO MEASURE & ASSESSCLEANED UP BROKEN TOUGHENED GLASS AND TEMP GLAZED BROKEN DOUBLE GLAZED UNIT6.38 CLEAR LAMINATED SAFETY GLASS1-665 X 2070RETURNED LATER DATE TO SUPPLY & INSTALL NEW DOUBLE GLAZED UNIT6MM EVANTAGE SUPERGREEN TOUGHENED / 12MM BLACK SPACER / 6MM CLEAR TOUGHENED SAFETY GLASS1-665 X 20702 MEN REQUIRED
MSA-DFES | WA5109617 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | multiple locations - 11x faulty lights - please see map | Electrical | General Electrical | 995.975 | Pass | Fail | -1 | 8 | 1463.5 | 2022-02-09 11:47 | 2022-02-16 17:00 | 2022-02-11 14:00 | 2022-02-16 17:00 | 2022-04-13 13:30 |  | WACCES | Arrived on site at 14:00 to investigate faulty lights as reported by station. Located 2 x lights out in study replaced tubes in one and ballast and tubes in other. Located 6 bunker lights on external replaced globes in 5 and will need to order in ballast to fix light #8. Will need to order in metal halide for light above sign and downlight for outside dry cleaning room. Left site at 16:00. materials 4 x 28w t5 840 tunes 1 x 14-35w t5 single ballast 5 x 26w 4 pin compact fluorescents
MSA-DTWD | WA6256816 | 2 | Precise Air Group | D048 & D048.1 - A/C unit blowing hot/cold, also requires vent adjustment - Notes | Air Conditioning | Ducted Split System |  | Pass | Fail | -1 | 8 | 1462.9333 | 2022-11-24 08:55 | 2022-11-29 17:00 | 2022-11-24 14:00 | 2022-11-29 17:00 | 2023-01-24 12:56 |  |  | Attended site to investigate 2 AC units in D block that need adjusting. Unit D4 keeps hearing and cooling. This usually means that controller is to close to the unit and the unit is basically blowing onto the controller causing jt to change so quickly. The other unit in the office next door unit D3 needs the vents adjusting. You can’t manually change these as they are motorised and if we were to change these the next time the unit turns off then back on it will adjust the vent to how it was. We have tried to adjust this by using the BMS. We don’t have the access ti do so as it has been restricted, we can change temps or adjust the vents. We will need to get NRP to visit site to have a look.Promap won’t work, won’t let me sync details to fill out for the job.Attended site liased with NRP and adjusted vents to achieve coorrect air flow.
MSA-DTWD | WA5216518 | 1 | Precise Air Group | room C50 - FCU5 motor tripped out, no airflow North side C block upper | Air Conditioning | Room Air Conditioners | 2743.48 | Pass | Fail | 0 | 8 | 1462.5167 | 2022-03-11 10:48 | 2022-03-14 17:00 | 2022-03-11 10:49 | 2022-03-14 17:00 | 2022-05-11 09:20 |  |  | Change AHU 5 motor.
MSA-DFES | WA4986225 | 3 | AWB Co. | Main Building - Cleaners store Room - mould issue - see notes below | Building | Internal Walls | 418.56 | Fail | Fail | 0 | 9 | 1461.3333 | 2021-12-31 12:22 | 2022-01-10 17:00 | 2022-01-13 14:47 | 2022-01-10 17:00 | 2022-03-15 12:07 |  | WCAPPR | Investigate roofing issues, removed roof sheet and flashings but no signs of water egressInvestigate via ceiling access found a/c had signs of water marks in muiltiple areas. Ceiling/corniceMould showning in a large area along a/c vent line, sealed off areasof concern via roof/ac unit, ceiling may need replacement
MSA-DTWD | WA5583728 | 2 | Precise Air Group | room A009 FCU faliure | Air Conditioning | Room Air Conditioners | 1491.64 | Pass | Fail | 0 | 9 | 1456.2167 | 2022-07-04 14:23 | 2022-07-07 17:00 | 2022-07-06 20:00 | 2022-07-07 17:00 | 2022-09-05 12:13 |  | WACCES | Picked up new fan motor assembly and installed into FCU in facilities office checked operation all running efficiently job completed
MSA-DTWD | WA5796755 | 2 | Equans Mechanical Services Australia | Room F60 - Aircon is not working | Air Conditioning | Room Air Conditioners | 2628.095 | Pass | Fail | 0 | 8 | 1446 | 2022-08-26 13:25 | 2022-08-31 17:00 | 2022-08-29 08:00 | 2022-08-31 17:00 | 2022-10-28 14:00 |  |  | Picked up required parts, went to site signed in checked in with Dennis. Gathered tools and equipment started removing old parts and replacing new. Once installed tested unit operation all ok. Cleaned up and disposed of rubbish and completed paperwork and signed out.
MSA-DTWD | WA5164009 | 2 | Ronley Holdings Pty Ltd | Workshops, the dust extractor is not dumping sawdust into bins | Electrical | General Electrical | 5240 | Fail | Fail | 3 | 11 | 1443.5 | 2022-02-18 14:48 | 2022-02-23 17:00 | 2022-03-14 09:30 | 2022-02-23 17:00 | 2022-05-13 13:00 |  | WACCES | The pulse valves have been replaced and are working as per design and the broken filter has been replaced with new. Due to the system not working correctly for some time, the remaining 31 filters are so blocked it is quite difficult to clear the build up of dust and the TAFE has requested pricing to replace the remaining filters with new. It should also be noted that when this system was installed, the system ductwork was installed along the front of the extractor unit, so close to the unit that it is not possible to fully open the doors to remove/replace the filters. It is difficult to understand how this was accepted at design and commissioning, very substandard. In order to replace the filters we will need to undo all the bolts on the doors and lift them off.
MSA-DFES | WA5611869 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Firefighters ensuite - water coming threw light fitting - please isolate/make safe | Electrical | Lighting, Internal | 134.46 | Pass | Fail | 0 | 9 | 1443 | 2022-07-14 10:00 | 2022-07-14 12:00 | 2022-07-14 10:30 | 2022-07-14 14:00 | 2022-09-12 13:30 |  |  | Located faulty light. Reconnect the light and it is now working.
MSA-DTWD | WA5298198 | 1 | BAKE-QUIP PTY LTD | Cafeteria - Fault in igniting deep fryers | Equipment | Catering Equipment | 1642.3 | Pass | Fail | 0 | 9 | 1442.75 | 2022-03-31 16:16 | 2022-04-01 17:00 | 2022-04-01 12:00 | 2022-04-01 17:00 | 2022-05-31 14:45 |  | WACCES | refer to service report for works.
MSA-DTWD | WA6254114 | 2 | AWB Co. | Various external lights do not work - see notes | Electrical | Lighting, External | 7771.62 | Pass | Fail | 0 | 8 | 1442.5 | 2022-11-22 15:41 | 2022-11-25 17:00 | 2022-11-24 12:30 | 2022-11-25 17:00 | 2023-01-23 15:00 |  | WACCES & WCAPPR | Attended site signed in jsa complete. Remove remaining light fittings as per list and replaced with new light fittings. Tested operational. Job complete
MSA-DTWD | WA5298214 | 1 | BAKE-QUIP PTY LTD | Cafeteria - 3 x faulty burners – gas smell coming from behind | Equipment | Cleaning Equipment | 1749.7 | Pass | Fail | 0 | 9 | 1442.25 | 2022-03-31 16:26 | 2022-04-01 17:00 | 2022-04-01 14:30 | 2022-04-01 17:00 | 2022-05-31 16:45 |  | WACCES & WCAPPR | REFER TO SERVICE REPORT FOR NOTES ON FURTHER GAS TESTING FOR LEAKS.
MSA-DTWD | WA5319198 | 3 | ECO PLUMBING AND GAS PTY LTD | Toilet in third cubicle cistern is leaking in to pan continuously | Plumbing & Drainage | Toilets/Cisterns | 260.855 | Pass | Fail | 0 | 9 | 1440.3833 | 2022-04-12 13:17 | 2022-04-21 17:00 | 2022-04-21 13:52 | 2022-04-21 17:00 | 2022-06-20 14:15 |  | WACCES | Ordered parts for hideaway cistern 20/6/22 installed new cistern parts.
MSA-DFES | WA5454847 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Pump House - level 2 - locker room 2 - Exhaust fan is making noises and partly working | Electrical | General Electrical | 326.88 | Fail | Fail | 1 | 10 | 1437.5 | 2022-05-17 15:17 | 2022-05-20 17:00 | 2022-05-30 12:00 | 2022-05-20 17:00 | 2022-07-29 09:30 |  | WACCES | Arrived on site at 09:00. Went to locker room 2 and was shown faulty exhaust fan, replaced with new fan and tested. Continued on site at 09:30
MSA-DTAG | WA5326011 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - Plantroom - Fault displayed in HWP-1 Unit | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2054.34 | Pass | Fail | -1 | 8 | 1422.5 | 2022-04-14 15:12 | 2022-04-26 17:00 | 2022-04-20 08:00 | 2022-04-26 17:00 | 2022-06-18 14:30 |  |  | Hired compression tool from supplier.Pick up all gear required for works. Attend site and access plantroom. Isolate all valves and heating water system. Drain water out of system. Cut old valves off and compress new fittings to pipework. Install new valves and connect. Deisolate water supply and check for leaks. Clean off all surface corrosion from pot and paint. Clean up area.SERVICE
MSA-DTWD | WA5627945 | 3 | AWB Co. | Grounds - Carpark light #41 opposite block 13 hit and damaged by broken tree branch- EWP Requires | Electrical | Lighting, External | 779.3 | Pass | Fail | -1 | 8 | 1422.3167 | 2022-07-15 09:36 | 2022-07-22 17:00 | 2022-07-18 08:00 | 2022-07-22 17:00 | 2022-09-15 14:19 |  |  | Attended site and signed in. Completed JSA and required paperwork for ewp works. Located pole which has been made redundant. Removed led off pole. Drove ewp around to pole with faulty top. Set up work area. Isolated circuit. Removed old pole top. Installed led pole top from other light. Energised circuit and tested. All working correctly. Cleaned and packed up site. Disposed of rubbish correctly. Notified relevant personnel of works completed. **job complete**
MSA-DTAG | WA5094927 | 1 | Bullant Security Pty Ltd | Custody - Downstairs Custody -Key has snapped off in half when trying to unlock cabinet | Security | Locksmith | 165 | Pass | Fail | 0 | 8 | 1416.5 | 2022-01-31 16:11 | 2022-02-01 17:00 | 2022-02-01 08:45 | 2022-02-01 17:00 | 2022-04-01 09:15 |  |  | Attend site and extract snapped key from the barrel move lock and cylinder from cupboard door and make 2x new keys to suit.
MSA-DTWD | WA5174910 | 1 | SCAVENGER SUPPLIES PTY LTD | fire pump shed - Jacking pump was activated for reasons unknown | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 5993.49 | Pass | Fail | 0 | 8 | 1416.2167 | 2022-02-21 09:08 | 2022-02-22 17:00 | 2022-02-21 14:00 | 2022-02-22 17:00 | 2022-04-21 14:13 |  | WACCES | WORK STARTED 21/02/2022 BRAF REQUIRED FOR FURTHER INVESTIGATIONSBRAF APPROVED 15/03/2022 SEE ATTACHMENTCOMPLETED 21/04/2022
MSA-DFES | WA5393041 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Mall Outside Office - downlight light is damaged | Electrical | Lighting, Internal | 637.29 | Pass | Fail | 0 | 8 | 1414.75 | 2022-05-03 14:16 | 2022-05-06 17:00 | 2022-05-06 09:45 | 2022-05-06 17:00 | 2022-07-04 08:30 |  | WACCES | Collected gear from workshop at 06:30 and continued to site arrived at 07:15. Removed cover and replaced damaged uplighter, tested circuit and check other uplighters all okay. Continued on site at 08:30
MSA-DFES | WA5680755 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Firefighters ensuite - Led Fluro need to be reconnected as the water leak fixed | Electrical | Lighting, Internal | 107.715 | Pass | Fail | 0 | 8 | 1413.75 | 2022-07-27 15:38 | 2022-08-01 17:00 | 2022-08-01 16:30 | 2022-08-01 17:00 | 2022-09-29 14:15 |  | WCAPPR | Arrived onsite at 16:30 to reconnect light located firefighters en-suite. Found leak had not been fixed yet and will need toreturn to site to reconnect when leak is fixed correctly. Staff onsite confirmed leak isn’t fixed and left site at 16:45Arrived on site at 14:00 to reconnect light, job has been reconnected under seperate work order, on the 12/8. No action needed. Left site at 14:15
MSA-DFES | WA5462479 | 2 | Seme Solutions Pty Ltd | Entry Corridor - Door opening switch from corridor into tunic room is not functioning | Security | Access Control | 292.5 | Pass | Fail | 0 | 8 | 1413.5667 | 2022-05-19 15:34 | 2022-05-24 17:00 | 2022-05-24 15:11 | 2022-05-24 17:00 | 2022-07-22 12:45 |  |  | Need to reattend if we get given access to Cockburn workstation to fault find
MSA-DTWD | WA5413183 | 2 | Protek 24/7 Building & Maintenance | Room H14 - Roof Leak | Roofing | Metal Roofing | 1341.375 | Pass | Fail | -1 | 8 | 1412.75 | 2022-05-12 09:37 | 2022-05-17 17:00 | 2022-05-13 12:30 | 2022-05-17 17:00 | 2022-07-11 09:15 |  |  | Sealed Window Pains to prevent further leaks Patched and painted walls
MSA-DTWD | WA6365968 | 2 | ACTION GLASS & ALUMINIUM | Vandals have thrown a metal object through level 3 window | Glazing | Window Glass | 3254.545 | Pass | Fail | 0 | 8 | 1410.75 | 2022-12-13 13:42 | 2022-12-16 17:00 | 2022-12-14 14:30 | 2022-12-16 17:00 | 2023-02-11 09:15 |  |  | ATTENDED SITEPATCHED TO SECURE BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-700 X 780PLUS 1.5 SQM OF SAFETY FILM AND SILICONERETURNED LATER DATE WITH 4 MEN AFTER HOURS TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-1500 X 1133PLUS 10 L/M OF RUBBER REPLACED PLUS SILICONEKNUCKLE BOOM LIFT AND CITY OF PERTH PARKING AND TRAFFIC MANAGEMENT PLAN REQUIRED COMPLETED AS PER APPROVED BRAF
MSA-DCA | WA5325236 | 2 | Techworks Electrical | Ground Level - City Room - Light to water feature outside main entrance is faulty - see notes | Electrical | Lighting, External | 981.1 | Pass | Fail | 0 | 8 | 1394.5 | 2022-04-14 08:32 | 2022-04-21 17:00 | 2022-04-20 05:30 | 2022-04-21 17:00 | 2022-06-17 08:00 |  | WACCES | Have found the light fitting to have damage right under the rim, there is a big crack on the fitting which as allowed water ingress into the light causing it to fail. We will need to order in a replacement.17/6/22 - Returned to replace light fitting.
MSA-DTAG | WA5792466 | 3 | Seme Solutions Pty Ltd | Issue with CCTV - See notes below | Security | CCTV Surveillance | 2776.83 | Pass | Fail | -1 | 7 | 1394 | 2022-08-23 14:34 | 2022-08-30 17:00 | 2022-08-24 12:00 | 2022-08-30 17:00 | 2022-10-21 14:00 |  |  | installed new IP camera for vehicle entr/exit gate (cam 18), had to change pole power from 24VAC to 12VDC to suit new camera requirements. Installed 12VDC PSU in L1 comms rack (Model OPS-12V-8A - SEME stock). Moxa failed after power change, required new moxa.Sourced moxa (SEME stock) and replaced, both cams on pole operational again. Job Complete - Camera 13 fixed on another job.
MSA-DTAG | WA5792436 | 3 | Seme Solutions Pty Ltd | CCTV2 (44) Waiting Not working | Security | CCTV Surveillance | 3993.59 | Pass | Fail | -1 | 8 | 1393.5 | 2022-08-23 14:16 | 2022-08-30 17:00 | 2022-08-25 13:00 | 2022-08-30 17:00 | 2022-10-22 14:30 |  |  | Cabled and installed new IP camera for waiting 10 (cam 44), confirmed online and operational.
MSA-DTAG | WA5521897 | 2 | AWB Co. | Basement - Cell 4 Custody - toilet light broken and will need replacement | Electrical | Lighting, Internal | 771.44 | Pass | Fail | 0 | 8 | 1391 | 2022-06-15 11:08 | 2022-06-20 17:00 | 2022-06-20 09:30 | 2022-06-20 17:00 | 2022-08-17 08:30 |  | WACCES | Job complete
MSA-DTWD | WA5479724 | 2 | Precise Air Group | Faulty Exhaust Fans - Inside ceiling space - Mechanical Services/Ventilation | Equipment | Building Equipment | 2413.96 | Pass | Fail | 0 | 8 | 1390.95 | 2022-05-27 11:15 | 2022-06-01 17:00 | 2022-05-30 14:48 | 2022-06-01 17:00 | 2022-07-27 13:45 |  |  | Returned back to site with new exhaust fan removed faulty fan and installed and wired new one in checked operation all running efficiently - Complete
MSA-DFES | WA5472093 | 2 | Protek 24/7 Building & Maintenance | Rear yard boundary fence - see notes below | Building | Steel Fencing & Gates | 1689.39 | Pass | Fail | 0 | 8 | 1390.75 | 2022-05-23 13:58 | 2022-05-26 17:00 | 2022-05-25 13:15 | 2022-05-26 17:00 | 2022-07-22 12:00 |  |  | relaced and remove damaged fencing
MSA-DTAG | WA5318399 | 1 | Midolo Building Services | Mandurah front entry - attempted break in - see details below | Building | General Building | 495.03 | Pass | Fail | 0 | 8 | 1390 | 2022-04-12 10:56 | 2022-04-13 17:00 | 2022-04-12 11:00 | 2022-04-13 17:00 | 2022-06-09 09:00 |  | WACCES | All issues rectified
MSA-DTAG | WA5216911 | 3 | Midolo Building Services | Level 1 - Corridor - Timber wall skirting is water damaged - replace | Building | General Building | 904.02 | Pass | Fail | -1 | 8 | 1388.5 | 2022-03-11 14:00 | 2022-03-18 17:00 | 2022-03-14 11:30 | 2022-03-18 17:00 | 2022-05-11 08:00 |  | WACCES | Installed & repaired new skirting - varnished timber skirting
MSA-DTWD | WA5215643 | 1 | AWB Co. | ALTENDORF F45 panel saw faulty | Equipment | Electrical Equipment | 1842.15 | Fail | Fail | 1 | 9 | 1372.2 | 2022-03-10 14:05 | 2022-03-11 17:00 | 2022-03-15 09:03 | 2022-03-11 17:00 | 2022-05-11 13:15 |  |  | Attended site. Signed in. Completed JSA. went to panel saw. Tried to use panel saw to see if it was operational. Panel saw was still stopping every 100mm or so. adjusted the machines settings/limits. Found that “collisions” was set on 4.0, this was the reason machine kept stopping and had error come up. Changed value from 4.0 to 8.0 to allow more current. Didn’t put value too high, still stops when wood is in the way as it should. Tested machine. Machine is now working as intended. Completed paperwork.Job complete
MSA-DCA | WA5392561 | 3 | Protek 24/7 Building & Maintenance | Maritime Archaeology - Ground - Office Areas - window in the far SW corner was rattling in rain/win | Building | General Building | 3681.35 | Pass | Fail | -1 | 7 | 1370.5 | 2022-05-03 10:40 | 2022-05-10 17:00 | 2022-05-05 11:45 | 2022-05-10 17:00 | 2022-07-01 14:15 |  | WACCES | Repaired leaking window
MSA-DTAG | WA6362799 | 2 | Sapio Pty Ltd | Level 1 - Patch Room - Camera Charlie 117/Lema 1 - Error message - Connection failed | Security | CCTV Surveillance | 462.68 | Pass | Fail | 0 | 8 | 1370 | 2022-12-09 13:12 | 2022-12-12 17:00 | 2022-12-12 15:00 | 2022-12-12 17:00 | 2023-02-07 17:00 |  |  | Work performed by Michael Tomlinson (07/02/2023) Close Off, rectified under WA6405108.
MSA-DFES | WA5417280 | 2 | AWB Co. | Rear Canopy Leaking close to center of rear engine door (1st light tanker) | Roofing | Metal Roofing | 2612.84 | Pass | Fail | 0 | 8 | 1368.5 | 2022-05-13 11:38 | 2022-05-18 17:00 | 2022-05-16 13:00 | 2022-05-18 17:00 | 2022-07-12 13:30 |  | WCAPPR | Attended, leaking to canopy above door 1, polycarbonate sheeting joins twinwall section. Flashing joins both and relieson silicon to stop water ingress, further works required
MSA-DTWD | WA5571214 | 3 | Protek 24/7 Building & Maintenance | Water damaged wooden storeroom door on external wall | Building | Doors | 2262.83 | Pass | Fail | -1 | 7 | 1366.25 | 2022-06-29 09:54 | 2022-07-06 17:00 | 2022-06-30 14:00 | 2022-07-06 17:00 | 2022-08-26 12:15 |  | WACCES | • Remove and dispose of damaged rebated double doors• Supply and install new rebated double doors• Reuse existing hardware (Hinges, handles & locks), install new storm-seal to both doors
MSA-DTAG | WA5792471 | 3 | Seme Solutions Pty Ltd | CCTV2 (26) Protective witness Exit Not working | Security | CCTV Surveillance | 1420.34 | Pass | Fail | -1 | 7 | 1365 | 2022-08-23 14:36 | 2022-08-30 17:00 | 2022-08-24 13:00 | 2022-08-30 17:00 | 2022-10-20 10:00 |  |  | installed new IP camera for protected witness exit (cam 25), confirmed online and operational.
MSA-DFES | WA5522448 | 3 | AWB Co. | Ground - South End Building - external brick work shows large c rack in mortar of wall | Building | External Walls | 4115 | Pass | Fail | 0 | 8 | 1352 | 2022-06-15 16:07 | 2022-06-22 17:00 | 2022-06-22 07:00 | 2022-06-22 17:00 | 2022-08-17 15:00 |  |  | wokrs completed
MSA-DTWD | WA5679548 | 3 | Australian Airconditioning Services Pty Ltd | A/C 4 stage 2 has no gas | Air Conditioning | Building HVAC Maintenance (Major Plant) | 3878.16 | Pass | Fail | -1 | 7 | 1349.5 | 2022-07-26 14:54 | 2022-08-02 17:00 | 2022-07-29 07:30 | 2022-08-02 17:00 | 2022-09-23 13:00 |  | WACCES | Replaced sight glass. Pressure test and evacuation successful. Charged and tested unit. All ok
MSA-DFES | WA5589648 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Appliance Parking Bay - Two fluorescent tube light are not working | Electrical | Lighting, External | 618.47 | Pass | Fail | 0 | 8 | 1347 | 2022-07-08 15:22 | 2022-07-15 17:00 | 2022-07-12 07:45 | 2022-07-15 17:00 | 2022-09-06 10:45 |  | WACCES | Arrived onsite 10:00 to replace faulty LED light in engine bay. Replaced light and tested all ok. Informed staff of works and left site at 1045.
MSA-DTWD | WA6154295 | 3 | AWB Co. | Main entrance - awning ceiling sagging | Building | Awnings | 1240.4675 | Pass | Fail | 0 | 8 | 1346.75 | 2022-11-07 11:44 | 2022-11-14 17:00 | 2022-11-11 09:00 | 2022-11-14 17:00 | 2023-01-06 11:45 |  |  | ceiling works completedThis was originally quoted however we managed to not need some materials and labour content was reduced as repair was a more simple fix
MSA-DTWD | WA5679452 | 1 | AWB Co. | External Lights - Security lights keep tripping the power | Electrical | Lighting, External | 5767.0875 | Pass | Fail | 0 | 8 | 1346.25 | 2022-07-26 13:57 | 2022-07-27 17:00 | 2022-07-27 12:00 | 2022-07-27 17:00 | 2022-09-21 14:15 |  |  | works completed as per sign slips
MSA-DFES | WA5982460 | 1 | Go Doors | Engine bay - Door 2 - Not working. | Building | Doors | 900 | Fail | Fail | 1 | 9 | 1346 | 2022-09-30 11:22 | 2022-10-03 17:00 | 2022-10-07 08:00 | 2022-10-03 17:00 | 2022-12-02 10:00 |  |  | Works completed
MSA-DTWD | WA5697809 | 3 | Protek 24/7 Building & Maintenance | B30 - Roof leak – two skylight sheets need replacing | Roofing | Rooflights and Skylights | 1060.5 | Pass | Fail | 0 | 8 | 1345.75 | 2022-08-09 12:01 | 2022-08-16 17:00 | 2022-08-15 12:45 | 2022-08-16 17:00 | 2022-10-10 14:30 |  | WACCES | Remove and replace skylights
MSA-DTWD | WA5100306 | 1 | Protek 24/7 Building & Maintenance | Cafeteria Courtyard - Damaged and raised brick paving causing an OSH issue | Paving & Roadworks | Paving | 3300.19 | Pass | Fail | 0 | 8 | 1345.25 | 2022-02-02 12:22 | 2022-02-03 17:00 | 2022-02-02 14:45 | 2022-02-03 17:00 | 2022-03-30 16:00 |  |  | Screed and relay pavers to affected area
MSA-DTAG | WA6258734 | 3 | Australian HVAC Services Pty. Ltd. | Level 11 - Admin Office - Very low air flow | Air Conditioning | Room Air Conditioners | 950.84 | Pass | Fail | -1 | 7 | 1344.2667 | 2022-11-25 15:44 | 2022-12-02 17:00 | 2022-11-25 15:44 | 2022-12-02 17:00 | 2023-01-20 16:00 |  |  | Install data loggers. Leave in position for a week. Return to site and remove. Download loggers information. Check temps and found between 22 and 24 all week. Airconditioning is working in required parameters.
MSA-DTAG | WA6379394 | 2 | Australian HVAC Services Pty. Ltd. | Level 4 - Adult community corrections - no air flow coming through aircon vents | Air Conditioning | Room Air Conditioners | 2521.74 | Pass | Fail | 0 | 8 | 1343.1 | 2022-12-19 10:52 | 2022-12-22 17:00 | 2022-12-19 12:00 | 2022-12-22 17:00 | 2023-02-13 11:06 |  | WACCES | Access level 4. Organise access into detention area to isolate power supply to Fire damper actuators. Access ceiling through manhole and disconnect electrical wiring to actuator. Unbolt actuator from shaft and remove. Fit new actuator to shaft and connect electrical wiring. Gain access to detention area and deisolate power supply. Carry out operational testing. Working ok. Will monitor over a week.
MSA-DTWD | WA5680182 | 2 | Australian Airconditioning Services Pty Ltd | Outdoor unit splashing water out of Air Con unit | Air Conditioning | Room Air Conditioners | 400.08 | Pass | Fail | 0 | 8 | 1343 | 2022-07-27 10:13 | 2022-08-01 17:00 | 2022-07-29 10:30 | 2022-08-01 17:00 | 2022-09-23 09:30 |  | WACCES | Drain kit was no longer available. Fitted PVC pipe to bottom of Condenser to redirect condensate to existing drain. All ok
MSA-DTWD | WA5832092 | 2 | AWB Co. | roof leak | Roofing | Metal Roofing | 1503.82 | Pass | Fail | 0 | 8 | 1343 | 2022-09-05 11:04 | 2022-09-08 17:00 | 2022-09-07 13:30 | 2022-09-08 17:00 | 2022-11-02 12:30 |  | WACCES | Works completed as per BRAF: Remove redundant A/C penetrations x 2Supply and install new sections of dry pan flashing to enclose void to locations.Supply all fixings and accessories required for install.Remove all waste from site.
MSA-DTWD | WA6109132 | 3 | AWB Co. | 3B-7 Engine Test Cell - Multiple lights out | Electrical | Lighting, Internal | 2267.915 | Pass | Fail | 0 | 8 | 1342 | 2022-10-20 14:09 | 2022-10-27 17:00 | 2022-10-24 14:00 | 2022-10-27 17:00 | 2022-12-19 12:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed. Isolated row of lights. Removed and replaced with remaining lights for job.Tested operational. Job completed
MSA-DTWD | WA6081790 | 2 | AWB Co. | Block 6 - A1 Metal fabrication 2 - Fan switch not working on Plasma Cutter | Electrical | General Electrical | 1160.18 | Pass | Fail | 0 | 8 | 1326.5 | 2022-10-18 14:36 | 2022-10-21 17:00 | 2022-10-20 08:30 | 2022-10-21 17:00 | 2022-12-14 15:00 |  | WCAPPR | Attended site signed in jsa completed. Installed gpo for lead to plug into indicator lamp and switch. Added one more gpo as per site request for other fan 1m away. Job completed
MSA-DFES | WA6000600 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Reception - foyer spot light - light bulb damaged will require a tall ladder | Electrical | Lighting, Internal | 294.93 | Pass | Fail | -1 | 7 | 1325 | 2022-10-10 09:13 | 2022-10-17 17:00 | 2022-10-13 07:15 | 2022-10-17 17:00 | 2022-12-07 12:15 |  | WACCES | Arrived onsite at 7:15 to investigate light not working located foyer. Found 1 x light was flashing due to faulty parts within. Gained access with tall ladder and found light was a complete LED unit. Parts are not repairable and will need a whole new fitting. Disconnected track light from tracking system to stop flashing. Documented all necessary information for replacement, notified staff of works completed whilst onsite and left site at 8:45Matthew Kenney (07/12/2022) - Work NoteArrived onsite at 11:15 to adjust uneven track lighting in reception, relocated existing track lights evenly, advised staff of works and left site at 12:15.Adam Back (13/10/2022) - Work NoteArrived onsite at 7:15 to investigate light not working located foyer. Found 1 x light was flashing due to faulty parts within. Gained access with tall ladder and found light was a complete LED unit. Parts are not repairable and will need a whole new fitting. Disconnected track light from tracking system to stop flas
MSA-DFES | WA6022740 | 2 | Protek 24/7 Building & Maintenance | West dorm-Plastic window lock.opener on end dorm broken. Unable to open window. | Building | Windows | 208.65 | Pass | Fail | 0 | 8 | 1320.5 | 2022-10-14 11:37 | 2022-10-19 17:00 | 2022-10-19 07:00 | 2022-10-19 17:00 | 2022-12-13 07:30 |  | WACCES | Removed and replaced damaged window latch
MSA-DTAG | WA5151113 | 0 | Sapio Pty Ltd | Room 4.01 – emergency lock duress (judicial door) – displaying as tampered and continuously flashing | Security | Monitoring | 1046.63 | Pass | Fail | 0 | 8 | 1319.5 | 2022-02-17 10:58 | 2022-02-17 12:58 | 2022-02-17 12:00 | 2022-02-17 14:58 | 2022-04-13 11:30 |  | WACCES & WCAPPR | Installed new In Session Panel and Emergency Lock Duress, tested, all OK.
MSA-DFES | WA5393037 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | External - Mural - light is faulty | Electrical | Lighting, External | 415.59 | Pass | Fail | 0 | 8 | 1319.25 | 2022-05-03 14:15 | 2022-05-10 17:00 | 2022-05-10 10:00 | 2022-05-10 17:00 | 2022-07-04 09:15 |  | WACCES | Continued on site at 08:30. Located faulty bunker light on mural wall, replaced with new led fitting and tested all okay. Continued on site at 09:15
MSA-DTWD | WA5472763 | 1 | BAKE-QUIP PTY LTD | Turbo Fan oven glass door shattered | Equipment | Catering Equipment | 744.1 | Pass | Fail | 0 | 8 | 1318.5 | 2022-05-24 10:20 | 2022-05-25 17:00 | 2022-05-25 10:00 | 2022-05-25 17:00 | 2022-07-19 08:30 |  | WACCES | Refer to service report
MSA-DCA | WA5324522 | 0 | Protek 24/7 Building & Maintenance | Main dock -Temperory fencing | Carpentry | Timber Fencing & Gates | 1000 | Pass | Fail | 0 | 8 | 1315 | 2022-04-13 18:27 | 2022-04-13 20:27 | 2022-04-13 18:30 | 2022-04-13 22:27 | 2022-06-07 13:30 |  |  | Roller door stuck open - not secured secured with temporary fencing
MSA-DFES | WA5163479 | 1 | Australian HVAC Services Pty. Ltd. | BMS - Exhaust fan in the comsend toilets is faulty | Air Conditioning | Room Air Conditioners | 440.985 | Pass | Fail | 0 | 7 | 1303.7006 | 2022-02-18 09:28 | 2022-02-21 17:00 | 2022-02-18 11:58 | 2022-02-21 17:00 | 2022-04-13 19:40 |  | WACCES | Attended site and accessed comcen. Replaced faulty airflow switch. Calibrated switch and confirmed operation. Cleared debris and completed job.
MSA-DFES | WA5416907 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - State Operator Centre - Various Lights out - see notes below | Electrical | Lighting, Internal | 999.395 | Pass | Fail | 0 | 8 | 1302.25 | 2022-05-13 09:17 | 2022-05-18 17:00 | 2022-05-18 09:15 | 2022-05-18 17:00 | 2022-07-11 15:30 |  | WACCES & WCAPPR | Job completed under WA5128285
MSA-DFES | WA5572087 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Staff Changerooms - LED light flashing in Female Staff Change Rooms + Light pole(see below) | Electrical | General Electrical | 1267.575 | Pass | Fail | 0 | 7 | 1300.25 | 2022-06-29 13:31 | 2022-07-04 17:00 | 2022-07-01 10:00 | 2022-07-04 17:00 | 2022-08-24 14:15 |  | WACCES | Continued on with works onsite. Located faulty pole light & LED light in female change room. Took note of parts required. Left site to retrieve parts, could only find 1 out of 3 parts after travelling to multiple wholesalers. Will need to return with parts to complete works. Informed staff of job status.Continued on site and replaced faulty light pole globe in carpark A. Found the capacitor to be faulty as well. Need to replace led in ladies bathroom as wellTested and notified staff of outcome before signing out
MSA-DTAG | WA5993811 | 1 | Sapio Pty Ltd | SAT - Camera C516 - L5.03 - Server Lost connection to camera. See notes | Security | CCTV Surveillance | 3738.56 | Pass | Fail | 0 | 8 | 1295.5 | 2022-10-05 12:13 | 2022-10-06 17:00 | 2022-10-05 14:30 | 2022-10-06 17:00 | 2022-11-28 14:00 |  | WACCES | Part delivered to Mario Kovac.camera installed and operational.no response from Midolo M.Kovac advised
MSA-DTAG | WA6365971 | 1 | AWB Co. | Staff kitchen - Registry - Call center - Lights are out. | Electrical | Lighting, Internal | 11535.895 | Pass | Fail | 0 | 8 | 1277.75 | 2022-12-13 13:41 | 2022-12-14 17:00 | 2022-12-14 10:45 | 2022-12-14 17:00 | 2023-02-05 16:30 |  |  | BRAF submitted for approval
MSA-DTWD | WA5549028 | 2 | Protek 24/7 Building & Maintenance | A Block leaks corridor - Roof. Box Gutter - Substantial roof/gutter leak above windows - see below | Building | General Building | 2322.51 | Fail | Fail | 1 | 9 | 1277.5 | 2022-06-17 12:09 | 2022-06-22 17:00 | 2022-06-30 10:00 | 2022-06-22 17:00 | 2022-08-22 15:30 |  | WACCES | • Remove and dispose of damaged sump & box gutter surrounding sump• Supply and install new sump and box gutter• Confirm integrity of ceiling under area where roof plumbing damage occurred
MSA-DFES | WA6008515 | 3 | Protek 24/7 Building & Maintenance | Superintendents office and main open plan office - Roof Leaks - | Roofing | Metal Roofing | 3004.81 | Pass | Fail | 0 | 7 | 1277.5 | 2022-10-11 16:09 | 2022-10-18 17:00 | 2022-10-17 07:00 | 2022-10-18 17:00 | 2022-12-09 12:30 |  | WACCES & WCAPPR | ? Remove and dispose of dek-tite to aerial unit? Supply and install new dek-tite to aerial unit and seal? Supply and install new flashing to air-con and seal? Apply new flexible pointing to parapet wall as required? Remove and dispose of 4x damaged ceiling tiles? Supply and install new ceiling tiles where damaged tiles removed? Carry out water-test once works complete
MSA-DCA | WA5831980 | 1 | Precise Air Group | Wardle Room - Beer Fridge not getting down to temperature (stuck at 20+deg)- See notes below | Refrigeration | Refrigerators | 3675.22 | Fail | Fail | 0 | 8 | 1275.6 | 2022-09-05 10:02 | 2022-09-06 17:00 | 2022-09-07 11:18 | 2022-09-06 17:00 | 2022-10-30 14:54 |  | WACCES | Parts are due in on 12/10/22 and will be installed as soon as they arrive.Replacement of EVAP Coil completed.
MSA-DTAG | WA6376450 | 3 | AWB Co. | Level 2 - Sallyport driveway roof (Hay St) - Light not working and cabling ducting falling off wall | Electrical | General Electrical | 3414.015 | Pass | Fail | 0 | 7 | 1274 | 2022-12-15 15:27 | 2022-12-22 17:00 | 2022-12-20 13:00 | 2022-12-22 17:00 | 2023-02-11 15:00 |  |  | Braf submitted
MSA-DFES | WA4983343 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Rear Engine Room Apron - 2 x domestic hoses and hose reel on the black reels faulty. | Plumbing & Drainage | Water | 2394.515 | Pass | Fail | -1 | 7 | 1272.7833 | 2021-12-23 08:49 | 2022-01-04 17:00 | 2021-12-31 08:43 | 2022-01-04 17:00 | 2022-02-22 09:30 |  | WACCES & WCAPPR | Returned back to site and installed new hose reals tested and all working correctly.
MSA-DTWD | WA6257271 | 2 | AWB Co. | A125, A126 and library - Light switches not responding to CBUS system - see notes | Electrical | General Electrical | 3228.76 | Pass | Fail | 0 | 7 | 1269.5 | 2022-11-24 13:24 | 2022-11-29 17:00 | 2022-11-28 11:30 | 2022-11-29 17:00 | 2023-01-20 09:00 |  | WACCES | Attended site signed in jsa completed. Installed cable as per dean’s requirements. Tested both ends. Made sure light switches worked in both rooms. Lights in hallway are now switched also.job completed
MSA-DCA | WA5564775 | 2 | Protek 24/7 Building & Maintenance | Jubilee - Level 1 - Reflections - see details below | Building | General Building | 904.11 | Pass | Fail | 0 | 8 | 1269 | 2022-06-21 11:54 | 2022-06-24 17:00 | 2022-06-24 12:00 | 2022-06-24 17:00 | 2022-08-16 09:00 |  | WACCES | ? Remove section of gyprock wall to allow access behind? Supply and install noggin support behind wall to provide strong support for mag-lock? Supply and install new section of gyprock where original removed. Tape and seal.? Sand back gyprock wall, prepare for painting, provide undercoat and 2x Coat of paint to suit surrounding wall onsite? Remove current fixings for mag-lock and provide new solid fixings into new noggin suppo
MSA-DTWD | WA5307544 | 2 | BAKE-QUIP PTY LTD | Kendrew- E-Block - Restaurant Kitchen - prover oven not working after catching fire | Equipment | Catering Equipment | 1768.07 | Pass | Fail | -1 | 7 | 1253.25 | 2022-04-07 14:40 | 2022-04-12 17:00 | 2022-04-08 08:30 | 2022-04-12 17:00 | 2022-05-30 13:45 |  | WACCES | Refer to service report
MSA-DFES | WA5383865 | 1 | ACTION GLASS & ALUMINIUM | Main Entrance - window shattered | Building | Windows | 3630.2 | Pass | Fail | 0 | 7 | 1252.1667 | 2022-04-28 08:01 | 2022-04-29 17:00 | 2022-04-29 09:00 | 2022-04-29 17:00 | 2022-06-20 13:10 |  | WCAPPR | ATTENDED SITE TO MEASURE & ASSESSPATCHED BROKEN PANEL WITH 2 SQM OF SAFETY FILMRETURNED LATER DATE WITH 3 MEN TO REGLAZE12.52 SOLTECH GREY CUSTOM TOUGHENED LAMINATED SAFETY GLASS1-2695 X 1120PLUS 3.8 L/M OF DOUBLE SIDED TAPE, 75mm FROST FILM STRIP APPLIED AND 4 TUBES OF BLACK SILICONE USEDRETURNED LATER DATE TO TOUCH UP SILICONE JOINS WITH 1 TUBE SILICONECOMPLETED AS PER APPROVED BRAF
MSA-DFES | WA5285595 | 0 | Protek 24/7 Building & Maintenance | Front Door - Door damaged - Lock barrell is broken - | Building | Doors | 4080.93 | Fail | Fail | 0 | 7 | 1250 | 2022-03-21 08:57 | 2022-03-21 10:57 | 2022-03-21 11:00 | 2022-03-21 12:57 | 2022-05-12 13:00 |  | WACCES | Remove & Dispose of 2x Doors & Door hardwareSupply and Install new Metal-Clad Door to suit frame specs
MSA-DTWD | WA5514071 | 3 | Schneider Electric Australia Pty Ltd | Faulty back-up batteries | Security | Access Control |  | Pass | Fail | -1 | 6 | 1248.5 | 2022-06-14 15:31 | 2022-06-21 17:00 | 2022-06-14 16:00 | 2022-06-21 17:00 | 2022-08-05 16:30 |  |  | Repairs
MSA-DTWD | WA6503554 | 2 | Precise Air Group | aircon making strange noises | Air Conditioning | Room Air Conditioners | 4911.78 | Pass | Fail | -1 | 7 | 1248.1167 | 2023-01-19 09:47 | 2023-01-24 17:00 | 2023-01-20 07:59 | 2023-01-24 17:00 | 2023-03-13 08:06 |  | WACCES
MSA-DTWD | WA6254047 | 1 | SCAVENGER SUPPLIES PTY LTD | Reset B Block Fire panel in Alarm | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Fail | 0 | 7 | 1242.8 | 2022-11-22 14:30 | 2022-11-23 17:00 | 2022-11-22 14:48 | 2022-11-23 17:00 | 2023-01-13 09:36 |  |  | 22/11/2022 ATTENDED BY -KR-FURTHER INVESTIGATION REQUIRED20/12/2022 QUOTE SENT TO ERIC REEDMAN FOR UPGRADE TO SYSTEMS
MSA-DTWD | WA6361758 | 2 | Protek 24/7 Building & Maintenance | Roof leak - Please contact Facilities on arrival for further description | Roofing | Metal Roofing | 2179.425 | Pass | Fail | 0 | 7 | 1229.5 | 2022-12-08 12:47 | 2022-12-13 17:00 | 2022-12-12 09:30 | 2022-12-13 17:00 | 2023-02-01 15:00 |  | WACCES | Remove and dispose of existing apron flashing from roof transferSupply and install new colorbond apron flashing and seal as requiredClean site & Demobilise
MSA-DTWD | WA5578408 | 2 | Equans Mechanical Services Australia | A305 Staffroom - Airconditioning not heating | Air Conditioning | Room Air Conditioners | 4731.91 | Pass | Fail | 0 | 7 | 1229 | 2022-07-01 11:29 | 2022-07-06 17:00 | 2022-07-04 08:00 | 2022-07-06 17:00 | 2022-08-24 13:00 |  | WACCES | SEE REPORT
MSA-DFES | WA4985800 | 3 | AWB Co. | Boundary Brick Wall - vehicle has hit boundary brick wall and requires repairing | Building | General Building | 3587 | Pass | Fail | -1 | 6 | 1228.65 | 2021-12-30 12:12 | 2022-01-07 17:00 | 2022-01-01 08:21 | 2022-01-07 17:00 | 2022-02-21 13:00 |  |  | Wall rebricked as per BRAF. Painter sealed and painted wall to match existing colour. Job complete
MSA-DTAG | WA5974404 | 1 | Sapio Pty Ltd | Custody - 34 of custody screens not working | Security | Monitoring | 791.72 | Pass | Fail | 0 | 7 | 1228.25 | 2022-09-23 11:19 | 2022-09-27 17:00 | 2022-09-24 10:00 | 2022-09-27 17:00 | 2022-11-14 14:15 |  |  | WA - Robert Thorne (14/11/2022) - Work Note Replaced UPS in ground floor room 101.Updated duress description to match new door numbers.
MSA-DTWD | WA6361199 | 2 | Protek 24/7 Building & Maintenance | roof is leaking very badly - this roof was resheeted by Protek | Roofing | Metal Roofing | 9397.27 | Pass | Fail | 0 | 7 | 1227 | 2022-12-08 08:02 | 2022-12-13 17:00 | 2022-12-12 07:00 | 2022-12-13 17:00 | 2023-02-01 10:00 |  | WACCES | ? Cleaned out gutters and sumps to help water drain? Carried out site measure to confirm materials required? Remove and dispose of Existing box gutter ? Remove and Dispose of Existing 3 Sumps ? Remove and Dispose Existing Parapet Capping covering removed Box gutter ? Supply and install new Colorbond box gutters ? Supply and Install 3x Colorbond Sumps ? Core drill / Remove brickwork to bring New Outlets from Box Gutter into Rain Heads ? Supply and Install 3x Colorbond Standard Rain Heads ? Supply and Install 100mm PVC Downpipe from Rain Heads to ground level Only
MSA-DTAG | WA5127206 | 1 | Midolo Building Services | Ground - Courtside - Court Room 1 - Door handle exiting Court room 1 has broken | Building | General Building | 399.59 | Pass | Fail | 0 | 7 | 1226 | 2022-02-14 11:46 | 2022-02-15 17:00 | 2022-02-15 07:00 | 2022-02-15 17:00 | 2022-04-07 09:00 |  | WACCES | new handle & fixings installed
MSA-DTWD | WA5674173 | 2 | Protek 24/7 Building & Maintenance | Roof leak along Northern side | Roofing | Metal Roofing | 1825.145 | Pass | Fail | 0 | 7 | 1223.5 | 2022-07-21 09:30 | 2022-07-26 17:00 | 2022-07-26 11:00 | 2022-07-26 17:00 | 2022-09-15 10:30 |  | WACCES | ? Remove and dispose of rusted sump? Supply and install new custom sump? Connect to existing downpipe system? Water test once works complete to ensure no leaks
MSA-DTWD | WA5460236 | 3 | AWB Co. | Francis St entry foyer - South Block - LED light blown - needs new fitting to match existing | Electrical | Lighting, Internal | 771.62 | Pass | Fail | 0 | 7 | 1223.0333 | 2022-05-18 12:02 | 2022-05-25 17:00 | 2022-05-24 12:28 | 2022-05-25 17:00 | 2022-07-14 11:30 |  |  | Attended site signed in jsa completed. Installed new light which was on order in B1 francis st exit level 2. Lights working now and job completed
MSA-DCA | WA5471171 | 1 | Protek 24/7 Building & Maintenance | Water leak coming through the ceiling | Roofing | Metal Roofing |  | Pass | Fail | 0 | 7 | 1222.75 | 2022-05-23 12:25 | 2022-05-24 17:00 | 2022-05-24 11:00 | 2022-05-24 17:00 | 2022-07-14 09:45 |  | WACCES | Repair Roof leaks
MSA-DTWD | WA5382881 | 0 | Techworks Plumbing | U Block - Gournd - outside male toilets - blocked toilets as sewer is back up | Plumbing & Drainage | Sewer Drains & Septic Systems | 11414.13 | Pass | Fail | 0 | 7 | 1222.1667 | 2022-04-27 09:50 | 2022-04-27 11:50 | 2022-04-27 11:30 | 2022-04-27 13:50 | 2022-06-17 09:40 |  | WACCES | Attended site signed in at office and seen Dennis.Went to u block, found an IO and tried to jet drains but we were unable to unblock anything, so we went and removed a sewer man hole to see if there was any debris inside, once we had removed the lid we found it to be full of water and waste, spoke to Dennis and he gave us a sewer diagram so we could see where the pump pit was located.Once we located the pump pit we found it to be filled also, found the pumps electrical board and the isolation was off, the board had Ben showing one of the pumps with a fault, we were able to pump most of the water out the pit and checked the man hole closest to the pit that was full and it had drained completely, pumps eventually tripped and the board had no power, a sparky will be back to inspect
MSA-DTWD | WA5378559 | 1 | Equans Mechanical Services Australia | Ground - Aircon to classrooms - Aircon not working again | Air Conditioning | Room Air Conditioners | 4483.48 | Pass | Fail | 0 | 7 | 1206 | 2022-04-20 15:50 | 2022-04-21 17:00 | 2022-04-21 09:00 | 2022-04-21 17:00 | 2022-06-10 15:00 |  | WACCES | Gathered required parts and consumables as per quotation removed old and replace with new parts. Completed test operations all ok cleaned up and completed paperwork and returned all cylinders back to supplier and disposed of all rubbish.
MSA-DTWD | WA5460176 | 3 | AWB Co. | Kitchen - Lights over stove and deep friers not working/flashing | Electrical | General Electrical | 1221.49 | Pass | Fail | 0 | 7 | 1205 | 2022-05-18 11:44 | 2022-05-25 17:00 | 2022-05-23 10:00 | 2022-05-25 17:00 | 2022-07-12 15:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed. Installed x3 led panels. Two will be left for john as ceiling is giving way and needs attention so no lights will be installed untill further notice. Job completed
MSA-DTWD | WA5037825 | 0 | ACTION GLASS & ALUMINIUM | Room C46 - glass door has been smashed | Glazing | Door Glass | 2540.8 | Pass | Fail | 0 | 7 | 1203.25 | 2022-01-17 08:04 | 2022-01-17 10:04 | 2022-01-17 09:00 | 2022-01-17 12:04 | 2022-03-08 12:15 |  |  | ATTENDED SITE REGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-990 X 745AND CLEANED UP BROKEN MIRRORS (MEASURED FOR NEW MIRRORS FOR ORDER WA5086917)RETURNED LATER DATESUPPLIED & FIT 8 NEW MIRRORS6MM VINYL SAFETY BACK MIRRORS8-900 X 800POLISHED EDGESPLUS MIRROR CLIPS2 MEN REQUIRED
MSA-DTAG | WA5462230 | 3 | Midolo Building Services | Outside - Cable for masting flag has been cut - unable to mast National flag | Building | General Building | 1431.05 | Fail | Fail | 2 | 9 | 1203 | 2022-05-19 12:42 | 2022-05-26 17:00 | 2022-06-07 11:30 | 2022-05-26 17:00 | 2022-07-27 14:30 |  | WACCES & WCAPPR | new cable & fixings etc. installed
MSA-DTAG | WA6257209 | 3 | Australian HVAC Services Pty. Ltd. | Custody staff kitchen - A/C ceiling vent is damaged | Air Conditioning | Building HVAC Maintenance (Major Plant) | 842.52 | Pass | Fail | -1 | 6 | 1202.8167 | 2022-11-24 12:52 | 2022-12-01 17:00 | 2022-11-25 08:00 | 2022-12-01 17:00 | 2023-01-14 10:49 |  | WACCES & WCAPPR | Oscar Holil (14/01/2023) - Work NotePicked up parts. Arrived on site and spoke to site representative about the works taking place. Gained access to detention security kitchen and moved all relevant tools and materials to the workspace. Removed old supply air grille and installed new grille. Cleaned ceiling and painted as required. Removed all materials, tools and debris from site.
MSA-DTWD | WA5203039 | 2 | Precise Air Group | B block - B45 - see details | Air Conditioning | Room Air Conditioners | 3471.4 | Pass | Fail | 0 | 7 | 1202.4 | 2022-03-03 10:09 | 2022-03-09 17:00 | 2022-03-08 07:30 | 2022-03-09 17:00 | 2022-04-27 09:54 |  |  | Arrived on site and confirmed job with site contact.2. Isolated chiller and removed failed fuses and wiring.3. Cleaned panel and removed as much burn marks as possible.4. Installed new wiring cable and mounted new breakers.5. Wired in new each fan with its own individual breaker.6. Confirmed operation of each fan individually and then together at 50% then 100%.7. Recorded amps for each fan and found no issues.8. Returned chiller to Auto and packed up site.
MSA-DCA | WA5174780 | 0 | Automatic Fire Protection (ARA) | Ground Floor - Fire Panel - alarming in gallery 1 -L2S87 | Fire Protection Services | Fire Protection - Monitor System | 651.135 | Pass | Fail | 0 | 7 | 1201.75 | 2022-02-21 08:39 | 2022-02-21 10:39 | 2022-02-21 09:45 | 2022-02-21 12:39 | 2022-04-12 11:30 |  | WCAPPR | 21/2/22 JNL2 S87 in maintenance fault. Located on ground floor in gallery 1 next to void however site do not want it to be replaced until artwork is removed from area. Site to advise when to return.11/4 KS GAAttended site and removed old faulty detector and fitted new checked AV now normal de isolated and left normal.
MSA-DTWD | WA5384093 | 3 | AWB Co. | Office 2-40 - IT Office - Lighting Sensor failed | Electrical | Lighting, Internal | 733.2 | Pass | Fail | 0 | 7 | 1201.5 | 2022-04-28 09:46 | 2022-05-05 17:00 | 2022-05-02 07:00 | 2022-05-05 17:00 | 2022-06-21 08:30 |  | WACCES & WCAPPR | Attended site signed in GSA completed. Installed new sensor in IT office and programmed by Sherlock electric programming company tested and commissioned all lighting is now operational.** job completed**
MSA-DTWD | WA6256709 | 0 | SCAVENGER SUPPLIES PTY LTD | Evacuation fire alarm going off - Site don't know where it is coming | Fire Protection Services | Fire Protection - Monitor System | 258.87 | Pass | Fail | 0 | 7 | 1201.2 | 2022-11-24 08:17 | 2022-11-24 10:17 | 2022-11-24 09:00 | 2022-11-24 12:17 | 2023-01-13 10:12 |  | WACCES | 24/11/22 - INITIAL ATTENDANCE - FURTHER WORKS REQUIRED. JOB REQUIRES FURTHER TIME. 20/12/22-QUOTE SENT TO ERIC REEDMAN FOR UPGRADE TO SYSTEM13/1/23 - As per email attached from Eric Reedman - this claim to be closed off and separate RCT's are issued for BRAF to install new system.
MSA-DFES | WA5311672 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | FF Dorm 4 and Gym - see details below | Electrical | Lighting, Internal | 993.56 | Pass | Fail | 0 | 7 | 1199.25 | 2022-04-11 07:58 | 2022-04-13 17:00 | 2022-04-12 10:30 | 2022-04-13 17:00 | 2022-06-01 09:45 |  | WACCES | Continued work on site at 0800 to replace 4 x light fittings with LED battens in gym. Replaced & reenergised fittings, informed staff and left site at 0945.
MSA-DFES | WA5971483 | 2 | Anvil Doors | Engine room - Rear garage door, door lifting bracket bent and loose. | Building | Automatic Doors | 4169 | Pass | Fail | 0 | 7 | 1184.5 | 2022-09-20 14:27 | 2022-09-23 17:00 | 2022-09-21 07:30 | 2022-09-23 17:00 | 2022-11-09 16:00 |  |  | Door #4- motor replacement and drive train required with new manual release ,hockey stick etc. Limits switch in controller not functioningproperly and E-Stop button,these will definitely need replacing. See photos of controller panel.Works completed on 3.1.22.-- Long delay in replacement motor to arrive in stockWorks completed on 9.11.2022
MSA-MRWA | WA5287806 | 2 | SONTEC WA PTY LTD | Geuterbruck Box offline meaning no visibility between staff at TOC and RNOC | Security | Security Management System | 1460.25 | Pass | Fail | 0 | 7 | 1180.8 | 2022-03-22 16:12 | 2022-03-25 17:00 | 2022-03-24 08:42 | 2022-03-25 17:00 | 2022-05-12 13:30 |  |  | 24/3/22 - Dean SimpsonNo visibility between TOC and RNOC.Return visit required with extra tech.25/3/22 - Dylan Parslow, Dean SimpsonTested recorder at RNOC.Hardware fault on recorder, recommend repair or replacement.BRAF submitted.29/4/22 - Dylan Parslow, Joshua ParkIP details provided are incorrect.Correct details required from IT Dept.2/5/22 - Dylan Parslow, Joshua ParkReinstalled recorder after repair.Still awaiting IP Address.Identified one camera locally not working. Recommend replacement.12/5/22 - Dylan Parslow, Joshua ParkProgrammed and connected CCTV recorder for RNOC.Tested connection to TOC.All working and online.
MSA-DTWD | WA6249670 | 2 | Equans Mechanical Services Australia | Exhaust fan in roof very noisy, making classroom delivery difficult | Air Conditioning | Building HVAC Maintenance (Major Plant) | 4339.9975 | Pass | Fail | 0 | 7 | 1180 | 2022-11-21 13:38 | 2022-11-24 17:00 | 2022-11-23 08:00 | 2022-11-24 17:00 | 2023-01-11 12:00 |  | WACCES & WCAPPR | Found the workshop exhaust fan near classroom B61 noise. Need a second person to access the roof as it is working at heights. Will return 24/11/2022 first thing in the morning with second person .Returned earlier then expected on the 23rd. Accessed the exhaust fan on B block roof , found the main pulley and fan bearings need replacing , unit badly corroded , will drop of for quote to repair .Dennis asked us to look at a evap that was over flowing with water on A block, accessed the roof and adjusted the water float . Did job because there was two of us on site .24/11/2022: Dropped exhaust assembly off to get quote to repair.3/1/2023 : Picked up parts from the workshop 11/1/23: fitted the exhaust fan to the roof.
MSA-DFES | WA6257450 | 2 | Protek 24/7 Building & Maintenance | Front grate outside the station has rusted through - notes | Building | Materials | 995.53 | Pass | Fail | 0 | 7 | 1179.5 | 2022-11-24 15:34 | 2022-11-29 17:00 | 2022-11-28 10:15 | 2022-11-29 17:00 | 2023-01-16 13:45 |  | WACCES | Option 1 - Replace damaged grate only ? Remove and dispose of 1x damaged grate piece? Supply and install 1x new Class D grate to drain
MSA-DTWD | WA5053086 | 1 | Equans Mechanical Services Australia | A Block - Ground - Western end evap aircon- Not cooling | Air Conditioning | Room Air Conditioners | 1158.76 | Fail | Fail | 0 | 7 | 1178.5 | 2022-01-18 12:58 | 2022-01-19 17:00 | 2022-01-20 12:00 | 2022-01-19 17:00 | 2022-03-10 14:30 |  |  | Picked up required parts, Arrived on site signed in, checked in with Dennis. Assisted with working at heights by James replaced pump on North evaporative unit. Dennis asked to check all units while on a block. Replaced sump dump kit also on a another unit a solenoid valve from van stock. Checked operation on all OK. Cleaned up and completed paperwork.
MSA-DTWD | WA5385835 | 3 | Equans Mechanical Services Australia | E & C Block - AHUC3 & AHUE1 both showing fan status fault | Air Conditioning | Room Air Conditioners | 1307.43 | Pass | Fail | -1 | 6 | 1178.5 | 2022-04-29 12:48 | 2022-05-06 17:00 | 2022-05-02 08:00 | 2022-05-06 17:00 | 2022-06-20 10:30 |  |  | Found C block AHU 3 running OK. Found A block AHU 1 realigned the pulleys and motor, test ran ok
MSA-DTWD | WA5199545 | 2 | SCAVENGER SUPPLIES PTY LTD | Western Entry - Fire panel showing Zone fault after evacuation drill | Fire Protection Services | Fire Protection - Monitor System | 2881.34 | Pass | Fail | 0 | 7 | 1178.5 | 2022-03-01 10:09 | 2022-03-04 17:00 | 2022-03-02 07:00 | 2022-03-04 17:00 | 2022-04-20 09:30 |  |  | 02/03/2022- 7am to 8am-call out-1 hour onsitechecking if further work required-10/03/2022-INVESTIGATION recommended full upgrade of system as parts not available for current system.BRAF- REQUIRED awaiting quotation.08/04/2022-BRAF SUBMITTED11/04/2022-braf approved
MSA-DCA | WA5697569 | 1 | WESTCOAST CONSTRUCTION & DEMOLITION | Frances street roof level-roof leak | Roofing | Metal Roofing | 2449.62 | Pass | Fail | 0 | 7 | 1178.2333 | 2022-08-09 10:22 | 2022-08-10 17:00 | 2022-08-09 10:33 | 2022-08-10 17:00 | 2022-09-27 12:47 |  |  | 2x technicians attended site 23/09/2022accessed both upper level roof and lower level roof. Applied Silicon to potential leak spots.
MSA-DCA | WA4994782 | 1 | Protek 24/7 Building & Maintenance | Male Toilet - ceiling leak - minor leak | Building | General Building | 1331.225 | Pass | Fail | 0 | 7 | 1177.75 | 2022-01-10 07:22 | 2022-01-10 17:00 | 2022-01-10 09:00 | 2022-01-10 17:00 | 2022-02-28 10:45 |  | WACCES | Repair ceiling leak in Male toilet
MSA-DTAG | WA5792446 | 3 | Seme Solutions Pty Ltd | CCTV1 (50) Sally port (6) not working | Security | CCTV Surveillance | 1592.78 | Fail | Fail | 0 | 7 | 1177 | 2022-08-23 14:21 | 2022-08-30 17:00 | 2022-09-02 12:30 | 2022-08-30 17:00 | 2022-10-21 13:30 |  | WACCES | cabled and installed new IP camera in sallyport (6) (cam 50), confirmed online and operational.
MSA-DFES | WA6301153 | 2 | Protek 24/7 Building & Maintenance | Ground - Front Entrance - Paving (walkway) - uneven pavers causing a trip hazard | Paving & Roadworks | Paving | 2295.44 | Pass | Fail | 0 | 7 | 1176.25 | 2022-12-02 14:26 | 2022-12-07 17:00 | 2022-12-06 09:15 | 2022-12-07 17:00 | 2023-01-24 09:30 |  | WACCES | ? Repaired locations where possible to minimise trip hazards? Carried out site measure to confirm materials required? Remove and dispose of damaged pavers from areas? Use quick-cut saw to release bond between pavers and concrete slab as required? Level sand under pavers and reinstate to correct levels? Replace the haunching along garden beds? Supply and install new replacement pavers as required? Reinstate existing pavers to be level with surrounding ground cover? Clean site & Demobilise
MSA-DFES | WA5680094 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Year yard ground-lights are tripping circuit breaker/rcd | Electrical | Lighting, Internal | 723.75 | Pass | Fail | 0 | 7 | 1175.25 | 2022-07-27 09:40 | 2022-08-01 17:00 | 2022-08-01 15:15 | 2022-08-01 17:00 | 2022-09-19 14:30 |  | WACCES | Replaced two lights on lighting tower. Overrode timer and tested all operating correctly. Cleaned up and signed out
MSA-DTWD | WA5226830 | 2 | CONNECT SECURITY SYSTEMS | E-Block - Various areas - Alarm faulting intermittently – various issues. Need to have system analys | Security | Monitoring | 2664.54 | Pass | Fail | 0 | 7 | 1175.1333 | 2022-03-14 13:29 | 2022-03-17 17:00 | 2022-03-16 20:00 | 2022-03-17 17:00 | 2022-05-04 19:08 |  |  | Attended 16/3/2022, 6/4/22 and 4/5/22
MSA-DFES | WA5570720 | 2 | Australian HVAC Services Pty. Ltd. | BMS keeps showing chiller fault HVAC to attend | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1897.67 | Pass | Fail | 0 | 7 | 1175.1286 | 2022-06-28 13:47 | 2022-07-01 17:00 | 2022-06-30 11:22 | 2022-07-01 17:00 | 2022-08-18 10:30 |  |  | Attended site with mizco and accessed chilled water plant. Replaced the water temperature sensors on the chillers as per scope. Calibrated new sensors and confirmed correct operation.Cleared debris from site and completed job.
MSA-DTWD | WA5101314 | 1 | ECO PLUMBING AND GAS PTY LTD | E.16 - Female Student Toilets - Faulty flush buttons in cubicles 2 & 3 | Plumbing & Drainage | Toilets/Cisterns | 1688.925 | Pass | Fail | 0 | 7 | 1171.25 | 2022-02-03 10:57 | 2022-02-04 17:00 | 2022-02-03 16:00 | 2022-02-04 17:00 | 2022-03-24 11:15 |  |  | Repalced 2x cisterns and flush buttons
MSA-DTWD | WA5827735 | 1 | AWB Co. | D44 Barista Training Room - LED Strip Lighting won’t turn off - See notes below | Electrical | Lighting, Internal | 1539.925 | Pass | Fail | 0 | 7 | 1156.5 | 2022-09-01 12:41 | 2022-09-02 17:00 | 2022-09-02 06:00 | 2022-09-02 17:00 | 2022-10-20 10:30 |  | WACCES & WCAPPR | Attended site and signed in. Completed jsa. Replaced switch in barista and commissioned to installation. All okay. Signed out. Job complete
MSA-DFES | WA6393045 | 3 | Australian HVAC Services Pty. Ltd. | ground-duty room-air con issues - see notes | Air Conditioning | Room Air Conditioners | 1485.6 | Pass | Fail | -1 | 6 | 1156.5 | 2022-12-28 08:50 | 2023-01-05 17:00 | 2022-12-30 12:00 | 2023-01-05 17:00 | 2023-02-16 16:30 |  | WACCES
MSA-DTWD | WA5603332 | 3 | AWB Co. | Level 1 - Verandah - Repair damaged verandah column feet | Building | General Building | 2282.19 | Pass | Fail | -1 | 6 | 1156.25 | 2022-07-12 09:52 | 2022-07-19 17:00 | 2022-07-15 10:45 | 2022-07-19 17:00 | 2022-09-01 15:00 |  |  | Attend site and supply quote as requested
MSA-DFES | WA4992258 | 2 | Protek 24/7 Building & Maintenance | Female Toilets - All Female toilet doors have damaged | Building | Doors | 3051.88 | Pass | Fail | -1 | 6 | 1156 | 2022-01-06 09:12 | 2022-01-11 17:00 | 2022-01-07 12:00 | 2022-01-11 17:00 | 2022-02-24 16:00 |  | WACCES | Water damaged doors to female toilets
MSA-DFES | WA5053259 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - issues with our charging point - see notes below | Electrical | General Electrical | 818.445 | Pass | Fail | 0 | 7 | 1156 | 2022-01-18 14:38 | 2022-01-21 17:00 | 2022-01-19 13:45 | 2022-01-21 17:00 | 2022-03-08 17:45 |  | WACCES | Arrived onsite at 14:30 to install new cable run for LV charger to reduce volt drop on charging point. Installed and tested and left site at 17:45
MSA-DCA | WA5390323 | 1 | EQUANS Mechanical Services (WA) Pty Limited | HBRC - Level 1 - Plant Room - Chiller 2 is in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 240.7 | Fail | Fail | 1 | 8 | 1155.0167 | 2022-05-02 11:52 | 2022-05-03 17:00 | 2022-05-11 07:00 | 2022-05-03 17:00 | 2022-06-28 10:01 |  |  | Attended site gained access and carried out inspection of CH-2 due to reported fault. Chiller internal control indicated stage 1 compressor to have active high pressure fault. On inspection manual trip switches were not active. Confirmed operation of condenser fans motors. Reset fault and normal operation resumed with chiller. Equipment will be kept under observation during site PM visit for further faults. Normal operation has restored.
MSA-DTWD | WA6518838 | 1 | Equans Mechanical Services Australia | S Block - chiller not working – will not reset | Air Conditioning | Room Air Conditioners |  | Pass | Fail | 0 | 7 | 1154.2833 | 2023-01-25 11:11 | 2023-01-27 17:00 | 2023-01-25 13:44 | 2023-01-27 17:00 | 2023-03-14 16:01
MSA-DTAG | WA5792439 | 3 | Seme Solutions Pty Ltd | CCTV1 (3) front entry inside foyer 3 not working | Security | CCTV Surveillance | 1595.44 | Fail | Fail | 0 | 7 | 1154 | 2022-08-23 14:19 | 2022-08-30 17:00 | 2022-09-02 13:30 | 2022-08-30 17:00 | 2022-10-20 15:30 |  | WCAPPR | installed new fisheye camera, unable to program view to change from overview to double panorama due to obsolete VMS software. Camera online and operational.
MSA-DTWD | WA5692152 | 2 | Protek 24/7 Building & Maintenance | 9G15 Workroom - Water leak down west wall | Building | Internal Walls | 1589.95 | Pass | Fail | -1 | 6 | 1152.25 | 2022-08-03 10:52 | 2022-08-08 17:00 | 2022-08-04 13:30 | 2022-08-08 17:00 | 2022-09-21 13:45 |  | WACCES | Remove and dispose off damaged flashings Supply and install new flashings and fixings
MSA-DTWD | WA6190703 | 1 | SCAVENGER SUPPLIES PTY LTD | Block 10 - Ground Floor - External wall north wing - EWIS alarm speaker has fallen off wall | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 404.53 | Pass | Fail | 0 | 7 | 1152 | 2022-11-16 10:04 | 2022-11-17 17:00 | 2022-11-16 12:00 | 2022-11-17 17:00 | 2023-01-03 12:00 |  | WACCES | 17/11/2022 PRIORITY 1 CALL OUT-ATTENDED BY KR17/11/2022 LABOUR ONSITE-1.5 HOURS-KRIMAGES & DOCS UPLOADED22/11/2022-PARTS ORDERED 22/11/22 -ashton SC-7893SCHEDULED 3/1/23 - COMPLETED
MSA-DTWD | WA5977309 | 2 | AWB Co. | F-Block & Assembly area 1-Outdoor light faulty-see notes | Electrical | Lighting, Internal | 3416.53 | Pass | Fail | 0 | 7 | 1151.5 | 2022-09-27 15:31 | 2022-09-30 17:00 | 2022-09-30 13:00 | 2022-09-30 17:00 | 2022-11-17 12:30 |  | WACCES & WCAPPR | Attended site and signed in. Completed jsa. Spoke to fm about job. Met ground scanner guy on site. Ground scanner scanned ground and traced cables. Put scanner on active to try and find break in ground. Located area where break was likely present. Dug up conduit around pole. Split cable and tested to see where fault was located. Replaced cable. Found j box with join in underground. Fault in j box. Tested cable each side of j box and fault was there. Went to wholesaler to pick up parts for job. Returned to site. Put couplings and corrie on where cables are coming up to the pit. Drilled holes in bottom of pit and brought up corrie. Fit off into junction box. Back filled the whole after pit had been placed in. Made pit level and re planted plants we had to remove. Cleaned up work area. Re energised circuit. All lights are now working. Took picture. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5674493 | 2 | Protek 24/7 Building & Maintenance | Level 2 - Middar - Leak from broken seal | Building | Windows | 1789.8 | Pass | Fail | -1 | 6 | 1151 | 2022-07-21 12:10 | 2022-07-26 17:00 | 2022-07-22 11:30 | 2022-07-26 17:00 | 2022-09-08 10:30 |  | WACCES & WCAPPR | ? Receive boom-lift, setup exclusion zone & warning signs for pedestrians? Inspect exterior of facade windows and confirm all potential leak locations? Clean & Re-seal above windows where leaks found? Water-test once works complete
MSA-DFES | WA4991687 | 3 | Protek 24/7 Building & Maintenance | Appliance Garage - ceiling - corridor - see details below | Building | General Building | 920.23 | Pass | Fail | -1 | 6 | 1149.5 | 2022-01-05 10:59 | 2022-01-12 17:00 | 2022-01-05 14:45 | 2022-01-12 17:00 | 2022-02-22 12:15 |  |  | Replace Bird deterrent bird spikes
MSA-DFES | WA5534390 | 2 | Protek 24/7 Building & Maintenance | Level 1 - Reception Area - Celling is sagging - See notes below | Building | Ceiling | 968.57 | Pass | Fail | 0 | 7 | 1149.5 | 2022-06-16 09:49 | 2022-06-21 17:00 | 2022-06-21 12:00 | 2022-06-21 17:00 | 2022-08-08 09:30 |  | WACCES & WCAPPR | Installation of 4 support plates
MSA-DTAG | WA6389091 | 3 | Sapio Pty Ltd | Level 23 security workstations, database wont display first and last name of users programmed in | Security | Security Management System | 269 | Pass | Fail | -1 | 6 | 1137 | 2022-12-21 13:24 | 2022-12-30 17:00 | 2022-12-22 07:30 | 2022-12-30 17:00 | 2023-02-07 16:30 |  |  | Rectification of Pacom licensing errors.
MSA-DTWD | WA5735723 | 2 | Protek 24/7 Building & Maintenance | L1 Walk way between block 1 and 9-Posts from hand rail to walkway roof damaged | Carpentry | Staircases, Balustrades and Handrails | 3922.745 | Pass | Fail | 0 | 6 | 1134 | 2022-08-16 14:56 | 2022-08-19 17:00 | 2022-08-17 07:00 | 2022-08-19 17:00 | 2022-10-03 13:00 |  | WACCES | Carry out lead testing on paint before works commenceCreate exclusion zone using solid barriers for either end of walkway Erect scaffolding from ground level in exclusion zoneRemove and dispose of dilapidated posts (To be done one at a time while propping up roof sections) Supply and install 7x new timber posts and fix to supportsPrepare and paint timbers to suit currently installed timbers
MSA-DFES | WA5478830 | 1 | Protek 24/7 Building & Maintenance | Storm water drain/Soakwell - flooding0 drains to be cleaned out | Building | General Building | 1913.08 | Pass | Fail | 0 | 7 | 1133 | 2022-05-26 14:00 | 2022-05-27 17:00 | 2022-05-27 07:00 | 2022-05-27 17:00 | 2022-07-13 12:00 |  | WACCES | Cleaned soak well drains
MSA-DTWD | WA5086756 | 3 | Protek 24/7 Building & Maintenance | Gate 10 - damaged - contractor onsite | Building | Steel Fencing & Gates | 2178.83 | Pass | Fail | -1 | 5 | 1129.9167 | 2022-01-21 12:33 | 2022-01-31 17:00 | 2022-01-21 12:35 | 2022-01-31 17:00 | 2022-03-09 14:30 |  | WACCES | Replace Damaged gate
MSA-DTWD | WA5401046 | 1 | Techworks Electrical | Walkway Lights - lights not working | Electrical | General Electrical | 19448.09 | Pass | Fail | 0 | 7 | 1129.4167 | 2022-05-10 15:14 | 2022-05-11 17:00 | 2022-05-11 06:00 | 2022-05-11 17:00 | 2022-06-27 07:25 |  |  | Reviewed light poles, found light poles to be rusted out and not working. Light pole numbers below that require replacing Light pole numbers:68, 67, 66, 65, 64, 63, 62, 61, 60, 59, 58, 57, 56, 55
MSA-DTWD | WA5689340 | 1 | Australian Airconditioning Services Pty Ltd | Level 5 - Ground and first south side - A/C 11 not working | Air Conditioning | Room Air Conditioners | 6984.39 | Pass | Fail | 0 | 7 | 1128 | 2022-08-02 12:10 | 2022-08-03 17:00 | 2022-08-03 10:30 | 2022-08-03 17:00 | 2022-09-19 10:30 |  | WACCES | Removed old compressor and installed new compressor. Found leak on distributor line and Schrader during pressure test. Replaced Schrader and fixed leak.Replaced contactor, overload and crankcase heaterEvacuated and charged unit. Test ran operation. All ok
MSA-DCA | WA6357222 | 2 | Precise Air Group | West Australia Opera Office - Aircon is permanently too cold | Air Conditioning | Ducted Split System | 1036.945 | Pass | Fail | 0 | 7 | 1128 | 2022-12-05 11:48 | 2022-12-08 17:00 | 2022-12-07 07:30 | 2022-12-08 17:00 | 2023-01-23 07:30 |  |  | Attended site and signed in. Accessed office on level 3 and spoke to employee. Found there was no airflow or temperature control for the area. Accessed roof space and checked ductwork found there was no way to change airflow there either. Recommend installing inline dampers to ductwork to lessen the airflow to the office. Quote to follow.Parts have been ordered. Install provisionally being booked for last week of FebruaryAll dampers will be in stock on 10/2/23 and schedule for install Monday the 13/2/23Installed and completed
MSA-DTWD | WA5067741 | 2 | Protek 24/7 Building & Maintenance | Gate 9 - Perimeter fence - broken gate | Building | General Building | 1348.75 | Pass | Fail | 0 | 6 | 1127.75 | 2022-01-19 10:51 | 2022-01-24 17:00 | 2022-01-21 13:15 | 2022-01-24 17:00 | 2022-03-09 13:00 |  | WACCES | Repair broken gate
MSA-DFES | WA5306310 | 2 | Protek 24/7 Building & Maintenance | Main Administration - Ground - Front Door & Male Toilet - | Building | General Building | 357.51 | Pass | Fail | 0 | 6 | 1126 | 2022-04-06 12:06 | 2022-04-11 17:00 | 2022-04-08 14:45 | 2022-04-11 17:00 | 2022-05-25 12:45 |  | WACCES | Replace broken door handles in Main Entrance and Male toilet
MSA-DCA | WA5839215 | 1 | Precise Air Group | AHU8 - AHU8 Vent motor faulty, tripping on over-current | Air Conditioning | Room Air Conditioners | 1272.67 | Pass | Fail | 0 | 6 | 1124.1667 | 2022-09-09 10:25 | 2022-09-12 17:00 | 2022-09-09 12:59 | 2022-09-12 17:00 | 2022-10-26 09:09 |  |  | found fan motor seized, required to be remvoed and repalced as a result.installed new motor, test operated
MSA-DCA | WA5010146 | 1 | Protek 24/7 Building & Maintenance | Hacket Hall - city room stairs - Paving repairs to external stairs outside Hackett Hall | Paving & Roadworks | Paving | 404 | Pass | Fail | 0 | 7 | 1123.75 | 2022-01-12 10:26 | 2022-01-13 17:00 | 2022-01-12 13:00 | 2022-01-13 17:00 | 2022-02-28 08:45 |  | WACCES | Repair broken Paving Inlay
MSA-DTAG | WA5978938 | 3 | Australian HVAC Services Pty. Ltd. | Ground Floor - Library - Air conditioning is too warm | Air Conditioning | Room Air Conditioners | 6722.89 | Pass | Fail | -1 | 6 | 1109 | 2022-09-28 14:22 | 2022-10-05 17:00 | 2022-09-29 07:00 | 2022-10-05 17:00 | 2022-11-14 12:00 |  |  | Attend site early morning. Meet with scaffolding contractors and supervise dismantling of scaffolding. Clean work area. Compile report of works completed.
MSA-DTWD | WA5216544 | 2 | M Construction (WA) | U011 - east facing exit door - requires attention faulty/damaged - made out of wood | Building | Doors | 1880.03 | Pass | Fail | -1 | 6 | 1107.5 | 2022-03-11 11:04 | 2022-03-16 17:00 | 2022-03-11 11:30 | 2022-03-16 17:00 | 2022-04-26 15:00 |  | WACCES | Installed new solid core door and painted to match. Re-used all door hardware and replaced new weather seal.
MSA-DTWD | WA6130373 | 1 | Equans Mechanical Services Australia | Kitchen-Freezer running warmer than required-see notes | Refrigeration | Freezers | 1066.6275 | Fail | Fail | 0 | 7 | 1105.75 | 2022-10-28 11:33 | 2022-10-31 17:00 | 2022-11-03 08:45 | 2022-10-31 17:00 | 2022-12-19 10:30 |  | WCAPPR | 3/11/22: Checked the freezer found the system running down to -18.5 & Coming on at -15. Will need to empty the freezer as it holds a lot of food, this has been arranged to be down on the 15th of December when the canteen closes for Christmas. 15/12/22: Returned to check the system for gas leaks, freezer not quite empty , picked up parts required for the job 19/12/22: Leak tested, repaired leak on the condenser, vaced out regased test ran all OK
MSA-DTAG | WA5163508 | 0 | Australian HVAC Services Pty. Ltd. | Court room 2 - air con has stopped working | Air Conditioning | Room Air Conditioners | 1430.57 | Pass | Fail | 0 | 7 | 1102.5 | 2022-02-18 09:44 | 2022-02-18 11:44 | 2022-02-18 10:00 | 2022-02-18 13:44 | 2022-04-05 08:30 |  |  | Attend site with icon logic. Access court 2 plantroom. Isolate FCU 4 and disconnect wiring to airflow switch. Unbolt failed airflow switch and install new. Connect wiring. Deisolate FCU 4 and set up and commission flow switch. Flow switch working as normal. Test operation of chilled water valve, working as normal.
MSA-DTWD | WA6415170 | 2 | Equans Mechanical Services Australia | Low air flow and cooling into room 341 - Adjusted settings which did not change airflow or temp | Air Conditioning | Room Air Conditioners | 579.96 | Pass | Fail | 0 | 6 | 1100.5 | 2023-01-11 13:33 | 2023-01-16 17:00 | 2023-01-13 14:00 | 2023-01-16 17:00 | 2023-02-28 10:30
MSA-DFES | WA5295586 | 2 | Go Doors | Front gate - see notes below | Building | Security Doors | 2643.55 | Pass | Fail | 0 | 6 | 1088.75 | 2022-03-29 16:13 | 2022-04-01 17:00 | 2022-04-01 07:15 | 2022-04-01 17:00 | 2022-05-16 16:00 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5417231 | 2 | AWB Co. | Thicknesser is not working | Electrical | General Electrical | 3104.52 | Pass | Fail | 0 | 6 | 1086 | 2022-05-13 11:21 | 2022-05-18 17:00 | 2022-05-16 09:00 | 2022-05-18 17:00 | 2022-06-30 15:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Located work area. Double checked parts we needed to complete job. Went to wholesaler to get parts. Returned to site. Located EWP guy, got ewp dropped off where we needed it. Set up work area with cones, etc. De energised circuit we had to remove. Took cabling out of isolator and pulled up to roof and coiled up neatly, cable tied to roof. Ran cable from board to steel beam where PowerPoint is going. Has to get lecturers to move a machine so we could access all areas for cable tieing as there were a lot of overhead obstacles. Fit off PowerPoint on steel beam. Removed duct entering switchboard and ran new cable down. Made sure switchboard was isolated. Connected up 3 phase rcd. Put board back together. Tested. Got lecturer to come and make sure everything is working as it should and that machine is rotating the correct way. Everything working as intended. Cleaned and packed up. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5407921 | 3 | AWB Co. | Ground -6B Metal Fab 2 workshop- Numerous lights not working | Electrical | General Electrical | 1669.27 | Pass | Fail | 0 | 6 | 1085.5 | 2022-05-11 15:05 | 2022-05-18 17:00 | 2022-05-16 10:00 | 2022-05-18 17:00 | 2022-06-30 15:30 |  | WACCES & WCAPPR | Attended site signed in jsa completed. Used ewp to removed all old lights in class x6 installed new chain and secured onto beams for new lights. installed flex and x6 new led batterns. Tested and working correctly.job completed
MSA-DTWD | WA5699668 | 2 | Protek 24/7 Building & Maintenance | Roof Leak - Water leaking at AC cassette closest to photocopier | Roofing | Metal Roofing | 1206.78 | Fail | Fail | 0 | 7 | 1085 | 2022-08-10 11:06 | 2022-08-15 17:00 | 2022-08-16 10:00 | 2022-08-15 17:00 | 2022-09-30 15:00 |  | WACCES | Supply and install colorbond flashing & fixings from flume pipe to gutter line Complete water-test once works complete
MSA-DFES | WA5985845 | 1 | Protek 24/7 Building & Maintenance | Board up old fire station one of the engine base door | Carpentry | Materials | 1878.77 | Pass | Fail | 0 | 6 | 1083.25 | 2022-10-01 09:07 | 2022-10-03 17:00 | 2022-10-01 10:00 | 2022-10-03 17:00 | 2022-11-15 13:15 |  | WACCES | Remove patch, cut out section of door, cut new timber to size and shape, oil and varnish sanding between coats,Bog door from glass removal., sand, undercoat 1x glossTint glass, paint door
MSA-DFES | WA5994347 | 3 | Protek 24/7 Building & Maintenance | Multiple Levels - Complex Building prop (cube) - Several Water Leaks - See Notes Below | Plumbing & Drainage | Water | 5298.92 | Pass | Fail | -1 | 6 | 1082.25 | 2022-10-05 15:34 | 2022-10-12 17:00 | 2022-10-07 08:45 | 2022-10-12 17:00 | 2022-11-21 11:00 |  | WACCES | ? Remove and dispose of dilapidated zinc flashings to 'roof' of container stack? Clean surfaces and prepare containers for new flashings? Supply and install new flashings and seal area
MSA-DTWD | WA5215720 | 2 | Water2water Pty Ltd | Outside (East side) - Water fountain does not appear to be cooling - see notes | Plumbing & Drainage | Water | 3394.8425 | Pass | Fail | 0 | 6 | 1082 | 2022-03-10 15:42 | 2022-03-15 17:00 | 2022-03-14 09:00 | 2022-03-15 17:00 | 2022-04-28 11:00 |  |  | 2 service techs! Removed old unit and replaced with new fountain!!!! Mounted new unit to the wall. Checked under pressure!
MSA-DTWD | WA6229329 | 1 | Australian Airconditioning Services Pty Ltd | Toilets - Toilet exhaust fans not working | Air Conditioning | Materials | 1662.06 | Pass | Fail | 0 | 6 | 1081.5 | 2022-11-18 09:38 | 2022-11-21 17:00 | 2022-11-21 07:30 | 2022-11-21 17:00 | 2023-01-05 09:00 |  | WACCES | Replaced faulty motor on TEF block 6. Tested unit. Fully operational.
MSA-MRWA | WA5562812 | 1 | AWB Co. | North End - faulty lighting - following power outage | Electrical | Lighting, Internal | 622.22 | Pass | Fail | 0 | 6 | 1081 | 2022-06-20 10:07 | 2022-06-21 17:00 | 2022-06-21 12:30 | 2022-06-21 17:00 | 2022-08-05 13:30 |  |  | Attended site and signed in. Completed JSA. Located dynalite system. Began fault finding. Carried out repairs to control modules and added new light fittings to the system to work with current setups. Tested all okay. Notified staff. Signed out. Job completeAdvised close costs to date
MSA-DFES | WA5677379 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Stores - Roof leak from skylight out the front of the stores entry | Roofing | Metal Roofing | 1000 | Pass | Fail | 0 | 6 | 1081 | 2022-07-25 14:16 | 2022-07-26 17:00 | 2022-07-26 09:00 | 2022-07-26 17:00 | 2022-09-09 10:00 |  | WACCES | Replace skylight sheet
MSA-DFES | WA5677405 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Spray Painters Bay - Roof Leaking from the roof near the chimney about the Spray Booth | Roofing | Metal Roofing | 850.53 | Pass | Fail | 0 | 6 | 1078 | 2022-07-25 14:23 | 2022-07-26 17:00 | 2022-07-26 14:30 | 2022-07-26 17:00 | 2022-09-09 12:30 |  | WACCES | Installed top hat for exhaust
MSA-DFES | WA5677384 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Tool Store (by staircase) - Roof Leaking from the stores roof | Roofing | Metal Roofing | 1287.6 | Pass | Fail | 0 | 6 | 1076.5 | 2022-07-25 14:18 | 2022-07-26 17:00 | 2022-07-26 13:00 | 2022-07-26 17:00 | 2022-09-09 09:30 |  | WACCES | ? Temporarily Remove fixed access ladder & reinstate once works complete - Subcontractor to complete? Remove old screws and silicone from affected roof sheets (x4)? Remove roof sheets to asses issues underneath ? Remove skylight sheets if found underneath raised roof sheets? Reinstate Anti-Con Insulation if required? Reinstall existing roof sheets using cyclone washers and new screws.? Fix adjacent roof sheeting to either side of repaired area using cyclone washers and screws as required? Remove and replace ridge capping with new to suit correct profile of roof sheeting
MSA-DTWD | WA6381856 | 0 | Schneider Electric Australia Pty Ltd | Fire door not locking | Security | Access Control |  | Fail | Fail | 0 | 7 | 1067.1667 | 2022-12-19 15:28 | 2022-12-19 17:28 | 2022-12-20 13:05 | 2022-12-19 19:28 | 2023-02-03 00:15 |  |  | Break glass for door has been reported to have been slightly engaged which resulted in the door unlocking. Site rectified the issue prior to attending. lx new resettable break glass has been provided as a spare.
MSA-DTWD | WA5397034 | 2 | Securex Security Systems & Services | C Block - Wiring to alarm panel cut not working - See notes below | Security | Monitoring | 550 | Pass | Fail | 0 | 6 | 1061.25 | 2022-05-06 12:55 | 2022-05-11 17:00 | 2022-05-10 07:30 | 2022-05-11 17:00 | 2022-06-23 12:45 |  |  | 10/05/2022, 730-900C block has 4 wires cut by electricians during constructions. Cannot gain access to other ends as its a suspended solidceiling. I can see 2 of the 4 cables from the man hole. Unsure of where the lan cable is. Nick will contact the guys whodisconnected it for more information and get them to try to fix what they cut and call us back to power up andcommission26/05/2022, 815-1000The electricians connected all the wires they cut. Need to install new pir cable is ran. Lan is still missing. Electricians willrun new lan.23/06/2022, 1215-1245This job is completed in conjunction with work order WA5548769Tested system after works competed and confirmed ok.
MSA-DTWD | WA5115895 | 1 | Equans Mechanical Services Australia | A/C unit not turning on. | Air Conditioning | Room Air Conditioners | 715.17 | Pass | Fail | 0 | 6 | 1059 | 2022-02-11 09:58 | 2022-02-14 17:00 | 2022-02-14 08:00 | 2022-02-14 17:00 | 2022-03-30 11:00 |  | WACCES | Picked up parts from the supplier, returned to site and fitted to the air-conditioning system, test ran all OK
MSA-DTWD | WA5798442 | 2 | COMMERCIAL PLUMBING AND GAS | Room A 39 - Gas heater faulty | Plumbing & Drainage | Gas | 1220.305 | Pass | Fail | 0 | 6 | 1058.5 | 2022-08-29 14:25 | 2022-09-01 17:00 | 2022-08-30 11:00 | 2022-09-01 17:00 | 2022-10-13 13:30 |  | WACCES | ordered and replaced parts until function restored
MSA-DFES | WA5302978 | 2 | Australian HVAC Services Pty. Ltd. | First Floor - Archive Room - AC-10 in Archive is not operating. The control pad is not working. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1570.02 | Pass | Fail | 0 | 6 | 1058.4833 | 2022-04-04 07:20 | 2022-04-06 17:00 | 2022-04-04 09:00 | 2022-04-06 17:00 | 2022-05-18 11:29 |  | WACCES | Attended service call, checked ac 10 condensing unit and evap unit boards for faults, ok. Tested wall controls & found board faulty, ordered new controlPicked up new parts attended site Installed test ran all working well
MSA-DCA | WA5833983 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 - Plant Room - Reverse Osmosis - Control system has been damaged | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2695 | Pass | Fail | 0 | 6 | 1058.4 | 2022-09-06 12:58 | 2022-09-06 14:58 | 2022-09-06 13:00 | 2022-09-06 16:58 | 2022-10-20 15:24 |  | WACCES | While onsite carrying out upgrade works, there were 2x power surges. RO control box had no power to it. Investigation found RO control box has electrically failed. Disassembled and remove control box.Dropped control box to supplier’s warehouse. Supplier had a refurbished 2nd hand operational control box. Returned to site and fitted control box. Energised power and ran RO system Left system running.Test control box and identify fault. Remove failed electrical component. Supply and install one (1) new Capacitor. Carry out testing of Control Box to confirm correct operation. Current refurbished control boxthat is installed at site will remain in the system. Return repaired control box to site. Ensure system is operational and no faults.
MSA-DTWD | WA6290634 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire detection speakers in b Block emitting hum noise | Fire Protection Services | Fire Protection - Monitor System | 360.18 | Fail | Fail | 0 | 6 | 1058.3333 | 2022-11-28 10:08 | 2022-11-29 17:00 | 2022-11-30 08:00 | 2022-11-29 17:00 | 2023-01-13 10:20 |  | WACCES | 30/11/2022-ATTENDED -BW13/1/23 - As per email attached from Eric Reedman - this claim to be closed off and separate RCT's are issued for BRAF to install new system.
MSA-DFES | WA5417569 | 2 | AWB Co. | Rear Yard - Near Drain - Possible Subsidence | Flooring | Concrete | 2162.5 | Pass | Fail | 0 | 6 | 1056.8167 | 2022-05-13 13:54 | 2022-05-18 17:00 | 2022-05-16 10:30 | 2022-05-18 17:00 | 2022-06-29 11:19 |  |  | Attended site spoke to manager wasn’t sure what the problem was in yard said it’s always been slightly sunken. 3m2 of very slightly sunken asphalt
MSA-DTWD | WA5191646 | 3 | AWB Co. | Outdoor area along the fence line - Clean up asbestos pieces along the fence line | Building | General Building | 1216.5 | Pass | Fail | 0 | 6 | 1056.5 | 2022-02-25 08:12 | 2022-03-04 17:00 | 2022-03-01 09:00 | 2022-03-04 17:00 | 2022-04-14 09:30 |  |  | Graham Coxhill (01/03/2022) - Work NoteAttended site discussed work with John. The garden beds are full of small and medium sized pieces of asbestos from a demolition complete by city of Vincent. Approximately 40-50m of garden bed has been affected and all asbestos is to be removed.
MSA-DTAG | WA5312404 | 1 | Water2water Pty Ltd | Waiting Area - Public drinking water fountain is dripping. Floor wet | Plumbing & Drainage | Water | 3985.11 | Pass | Fail | 0 | 6 | 1056.4167 | 2022-04-11 13:33 | 2022-04-12 17:00 | 2022-04-12 08:55 | 2022-04-12 17:00 | 2022-05-26 09:20 |  | WACCES | Fountain is leaking from multiple places, unable to repair. Only option is replacement! Tech isolated power & water, 2 x technicians to attend after hours.
MSA-DTWD | WA6184515 | 2 | Precise Air Group | Metals & Engineering section - loud air noise coming from ceiling - see notes | Air Conditioning | Room Air Conditioners | 1554.865 | Pass | Fail | 0 | 6 | 1055.5333 | 2022-11-15 12:43 | 2022-11-18 17:00 | 2022-11-15 15:11 | 2022-11-18 17:00 | 2022-12-29 14:43 |  | WCAPPR | Removed old ductwork,cut all back and installed new 3 m x 300mm duct and joiner .taped all up and checked operation all good .travelled to site signed in got keys found D BLOCK Plantroom on top of roof found pressure relief valve continuously leaking from surge tank tried fixing it but valve is faulty needs replacing with new one .put all information in remarks .Arrived on site and isolated water supply, drained water line, removed old valve, headed to suppliers and sourced new parts, headed to site and set up new valve, installed new valve and tighten all fittings, turned on water and flush system to make sure there are no air locks, checked for leaks, all as it should be with no further faults found
MSA-DTAG | WA6258535 | 1 | Australian HVAC Services Pty. Ltd. | Level 10 - Entire Floor - Different temperatures - See Notes Below | Air Conditioning | Room Air Conditioners | 2776.31 | Pass | Fail | 0 | 6 | 1055 | 2022-11-25 12:50 | 2022-11-28 17:00 | 2022-11-28 12:00 | 2022-11-28 17:00 | 2023-01-11 11:00 |  |  | Assist in control upgrade.Attend site with icon logic. Acess level 10 DD10.02 Isolate box and disconnect wiring to old controllers. Unbolt controllers from shaft and remove. Install new controllers and stoke operation. Connect wiring to controllers. Remove old wall sensor and fit new. Program new controllers and commission operation. Vav box working as normal.
MSA-DCA | WA5586581 | 0 | Protek 24/7 Building & Maintenance | damaged wall panel - need to be made safe | Building | Internal Walls | 768.82 | Pass | Fail | 0 | 6 | 1054.5 | 2022-07-06 13:05 | 2022-07-06 15:05 | 2022-07-06 14:30 | 2022-07-06 17:05 | 2022-08-19 13:00 |  |  | Replace damaged wall panel
MSA-DTWD | WA5141454 | 1 | Equans Mechanical Services Australia | 5F12 and 5F13 - Ducted A/C on north side classrooms not working | Air Conditioning | Room Air Conditioners | 3213.45 | Pass | Fail | 0 | 6 | 1040.5 | 2022-02-16 10:22 | 2022-02-17 17:00 | 2022-02-17 07:30 | 2022-02-17 17:00 | 2022-04-01 16:00 |  |  | Travelled to site and signed in. Located block 5 first floor plantroom and found temperzone unit not cooling investigated condenser and found that stage 1 had no gas and stage 2 was short on gas.Braf will have to be created for repairs and also possibly replacement due to age and being on R22 refrigerant.
MSA-DTWD | WA6020361 | 2 | AWB Co. | Car park - Circuit blue 7 eastern roadway of car park - Faulty light??? Tripping out circuit blue 7 | Electrical | Lighting, External | 4625.1675 | Pass | Fail | 0 | 6 | 1039.5 | 2022-10-13 12:26 | 2022-10-18 17:00 | 2022-10-18 07:00 | 2022-10-18 17:00 | 2022-11-30 14:30 |  |  | Attended site signed in jsa completed. Dug trench from one pole to next. Installed conduit with 4mm cable between the two and put one way box on side of pole and sealed. Proceeded to other side to do the same. Couldnt dig as tree really in the way advised site of this and they are happy to decomission pole. cleaned up site and tested operational pole lights. Job completed
MSA-DTWD | WA5761388 | 2 | AWB Co. | H Block - Roof - Roof leaks x 2 skylights sheets need to be replaced with metal sheets - See notes | Roofing | Rooflights and Skylights | 1328.38 | Pass | Fail | 0 | 6 | 1038.6667 | 2022-08-18 08:46 | 2022-08-23 17:00 | 2022-08-22 09:20 | 2022-08-23 17:00 | 2022-10-04 16:00 |  |  | nvestigated leak at above property.Repairs carried out:Investigated the 2 skylight sheets in Block H class rooms.Sealed the washers on screws on the skylight sheets.Also cleaned out a sump that was fully blocked.Scope of works: Replace existing skylight sheets with Colorbond metal sheets. Additional to works already quoted.Carried out works as below:Pre-order materials required for worksNotify contacts as requiredMobilise to siteSetup work area, including scissor liftRemove and dispose of existing skylight sheetsSupply and install Corrugated Surfmist sheets as below:Bock H- 2 x 7000mmSupply and install Anti-con under all sheetsClean up work area leaving site neat and tidy. Remove all rubbish
MSA-DTAG | WA6291409 | 2 | Sapio Pty Ltd | Registry - ground - Security Screen not working again that shows camera views | Security | CCTV Surveillance | 851.29 | Pass | Fail | 0 | 6 | 1035.5 | 2022-11-28 14:54 | 2022-12-01 17:00 | 2022-11-30 08:00 | 2022-12-01 17:00 | 2023-01-12 11:30 |  |  | Work performed by Ryan Craven 12/01/2023:Removed old HDMI lead, replaced with new lead. Repopulated corresponding screen as to Staff's request. Job completed.
MSA-DTWD | WA5473316 | 3 | AWB Co. | Water leak & ceiling damage | Roofing | Metal Roofing | 2474.12 | Pass | Fail | 0 | 6 | 1033.25 | 2022-05-24 13:47 | 2022-05-31 17:00 | 2022-05-30 14:45 | 2022-05-31 17:00 | 2022-07-12 16:00 |  |  | Removed existing rusted flashings from around air con unit and disposed of.Treated rusted areas with anti rusting agent.Stripped silicone from roof sheet joins.Installed drypan flashings around air con unit and up to ridge line.Cleaned and disposed of all rubbish
MSA-DTWD | WA5488231 | 3 | AWB Co. | J100 Nth - Down pipe has come away from Box gutter spout | Roofing | Guttering | 1649.77 | Pass | Fail | 0 | 6 | 1032.9833 | 2022-06-02 11:26 | 2022-06-10 17:00 | 2022-06-09 08:01 | 2022-06-10 17:00 | 2022-07-22 09:00 |  | WACCES | Attended, measured up, returned with materials to install section of gutter and flashing
MSA-DTAG | WA5612414 | 2 | Australian HVAC Services Pty. Ltd. | Roof - AC Plant - Level 1 officers report too cold – air output cooling and heating both in error | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1121.31 | Pass | Fail | 0 | 6 | 1031.5 | 2022-07-14 11:44 | 2022-07-19 17:00 | 2022-07-18 12:30 | 2022-07-19 17:00 | 2022-08-30 12:00 |  |  | Attend site with icon logic. Access BMS and carry out graphic changes. Now only heating or cooling is displayed on the AC units. Test operation of AC units and found to be controlling as normal.
MSA-DTWD | WA5833339 | 2 | Securex Security Systems & Services | Walkway between A and L block - Swipe card will not unlock external security gate- See notes below | Security | Access Control | 1828.6 | Pass | Fail | 0 | 6 | 1031.25 | 2022-09-06 09:19 | 2022-09-09 17:00 | 2022-09-07 12:45 | 2022-09-09 17:00 | 2022-10-20 12:00 |  | WACCES | 07/09/2022, 1245-1315Lock mechanically damaged see pic, needs to be replaced. Follow up required20/10/2022, 1030-1200Replaced lock tested ok.
MSA-DTWD | WA5479497 | 2 | Australian HVAC Services Pty. Ltd. | A Block - Level 2 - 2 x ceiling vents have broken clips | Air Conditioning | Room Air Conditioners | 1188.37 | Pass | Fail | 0 | 6 | 1031 | 2022-05-27 09:56 | 2022-06-01 17:00 | 2022-05-31 13:00 | 2022-06-01 17:00 | 2022-07-13 12:00 |  |  | Paul Veurink (31/05/2022) - Work NoteTraveled to site. Signed in. Spoke with Kim. He showed me to the tower L2 open Office space and the 2 outlets. 1st outlet. Open Office area. Above desks. Corner of frame is hanging low. It's attached to the solid duct above. Will need to inform Kim before we attend site so they can move people from their desks. We will need to remove metal ceiling strips, locate the hangers for the duct and lift the duct up. Then support the outlet, maybe with a new hanger into the concrete above. Remove and replace outlet frame and core. Then close up ceiling, clean area 2nd outlet. (Same office area as 1st outlet)Clips to hold bracket in place have broken off. Recommend removing old frame and replacing with new core and frame.Explained to Kim what I found and what how we intend to fix the outlets and that we will need to either attend site after hours or move people away from the area. He said if we give him notice of when we are coming he can have
MSA-DFES | WA6361883 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Report of high water use. Suspected leak. | Plumbing & Drainage | Water | 2855.75 | Pass | Fail | 0 | 6 | 1030.75 | 2022-12-08 14:59 | 2022-12-13 17:00 | 2022-12-12 09:15 | 2022-12-13 17:00 | 2023-01-24 08:00 |  | WACCES | Arrived on site signed in went to water meter, isolated the retic, did a timer test 1minute and 5 seconds using 2 litres of water, re opened retic and did another timer test 1 minute 3 seconds using 10 litres of water, leak is on the retic line, informed Deborah she still wants leak detection, leak detection can come by any time, Deborah has given the go ahead to find the leak but she will let us know if she wants us to do it or her retic guy to repair.
MSA-DTWD | WA6132324 | 3 | Equans Mechanical Services Australia | 19Ab: Split System not working | Air Conditioning | Room Air Conditioners | 7951.075 | Pass | Fail | -1 | 6 | 1029 | 2022-10-31 13:20 | 2022-11-07 17:00 | 2022-11-03 13:00 | 2022-11-07 17:00 | 2022-12-16 10:00 |  |  | ATTENDED SITE, TO INVESTIGATE AC IN ONE OF CLASSROOMS NOT WORKING, THIS AC IS 20YEARS OLD AND NEEDS A QUOTE FOR NEW AC
MSA-DFES | WA5395231 | 3 | Protek 24/7 Building & Maintenance | Top Car Park - Ground Level - Cnr Leake and Durban Streets - External Fencing damaged | Building | Steel Fencing & Gates | 2181.045 | Pass | Fail | 0 | 6 | 1028.5 | 2022-05-05 11:32 | 2022-05-12 17:00 | 2022-05-09 13:30 | 2022-05-12 17:00 | 2022-06-21 10:00 |  | WACCES | Replace and dispose of Damaged Fencing
MSA-DTWD | WA5312304 | 3 | AWB Co. | Room E105 - Recurring water leak over desks | Roofing | Metal Roofing | 987.25 | Pass | Fail | -1 | 5 | 1016.5 | 2022-04-11 09:57 | 2022-04-20 17:00 | 2022-04-14 06:00 | 2022-04-20 17:00 | 2022-05-26 14:30 |  | WACCES | Removed ducting and fitted drypan flashings as per BRAF. Job complete
MSA-DTWD | WA5692349 | 3 | Precise Air Group | Heating problem with FCU 38 | Air Conditioning | Room Air Conditioners |  | Fail | Fail | 16 | 22 | 1012.3617 | 2022-08-03 12:21 | 2022-08-10 17:00 | 2022-11-30 15:54 | 2022-08-10 17:00 | 2023-01-11 20:16 |  |  | Works picked up on Maintenance, equipment has now being working. please close of work order now works to date
MSA-DCA | WA5987753 | 2 | Protek 24/7 Building & Maintenance | Ground - Hacket Hall foyer - learning studio 2 & 3 - Wooden floor cracks and breaks - see notes | Flooring | Timber | 4948.6 | Pass | Fail | 0 | 6 | 1011.5 | 2022-10-03 14:07 | 2022-10-06 17:00 | 2022-10-05 09:30 | 2022-10-06 17:00 | 2022-11-16 13:00 |  |  | ? Remove and dispose of damaged floor boards as previously identified by site? Supply and install new floating floor boards where damaged pieces removed and apply stain? Sand back and fill cracks in floor boards as previously identified and marked out by site using wood putty and re-stain as required
MSA-DTWD | WA5689903 | 3 | AWB Co. | Car Park 2 - Car park lamp number 13 far N/W corner-Lamp /lens cover hanging off-will need and ewp | Electrical | Lighting, External | 1731.255 | Pass | Fail | -1 | 5 | 1011.5 | 2022-08-02 14:51 | 2022-08-09 17:00 | 2022-08-04 07:00 | 2022-08-09 17:00 | 2022-09-15 10:30 |  |  | Attended site and signed in. Completed JSA and required paperwork for EWP works. Located pole out in car park and set up work area. Isolated pole. Removed old faulty pole top. Supplied and replaced with new led pole top. Energised circuit and tested. All working correctly. Cleaned and packed up site. Disposed of rubbish correctly. Notified relevant personnel of works completed. **job complete**
MSA-DFES | WA5400518 | 3 | Protek 24/7 Building & Maintenance | Various location cupboard fittings/rails: see locations below | Furniture | Indoor Furniture | 346.625 | Pass | Fail | -1 | 5 | 1011 | 2022-05-10 11:20 | 2022-05-17 17:00 | 2022-05-11 10:45 | 2022-05-17 17:00 | 2022-06-22 13:45 |  | WACCES | Repair various jobs:Station Officer Shower curtain rail requires re-fixing – loose, screws missingHallway Lockers – locker 2 lower hinge needs replacing. Locker 3 rail/handle missingFirefighter Dorm 5 (3 bedded room) bedding locker C7 vent missingFirefighter Dorm 1 – Locker A3 (FF Lee) upper cupboard hinge brokenKitchen cupboard hinge broken – left of oven lower door
MSA-DTWD | WA5832467 | 2 | ACTION GLASS & ALUMINIUM | N207 - Window Glass Broken | Glazing | Window Glass | 1367.005 | Fail | Fail | 1 | 7 | 1010.95 | 2022-09-05 13:28 | 2022-09-08 17:00 | 2022-09-16 11:18 | 2022-09-08 17:00 | 2022-10-28 14:15 |  |  | ATTENDED SITE TO MEASURE & ASSESSPATCHED & MADE SAFE BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-550 X 200PLUS SAFETY FILM 1-550 X 500RETURNED LATER DATE WITH 3 MEN AND ELEVATED WORK PLATFORM (CHERRY PICKER)REGLAZED WINDOW5MM SPOTSWOOD TOUGHENED SAFETY GLASS1-560 X 853PLUS SILICONE AND 2.5 L/M OF PUTTY USEDAS PER APPROVED BRAF
MSA-DFES | WA5471718 | 2 | Protek 24/7 Building & Maintenance | Stores/ above bus bar - Store back wall - Leak from roof | Roofing | Metal Roofing | 2191.54 | Pass | Fail | 0 | 6 | 1010.5 | 2022-05-23 13:12 | 2022-05-26 17:00 | 2022-05-26 11:30 | 2022-05-26 17:00 | 2022-07-07 14:00 |  | WACCES | Removal & replacement of guttering
MSA-DTWD | WA5699510 | 3 | Precise Air Group | A block Boiler short cycling and tripping out regularly | Mechanical Services | Boilers | 309.18 | Fail | Fail | 17 | 23 | 1010 | 2022-08-10 10:10 | 2022-08-17 17:00 | 2022-12-12 09:30 | 2022-08-17 17:00 | 2023-01-23 11:30 |  |  | ravelled to site and signed in.Accessed A Block roof boiler room and carried out checks.Heater was running on arrival.Removed pilot assembly and cleaned, no defects found.Replaced gas train and burner rail test points so gas pressure could be measured.Unable to address frequency of burner cycling due to burner already being at maximum turn down 0.2kPa burner head at lowfire.Monitored operation without any issues.Packed up and signed out
MSA-DFES | WA5460299 | 3 | Protek 24/7 Building & Maintenance | Ground - Pump House - Bootom of entry door is broken at the bottom - base is dragging on floor | Building | Doors | 1630.685 | Pass | Fail | -1 | 5 | 1009.5 | 2022-05-18 12:44 | 2022-05-25 17:00 | 2022-05-19 07:30 | 2022-05-25 17:00 | 2022-06-30 09:00 |  |  | Supply and install new solid core doors
MSA-DTWD | WA5696291 | 2 | Precise Air Group | The heating is not turning on | Air Conditioning | Room Air Conditioners | 1735.47 | Pass | Fail | 0 | 6 | 1008.5 | 2022-08-08 10:50 | 2022-08-11 17:00 | 2022-08-09 11:00 | 2022-08-11 17:00 | 2022-09-20 11:30 |  |  | Attended site and successfully replaced outdoor pcb. Test ran and confirmed unit back in normal operation
MSA-DTWD | WA5116455 | 2 | Equans Mechanical Services Australia | H block - HG01 work shop - evaps ACs not working - roof access will be required | Air Conditioning | Room Air Conditioners | 1373.17 | Fail | Fail | 0 | 6 | 1006.5 | 2022-02-11 15:27 | 2022-02-16 17:00 | 2022-02-17 13:00 | 2022-02-16 17:00 | 2022-03-31 11:30 |  |  | Replaced evaporative cooler fan motor, belt and pulley. Started unit and checked operation. All ok.
MSA-DTWD | WA5377807 | 3 | Protek 24/7 Building & Maintenance | 3B Automotive and 3D Heavy plant - Personnel doors are weather damaged - Frames are loose | Building | Doors | 1436.4 | Pass | Fail | -1 | 5 | 1006.25 | 2022-04-20 09:15 | 2022-04-28 17:00 | 2022-04-20 10:45 | 2022-04-28 17:00 | 2022-06-01 09:00 |  | WACCES | Replace damaged doors
MSA-DFES | WA5304154 | 1 | Australian HVAC Services Pty. Ltd. | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Air Conditioning | Room Air Conditioners | 543.81 | Pass | Fail | 0 | 6 | 1006 | 2022-03-29 08:00 | 2022-03-29 17:00 | 2022-03-29 10:30 | 2022-03-29 17:00 | 2022-05-10 08:30 | 1 | WACCES | Pick up new water temperature sensor from workshop. Travel to site, access plant room and isolate chiller 1. Disconnect sensor wiring from leaving water temp sensor and remove. Apply heat transfer past to new sensor and install. Connect sensors wiring and test operation of sensor. Found to be working as normal.
MSA-DTWD | WA5566795 | 3 | Protek 24/7 Building & Maintenance | LG 12a and LG 12b - Partition doors that divide the two rooms are faulty - see details below | Building | General Building | 950.36 | Pass | Fail | -1 | 5 | 1003.5 | 2022-06-23 11:30 | 2022-06-30 17:00 | 2022-06-23 13:30 | 2022-06-30 17:00 | 2022-08-04 09:00 |  |  | Inspected doors with contractor and adjusted rollers to free up the doors
MSA-DTWD | WA5472120 | 2 | Techworks Electrical | Kendrew- D-Block- Library large overhead lights not working | Electrical | General Electrical | 4196.93 | Pass | Fail | 0 | 6 | 991.5 | 2022-05-23 14:22 | 2022-05-26 17:00 | 2022-05-24 09:00 | 2022-05-26 17:00 | 2022-07-04 16:30 |  | WCAPPR | Replaced faulty lights in library at high level
MSA-DFES | WA6253716 | 2 | Dom's Total Grounds Maintenance | 2 x Retic stations remain on regardless of station controller. Suspect faulty solenoids | Landscaping & Gardening | Grounds Maintenance | 3672 | Pass | Fail | 0 | 6 | 989.6667 | 2022-11-22 11:30 | 2022-11-25 17:00 | 2022-11-23 08:00 | 2022-11-25 17:00 | 2023-01-03 13:40 |  |  | BRAF to be raised to do Retic Repairs
MSA-DFES | WA5399167 | 2 | Go Doors | Engine Room Door - automatic door has broken lifiting cable and one guide wheel has come off | Building | Automatic Doors | 1822.65 | Pass | Fail | 0 | 6 | 988.75 | 2022-05-09 16:23 | 2022-05-12 17:00 | 2022-05-10 11:45 | 2022-05-12 17:00 | 2022-06-20 16:30 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA6291424 | 1 | Equans Mechanical Services Australia | AT205 to 2AT212 - AT236 - Air conditioners are in alarm and not cooling - Please attend 29/11 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 11639.995 | Fail | Fail | 0 | 6 | 988 | 2022-11-28 15:07 | 2022-11-28 17:07 | 2022-11-29 12:00 | 2022-11-28 19:07 | 2023-01-09 16:00 |  | WACCES | Arrived on site signed in. Checked in with Dennis assisted by Dave removed old condenser fan motor installed new. Tested system all ok. Cleaned up and completed paperwork and signed out.
MSA-DTWD | WA5141413 | 1 | BJ SYSTEMS | Kendrew- E-Block- faulty alarm pannel at entrance to building | Security | Monitoring | 797.63 | Pass | Fail | 0 | 6 | 986.25 | 2022-02-16 10:01 | 2022-02-17 17:00 | 2022-02-16 12:30 | 2022-02-17 17:00 | 2022-03-29 14:45 |  |  | 16/02/2022 - 2x buttons are not working on keypad, need to return to replace 29/03/2022 - E Block front entry, replaced RAT, tested with code, can now arm and disarm. All working correctly
MSA-DFES | WA5761506 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | L1-comcen kitchen-Rangehood has been problematic to turn on for some time. Now unable to turn it on. | Electrical | General Electrical | 598.185 | Pass | Fail | 0 | 6 | 985 | 2022-08-18 09:46 | 2022-08-23 17:00 | 2022-08-23 08:00 | 2022-08-23 17:00 | 2022-10-03 09:00 |  | WACCES | Arrived onsite at 7:45 to replace range hood in COMCEN kitchen, replaced range hood and tested, all functions working as intended. Removed old range hood and advised staff of works, continued onsite at 9:00.
MSA-DFES | WA6375834 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Murray St Pedestrian Accessway - faulty compressor for the bollards - see notes below | Equipment | Compressors, Generators | 453.46 | Pass | Fail | -1 | 5 | 985 | 2022-12-15 10:57 | 2022-12-20 17:00 | 2022-12-15 12:15 | 2022-12-20 17:00 | 2023-01-25 13:15 |  |  | Arrived on site at 1215. Found compressor running loud and hot, began investigating and found elbow join out of compressor to be cracked, causing air to leak out and motor to overwork to keep pressure up. Checked everything else and electrically all other components were fine. Will need someone to come fix compressor air pipes and joins. Left motor off, will need to be turned back once compressor pipers are fixed. Alerted staff of works and left at 1315.
MSA-DCA | WA6361904 | 3 | Protek 24/7 Building & Maintenance | Women’s staff bathroom - two sliding doors has derailed and it won’t move or lock | Building | Doors | 439.73 | Pass | Fail | -1 | 5 | 984.75 | 2022-12-08 15:31 | 2022-12-15 17:00 | 2022-12-09 11:00 | 2022-12-15 17:00 | 2023-01-19 11:45 |  | WACCES | Removed lock so that no one would get stuck inside Install new lock
MSA-DFES | WA5853668 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room light timer doesn’t work and the lights all stay on 24hrs -see notes | Electrical | Lighting, External | 1263.7 | Pass | Fail | -1 | 5 | 984.5 | 2022-09-12 10:05 | 2022-09-19 17:00 | 2022-09-15 12:00 | 2022-09-19 17:00 | 2022-10-26 12:30 |  | WACCES | Arrived onsite at 7:30 to investigate lights not working located appliance bay. Adjusted settings to appropriate levels of time, sensitivity etc to suit scenario using RF remote to programme sensor and found no result as sensors seemed to be faulty even under new programming. Replaced all 4 x sensor and tested. Adjusted settings to clients request. Satisfied with works completed, continued onsite at 12:30
MSA-DFES | WA5853687 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | 1 -3 ground light globes in the pathway leading from the flag to the front door keep going out. | Electrical | General Electrical | 1240.56 | Pass | Fail | -1 | 5 | 984.25 | 2022-09-12 10:15 | 2022-09-19 17:00 | 2022-09-15 14:30 | 2022-09-19 17:00 | 2022-10-26 14:45 |  | WACCES | Continued onsite at 12:30 to install 3 x uplights. Wired in new uplights and sealed appropriately. Tested new uplights, all good. Notified staff fo works completed whilst onsite and left site at 14:45
MSA-DCA | WA5979870 | 2 | Precise Air Group | Split air-conditioning system in Green Room is not operating - see notes below | Air Conditioning | Ducted Split System | 641.65 | Fail | Fail | 8 | 14 | 984.0167 | 2022-09-29 10:47 | 2022-10-04 17:00 | 2022-11-30 09:53 | 2022-10-04 17:00 | 2023-01-10 09:54 |  |  | Attended site and signed in. Checked unit in green room and found it was in fault. Checked fault and indicated a faulty suction pipe thermistor. Isolated power and pulled apart outdoor unit, tested suction thermistor and found very low resistance, recommend replacing. Quote to follow.31/10/22Picked up parts and attended site. Isolated AC unit and tested. Swapped out faulty thermistors for new ones. Energised unit and ran, found system operating correctly
MSA-DCA | WA6482136 | 3 | Protek 24/7 Building & Maintenance | Main Foyer North Side -Door is sticking and difficult to open - See Notes Below | Building | Doors | 2057.16 | Pass | Fail | -1 | 5 | 984 | 2023-01-18 07:40 | 2023-01-24 17:00 | 2023-01-18 13:15 | 2023-01-24 17:00 | 2023-02-28 13:15 |  | WACCES
MSA-MRWA | WA5101416 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Metrology Lab - failed air compressor filter | Air Conditioning | Room Air Conditioners | 450 | Pass | Fail | 0 | 6 | 983 | 2022-02-03 11:55 | 2022-02-04 17:00 | 2022-02-04 12:00 | 2022-02-04 17:00 | 2022-03-17 11:00 |  |  | coalescing oil filter valve body on the air compressor line has failed purging air constantly. Replacement required. Obtained parts and purged system and installed new valve body and tested all ok.
MSA-DTWD | WA5587537 | 2 | Equans Mechanical Services Australia | H10 - Aircon keypad flashing green light and not heating - No fault number | Air Conditioning | Room Air Conditioners | 976.99 | Pass | Fail | -1 | 5 | 980.85 | 2022-07-07 08:57 | 2022-07-12 17:00 | 2022-07-07 10:30 | 2022-07-12 17:00 | 2022-08-17 07:21 |  |  | Works completed, BRAF DECLINED waiting on warranty
MSA-DTWD | WA6113710 | 2 | Protek 24/7 Building & Maintenance | Several Trip Hazards on concrete footpaths - Map sent in email | Flooring | Concrete | 3746.28 | Pass | Fail | 0 | 6 | 979 | 2022-10-24 14:17 | 2022-10-27 17:00 | 2022-10-26 12:00 | 2022-10-27 17:00 | 2022-12-06 07:00 |  | WACCES | Located 3 areas with damaged or inadequate footpaths that are potential trip hazardsDamage to two locations caused by vehicles driving over themCarried out site measure to confirm materials requiredGrind lipping at control joints to E BlockCut-out damaged sections of pathway and prepared area for replacement. Form up and pour new 20MpaConcrete to pathway to J BlockAs per Braf Document 16/11/2022 cost of works to Date $3746.28
MSA-DTAG | WA6394177 | 3 | Sapio Pty Ltd | Courtroom 4 duress button stuck in alarm | Security | Monitoring | 3389.14 | Pass | Fail | -1 | 4 | 978.4667 | 2022-12-30 09:01 | 2023-01-09 17:00 | 2022-12-30 09:02 | 2023-01-09 17:00 | 2023-02-09 03:30
MSA-DTAG | WA5201086 | 1 | Australian HVAC Services Pty. Ltd. | Level 1 - Aircon in room turns on but doesnt seem to blow cold air | Air Conditioning | Room Air Conditioners | 3075.12 | Pass | Fail | 0 | 6 | 965 | 2022-03-02 11:20 | 2022-03-03 17:00 | 2022-03-02 12:00 | 2022-03-03 17:00 | 2022-04-11 17:00 |  |  | 40995Attend site with Airtek. Access roof and isolate AC 3. Remove old controller and associated wiring. Run new cable to room 119 below and mount wall controller. Modify existing cabling to suit new controls. Deisolate and commission operation. Check airflows, ok. Unit now controlling correctly. Train staff in operation of AC unit control.
MSA-DTWD | WA5879836 | 3 | COMMERCIAL PLUMBING AND GAS | Cold water tap leaking in Soil Lab sink | Plumbing & Drainage | Water | 1674.435 | Pass | Fail | 0 | 6 | 964 | 2022-09-15 09:36 | 2022-09-22 17:00 | 2022-09-21 14:00 | 2022-09-22 17:00 | 2022-10-31 18:00 |  | WACCES | sourced and replaced new tap assembly
MSA-DTWD | WA5390659 | 2 | Schneider Electric Australia Pty Ltd | A126 - Auto Door - relay access control fault | Electrical | General Electrical |  | Pass | Fail | 0 | 6 | 963 | 2022-05-02 14:35 | 2022-05-05 17:00 | 2022-05-05 11:00 | 2022-05-05 17:00 | 2022-06-14 14:00 |  |  | job completed - Attended site to assist with the changeover of a faulty power supply.Located and isolated security panel using lock out tag out procedure and ensured power wasde-energised.Disconnected existing power supply unit and removed from panel and replaced it with new powersupply unit.Wired and connected new cables into existing circuit breaker and terminals and reinstated anyremoved cable ducting.Removed any tags and locks and re-energised circuit with successful operation of the new powersupply unit.Returned to site and replaced batteriesChecked and tested battery back up function
MSA-DTWD | WA5686818 | 3 | Equans Mechanical Services Australia | Rooms AF2.12, AF2.38, AF2.41 - Daiken unit, AC3 (3.1, 3.2, 3.3) not working. | Air Conditioning | Room Air Conditioners | 5260.03 | Fail | Fail | 0 | 6 | 963 | 2022-08-01 11:03 | 2022-08-08 17:00 | 2022-08-11 12:30 | 2022-08-08 17:00 | 2022-09-20 15:30 |  |  | ACCESSED THE UNIT ON THE ROOF, CHECKED FOR LEAKS, PRESSURISED WITH NITROGEN, HAD TO GET OFF THE ROOF A FEW TIMES DUE TO RAIN. USED TWO PEOPLE TO LIFT EQUIPMENT UP TO JOB , PUT ONTO VAC PUMP.ACCESSED THE CONDENSER UNIT FOR THE UNIT IN GF29, FOUND IT ON R22 LOW ON GAS , AND THE OUT DOOR PC BOARD IS BURNT OUT
MSA-DFES | WA5301790 | 1 | Securex Security Systems & Services | Ground - Various - 2 cameras on station CCTV not working | Security | CCTV Surveillance | 4426.27 | Pass | Fail | 0 | 5 | 962 | 2022-04-01 12:35 | 2022-04-04 17:00 | 2022-04-01 15:15 | 2022-04-04 17:00 | 2022-05-11 17:15 |  |  | 01/04/20225 cameras out.1 in undercover parking. 4 in garage all analogue cameras require scissor to reach cameras in garage.10/05/2022Replaced 4x faulty cameras and changed them to new power supply and testedOne x camera in engine bay is not working has power but no imageAppears to be cable faultChecked all other cameras and found additional faultsFront entry cam not workingGym/ car park not workingWest office outside cam not workingEngine bay camera blurredRecommend quote for full system upgrade.
MSA-DFES | WA5368579 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Multiple areas - please see details below | Electrical | General Electrical | 1927.305 | Pass | Fail | 0 | 6 | 961.25 | 2022-04-19 11:35 | 2022-04-22 17:00 | 2022-04-22 12:45 | 2022-04-22 17:00 | 2022-06-01 14:00 |  | WACCES | Arrived on site at 1030 to tend to lights not working around station. Located and replaced 2 x bunker light fluros near staircase, investigated faulty flood light on roof of station and discovered voltage to light with light not energising, located/replaced 2 x fluros/starters not working above exit door beside engine room, also located 10 x black external lights not working around station, two of which containing faulty tombstones & ballasts. Replaced & reenergised 1 x black external fluro. Will need to return to site to replace spot light & all fluro's/components for black external lights. Left site at 1400 and finished day at office.
MSA-DTWD | WA5699736 | 1 | Protek 24/7 Building & Maintenance | 3D4 Fuel injection room-From 2nd row light fitting-Protek on site | Roofing | Metal Roofing | 1474.03 | Pass | Fail | 0 | 6 | 961 | 2022-08-10 11:50 | 2022-08-11 17:00 | 2022-08-11 11:30 | 2022-08-11 17:00 | 2022-09-20 12:30 |  |  | Repair water leak
MSA-DFES | WA5833817 | 2 | Protek 24/7 Building & Maintenance | Roof leak in the same location as pervious WO WA577394 | Roofing | Tiled Roofing | 767.58 | Pass | Fail | 0 | 6 | 961 | 2022-09-06 12:00 | 2022-09-09 17:00 | 2022-09-09 10:00 | 2022-09-09 17:00 | 2022-10-19 11:00 |  | WACCES | repair roof leak - Remove and replace 125 roof screws
MSA-DCA | WA5649809 | 1 | ACTION GLASS & ALUMINIUM | Large frosted glass window shattered and fallen down | Glazing | Window Glass | 10224.27 | Pass | Fail | 0 | 6 | 960.6667 | 2022-07-17 10:33 | 2022-07-18 10:33 | 2022-07-17 11:00 | 2022-07-18 10:33 | 2022-08-26 11:40 |  |  | ATTENDED SITE AFTER HOURS WITH 2 MENBOARDED UP WINDOW TO MAKE SAFE15MM BOARD2-1200 X 1460, 1-620 X 1460PLUS 3 TIMBER BATONS AND 76 SCREWS USEDALSO 4 SQM OF SAFETY FILMRETURNED TO SITE TO CHECK MEASURE NEW PANELRETURNED TO SITE WITH 5 MEN TO REGLAZE15MM CLEAR TOUGHENED SAFETY GLASS1-1450 X 3018POLISHED EDGES6 TUBES OF BLACK SILICONE USED FOR BUTT JOINRETURNED LATER DATE REMOVED TIMBER BLOCK AND FINISHED OFF SILICONE BUTT JOIN1 TUBE BLACK SILICONE USEDCRANE REQUIREDCOMPLETED AS PER APPROVED BRAF
MSA-DTWD | WA5499080 | 2 | Falcetta Plumbing and Gas | B&D Block - Reduced water pressure from main water supply | Plumbing & Drainage | Water | 5297.86 | Pass | Fail | 0 | 6 | 959.5 | 2022-06-10 09:51 | 2022-06-15 17:00 | 2022-06-14 14:30 | 2022-06-15 17:00 | 2022-07-24 14:00 |  | WCAPPR | repaired leak to 100mm main below bitumen
MSA-DTAG | WA5473336 | 1 | Bullant Security Pty Ltd | Entry to court room 3 - Lock on door to court room 3/chambers area is not latching | Security | Locksmith | 612.64 | Pass | Fail | 0 | 6 | 958.4167 | 2022-05-24 14:02 | 2022-05-25 17:00 | 2022-05-25 11:50 | 2022-05-25 17:00 | 2022-07-04 10:15 |  |  | Attended site, door closer not strong enough for door, it is leaking oil. Will need to be replaced with a stronger one.Date on site: 25/5/2022Time on site: 11:50 - 12:05Attended site, fitted new door closer on courtroom 3 door.Date on site: 4/7/2022Time on site: 09:00 - 10:15
MSA-DTWD | WA5471321 | 2 | Protek 24/7 Building & Maintenance | B2428 Classroom - Roof leak - See facilities for exact location | Roofing | Tiled Roofing | 970.52 | Pass | Fail | 0 | 6 | 958 | 2022-05-23 12:41 | 2022-05-26 17:00 | 2022-05-26 14:15 | 2022-05-26 17:00 | 2022-07-05 12:15 |  | WCAPPR | repair water leak in roof
MSA-DTWD | WA6519335 | 1 | Australian Airconditioning Services Pty Ltd | Room 8G3 - Faulty Air conditioner #2 | Air Conditioning | Room Air Conditioners |  | Pass | Fail | 0 | 6 | 957.75 | 2023-01-25 15:41 | 2023-01-27 17:00 | 2023-01-27 11:30 | 2023-01-27 17:00 | 2023-03-08 09:15
MSA-DFES | WA5585297 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Career-Passage way-small fluro has broken cover | Electrical | Lighting, Internal | 312.595 | Pass | Fail | 0 | 6 | 957.5 | 2022-07-05 14:21 | 2022-07-08 17:00 | 2022-07-07 09:45 | 2022-07-08 17:00 | 2022-08-16 07:15 |  | WACCES | Arrived on site at 0630 to replaced 1 x damaged light fitting in station passage. Replaced/reenergised fitting, informed staff of works and left site at 0715.
MSA-DTAG | WA6298425 | 3 | AHS Services WA Pty Ltd (Anchor) | Security Staff Kitchen - Hot water tap is dripping (see notes) | Plumbing & Drainage | HWS/Units Electric & Gas | 252.13 | Pass | Fail | -1 | 5 | 956.4667 | 2022-12-01 09:58 | 2022-12-08 17:00 | 2022-12-02 13:00 | 2022-12-08 17:00 | 2023-01-11 09:28 |  | WCAPPR | Replaced faulty hot spindle
MSA-DFES | WA5291557 | 1 | Go Doors | Exit Boom - Main gate - currenlty stuck open - unable to register any inputs | Building | Automatic Doors | 3450.23 | Pass | Fail | 0 | 6 | 942.5 | 2022-03-28 07:13 | 2022-03-28 17:00 | 2022-03-28 09:45 | 2022-03-28 17:00 | 2022-05-06 16:15 |  |  | COMPLETED QUOTED WORKS.
MSA-DTWD | WA5086917 | 3 | ACTION GLASS & ALUMINIUM | C Block - Ground Floor - C46 Hair Salon - 8 x mirrors smashed | Glazing | Mirrors | 1723.2 | Pass | Fail | 0 | 5 | 942.0167 | 2022-01-21 16:16 | 2022-01-31 17:00 | 2022-01-28 07:49 | 2022-01-31 17:00 | 2022-03-08 13:50 |  |  | MEASURED THESE MIRRORS WHILE ON SITE DOING WORK ORDER WA5037825ATTENDED SITE TO MEASURE & ASSESSRETURNED LATER DATESUPPLIED & FIT 6 MIRRORS6MM VINYL SAFETY BACK MIRRORS6-900 X 800POLISHED EDGESPLUS MIRROR CLIPS 2 MEN REQUIRED
MSA-DCA | WA5869352 | 3 | Protek 24/7 Building & Maintenance | Theatre/Bar - Door handle broken off | Building | Doors | 981.48 | Pass | Fail | -1 | 5 | 941.25 | 2022-09-14 13:17 | 2022-09-21 17:00 | 2022-09-15 07:00 | 2022-09-21 17:00 | 2022-10-24 12:15 |  |  | ? Remove and dispose of damaged door? Supply new 'Solid Core' plain style door in Maple colour? Retro-fit all door hardware to new door & hang door to frame
MSA-DFES | WA5081035 | 0 | Protek 24/7 Building & Maintenance | Front Entry Door - has been vandalized and kicked in | Building | Doors | 2504.06 | Pass | Fail | 0 | 6 | 941 | 2022-01-20 10:28 | 2022-01-20 12:28 | 2022-01-20 11:45 | 2022-01-20 14:28 | 2022-02-28 16:45 |  | WACCES | Repair front entry door
MSA-DTAG | WA5285829 | 1 | Sapio Pty Ltd | Level 10 - Secuirty Camera not extending to displays | Security | CCTV Surveillance | 3499.09 | Pass | Fail | 0 | 5 | 939.75 | 2022-03-21 10:28 | 2022-03-22 17:00 | 2022-03-21 12:00 | 2022-03-22 17:00 | 2022-04-29 15:45 |  |  | Installed & programmed IndigoVision to new Workstation. Performed cable management of HDMI cablingunder desk. Installed monitors on dual stand and installed cable management of HDMI cables and IEC leads.
MSA-DTAG | WA5481492 | 3 | Australian HVAC Services Pty. Ltd. | FER/Sheriff’s Office Main area - Staff are noticing air con is colder than usual | Air Conditioning | Room Air Conditioners | 1434.45 | Pass | Fail | -1 | 5 | 938.5 | 2022-05-30 13:42 | 2022-06-07 17:00 | 2022-05-31 12:00 | 2022-06-07 17:00 | 2022-07-09 14:30 |  | WACCES | Drain water from heating pipework. Disconnect wiring to flow switch. Unscrew old flow switch from pipe and remove. Fit new thread tape to thread. Install new flow switch and use correct paddle length. Connect wiring to new flow switch. Fill system with water and test operation of flow switch. Carry out adjustments to spring pressure and confirm correct operation. Flow Switch working as normal. Clean area
MSA-DTWD | WA6159311 | 0 | Techworks Plumbing | T Block - Water leak from roof outside cafeteria alfresco area | Plumbing & Drainage | Water | 1941.32 | Pass | Fail | 0 | 6 | 938.5 | 2022-11-10 14:10 | 2022-11-10 16:10 | 2022-11-10 14:30 | 2022-11-10 18:10 | 2022-12-19 17:00 |  |  | Daniel Farrell (19/12/2022) - Work NoteAttended site and signed in Removed tiles and observed cisternthe 15mm copper line branched into the flush pipe which charges the floor waste had been unsuccessfully sealed with sikaflexRemoved all caulk from branch connection and cleaned areasealed branch back up with silconeCleaned and mopped area thoroughly placed pan and components back inside cubicleinformed Kristy that I would like to come back and test the new seal at some point before the tilersDaniel Farrell (11/11/2022) - Work NoteAttended site and signed inbunted off area under leakremoved another panel and proceeded to removed lagging on dropperflushed cistern, poured water down toilet and noticed no leaks chipped open wall around pan adaptor to check areaabove the adaptor was damp, so checked around flush pipesteel cistern support was heavily corroded from water damageDaniel Farrell (11/11/2022) - Work NoteAttended site and signed inbunted off area under leak
MSA-DTAG | WA5673955 | 0 | SCAVENGER SUPPLIES PTY LTD | entry fire panel will not turn off making screeching noise | Fire Protection Services | Fire Protection - Monitor System | 7010.69 | Pass | Fail | 0 | 6 | 938.0833 | 2022-07-21 07:45 | 2022-07-21 09:45 | 2022-07-21 08:00 | 2022-07-21 11:45 | 2022-08-29 10:05 |  | WACCES | COMPLETED 27/08/2022CALL OUT 21/07/2022-8.00AM-9.30AM-WBNORMAL LABOUR-1.5 HOURS-WB-SS/T5/REPORT/IMAGES UPLOADEDBRAF TO BE DRAFTED-DCBRAF SUBMITTEDBR TO ODERED 25 SENSORSBRAF approved 19/08/2022-PW advised 23/08/2022
MSA-DTWD | WA5413578 | 2 | SCAVENGER SUPPLIES PTY LTD | G & H Blocks - Voice or siren not audible in either block | ICT/Audiovisual | Hardware / Equipment | 1326.12 | Pass | Fail | -1 | 5 | 937.8667 | 2022-05-12 12:08 | 2022-05-17 17:00 | 2022-05-12 12:09 | 2022-05-17 17:00 | 2022-06-20 14:01 |  |  | WORK STARTED 11/05/2022 - THIS WORK ORDER CARRIED OVER FROM PREVIOUS WORK ORDER WA5395171 AS FURTHER WORK REQUIREDATTENDED THIS WORK ORDER 1ST TIME 11/05/2022. SIGNATURE SLIP FOR 2 X WORK ORDERS. COULD NOT ENTER THE START DATE FOR THE CORRECT START OF WORK ON PROMAP. WOULD NOT ALLOW16/06/2022-TO CUT MANHOLE 20/06/2022- REMAINDER OF WORK COMPLETED. 2 C TECHNICIANS**BRAF SENT FOR APPROVAL 21/06/2022***
MSA-MRWA | WA5715080 | 3 | AWB Co. | LED office light will not illuminate Ref AJ for fitting type | Electrical | Lighting, Internal | 517.01 | Pass | Fail | -1 | 5 | 935 | 2022-08-12 11:04 | 2022-08-19 17:00 | 2022-08-15 09:45 | 2022-08-19 17:00 | 2022-09-23 08:45 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located faulty light above desk. Removed old fitting. Supplied and installed new led panel. Reset lights, all lights working properly. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5496991 | 1 | BAKE-QUIP PTY LTD | Dough Break machine is faulty - See notes below | Equipment | Catering Equipment | 357.9 | Pass | Fail | 0 | 6 | 929 | 2022-06-09 13:35 | 2022-06-10 17:00 | 2022-06-10 15:30 | 2022-06-10 17:00 | 2022-07-19 08:30 |  | WACCES | REFER TO SERVICE REPORT.
MSA-DFES | WA5693757 | 0 | WESTCOAST CONSTRUCTION & DEMOLITION | Roof - whilrbird has been removed due to breakin needs to be fixed | Roofing | Metal Roofing | 1711.56 | Fail | Fail | 0 | 6 | 918.85 | 2022-08-04 15:08 | 2022-08-04 17:08 | 2022-08-05 08:55 | 2022-08-04 19:08 | 2022-09-12 15:46 |  |  | Removed flashing and installed new whirly bird. Siliconed and touched to help dry as wet weather was fast approaching.Tip scrap materials
MSA-DTAG | WA5392990 | 1 | Sapio Pty Ltd | Front auto door going into alarm. Please attend and investigate cause as well as amend configuration | Security | Monitoring | 5699.28 | Pass | Fail | 0 | 5 | 917 | 2022-05-03 13:54 | 2022-05-04 17:00 | 2022-05-04 09:30 | 2022-05-04 17:00 | 2022-06-11 14:30 |  |  | reattended site after hours and ran cable from existing Gallagherpanel with spare inputs. Cabled, programmed and installed T30 on external wall for afterhours access to auto door,Installed REX, break glass and REX detector on internal wall. Programmed free access during normal court operationsand lock during afterhours with REX and keypad as overrides. Updated monitoring with additional input list and tested andcommissioned new door.
MSA-DTWD | WA5680674 | 2 | Protek 24/7 Building & Maintenance | Water leak in south east corner of workshop from windows | Roofing | Metal Roofing | 1000 | Pass | Fail | 0 | 5 | 916.75 | 2022-07-27 14:13 | 2022-08-01 17:00 | 2022-08-01 07:45 | 2022-08-01 17:00 | 2022-09-08 12:30 |  | WACCES | Installed flashing over Louvre to prevent weather ingress
MSA-DTWD | WA5549123 | 1 | Protek 24/7 Building & Maintenance | D28 - Roof leak | Building | General Building | 3997.06 | Pass | Fail | 0 | 5 | 916.5 | 2022-06-17 13:12 | 2022-06-20 17:00 | 2022-06-20 10:30 | 2022-06-20 17:00 | 2022-07-28 15:00 |  | WACCES | Replace roof sheets
MSA-DFES | WA5727662 | 3 | Australian HVAC Services Pty. Ltd. | Dorm 1 AC is not operating when used in ‘heat’ mode.see ntoes | Plumbing & Drainage | Water | 3384.85 | Pass | Fail | -1 | 5 | 916 | 2022-08-15 11:07 | 2022-08-22 17:00 | 2022-08-16 13:30 | 2022-08-22 17:00 | 2022-09-23 17:30 |  | WACCES | New unit installed as per BRAF
MSA-DTWD | WA6450157 | 3 | ACTION GLASS & ALUMINIUM | Level 1 - Exterior - broken windows | Glazing | Window Glass | 10097.385 | Pass | Fail | 0 | 5 | 915.1667 | 2023-01-16 09:39 | 2023-01-23 17:00 | 2023-01-23 10:35 | 2023-01-23 17:00 | 2023-03-02 13:45
MSA-DTWD | WA6403048 | 1 | Precise Air Group | D-Block Chiller not working | Refrigeration | Chiller | 4718.58 | Pass | Fail | 0 | 5 | 915.0333 | 2023-01-06 08:27 | 2023-01-09 17:00 | 2023-01-06 13:05 | 2023-01-09 17:00 | 2023-02-13 16:07
MSA-DTWD | WA6298635 | 2 | AWB Co. | A Block - Level 1 - North West cnr - Damaged ceiling slats/strips | Building | Ceiling | 514.4625 | Pass | Fail | 0 | 5 | 915 | 2022-12-01 11:44 | 2022-12-06 17:00 | 2022-12-06 12:30 | 2022-12-06 17:00 | 2023-01-13 15:30 |  |  | Works completed
MSA-DTWD | WA5490832 | 2 | Australian Airconditioning Services Pty Ltd | F24 - Daikin air conditioners blowing cold air | Air Conditioning | Room Air Conditioners | 1742.125 | Fail | Fail | 4 | 9 | 914.8917 | 2022-06-03 09:47 | 2022-06-09 17:00 | 2022-07-05 09:06 | 2022-06-09 17:00 | 2022-08-12 12:00 |  | WACCES | Returned and replaced PCBs. Test ran operation in heating and cooling. All ok
MSA-DTWD | WA5018460 | 0 | Precise Air Group | Homestead main freezer - running at 17 degrees and not minus 18. | Refrigeration | Freezers | 4959.67 | Pass | Fail | 0 | 5 | 914.6833 | 2022-01-14 11:47 | 2022-01-14 13:47 | 2022-01-14 12:00 | 2022-01-14 15:47 | 2022-02-21 14:41 |  |  | Works completed as per braf
MSA-DCA | WA5688191 | 2 | Dormakaba Australia Pty Ltd | Level 3 - Connections - Repair Extra large auto door - See notes below | Building | Automatic Doors | 5835.99 | Pass | Fail | 0 | 5 | 913.5167 | 2022-08-02 10:26 | 2022-08-05 17:00 | 2022-08-05 07:40 | 2022-08-05 17:00 | 2022-09-12 09:11 |  |  | 5/8/22 - Found that the door is jamming, we have tried to raise door to see if it is jamming down the bottom, this didn''t work, took the belt off the door to see if the motor has seized, cannot find the issue limited access, limited time. We will need to return with more time to try to find the issue.31/8/22 - Inspected door and found that the door was fouling on the floor guide, removed ends stops to gain access to floor guide and refitted as necessary and refitted end stops. Once power was returned to door we were getting a fault with no auxiliary devices powering up, replaced controller and found controller powering up but not driving door etc. Quote to return with two technicians out of business hours and replace controller, lock motor only and motor loom.12/9/22 - Replaced faulty motor, motor loom and transformer as per quotation, reset and tested operation upon completion and left in good working order.
MSA-DFES | WA5869526 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Engine Bays - Multiple charger cable pulleys not working - See notes below | Building | Columns | 2074.2 | Pass | Fail | 0 | 5 | 913.5 | 2022-09-14 14:21 | 2022-09-21 17:00 | 2022-09-19 13:00 | 2022-09-21 17:00 | 2022-10-27 14:30 |  |  | ? Receive scissor lift and setup inside of exclusion zone ? Electrician attendance to replace outlets with suspended power outlets to each bay ? Remove and dispose of 7 bays of dilapidated rope pulley systems ? Supply and new rope pulley system to each bay, including pulleys, cleats & rope as required? Carry out testing of each system once installed to confirm correct function
MSA-DFES | WA5473433 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | front entrance fluro light not working | Electrical | Lighting, Internal | 893.105 | Pass | Fail | 0 | 5 | 912.5 | 2022-05-24 15:12 | 2022-05-27 17:00 | 2022-05-27 09:00 | 2022-05-27 17:00 | 2022-07-04 09:30 |  | WACCES | Arrived onsite at 900. Found external light circuit has tripped and won’t reset. Upon investigation, found 1 up light has filled with water and causing the circuit to trip. Removed uplight from circuit and reenergised. Found 2 bunker lights and 2 fluro battens are not working. Replaced 2 lamps in bunker lights but will need to order new uplight and 4 fluros for battens. Notified staff and left site at 1200Continued on site at 09:15. Uplighter replaced under Order No: AMS1053782 Request No: WA539304. No action needed lift site at 09:30
MSA-DTWD | WA5294182 | 3 | Equans Mechanical Services Australia | Level 2 - Male toilet - Exhaust Fan Not working | Air Conditioning | Room Air Conditioners | 1255.07 | Pass | Fail | -1 | 5 | 912 | 2022-03-28 13:45 | 2022-04-04 17:00 | 2022-03-29 14:00 | 2022-04-04 17:00 | 2022-05-06 14:00 |  |  | .
MSA-DTWD | WA5393854 | 2 | AWB Co. | Power isolator faulty to Panel Saw | Electrical | General Electrical | 995.95 | Pass | Fail | 0 | 5 | 911.5 | 2022-05-04 10:43 | 2022-05-09 17:00 | 2022-05-09 09:45 | 2022-05-09 17:00 | 2022-06-16 09:15 |  | WACCES | Attended site and signed in. Completed JSA. Located panel saw. Supply and replace contactor for saw. Tested all okay. Signed out job complete
MSA-DTWD | WA5686985 | 1 | Australian Airconditioning Services Pty Ltd | A/C not working again | Air Conditioning | Room Air Conditioners | 1611.55 | Pass | Fail | 0 | 5 | 909.25 | 2022-08-01 12:28 | 2022-08-02 17:00 | 2022-08-01 14:15 | 2022-08-02 17:00 | 2022-09-08 11:30 |  | WACCES | Replaced PCB, radiator fins and sensors. Tested operation. All ok
MSA-DFES | WA5090343 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Entire facility - Lights are staying on all day/night by sensors/timers - see details | Electrical | General Electrical | 2615.358 | Pass | Fail | 0 | 5 | 893.5 | 2022-01-25 11:22 | 2022-02-02 17:00 | 2022-02-01 10:45 | 2022-02-02 17:00 | 2022-03-10 16:15 |  |  | Arrived on site and checked why the street lights were staying on. I found that the override was left on. I checked the PECELL and it is working. Staff asked to check the site for faulty lights. I found various lights that are faulty please refer to the pictures for there locations. I also fixed a light with a falling diffuser, re fixed a light into position and replaced a faulty light switch. Will need to order new parts and return to install. Advised staff of work completed.
MSA-DCA | WA6402597 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Ground Level - Control Room - BMS Fire Alarm Fault | Building | General Building | 371.62 | Pass | Fail | 0 | 5 | 891 | 2023-01-05 13:34 | 2023-01-10 17:00 | 2023-01-09 07:00 | 2023-01-10 17:00 | 2023-02-15 10:00 |  | WACCES
MSA-MRWA | WA5116128 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Retrospective WO * Meeting room 242 – A/C not working ** attended on 10/02/2022 | Air Conditioning | Room Air Conditioners | 973.25 | Pass | Fail | -1 | 5 | 890.5 | 2022-02-10 11:00 | 2022-02-15 17:00 | 2022-02-10 11:30 | 2022-02-15 17:00 | 2022-03-19 14:00 | 1 | WACCES | Travelled to site and signed in. Located meeting room on level 2. Investigated unit and found that the Smartpak controller relay had stuck open and damaged the controller. Ordered new controller and awaiting parts.Received parts, travelled to site and signed in. Isolated and unwired faulty controller and installed and wired up new controller. Tested operations. Pac unit now runs without fault.
MSA-DTAG | WA5081569 | 3 | Midolo Building Services | Lower - Custody - see details below | Building | General Building | 487.87 | Pass | Fail | 0 | 5 | 890 | 2022-01-20 16:05 | 2022-01-28 17:00 | 2022-01-25 07:00 | 2022-01-28 17:00 | 2022-03-03 09:00 |  | WACCES | Hinges have been replaced
MSA-DTWD | WA5395524 | 2 | Protek 24/7 Building & Maintenance | Outside FG14 - see details below | Building | General Building | 5025.2 | Pass | Fail | 0 | 5 | 887.75 | 2022-05-05 13:49 | 2022-05-10 17:00 | 2022-05-09 14:15 | 2022-05-10 17:00 | 2022-06-15 14:00 |  | WACCES | Replace damaged wall panels
MSA-DTWD | WA5793699 | 1 | SENTINEL LOCK SERVICE PTY LTD | Key pad on door lock faulty | Security | Locksmith | 975.24 | Pass | Fail | 0 | 5 | 886.75 | 2022-08-24 09:31 | 2022-08-25 17:00 | 2022-08-24 13:30 | 2022-08-25 17:00 | 2022-09-30 12:15 |  | WACCES | 10G75 - Key pad lock on door faulty.Lock and pad replaced.
MSA-DFES | WA5570749 | 2 | Protek 24/7 Building & Maintenance | Driveway in front of engine room - Grates over drain have lifted creating trip hazard | Building | General Building | 1398.74 | Fail | Fail | 1 | 7 | 885.75 | 2022-06-28 14:17 | 2022-07-01 17:00 | 2022-07-11 13:45 | 2022-07-01 17:00 | 2022-08-17 11:30 |  | WACCES & WCAPPR | Replace grates over drain
MSA-DTWD | WA5680791 | 3 | Protek 24/7 Building & Maintenance | Leaking Roof - Ceiling damage western end | Roofing | Metal Roofing | 2906.415 | Pass | Fail | 0 | 5 | 872.75 | 2022-07-27 16:24 | 2022-08-03 17:00 | 2022-08-02 07:30 | 2022-08-03 17:00 | 2022-09-07 16:15 |  | WACCES | ? Temporarily remove light fittings & aluminium cornice and reinstate once works complete? Remove and dispose of damaged ceiling sheets? Supply and install new ceiling sheets and fixings? Supply and install Compriband foam seal under Trim-Dek roof sheets
MSA-DTWD | WA5397283 | 2 | Techworks Electrical | Ground Level - External - replace all walkway and external building lights, that are not working | Electrical | Lighting, External | 3986.4 | Pass | Fail | 0 | 5 | 872.5 | 2022-05-06 14:32 | 2022-05-11 17:00 | 2022-05-11 07:00 | 2022-05-11 17:00 | 2022-06-16 15:30 |  | WCAPPR | Replaced lights above stair cases with scaffolders, then replaced lights around campus that failed with new led WP battons.
MSA-DTWD | WA6131860 | 3 | ACTION GLASS & ALUMINIUM | Cracked windows | Glazing | Window Glass | 5017.185 | Pass | Fail | -1 | 4 | 872.25 | 2022-10-31 10:09 | 2022-11-07 17:00 | 2022-11-01 08:00 | 2022-11-07 17:00 | 2022-12-07 16:15 |  |  | ATTENDED SITEMEASURED & ASSESSED CRACKED PANELSRETURNED LATER DATE WITH 2 MEN TO REGLAZE 9 HILITE PANELS6.38 TRANSLUCENT LAMINATED SAFETY GLASS WITH ARRISED EDGES(1)1-1932x578. (2)1-1932x578. (3)1-1932x575 (4)1-1932x576. (5)1-1932x582. (6)1-1932x578(7)1-1932x580. (8)1-1932x583. (9)1-1932x580PLUS CLEAR ANODISED ANGLE 18-1932mmAND 2 TUBES OF SILICONE AND 55 RIVETSAS PER APPROVED BRAF
MSA-DTWD | WA5086792 | 1 | Equans Mechanical Services Australia | A Block - Ground Floor - AG10B Café Kitchen - Cool Room not working. Condenser not working | Refrigeration | Coolroom | 9627.62 | Pass | Fail | 0 | 5 | 868.75 | 2022-01-21 13:07 | 2022-01-24 17:00 | 2022-01-24 10:15 | 2022-01-24 17:00 | 2022-03-01 15:00 |  |  | .
MSA-DTWD | WA5987735 | 2 | COMMERCIAL PLUMBING AND GAS | Water leak to ring main B Block | Roofing | Metal Roofing | 15867.025 | Pass | Fail | 0 | 5 | 868 | 2022-10-03 13:57 | 2022-10-06 17:00 | 2022-10-04 10:00 | 2022-10-06 17:00 | 2022-11-09 14:00 |  |  | installed bypass within existing 100mm copper line
MSA-DTAG | WA5521927 | 2 | Sapio Pty Ltd | Court aerial – Security room - TVs showing weak signal - See notes below | ICT/Audiovisual | General AV works | 787.22 | Pass | Fail | -1 | 5 | 867.5 | 2022-06-15 11:20 | 2022-06-20 17:00 | 2022-06-16 08:00 | 2022-06-20 17:00 | 2022-07-22 11:30 |  |  | Removed analogue amplifiers, power supply and modulator and replace with digital amplifier and power supply.Programmed and commissioned system.
MSA-DTWD | WA4991852 | 1 | Equans Mechanical Services Australia | Ground - Building Aircon - BMS Aircon - Aircon not working in building | Air Conditioning | Room Air Conditioners | 857.95 | Pass | Fail | 0 | 5 | 866.05 | 2022-01-05 12:57 | 2022-01-06 17:00 | 2022-01-06 07:31 | 2022-01-06 17:00 | 2022-02-11 09:34 |  |  | 6th: Checked the mechanical plans , found condenser 2 supplies the area faulting out. Reset the FCU'S , reset the Daikin controller in the mssb . Logged slave 1&2 off , turned all fcus on and master unit loaded up and cut in and out several times. Logged slave 1 back on, ran up and will leave for a couple of days, if nothing happens the problem is with the slave 2 inverter board.7th: Had L5 fault on the controller in the server room, the air-conditioning is still running OK, reset the controller will get DAIKIN to check with lap top.28/01/22 Attended site with the Daikin tech , quote to repair being sent through.
MSA-MRWA | WA5399173 | 3 | AWB Co. | Faulty lights - multiple locations - see notes below | Electrical | Lighting, Internal | 797.5475 | Pass | Fail | -1 | 4 | 865.5 | 2022-05-09 16:39 | 2022-05-16 17:00 | 2022-05-10 06:00 | 2022-05-16 17:00 | 2022-06-15 07:30 |  | WCAPPR | Attended site and signed in, completed jsa,located strip lighting in corridor on level 2, removed ceiling panel and wired in new power pack, lights now working as intended, replaced ceiling tile, packed up, completed paperwork, signed out ***job completed***
MSA-DTWD | WA5238570 | 3 | AWB Co. | N block - 2 x Security lights out Campus grounds around N block | Electrical | Lighting, External | 3454.32 | Pass | Fail | -1 | 4 | 865 | 2022-03-16 07:37 | 2022-03-22 17:00 | 2022-03-17 12:45 | 2022-03-22 17:00 | 2022-04-22 13:45 |  | WCAPPR | Attended site and signed in. Signed onto jsa. Spoke to taeo about job. Went over to work are and double checked all parts we needed while we waited for excavator to arrive. Went to whole sale to get parts required for job. Returned to site. Discussed with excavator guy where trench was going when he arrived. Spotted excavator and dug around any tree roots as he went. Hit water pipe. Had to find get in and kink the pipe to stop water supply, temporary fix until plumber can come out. Met with AJ on site and he called plumber to come and fix later on in the day. After trench had been dug we laid conduits out and rang cable through it. Brought corrie up to wall one end and brought corrie up to light pole on the other end. Plumber arrived and fixed leak. Saddled light pole and made entry for j box, mounted j box and connected up cables in light pole. Saddled conduit onto wall outside building. Mounted pe cell base. Went inside and ran cable to pe cell and brought cable we ran last visit to
MSA-DTWD | WA5706125 | 3 | Protek 24/7 Building & Maintenance | Water leaking from ceiling next to A/C ceiling unit | Building | Ceiling | 1225.72 | Pass | Fail | 0 | 5 | 865 | 2022-08-11 08:39 | 2022-08-18 17:00 | 2022-08-16 08:30 | 2022-08-18 17:00 | 2022-09-21 09:30 |  |  | • Attend site, sign in & establish work zone• Remove and dispose of dilapidated Dek-tites• Supply and install new dry-pan flashing & fixings to roof to provide additional cover• Supply and install new dek-tites to A/C penetrations and seal• Remove and dispose of 2x damaged ceiling tiles• Supply and install 2x ceiling tiles
MSA-DTWD | WA5308414 | 3 | Water2water Pty Ltd | BF20 Kitchen - Tap for boiling water system sometimes does not always turn off fully & cont to run | Plumbing & Drainage | Water | 373.485 | Pass | Fail | 0 | 5 | 864.3333 | 2022-04-08 11:47 | 2022-04-19 17:00 | 2022-04-19 12:10 | 2022-04-19 17:00 | 2022-05-25 12:30 |  | WACCES | New spindle for tap required. Extremely difficult part to locate. Restarted works 11.30am 25/5 and completed 12.30pm 25/5Replaced spindle.
MSA-DFES | WA5836902 | 3 | Australian HVAC Services Pty. Ltd. | Air Conditioner in Server room leaking water onto the floor | Air Conditioning | Room Air Conditioners | 353.025 | Pass | Fail | -1 | 4 | 864.25 | 2022-09-07 15:53 | 2022-09-14 17:00 | 2022-09-07 16:00 | 2022-09-14 17:00 | 2022-10-13 16:15 |  | WACCES | Drips fixed.
MSA-DTWD | WA5689851 | 2 | AWB Co. | L1 ladies toilet, water leak | Roofing | Rooflights and Skylights | 2835.47 | Pass | Fail | 0 | 5 | 863.6667 | 2022-08-02 14:21 | 2022-08-05 17:00 | 2022-08-02 14:50 | 2022-08-05 17:00 | 2022-09-07 14:30 |  |  | Re-secured lead flashing and sealedSealed gaps found between flashings.Recommend new wakaflex flashing BRAF to followPicked up materials and delivered to siteInstalled wakaflex flashing from gutter line to top of metal flashing and sealed.
MSA-DFES | WA5735509 | 3 | Australian HVAC Services Pty. Ltd. | Administration building - lecture room 3 & 4 - air con in error | Air Conditioning | Room Air Conditioners | 2456.21 | Pass | Fail | -1 | 4 | 863.5 | 2022-08-16 13:28 | 2022-08-23 17:00 | 2022-08-16 13:30 | 2022-08-23 17:00 | 2022-09-21 13:00 |  |  | No further faults can be found.
MSA-DFES | WA5761270 | 1 | Go Doors | Gate D008 - gate open and will not close - not responding to FOB or swipe cards | Building | Steel Fencing & Gates | 939 | Pass | Fail | 0 | 5 | 863 | 2022-08-18 07:44 | 2022-08-18 17:00 | 2022-08-18 11:00 | 2022-08-18 17:00 | 2022-09-23 10:00 |  |  | Please see attachments.
MSA-DCA | WA5108377 | 2 | Techworks Electrical | Main Building - Ground Level – Back of House - see details below | Electrical | General Electrical | 414 | Pass | Fail | 0 | 5 | 863 | 2022-02-08 13:16 | 2022-02-11 17:00 | 2022-02-10 10:00 | 2022-02-11 17:00 | 2022-03-18 09:00 |  | WACCES | COMPLETED REPLACEMENT
MSA-DFES | WA6166030 | 2 | AHS Services WA Pty Ltd (Anchor) | Outside yard area - Foam Separation Unit is not working - See notes below | Plumbing & Drainage | Water | 5046.685 | Pass | Fail | 0 | 5 | 863 | 2022-11-11 11:37 | 2022-11-16 17:00 | 2022-11-14 10:30 | 2022-11-16 17:00 | 2022-12-20 09:30 |  | WACCES | Located pump under bin..Had to get moved.Tried but unable to lift lid.Will return with second person.Spoke to manufacturers about fault on control box..waiting to hear back.Picked up new gauge15/11.lifted pit lid to access pump.Found check valve faulty.Picked up materials,removed and replaced.Unit still not working when turned back on..Had an electrician come out and he found backwash pump loose and not working.Removed pump and took to Perth rewinds to get looked at.Had to strip down and clean out all the solenoids on the unit,found to be full of sand.Turned unit back on and tested.Also replaced damaged gauge.22-11. Returned as high alarm showing.cleaned out pit and reset control box.Found control box flashing.Arranged to meet electrian to check over.25/11 Electrician checked over all power-found to be all good.20/12.Met electrician on site and reconnected backflow pump.Repositioned floats and tested -all good
MSA-DFES | WA5609174 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Lights faulty - See notes below | Electrical | Lighting, Internal | 483.365 | Pass | Fail | 0 | 5 | 862.75 | 2022-07-13 14:42 | 2022-07-20 17:00 | 2022-07-18 12:15 | 2022-07-20 17:00 | 2022-08-23 11:00 |  | WACCES | Continued onsite at 9:00 to install final lights to close out job. Found some lights had already been replaced under seperate jobs. Only used parts necessary to complete tasks mentioned in original job that hadn’t already been replaced. Liased with staff onsite to confirm all lighting was corrected. Left site at 11:00
MSA-DCA | WA5572544 | 1 | Techworks Electrical | James street Entrance - Bollards on James street - Compressor making weird noise | Equipment | Electrical Equipment | 341.91 | Pass | Fail | 0 | 5 | 861.5 | 2022-06-30 08:24 | 2022-07-01 17:00 | 2022-06-30 15:30 | 2022-07-01 17:00 | 2022-08-05 13:00 |  | WACCES | Inspected compressor and found a release valve was stuck open, so the compressor motor was running trying to pump air into the system the same time the release valve was open.. Replaced parts and compressor now working
MSA-DTWD | WA5582912 | 3 | ACTION GLASS & ALUMINIUM | Library - Ramp balustrade glass smashed | Glazing | Glass wall | 1116.55 | Pass | Fail | -1 | 4 | 861.5 | 2022-07-04 09:10 | 2022-07-11 17:00 | 2022-07-05 11:00 | 2022-07-11 17:00 | 2022-08-10 08:30 |  |  | ATTENDED SITE TO ASSESSRETURNED LATER DATE WITH 2 MEN SUPPLIED & FIT NEW GLASS PANEL TO BALUSTRADE12MM CLEAR TOUGHENED SAFETY GLASS SHAPED1-906 X 1174POLISHED EDGESBLACK SILICONE AND DOUBLE SIDED TAPE USEDAS PER APPROVED BRAF
MSA-DTAG | WA6126887 | 0 | Midolo Building Services | nterview Rooms 1 & 4 Fault description Damage to walls (holes have been made)-see notes | Building | Internal Walls | 14365.78 | Pass | Fail | 0 | 5 | 860.5 | 2022-10-25 14:55 | 2022-10-25 16:55 | 2022-10-25 15:00 | 2022-10-25 18:55 | 2022-11-30 11:30 |  | WACCES | repairs to walls completed
MSA-DTWD | WA5091702 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block South East corner of building has a blocked drain | Plumbing & Drainage | Drainage |  | Pass | Fail | 0 | 5 | 860.3 | 2022-01-27 10:24 | 2022-02-01 17:00 | 2022-01-31 12:28 | 2022-02-01 17:00 | 2022-03-08 08:46 |  |  | braf not approvedGood MorningAre we able to please request that work order WA5091702 be closed for $0.00.The fault was rectified however I believe this was included in the times for the signature slip under WA5086876.regardsAndrew PageAHS Services WA Pty Ltd
MSA-DTAG | WA6467752 | 3 | Australian HVAC Services Pty. Ltd. | Level 4- Plantroom- Old cooling tower see notes | Air Conditioning | Cooling Tower | 3170.54 | Pass | Fail | -1 | 4 | 859.7333 | 2023-01-17 15:16 | 2023-01-24 17:00 | 2023-01-17 15:17 | 2023-01-24 17:00 | 2023-02-22 11:01
MSA-DTAG | WA6425747 | 1 | Midolo Building Services | Custody Area - Basement - Stairwell - Handrail is wobbly - See Notes Below | Building | Steel Work | 341.72 | Pass | Fail | 0 | 5 | 859.5 | 2023-01-12 11:27 | 2023-01-13 17:00 | 2023-01-12 13:15 | 2023-01-13 17:00 | 2023-02-17 08:45 |  | WACCES
MSA-DTWD | WA6148717 | 2 | Securex Security Systems & Services | Ground - Admin Office - Security door controller software showing offline - See notes | Security | Access Control | 730 | Pass | Fail | 0 | 5 | 848.25 | 2022-11-04 08:10 | 2022-11-09 17:00 | 2022-11-09 08:00 | 2022-11-09 17:00 | 2022-12-14 16:15 |  |  | (09/11/2022) - Work NoteClient unable to access Titan. Checked IP addresses in Titan and challenger. Rebooted system but still no access.Possible Tecom panel issue.(01/12/2022) - Work NoteNot able to complete(14/12/2022)Found management software IP address was wrong on the challengerUpdated IP address on keypadConnected network cable of challenger panel to switch (port 17)All ok
MSA-DTAG | WA5053257 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Registry – Clerk Typist area - no cool airflow | Air Conditioning | Room Air Conditioners | 1666.83 | Pass | Fail | 0 | 5 | 846 | 2022-01-18 14:37 | 2022-01-19 17:00 | 2022-01-19 08:00 | 2022-01-19 17:00 | 2022-02-23 14:00 |  | WACCES | Works complete
MSA-DTWD | WA5390166 | 2 | High Tech Pest Control | Entrance Driveway – Hayman Road -Existing Bee relocation box on site – needs monitoring & relocating | Pest Control | General Pest | 779.5 | Pass | Fail | 0 | 5 | 846 | 2022-05-02 10:36 | 2022-05-05 17:00 | 2022-05-04 08:00 | 2022-05-05 17:00 | 2022-06-08 14:00 |  |  | Bee Relocation - Entrance Haymand Rd Driveway including Monitoring.Removed.
MSA-DTWD | WA5693495 | 2 | M Construction (WA) | T2 Classroom - Roof leak at ridge cap level - See notes below | Roofing | Metal Roofing | 1547.92 | Pass | Fail | -1 | 4 | 845.5 | 2022-08-04 12:54 | 2022-08-09 17:00 | 2022-08-05 11:30 | 2022-08-09 17:00 | 2022-09-09 17:00 |  | WACCES | As per scope
MSA-DTWD | WA5693501 | 2 | M Construction (WA) | Water leak - see notes | Roofing | Metal Roofing | 1113.42 | Pass | Fail | -1 | 4 | 845.5 | 2022-08-04 12:57 | 2022-08-09 17:00 | 2022-08-05 11:30 | 2022-08-09 17:00 | 2022-09-09 17:00 |  | WACCES | Completed as per scope
MSA-DTWD | WA5588228 | 2 | Falcetta Plumbing and Gas | Hot water system not working | Plumbing & Drainage | Water | 2370 | Pass | Fail | -1 | 4 | 845 | 2022-07-07 12:53 | 2022-07-12 17:00 | 2022-07-08 10:00 | 2022-07-12 17:00 | 2022-08-12 15:00 |  |  | Removed faulty unit and installed equivalent replacement
MSA-DTAG | WA5369097 | 3 | Sapio Pty Ltd | Entrance desk ( Fish bowl ) - PA System not operational | Security | Security Management System | 1251.4 | Pass | Fail | -1 | 4 | 844.5 | 2022-04-19 16:53 | 2022-04-27 17:00 | 2022-04-21 08:30 | 2022-04-27 17:00 | 2022-05-26 13:00 |  |  | Replaced PA Handset in Security (Fish Bowl), configured settings and tested with Security.
MSA-DFES | WA5288940 | 3 | Protek 24/7 Building & Maintenance | Ground - Main Administration - First Aid Room - external door has cracks and is starting to break | Building | Doors | 1591.5 | Pass | Fail | -1 | 4 | 843.75 | 2022-03-23 16:45 | 2022-03-30 17:00 | 2022-03-24 11:45 | 2022-03-30 17:00 | 2022-04-28 15:30 |  | WACCES | Supplied & Installed new Rebated Door
MSA-DTAG | WA6151909 | 3 | MALCO FLOORING PTY LTD | Ground - Carpet in custody office is threadbare in places posing an OSH issue | Flooring | Carpet | 1555 | Pass | Fail | -1 | 4 | 843.6333 | 2022-11-07 09:50 | 2022-11-14 17:00 | 2022-11-09 08:30 | 2022-11-14 17:00 | 2022-12-14 12:08 |  |  | GROUND CARPET IN CUSTODY OFFICE IS THREADBARE IN PLACES POSING AN OSH ISSUE.REPLACED
MSA-DTAG | WA5395379 | 1 | AWB Co. | Basement - Cell 4 - Custody - light and plastic cover -may need replacing h | Electrical | General Electrical | 2005.436 | Pass | Fail | 0 | 5 | 842.25 | 2022-05-05 12:38 | 2022-05-06 17:00 | 2022-05-06 07:00 | 2022-05-06 17:00 | 2022-06-10 09:15 |  | WACCES & WCAPPR | Attended site and signed in, completed jsa,got keys from security at front desk, went down to cell area and spoke with security, got smoke alarms turned off, isolated lighting and removed old fitting, cut out part of ceiling so new light would fit , moved timber, mounted new light, connected light and re energised circuit, put cover on and siliconed th3 outside to the fitting, cleaned up, packed up, completed paperwork, signed out returned keys, ***job completed***claim matched to BRAF
MSA-DTAG | WA5472229 | 1 | Midolo Building Services | Room 217 Flooding in room from the roof | Building | Ceiling | 1013.91 | Fail | Fail | 0 | 5 | 842.25 | 2022-05-23 16:06 | 2022-05-24 17:00 | 2022-05-25 07:45 | 2022-05-24 17:00 | 2022-06-29 10:00 |  | WACCES | unblocked drain, dried carpet, painted
MSA-DTWD | WA5982470 | 1 | AWB Co. | Cafeteria - Hole in ceiling - see notes below | Building | Ceiling | 5607.4625 | Pass | Fail | 0 | 5 | 841.75 | 2022-09-30 11:19 | 2022-10-01 11:19 | 2022-09-30 13:15 | 2022-10-01 11:19 | 2022-11-04 15:00 |  |  | Works completed
MSA-DTWD | WA4991030 | 3 | AWB Co. | Faulty power points middle row | Electrical | General Electrical | 986.555 | Pass | Fail | 0 | 5 | 841.5 | 2022-01-04 14:24 | 2022-01-11 17:00 | 2022-01-10 13:00 | 2022-01-11 17:00 | 2022-02-14 14:30 |  | WACCES & WCAPPR | Attended site and signed in. Completed JSA. Located classroom. Supplied and replace all double GPOs with new quad GPOs down middle strip of classroom. Notified fm of works completed. **job complete**
MSA-DTAG | WA5869407 | 3 | Sapio Pty Ltd | Liaise with Dell for warranty purposes in relation to the ongoing RAID issue with NVR’s | Security | Security Management System | 1172.84 | Pass | Fail | -1 | 4 | 841.5 | 2022-09-14 13:41 | 2022-09-21 17:00 | 2022-09-14 15:00 | 2022-09-21 17:00 | 2022-10-19 16:30 |  |  | WA - Sasa Nikolic (19/10/2022) - Work NoteUpgraded firmware to Dell NVR 1 Custodial server as per Dell technical support, to:BIOS 2.15.0Controller PERC H730 Mini 25.5.9.0001 andiDRAC8 2.83.83.83 Build 5Checked NVR status. No fault present.
MSA-DTWD | WA5081363 | 2 | ACTION GLASS & ALUMINIUM | External - D Block - D-Block external G/Floor North East corner of building has a broken glass panel | Building | Windows | 521.8 | Pass | Fail | -1 | 4 | 841.1167 | 2022-01-20 13:16 | 2022-01-25 17:00 | 2022-01-21 09:15 | 2022-01-25 17:00 | 2022-02-25 10:22 |  | WACCES | ATTENDED SITE TEMP GLAZED BROKEN PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-551 X 947RETURNED LATER DATE TO REGLAZE6MM CLEAR TOUGHENED SAFETY GLASS PAINTED DARK GREY TO MATCH1-551 X 947
MSA-DFES | WA5578571 | 2 | AWB Co. | Kitchen right hand stove cupboard door - cupboard is damaged | Building | Internal Walls | 1149.3825 | Pass | Fail | 0 | 5 | 841.1 | 2022-07-01 13:09 | 2022-07-06 17:00 | 2022-07-06 07:42 | 2022-07-06 17:00 | 2022-08-10 08:48 |  |  | Works completed
MSA-DTWD | WA5674383 | 2 | Protek 24/7 Building & Maintenance | Roof leak in center of room near air con vent | Roofing | Metal Roofing | 1223.57 | Pass | Fail | 0 | 5 | 841 | 2022-07-21 11:34 | 2022-07-26 17:00 | 2022-07-25 10:30 | 2022-07-26 17:00 | 2022-08-29 11:30 |  | WACCES | ? Supply and install dry pan flashing to A/C unit? Remove and dispose of deck tights to A/C Unit fittings? Supply and install new deck tights and fixings? Complete water-test once works complete
MSA-DTAG | WA5780787 | 2 | Australian HVAC Services Pty. Ltd. | Air conditioning vent appears to be blowing out warm air instead of cool. | Air Conditioning | Room Air Conditioners | 2069.36 | Pass | Fail | -1 | 4 | 840.5 | 2022-08-19 12:20 | 2022-08-24 17:00 | 2022-08-19 14:30 | 2022-08-24 17:00 | 2022-09-23 15:00 |  |  | Attend site with icon logic. Organise access to level 7 VAV 7.10. Isolate box, disconnect wiring and remove failed controller. Install new controller and wire up. Replace old sensor in court room with new. Program controller and commission operation. Box now working ok
MSA-DCA | WA5697987 | 2 | Protek 24/7 Building & Maintenance | Leak coming from ceiling in toilet - See notes below | Building | Ceiling | 1269.77 | Pass | Fail | 0 | 5 | 840.25 | 2022-08-09 13:31 | 2022-08-12 17:00 | 2022-08-11 12:30 | 2022-08-12 17:00 | 2022-09-15 12:45 |  | WACCES | Remove flashing on roof to access open areas under the flashing and seal then replace flashing Remove old silcone from around duct penetrations clean area and resealRemove and install 2 new dektites
MSA-DTWD | WA5010352 | 2 | Protek 24/7 Building & Maintenance | C Block - Ground Floor - Fire exit door near stair - latch on emergency exit door is faulty | Building | Fire Door | 1930.355 | Pass | Fail | 0 | 5 | 840.25 | 2022-01-12 12:47 | 2022-01-17 17:00 | 2022-01-14 13:00 | 2022-01-17 17:00 | 2022-02-18 13:15 |  | WACCES | install new door
MSA-DTWD | WA5674532 | 3 | Protek 24/7 Building & Maintenance | AF 11 - Grill has fallen from roof apex. Access via roof | Building | Ceiling | 1362 | Pass | Fail | 0 | 5 | 840.25 | 2022-07-21 12:23 | 2022-07-28 17:00 | 2022-07-28 13:45 | 2022-07-28 17:00 | 2022-09-01 14:00 |  | WACCES | replace frill in roof
MSA-DTWD | WA6190691 | 1 | SCAVENGER SUPPLIES PTY LTD | EWIS alarm sounding low battery power. | Fire Protection Services | Fire Protection - Monitor System | 3304.45 | Pass | Fail | 0 | 5 | 840 | 2022-11-16 10:00 | 2022-11-17 17:00 | 2022-11-16 13:00 | 2022-11-17 17:00 | 2022-12-21 13:00 |  | WACCES | INITIAL VISIT - 16/11/22 - SEE JOB REPORT- Priority 1* Call out charge for DTWD,DOES,DOEN,DLGSC (Refer to Schedule 3 - Scope of work)- 1.5 Hours on site 16/11/22*Second visit required for further investigation. POSSIBLE BRAF-emailed BR re review22/11/2022-BRAF SUBMITTED-NEW POWER SUPPLY/CHARGER TO BE ORDERED ON APPROVAL-BR23/11/2022- VERBAL APPROVAL GIVEN BY DON GILENO-PARTS TO BE ORDEREDBRAF APPROVED-24-11-22PARTS ORDERED PO 9278 23/11/22 -SC-7892Difficulty in getting power supply possible re-quote for whole new system
MSA-DCA | WA5768637 | 1 | EQUANS Mechanical Services (WA) Pty Limited | North/East Corner - No Power to Dampers | Electrical | General Electrical | 315.315 | Fail | Fail | 1 | 6 | 839.65 | 2022-08-18 15:09 | 2022-08-19 17:00 | 2022-08-24 11:00 | 2022-08-19 17:00 | 2022-09-28 10:39 |  |  | Completed
MSA-DTWD | WA5301388 | 1 | Precise Air Group | K block - K02 - Commercial Refrigerated display case not working | Refrigeration | Refrigerators | 1375.53 | Pass | Fail | 0 | 5 | 838.8833 | 2022-04-01 08:43 | 2022-04-04 17:00 | 2022-04-01 10:00 | 2022-04-04 17:00 | 2022-05-06 08:53 |  |  | Attended supplier and collected parts. Attended site and completed pre start paperwork and signed in. Accessed display fridge and completed controls retrofit. Removed old control system and installed new relay board, controller and temp probes. Checked over works and test ran system. Found all components to operate as required. Some wiring also had to be altered. Observed system run with out fault. Left all ok. No further works required.
MSA-DTWD | WA5438156 | 2 | Techworks Plumbing | Solenoid Failed during power cut - water flow isolated | Plumbing & Drainage | Water | 1384.82 | Pass | Fail | 0 | 5 | 838.5 | 2022-05-16 12:47 | 2022-05-19 17:00 | 2022-05-17 13:00 | 2022-05-19 17:00 | 2022-06-21 11:30 |  |  | Attended site at murdock tafe and signed into the office. Spoke to Peter he told us the issue and what was going on, we went to level two staff toilets to test and make sure it was the same issue with the power cells that we had on level one student toilets. We tested by taking one of the working urinals power cells and plugged it into the urinals that was running. Power cell made solenoid close and the urinal worked fine so we could be positive that this was the issue.We spoke to Peter and he asked us to grab a few of them at the supplier in case more go in the future. We will go and order some from Reece and have them sent to the yard and we will be back to have them fixed. We signed out and completed paperwork21/6 - Attended Signed in The lady in office escorted us to the toilet Found the urinal that wasn't working Grabbed the ladder to go in the man hole Replaced the sensor Did some test flushes and its back working order Signed out and left
MSA-DTAG | WA5861350 | 1 | Automatic Fire Protection (ARA) | ground main fire panel - Fire panel beeping with an “Earth Fault Alarm” | Fire Protection Services | Fire Protection - Monitor System | 638.755 | Pass | Fail | 0 | 5 | 838.5 | 2022-09-13 08:56 | 2022-09-14 17:00 | 2022-09-13 09:00 | 2022-09-14 17:00 | 2022-10-18 07:30 |  | WCAPPR | 13/09/2022earth fault found on main fipnarrowed down to earth fault on loop 2located detector l2 d117 ground lift lobby full of water due to leak in ceiling (photos attached)bypassed detector until leak is fixed and isolated on fip.18/10/22Detector already re installed on arrival. No works performed.
MSA-DFES | WA4986160 | 1 | Australian HVAC Services Pty. Ltd. | Officer's Dorm - Air-con dorm is faulty | Air Conditioning | Room Air Conditioners | 3177.585 | Pass | Fail | -1 | 4 | 838 | 2021-12-31 10:44 | 2022-01-04 17:00 | 2021-12-31 14:00 | 2022-01-04 17:00 | 2022-02-04 12:00 |  |  | Attended site and inspected ac5 in officers dorm. Found system showing L5 fault. Inspected Outdoor system and found inverter pcb faulty. Called supplier and found these parts are no longer available. Replacement system will be required. Braf to be submitted.Replaced unit as per braf.
MSA-DTWD | WA5094935 | 2 | Equans Mechanical Services Australia | B Block - Second level - Split AC has lower condenser fan fault | Air Conditioning | Room Air Conditioners | 597.19 | Pass | Fail | 0 | 5 | 838 | 2022-01-31 16:51 | 2022-02-03 17:00 | 2022-02-02 12:00 | 2022-02-03 17:00 | 2022-03-09 10:00 |  | WACCES | Located under ceiling cassette and test ran and unit faulted with a E7 fault. Checked over condenser and found that the lower condenser fan had failed causing the E7 fault. To source parts and once available to return and fit. Part to come from East. RETURNED TO SITE AND FITTED PART
MSA-DTWD | WA5472777 | 3 | AWB Co. | We have a water leak in the roof of E609 Midland | Roofing | Metal Roofing | 3780 | Pass | Fail | -1 | 4 | 837.5 | 2022-05-24 10:29 | 2022-05-31 17:00 | 2022-05-26 14:30 | 2022-05-31 17:00 | 2022-06-30 12:00 |  |  | investigated leak.measured to remove 4 ducted collumns and drypan over
MSA-DTAG | WA6000647 | 2 | Sapio Pty Ltd | Magistrate Dewsbury’s Chamber - Replace duress alarm - see notes below | Security | Security Management System | 4182.78 | Pass | Fail | 0 | 5 | 837 | 2022-10-10 09:24 | 2022-10-13 17:00 | 2022-10-10 13:00 | 2022-10-13 17:00 | 2022-11-14 10:00 |  | WCAPPR | Tested duress button and confirmed correct operation
MSA-DCA | WA5656655 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Ngalang Koort - Ground Level - Picket Walkway (Corridor) - faulty air con sensor - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 945 | Pass | Fail | 0 | 5 | 835.5 | 2022-07-18 16:11 | 2022-07-21 17:00 | 2022-07-21 13:30 | 2022-07-21 17:00 | 2022-08-25 09:00 |  |  | Honeywell replaced faulty sensor and tested, all ok. Completed paperwork.
MSA-DTAG | WA5142144 | 0 | Australian HVAC Services Pty. Ltd. | Room adjacent to Court 9 - Split-system airconditioning unit in room adjacent to Court 9 is leaking | Air Conditioning | Room Air Conditioners | 1105.15 | Pass | Fail | 0 | 5 | 834.5 | 2022-02-16 13:54 | 2022-02-16 15:54 | 2022-02-16 14:00 | 2022-02-16 17:54 | 2022-03-23 08:30 |  |  | 40678Pick up pump from supplier. Attend site. Access switchboard and isolate AC unit serving room 101. Access room 101 AC unit and dismantle. Remove pipework ducting. Access passage and remove panels from above fire door. Access pump and disconnect electrical feed and piping. Disconnect sensor wire. Access unit and remove sensor wires and pull through. Run new sensor wire to pump and connect. Connect electrical wiring and pipework to new pump. Deisolate AC unit and test operation. Found new pump to start and operate as normal. Reassemble unit. Replace panel and clean up area.
MSA-DTWD | WA5565262 | 3 | Falcetta Plumbing and Gas | B402 - Boiler Room - Water filter damaged/leaking | Plumbing & Drainage | Water | 1882.045 | Pass | Fail | -1 | 4 | 824.5 | 2022-06-21 16:54 | 2022-06-28 17:00 | 2022-06-24 11:00 | 2022-06-28 17:00 | 2022-07-28 19:30 |  | WACCES | replaced free standing filter with equivalent and custom stand
MSA-DFES | WA6111578 | 1 | Anvil Doors | Front centre roller door - spring has broken and roller door won't open or close | Building | Security Doors | 4968.75 | Pass | Fail | 0 | 4 | 823.75 | 2022-10-21 08:56 | 2022-10-24 17:00 | 2022-10-21 12:25 | 2022-10-24 17:00 | 2022-11-24 20:10 |  |  | Spring has snapped, Spring has been removed for exact replacement. Job pending quotationWork is now complete 24.11.2022
MSA-DFES | WA5108642 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Male toilet - male toilet sink leaking | Plumbing & Drainage | Water | 1534.765 | Pass | Fail | 0 | 5 | 823.6833 | 2022-02-08 15:41 | 2022-02-11 17:00 | 2022-02-11 13:04 | 2022-02-11 17:00 | 2022-03-17 20:45 |  |  | Re attend site to remove old failed ball valve and install new ball valve assembly
MSA-DTWD | WA5673063 | 1 | Equans Mechanical Services Australia | AF04 is taking all day to heat up - see notes below | Air Conditioning | Room Air Conditioners | 1945.115 | Pass | Fail | 0 | 5 | 823 | 2022-07-20 11:54 | 2022-07-21 17:00 | 2022-07-21 08:00 | 2022-07-21 17:00 | 2022-08-24 15:00 |  |  | UNIT CONTINUALLY LEAKING UNDER TESTS. NOT WORTH REPAIRING - REQUIRES REPLACEMENT
MSA-DFES | WA5696842 | 2 | Protek 24/7 Building & Maintenance | Gym - Water Leaking from skylight - Water damaging ceiling | Building | Ceiling | 1619.11 | Pass | Fail | 0 | 5 | 819.5 | 2022-08-08 15:19 | 2022-08-11 17:00 | 2022-08-09 10:00 | 2022-08-11 17:00 | 2022-09-12 13:30 |  | WACCES & WCAPPR | Clean and re-seal silicone between roof sheet and skylightSupply and install drypan flashing and fixingsRemove mould from ceiling and patchStain block and patch/paint ceiling
MSA-DFES | WA5109494 | 1 | Go Doors | Rear engine room door - motor has burnt out - see notes | Building | Automatic Doors | 3047.63 | Pass | Fail | 0 | 5 | 819.25 | 2022-02-09 10:37 | 2022-02-10 17:00 | 2022-02-09 12:15 | 2022-02-10 17:00 | 2022-03-15 15:30 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5693764 | 0 | WESTCOAST CONSTRUCTION & DEMOLITION | front - External door - damaged - vent kicked - please secure | Building | Doors | 889.84 | Fail | Fail | 0 | 5 | 818.6333 | 2022-08-04 14:58 | 2022-08-04 16:58 | 2022-08-05 08:55 | 2022-08-04 18:58 | 2022-09-08 11:33 |  |  | Our building technician attended site & brought plywood to board up the damaged door vent.He installed the plywood and measured up for a new grille to replace.The measurements came to 625mm x 320mm. There are no damages to the door.
MSA-DFES | WA5681655 | 3 | AWB Co. | Ground Floor - Meeting Room 1 - Leak in roof - See notes below | Roofing | Metal Roofing | 510.51 | Pass | Fail | -1 | 4 | 817.75 | 2022-07-28 13:49 | 2022-08-04 17:00 | 2022-07-29 09:15 | 2022-08-04 17:00 | 2022-09-01 11:00 |  | WACCES | Investigated area above suspected leak. Found anchor point over area with possible water entries through large rivet fixings. Found bolt fixings in sheets and silicone repair. Sealed anchor point fixings and renewed silicone repairs and sealed bolt fixings. Will have to return to replace ceiling tiles. Sourced and returned to replace ceiling tiles
MSA-DTWD | WA5471526 | 3 | Protek 24/7 Building & Maintenance | Wood workshop - Various leaks, various locations - Water Leak - Ceiling | Roofing | Metal Roofing | 994.73 | Pass | Fail | 0 | 4 | 816.5 | 2022-05-23 12:58 | 2022-05-30 17:00 | 2022-05-27 09:00 | 2022-05-30 17:00 | 2022-06-30 09:30 |  | WCAPPR | Replaced 4 Dektites with new ones
MSA-DFES | WA5518725 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Driving Simulator - Dome - near Heritage Shed - Power is tripping - See notes below | Electrical | General Electrical | 1974.6 | Pass | Fail | 0 | 5 | 816.25 | 2022-06-15 08:38 | 2022-06-22 17:00 | 2022-06-21 09:00 | 2022-06-22 17:00 | 2022-07-25 09:15 |  | WACCES | Continued on site at 0900 to investigate power tripping in driving simulator room. Located building and found 2 x local rcds on heritage shed supplying 3Phase supply for simulator room sub board, also discovered both 3Phase plugs on ground exposed to water. Opened both plugtops and cleared water from cables/terminals. Connected all cables for machines inside simulator rm and energised.No circuits tripped during investigation. Could not complete job due to p1 callout will need to return to site to continue investigation, informed staff and Left site at 1100.
MSA-DCA | WA6111630 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 is out of service | Refrigeration | Chiller | 1953.01 | Pass | Fail | -1 | 4 | 816 | 2022-10-21 09:27 | 2022-10-26 17:00 | 2022-10-21 13:00 | 2022-10-26 17:00 | 2022-11-24 13:00 |  | WACCES | Attended site and investigated chiller fault. Found both chillers operational and no faults displayed on touch panel. Chiller 1 is still running at 50% capacity due to compressor being tagged out of service in 2017. Airvision to attend site and check over faulty compressor and provide an updated quote.Airvision attended site and carried out testing. Compressor requires replacing. quote to be submitted. Completed paperwork
MSA-DFES | WA5295447 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Engine Room - Near BA Room - HWS is leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 1793.96 | Pass | Fail | 0 | 5 | 815.9167 | 2022-03-29 13:39 | 2022-03-30 17:00 | 2022-03-30 12:00 | 2022-03-30 17:00 | 2022-05-03 11:55 |  |  | Had replaces and upgraded 50lt hot water system to a 80lt hot water and redo all pipe work
MSA-DTWD | WA5677950 | 3 | Australian Airconditioning Services Pty Ltd | A/C has a noisy rattle | Air Conditioning | Room Air Conditioners | 930.09 | Pass | Fail | -1 | 4 | 815.5 | 2022-07-26 08:39 | 2022-08-02 17:00 | 2022-07-26 13:00 | 2022-08-02 17:00 | 2022-08-29 12:30 |  | WACCES | complete
MSA-DFES | WA5312514 | 2 | AWB Co. | Radio Communications - Ground - Project Room/Men's toilet - see details | Building | General Building | 1507.33 | Pass | Fail | 0 | 5 | 815.25 | 2022-04-11 14:42 | 2022-04-14 17:00 | 2022-04-14 11:30 | 2022-04-14 17:00 | 2022-05-18 10:45 |  | WCAPPR | Found perished down pipe pop- cleaned back and re sealed, found 2 x ac flashings and decktie not sealed clean back and sealedFitted drypan flashings to extraction vent.replaced ceiling tiles
MSA-DCA | WA5795159 | 2 | Protek 24/7 Building & Maintenance | B1 Basement Level - Entry Lobby - outer entry security/fire door is damaged - See notes below | Building | Fire Door | 508.7 | Pass | Fail | -1 | 4 | 815.25 | 2022-08-25 09:44 | 2022-08-30 17:00 | 2022-08-26 09:45 | 2022-08-30 17:00 | 2022-09-29 09:00 |  | WACCES | Remove and dispose of damaged door seal & fixingsSupply and install new door seal to match currently installed seal
MSA-DCA | WA4992323 | 1 | GPS Plumbing & Gas Services PtyLtd | Male toilet - increase waterflow to urinal | Plumbing & Drainage | Toilets/Cisterns | 740.5225 | Fail | Fail | 1 | 5 | 815.2333 | 2022-01-06 10:11 | 2022-01-07 17:00 | 2022-01-11 09:39 | 2022-01-07 17:00 | 2022-02-14 08:53 |  | WACCES | Replaced cartridge to urinal flushing valve
MSA-DTWD | WA4995261 | 2 | Techworks Electrical | C-Block room's C008, C010, C014, C208, C210, C216 all have broken floor skirting wire ducts | Electrical | General Electrical | 2963.01 | Pass | Fail | 0 | 5 | 814.7 | 2022-01-10 11:19 | 2022-01-13 17:00 | 2022-01-12 12:30 | 2022-01-13 17:00 | 2022-02-15 11:12 |  | WACCES | Measured skirting duct lid throughout C block .Waiting on duct lid to be delivered .Install skirting lid to rooms where missing. Screwed back all skirting in room to prevent further skirting falling off. Gave spare ducting to dave for future jobs. Duct systems did still have more ducting lid on back order
MSA-DTWD | WA5414051 | 3 | AWB Co. | Level 2 - carpark - Replace faulty PE cell to carpark external lighting | Electrical | General Electrical | 670.52 | Pass | Fail | 0 | 5 | 814.5 | 2022-05-12 16:22 | 2022-05-19 17:00 | 2022-05-18 11:30 | 2022-05-19 17:00 | 2022-06-21 10:00 |  | WACCES | Attended site signed in GSA completed. Installed pe sensor in Carpark and programmed by Sherlock electric programming company tested and commissioned all lighting is now operational.** job completed**
MSA-DFES | WA5673158 | 3 | Protek 24/7 Building & Maintenance | Straighten fence frame and replace damaged wire on 1 x gate caused by Contractor truck - see notes | Building | Steel Fencing & Gates | 1000 | Pass | Fail | -1 | 4 | 814.5 | 2022-07-20 12:44 | 2022-07-27 17:00 | 2022-07-21 13:00 | 2022-07-27 17:00 | 2022-08-24 11:30 |  | WACCES | Replace damaged Fence
MSA-DTWD | WA5869643 | 2 | AWB Co. | 6BFab2 - faulty power pendant | Electrical | Distribution Board | 2134.02 | Pass | Fail | -1 | 4 | 814.05 | 2022-09-14 15:02 | 2022-09-19 17:00 | 2022-09-15 14:27 | 2022-09-19 17:00 | 2022-10-19 12:30 |  |  | Work NoteAttended site and signed in. Completed jsa. Located metal fab workshop. Liaised with site about works going ahead. Found to be circuit overloaded. Suggest to install new seperate gpo.**will submit BRAF**Work NoteAttended site signed in jsa completed. Installed new cable from board in workshop along perling to drop down with jackchain into a 15a pendant outlet. Ceiling rose installed on trunking.tested alsoJob completed
MSA-DFES | WA6373494 | 2 | Go Doors | The manual over ride switch is playing up the northern/east end roller door - see notes below | Building | Doors | 2120.8 | Pass | Fail | -1 | 4 | 813.75 | 2022-12-14 14:29 | 2022-12-19 17:00 | 2022-12-15 12:45 | 2022-12-19 17:00 | 2023-01-18 10:30 |  | WACCES | Completed works. Please see attachments.
MSA-DTWD | WA5200205 | 2 | AWB Co. | Creche 3 x pagodas with shade cloth clips that are coming off & creating a sharp hazard for children | Building | External Walls | 168.75 | Pass | Fail | 0 | 5 | 813.2833 | 2022-03-01 15:47 | 2022-03-04 17:00 | 2022-03-03 13:00 | 2022-03-04 17:00 | 2022-04-06 10:17 |  |  | k NoteAttended site, filled out JSA, all pergolas rotten and unsafe to go on top, Theo would like a quote on installing all new.Spoke to Alex to follow up on doing a quote.Photos attached.BRAF declined for further works
MSA-DFES | WA5686714 | 2 | Go Doors | Location 12 – Engine Room-Bay 1 rear door operation button/remote open/close not functionin-see not | Building | Doors | 2393.6 | Pass | Fail | 0 | 5 | 813.25 | 2022-08-01 10:20 | 2022-08-04 17:00 | 2022-08-04 11:30 | 2022-08-04 17:00 | 2022-09-07 08:45 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5980363 | 3 | Protek 24/7 Building & Maintenance | Ground-Student dinning room-North entry door has lost some of the clear plastic strips | Building | Doors | 949.855 | Pass | Fail | -1 | 4 | 811.5 | 2022-09-29 14:20 | 2022-10-06 17:00 | 2022-09-30 13:30 | 2022-10-06 17:00 | 2022-11-03 09:00 |  | WACCES | Remove and replace plastic flap door
MSA-DTWD | WA6190938 | 1 | Precise Air Group | M Block - M004 - M005 - M006 - M007 - aircon not functioning in classrooms M block | Air Conditioning | Room Air Conditioners | 208.34 | Pass | Fail | 0 | 5 | 809.9333 | 2022-11-16 11:33 | 2022-11-17 17:00 | 2022-11-17 14:04 | 2022-11-17 17:00 | 2022-12-21 08:00 |  |  | Travelled to site checked in to facilities manager checked operation of M Block ,has been quoted for repairs or replacement waiting on approval.Attended site and spoke to facility manager about M block that has been attended to and quotes submitted.Works to be completed on another WO# WA5706228, BRAF has been submitted but not approved
MSA-DTWD | WA5700019 | 2 | Precise Air Group | Fridge is not getting cold. | Refrigeration | Refrigerators | 1781.27 | Fail | Fail | 0 | 5 | 808.4833 | 2022-08-10 14:02 | 2022-08-15 17:00 | 2022-08-16 14:18 | 2022-08-15 17:00 | 2022-09-19 06:47 |  |  | 15-09-22Attended site and signed in. Gained access to C block and fa ulty fridge. Reclaimed remaining refrigerant charge and pull ed half of the name plate charge. Pressure tested system and found leak on discharge line schrader valve. Released nitro gen and replaced with new valve, test again and found it hol ding. Evacuated system bellow 300 microns and system passed decay test. Weighed in refrigerant charge and tested fridge. Found it operating correctly and test cabinet to 2.5-3 C
MSA-DTWD | WA5680067 | 1 | Protek 24/7 Building & Maintenance | G10-Fault description Roof is leaking in center of room-see notes | Roofing | Metal Roofing | 2636.35 | Pass | Fail | 0 | 5 | 796 | 2022-07-27 09:37 | 2022-07-28 17:00 | 2022-07-28 07:00 | 2022-07-28 17:00 | 2022-08-30 11:00 |  |  | ? Remove and dispose of damaged roof flashings? Supply and install new flashings and seal? Confirm roof water-tight once works complete
MSA-DTWD | WA5288917 | 1 | AWB Co. | block 3 - ground - 3F - cold well pump shows cooling tower fan warning for low speed | Electrical | General Electrical | 5692.0075 | Pass | Fail | 0 | 5 | 795 | 2022-03-23 15:39 | 2022-03-24 17:00 | 2022-03-24 11:30 | 2022-03-24 17:00 | 2022-04-26 14:30 |  |  | Attended site signed in jsa completed. Installed motor and terminals fit off, belts put on and load tested. All passed and job completed
MSA-DTWD | WA5285887 | 2 | Ronley Holdings Pty Ltd | U Block - U024.3 - Air extraction system is faulty - see details below | Equipment | Building Equipment | 1300 | Fail | Fail | 1 | 6 | 794.5 | 2022-03-21 10:27 | 2022-03-24 17:00 | 2022-03-31 13:30 | 2022-03-24 17:00 | 2022-05-03 16:00 |  |  | There were two site visists. 1st by Ronley Holdings on 31/03/2022. 2nd by Ronley Holdings and Lasi Controls. Many issues were identified and a report along with pricing has been uploaded in to ProMap. Amount the 'Failures' was Alignment, Corrosion, Loose.
MSA-DCA | WA5833821 | 2 | Precise Air Group | Main Building - Lvl 1- Regional Arts Room Unit 5 - Please check aircon faults | Air Conditioning | Room Air Conditioners | 1616.14 | Pass | Fail | 0 | 4 | 794.3667 | 2022-09-06 12:01 | 2022-09-09 17:00 | 2022-09-07 11:00 | 2022-09-09 17:00 | 2022-10-10 13:22 |  |  | Attended site and gained access to studio 3. Check control switch and found no water. Accessed evap unit on the roof, found slight water pooling on top of the isolator. Isolator is weatherproof and still in ok condition. Opened isolator and found it all ok. Ran unit and checked over, operating correctly on inspection. We will continue to monitor on maintenance.
MSA-DTWD | WA5200141 | 3 | Milners Tree Solutions Pty Ltd | Carpark Sth - Dead tree in danger of falling on car or person | Landscaping & Gardening | Grounds Maintenance | 4000 | Pass | Fail | -1 | 4 | 792.5 | 2022-03-01 14:48 | 2022-03-09 17:00 | 2022-03-03 07:00 | 2022-03-09 17:00 | 2022-04-05 07:30 |  |  | dead trees removed. stump grinding
MSA-DFES | WA5394350 | 1 | Go Doors | Entrance Roller Doors - Door 1 - not closing automatically and not sealing properly | Building | Automatic Doors | 3506 | Pass | Fail | 0 | 5 | 792.5 | 2022-05-04 15:12 | 2022-05-05 17:00 | 2022-05-05 16:00 | 2022-05-05 17:00 | 2022-06-07 16:30 |  |  | Please see attachments
MSA-DCA | WA6375744 | 3 | Critical Fire Protection & Training | Retrospective Work Order - DO NOT ATTEND - faulty fire extinguisher replacement | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 213.84 | Pass | Fail | -1 | 4 | 792 | 2022-12-14 06:30 | 2022-12-20 17:00 | 2022-12-15 08:00 | 2022-12-20 17:00 | 2023-01-17 08:00 | 1 |  | Extinguisher was discharged by tenant.CF supplied new extinguisher only.After complete, site requested we return to install extinguisher in a new location.
MSA-MRWA | WA5193701 | 2 | TK Elevator Australia Pty Ltd | Level 5 -L5 West – Down call button sticking / Lift 1- Lift light out | Lifts | Lifts |  | Pass | Fail | -1 | 4 | 791.6667 | 2022-02-25 13:09 | 2022-03-02 17:00 | 2022-02-25 15:09 | 2022-03-02 17:00 | 2022-03-30 14:49 |  | WCAPPR | Replaced 1x28w fluro tube for car light. Opened and cleaned downhall button (West side). Tested button working. Put new button on order.
MSA-DCA | WA6503341 | 2 | ADVANCED LOCK & KEY | Jubilee Building - Ground Level - Reception inner entry door loose (see notes) | Security | Keys & Access | 551.11 | Pass | Fail | -1 | 4 | 789.25 | 2023-01-19 08:17 | 2023-01-24 17:00 | 2023-01-19 15:05 | 2023-01-24 17:00 | 2023-02-21 12:20 |  | WACCES
MSA-DTWD | WA5323618 | 1 | ACTION GLASS & ALUMINIUM | Unit 5 - West end entry doors - Lamination in glass damaged and door cant bee seen through | Building | Windows | 1031.8 | Pass | Fail | 0 | 5 | 789.1333 | 2022-04-13 09:42 | 2022-04-14 17:00 | 2022-04-14 14:00 | 2022-04-14 17:00 | 2022-05-17 11:08 |  |  | ATTENDED SITE TO MEASURE & ASSESSRETURNED LATER DATE REGLAZED 2 DOOR PANELS6.38 CLEAR LAMINATED SAFETY GLASS2-2000 X 7628 L/M OF RUBBER REPLACED PLUS 8 SCREWS
MSA-DTWD | WA5141531 | 1 | Precise Air Group | G Block - Level 1 - G108 - water dripping from Aircon Condensation onto chairs | Air Conditioning | Room Air Conditioners | 506.36 | Pass | Fail | 0 | 5 | 788 | 2022-02-16 10:54 | 2022-02-17 17:00 | 2022-02-16 13:30 | 2022-02-17 17:00 | 2022-03-21 09:30 |  |  | Picked up filter and returned to site. Fitted and test ran system. Disposed of old filter. Left running all ok. No further works required.
MSA-DTWD | WA6527961 | 3 | Protek 24/7 Building & Maintenance | Courtyard – center of campus-Uneven brick paving around courtyard – behind lunch tables | Paving & Roadworks | Paving | 473.835 | Pass | Fail | -1 | 4 | 784.75 | 2023-02-02 07:47 | 2023-02-08 17:00 | 2023-02-02 14:15 | 2023-02-08 17:00 | 2023-03-07 07:00
MSA-MRWA | WA6373495 | 1 | EQUANS Mechanical Services (WA) Pty Limited | pump room-failed pump | Plumbing & Drainage | Water | 5417.01 | Pass | Fail | 0 | 5 | 775.6667 | 2022-12-14 14:33 | 2022-12-15 17:00 | 2022-12-15 07:30 | 2022-12-15 17:00 | 2023-01-16 15:10 |  |  | During maintenance noted that pump 1 motor was very hot and noisy. Advised programmed. Advised duty pump no 2 out of action due to damaged coupling. Discussed ramifications on water supply to top floors and to cooling towers should pump 1 fail. Obtained permission to investigate damage to coupling. Found rubber grommets on bolts worn. Obtained permission to replace. ON testing found seal on pump leaking. Obtained permission to remove cassette and have seal replaced and pump overhauled. this strategy would minimize the need for realignment. However, unable to remove cassette as originally intended. As shafts to close to allow pump cassette to be removed. Had to remove pump end housing and thus any alignment. Brendan agreed to undertake and approve final manual alignment as he has expertise in this area.Found inlet and outlet almost completely blocked. Send pump off to be overhauls and cleaned out inlet and out let. Pump due back same day. However, on inspection it was found that the
MSA-DTWD | WA5381761 | 2 | BAKE-QUIP PTY LTD | - E-Block Restaurant kitchen the Dishwasher has a dislodged panel light | Equipment | Catering Equipment | 736 | Pass | Fail | 0 | 4 | 771.25 | 2022-04-26 11:24 | 2022-04-29 17:00 | 2022-04-28 07:30 | 2022-04-29 17:00 | 2022-05-30 10:45 |  | WACCES & WCAPPR | REFER TO SERVICE REPORT.
MSA-DTAG | WA5399220 | 3 | Midolo Building Services | L5 Damage/stains to ceiling tiles | Building | Ceiling | 466.92 | Pass | Fail | -1 | 4 | 770.75 | 2022-05-09 19:06 | 2022-05-16 17:00 | 2022-05-12 12:00 | 2022-05-16 17:00 | 2022-06-13 14:45 |  | WACCES & WCAPPR | ceiling tiles replaced
MSA-DCA | WA5566139 | 2 | ACTION GLASS & ALUMINIUM | Level 1 - Terrace Bar Corporate Lounge - Cracked windowpane | Glazing | Window Glass | 1319 | Pass | Fail | -1 | 4 | 770.5833 | 2022-06-22 15:44 | 2022-06-27 17:00 | 2022-06-23 11:40 | 2022-06-27 17:00 | 2022-07-25 14:15 |  |  | ATTENDED SITEPATCHED TO SECURE BROKEN WINDOW WITH SAFETY FILM 1-800 X 500RETURNED LATER DATE WITH 2 MEN TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-842 X 2028POLISHED EDGESTINT FILM APPLIED2 TUBES OF SILICONE USED FOR BUTT JOINS
MSA-DTWD | WA5301714 | 3 | Protek 24/7 Building & Maintenance | C block one section of gutter damaged North side | Roofing | Guttering | 556.2 | Pass | Fail | -1 | 4 | 770.25 | 2022-04-01 11:50 | 2022-04-08 17:00 | 2022-04-04 12:30 | 2022-04-08 17:00 | 2022-05-06 14:45 |  | WACCES | Replace section of Gutter
MSA-DTWD | WA5511741 | 3 | AWB Co. | Workshop B127 - Replace drummy and missing tiles | Flooring | Tiling | 3546.805 | Pass | Fail | -1 | 4 | 769.5 | 2022-06-13 08:26 | 2022-06-20 17:00 | 2022-06-16 07:00 | 2022-06-20 17:00 | 2022-07-18 08:30 |  |  | Craig Adams (11/07/2022) - Work NoteAttended site, signed in, filled out JSA started removing tile and disposed in to skip.Got called to a P1 for City of Canning.Mark Crewe (11/07/2022) - Work NoteSame as CraigCraig Adams (12/07/2022) - Work NotePicked up materials, attended site filled out JSA, installed tiles.Craig Adams (13/07/2022) - Work NoteAttended site, signed in, signed JSA,Removed all spacers and packers, grouted tiles and cleaned underneath all cabinets,Need to re attend to silicone around work tops. ( 1 x tube White silicone left on bench top )Mark Crewe (18/07/2022) - Work NoteReturned to clean around tiles and bench top then applied silicone between gaps to complete the job.Mark Crewe (16/06/2022) - Work NoteI have inspected the loose and damaged tiles in workshopB 127. The tiles on the splash backs have fallen off in places. After speaking with Dave he would like them all to be removed and replaced. The total length of the bench is just under eleven meters w
MSA-DFES | WA5413072 | 1 | Protek 24/7 Building & Maintenance | Station officers dormitory - Water leak from roof | Roofing | Metal Roofing | 948.88 | Pass | Fail | 0 | 4 | 769.25 | 2022-05-12 08:48 | 2022-05-13 17:00 | 2022-05-12 10:15 | 2022-05-13 17:00 | 2022-06-13 11:30 |  |  | Repair damaged roof tiles
MSA-DTAG | WA6538924 | 3 | Australian HVAC Services Pty. Ltd. | 2A - File Room - Check air flow in file room | Air Conditioning | Ducted Split System | 567.86 | Pass | Fail | -1 | 4 | 769 | 2023-02-08 09:16 | 2023-02-15 17:00 | 2023-02-09 08:00 | 2023-02-15 17:00 | 2023-03-13 09:00
MSA-DTWD | WA5836918 | 1 | High Tech Pest Control | Staff Carpark on Bank street-Large population of bees - see notes | Pest Control | General Pest | 1067.98 | Pass | Fail | 0 | 5 | 768.1667 | 2022-09-07 16:25 | 2022-09-08 17:00 | 2022-09-08 12:20 | 2022-09-08 17:00 | 2022-10-10 12:30 |  |  | Bee box has been removed & bees relocated.
MSA-DFES | WA5016846 | 2 | Water2water Pty Ltd | Second level, southside kitchen - Zip unit not working showing lights | Plumbing & Drainage | Water | 5577.68 | Pass | Fail | -1 | 4 | 767.3167 | 2022-01-13 08:10 | 2022-01-18 17:00 | 2022-01-13 15:45 | 2022-01-18 17:00 | 2022-02-14 15:04 |  |  | INSTALLED NEW CAPEX ASSET ZIP HYDROTAP 51702 INC FAN KIT REMOVED OLD TO TIP NEW ASSET PROG CODE A401914008 ZIP SERIAL NUMBER MANUFACTURERS 202201304026 Attended 13.1.22 - unit not repairable quoting to replaceUnit replaced
MSA-DTWD | WA5301719 | 3 | Protek 24/7 Building & Maintenance | D Block Gutters rusted through, leaking over doorway | Roofing | Guttering | 2467.24 | Pass | Fail | -1 | 4 | 767 | 2022-04-01 11:59 | 2022-04-08 17:00 | 2022-04-04 13:30 | 2022-04-08 17:00 | 2022-05-06 12:30 |  | WACCES | Replace leaking gutters
MSA-DFES | WA5982862 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Engine Bay 2 - Ceiling cable disconnected from ceiling | Electrical | General Electrical | 622.775 | Pass | Fail | -1 | 4 | 766.5 | 2022-09-30 15:25 | 2022-10-07 17:00 | 2022-10-03 10:00 | 2022-10-07 17:00 | 2022-11-04 08:30 |  | WCAPPR | Matthew Kenney (03/10/2022) - Work NoteArrived onsite at 10:00 to investigate fallen cable in engine bay 2, found that cable had been disconnected from track and was tagged out of service. Due to height of track a scissor lift is required to reconnect cable. Advised staff of what is required and left site at 10:30.Tasz Cumming (04/11/2022) - Work NoteArrived onsite and located damaged cableFolded back a section of the mini orb ceiling to reach other end of cable in ceiling and joined .Re-secured the catenary to unistrut and re-energized feedTested for correct operation.
MSA-DFES | WA5596752 | 2 | AWB Co. | Level 1 - Room 30 (Engine Bay) - water leaking through ceiling in the south eastern air vent | Roofing | Metal Roofing | 3458.24 | Pass | Fail | 0 | 4 | 765.5667 | 2022-07-11 10:15 | 2022-07-14 17:00 | 2022-07-11 12:35 | 2022-07-14 17:00 | 2022-08-12 10:09 |  |  | Craig Adams (26/07/2022) - Work NoteAttended site, photos attached,(ceiling 1 - 2) the ceiling is approximately 8m - 10m high, would require a scissor lift, cut 1m x1m section out of ceiling install new and flush ( not sure what type or thickness of plaster board ) until up there to examine. It’s also fine to close off one roller door if fire station does have a call out they said they can park other truck behind the other and use other entry roller door.Attended, required dry day.I Re-attended and investigated leak, found issues with fixings to extraction unit. Carried outrepairs
MSA-DTWD | WA5141307 | 2 | AWB Co. | Ceiling Fans not working | Electrical | General Electrical | 1678.97 | Pass | Fail | -1 | 4 | 765.5 | 2022-02-16 09:16 | 2022-02-21 17:00 | 2022-02-17 11:45 | 2022-02-21 17:00 | 2022-03-21 09:15 |  | WACCES | Attended site signed in completed jsa.Attached new jhook pole to new fan and connected to existing cables. Fan works correctly.***job completed***
MSA-DTAG | WA6362922 | 1 | Sapio Pty Ltd | Ground floor - Main door card reader is not reading - See Notes Below | Security | Access Control | 269 | Pass | Fail | 0 | 4 | 763.5 | 2022-12-09 15:21 | 2022-12-12 17:00 | 2022-12-09 16:30 | 2022-12-12 17:00 | 2023-01-10 12:00 |  |  | Cleared database issues related to ongoing Gallagher works. Reset Steve"s log in to server. Rectified 6.04 Office Door.
MSA-DTWD | WA5413948 | 2 | AWB Co. | tiling workshop - faulty high bay light | Electrical | General Electrical | 3973.76 | Pass | Fail | 0 | 4 | 752.75 | 2022-05-12 15:36 | 2022-05-17 17:00 | 2022-05-16 07:45 | 2022-05-17 17:00 | 2022-06-16 16:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,completed restart ewp check list, completed rescue plan, set up work area, removed old high bay lights and replaced with new, replaced faulty lights in bricklaying with new lights , all lights working as intended, off hired ewp , packed up, completed paperwork, signed out **job completed***
MSA-DCA | WA6535078 | 3 | GPS Plumbing & Gas Services PtyLtd | urinal not flushing | Plumbing & Drainage | Toilets/Cisterns | 1849.845 | Pass | Fail | -1 | 4 | 751.6667 | 2023-02-06 13:57 | 2023-02-13 17:00 | 2023-02-07 07:50 | 2023-02-13 17:00 | 2023-03-10 15:30 |  | WACCES
MSA-DFES | WA5694432 | 3 | Critical Fire Protection & Training | S/O’s Dorm 1 (closest to kitchen) - Fire door faulty - See notes below | Building | Fire Door | 161.765 | Fail | Fail | 1 | 5 | 749.4167 | 2022-08-05 10:04 | 2022-08-12 17:00 | 2022-08-16 08:05 | 2022-08-12 17:00 | 2022-09-16 13:30 |  | WACCES | Removed old door anvil as was split and anvil magnetic receiver ripped from mount. Replaced with new, supplied and installed new anvil to door and confirm correct operation of door magnet holder with door closer arms attached.
MSA-DFES | WA5995703 | 3 | Go Doors | RETROSPECTIVE WORK ORDER-Yard - Gate D007 (Gate#2) - Security Gate D007 motor is defective -see note | Building | Steel Fencing & Gates | 1118.91 | Pass | Fail | -1 | 4 | 747.5 | 2022-09-30 07:00 | 2022-10-06 17:00 | 2022-09-30 14:45 | 2022-10-06 17:00 | 2022-10-31 18:15 | 1 |  | Completed works. Please see attachments.
MSA-DTWD | WA6155156 | 2 | Australian Airconditioning Services Pty Ltd | External area roof - Daikin AC panel showing U4 Fault - see notes | Air Conditioning | Ducted Split System | 1966.7 | Pass | Fail | 0 | 4 | 747.5 | 2022-11-08 08:22 | 2022-11-11 17:00 | 2022-11-08 08:30 | 2022-11-11 17:00 | 2022-12-09 12:00 |  | WACCES | complete
MSA-DTAG | WA5085615 | 1 | Sapio Pty Ltd | Ground - Custody - Issue logging in to alarm programs / Cell 3 camera is blurry - see details below | Security | CCTV Surveillance | 1996.73 | Pass | Fail | 0 | 4 | 747 | 2022-01-21 09:22 | 2022-01-24 17:00 | 2022-01-21 11:00 | 2022-01-24 17:00 | 2022-02-21 14:00 |  |  | Reset Gallagher security basenent office login after lockout due to failed attempts.Cell3 has a standard camera in a housing rather than a corner cell camera. Due to this the lightevel and the picture is different.
MSA-DCA | WA5683012 | 1 | Techworks Electrical | City room - mistor water feature has lost power | Electrical | General Electrical | 422.34 | Pass | Fail | 0 | 4 | 747 | 2022-07-29 14:41 | 2022-08-01 17:00 | 2022-08-01 13:00 | 2022-08-01 17:00 | 2022-09-01 16:00 |  |  | Isolated lump as this was causing the issue.
MSA-DTWD | WA5413562 | 2 | Protek 24/7 Building & Maintenance | A student Support Hub - Rain dripping through small hole in the ceiling | Roofing | Metal Roofing | 425.5 | Pass | Fail | -1 | 4 | 746.5 | 2022-05-12 11:59 | 2022-05-17 17:00 | 2022-05-13 10:15 | 2022-05-17 17:00 | 2022-06-13 12:45 |  | WACCES | Repair leak in the ceiling - Student hubBRAF Declined
MSA-DCA | WA4992509 | 1 | Protek 24/7 Building & Maintenance | wooden bollard near chapel - pushed over, out of ground | Building | Doors | 919.75 | Pass | Fail | 0 | 4 | 745.75 | 2022-01-06 12:51 | 2022-01-07 17:00 | 2022-01-07 13:15 | 2022-01-07 17:00 | 2022-02-07 15:00 |  |  | Fabricate and fit 2 anchors for 2 existing bollards
MSA-DFES | WA5190866 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | The following lights are not working and need to be replaced - see notes below | Electrical | Lighting, Internal | 852.24 | Pass | Fail | 0 | 4 | 745.5 | 2022-02-24 16:07 | 2022-03-03 17:00 | 2022-03-01 08:30 | 2022-03-03 17:00 | 2022-04-01 10:00 |  | WACCES | Continued on site at 0830 to investigate faulty flag pole light. Discovered blown tube that needs replacing. Could not find available parts from surrounding wholesalers. Will need to return to site once correct light fitting has been ordered. Left to wholesaler at 0930 to grab more parts for job, arrived back on site at 1045. Replaced and reenergised lights in main dining and staff room. Left site at 1240.
MSA-DTAG | WA5399132 | 1 | Dormakaba Australia Pty Ltd | Staff Carpark - Garage # 2 roller door not working - see notes below | Building | Automatic Doors | 235 | Pass | Fail | 0 | 4 | 744.8 | 2022-05-09 15:35 | 2022-05-10 17:00 | 2022-05-10 13:51 | 2022-05-10 17:00 | 2022-06-10 14:39 |  |  | Refitted loose guide to magistrate no 2 roller door which was interfering with PE.***Please note - 4 x remotes for 4 x roller doors - Cost to supply new remotes are;$67.50 + gst each plus labour to program - if you wish to have these done, new work order will have to be issued***
MSA-DTWD | WA5383877 | 3 | AWB Co. | Exterior W108 - Remove damaged sheets from exterior foyer roof W108 | Building | General Building | 627.5 | Pass | Fail | 0 | 4 | 744.8 | 2022-04-28 07:59 | 2022-05-04 17:00 | 2022-05-03 08:12 | 2022-05-04 17:00 | 2022-06-03 09:00 |  |  | Attended site and investigated works Returned and removed sheets as per signature slip attached.
MSA-DTWD | WA5133064 | 3 | Daniel Chrisp Pty Ltd | Recycled Water resevoir appears to be empty and reed gardens not being reticulated | Plumbing & Drainage | Water | 1000 | Fail | Fail | 3 | 7 | 744.0667 | 2022-02-15 07:32 | 2022-02-21 17:00 | 2022-03-11 16:30 | 2022-02-21 17:00 | 2022-04-11 16:34 |  |  | Investigation faulty pumps Hypo & Contact Tanks Pump replaced
MSA-DTWD | WA5094731 | 2 | Precise Air Group | N Block -Ground - N35 - FCU 9 in staff room no power | Air Conditioning | Room Air Conditioners | 5479.65 | Fail | Fail | 31 | 36 | 744.0167 | 2022-01-31 13:20 | 2022-02-03 17:00 | 2022-09-09 15:29 | 2022-02-03 17:00 | 2022-10-10 15:30 |  | WACCES | subcontractor complete
MSA-DTWD | WA6008408 | 2 | Precise Air Group | AC not turning on | Air Conditioning | Room Air Conditioners | 1192.43 | Fail | Fail | 0 | 5 | 743.8333 | 2022-10-11 14:12 | 2022-10-14 17:00 | 2022-10-17 08:00 | 2022-10-14 17:00 | 2022-11-17 07:50 |  |  | arrived on site and signed in, we located unit and unit and in fault with error code u4 communication fault.located out door unit and found 2 crispy lizard on pcbs that have shorted both boards and will need replacing, contacted dakin spare parts for price and availability, source new parts, isolated and tagged out equipment and went a got parts, returned to site with new parts and disabled unit, removed old boards and replaced with new boards tested unit. Unit operating as it should
MSA-DTWD | WA6020712 | 1 | COMMERCIAL PLUMBING AND GAS | Café rear Carpark - Untraceable Gas Smell – Suspected leak from gas pit | Plumbing & Drainage | Gas | 1995.72 | Pass | Fail | 0 | 4 | 743 | 2022-10-13 16:57 | 2022-10-14 17:00 | 2022-10-13 17:30 | 2022-10-14 17:00 | 2022-11-13 16:30 |  |  | replaced valve and installed valve box in bitumen
MSA-DTWD | WA6361762 | 3 | AWB Co. | Various locations - T Block - faulty lighting - see notes below | Electrical | Lighting, Internal | 1109.94 | Pass | Fail | 0 | 4 | 743 | 2022-12-08 12:55 | 2022-12-15 17:00 | 2022-12-13 09:00 | 2022-12-15 17:00 | 2023-01-13 08:00 |  | WACCES | Attended site signed in jsa completed. Replaced remaining ballasts and tubes. Tested operational.Job complete
MSA-DCA | WA5548894 | 0 | Protek 24/7 Building & Maintenance | Outside North facing board walk - Fencing wires have been cut off - wooden fence | Building | Steel Fencing & Gates | 1142.7 | Fail | Fail | 0 | 4 | 742.5 | 2022-06-17 10:40 | 2022-06-17 12:40 | 2022-06-17 12:45 | 2022-06-17 14:40 | 2022-07-18 11:15 |  | WACCES | Supply and install new stainless steel fencing lines. Needs to be spec'd for proximity to sea wate
MSA-MRWA | WA6154648 | 2 | AWB Co. | Hall - Led strip lights not working - see notes below | Electrical | Lighting, Internal | 806.5625 | Pass | Fail | 0 | 4 | 742.25 | 2022-11-07 14:45 | 2022-11-10 17:00 | 2022-11-08 08:45 | 2022-11-10 17:00 | 2022-12-09 07:00 |  | WACCES & WCAPPR | Attended site and signed in. Completed JSA. Went to faulty lighting. Setup up signage. Installed new led lights. Tested to see if they were working. All working. Put power packs requested by Craig for lighting in level 9 storeroom , Packed up. Sign out. Completed paper work. ***Job Complete***
MSA-DTWD | WA5656531 | 2 | Techworks Plumbing | L1-A/T Block male and female toilet flushing knobs are broken | Plumbing & Drainage | Toilets/Cisterns | 1467.81 | Pass | Fail | 0 | 4 | 741.5 | 2022-07-18 14:35 | 2022-07-21 17:00 | 2022-07-19 12:00 | 2022-07-21 17:00 | 2022-08-19 09:30 |  | WACCES | Daniel Farrell (19/07/2022) - Work NoteAttended site for broken flush buttons, after observation it was apparent that wear and tear had caused the buttons to acquire friction and eventually become static, getting pushed through the face panel on last use.went to Reece get new buttons, however they only had one button and hose assembly so drove to port Kennedy. After arrival, it was revealed the new flush buttons were too wide for the panel holes. Ryan Wright (19/08/2022) - Work NoteAttended site & signed in at front reception.spoke with Rick the maintenance man who showed us where Dan had left off. We removed the cistern access covers and took them to galvins for the correct holesaw size. Ended up having to go bunnings for a 60mm holesaw & some cutting fluid. Once returned to site & re signed in we re assessed our SWMS to incorporate all relevant PPE. Cut the holes bigger to fit the new cistern buttons installed back on wall, tested & commissioned signed out at reception &
MSA-DTWD | WA6294203 | 2 | AWB Co. | B16 - Faulty industrial Exhaust Fan System causing toilets to smell | Electrical | Lighting, Internal | 964.56 | Pass | Fail | 0 | 4 | 740.25 | 2022-11-30 13:35 | 2022-12-05 17:00 | 2022-12-05 13:15 | 2022-12-05 17:00 | 2023-01-05 09:30 |  | WCAPPR | Attended site, signed in, completed jsa, picked up new fan belts, set up work area, located exhaust fan on roof, checked for isolation, removed cover, installed new belt, put cover back on, tested fan, fan working as intended, pack up site and cleaned up, completed paperwork, signed out. ***job complete***
MSA-DTWD | WA5781148 | 3 | Equans Mechanical Services Australia | G Block - 1st Floor - GF29 - Airconditioner not working - See n | Air Conditioning | Room Air Conditioners | 534.915 | Pass | Fail | -1 | 3 | 739.6667 | 2022-08-19 13:16 | 2022-08-26 17:00 | 2022-08-19 13:20 | 2022-08-26 17:00 | 2022-09-19 09:00 |  |  | Accessed the condenser unit for the unit in GF29, found it on R22 low on gas , and the out door pc board is Burnt out . Putting in das to replace .
MSA-DTAG | WA5961994 | 1 | Water2water Pty Ltd | Security Kitchen - Fault description Water urn (instant water) is leaking water internally | Plumbing & Drainage | Water | 2862.77 | Pass | Fail | 0 | 4 | 739.5833 | 2022-09-19 11:33 | 2022-09-20 17:00 | 2022-09-19 13:30 | 2022-09-20 17:00 | 2022-10-20 09:05 |  |  | New unit required. BRAF submitted 21.9.22 20/10/2022 installed new 15l rheem and calibration. All tested ok. Start 7 am to 9 am.
MSA-DTWD | WA5781152 | 3 | Equans Mechanical Services Australia | G Block - Ground Floor - GF7- Airconditioner not working - See n | Air Conditioning | Room Air Conditioners | 405.405 | Pass | Fail | -1 | 3 | 739.5 | 2022-08-19 13:22 | 2022-08-26 17:00 | 2022-08-19 15:00 | 2022-08-26 17:00 | 2022-09-19 10:30 |  |  | Found the Mitsubishi under ceiling slung unit not working properly , the left hand side of the evap has sagged down. It is connected to the building via brackets which due to the heritage listing cannot be touched , the compressor is down to earth and the system is on R22. Recommend that a high wall split be installed. DAS TO BE SUBMITTED
MSA-DCA | WA5195537 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Both chillers are not running - Batavia Gallery has high humidity | Air Conditioning | Room Air Conditioners | 1296.925 | Pass | Fail | 0 | 4 | 736.7333 | 2022-02-28 12:48 | 2022-03-01 17:00 | 2022-02-28 17:48 | 2022-03-01 17:00 | 2022-03-31 10:32 |  |  | BRAF Investigation into chiller faults completed by specialist chiller contractor AV. Following report detailing fault. Further Quote will be submitted for equipment repairs.
MSA-DTAG | WA5207348 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Mandurah Court Mens Public Toilet - Blood left over the mens toilet cubicle - see notes below | Cleaning | Cleaning | 300 | Fail | Fail | 1 | 5 | 733.1833 | 2022-03-08 12:29 | 2022-03-09 17:00 | 2022-03-14 13:13 | 2022-03-09 17:00 | 2022-04-14 02:24 |  |  | Works completed as per work order WA5207348
MSA-DTAG | WA5201075 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ladies Bathroom – 1987 Wing - Bathroom needs a biohazard clean - see notes below | Cleaning | Sanitary Services | 500 | Fail | Fail | 2 | 6 | 730.3167 | 2022-03-02 11:17 | 2022-03-02 13:17 | 2022-03-14 15:51 | 2022-03-02 15:17 | 2022-04-14 02:10 |  |  | Attended 22/02/22
MSA-DTWD | WA5887673 | 3 | Equans Mechanical Services Australia | Level 8 - Room C800 - AHU4 SA fan requires new Belts | Air Conditioning | Room Air Conditioners | 1805.155 | Pass | Fail | 0 | 4 | 724 | 2022-09-16 09:13 | 2022-09-23 17:00 | 2022-09-20 09:30 | 2022-09-23 17:00 | 2022-10-20 13:30 |  |  | BELTS FITTED
MSA-DTAG | WA5038539 | 3 | Midolo Building Services | Grounds - signage damaged - see notes below | Signage | General Signage | 1292.25 | Pass | Fail | -1 | 3 | 723.5 | 2022-01-17 14:14 | 2022-01-24 17:00 | 2022-01-18 09:00 | 2022-01-24 17:00 | 2022-02-17 12:30 |  | WACCES | Sign has been replaced
MSA-DTWD | WA6368675 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire pumps tanks - One of the two tanks are over flowing. | Fire Protection Services | Fire Protection - Monitor System | 1248.06 | Pass | Fail | 0 | 4 | 723.05 | 2022-12-14 07:53 | 2022-12-14 17:00 | 2022-12-14 08:39 | 2022-12-14 17:00 | 2023-01-13 11:42 |  | WACCES | CALL OUT-ATTENDED-8.30AM 14/12/22 BW-PWLABOUR 30 MIN-ONSITE 8.30AM TO 9.00AM BW-PWJR- NEW FLOAT VALVE NEEDS TO BE SOURCED19/12/2022 - New Float Valve installed. Further investigation for new diaphragm. Will be installed on WA6400130.
MSA-DFES | WA5511969 | 1 | WA BOILER SPARES & SERVICE | Applied Training Ground - There is a leaking valve on the Gantry | Plumbing & Drainage | Gas | 860 | Pass | Fail | 0 | 4 | 722 | 2022-06-13 11:41 | 2022-06-14 17:00 | 2022-06-14 07:30 | 2022-06-14 17:00 | 2022-07-14 09:30 |  |  | Tested gas valve to confirm leaking through. Removed gas valve to workshop for repairs. Returned to site, reinstalled gas valve and tested for correct operation
MSA-DCA | WA6153432 | 2 | Techworks Electrical | B1 Basement Level - Security Control - 5x Helvar lighting control faults - See notes below | Electrical | General Electrical | 1506.8 | Fail | Fail | 4 | 8 | 722 | 2022-11-07 10:19 | 2022-11-10 17:00 | 2022-12-06 06:00 | 2022-11-10 17:00 | 2023-01-05 08:00 |  | WACCES | Came and investigated faults with light applications, light fittings have failed, light apps have supplied the lights and they are all in warranty so they are following up with warranty about replacement fittings. Met with Koby from light applications, went through the faults in his list and inspected the necessary lights for issues. Light applications sourcing replacement fitting and transformer. Quote for rectification works to follow.
MSA-DTWD | WA5325957 | 2 | Protek 24/7 Building & Maintenance | K Block - Damaged Carpet | Flooring | Carpet | 176.875 | Pass | Fail | 0 | 4 | 721.75 | 2022-04-14 14:29 | 2022-04-21 17:00 | 2022-04-21 07:30 | 2022-04-21 17:00 | 2022-05-21 09:15 |  |  | Report/Record - BRAF Declined
MSA-DCA | WA5479923 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Ground Floor - Kimberley Room - Noise coming from ceiling | Air Conditioning | Room Air Conditioners | 240.7 | Pass | Fail | 0 | 4 | 720.4667 | 2022-05-27 13:00 | 2022-06-01 17:00 | 2022-05-30 12:37 | 2022-06-01 17:00 | 2022-06-29 13:05 |  |  | Attended site gained access and carried out inspection. Alexander room noise found to be caused by cable tie rubbing on duct work. Adjustment has been made. Air noise also found present from one of the diffusers. Balance point has been adjusted to prevent noise. Kimberley room noise found to be caused by clock on wall. The gears sound very similar to that of a VAV when it is driving. This has been reported to site FM Ben. No further action able to be taken on this job.
MSA-DTWD | WA5367365 | 0 | AWB Co. | BMI System - Faulty - not working | Electrical | General Electrical | 1076.52 | Pass | Fail | 0 | 4 | 719.9667 | 2022-04-19 07:16 | 2022-04-19 09:16 | 2022-04-19 07:17 | 2022-04-19 11:16 | 2022-05-19 07:15 |  | WACCES | Attended site signed in jsa completed. Spoke with pete on site and got access to board. Replaced meter with new and tested. All operational. *** job completed***
MSA-DCA | WA6379105 | 1 | Protek 24/7 Building & Maintenance | Wooden Steps to east of SLWA-Tactile plates are missing and loose-see notes | Building | Foundations | 374.38 | Pass | Fail | 0 | 4 | 718.75 | 2022-12-19 09:12 | 2022-12-20 17:00 | 2022-12-19 13:30 | 2022-12-20 17:00 | 2023-01-18 12:15 |  | WACCES | Installed tactile plates on flooring
MSA-DTWD | WA6008353 | 2 | Water2water Pty Ltd | Clarkson E-Cafe hot water urn not working | Plumbing & Drainage | Water | 2170.575 | Pass | Fail | 0 | 4 | 717.5 | 2022-10-11 13:29 | 2022-10-14 17:00 | 2022-10-12 13:00 | 2022-10-14 17:00 | 2022-11-11 10:30 |  |  | Year 2011 unit not worth repairing failed element (potentially more parts) Tank is corroded and full of scale (unable to access internally to clean) Unit to be replaced. Replaced unit with new 5L Zip ECONOBOIL and maxiflow scale filtration system. All ok.
MSA-DTWD | WA5680500 | 1 | AWB Co. | switch rod faulty - see notes | Electrical | General Electrical | 813.925 | Pass | Fail | 0 | 4 | 717 | 2022-07-27 12:44 | 2022-07-28 17:00 | 2022-07-28 13:00 | 2022-07-28 17:00 | 2022-08-27 10:00 |  |  | Work NoteAttended site signed in jsa completed, sharon showed which main switch was faulty. She had also mentioned the upgrades being done by EMCO building had been in the switch panel. Fault is they havent pushed back the metal rod that slides through in order for you to close the door. by not doing this they have bent the mechanism of the main switch for A block which feeds two switchboards. in order to further investigate safely i will need to switch power off to the main switch to safely investigate if it is repairable or if site will need a new Mainswitch which is 630A which nilsen have installed.spoke to sharon she would like a report done and sent to her about todays findings.job not completedWork NoteAttended site signed in jsa completed, sharon showed which main switch was faulty. She had also mentioned the upgrades being done by EMCO building had been in the switch panel. Fault is they havent pushed back the metal rod that slides through in order for you to close the door
MSA-DCA | WA5151672 | 2 | Protek 24/7 Building & Maintenance | Alexander Library Building - Level 3 - Executive suite, door to female bathroom | Building | General Building | 686.71 | Pass | Fail | 0 | 4 | 713.5 | 2022-02-17 15:47 | 2022-02-22 17:00 | 2022-02-22 15:00 | 2022-02-22 17:00 | 2022-03-24 08:30 |  | WACCES | Repair door to Bathroom
MSA-DCA | WA6363584 | 0 | EQUANS Mechanical Services (WA) Pty Limited | LChiller - fault light showing | Refrigeration | Chiller | 980.365 | Pass | Fail | 0 | 4 | 706 | 2022-12-12 05:02 | 2022-12-12 07:02 | 2022-12-12 06:00 | 2022-12-12 09:02 | 2023-01-10 16:00 |  | WACCES | Checked unit and found actuator to be seized and need replacing, have ordered. Returned to site with new actuator and installed. Tested on BMS that it opens closes and runs on automatic. Actuator runs all okay, cleaned sites and returned valve back to Auto on the BMS system.
MSA-DFES | WA5706996 | 3 | Australian HVAC Services Pty. Ltd. | Career - TV Room - Air cond in TV room – noisy then stopped working | Air Conditioning | Room Air Conditioners | 4155 | Pass | Fail | 0 | 4 | 703.5 | 2022-08-11 15:33 | 2022-08-18 17:00 | 2022-08-16 08:00 | 2022-08-18 17:00 | 2022-09-14 15:30 |  |  | Attended service call, checked ac in tv room & found outdoor fan & pc board failed. Unit is old & parts are no longer available. Sending info for braf/dad for unit replacement New AC installed as per BRAF.
MSA-DFES | WA5325993 | 3 | Protek 24/7 Building & Maintenance | Main Building - Roof - A large number of roof tiles are cracked and/or broken | Roofing | Tiled Roofing | 1662.5 | Pass | Fail | -1 | 3 | 703 | 2022-04-14 14:48 | 2022-04-26 17:00 | 2022-04-20 07:00 | 2022-04-26 17:00 | 2022-05-19 14:00 |  | WACCES | Repair damaged tiles to main roof
MSA-DTWD | WA5827230 | 1 | Precise Air Group | Roof - E-Block the e-vap on the roof is continuously dumping water again | Air Conditioning | Room Air Conditioners | 1258.81 | Pass | Fail | 0 | 4 | 700.9667 | 2022-09-01 08:59 | 2022-09-02 17:00 | 2022-09-01 11:02 | 2022-09-02 17:00 | 2022-09-30 16:00 |  |  | Attended site and carried out minor repairs on evap units
MSA-DTWD | WA6540218 | 1 | Equans Mechanical Services Australia | Condensation from the southerly A/C unit is not drained externally and leaks into the room | Air Conditioning | Ducted Split System | 527.37 | Fail | Fail | 1 | 5 | 700 | 2023-02-09 09:15 | 2023-02-10 17:00 | 2023-02-14 07:30 | 2023-02-10 17:00 | 2023-03-15 11:30 |  | WCAPPR
MSA-DTWD | WA5290933 | 3 | Daniel Chrisp Pty Ltd | D Block - Plant room -All instrumentation cannnot be viewed on BMS to Black Water Plant | Waste Management | Plant & Pumps | 6787.91 | Fail | Fail | 22 | 26 | 699.9833 | 2022-03-25 13:03 | 2022-04-01 17:00 | 2022-08-31 10:53 | 2022-04-01 17:00 | 2022-09-29 14:52 |  | WACCES & WCAPPR | The Tosibox has been installed on 31/08/2022 invoice submitted. A Control Power Supply & PLC Card are required attached is Q-11489 plus a DAS.
MSA-DTWD | WA5287436 | 2 | Protek 24/7 Building & Maintenance | Southern wall - Ground - Near room AT106 - Damaged panel of southern wall | Building | General Building | 928.22 | Pass | Fail | 0 | 4 | 699.75 | 2022-03-22 12:39 | 2022-03-25 17:00 | 2022-03-23 09:15 | 2022-03-25 17:00 | 2022-04-21 13:00 |  | WACCES | Repair damaged wall panel
MSA-DTWD | WA5688037 | 0 | Protek 24/7 Building & Maintenance | Roof leak near box gutter - currently onsite | Roofing | Metal Roofing | 9149.88 | Pass | Fail | 0 | 4 | 699.75 | 2022-08-02 09:21 | 2022-08-02 11:21 | 2022-08-02 10:30 | 2022-08-02 13:21 | 2022-08-31 14:15 |  | WACCES | Replace with new sheets, flashings & dektites
MSA-DTWD | WA5692189 | 2 | Protek 24/7 Building & Maintenance | 3D3 Auto Electrical work shop-Water leak down east wall | Building | External Walls | 831.67 | Fail | Fail | 0 | 4 | 699.25 | 2022-08-03 11:07 | 2022-08-08 17:00 | 2022-08-10 11:30 | 2022-08-08 17:00 | 2022-09-08 14:45 |  | WACCES | Installed new apron
MSA-DTAG | WA5880736 | 3 | Midolo Building Services | Level 1 - Kitchen for Links - Position a paper towel dispenser on the wall | Building | Internal Walls | 250.75 | Pass | Fail | 0 | 4 | 699 | 2022-09-15 16:37 | 2022-09-22 17:00 | 2022-09-20 10:15 | 2022-09-22 17:00 | 2022-10-19 13:15 |  | WACCES | new dispenser installed
MSA-DFES | WA5694818 | 2 | Securex Security Systems & Services | alarm system multiple locations low battery alarm-error as battery was replaced 2 weeks ago | Security | Security Management System | 2237.27 | Fail | Fail | 0 | 4 | 698.9167 | 2022-08-05 13:39 | 2022-08-10 17:00 | 2022-08-11 08:05 | 2022-08-10 17:00 | 2022-09-09 11:00 |  |  | 11/08/2022, 805-850Found charging voltage of main panel(DGP16) only 9.5vdc.Replacement required.09/09/2022, 730-1100Replaced panel and programmed as per settings of v8 panel, tested arming etc all ok Staff all left site before I finished so unable to get a docket signed
MSA-DTAG | WA5296589 | 3 | Australian HVAC Services Pty. Ltd. | Level 6 - BMS serving levels 3, 4, 5 & 6 is offline after the FIP was activated | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1248.86 | Pass | Fail | -1 | 3 | 698.5 | 2022-03-30 13:29 | 2022-04-06 17:00 | 2022-03-30 13:30 | 2022-04-06 17:00 | 2022-04-28 16:00 |  |  | Attend site with icon logic. Icon logic carried out full reset of floor controls and main plantroom controls. Program licensing has also now been updated.
MSA-DTWD | WA5534187 | 2 | Protek 24/7 Building & Maintenance | Corridor south - Roof adjacent to west facing wall - Mould indicates leak on roof - See notes | Roofing | Metal Roofing | 1910.09 | Fail | Fail | 0 | 5 | 698 | 2022-06-16 07:35 | 2022-06-20 17:00 | 2022-06-23 12:00 | 2022-06-20 17:00 | 2022-07-22 14:00 |  | WACCES | Supply & Install new apron flashing
MSA-DTWD | WA6292917 | 3 | AWB Co. | Block B & D - Security lights inoperative at night. | Electrical | Lighting, External | 1676.32 | Pass | Fail | 0 | 4 | 698 | 2022-11-29 14:22 | 2022-12-06 17:00 | 2022-12-06 13:00 | 2022-12-06 17:00 | 2023-01-04 15:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed.installed remaining lights in B block outside.tested operational.Job completed.
MSA-DTWD | WA5393827 | 3 | Australian HVAC Services Pty. Ltd. | Air handling unit - wiring issue | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2100.31 | Pass | Fail | -1 | 3 | 697.8833 | 2022-05-04 10:32 | 2022-05-11 17:00 | 2022-05-04 14:07 | 2022-05-11 17:00 | 2022-06-02 16:00 |  |  | Electrical wiring issue rectified with contractor as per BRAF
MSA-DTWD | WA5585217 | 3 | Falcetta Plumbing and Gas | Male toilet - Toilet bowl broken | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Fail | -1 | 4 | 697.75 | 2022-07-05 13:31 | 2022-07-12 17:00 | 2022-07-08 13:15 | 2022-07-12 17:00 | 2022-08-06 15:00 |  | WACCES | fabricate bracket, prep, replace
MSA-DTWD | WA5499922 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 1146.01 | Fail | Fail | 0 | 4 | 696.5 | 2022-06-10 15:45 | 2022-06-13 17:00 | 2022-06-14 10:30 | 2022-06-13 17:00 | 2022-07-13 11:00 |  |  | clean and seal leaking AC Unit
MSA-DFES | WA5366420 | 2 | ACTION GLASS & ALUMINIUM | Front windows - 1x smashed - 3x slight damaged | Glazing | Window Glass | 1248.25 | Pass | Fail | 0 | 4 | 696.25 | 2022-04-18 08:40 | 2022-04-21 17:00 | 2022-04-18 10:30 | 2022-04-21 17:00 | 2022-05-17 10:45 |  |  | ATTENDED SITE AFTER HOURSPATCHED TO SECURE BROKEN OVERSIZE WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-600 X 915PLUS SILICONE, 2 L/M OF DOUBLE SIDED TAPE AND 2 SQM OF SAFETY FILMRETURNED LATER DATE TO REGLAZE6.38 GREY LAMINATED SAFETY GLASS1-2614 X 836 ARRISED EDGES2 MEN REQUIRED
MSA-DFES | WA5677394 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Workshop Welding Bay - Roof Leak- See notes below | Roofing | Metal Roofing | 1000 | Pass | Fail | 0 | 4 | 696 | 2022-07-25 14:20 | 2022-07-26 17:00 | 2022-07-26 12:00 | 2022-07-26 17:00 | 2022-08-24 12:00 |  | WACCES | Sealed up lap
MSA-DTWD | WA6529042 | 3 | AWB Co. | External awning - 5 x external lights out | Electrical | Lighting, External | 3512.41 | Pass | Fail | 0 | 4 | 695.5 | 2023-02-02 13:52 | 2023-02-09 17:00 | 2023-02-09 10:30 | 2023-02-09 17:00 | 2023-03-10 10:00 |  | WCAPPR
MSA-DFES | WA5480036 | 3 | Protek 24/7 Building & Maintenance | Firefighter toilet door - has received moister damage, resulting in it swelling & scrubbing on floo | Building | General Building | 679.41 | Pass | Fail | -1 | 4 | 695.5 | 2022-05-27 14:43 | 2022-06-03 17:00 | 2022-05-30 13:00 | 2022-06-03 17:00 | 2022-06-28 12:30 |  | WACCES | Replace Toilet door
MSA-DTWD | WA6540879 | 2 | Equans Mechanical Services Australia | Level 2 - room 1-08 - VAV-LG-1-04 not working RM 26.2 degrees | Air Conditioning | Ducted Split System | 174.555 | Pass | Fail | 0 | 4 | 695.5 | 2023-02-09 15:38 | 2023-02-14 17:00 | 2023-02-13 13:00 | 2023-02-14 17:00 | 2023-03-14 12:30 |  | WCAPPR
MSA-DTWD | WA5127253 | 3 | ACTION GLASS & ALUMINIUM | Residence workshop facing Beaufort Street - Broken window | Glazing | Window Glass | 766.88 | Pass | Fail | -1 | 4 | 695.2 | 2022-02-14 12:04 | 2022-02-21 17:00 | 2022-02-17 10:15 | 2022-02-21 17:00 | 2022-03-18 09:27 |  |  | ATTENDED SITE PATCHED TO MAKE SAFE BROKEN HILITE WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-550 X 912 PLUS .5 SQM OF SAFETY FILMRETURNED LATER DATE WITH 2 MEN REGLAZED WINDOW5MM SPOTSWOOD TOUGHENED SAFETY GLASS1-563 X 1044PLUS SUPPLIED & FIT NEW 12x12 TIMBER BEAD 1-1035mmPLUS SILICONE AND 6 NAILS
MSA-DTWD | WA6191346 | 2 | COMMERCIAL PLUMBING AND GAS | Leaking toillet - Centre cubicle leaks at back of pan when flushed | Plumbing & Drainage | Toilets/Cisterns | 729.355 | Pass | Fail | -1 | 4 | 695 | 2022-11-16 15:37 | 2022-11-21 17:00 | 2022-11-17 17:00 | 2022-11-21 17:00 | 2022-12-16 16:00 |  |  | replaced cistern and repaired pan
MSA-DTWD | WA5472973 | 3 | AWB Co. | Water leak - SE corner of room | Roofing | Metal Roofing | 1358.13 | Pass | Fail | 0 | 4 | 694.7667 | 2022-05-24 12:03 | 2022-05-31 17:00 | 2022-05-30 13:00 | 2022-05-31 17:00 | 2022-06-28 11:46 |  |  | Attended and found sump pop split allowing water ingress. Wall cladding also split. Re-sealed. Ceiling damaged,carpenter to attend once leak confirm resolved next rain.Attended site and completed roof repairs
MSA-DTWD | WA6522944 | 2 | Australian Airconditioning Services Pty Ltd | D19 - Bakery Lab - Air handling unit blowing hot air | Air Conditioning | Evaporative Coolers | 456.83 | Pass | Fail | 0 | 4 | 694.5 | 2023-01-31 11:08 | 2023-02-03 17:00 | 2023-01-31 12:00 | 2023-02-03 17:00 | 2023-03-01 10:30 |  | WACCES
MSA-DTAG | WA5308492 | 1 | Australian HVAC Services Pty. Ltd. | Roof - AC - Library FCU 9 s/Air temp 14C. HW valve 100% open | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1024.87 | Pass | Fail | 0 | 4 | 694.3333 | 2022-04-08 12:40 | 2022-04-11 17:00 | 2022-04-08 12:40 | 2022-04-11 17:00 | 2022-05-07 11:00 |  |  | Attend site. Access detention stairwell and set extension ladder. Fill in jas for safe access working off extension ladder. Access unit and check controls. Found chilled water modulating valve stuck in the open position. Remove actuator from valve an test operation, found actuator to work as normal. Check valve operation with shifter and found to be stiff. Move valve in 360 motion and found to free up. Install actuator on valve and found to start driving. Valve now working ok.
MSA-DFES | WA5495819 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Level - Engine Room - Green flashing warning lights not working - See notes | Electrical | Emergency & Exit Lighting | 348.645 | Pass | Fail | 0 | 4 | 691.5 | 2022-06-08 16:25 | 2022-06-15 17:00 | 2022-06-15 13:30 | 2022-06-15 17:00 | 2022-07-14 09:00 |  | WACCES | Arrived on site at 0700 to replace blown globes in station status lighting. Discovered all status lights with no voltage and began investigating all relative ELV terminal boxes. Staff had informed that lights have had ongoing problems long term and will be placing a new request to replace all status lighting along with led replacements for all light fittings in engine bay. Reinstated all status lights and left site at 0900.
MSA-DCA | WA5691582 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Temperature alarm - Chilled water plant chiller | Building | Materials | 202.705 | Pass | Fail | 0 | 4 | 682.5 | 2022-08-03 04:28 | 2022-08-03 06:28 | 2022-08-03 05:30 | 2022-08-03 08:28 | 2022-08-31 16:00 |  |  | Attended site. Checked over bms and checked alarms. Found chiller 1 in alarm, cooling towers were in alarm but had been cleared. Dialled into ets bms and switched AGWA to local. Cleared flow fault on chiller 1. Tested operation of chiller 1 and chiller 2. Both chillers operating as required. Checked alarm history on chillers and cooling tower vsds. Checked over pumps and cooling towers, all ok. Alarms on bms had cleared. Plant running in local. Completed paperwork.
MSA-DTWD | WA5761755 | 2 | Protek 24/7 Building & Maintenance | 6E41 store / office-Water leaking through ceiling | Building | Ceiling | 1000 | Pass | Fail | 0 | 4 | 678 | 2022-08-18 11:36 | 2022-08-23 17:00 | 2022-08-23 09:45 | 2022-08-23 17:00 | 2022-09-20 15:45 |  | WACCES | Removed flashings from roof , inspect ceiling cavity, to find point of entry of roof leak , after further investigation, box gutter had various holes in it and was leaking into the roof cavity , then tracking down the roof sheet insulation, and dropping onto the storeroom ceiling below .BRAF submitted and declined
MSA-DTWD | WA5978276 | 3 | Critical Fire Protection & Training | Room C800 - Jacking Pump will not maintain pressure - See notes below | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 899.03 | Fail | Fail | 0 | 4 | 676 | 2022-09-28 09:51 | 2022-10-05 17:00 | 2022-10-06 08:00 | 2022-10-05 17:00 | 2022-11-03 12:00 |  | WACCES | I have investigated the pumps at Perth campus, and found:The pressure switches work but the jacking pump is not switching off automatically.I believe the gauge on the system is faulty and the switches have not been adjustedcorrectly.Recommend to replace the gauge on the pressure switch manifold, and also install apressure gauge on the pump discharge. Adjust the pressure switches.If this fails to achieve the pressure requirements, a pump change over may be required,as the main hydrant pump is over 30 years old. -Attend site during normal working hours-Replace gauge on the pressure switch manifold-Install pressure gauge on the pump discharge-Adjust existing pressure switches
MSA-DTWD | WA5706096 | 2 | AWB Co. | LED light above welding bays has stopped functioning - See notes below | Electrical | Lighting, Internal | 999.81 | Pass | Fail | -1 | 3 | 675.5 | 2022-08-11 08:41 | 2022-08-16 17:00 | 2022-08-12 07:00 | 2022-08-16 17:00 | 2022-09-09 10:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Met with ewp guy and collected ewp. Moved tables around so we could access faulty hi bay. Replaced faulty hi bay with new led hi bay, took pictures and packed up. Moved everything back to original position. Completed paperwork. Signed out, Job complete
MSA-DTAG | WA4993493 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Registry - Aircon in registry not working | Air Conditioning | Room Air Conditioners | 2186.35 | Pass | Fail | 0 | 4 | 675.25 | 2022-01-07 15:31 | 2022-01-10 17:00 | 2022-01-10 08:45 | 2022-01-10 17:00 | 2022-02-07 12:00 |  | WACCES | Awaiting braf approval to order parts then 10+ days wait times due to covid transport issues.Picked up parts from office & attended site, isolated pac 1& 2 replaced fan boards as per quote, tested operation ok
MSA-DTWD | WA6516826 | 2 | Australian Airconditioning Services Pty Ltd | Skope under bench fridge running warm | Refrigeration | Refrigerators | 1276.36 | Pass | Fail | 0 | 4 | 674.75 | 2023-01-23 15:44 | 2023-01-27 17:00 | 2023-01-25 12:30 | 2023-01-27 17:00 | 2023-02-22 15:15
MSA-DTWD | WA6407574 | 3 | Protek 24/7 Building & Maintenance | Repair, patch and paint water damaged wall. - see notes below | Building | Internal Walls | 1636.555 | Pass | Fail | -1 | 3 | 674.75 | 2023-01-10 09:57 | 2023-01-17 17:00 | 2023-01-10 12:00 | 2023-01-17 17:00 | 2023-02-07 14:45 |  | WACCES
MSA-DTWD | WA6148016 | 3 | AWB Co. | Room J100 - GPOs x 2 J 100 - see notes below | Electrical | General Electrical | 1445.8 | Pass | Fail | 0 | 4 | 673.75 | 2022-11-03 11:31 | 2022-11-10 17:00 | 2022-11-09 07:45 | 2022-11-10 17:00 | 2022-12-07 09:30 |  | WACCES | Attended site and signed in. Completed JSA. Located 3 phase GPOs. Isolated circuits. Tested that circuit was isolated. Removed old GPOs. Mounted new GPOs to walls and installed. Reenergised circuit. Tested GPOs. All working as intended. Packed up cleaned up. Completed paperwork. Signed out. ***Job complete***
MSA-DFES | WA6184716 | 3 | Protek 24/7 Building & Maintenance | Fleet Stores, Peel Road entrance - Fire exit door, next to roller door -damaged door-see notes | Building | Doors | 1293.93 | Pass | Fail | -1 | 3 | 672.75 | 2022-11-15 14:44 | 2022-11-22 17:00 | 2022-11-17 11:00 | 2022-11-22 17:00 | 2022-12-15 11:45 |  | WACCES | ? Remove and dispose of damaged fire door and fixings? Supply and install new solid core fire door and fix to frame? Apply undercoat and paint to door to match existing? Install original door hardware onto door and function test
MSA-DTAG | WA5383129 | 1 | Sapio Pty Ltd | Level 5 - C508-5.01 Hearing room - PTZ is offline and not working | Security | CCTV Surveillance | 5616.93 | Pass | Fail | 0 | 4 | 672.5 | 2022-04-27 12:35 | 2022-04-28 17:00 | 2022-04-27 15:30 | 2022-04-28 17:00 | 2022-05-25 16:00 |  |  | Removed faulty camera and installed new Axis P5655 PTZ camera. Tested for correct operation.
MSA-DTWD | WA5479755 | 3 | AWB Co. | 11 x high awning lights out over roller doors South wall | Electrical | Lighting, Internal | 2788.215 | Pass | Fail | -1 | 3 | 672.5 | 2022-05-27 11:28 | 2022-06-03 17:00 | 2022-05-30 09:45 | 2022-06-03 17:00 | 2022-06-27 10:15 |  | WCAPPR | Attended site and signed in, reviewed JSA, spoke with fm about job,removed remaining lights and replaced with new, changed tubes in lights , completed paperwork signed out*job completed*
MSA-DTWD | WA6376032 | 3 | AWB Co. | Broken light fitting | Electrical | Lighting, Internal | 678.515 | Pass | Fail | -1 | 3 | 672 | 2022-12-15 12:37 | 2022-12-22 17:00 | 2022-12-15 13:30 | 2022-12-22 17:00 | 2023-01-12 13:30 |  | WACCES | Attended site signed in jsa completed, removed x2 old lights and installed new panel kits and new led panels. Tested operational.Job completed
MSA-DTAG | WA5188724 | 3 | Midolo Building Services | External - Handrail in front of flagpole is loose | Building | Steel Work | 1327.16 | Pass | Fail | -1 | 3 | 671.5 | 2022-02-23 11:05 | 2022-03-02 17:00 | 2022-02-24 14:00 | 2022-03-02 17:00 | 2022-03-24 13:30 |  | WACCES | handrails repaired and re secured in place
MSA-DFES | WA5384469 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Building - Ground - Electrical circuit B-15 Tripping to drying cabinet and Exhaust fan in tunic room | Electrical | General Electrical | 958.48 | Pass | Fail | 0 | 4 | 671.25 | 2022-04-28 13:08 | 2022-05-05 17:00 | 2022-05-05 15:15 | 2022-05-05 17:00 | 2022-06-02 14:30 |  | WACCES | Arrived onsite at 1318. Found faulty fan location in tunic room. Installed new fan with junction box and new fixings and tested. Notified staff and signed out at 1420
MSA-DFES | WA5563074 | 3 | AWB Co. | Dormitory bathrooms -dorm 3 bathroom- soap holder cracked | Building | General Building | 578.95 | Pass | Fail | -1 | 3 | 670 | 2022-06-20 11:42 | 2022-06-27 17:00 | 2022-06-23 13:00 | 2022-06-27 17:00 | 2022-07-21 11:00 |  |  | Craig Adams (23/06/2022) - Work NoteAttended site, measured tiles and soap holder, drove to Bunnings to pick up materials and soap holder to match existing.Craig Adams (24/06/2022) - Work NoteDrove to Bayswater Bunnings pick up 200mm tile soap holder checked online before attending was saying low in stock 1 left was broken,Rang around drove to Malaga only store in the area had them in stockCraig Adams (21/07/2022) - Work NoteAttended site, filled out JSA, removed damaged tile soap holder and replaced with new.
MSA-DFES | WA5677353 | 1 | Protek 24/7 Building & Maintenance | Spray Painters Bay-Roof Leaking from the roof Above the spray painters prep bay | Roofing | Metal Roofing | 517.78 | Pass | Fail | 0 | 4 | 667.75 | 2022-07-25 14:09 | 2022-07-26 17:00 | 2022-07-26 13:30 | 2022-07-26 17:00 | 2022-08-23 09:15 |  |  | Located and sealed Leaking points
MSA-DTWD | WA6113670 | 3 | Precise Air Group | Supply temporary Cold Display fridge cafe N106 | Refrigeration | Refrigerators | 2046 | Pass | Fail | -1 | 3 | 667.0833 | 2022-10-24 13:52 | 2022-10-31 17:00 | 2022-10-25 12:15 | 2022-10-31 17:00 | 2022-11-22 07:20 |  | WACCES | delivered Fridges to site, had firdges on hire. picked up fridges
MSA-DTAG | WA5398342 | 1 | Sapio Pty Ltd | Main office - camera fault - see notes below | Security | CCTV Surveillance | 4294.02 | Pass | Fail | 0 | 4 | 667 | 2022-05-09 09:38 | 2022-05-10 17:00 | 2022-05-09 14:30 | 2022-05-10 17:00 | 2022-06-06 09:30 |  |  | Installed new IP Camera and replaced coax cable with Cat6
MSA-DTWD | WA5109754 | 3 | AWB Co. | J107,J127 - 2 of the Red J block identifier signs have fallen off the building entrances & missing | Building | Internal Walls | 837 | Pass | Fail | 0 | 4 | 666.9833 | 2022-02-09 12:19 | 2022-02-16 17:00 | 2022-02-15 18:42 | 2022-02-16 17:00 | 2022-03-15 13:41 |  |  | replacement of signs as per request
MSA-DTAG | WA5226515 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Mazza Chambers & surrounding areas - covid clean | Cleaning | Cleaning | 500 | Fail | Fail | 0 | 4 | 661.9333 | 2022-03-14 09:42 | 2022-03-14 11:42 | 2022-03-17 12:22 | 2022-03-14 13:42 | 2022-04-14 02:18 |  |  | As per work order
MSA-DTWD | WA5494147 | 3 | AWB Co. | F7 - Electrical storage hot water unit leaking | Electrical | General Electrical | 2072.59 | Pass | Fail | -1 | 3 | 654 | 2022-06-07 12:54 | 2022-06-14 17:00 | 2022-06-08 07:00 | 2022-06-14 17:00 | 2022-07-05 13:00 |  |  | attended site signed in jsa completed. removed old isolator and installed new 20a single phase isolator switch. Tested operational to complete hws install. ** job completed **
MSA-DTWD | WA5379708 | 3 | Equans Mechanical Services Australia | Air conditioner in Horticulture staff office is not working - see notes below | Air Conditioning | Room Air Conditioners | 1564.77 | Pass | Fail | -1 | 3 | 653.75 | 2022-04-21 13:35 | 2022-04-29 17:00 | 2022-04-22 08:00 | 2022-04-29 17:00 | 2022-05-19 13:45 |  |  | Gathered tools and equipment, removed old a/C and replaced with new. Tested operatallok cleaned up work area. Completed paperwork and signed out. Disposed of old unit.
MSA-DTWD | WA5381759 | 1 | BAKE-QUIP PTY LTD | Kendrew- E-Block- Restaurant Kitchen, Combi steamer oven broken power point switch | Equipment | Catering Equipment | 830.9 | Fail | Fail | 0 | 4 | 653.5 | 2022-04-26 11:24 | 2022-04-27 17:00 | 2022-04-28 08:30 | 2022-04-27 17:00 | 2022-05-25 14:00 |  |  | Refer to service report
MSA-DTWD | WA5377802 | 3 | Protek 24/7 Building & Maintenance | Personnel door us weather damaged | Building | Doors | 1141.75 | Pass | Fail | -1 | 3 | 652.75 | 2022-04-20 09:09 | 2022-04-28 17:00 | 2022-04-20 10:00 | 2022-04-28 17:00 | 2022-05-17 14:45 |  | WACCES | Replace Damaged door
MSA-DCA | WA5391003 | 1 | Techworks Electrical | GF Kitchen Main - Power supply to Dishwasher is tripping | Electrical | General Electrical | 1373.83 | Pass | Fail | 0 | 4 | 652.5 | 2022-05-02 15:52 | 2022-05-03 17:00 | 2022-05-03 07:30 | 2022-05-03 17:00 | 2022-05-30 12:00 |  | WACCES | Dishwasher was tripping breaker, began fault finding machine, investigated and found 1 of the elements to be causing the fault. Disconnected this element until we can replace the element.No material used Replaced element
MSA-DTWD | WA5270499 | 0 | ACTION GLASS & ALUMINIUM | E80 - smashed external window - (For risk cover) | Building | General Building | 1177 | Pass | Fail | 0 | 4 | 652 | 2022-03-18 08:20 | 2022-03-18 10:20 | 2022-03-18 10:00 | 2022-03-18 12:20 | 2022-04-14 14:00 |  |  | ATTENDED SITEPATCHED WINDOW TO MAKE SAFE6.38 CLEAR LAMINATED SAFETY GLASS1-400 X 700PLUS SILICONE, 2 L/M OF DOUBLE SIDED TAPE AND 1 SQM OF SAFETY FILMRETURNED LATER DATE TO REGLAZE6.38 GREY LAMINATED SAFETY GLASS1-1066 X 2318PLUS SILICONE2 MEN REQUIRED
MSA-DTWD | WA5831972 | 2 | AWB Co. | A Block - Level 1 - Back flow valve cupboard-The outer skin has come off the door - See notes below | Building | Doors | 1670.92 | Pass | Fail | 0 | 4 | 652 | 2022-09-05 09:56 | 2022-09-08 17:00 | 2022-09-07 07:00 | 2022-09-08 17:00 | 2022-10-04 11:00 |  |  | Works completed
MSA-DTWD | WA5697898 | 2 | M Construction (WA) | A231 and A234 - windows are failing to shut | Building | Windows | 887.42 | Pass | Fail | 0 | 4 | 651.5 | 2022-08-09 12:37 | 2022-08-12 17:00 | 2022-08-12 07:00 | 2022-08-12 17:00 | 2022-09-08 10:30 |  |  | Attended site and inspected window which was failing to shut, will engage with subcontractor to complete these works. Returned to site with subcontractor and windows have been completed and are now operational.
MSA-DTWD | WA6509382 | 2 | Techworks Electrical | Canteen kitchen - Auto electric Nitro liquid dispenser and on low voltage | Electrical | General Electrical | 1990.925 | Pass | Fail | 0 | 4 | 651 | 2023-01-20 10:13 | 2023-01-25 17:00 | 2023-01-24 09:00 | 2023-01-25 17:00 | 2023-02-20 12:00
MSA-DCA | WA5380504 | 3 | Precise Air Group | Ground - Wardle Room -Under Bench Fridge not getting down to temperature (stuck at 12deg) | Refrigeration | Refrigerators | 3676.67 | Pass | Fail | -1 | 3 | 650.3333 | 2022-04-22 13:04 | 2022-05-02 17:00 | 2022-04-27 08:00 | 2022-05-02 17:00 | 2022-05-24 10:20 |  |  | Attended site and gained access to the fridge not working properly. Tested and took readings and found it was showing signs system was running short on refrigerant. Picked up parts from supplier and returned to site to check for a leak. Reclaimed system and found half the charge left, pressurised and started checking for leaks. After checking found a leak in the next fridge over that is connected on the same refrigeration circuit. Leak is present in the evaporator and will need to be replaced. Quote to follow
MSA-DTAG | WA5566572 | 2 | AWB Co. | Ground - Public male toilet - Hand-dryer is broken | Electrical | General Electrical | 1038.21 | Pass | Fail | 0 | 4 | 650.25 | 2022-06-23 09:43 | 2022-06-28 17:00 | 2022-06-28 07:00 | 2022-06-28 17:00 | 2022-07-25 09:15 |  |  | Attended site and signed in. Completed JSA. Located faulty hand dryer. Replaced with new one. Took picture, working as intended, completed paperwork. Signed out.Job complete
MSA-DFES | WA5689776 | 2 | AWB Co. | Front Window at Reception Area-Water Leak – please Inspect and replace front window seals | Building | Windows | 1682.69 | Pass | Fail | 0 | 4 | 649.75 | 2022-08-02 13:31 | 2022-08-05 17:00 | 2022-08-03 08:45 | 2022-08-05 17:00 | 2022-08-30 10:30 |  | WACCES | works completed as per sign slips
MSA-MRWA | WA6381792 | 1 | AWB Co. | Blinking light | Electrical | Lighting, Internal | 570.12 | Pass | Fail | 0 | 4 | 649.75 | 2022-12-19 14:43 | 2022-12-20 17:00 | 2022-12-20 06:00 | 2022-12-20 17:00 | 2023-01-16 07:45 |  | WACCES | Attended site, signed in, completed jsa, located faulty light, set up work area, replaced old ballast with new ballast and installed new tubes (provided by site), tested to see if everything was working, all working, pack up cleaned up, completed paperwork, signed out, ***Job Complete***
MSA-DCA | WA5494028 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 2 - Main Auditorium Bio Box - Bio Box has a fault - See notes below | Electrical | General Electrical | 308.37 | Pass | Fail | 0 | 4 | 648.8333 | 2022-06-07 12:10 | 2022-06-10 17:00 | 2022-06-09 14:55 | 2022-06-10 17:00 | 2022-07-06 15:45 |  | WACCES | Arrived onsite at 14:30 to install 1 x LED batten to bio box. Installed and tested light and notified staff of works completed. Left site at 15:45
MSA-DCA | WA5879787 | 2 | Techworks Plumbing | Level 2 - Female cubicle 3 - toilet seat has come off | Plumbing & Drainage | Toilets/Cisterns | 716.47 | Pass | Fail | -1 | 3 | 648 | 2022-09-15 09:08 | 2022-09-20 17:00 | 2022-09-15 15:00 | 2022-09-20 17:00 | 2022-10-12 15:00 |  | WACCES | New toilet seat required 15/09/2022
MSA-DTAG | WA6021438 | 1 | Bullant Security Pty Ltd | L1-Judicial Corridor – Door to stairs near Murphy JA chambers-handle on door broken - see notes | Security | Locksmith | 634.09 | Pass | Fail | 0 | 4 | 648 | 2022-10-14 07:57 | 2022-10-14 17:00 | 2022-10-14 10:40 | 2022-10-14 17:00 | 2022-11-10 10:40 |  | WACCES | Attended site and viewed door, 530 DX was on door and latch jammed in strike. Applied pressure and was able to open. Handle to be replaced as this is a fire exit and requires a lever.Returned to site and replaced existing code lock with one that was compliant. Code set as per existing.
MSA-DTWD | WA6191403 | 1 | Precise Air Group | Pavilion Restaurant drinks cool room hot | Refrigeration | Coolroom | 1826.62 | Pass | Fail | 0 | 4 | 647.9 | 2022-11-16 16:30 | 2022-11-17 17:00 | 2022-11-17 15:06 | 2022-11-17 17:00 | 2022-12-14 15:00 |  |  | Attended site and signed in. Gained access to pavilion cool room, found no cooling present and room was at 17°C. Accessed condensing unit and found system short cycling on HP. Tested unit and found that the HP fan cycle switch is faulty and requires replacing. This will require removing the refrigerant from the cool room, swapping the pressure switch, evacuating and testing the system. Have safely bypassed the switch to have the cool room running in the meantime. Quote to follow for repairs . 14/12/22 picked up new HP pressure control switch for condenser fan ,Reclaimed refrigerant out of system and replace with new switch, pressure tested system then vacuumed it out ,added new R404a refrigerant 4.0kg and tested unit all operational again .Needed apprentice for day to help load up gear onto roof and be spotter .job completed
MSA-DTWD | WA6521948 | 1 | Precise Air Group | Cool room - The temperature is too high and climbing steadily throughout the day. currently 14 deg | Refrigeration | Coolroom | 2053.47 | Pass | Fail | 0 | 4 | 647.6 | 2023-01-30 14:50 | 2023-01-31 17:00 | 2023-01-31 15:09 | 2023-01-31 17:00 | 2023-02-27 14:45
MSA-DFES | WA5207278 | 1 | Go Doors | Main Security Gate - Staff Car park entrance - see notes beloww | Building | Automatic Doors | 953.8 | Fail | Fail | 1 | 5 | 647 | 2022-03-08 12:00 | 2022-03-09 17:00 | 2022-03-15 12:15 | 2022-03-09 17:00 | 2022-04-11 11:15 |  | WACCES | Completed works. Please see attachments.
MSA-DFES | WA5696241 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Bay - Lights not working - See notes below | Electrical | Lighting, Internal | 576.645 | Pass | Fail | 0 | 4 | 646.8333 | 2022-08-08 10:26 | 2022-08-11 17:00 | 2022-08-10 12:00 | 2022-08-11 17:00 | 2022-09-06 10:50 |  |  | Located faulty light. There was no power to the light. Found a switch and I have power at the light. The light is controlled from a switch and sensor the sensor and light will need replacement. The sensor is 4.2 meters high I did not have to correct ladder to do the job day. Will need to return to complete.Arrived 0830Signed in and collected keysAccess to correct yard and building.Remove and replace sensor, light and light cable as it’s non-compliant. Test and take photos no asbestos register availableSign out at 1050
MSA-DTAG | WA5998309 | 3 | Bullant Security Pty Ltd | Ground - Registry - Lock barrel to fit existing master key - See notes | Security | Locksmith | 472.09 | Pass | Fail | 0 | 3 | 646.5 | 2022-10-07 13:59 | 2022-10-14 17:00 | 2022-10-11 10:30 | 2022-10-14 17:00 | 2022-11-07 09:00 |  |  | Attend site, view 2 x lock cylinders that need to be changed to suit existing master key, will return with replacement cylinders. Date on site: 11/10/2022 Time on site: 10:30 - 11:00 Attend site, supply and install 2 x 570 oval cylinders keyed to site restricted system and supply 2 x keys.Date on site: 07/11/2022Time on site: 08:30 - 09:00
MSA-DTWD | WA5588148 | 3 | Australian Airconditioning Services Pty Ltd | Leaking sight glass | Air Conditioning | Room Air Conditioners | 3113.13 | Pass | Fail | -1 | 3 | 644.5 | 2022-07-07 13:30 | 2022-07-14 17:00 | 2022-07-07 14:00 | 2022-07-14 17:00 | 2022-08-03 10:30 |  |  | Sight glass replaced. All leaks repaired. Unit operational
MSA-DTWD | WA5706126 | 3 | Protek 24/7 Building & Maintenance | Water leak in line with North -South gables at both ends | Roofing | Metal Roofing | 1235.14 | Pass | Fail | 0 | 4 | 644.5 | 2022-08-11 08:56 | 2022-08-18 17:00 | 2022-08-16 14:00 | 2022-08-18 17:00 | 2022-09-12 10:30 |  |  | Supply and install new gutter pop
MSA-DTWD | WA5379440 | 2 | AWB Co. | North Block - Passage - Replace lights not working in corridor - N Block Ground Entry from carpark | Electrical | Lighting, External | 701.195 | Pass | Fail | 0 | 4 | 631 | 2022-04-21 11:14 | 2022-04-27 17:00 | 2022-04-27 07:00 | 2022-04-27 17:00 | 2022-05-23 14:00 |  | WACCES | Attended site signed in jsa completed. Removed lights and replaced drivers for two led lights. Now operational and working.*** job completed ****
MSA-DTWD | WA6538963 | 2 | ACTION GLASS & ALUMINIUM | Balcony - Glass panel (1 off) removed previously, requires replacement | Glazing | Glass wall | 1422.05 | Pass | Fail | -1 | 3 | 628 | 2023-02-08 09:30 | 2023-02-13 17:00 | 2023-02-09 09:30 | 2023-02-13 17:00 | 2023-03-07 13:30
MSA-DTWD | WA6191366 | 2 | SCAVENGER SUPPLIES PTY LTD | D207 External - PA speaker not working during announcements | Fire Protection Services | Fire Protection - Monitor System | 1012.33 | Pass | Fail | 0 | 3 | 627.5 | 2022-11-16 15:51 | 2022-11-21 17:00 | 2022-11-18 11:00 | 2022-11-21 17:00 | 2022-12-14 14:30 |  | WCAPPR | P2 CALL AOUT- ATTENDED 18-11-2022-NO SS AUTHORISEDNORMAL LABOUR-18-11-2022-DPH/PW 1.5HOURS X2 TECHSC-7906-SCHEDULED WORK FOR 12/12/2022Completed 14/12/2022
MSA-DTWD | WA6000735 | 3 | AWB Co. | Glazing workshop-Two steel posts that need repair as rusty | Building | Steel Work | 5558.475 | Pass | Fail | -1 | 3 | 627.4167 | 2022-10-10 10:11 | 2022-10-17 17:00 | 2022-10-13 07:00 | 2022-10-17 17:00 | 2022-11-08 10:25 |  |  | works completedBRAF approval attached
MSA-DTWD | WA5836919 | 2 | AWB Co. | 6E Cabinet Making - faulty 20amp GPO | Electrical | General Electrical | 2587.25 | Pass | Fail | -1 | 3 | 626.25 | 2022-09-07 16:28 | 2022-09-12 17:00 | 2022-09-08 13:45 | 2022-09-12 17:00 | 2022-10-04 16:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed all pre starts completed. Ran new circuit from board in classroom to location of machine. Terminated into box and board. all tested and recorded results. Ewp off hiredJob completed
MSA-DCA | WA6414977 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Level 3 - ICT Server Room - AC’s 2 and 5 displaying error messages | Air Conditioning | Building HVAC Maintenance (Major Plant) | 685.82 | Pass | Fail | 0 | 4 | 626 | 2023-01-11 11:28 | 2023-01-18 17:00 | 2023-01-18 07:00 | 2023-01-18 17:00 | 2023-02-13 09:00
MSA-DCA | WA5477522 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Main Stairs - 4 of the track lights are not functioning | Electrical | General Electrical | 894.1215 | Pass | Fail | 0 | 4 | 625.5 | 2022-05-25 14:20 | 2022-05-26 17:00 | 2022-05-26 08:00 | 2022-05-26 17:00 | 2022-06-21 09:30 |  | WCAPPR | Continued on site at 09:15. To investigate track lighting on level 1, job for same lights has already been attended under work order AMS1072727 WA5477522. No action needed continued on site at 09:30
MSA-DTWD | WA5216675 | 2 | Techworks Electrical | Kendrew- A-Block room A105 lights not working | Electrical | General Electrical | 2202.21 | Pass | Fail | 0 | 4 | 625 | 2022-03-11 11:57 | 2022-03-16 17:00 | 2022-03-16 12:00 | 2022-03-16 17:00 | 2022-04-11 13:00 |  | WACCES | Replaced faulty fluro light panels with new led panels
MSA-DTWD | WA5105552 | 3 | AWB Co. | E400 Damaged 15 amp Outlet for asset 104015 | Electrical | General Electrical | 1336.26 | Pass | Fail | 0 | 4 | 624.5 | 2022-02-04 11:59 | 2022-02-11 17:00 | 2022-02-11 14:30 | 2022-02-11 17:00 | 2022-03-09 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Drove around to E Block and parked van up. Set up work area and brought all gear inside. Figured out what else we needed and went to wholesaler. Returned to site and brought all parts in. Fit off mounting block where it was needing to go. Pushed couplings, corrie and conduit onto cable where required and ran back to board. Saddled all conduit onto wall. De energised switchboard and took necessary covers off. Brought cable down cable tray and into switchboard. Fit off RCD and labelled Neutral bar number on chassis cover.Labelled circuit on legend .Did continuity and I.R Test on circuit, Put all covers back on board. Put fire seal across top of switchboard as there was a big gap at entry. Re energised switchboard. Tested rcd push button function. Injection tested rcd from gpo , All tested passed . recorded down all results. Put new 15A plug top on machine that is going to be plugged into new 15A GPO. test and tagged lead
MSA-DFES | WA5390823 | 2 | Protek 24/7 Building & Maintenance | Single level - please see details below | Building | Steel Fencing & Gates | 1193.95 | Fail | Fail | 0 | 4 | 624 | 2022-05-02 15:04 | 2022-05-05 17:00 | 2022-05-06 11:30 | 2022-05-05 17:00 | 2022-06-01 11:30 |  | WACCES | Replace Cyclone Mesh fence
MSA-DCA | WA6529070 | 0 | Techworks Electrical | Dimmer room - Circit braker not working | Electrical | General Electrical |  | Pass | Fail | 0 | 4 | 618 | 2023-02-02 14:14 | 2023-02-02 16:14 | 2023-02-02 15:30 | 2023-02-02 18:14 | 2023-02-28 09:30
MSA-DTWD | WA5413467 | 2 | AWB Co. | M Block - wall and slaw tiling - undercover area - 2 x lights not working | Electrical | Lighting, External | 823.36 | Pass | Fail | 0 | 3 | 608.75 | 2022-05-12 11:20 | 2022-05-17 17:00 | 2022-05-16 07:00 | 2022-05-17 17:00 | 2022-06-10 15:45 |  | WCAPPR | Attended site and signed in, completed jsa, spoke with fm about job, isolated lighting circuits and removed old lamps and holders, replaced with new , tested lights and working as intended , completed paperwork, signed out, **job completed***
MSA-MRWA | WA5090373 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Office - Administration - A/C not working | Air Conditioning | Room Air Conditioners | 782.95 | Pass | Fail | 0 | 4 | 607.5 | 2022-01-25 11:39 | 2022-01-27 17:00 | 2022-01-27 08:00 | 2022-01-27 17:00 | 2022-02-21 15:30 |  | WACCES | Replaced PCB and thermistors on VRV condenser
MSA-DTWD | WA5562795 | 1 | Damian Rak Electrical Pty Ltd | Please secure circuit breaker | Electrical | General Electrical |  | Fail | Fail | 1 | 4 | 605.5 | 2022-06-20 10:02 | 2022-06-21 17:00 | 2022-06-27 10:30 | 2022-06-21 17:00 | 2022-07-22 16:00 |  |  | Completed
MSA-DFES | WA5985875 | 1 | Go Doors | Kalamunda Vols rear gate of the station have to open manuallyand opening automatically | Building | Materials | 2003.34 | Pass | Fail | 0 | 3 | 604 | 2022-10-01 11:58 | 2022-10-03 17:00 | 2022-10-01 14:00 | 2022-10-03 17:00 | 2022-10-26 18:00 |  |  | Works completed
MSA-DFES | WA6519261 | 1 | ACTION GLASS & ALUMINIUM | Bushfire risk management office-window has a crack-see notes | Glazing | Window Glass | 1379.57 | Pass | Fail | 0 | 4 | 603.75 | 2023-01-25 14:27 | 2023-01-27 17:00 | 2023-01-27 06:45 | 2023-01-27 17:00 | 2023-02-21 10:30
MSA-DTAG | WA6145158 | 2 | AHS Services WA Pty Ltd (Anchor) | G4S Staff room - Flush button in female toilet is faulty | Plumbing & Drainage | Water | 358.2 | Fail | Fail | 3 | 7 | 603.45 | 2022-11-02 11:24 | 2022-11-07 17:00 | 2022-11-28 08:33 | 2022-11-07 17:00 | 2022-12-23 12:00 |  |  | 28/11 found flush system to be a zern valve.Quoted required to replace23/12 parts ordered on job number WA6203592
MSA-DFES | WA6249799 | 2 | AWB Co. | Ground - Engine room - Ceiling tiles have fallen down - see notes | Building | Ceiling | 894.59 | Pass | Fail | 0 | 4 | 603 | 2022-11-21 14:52 | 2022-11-24 17:00 | 2022-11-24 14:00 | 2022-11-24 17:00 | 2022-12-19 17:00 |  |  | works completed Attended Site 24/12/2022Inspected missing / damage ceiling TilesCleaned Exhaust fan Will need to re attend with Ladder Attended Site and Completed Works 19/12/2022 Replaced 9 panels, 1 panel was left as power was still live as per photosJob Complete
MSA-DTWD | WA5792055 | 2 | AWB Co. | Breaker will not reset in switchboard in room B61 | Electrical | Distribution Board | 1194.4425 | Pass | Fail | 0 | 3 | 602.5 | 2022-08-23 11:13 | 2022-08-26 17:00 | 2022-08-25 11:00 | 2022-08-26 17:00 | 2022-09-19 13:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located pole with burnt top. Set up work area. Isolated. Dropped pole down. Replaced pole top with new led top. Swung pole back to original state. Energised circuit. Light now working. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5017335 | 2 | AWB Co. | Ground - Between A and N blocks - Damaged electrical pit | Electrical | General Electrical | 935.12 | Pass | Fail | -1 | 3 | 602.25 | 2022-01-13 12:56 | 2022-01-18 17:00 | 2022-01-14 11:45 | 2022-01-18 17:00 | 2022-02-08 14:00 |  | WACCES | Attended site and signed in. Completed JSA. Located pit. Set up work area. Removed cracked and broken pieces of old pit. Dug out sand around pit. Made new foundation and lip out of concrete. Placed pit lid on. Notified fm of works completed **job complete**
MSA-DTWD | WA5381525 | 3 | Protek 24/7 Building & Maintenance | Room B332 - Vinyl lifting, damaged and sections broken out | Flooring | Vinyl | 2072.25 | Pass | Fail | -1 | 3 | 602.25 | 2022-04-26 09:36 | 2022-05-03 17:00 | 2022-04-28 09:45 | 2022-05-03 17:00 | 2022-05-23 12:00 |  | WACCES | Remove and replace vinyl floor covering
MSA-DCA | WA6112187 | 1 | Protek 24/7 Building & Maintenance | Stairwell 1, Pool Plant/Light Well-HAZCHEM door for the Pool Plant and Light Well is unable to close | Building | Doors | 625.1 | Pass | Fail | 0 | 4 | 601.75 | 2022-10-21 13:38 | 2022-10-24 17:00 | 2022-10-24 08:15 | 2022-10-24 17:00 | 2022-11-18 10:00 |  | WCAPPR | Eased door so that it shuts and locks
MSA-DTWD | WA6178842 | 2 | WESTERN IRRIGATION PTY LTD | Child Care - Retic control box showing fault on station 8 & sprinklers not working | Landscaping & Gardening | Grounds Maintenance | 5287.33 | Fail | Fail | 0 | 4 | 601.5833 | 2022-11-14 14:00 | 2022-11-17 17:00 | 2022-11-18 10:15 | 2022-11-17 17:00 | 2022-12-13 11:50 |  |  | Excavate and trace mainline, replace faulty valve, repair pipework and low voltage wiring. Required use of excavator to expose pipework and trace.
MSA-DTWD | WA5306438 | 1 | AWB Co. | E block - E603 - exhaust fan is grinding grinding noise and has completely stopped working. | Electrical | General Electrical | 549.1 | Pass | Fail | 0 | 4 | 601 | 2022-04-06 13:29 | 2022-04-07 17:00 | 2022-04-07 07:30 | 2022-04-07 17:00 | 2022-05-02 08:30 |  | WACCES | Attended site and signed in, completed jsa, spoke with fm about job, located fan and removed ceiling panels , taped on ducting to fan , mounted fan in roof space, re fitted ceiling panels, tested fan and working as intended, cleaned up,packed up, completed paperwork, signed out Job complete
MSA-DTWD | WA5728137 | 3 | AWB Co. | 7 x faulty lights | Electrical | Lighting, Internal | 2499.4975 | Pass | Fail | 0 | 4 | 601 | 2022-08-15 14:46 | 2022-08-22 17:00 | 2022-08-22 11:00 | 2022-08-22 17:00 | 2022-09-16 12:00 |  |  | Attended site and signed in. Completed JSA and paperwork required for ewp works. Liaised with fm about works going ahead. Located room E208. Set up work area and moved equipment to suit works. Isolated circuit requiring work. Removed 6x old faulty light fittings and installed 6x new LED battens. Rearranged room to suit ewp works on other side of room. Removed 6x fittings and installed 6x new LED battens. Disposed of all rubbish. Rewired control box to suit new lights. Drove ewp back to location where it got dropped off. Rearranged room back to original state. Notified relevant personnel of works completed. Completed paperwork. **job complete**
MSA-DCA | WA5565818 | 1 | Techworks Electrical | Main Building - CS2 - Emergency Exit Light out | Electrical | General Electrical | 259.03 | Pass | Fail | 0 | 4 | 601 | 2022-06-22 11:43 | 2022-06-23 17:00 | 2022-06-23 07:00 | 2022-06-23 17:00 | 2022-07-18 08:00 |  | WCAPPR | Replaced tube and all working well.
MSA-DTWD | WA6528298 | 1 | Australian Airconditioning Services Pty Ltd | 3CF1 - A/C has broken facia and vents stuck closed | Air Conditioning | Evaporative Coolers | 679.67 | Pass | Fail | 0 | 4 | 601 | 2023-02-02 10:16 | 2023-02-03 17:00 | 2023-02-03 08:30 | 2023-02-03 17:00 | 2023-02-28 09:30
MSA-DFES | WA6526879 | 3 | ADVANCED LOCK & KEY | Practical Training Ground - Engine bay - Broken door lock on dry-cleaning cupboard | Security | Locksmith |  | Pass | Fail | 0 | 3 | 600.75 | 2023-02-01 11:37 | 2023-02-08 17:00 | 2023-02-06 14:15 | 2023-02-08 17:00 | 2023-03-03 15:00 |  | WACCES
MSA-DTWD | WA5413455 | 1 | Lane's Plumbing | BLD 833 - Unisex Toilet Cistern Faulty | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Fail | 0 | 3 | 600.5 | 2022-05-12 11:16 | 2022-05-13 17:00 | 2022-05-12 13:30 | 2022-05-13 17:00 | 2022-06-06 14:00 |  |  | job completed - REPLACE BUTTON ASSEMBLY TO UNISEX TOILET BLD 833
MSA-DTWD | WA6000737 | 3 | AWB Co. | water damaged ceiling | Building | Ceiling | 1998.595 | Pass | Fail | 0 | 4 | 600.5 | 2022-10-10 10:12 | 2022-10-17 17:00 | 2022-10-17 13:30 | 2022-10-17 17:00 | 2022-11-11 14:00 |  |  | Works completed
MSA-DTWD | WA5379858 | 2 | SENTINEL LOCK SERVICE PTY LTD | C20 Customer Service Centre - Sticky lock on rear access door | Security | Locksmith | 314.83 | Fail | Fail | 0 | 4 | 599.9167 | 2022-04-21 16:52 | 2022-04-27 17:00 | 2022-04-29 14:30 | 2022-04-27 17:00 | 2022-05-24 14:25 |  | WACCES | Block C _ C20 - Door lock faulty to rear access.Lock repaired.Digital pad serviced - new spring kit for pad installed.Lock serviced and internal mechanisms repaired.
MSA-DFES | WA5511717 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Laboratory Field Analysis- Ground Floor -outside the carpark -Light covers dropped from ceiling | Electrical | Lighting, Internal | 403.435 | Pass | Fail | 0 | 3 | 599.5 | 2022-06-13 07:57 | 2022-06-17 17:00 | 2022-06-16 11:15 | 2022-06-17 17:00 | 2022-07-11 10:45 |  | WACCES | Arrived onsite at 8:30 to install 1 x LED batten into laboratory field analysis. Installed and tested 1 x LED batten and notified site of works completed, continued onsite at 10:45
MSA-DTAG | WA5105654 | 1 | Australian HVAC Services Pty. Ltd. | Roof - Court 1 & Court 5 - a/c area warm, 25C incoming, no cool airflow | Air Conditioning | Room Air Conditioners | 785.81 | Pass | Fail | 0 | 3 | 598.9 | 2022-02-04 12:34 | 2022-02-07 17:00 | 2022-02-04 12:35 | 2022-02-07 17:00 | 2022-03-01 11:29 |  |  | 40552
MSA-DTWD | WA5691754 | 3 | Dormakaba Australia Pty Ltd | Lecture Theatre Auto door has lost oil and is closing to fast on manual action | Building | Automatic Doors | 3899.48 | Pass | Fail | -1 | 3 | 598.3333 | 2022-08-03 07:47 | 2022-08-09 17:00 | 2022-08-04 12:41 | 2022-08-09 17:00 | 2022-08-29 11:01 |  |  | 4/8/22 - Internal lecture theatre D22 door. Found hydraulic fluid has leaked out of unit and is causing door to slam closed. Advised Theo from engineering that unit will require replacement, quotation required to replace ED800 for ED100 with standard arm, existing external and internal buttons can be re used and advised engineering that power to door will need to be isolated via switchboard when we do replacement as power is coming through roof with no access to GPO. Pictures attached for reference29/8/22 - Note new IP number 1171232 ED100 level 2 lecture theatre. Removed old unit and fitted new ED100 complete with standard arm, 30mm spindle and cover, wired in push buttons and commissioned.
MSA-DFES | WA5682716 | 1 | Protek 24/7 Building & Maintenance | Level 2 – Wellness Branch-Water leak 3 spots-see notes | Roofing | Metal Roofing | 2665.58 | Pass | Fail | 0 | 4 | 595.75 | 2022-07-29 11:02 | 2022-08-01 17:00 | 2022-08-01 12:15 | 2022-08-01 17:00 | 2022-08-26 08:00 |  | WACCES | Remove and replace water membrane around drain and replace Remove and replace damaged ceiling sheets
MSA-DTAG | WA6414929 | 3 | Midolo Building Services | Front Desk - several office drawers are stiff/runners need lubricating | Furniture | Office Furniture | 627.9 | Pass | Fail | -1 | 3 | 595.5 | 2023-01-11 11:00 | 2023-01-18 17:00 | 2023-01-13 14:30 | 2023-01-18 17:00 | 2023-02-07 10:00 |  | WACCES
MSA-DTWD | WA6360846 | 2 | AWB Co. | Ground Floor - M Block - Paint Store - Replace defective ceiling light with led | Electrical | Lighting, Internal | 677.52 | Pass | Fail | 0 | 4 | 594.25 | 2022-12-07 15:23 | 2022-12-12 17:00 | 2022-12-12 14:45 | 2022-12-12 17:00 | 2023-01-06 09:00 |  | WACCES | Attended site, sign in, completed jsa, went to faulty light location, started removing light, finished removing light and installed new high bay light, tested light, light working as intended, pack up cleaned up, completed paperwork, sign out. ***Job complete***
MSA-DTAG | WA5566659 | 3 | Sapio Pty Ltd | Ground - Courtside - PA System is cutting in and out – currently not working | ICT/Audiovisual | General AV works | 3538.08 | Pass | Fail | -1 | 3 | 583.5 | 2022-06-23 10:31 | 2022-06-30 17:00 | 2022-06-24 09:00 | 2022-06-30 17:00 | 2022-07-18 16:30 |  |  | Supplied and installed new Audio Matrix Switcher. Programmed zones and adjusted audio volume to each. Tested. Ok.
MSA-DTWD | WA6000459 | 0 | ACTION GLASS & ALUMINIUM | Library - Broken window | Glazing | Window Glass | 3994.56 | Fail | Fail | 0 | 3 | 581.9167 | 2022-10-10 08:01 | 2022-10-10 10:01 | 2022-10-10 10:15 | 2022-10-10 12:01 | 2022-11-03 16:10 |  |  | ATTENDED SITEPATCHED & MADE SAFE BROKEN OVERSIZE WINDOW5.38 CLEAR LAMINATED SAFETY GLASS2-1600 X 9206 SQM OF SAFETY FILM AND 4 TUBES OF SILICONERETURNED LATER DATE WITH 5 MEN TO REGLAZE10.38 GREY LAMINATED SAFETY GLASS1-1760 X 2360POLISHED EDGES2.5 L/M OF RUBBER REPLACED AND 2 TUBES OF SILICONE USEDCOMPLETED AS PER APPROVED BRAF
MSA-DTAG | WA5861633 | 3 | Midolo Building Services | External-Balcony exit door skin has delaminated | Building | Doors | 969.76 | Pass | Fail | 0 | 3 | 580.5 | 2022-09-13 10:25 | 2022-09-20 17:00 | 2022-09-20 10:30 | 2022-09-20 17:00 | 2022-10-14 15:00 |  | WACCES | DOOR REMOVED - SKIN & EDGING SECURED & DOOR RE HUNG
MSA-DTWD | WA5482147 | 0 | SCAVENGER SUPPLIES PTY LTD | Ground - Zone 2 - alarm fault buzzer is faulty | Fire Protection Services | Fire Protection - Monitor System | 345.85 | Pass | Fail | 0 | 3 | 579.2333 | 2022-05-31 09:20 | 2022-05-31 11:20 | 2022-05-31 10:15 | 2022-05-31 13:20 | 2022-06-24 13:29 |  | WCAPPR | 31/05/2022-WARREN BLAY ATTENDED CALL OUT-31/05/2022-BEN COWDRAY -Requires additional time on site - see report RE OTHER CONDITIONS-MANHOLE COVER TO BE INSTALLED TO ALLOW ACCESS TO FAULTY SENSOR.24-06-2022-WARREN BLAY TO ATTEND TO FINALISEREQUESTED MANHOLE COVER WAS NEVER AUTHORISEDCLOSE JOB COMPLETED
MSA-DTWD | WA5887624 | 2 | ACTION GLASS & ALUMINIUM | Glass on Bi fold doors have been vandalilsed | Glazing | Door Glass | 7734.88 | Pass | Fail | 0 | 3 | 579 | 2022-09-16 08:57 | 2022-09-21 17:00 | 2022-09-20 10:00 | 2022-09-21 17:00 | 2022-10-14 13:00 |  | WACCES | ATTENDED SITE MEASURED & ASSESSED SCRATCHED GLASS PANELSRETURNED LATER DATE REMOVED & REPLACED ANTI GRAFITTI FILM ON GLASS DOORSCOMPLETED AS PER APPROVED BRAF
MSA-DTWD | WA6376017 | 3 | AWB Co. | Broken light fitting at east end of passageway - see note | Electrical | Lighting, Internal | 462.85 | Pass | Fail | 0 | 3 | 578 | 2022-12-15 12:30 | 2022-12-22 17:00 | 2022-12-19 12:00 | 2022-12-22 17:00 | 2023-01-12 14:00 |  | WACCES | Attended site signed in jsa completed. installed seamless fitting next to light and plugged into battery system. Tested operational.Joh completed.
MSA-DFES | WA5098541 | 0 | Australian HVAC Services Pty. Ltd. | Lunch Room - second air -con is not working at all now | Air Conditioning | Room Air Conditioners | 756.2 | Pass | Fail | 0 | 3 | 577 | 2022-02-01 09:45 | 2022-02-01 11:45 | 2022-02-01 11:00 | 2022-02-01 13:45 | 2022-02-25 12:00 |  | WACCES | Travelled to site to replace indoor PCBs on Daikin unit in lunch room.Checked operation all working ok.
MSA-DTWD | WA5407934 | 3 | AWB Co. | 1F16 - Noisy and faulty fluroes in office | Electrical | General Electrical | 713.46 | Pass | Fail | 0 | 3 | 576.5 | 2022-05-11 15:11 | 2022-05-18 17:00 | 2022-05-16 11:30 | 2022-05-18 17:00 | 2022-06-09 12:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed. Isolated blue 4 and commenced works. Removed x4 fluros and disposed of in correct bins. installed x4 new surface mount kits. Kits are slightly smaller so needs paint around lights. Installed x4 panels in room and tested. *** job completed ***
MSA-DTWD | WA5307108 | 3 | AWB Co. | E101 - Wall Exhaust fan Noisy and has no blades | Electrical | General Electrical | 635.7 | Pass | Fail | -1 | 3 | 576.25 | 2022-04-07 10:09 | 2022-04-14 17:00 | 2022-04-08 12:45 | 2022-04-14 17:00 | 2022-05-02 13:00 |  | WACCES | Attended site and signed in, completed jsa , spoke to fm about job, removed old fan , replaced with new, tested fan and working as intended, cleaned up,packed up, completed paperwork,signed out Job completed
MSA-DTWD | WA5568916 | 3 | AWB Co. | LG 02 and LG 03 -Two square panels are not working | Electrical | Lighting, Internal | 913 | Pass | Fail | -1 | 3 | 575.25 | 2022-06-27 10:06 | 2022-07-04 17:00 | 2022-06-28 10:15 | 2022-07-04 17:00 | 2022-07-22 09:30 |  | WACCES & WCAPPR | Attended site signed in jsa completed. Removed two panels and replaced with two new led SAL panels. Tested and working fine.Job completed
MSA-DCA | WA5472788 | 1 | Techworks Electrical | Level 4 - Plant room - Lights have tripped out | Electrical | Lighting, Internal | 2313.16 | Pass | Fail | 0 | 3 | 575 | 2022-05-24 10:33 | 2022-05-25 17:00 | 2022-05-24 12:30 | 2022-05-25 17:00 | 2022-06-17 11:30 |  | WCAPPR | Tasks completed 1. arrived onsite and was met with Michael who showed me up to the issue. Found that one of the lights had a melted plug top that was causing a dead short to earth. The plug top had melted the 413 also meaning when plug top was removed dead short was still there.2. grabbed a new CBI RCBO from city’s and installed after testing to find what neutral was the one I needed. 3. rcbo tripped when lights where turned on meaning the 413 will need to be replaced and then circuit tested again. This will require a scaffold with a platform at 4m high to be able to reach the 413 in a safe manner as the 14ft steps that are in the plant room do not reach.Tasks completed on return trip. 1. Met with Michael and scaffolders and took everything up to plant room and set everything up. 2. Replaced the faulty 413 and tested. All working well.
MSA-DTAG | WA6021634 | 3 | Australian HVAC Services Pty. Ltd. | Level 12 - Room 12.03 - A/C Fault - possible BMS Failure | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2982.76 | Pass | Fail | -1 | 2 | 575 | 2022-10-14 09:23 | 2022-10-21 17:00 | 2022-10-14 10:30 | 2022-10-21 17:00 | 2022-11-07 09:30 |  |  | Attend site with icon logic. Access level 12 vav DD 12.12. Isolate box and disconnect electrical wiring to controllers. Unbolt controllers from shaft and remove. Install new controllers to shaft and stroke operation. Connect electrical wiring. Access wall sensor and disconnect. Install new wall sensor. Deisolate and check operation. Carry out programming of new controls. Calibrate wall sensor. Check airflows and found to be as per design. Box is working as normal. Clean up area.
MSA-DTWD | WA5390664 | 1 | Equans Mechanical Services Australia | D213 - A/C not working | Air Conditioning | Room Air Conditioners | 287.79 | Pass | Fail | 0 | 3 | 573.6333 | 2022-05-02 14:44 | 2022-05-03 17:00 | 2022-05-03 12:50 | 2022-05-03 17:00 | 2022-05-27 10:28 |  |  | Unit failure due to power , reset and checked all ok
MSA-DTAG | WA6357643 | 1 | Sapio Pty Ltd | Ground Floor - POP Interview Room 2 - duress button is stuck and is unable to be reset - See Notes | Security | Monitoring | 691 | Pass | Fail | 0 | 3 | 571.5 | 2022-12-05 15:04 | 2022-12-06 17:00 | 2022-12-06 14:00 | 2022-12-06 17:00 | 2022-12-30 09:30 |  |  | Work performed by Michael Tomlinson & Marco Guerrini (30/12/2022)Fault find the cable servicing input 210 Hold up Interview Room 2.Fixed and tested cable integrity ok.Installed the new Holdup button and tested ok.Job completed.
MSA-DTWD | WA5094011 | 0 | Precise Air Group | Chiller will not reset | Air Conditioning | Room Air Conditioners | 21290.52 | Fail | Fail | 0 | 3 | 570.3 | 2022-01-31 07:52 | 2022-01-31 09:52 | 2022-01-31 14:23 | 2022-01-31 11:52 | 2022-02-24 08:41 |  |  | Completed quoted works
MSA-DFES | WA6539730 | 2 | ACTION GLASS & ALUMINIUM | Gym - Large Mirror in Gym with crack across it | Glazing | Mirrors | 508.175 | Pass | Fail | 0 | 3 | 559 | 2023-02-08 16:42 | 2023-02-13 17:00 | 2023-02-13 09:30 | 2023-02-13 17:00 | 2023-03-08 16:30 |  | WACCES
MSA-DTWD | WA5565160 | 2 | Water2water Pty Ltd | J121 - Water Cooler tripping power circuit | Plumbing & Drainage | Water | 2442.88 | Pass | Fail | 0 | 3 | 558.0167 | 2022-06-21 14:15 | 2022-06-24 17:00 | 2022-06-22 09:00 | 2022-06-24 17:00 | 2022-07-15 15:01 |  |  | Replaced old fountain with new zip sitemaster fountain with filter system.
MSA-DTAG | WA5692462 | 2 | Australian HVAC Services Pty. Ltd. | Level 6 - No air flow in Prisoners Review Board office | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1835.06 | Pass | Fail | -1 | 3 | 557 | 2022-08-03 13:25 | 2022-08-08 17:00 | 2022-08-04 08:00 | 2022-08-08 17:00 | 2022-08-27 13:00 |  | WACCES | Pick up Actuators from office. Travel to site. Access level 6 and isolate power supply to floor fire dampers. Access office area and locate failed actuator. Access ceiling and disconnect electrical wiring. Unbolt actuator from shaft and remove. Remove old mounting bracket. Install new mounting bracket and fit new actuator. Set correct direction and secure actuator to shaft. Connect electrical wiring. Deisolate power supply and test operation, working ok.Access plantroom area and locate failed actuator. Access and disconnect electrical wiring. Unbolt actuator from shaft and remove. Remove old mounting bracket. Install new mounting bracket and fit new actuator. Set correct direction and secure actuator to shaft. Connect electrical wiring. Deisolate power supply and test operation, working ok.Dispose of old actuators.
MSA-DTWD | WA5588941 | 3 | AWB Co. | Rear Carpark - Level 1 - External - Damaged pavers and curb rear carpark on corner near plant room | Flooring | Concrete | 1236.42 | Fail | Fail | 1 | 4 | 557 | 2022-07-08 08:31 | 2022-07-15 17:00 | 2022-07-19 09:00 | 2022-07-15 17:00 | 2022-08-11 14:00 |  |  | works completed as per request
MSA-DFES | WA5304877 | 3 | Protek 24/7 Building & Maintenance | Ground - Engine Room - see details below | Building | General Building | 1453.825 | Pass | Fail | -1 | 2 | 556.25 | 2022-04-05 10:27 | 2022-04-12 17:00 | 2022-04-06 10:30 | 2022-04-12 17:00 | 2022-04-29 14:45 |  | WACCES | Repair Rust to engine room door
MSA-DTWD | WA5470693 | 3 | AWB Co. | G Block - wood, auto & metals - Roof Lights - Various Lights need replacing - LED & incadescents | Electrical | Lighting, External | 1693.86 | Pass | Fail | -1 | 2 | 556 | 2022-05-23 11:47 | 2022-05-30 17:00 | 2022-05-24 09:30 | 2022-05-30 17:00 | 2022-06-16 13:30 |  |  | Attended site signed in jsa completed. Located keys and found ewp. Completed scissor lift work by replacing x6 led hi bay lights in G block.All tested and job completed
MSA-DTWD | WA5496478 | 3 | AWB Co. | Two faulty fluro units & one unit is flickering | Electrical | Lighting, Internal | 1221.66 | Pass | Fail | 0 | 3 | 556 | 2022-06-09 10:21 | 2022-06-16 17:00 | 2022-06-13 10:30 | 2022-06-16 17:00 | 2022-07-06 14:30 |  |  | Attended site signed in jsa completed. Isolated circuit B2 to replace lights in classroom. Removed 8 fittings and upon removal found disintigrated cables from heat being so close to the ballast etc. had to remove old wiring and put new in most lights. all installed tested and working. packed up and removed old fittings into bin requested by site. *** job completed ***
MSA-DTWD | WA6364236 | 2 | AWB Co. | Outside - pond pump damaged. | Electrical | General Electrical | 973.78 | Pass | Fail | 0 | 3 | 556 | 2022-12-12 10:22 | 2022-12-15 17:00 | 2022-12-13 09:00 | 2022-12-15 17:00 | 2023-01-05 13:00 |  | WCAPPR | Arrived at site, signed in, completed jsa, spoke to fm about works going ahead , ran cable in conduit to rcd mounted on wall, re wired all components to 2.5mm as some cables were not big enough, mounted gpo on wall ,isolated power, wired into circuit, re energised circuit, tested gpo and working as intended, plugged in pump and tested, working as intended, completed paperwork, signed out *job complete*
MSA-DTWD | WA5686700 | 1 | Protek 24/7 Building & Maintenance | Roof leak near control room TM159 | Roofing | Metal Roofing | 1929.58 | Pass | Fail | 0 | 3 | 555.5 | 2022-08-01 10:18 | 2022-08-02 17:00 | 2022-08-02 09:45 | 2022-08-02 17:00 | 2022-08-25 13:15 |  | WACCES | ? Remove and dispose of damaged flashings? Supply and install new flashings & fixings? Clean and reseal joins
MSA-DTAG | WA6402481 | 1 | Midolo Building Services | Custody lower - Cell 4 and Surrounds - Water Leak in wall - See Notes Below | Building | Internal Walls | 3667.72 | Fail | Fail | 0 | 4 | 555.3333 | 2023-01-05 11:43 | 2023-01-06 17:00 | 2023-01-09 07:30 | 2023-01-06 17:00 | 2023-02-01 10:50 |  | WACCES
MSA-DTWD | WA6426132 | 3 | AWB Co. | Francis st path - Pathway lights out x3 - Broken with no power | Electrical | Lighting, External | 2038.82 | Pass | Fail | 0 | 3 | 555 | 2023-01-12 14:42 | 2023-01-19 17:00 | 2023-01-17 11:15 | 2023-01-19 17:00 | 2023-02-09 14:15 |  | WCAPPR
MSA-DTWD | WA5470117 | 2 | AWB Co. | Creche LG05 - External - Lighting which appears to be LED. Flashing x 1, not operating x1 | Electrical | Lighting, External | 503.27 | Pass | Fail | 0 | 3 | 554.5 | 2022-05-23 08:08 | 2022-05-26 17:00 | 2022-05-24 08:30 | 2022-05-26 17:00 | 2022-06-16 11:00 |  | WACCES | Attended site signed in jsa completed. Replaced drivers for 3 lights. Replaced 6 tubes. job is now completed
MSA-DFES | WA5793161 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Administration - North East Kitchen - No hot water in Kitchen-North East Region Lower Floor | Plumbing & Drainage | Water | 1978.91 | Pass | Fail | 0 | 3 | 554.0833 | 2022-08-23 16:49 | 2022-08-26 17:00 | 2022-08-24 09:30 | 2022-08-26 17:00 | 2022-09-16 11:35 |  |  | Arrived on site and singed in went to kitchen north east removed stiebel Eltron and installed a new super x had to a new 15mm pipe for relief valve.and modify pipe work tested and everything was fine
MSA-DTWD | WA6112200 | 2 | ACTION GLASS & ALUMINIUM | Broken windows in C101 | Glazing | Window Glass | 1106.805 | Pass | Fail | 0 | 3 | 553.75 | 2022-10-21 13:54 | 2022-10-26 17:00 | 2022-10-25 08:00 | 2022-10-26 17:00 | 2022-11-17 09:45 |  |  | ATTENDED SITETEMP GLAZED BROKEN WINDOW PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-564 X 1125RETURNED LATER DATE TO REGLAZE6.52 GREY TOUGHENED LAMINATED SAFETY GLASS1-564 X 11253.5 L/M OF RUBBER REPLACED PLUS SILICONE
MSA-DTWD | WA5385655 | 2 | ECO PLUMBING AND GAS PTY LTD | M009.2 - Hot water system - faulty | Plumbing & Drainage | HWS/Units Electric & Gas | 290.98 | Fail | Fail | 0 | 3 | 553.5 | 2022-04-29 11:33 | 2022-05-04 17:00 | 2022-05-05 15:30 | 2022-05-04 17:00 | 2022-05-28 17:00 |  |  | Repaired hot water unit
MSA-DTWD | WA6149102 | 2 | AWB Co. | External junction box is damaged | Electrical | General Electrical | 776.485 | Pass | Fail | 0 | 3 | 553 | 2022-11-04 12:12 | 2022-11-09 17:00 | 2022-11-09 08:00 | 2022-11-09 17:00 | 2022-12-02 09:00 |  | WCAPPR | Attended site signed in jsa completed. Isolated board in j block. Pulled cable out and replaced junction box.Fed back in and connected. All tested and operationalJob completed
MSA-DFES | WA5676348 | 3 | Protek 24/7 Building & Maintenance | Ground - Location 1 – Undercover car park - Roof drain down pipe rusted through | Roofing | Metal Roofing | 851.13 | Pass | Fail | 0 | 3 | 553 | 2022-07-25 07:51 | 2022-07-29 17:00 | 2022-07-26 13:00 | 2022-07-29 17:00 | 2022-08-18 14:00 |  | WACCES | Sealed pops
MSA-DFES | WA4994949 | 1 | Go Doors | Electric sliding Gate - Entrance to the rear - cant close the gate unless done manually | Building | General Building | 1322.43 | Pass | Fail | 0 | 3 | 552.25 | 2022-01-10 09:06 | 2022-01-11 17:00 | 2022-01-10 10:00 | 2022-01-11 17:00 | 2022-02-02 10:15 |  |  | Completed works.
MSA-DTWD | WA5201011 | 1 | Protek 24/7 Building & Maintenance | roof leak | Building | Ceiling | 1420.74 | Pass | Fail | 0 | 3 | 552 | 2022-03-02 10:59 | 2022-03-03 17:00 | 2022-03-02 12:15 | 2022-03-03 17:00 | 2022-03-25 12:15 |  | WACCES | Repair Roof leak
MSA-MRWA | WA5973389 | 2 | AWB Co. | Flickering light opposite room 517 | Electrical | Lighting, Internal | 336.6 | Pass | Fail | 0 | 3 | 552 | 2022-09-21 12:46 | 2022-09-27 17:00 | 2022-09-27 07:00 | 2022-09-27 17:00 | 2022-10-20 07:00 |  | WACCES | Attended site and signed in. Completed jsa. Set up work area on level 5. Located drivers in level 9 storeroom. Returned to level 5. Installed new driver supplied by site. Tested to make sure it was operating correctly. Completed paperwork. Signed out. **job complete**
MSA-DFES | WA5482774 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Applied Training Ground - Ceiling - Engine Room - please see details | Electrical | General Electrical | 733.795 | Pass | Fail | 0 | 3 | 551.75 | 2022-05-31 15:16 | 2022-06-08 17:00 | 2022-06-08 10:15 | 2022-06-08 17:00 | 2022-07-01 10:00 |  |  | Attended site and signed in, investigated high bay lights that were not turning off. Found a junction where old sensor was removed & not replaced. Picked up parts from wholesaler. Returned & installed new WP sensor. All working correctly. Informed staff of job completion.
MSA-DCA | WA5686466 | 1 | CONNECT SECURITY SYSTEMS | zone 50-water leak into smoke detector | Fire Protection Services | Smoke and Heat Detection | 911.42 | Pass | Fail | 0 | 3 | 551.2667 | 2022-08-01 08:42 | 2022-08-02 17:00 | 2022-08-01 11:42 | 2022-08-02 17:00 | 2022-08-24 10:58 |  |  | Removed zone 50 smoke detector until leaks resolved in P Block. Replaced vandal damaged PE Beam outside P Block with new.
MSA-DTWD | WA5549136 | 1 | Protek 24/7 Building & Maintenance | F5 - Roof leak - Water is leaking in from window frames On SW side | Building | General Building | 1869.875 | Pass | Fail | 0 | 3 | 551.25 | 2022-06-17 13:17 | 2022-06-20 17:00 | 2022-06-20 08:45 | 2022-06-20 17:00 | 2022-07-13 08:00 |  | WACCES | Repair leaking windows
MSA-DTWD | WA5513768 | 2 | Dormakaba Australia Pty Ltd | South Entrance - External Glass Door - door censors are not operating effectively - see notes below | Building | Automatic Doors | 3409.32 | Pass | Fail | 0 | 3 | 551.2167 | 2022-06-14 13:07 | 2022-06-17 17:00 | 2022-06-15 12:17 | 2022-06-17 17:00 | 2022-07-08 11:30 |  |  | 15/6/22 - Attended site and found microhead sensor only working intermittently, replaced sensor as authorised By Kevin, also replaced 4 out of date batteries as requested and authorised by Kevin, adjusted field size on ixio sensor, tested all working fine now. Needed 4 batteries as this unit has 2 motors. Please quote to supply and install 16 heavy duty track wheels as requested by Kevin, this will require 3 technicians for safety as the are large heavy doors. Works to be carried out in July when school closes for break.8/7/22 - Attended site and replaced 16 heavy duty track wheels as per quote. Also found pib boards to be faulty replaced 2 boards tested and all working fine now.
MSA-DTWD | WA5512058 | 2 | Equans Mechanical Services Australia | AT234 - Server Room - Software not responding to unit in server room - See notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 790.13 | Fail | Fail | 1 | 4 | 551 | 2022-06-13 12:52 | 2022-06-16 17:00 | 2022-06-22 11:30 | 2022-06-16 17:00 | 2022-07-15 10:30 |  |  | SEE REPORT
MSA-DFES | WA5513382 | 1 | Protek 24/7 Building & Maintenance | External Ground Floor - Main Carpark - fence posts starting to fall - See notes below | Building | Steel Fencing & Gates | 3685.36 | Pass | Fail | 0 | 3 | 551 | 2022-06-14 10:01 | 2022-06-15 17:00 | 2022-06-14 15:15 | 2022-06-15 17:00 | 2022-07-07 14:15 |  | WACCES | replace fence posts
MSA-DTWD | WA5513763 | 2 | Dormakaba Australia Pty Ltd | North Entrance - External Glass Door - door censors are not operating effectively - see notes below | Building | Automatic Doors | 2039.8 | Pass | Fail | 0 | 3 | 550.8833 | 2022-06-14 13:03 | 2022-06-17 17:00 | 2022-06-15 13:54 | 2022-06-17 17:00 | 2022-07-08 12:47 |  |  | 15/6/22 - 1046834 - Attended site replaced 2 out of date batteries as authorised by Kevin. Adjusted sensitivity on internal sensor, reattached mounting for sensor and exit sign as it was on an angle with iponly 2 screws attached, this was also affecting the angle of the sensor. Tested all working fine now. Noticed track wheels are noisy and need replacing. Please quote to supply and install 8 heavy duty track wheels, 3 technicians will be required as these doors are large and heavy. Works need to be carried out in July during school break.15/6/22 - 1052999 - Attended site replaced 2 out of date batteries as authorised by Kevin. Adjusted sensitivity on internal sensor, reattached mounting for senso and exit sign as it was on an angle with iponly 2 screws attached, this was also affecting the angle of the sensor. Tested all working fine now.8/7/22 - 1046834 - Attended site and replaced 8 times heavy duty track wheels as per quote. Tested and all working fine now.
MSA-DTWD | WA5304718 | 2 | AWB Co. | T040 - Circuit of power points keep tripping out | Electrical | General Electrical | 635.935 | Pass | Fail | 0 | 3 | 546 | 2022-04-05 09:25 | 2022-04-08 17:00 | 2022-04-05 13:30 | 2022-04-08 17:00 | 2022-04-28 07:30 |  | WCAPPR | Attended site signed in completed jsa. spoke with pete to let us in to T block. Isolated r6 and replaced two double gpo’s to avoid tripping as too many outlets on one circuit and no other way to run cables into wall. ** job completed ***
MSA-DTWD | WA5438033 | 3 | Equans Mechanical Services Australia | Room B127 - Dust extractor fan not working | Equipment | Electrical Equipment | 1861.44 | Fail | Fail | 0 | 3 | 546 | 2022-05-16 12:14 | 2022-05-23 17:00 | 2022-05-24 15:00 | 2022-05-23 17:00 | 2022-06-16 09:00 |  |  | ATTENDED SITE, SIGNED IN AND ACCESSED BUILDING B6 WITH P.A.P.S AND INVESTIGATED THE DUST EXTRACTION FAN. AFTER MONITORING THE FANS RUNNING CONDITIONS, CHECKING FOR RESTRICTIONS AND RECORDING AMP DRAWS WE FOUND THE STAR AND DELTA CONTRACTORS FAULTY. REPLACED BOTH CONTRACTORS AND SET TIMERS. STARTED THE FAN AND MONITORED THE CURRENT AND RUNNING CONDITIONS, AMP DRAWS WITHIN RANGE AND UNIT NOW RUNNING CORRECTLY.
MSA-DTWD | WA5628317 | 3 | M Construction (WA) | Ground Level - Main Entrance - 3 x broken tiles Aberdeen St entrance steps | Flooring | Tiling | 732.6 | Pass | Fail | 0 | 3 | 535.5 | 2022-07-15 13:22 | 2022-07-22 17:00 | 2022-07-20 07:00 | 2022-07-22 17:00 | 2022-08-11 14:30 |  |  | Inspected broken tiles, will return with materials to complete job. Secure area, grind out 3 broken tiles, replace with new tiles. Grout in tile, clean up. apply caution tape to stop foot traffic.
MSA-DTWD | WA5799336 | 3 | AWB Co. | Damaged mechanical door | Building | Doors | 2293.52 | Pass | Fail | -1 | 2 | 535 | 2022-08-30 11:16 | 2022-09-06 17:00 | 2022-09-01 07:00 | 2022-09-06 17:00 | 2022-09-23 14:00 |  |  | works completedsupplied, installed and painted new doorschool holiday works and completion
MSA-DTWD | WA5385580 | 2 | M Construction (WA) | Faulty timber decking | Carpentry | Timber (all types) | 1090.86 | Pass | Fail | 0 | 3 | 534.5 | 2022-04-29 10:53 | 2022-05-04 17:00 | 2022-05-03 10:15 | 2022-05-04 17:00 | 2022-05-25 16:45 |  | WACCES | Attended site and repaired decking.
MSA-DTWD | WA5382606 | 3 | Falcetta Plumbing and Gas | East Block - Level 5 - Male student Toilet - Toilet pan leaking from seal | Plumbing & Drainage | Toilets/Cisterns | 1629.97 | Pass | Fail | -1 | 2 | 534 | 2022-04-27 08:01 | 2022-05-04 17:00 | 2022-04-28 13:00 | 2022-05-04 17:00 | 2022-05-20 19:00 |  | WACCES | replaced 1x cistern, 2x button assemblies, repaired 1x pan, repaired 1x urinal cistern
MSA-DFES | WA5569528 | 3 | Protek 24/7 Building & Maintenance | Western Hallway - Skirting boards have been water damaged - no water leaks found | Building | Internal Walls | 1000 | Pass | Fail | -1 | 3 | 533 | 2022-06-27 15:30 | 2022-07-04 17:00 | 2022-06-30 09:00 | 2022-07-04 17:00 | 2022-07-22 14:00 |  | WACCES | Replace skirting
MSA-DTWD | WA5385955 | 1 | UNIVERSAL DOORS | Block 3 Heavy Auto - Faulty roller door | Building | Roller Shutters |  | Pass | Fail | 0 | 3 | 532.6667 | 2022-04-29 13:50 | 2022-05-02 17:00 | 2022-05-02 08:35 | 2022-05-02 17:00 | 2022-05-24 13:15 |  |  | job copmleted - supplied and installed 1 x Grifco 1hp, 3ph operator with mounting plate
MSA-DTWD | WA5126944 | 1 | Equans Mechanical Services Australia | D Block - Ground - Please check that “After Hours” is working correctly - see details below | Air Conditioning | Room Air Conditioners | 1000 | Fail | Fail | 0 | 3 | 532 | 2022-02-14 10:34 | 2022-02-15 17:00 | 2022-02-17 11:00 | 2022-02-15 17:00 | 2022-03-11 15:00 |  | WACCES | PLEASE SEE DETALIED REPORT
MSA-DCA | WA6653807 | 1 | Techworks Electrical | Various Levels - Light switches not working (see notes) | Electrical | Lighting, Internal |  | Pass | Fail | 0 | 3 | 532 | 2023-02-21 07:08 | 2023-02-21 17:00 | 2023-02-21 08:00 | 2023-02-21 17:00 | 2023-03-15 12:00
MSA-DCA | WA6231181 | 1 | Protek 24/7 Building & Maintenance | Robert Steele/Shipwrights Office - rear of building - Brackets to rear roller doors have all failed | Building | Doors | 1213.19 | Pass | Fail | 0 | 3 | 532 | 2022-11-18 14:34 | 2022-11-21 17:00 | 2022-11-21 07:45 | 2022-11-21 17:00 | 2022-12-13 11:45 |  |  | Adjusted doors where possible and wedged doors shut that couldn't be repairedRepair doors 1-3
MSA-DTWD | WA5696710 | 1 | Precise Air Group | cafeteria kitchen-faulty lagging on refrigeration pipes | Refrigeration | Refrigerators | 4277.35 | Fail | Fail | 7 | 10 | 531.6833 | 2022-08-08 13:54 | 2022-08-09 17:00 | 2022-09-27 10:02 | 2022-08-09 17:00 | 2022-10-19 13:43 |  |  | Freezer room suction line was freezing up due to pipe insulation deteriorated and leaking on ceiling,remove all old insulation cleaned all pipes and cut,glued and taped new insulation so the pipes were sealed correctly
MSA-DFES | WA6107173 | 1 | Australian HVAC Services Pty. Ltd. | Server room - aircon blowing hot air and green flashing light | Air Conditioning | Building HVAC Maintenance (Major Plant) | 4757.85 | Pass | Fail | 0 | 3 | 531.5 | 2022-10-20 08:37 | 2022-10-21 17:00 | 2022-10-20 12:00 | 2022-10-21 17:00 | 2022-11-11 15:30 |  |  | Luke Robson (11/11/2022) -Work NoteRemoval and replacement of AC 6 in server room completed.
MSA-DTWD | WA6130852 | 3 | SCAVENGER SUPPLIES PTY LTD | 3D16-Faulty PA speaker - Inaudible | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Fail | -1 | 3 | 531.5 | 2022-10-28 16:43 | 2022-11-04 17:00 | 2022-10-31 10:00 | 2022-11-04 17:00 | 2022-11-22 13:30 |  | WCAPPR | 31/10/2022- Need to return to site22/11/22 - Further investigation while completing other RCT at this site. Job on hold for access and more info. Possible quote to be organised for additional works/ new system.19/01/23 - Claim submitted today as approval on Quote SC8511 has been granted for - SCOPE OF WORKSBlock 3 Heavy Auto Hardstand - Supply and install external PA speaker to existing EWIS system in Block 3 heavy auto hardstand.This RCT claim can be closed.
MSA-DTWD | WA5307984 | 2 | ACTION GLASS & ALUMINIUM | T041 - Glass door has dropped - needs adjusting | Building | Doors | 542.5 | Pass | Fail | 0 | 3 | 531.1667 | 2022-04-08 08:16 | 2022-04-13 17:00 | 2022-04-12 09:05 | 2022-04-13 17:00 | 2022-05-04 12:15 |  | WACCES | ATTENDED SITEATTEMPTED TO ADJUST BOTTOM RAILRETURNED LATER DATE ADJUSTED AND REFIT BOTTOM DOOR RAIL WITH SIKAFLEX.RETURNED LATER DATE REFIT COVER PLATES AND END CAPS
MSA-DTWD | WA5473387 | 3 | Falcetta Plumbing and Gas | Faulty drain connection | Plumbing & Drainage | Drainage | 444.105 | Pass | Fail | -1 | 2 | 530.5 | 2022-05-24 14:32 | 2022-05-31 17:00 | 2022-05-26 15:30 | 2022-05-31 17:00 | 2022-06-17 18:00 |  | WACCES | replaced flexy drains with PVC
MSA-DTWD | WA6403317 | 1 | Equans Mechanical Services Australia | T Block - South Side - AC cutting out (see notes) - A40326059I | Air Conditioning | Package | 534.915 | Pass | Fail | 0 | 3 | 530.5 | 2023-01-06 09:37 | 2023-01-09 17:00 | 2023-01-09 08:00 | 2023-01-09 17:00 | 2023-01-31 10:30
MSA-DTWD | WA5681417 | 2 | AWB Co. | Exhaust Fan faulty | Electrical | General Electrical | 1408.9925 | Pass | Fail | 0 | 3 | 530.5 | 2022-07-28 11:50 | 2022-08-02 17:00 | 2022-08-02 07:00 | 2022-08-02 17:00 | 2022-08-24 09:30 |  | WACCES & WCAPPR | Attended site and signed in. Completed jsa. Completed pre roof checklist. Set up ladder on roof access point. Inspected harness. Put harness on. Got onto roof and replaced fan belts of motor. Went into cleaners room duct and accessed control box for motors. Connected back up. Tested. Checked for all exhaust fans working. All working as intended. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA6365750 | 3 | AWB Co. | Various Locations - high globes are faulty | Electrical | Lighting, Internal | 1224.265 | Pass | Fail | -1 | 2 | 530.5 | 2022-12-13 12:10 | 2022-12-20 17:00 | 2022-12-15 13:00 | 2022-12-20 17:00 | 2023-01-06 15:30 |  | WACCES | Attended site and signed in. Liaised with site about works going ahead. Completed JSA. Located room B30. Set up work area. Isolated lights. Supplied and replaced old fitting with new LED. Energised and tested. All working fine. Notified relevant personnel of works completed. **job complete**
MSA-DFES | WA5454784 | 1 | Australian HVAC Services Pty. Ltd. | Plant Room - Chiller 2 - Hasn't started | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2126.02 | Pass | Fail | 0 | 3 | 529.5239 | 2022-05-17 14:23 | 2022-05-18 17:00 | 2022-05-17 14:26 | 2022-05-18 17:00 | 2022-06-08 15:57 |  | WACCES | Chiller 2 DPT faulty causing chiller 2 fault. Replaced DPT and confirmed chiller system operating correctly.
MSA-DTWD | WA5687273 | 2 | Protek 24/7 Building & Maintenance | Roof leak near pallet racking under saw tooth roof | Roofing | Metal Roofing | 552.81 | Pass | Fail | 0 | 3 | 529.25 | 2022-08-01 15:00 | 2022-08-04 17:00 | 2022-08-02 14:00 | 2022-08-04 17:00 | 2022-08-24 15:15 |  | WACCES | Carried out water-test to confirm leak locationCleaned and temporary sealed glass to slow water ingressBRAF declined
MSA-DFES | WA5438211 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - Front Driveway - Driveway is getting flooded everytime it rains | Plumbing & Drainage | Drainage | 1530.14 | Fail | Fail | 0 | 3 | 529.25 | 2022-05-16 13:11 | 2022-05-23 17:00 | 2022-05-24 12:00 | 2022-05-23 17:00 | 2022-06-15 13:15 |  |  | 24/05/2022Attend site to investigate blocked storm curb drain. Found curb drain full of water. Used Flexdrive pump to pump out the water. Found large amount of mud at the bottom of the tank. Also found outlet blocks with roots and dirt. Will need to have job raised in order to book in pump truck to clear pit. Pack up and cleanup site. Advised admin.15/06/2022Return to site with TerraVac. Pump out storm water pit located at the front of complex. Pressure jet 150mm outlet. Remove mud and litter from bottom of storm pit. All okay. Pack up and clean up site.
MSA-DTWD | WA6113151 | 2 | AWB Co. | Main car Park West Main Entry -Car Park - Concrete power box has been driven over & damaged | Electrical | General Electrical | 2424.285 | Pass | Fail | 0 | 3 | 529 | 2022-10-24 09:21 | 2022-10-27 17:00 | 2022-10-25 07:00 | 2022-10-27 17:00 | 2022-11-16 08:00 |  | WACCES | Attended site signed in jsa completed. ANZ enviro removed pit by 6:30 am. Install new pit in same location and make secure.Job completed
MSA-DTWD | WA5368834 | 2 | Securex Security Systems & Services | Camera in alarm on CCTV System | Security | CCTV Surveillance | 856.27 | Pass | Fail | 0 | 3 | 528.5 | 2022-04-19 13:19 | 2022-04-22 17:00 | 2022-04-20 08:45 | 2022-04-22 17:00 | 2022-05-12 09:15 |  |  | 20/04/2022Camera sending alarm for video loss, constantly dropping out and in. Silenced the alarm in programming andrecommend replacing camera, analog dome 24vac. Not sure if worth replacing as guard mentioned Steve is consideringupgrading entire system may be best to follow up with Steve before replacing.12/05/2022Replaced camera upstairs in north block
MSA-DTWD | WA5163985 | 3 | AWB Co. | Museum ST entry - Brickwork falling away, rusted frame | Building | Internal Walls | 2268.815 | Fail | Fail | 1 | 4 | 528.4667 | 2022-02-18 14:25 | 2022-02-25 17:00 | 2022-03-03 09:02 | 2022-02-25 17:00 | 2022-03-25 09:30 |  |  | Replace retic box and repair bricks around
MSA-DTWD | WA6450111 | 1 | AWB Co. | Alfresco-Wooden door blown off hinges, smashing 4 x floating floor tiles door and tiles need replaci | Building | External Walls | 3729 | Pass | Fail | 0 | 3 | 528.1167 | 2023-01-16 09:17 | 2023-01-17 17:00 | 2023-01-16 11:00 | 2023-01-17 17:00 | 2023-02-07 11:07
MSA-DFES | WA5972828 | 3 | Critical Fire Protection & Training | ground-West End Office TDSC-Evacuation Speakers are not working in this office | Fire Protection Services | Fire Protection - Monitor System | 1730.3 | Pass | Fail | 0 | 3 | 528 | 2022-09-21 08:58 | 2022-09-29 17:00 | 2022-09-29 12:00 | 2022-09-29 17:00 | 2022-10-21 12:00 |  |  | Attend site carry out the following:Rewire OWS/ modify cabling to enable approx. 5 speakers in west end office and adjacent passage and rooms tooperate as intended.Replace 2 x speakers old original with new equivalent in west end office,Job done later in day to minimise disruption to operationsTest and commission
MSA-DFES | WA6523460 | 1 | ACTION GLASS & ALUMINIUM | Main entry left to the Auto door - Window glass Panel is broken | Glazing | Window Glass | 920.945 | Pass | Fail | 0 | 3 | 526.75 | 2023-01-31 17:39 | 2023-02-01 17:00 | 2023-02-01 11:15 | 2023-02-01 17:00 | 2023-02-23 10:00
MSA-DTWD | WA5962393 | 0 | SCAVENGER SUPPLIES PTY LTD | Security Alarm Panel - showing no comms | Fire Protection Services | Fire Protection - Monitor System | 693.62 | Pass | Fail | 0 | 3 | 526.5 | 2022-09-19 13:48 | 2022-09-19 15:48 | 2022-09-19 14:30 | 2022-09-19 17:48 | 2022-10-11 13:00 |  | WACCES | initial visit 19/9/22 2:30pmsecond visit 20/9/2022 13:10pm waiting on re-install 240 volt isolation switchCompleted 11/10/2022
MSA-DFES | WA5481662 | 2 | Securex Security Systems & Services | Room 10 - Ground - CCTV camera STILL not working | Security | CCTV Surveillance | 886 | Pass | Fail | 0 | 3 | 525.5 | 2022-05-30 15:34 | 2022-06-02 17:00 | 2022-06-02 12:00 | 2022-06-02 17:00 | 2022-06-24 09:30 |  |  | Iain McGillemhaoil (02/06/2022, 1200-1230) - Work NoteCamera 17 is not working, appears to be power but no picture. Tried resetting but couldn’t get picture working. Cable toother nvr is Cat6.Iain McGillemhaoil (10/06/2022, 1600-1630) - Work NoteCamera 1 front entry faulty not 17, no power cable at all. Tested coax ok but will need a connection for powerRecable power 15m difficult roof space, unsure how to get it through6ft steps.Iain McGillemhaoil (24/06/2022, 730-930) - Work NoteKarl Brook (24/06/2022, 800-930) - Work NoteRan new cable for power, connected found exisiting camera doesn’t work, so replaced with new one all good.
MSA-DTWD | WA5454500 | 3 | AWB Co. | A20 Open Office Area - Light fittings not working | Electrical | Lighting, Internal | 2204.43 | Pass | Fail | 0 | 3 | 524.6 | 2022-05-17 11:58 | 2022-05-24 17:00 | 2022-05-24 13:09 | 2022-05-24 17:00 | 2022-06-15 09:45 |  |  | Attended site signed in jsa completed, cleaned let us into A block. Replaced remaining tubes in block on high ceiling with ewp. ewp off hired to hammy hill.*** job completed ***
MSA-DTWD | WA5127894 | 2 | Lane's Plumbing | Supply room - R/O Filter system to labs leaking | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 3 | 524.5 | 2022-02-14 14:50 | 2022-02-17 17:00 | 2022-02-15 15:00 | 2022-02-17 17:00 | 2022-03-09 11:30 |  |  | JOB COPMLETED - REPLACE LEAKING RO FILTER SYSTEM TO LABS
MSA-DTAG | WA5101219 | 2 | Sapio Pty Ltd | Level 1 - Stairwell - alarm zone 112 - see notes below | Security | Monitoring | 803.33 | Pass | Fail | 0 | 3 | 520 | 2022-02-03 10:39 | 2022-02-08 17:00 | 2022-02-08 17:00 | 2022-02-08 17:00 | 2022-03-02 09:00 |  |  | Replaced and tested duress in Stairwell Zone 112.
MSA-DTWD | WA6298984 | 2 | Precise Air Group | U011 - Air con is blowing hot air | Air Conditioning | Room Air Conditioners | 1962.6 | Pass | Fail | 0 | 3 | 519.7667 | 2022-12-01 16:13 | 2022-12-06 17:00 | 2022-12-05 17:14 | 2022-12-06 17:00 | 2022-12-27 09:00 |  |  | Chech operation of evap units AC 6&8 require new water pumps then unit needs test run to check float levelsall parts fitted, no water to units due to main water line isolated for other project on site.Site called to say water was reinstated and they had turned the evaps on and all are running now.
MSA-DTWD | WA5693053 | 2 | Australian Airconditioning Services Pty Ltd | F13 Textile Workshop - Split System isn’t running –Outdoor Unit was noisy before it failed-See notes | Air Conditioning | Ducted Split System | 6763.5 | Pass | Fail | 0 | 3 | 510.2833 | 2022-08-04 09:07 | 2022-08-09 17:00 | 2022-08-08 08:13 | 2022-08-09 17:00 | 2022-08-29 14:30 |  | WACCES | SUPPLY AND INSTALLED NEW 10KW DAIKIN INVERTER WALL MOUNTED SPLIT SYSTEM
MSA-DTWD | WA5413860 | 2 | Water2water Pty Ltd | Zip Boiler not heating in A111 | Plumbing & Drainage | HWS/Units Electric & Gas | 2236.925 | Pass | Fail | 0 | 3 | 510 | 2022-05-12 14:21 | 2022-05-17 17:00 | 2022-05-17 09:00 | 2022-05-17 17:00 | 2022-06-07 15:00 |  |  | Tried to fix, needs new unit.
MSA-DTWD | WA5987347 | 3 | AWB Co. | fire door jamming | Building | Fire Door | 3118.7675 | Pass | Fail | 0 | 3 | 510 | 2022-10-03 10:57 | 2022-10-10 17:00 | 2022-10-07 09:30 | 2022-10-10 17:00 | 2022-10-28 15:30 |  |  | works completedBRAF approval attached
MSA-DCA | WA5861261 | 0 | Protek 24/7 Building & Maintenance | Collection Block 10 - Significant leak with water gathering in ceiling - Please see notes | Roofing | Metal Roofing | 1929.96 | Pass | Fail | 0 | 3 | 509.25 | 2022-09-13 08:13 | 2022-09-13 10:13 | 2022-09-13 09:45 | 2022-09-13 12:13 | 2022-10-04 15:00 |  |  | ? Supply and Install 30x30mm compriband to step in roof construction? Seal open joints with sillicone
MSA-DTAG | WA6540837 | 3 | Australian HVAC Services Pty. Ltd. | 1903-ground-R111-air con to server room turns off intermittently | Air Conditioning | Room Air Conditioners |  | Pass | Fail | -1 | 2 | 508.75 | 2023-02-09 14:55 | 2023-02-16 17:00 | 2023-02-10 07:00 | 2023-02-16 17:00 | 2023-03-03 11:45
MSA-DTWD | WA5395039 | 2 | AWB Co. | Ground Floor - F Block - Room F1 - High lights in F1 not working correctly – See notes below | Electrical | Lighting, Internal | 1531.28 | Pass | Fail | -1 | 2 | 508.5 | 2022-05-05 10:28 | 2022-05-10 17:00 | 2022-05-05 13:30 | 2022-05-10 17:00 | 2022-05-26 18:00 |  | WACCES | Replace faulty highbay lights. Install new diffuerses and adjust hight for the lights- F block F1
MSA-DTAG | WA6464880 | 0 | Sapio Pty Ltd | Level 3 - Door L3 Staff Entry - Public Lift Lobby 2 Secure Area - Door locked/not opening (see notes | Security | Access Control | 451.92 | Pass | Fail | 0 | 3 | 508.4833 | 2023-01-17 11:30 | 2023-01-17 13:30 | 2023-01-17 11:31 | 2023-01-17 15:30 | 2023-02-07 16:00
MSA-DTAG | WA5186604 | 3 | Seme Solutions Pty Ltd | monitoring station communication check | Security | Monitoring | 455 | Pass | Fail | 0 | 3 | 508 | 2022-02-22 08:53 | 2022-03-01 17:00 | 2022-03-01 11:30 | 2022-03-01 17:00 | 2022-03-22 15:30 |  |  | Armed all areas and triggered zones through to Sapio Monitoring. Zones updated. Areas open/close and alarms confirmed by monitoring. Site is online and has been monitored since 4th of March by Sapio.
MSA-DTWD | WA5230942 | 3 | AWB Co. | G block -Rotunda - 8 x Fluoro lights at height faulty ballasts | Electrical | General Electrical | 3623.09 | Pass | Fail | -1 | 2 | 508 | 2022-03-15 08:51 | 2022-03-22 17:00 | 2022-03-17 11:30 | 2022-03-22 17:00 | 2022-04-07 15:30 |  |  | Attended site and signed in. Completed JSA, rescue plan and ewp check sheet. Located work area, set up danger tape and cones around area. Used ewp to access the light fittings above the tree. Supply and replaced 12x old fluro fittings with new led fittings. Tested all okay. Dispose of old light fittings. Clean and tidy site. Off hire ewp. Signed out. Job complete
MSA-DTWD | WA5115746 | 3 | Equans Mechanical Services Australia | Building 2 - Level 4 - All classrooms - Air in Chilled Water system - excessive noise | Air Conditioning | Room Air Conditioners | 734.06 | Pass | Fail | 0 | 3 | 507.75 | 2022-02-11 08:52 | 2022-02-18 17:00 | 2022-02-18 09:00 | 2022-02-18 17:00 | 2022-03-11 12:45 |  |  | Arrived on site and informed customer of works to be doneThere were no chillers in fault when I arrived. - Nor while there no chiller faulted.Ran both chillers up and reviewed operations. Carried out a running Data LogFound chiller 2 Ckt C was being held out to run by a Low Oil LevelReviewed alarm history, found a number of low oil pressure, low suction Temperature.Left chillers operational - for now...
MSA-DFES | WA5687329 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Driveway - driveway is flooded - See notes below | Plumbing & Drainage | Drainage | 592.79 | Fail | Fail | 9 | 12 | 507.75 | 2022-08-01 16:00 | 2022-08-04 17:00 | 2022-10-05 09:45 | 2022-08-04 17:00 | 2022-10-26 13:30 |  | WACCES | Installed new soakwell. Backfill and clean area
MSA-DTAG | WA6108912 | 1 | Sapio Pty Ltd | Two cameras are currently offline these are AD10 and AD12 PTZs | Security | Security Management System | 5599.63 | Pass | Fail | 0 | 3 | 507 | 2022-10-20 12:02 | 2022-10-21 17:00 | 2022-10-21 08:30 | 2022-10-21 17:00 | 2022-11-11 11:30 |  | WACCES | Installed replacement PTZ
MSA-DTWD | WA6535236 | 2 | AWB Co. | Repair power lighting issues | Electrical | Lighting, Internal | 1820.46 | Pass | Fail | 0 | 3 | 507 | 2023-02-06 16:19 | 2023-02-09 17:00 | 2023-02-08 09:45 | 2023-02-09 17:00 | 2023-03-01 12:45
MSA-DTWD | WA5112109 | 2 | AWB Co. | Level 1 - Outside Metal Workshop - Rectify uneven pavers | Building | General Building | 595 | Pass | Fail | 0 | 3 | 506.8667 | 2022-02-10 13:05 | 2022-02-15 17:00 | 2022-02-15 07:00 | 2022-02-15 17:00 | 2022-03-08 09:52 |  |  | paving works completed as per request
MSA-DTAG | WA6366016 | 1 | GPS Plumbing & Gas Services PtyLtd | ground-Effluent pump not working | Plumbing & Drainage | Drainage | 3958.035 | Pass | Fail | 0 | 3 | 506.8333 | 2022-12-13 14:05 | 2022-12-14 17:00 | 2022-12-14 07:00 | 2022-12-14 17:00 | 2023-01-04 09:50 |  | WACCES | Replaced and tested pump. Electrician connected to new pump to original box
MSA-DTAG | WA5151388 | 3 | Seme Solutions Pty Ltd | Alarm sensor 67 and 68 activates afterhours on a regular basis | Security | Monitoring | 260 | Fail | Fail | 1 | 4 | 506.75 | 2022-02-17 12:42 | 2022-02-24 17:00 | 2022-03-01 10:30 | 2022-02-24 17:00 | 2022-03-22 13:15 |  | WCAPPR | Replaced Duress button for office zone 85. Tested operation and checked with monitoring. All is in working order now.
MSA-DTWD | WA6540868 | 2 | Australian Airconditioning Services Pty Ltd | Split System AC on LHS not cooling properly - Unit located on roof will require 2 techs | Air Conditioning | Ducted Split System |  | Pass | Fail | 0 | 3 | 506.5833 | 2023-02-09 15:25 | 2023-02-14 17:00 | 2023-02-14 07:23 | 2023-02-14 17:00 | 2023-03-07 09:58 |  | WACCES
MSA-DTWD | WA5301876 | 3 | Falcetta Plumbing and Gas | Level 5 - plant room - hot water storage tank leaking | Plumbing & Drainage | Water | 5323.38 | Pass | Fail | -1 | 2 | 506.5 | 2022-04-01 13:50 | 2022-04-08 17:00 | 2022-04-01 15:30 | 2022-04-08 17:00 | 2022-04-22 18:00 |  | WACCES | replaced storage tank and lowered 2x old units to ground floor
MSA-DTAG | WA5325833 | 1 | Midolo Building Services | Hallway near Court 4/Room 215 - Level 1 - Significant water damage/crack in ceiling | Building | General Building | 1023.12 | Pass | Fail | 0 | 3 | 506.5 | 2022-04-14 12:56 | 2022-04-19 17:00 | 2022-04-19 07:30 | 2022-04-19 17:00 | 2022-05-10 10:00 |  | WACCES | CEILING REPAIRED
MSA-DCA | WA5499048 | 3 | GPS Plumbing & Gas Services PtyLtd | Conservation Labs -Leak, possibly from PVS piping | Plumbing & Drainage | Water | 878.94 | Pass | Fail | -1 | 2 | 506.0833 | 2022-06-10 09:38 | 2022-06-17 17:00 | 2022-06-13 10:30 | 2022-06-17 17:00 | 2022-07-04 12:35 |  | WCAPPR | Repaired stormwater pipes near the ceiling in upstairs .
MSA-DTWD | WA4993099 | 2 | Securex Security Systems & Services | G Block - Ground - Electronic entry door keypad - Code needs changing as number is compromised | Security | Keys & Access | 448.51 | Pass | Fail | 0 | 3 | 505.75 | 2022-01-07 09:25 | 2022-01-12 17:00 | 2022-01-11 10:15 | 2022-01-12 17:00 | 2022-02-01 12:00 |  |  | Ian Fouche (11/01/2022, 1015-1100) - Work NoteReplaced power supoly for rear lock as it died when pulling the reader Down.Ness s2 reader stand alone. Unknown master code and cannot default the system with out 2 ness EM swipe cards needto order from Ness.Ian Fouche (01/02/2022, 1030-1200) - Work NoteNone of 4 keypads would default. Rang tech support they think it could be faulty only 1 keypad was using the defaultmaster code. Apparently a company has changed the code before maybe they locked them out.
MSA-DFES | WA5454861 | 2 | Go Doors | Area 35 - Rear Yard - Touch pads for gate opening not working- see notes below | Building | Automatic Doors | 537.36 | Fail | Fail | 7 | 10 | 505.75 | 2022-05-17 15:21 | 2022-05-20 17:00 | 2022-07-05 09:00 | 2022-05-20 17:00 | 2022-07-26 10:45 |  |  | Attended site to complete Quote #29316 - Wireless Keypad. Included in the scope of quoted works, is thesupply and install of the following:A technician to attend site during business hoursDecommission existing keypadSupply and install wireless security keypadTest operationLeave site clean and tidy
MSA-DTWD | WA5693386 | 2 | M Construction (WA) | cafeteria next to dishwasher water leak from ceiling | Building | Ceiling | 525.35 | Pass | Fail | -1 | 2 | 505.7333 | 2022-08-04 11:54 | 2022-08-09 17:00 | 2022-08-05 14:00 | 2022-08-09 17:00 | 2022-08-26 15:44 |  |  | Attended site 5/8 and inspected roof space and found that re fridge lines are freezing over causing moisture in the ceiling.Returned to site 6/8 and found the cover was exposed and opens the ceiling with clear film tape edges. Reattended site 9/8 andscrewed up edge of sheets with plastic wrap and taped open area. Submitted BRAF to replace ceiling. Works Declined.
MSA-DTWD | WA6450299 | 3 | Techworks Plumbing | Anti-vandal basin tap leaking | Plumbing & Drainage | Water | 1506.95 | Pass | Fail | -1 | 2 | 505.7333 | 2023-01-16 10:44 | 2023-01-23 17:00 | 2023-01-19 08:30 | 2023-01-23 17:00 | 2023-02-09 10:14 |  | WACCES
MSA-DTWD | WA5193749 | 1 | Equans Mechanical Services Australia | 1 student lunch room - Aircon water dripping from it on to floor in student lunchroom | Air Conditioning | Room Air Conditioners | 479.24 | Pass | Fail | 0 | 3 | 505.5 | 2022-02-25 13:47 | 2022-02-28 17:00 | 2022-02-28 07:30 | 2022-02-28 17:00 | 2022-03-21 09:00 |  | WACCES | Found the drip tray cracked and leaking, silicones up and ordered a new tray . The silicone may help until the new tray arrives .
MSA-DTWD | WA5477356 | 2 | AWB Co. | L007 - FAULTY POWER TO ROLLER DOOR CONTROLLER | Electrical | General Electrical | 1014.67 | Pass | Fail | 0 | 3 | 505.25 | 2022-05-25 13:12 | 2022-05-30 17:00 | 2022-05-27 13:15 | 2022-05-30 17:00 | 2022-06-17 14:30 |  | WCAPPR | Attended site and signed in,completed jsa , spoke with fm about the job, isolated and disconnected old circuit, isolated dB and tested cables in board to determine which cables were in wall box next to door , found cables , I.r tested cable , cable all good, re wired circuit into existing circuit breaker, wired cable into control box, inspected contactor and neutral is required . Tested and used one of old cable to make a neutral, wired in neutral, re energised circuit and tested door, roller door company didn’t set limit switch correctly and will have to return to rectify, all controls working as intended , called fm and discussed the limit switch issue and he said to close job off, circuit isolated so no damage can be caused to roller door ,packed up, completed paperwork, signed out, ***job completed***
MSA-DCA | WA6298416 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Defence Gallery-Fault description Leak – possibly from mechanical pipe? AHU | Air Conditioning | Room Air Conditioners | 371.62 | Pass | Fail | 0 | 3 | 504.9167 | 2022-12-01 09:53 | 2022-12-02 17:00 | 2022-12-01 10:00 | 2022-12-02 17:00 | 2022-12-22 10:55 |  |  | Checked Heating water coil and found corroding coil is cause of leak. Subcontractor to attend site to quote replacement of coil on separate job Number.
MSA-DTWD | WA5686528 | 2 | Dormakaba Australia Pty Ltd | External (Tool shed) - Lock on Roller door needs to be replaced - See notes below | Building | Roller Shutters | 612.35 | Pass | Fail | 0 | 3 | 504.65 | 2022-08-01 09:07 | 2022-08-04 17:00 | 2022-08-02 08:21 | 2022-08-04 17:00 | 2022-08-23 09:00 |  |  | 2/8/22 - Inspection of door found doors lock is faulty requires replaceNote they don’t make this lock anymoreReturn visit to replace lock with a boss floor anchor lock as per pictureX1tech x2 hours23/8/22 - Installed new floor lock as required
MSA-DTAG | WA5226530 | 3 | Water2water Pty Ltd | Basement - Custody - Drink fountain in cell 2 has very low water pressure | Plumbing & Drainage | Water | 327.8925 | Pass | Fail | 0 | 3 | 504.5 | 2022-03-14 09:45 | 2022-03-21 17:00 | 2022-03-18 07:30 | 2022-03-21 17:00 | 2022-04-08 08:00 |  | WACCES & WCAPPR | Replaced plvall working okay
MSA-DTWD | WA5472123 | 2 | AWB Co. | Roof leaking above the pedestal grinders | Roofing | Metal Roofing | 746.68 | Pass | Fail | 0 | 3 | 504 | 2022-05-23 14:25 | 2022-05-26 17:00 | 2022-05-26 13:00 | 2022-05-26 17:00 | 2022-06-16 13:00 |  |  | Attended and located leak, required return. Sealed completely around base flashing to A/C and repaired rusted sump.May need replacement if issue persits.
MSA-DTAG | WA5257534 | 3 | Australian HVAC Services Pty. Ltd. | Basement - Storm water pump is continually running | Waste Management | Plant & Pumps | 1828.09 | Pass | Fail | -1 | 2 | 503.9167 | 2022-03-17 13:02 | 2022-03-24 17:00 | 2022-03-17 13:05 | 2022-03-24 17:00 | 2022-04-07 13:00 |  |  | Pick up pump from BPR. Attend site. Access Basement and install pump into position. Connect pipework and Electrical wiring. Fill pump with water for priming. Remove grate from carpark floor to access sump. Fill sump with water to test operation of pump. Found pump to start on float activation and pump out water. Found pump to stop on low level float. Replace grate and clean up area.
MSA-DTAG | WA6208265 | 2 | Sapio Pty Ltd | Court 2 - Green override button on JSO desk to open public entrance to court is not working | Security | Access Control | 416.73 | Fail | Fail | 0 | 3 | 503.5 | 2022-11-17 15:35 | 2022-11-22 17:00 | 2022-11-23 09:30 | 2022-11-22 17:00 | 2022-12-14 09:00 |  | WACCES | Replaced override button and tested for correct operation. Tested OK.
MSA-DTWD | WA5981807 | 3 | AWB Co. | 3D25 Staff room - Faulty PowerPoints | Electrical | General Electrical | 1211.795 | Pass | Fail | 0 | 3 | 503 | 2022-09-30 08:56 | 2022-10-07 17:00 | 2022-10-05 14:00 | 2022-10-07 17:00 | 2022-10-26 13:00 |  | WCAPPR | Attended site signed in jsa completed. ran new circuit from HV workshop db to 3D25 staff office. All tested and operational. safety cert completedJob completed
MSA-DTWD | WA5400591 | 2 | M Construction (WA) | Restaurant female toilets door vent broken | Building | Doors | 543.96 | Pass | Fail | 0 | 3 | 502.3333 | 2022-05-10 11:51 | 2022-05-13 17:00 | 2022-05-10 13:45 | 2022-05-13 17:00 | 2022-05-31 12:05 |  |  | Attend site find female toilet E Block. Ordered vent from supplier, attend site, collect materials from supplier, attend site, fit toilet door vent, remove rubbish. Job Complete.
MSA-DTWD | WA5472119 | 2 | AWB Co. | Roof leaking in the middle of the room | Roofing | Metal Roofing | 375 | Pass | Fail | 0 | 3 | 501.5 | 2022-05-23 14:22 | 2022-05-26 17:00 | 2022-05-26 12:30 | 2022-05-26 17:00 | 2022-06-16 10:00 |  |  | repairs to roof sheets completed as per request
MSA-DTWD | WA5407239 | 2 | ECO PLUMBING AND GAS PTY LTD | Leaking basin tap | Plumbing & Drainage | Water | 252.7 | Fail | Fail | 0 | 3 | 501.5 | 2022-05-11 10:41 | 2022-05-16 17:00 | 2022-05-19 16:30 | 2022-05-16 17:00 | 2022-06-09 14:00 |  |  | Repaired leaking tap
MSA-DTWD | WA5734527 | 2 | AWB Co. | All gutters, down pipes blocked | Roofing | Guttering | 714.195 | Pass | Fail | 0 | 3 | 501.25 | 2022-08-16 07:42 | 2022-08-18 17:00 | 2022-08-17 13:15 | 2022-08-18 17:00 | 2022-09-07 10:30 |  |  | Attended and investigated locations, returned and completed clean and flushed downpipes to areas as per signature slipattached.
MSA-DTAG | WA5490901 | 1 | Sapio Pty Ltd | Registry of Births, Deaths and Marriages - Level 10 - Comms room - please see details below | Security | CCTV Surveillance | 1910.97 | Pass | Fail | -1 | 2 | 501 | 2022-06-03 10:07 | 2022-06-07 17:00 | 2022-06-03 14:30 | 2022-06-07 17:00 | 2022-06-24 11:30 |  |  | Installed time server and sync Gallagher and Indigo to time server.
MSA-DTWD | WA5438239 | 2 | ECO PLUMBING AND GAS PTY LTD | has water on floor at base of toilet - possible leak in pipe | Plumbing & Drainage | Toilets/Cisterns | 316.79 | Pass | Fail | 0 | 3 | 500.75 | 2022-05-16 13:21 | 2022-05-19 17:00 | 2022-05-19 15:45 | 2022-05-19 17:00 | 2022-06-09 12:30 |  | WACCES | Replaced rubbers and sealed with putty
MSA-DTAG | WA5296692 | 1 | Sapio Pty Ltd | 565 Hay street - see below details | Security | CCTV Surveillance | 2828.91 | Pass | Fail | 0 | 3 | 500.7 | 2022-03-30 14:47 | 2022-03-31 17:00 | 2022-03-30 14:48 | 2022-03-31 17:00 | 2022-04-20 11:30 |  |  | Replaced cameras on SAT Level 03 and DMJC Level 09.
MSA-DTWD | WA5438230 | 2 | ECO PLUMBING AND GAS PTY LTD | One cubicle toilet not working | Plumbing & Drainage | Toilets/Cisterns | 812.3 | Pass | Fail | 0 | 3 | 500.5 | 2022-05-16 13:19 | 2022-05-19 17:00 | 2022-05-19 15:00 | 2022-05-19 17:00 | 2022-06-09 11:30 |  | WACCES | Replaced in wall cistern
MSA-DTWD | WA5693360 | 2 | Australian Airconditioning Services Pty Ltd | AC Condenser Unit for FG30 Lunchroom is leaking water all over the floor | Air Conditioning | Room Air Conditioners | 863.4 | Pass | Fail | -1 | 2 | 500.1531 | 2022-08-04 11:44 | 2022-08-09 17:00 | 2022-08-05 12:25 | 2022-08-09 17:00 | 2022-08-26 08:34 |  | WACCES | Checked unit and found when unit installed no drain for outdoor unit. Need to run a new drain for it. Returned to site and fitted new drain. Tested. All ok.
MSA-DTAG | WA5018137 | 1 | Seme Solutions Pty Ltd | Custody - Control Room -Security monitors have gone down. All 3 screens are blank. | Security | CCTV Surveillance | 260 | Pass | Fail | 0 | 3 | 500.05 | 2022-01-14 09:14 | 2022-01-17 17:00 | 2022-01-17 14:57 | 2022-01-17 17:00 | 2022-02-07 11:00 |  |  | Upon arrival ALL sirens were functioning. The security staff are all limited to 10 streams so we could meet consultant specifications of screen layout/CCTN Matrix's. Seme have allowed/adjusted their profiles to allow 14.
MSA-DTAG | WA5683053 | 0 | Sapio Pty Ltd | ground custody-Cameras on Poles 6 & 7 have dropped out | Security | CCTV Surveillance | 2934.75 | Pass | Fail | 0 | 3 | 500 | 2022-07-29 15:27 | 2022-07-29 17:27 | 2022-07-29 16:00 | 2022-07-29 19:27 | 2022-08-19 12:00 |  |  | Tested fibre link on Poles 6 & 7, found break at EC. Respliced fibre pigtails at cabinet and retested. Cameras are back on line. Job completed.
MSA-DFES | WA6389850 | 2 | Critical Fire Protection & Training | Pillar hydrant in rear yard is damaged and needs replacing. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 2784.2 | Pass | Fail | -1 | 2 | 500 | 2022-12-21 18:38 | 2022-12-28 17:00 | 2022-12-22 16:00 | 2022-12-28 17:00 | 2023-01-12 12:00 |  | WACCES | Site had driven off from the hydrant with the hose still attached.This has damaged the hydrant underground with repairs required.
MSA-DCA | WA5596733 | 2 | Dormakaba Australia Pty Ltd | Ground Floor Exterior - Auto Doors Murray St side - auto doors opening and not closing - See notes | Building | Automatic Doors | 625.41 | Pass | Fail | 0 | 3 | 499.55 | 2022-07-11 10:07 | 2022-07-14 17:00 | 2022-07-11 13:27 | 2022-07-14 17:00 | 2022-08-01 09:00 |  |  | 11/7/22 - Door was working correctly on arrival, tested all sensors, checked all fixings, checked board, checked door history, tested door in all modes number of times, no fault found, all working fine.Nobody onsite to sign paperwork.1/8/22 - Replaced push button and fitted new mounting bracket for button, tested al ok.Note-Nobody onsite to sign paperwork.
MSA-DCA | WA5565002 | 0 | Precise Air Group | Cooling towers is leaking chemicals | Air Conditioning | Cooling Tower | 2638.7 | Pass | Fail | 0 | 3 | 498 | 2022-06-21 13:11 | 2022-06-21 15:11 | 2022-06-21 14:00 | 2022-06-21 17:11 | 2022-07-12 08:00 |  |  | Attended site and located leak in plant room. Checked the towers and pumps for a leak. Appeared to be coming from dosing containers. Isolated and contacted hydroflow. Waited until they attended and handed over to hydroflow who remedied the issue.
MSA-DTWD | WA5312452 | 1 | AWB Co. | Cafeteria - damaged to the internal walls and damaged to the floor tiling | Building | Internal Walls | 557.56 | Pass | Fail | 0 | 3 | 497 | 2022-04-11 14:08 | 2022-04-12 17:00 | 2022-04-12 15:00 | 2022-04-12 17:00 | 2022-05-03 08:00 |  |  | Arrived on site and signed in was taken to the canteen and measured up the damage took some photos and a Sampleof tile.450mm up the wall2100mm long3 edge/ wall tilesSigned out left siteScraped plaster off wall and applied first coat of plasterScrapped back plaster then sealed the wall with bondcrete. Applied another base coat and a topcoat
MSA-DTAG | WA6249008 | 1 | Water2water Pty Ltd | Level 11-Repairs required - Billi Unit error message – Fault - Leak | Plumbing & Drainage | Water | 1179.85 | Pass | Fail | 0 | 3 | 486.9167 | 2022-11-21 09:12 | 2022-11-22 17:00 | 2022-11-22 10:05 | 2022-11-22 17:00 | 2022-12-12 17:00 |  |  | Replaced Hot tank. Checked and tested okay
MSA-DTWD | WA5109767 | 1 | CPB ELECTRICAL SERVICE | Convection oven - faulty filters - see notes | Equipment | Catering Equipment | 2476 | Pass | Fail | 0 | 3 | 486.5 | 2022-02-09 12:59 | 2022-02-10 17:00 | 2022-02-10 10:30 | 2022-02-10 17:00 | 2022-03-02 17:00 |  |  | Date - 10/2/22Make - Blue seal combi Technician - BMArrived at site liaise with reception, sign in, walk to location, identify faulty filter system, isolate remove panels tested and found the system was plumb up incorrectly swapped to correct position, reassemble all components and found small leaks coming from lots of places, recommend replacing all the blue tubing, the manifold has small leaks recommend replacing the manifold to stop future leaks, all the filters require replacement also well 2 year out of date, 1 x quad RO system, AX12 or AX10Would recommend replacing the whole filtration system due age and for reliability.2/3/22 BMArrived at site liaise with reception, identify faulty RO system, isolate remove faulty RO system supply and replace system reassemble all components and test all components for correct function all okay.
MSA-DTAG | WA5090747 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Public disabled toilet - Button has broken off so unable to flush | Plumbing & Drainage | Toilets/Cisterns | 1181.4425 | Pass | Fail | 0 | 3 | 485.9167 | 2022-01-25 16:01 | 2022-01-27 17:00 | 2022-01-27 10:35 | 2022-01-27 17:00 | 2022-02-16 16:30 |  |  | Completed
MSA-DTWD | WA6113485 | 2 | Equans Mechanical Services Australia | Airconditioning split not working properly | Air Conditioning | Ducted Split System | 4119.12 | Fail | Fail | 1 | 4 | 485.5 | 2022-10-24 11:59 | 2022-10-27 17:00 | 2022-11-01 09:30 | 2022-10-27 17:00 | 2022-11-21 15:00 |  | WACCES | Checked the ceiling cassette in the server room AG07 , found the compressor inefficient, quote to repair or replace being submitted.Picked up parts from suppliers. Carried tools and parts onto second floor roof. Reclaimed gas. Replaced the compressor, put onto VAC pump.Test run al ok. Removed all tools off roof and disposed of rubbish.
MSA-DTWD | WA6166420 | 2 | Precise Air Group | replace valve in D Block AHU plant room Level 4 Roof Top | Air Conditioning | Building HVAC Maintenance (Major Plant) | 801.88 | Fail | Fail | 1 | 4 | 485.5 | 2022-11-11 14:57 | 2022-11-16 17:00 | 2022-11-22 10:30 | 2022-11-16 17:00 | 2022-12-12 16:00 |  |  | Checked operation of purging relief valve found to be faulty ,wear and tear new valve is in process of being quoted Quote under 2k vallue part has been ordered eta 29th November Arrived on site and isolated water supply, drained water line, removed old valve, headed to suppliers and sourced new parts, headed to site and set up new valve, installed new valve and tighten all fittings, turned on water and flush system to make sure there are no air locks, checked for leaks, all as it should be with no further faults found
MSA-DFES | WA5715344 | 3 | Complete Pest Management Services | Ground Floor - Lawns - Rabbit infestation on site | Pest Control | General Pest | 3224.36 | Fail | Fail | 1 | 3 | 485 | 2022-08-12 13:50 | 2022-08-19 17:00 | 2022-08-23 13:30 | 2022-08-19 17:00 | 2022-09-12 18:30 |  |  | 23/08/22Located and fumigated 21 rabbit holes within an area of only 400m2.A brief survey of just the bushland along the east side of the Academy identified several large rabbit warrens withmultiple entry points.To locate and fumigate rabbit warrens in all areas will require 2 technicians for a minimum of one full day.Additionally many of the large old trees to the east and close to buildings have very active termite infestationscreating a high risk to buildings.12/09/2269 rabbit holes fumigated in surrounding bushland
MSA-DTWD | WA6257310 | 2 | COMMERCIAL PLUMBING AND GAS | First floor-male toilet-Faulty cistern in male toilet duct | Plumbing & Drainage | Toilets/Cisterns | 685.115 | Pass | Fail | -1 | 2 | 485 | 2022-11-24 14:03 | 2022-11-29 17:00 | 2022-11-25 12:00 | 2022-11-29 17:00 | 2022-12-15 17:00 |  |  | replaced urinal cistern
MSA-DTWD | WA5101346 | 1 | Equans Mechanical Services Australia | AC not working - Doesn’t appear to be blowing any air. Very hot and stuffy in classroom. | Air Conditioning | Room Air Conditioners | 2344 | Pass | Fail | 0 | 3 | 484.5 | 2022-02-03 11:18 | 2022-02-04 17:00 | 2022-02-04 08:30 | 2022-02-04 17:00 | 2022-02-24 13:00 |  |  | Compressor has failed and is bypassing. Awaiting pricing from suppliers to submit Braf
MSA-DFES | WA5478179 | 3 | Protek 24/7 Building & Maintenance | Ground Floor -Engine Room - Gym - damaged ceiling panels - see notes below | Roofing | Metal Roofing | 513.25 | Pass | Fail | 0 | 3 | 484.5 | 2022-05-26 09:58 | 2022-06-02 17:00 | 2022-06-02 11:30 | 2022-06-02 17:00 | 2022-06-22 16:00 |  |  | Replaced damaged ceiling tiles
MSA-DTWD | WA6178699 | 2 | AWB Co. | CG10 Workshop - Electrical Switch from test bench motor is broken | Electrical | General Electrical | 1916.58 | Pass | Fail | 0 | 3 | 484 | 2022-11-14 12:50 | 2022-11-17 17:00 | 2022-11-17 13:00 | 2022-11-17 17:00 | 2022-12-07 17:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Spoke to fm. Located motor/machine. Spoke to technician to confirm what he wanted and how he wanted it controlled. Left site to pick up parts from wholesaler. Returned to site. Started installation of new parts. Installed RCD and holder. Installed dol stop/start. Installed isolator. Installed junction box on motor. Install lead and plugtop. Installed earth bond. Installed emergency stop. Spoke with lecturer and had him move motor with forklift to suitable location for testing. Plugged into circuit and tested. Working as intended. Packed up and cleaned up. Completed paperwork. Signed out. Returned key to security guard. ***job complete***
MSA-DTWD | WA5133836 | 1 | Equans Mechanical Services Australia | E Block - Ground - E35 Walk in Cool room - Cool room running 8 degrees over set point | Refrigeration | Coolroom | 3209.79 | Pass | Fail | 0 | 3 | 483.55 | 2022-02-15 14:52 | 2022-02-16 17:00 | 2022-02-16 11:00 | 2022-02-16 17:00 | 2022-03-08 14:33 |  |  | Coolroom compressor has failed. Braf to be submitted to quote repairs. Picked up parts. Replaced compressor as per braf. Checked operation. All ok.
MSA-DCA | WA5861948 | 1 | Protek 24/7 Building & Maintenance | Basement - Stairwell 1, Pool Plant/Light Well - Door is water damaged and swelling - See notes below | Building | Doors | 401.61 | Pass | Fail | 0 | 3 | 483.5 | 2022-09-13 12:38 | 2022-09-14 17:00 | 2022-09-14 08:00 | 2022-09-14 17:00 | 2022-10-04 11:30 |  | WACCES | Remove old door seal and installed new
MSA-DFES | WA5992728 | 3 | AWB Co. | Officers Dorm 2 - magnet which holds the door open is not working | Building | Doors | 312.9475 | Pass | Fail | -1 | 2 | 483.5 | 2022-10-04 16:44 | 2022-10-11 17:00 | 2022-10-07 07:00 | 2022-10-11 17:00 | 2022-10-27 10:30 |  |  | Works completed
MSA-DFES | WA5319223 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Rear yard - Flood light is faulty | Electrical | Lighting, External | 542.38 | Pass | Fail | -1 | 2 | 483.25 | 2022-04-12 13:20 | 2022-04-21 17:00 | 2022-04-14 09:30 | 2022-04-21 17:00 | 2022-05-04 12:45 |  | WCAPPR | Arrived onsite at 11:15 to install 1 x floodlight to rear yard door. Installed and tested light and continued onsite at 12:45
MSA-DTWD | WA5753301 | 2 | AWB Co. | Printing Area - B Block - Ground Floor - Water Leaks coming through roof | Roofing | Metal Roofing | 1420.39 | Pass | Fail | -1 | 2 | 482.9667 | 2022-08-17 15:27 | 2022-08-22 17:00 | 2022-08-18 10:02 | 2022-08-22 17:00 | 2022-09-07 13:00 |  | WACCES | Traced multiple leaksPut in section of flashing over rusted frameCleaned out sump sealed out letSealed cracks in skylight need new one.Returned and installed new skylight.
MSA-DTWD | WA5323376 | 0 | ACTION GLASS & ALUMINIUM | A07B - x 2 broken windows | Building | Windows | 1922.55 | Fail | Fail | 0 | 3 | 482.5833 | 2022-04-13 07:34 | 2022-04-13 09:34 | 2022-04-13 09:49 | 2022-04-13 11:34 | 2022-05-03 12:24 |  |  | ATTENDED SITE PATCHED TO SECURE 2 BROKEN WINDOWS4MM CLEAR 2-1500 X 900 PLUS 6.5 SQM OF SAFETY FILM AND 2 TUBES OF SILICONERETURNED LATER DATE TO REGLAZE 6.38 CLEAR LAMINATED SAFETY GLASS1-1587 X 9451-1574 X 954PLUS 10 L/M OF RUBBER, 4 RIVETS & 7 SCREWS2 MEN REQUIRED
MSA-DTWD | WA6231139 | 2 | SCAVENGER SUPPLIES PTY LTD | Faulty PA speaker | Fire Protection Services | Fire Protection - Monitor System | 1032.33 | Pass | Fail | 0 | 3 | 482.5 | 2022-11-18 14:06 | 2022-11-23 17:00 | 2022-11-22 11:00 | 2022-11-23 17:00 | 2022-12-12 13:30 |  | WCAPPR | 22/11/2022-ATTENDED BW-RE ATTENDANCE SCHEDULED 12/12/22-NO ACCESS AS AREA BEING USED-KITCHENCOMPLETED 12/12/22-BW-AB
MSA-DTWD | WA6257304 | 3 | COMMERCIAL PLUMBING AND GAS | Faulty cistern in L/H Cubical | Plumbing & Drainage | Toilets/Cisterns | 196.4025 | Pass | Fail | -1 | 2 | 482.5 | 2022-11-24 13:57 | 2022-12-01 17:00 | 2022-11-25 12:30 | 2022-12-01 17:00 | 2022-12-15 15:00 |  |  | replaced button assembly mounting bracket
MSA-DCA | WA6372940 | 2 | GPS Plumbing & Gas Services PtyLtd | 2nd cubicle in Ladies Room BOH - Coroma push button needs replacing. | Plumbing & Drainage | Toilets/Cisterns | 289.1325 | Pass | Fail | 0 | 2 | 482.4333 | 2022-12-14 12:40 | 2022-12-19 17:00 | 2022-12-16 13:06 | 2022-12-19 17:00 | 2023-01-05 15:32 |  | WACCES | Replaced cistern button in ladies toilet
MSA-DTAG | WA5385738 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Various Locations - Covid Clean - see notes below | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 3 | 482.35 | 2022-04-29 12:03 | 2022-04-29 14:03 | 2022-05-03 09:57 | 2022-04-29 16:03 | 2022-05-23 12:18 |  |  | As per work order no# WA5385738
MSA-DCA | WA5479761 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 - Plant Room - Issues on AHU B1-01 and AHU 03-04 - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1370.01 | Fail | Fail | 5 | 8 | 482 | 2022-05-27 11:31 | 2022-05-30 17:00 | 2022-07-05 08:00 | 2022-05-30 17:00 | 2022-07-25 10:00 |  | WACCES | Met subcontractor on-site. Carried out replacement of expansion tank. Installed new drain pan. Restored water supply, all ok. Completed paperwork. Disposed of old tank and pan.
MSA-DTWD | WA4992361 | 1 | BJ SYSTEMS | T, U & V Blocks - BMS Security Systems - see notes below | Security | Access Control | 80 | Fail | Fail | 1 | 4 | 482 | 2022-01-06 10:46 | 2022-01-07 17:00 | 2022-01-14 08:15 | 2022-01-07 17:00 | 2022-02-03 10:15 |  |  | 14/01/2022 - Return as controllers offline in T, U & V Block03/02/2022 - Already attended site for same job on 03/02/2022. Job complete
MSA-DTAG | WA5038237 | 3 | Australian HVAC Services Pty. Ltd. | Ground - Room R111 - BMS monitor is not responding | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1017.44 | Pass | Fail | -1 | 2 | 482 | 2022-01-17 11:28 | 2022-01-24 17:00 | 2022-01-18 10:00 | 2022-01-24 17:00 | 2022-02-07 12:00 |  |  | Lasi controls attended site and picked up failed hard drive. Once new power pack and drive installed lasi returned to site and installed. Attend site and test operation of BMS. Found all working as normal.
MSA-DTWD | WA5993551 | 0 | Precise Air Group | 2 x fridges arent working | Refrigeration | Refrigerators | 208.34 | Fail | Fail | 0 | 3 | 481.8333 | 2022-10-05 11:02 | 2022-10-05 13:02 | 2022-10-05 13:34 | 2022-10-05 15:02 | 2022-10-25 15:24 |  |  | arrived on site and signed in, located cafeteria and located 2x domestic fridge and freezer, after investigation we found both top be short on refrigerant and it will be more cost-effective to just replace both units then to carry out any further investigation. spoke to Steve (fm) and he is going to order new equipment.
MSA-DCA | WA5390402 | 2 | Techworks Plumbing | Geology Building - Level 1 - Female toilet - Repair toilet seat to female toilet | Plumbing & Drainage | Toilets/Cisterns | 629.15 | Pass | Fail | 0 | 3 | 481.5 | 2022-05-02 12:34 | 2022-05-05 17:00 | 2022-05-03 13:30 | 2022-05-05 17:00 | 2022-05-23 15:00 |  | WACCES | Toilet seat cracked more then likely from incorrect use. Have ordered a replacement.
MSA-DTWD | WA5413354 | 2 | AWB Co. | Plumbing Section - Workshops roof water leak Plumbing section near Technicians office | Roofing | Metal Roofing | 437.29 | Pass | Fail | -1 | 2 | 481.5 | 2022-05-12 10:26 | 2022-05-17 17:00 | 2022-05-12 13:30 | 2022-05-17 17:00 | 2022-06-01 15:00 |  | WCAPPR | Attended and investigated, required return in dry weather repair. Checked beams and sealed flashings, completed as per signature slips.
MSA-DTWD | WA6522549 | 2 | Techworks Electrical | Workshops - Class Room 4 - Faulty under bench GPO, tagged out. | Electrical | Distribution Board | 422.34 | Pass | Fail | 0 | 2 | 481 | 2023-01-31 08:44 | 2023-02-03 17:00 | 2023-01-31 14:00 | 2023-02-03 17:00 | 2023-02-20 15:00 |  | WACCES
MSA-DFES | WA5325980 | 3 | Protek 24/7 Building & Maintenance | Relivers Block -Stations Officers Bathroom- Issues with shower glass - see notes | Building | Internal Screens | 440.61 | Pass | Fail | -1 | 2 | 481 | 2022-04-14 14:30 | 2022-04-26 17:00 | 2022-04-20 08:30 | 2022-04-26 17:00 | 2022-05-10 09:30 |  | WACCES | Replace Shower glass
MSA-DTWD | WA6111882 | 1 | WESTERN IRRIGATION PTY LTD | Water recycling shed-Fault description Circuit breaker tripped in water recycling shed - see notes | Landscaping & Gardening | Grounds Maintenance | 2486.8 | Pass | Fail | 0 | 2 | 480.75 | 2022-10-21 11:18 | 2022-10-24 17:00 | 2022-10-21 11:30 | 2022-10-24 17:00 | 2022-11-10 12:15 |  | WACCES | Replace failed sump pump
MSA-DTWD | WA5396604 | 1 | Techworks Plumbing | Block 10 - First floor male toilet - Cracked Toilet Bowl | Plumbing & Drainage | Toilets/Cisterns | 748.31 | Pass | Fail | 0 | 2 | 480.5 | 2022-05-06 10:20 | 2022-05-09 17:00 | 2022-05-06 11:00 | 2022-05-09 17:00 | 2022-05-26 11:30 |  | WACCES | Please see emails for full breakdown of work.
MSA-DCA | WA6145809 | 2 | ACTION GLASS & ALUMINIUM | Ground Level - Corporate Lounge - Cracked Window | Glazing | Window Glass | 1351.03 | Pass | Fail | -1 | 2 | 480.5 | 2022-11-02 15:22 | 2022-11-07 17:00 | 2022-11-03 09:30 | 2022-11-07 17:00 | 2022-11-23 10:00 |  |  | ATTENDED SITE MADE SAFE BROKEN PANEL WITH 1 SQM OF SAFETY FILMRETURNED LATER DATE WITH 2 MEN TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-827 X 1800 ARRIS EDGESRETURNED LATER DATE TO SUPPLY & FIT TINT FILMAS PER APPROVED BRAF1-827 X 1800
MSA-DTWD | WA5571264 | 3 | Protek 24/7 Building & Maintenance | Level 3 - Building 6 - B326 NW corner of room - Linoleum floor covering damaged | Flooring | Cork | 1025.9 | Pass | Fail | -1 | 2 | 480.25 | 2022-06-29 10:06 | 2022-07-06 17:00 | 2022-06-30 11:45 | 2022-07-06 17:00 | 2022-07-20 12:00 |  | WACCES | Patch existing vinyl
MSA-DFES | WA6255801 | 2 | Protek 24/7 Building & Maintenance | First Floor - Kids space area - A piece of ceiling plaster / paint has fallen - See Notes | Building | Ceiling | 1006.39 | Pass | Fail | 0 | 2 | 480.25 | 2022-11-23 13:57 | 2022-11-28 17:00 | 2022-11-25 09:45 | 2022-11-28 17:00 | 2022-12-15 10:00 |  | WACCES | ? Clean loose debris around the hole? Insert mesh back-block to provide support for fix? Apply epoxy bog into mesh and smooth the face to match metal ceiling tile? Sand flush and paint to match existing
MSA-DFES | WA5495804 | 3 | ACTION GLASS & ALUMINIUM | Ground - Office - Window is cracked - See notes below | Glazing | Window Glass | 1740.95 | Pass | Fail | -1 | 2 | 480.0833 | 2022-06-08 15:53 | 2022-06-15 17:00 | 2022-06-10 11:10 | 2022-06-15 17:00 | 2022-06-30 11:15 |  |  | ATTENDED SITEMADE SAFE BROKEN WINDOW PANEL WITH 1 SQM OF SAFETY FILMTINT FILM SUPPLIED & FIT IN FACTORYRETURNED LATER DATE WITH 2 MEN TO REGLAZE10.38 GREEN LAMINATED SAFETY GLASS1-842 X 1963POLISHED EDGESPLUS 5 L/M OF RUBBER REPLACED AND SILICONEAS PER APPROVED BRAF
MSA-DTWD | WA5413441 | 2 | AWB Co. | Electro Technology Workshops - Roof Leak | Roofing | Metal Roofing | 498.75 | Pass | Fail | -1 | 2 | 479.25 | 2022-05-12 11:13 | 2022-05-17 17:00 | 2022-05-12 14:15 | 2022-05-17 17:00 | 2022-06-01 13:30 |  | WCAPPR | Attended and was required to arrange return to seal in better weather. Returned and completed resealing of flashing as per signature slips attached.
MSA-DTWD | WA5584938 | 3 | AWB Co. | Replace lights not working Chemical Store A313-Special lights as Chemical Store | Electrical | Lighting, Internal | 352.385 | Pass | Fail | -1 | 2 | 479.25 | 2022-07-05 11:34 | 2022-07-12 17:00 | 2022-07-08 11:15 | 2022-07-12 17:00 | 2022-07-28 10:30 |  |  | Attended site signed in jsa completed. Replaced 8 tubes in chemical store. Had to wait to get in as was in use. All lights working nowJob completed
MSA-DTAG | WA5200208 | 3 | Australian HVAC Services Pty. Ltd. | Lvl 12 - Chambers 12.08 - Air con does not seem to be working, chambers quite warm | Air Conditioning | Room Air Conditioners | 428.31 | Pass | Fail | -1 | 2 | 479.15 | 2022-03-01 15:50 | 2022-03-09 17:00 | 2022-03-04 08:00 | 2022-03-09 17:00 | 2022-03-24 07:09 |  |  | Works complete temps ok
MSA-DTWD | WA5201209 | 3 | AWB Co. | Block A - meeting room level 2 - faulty TV brackets - site has new ones | Building | Internal Walls | 1503.065 | Pass | Fail | -1 | 2 | 479 | 2022-03-02 12:41 | 2022-03-10 17:00 | 2022-03-03 14:00 | 2022-03-10 17:00 | 2022-03-23 13:00 |  | WCAPPR | Attended site and signed in. Signed onto and reviewjsa. Spoke to Kim about job. Kim got IT guy to come meet us in lobby, went up to level 2 meeting room. Took packaging off Tv and mounted brackets into back. Sat Tv on wall bracket. Hooked in and made secure. Took picture of TV working. Contacted IT department and had them come up and confirm position, he wanted to put cables in the back of tv, took tv off of wall while he plugged in hdmi cables , re mounted tv, mounted bracket above tv for camera , mounted camera to bracket , cleaned up work area , took old tv box and rest of rubbish to skip , packed up, completed paperwork , signed out ***job completed***
MSA-DCA | WA5836588 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - Heath Ledger Dock - Smell coming from AC Pipe | Air Conditioning | Room Air Conditioners | 833.67 | Pass | Fail | 0 | 3 | 478.9167 | 2022-09-07 12:56 | 2022-09-08 17:00 | 2022-09-07 14:30 | 2022-09-08 17:00 | 2022-09-27 13:25 |  |  | Completed
MSA-DTAG | WA5995755 | 2 | GPS Plumbing & Gas Services PtyLtd | Location of potential leak is unkown -The water usage account has increased by 67KL in 64 days. | Plumbing & Drainage | Water | 1439.795 | Pass | Fail | 0 | 2 | 478.65 | 2022-10-06 16:18 | 2022-10-11 17:00 | 2022-10-08 11:00 | 2022-10-11 17:00 | 2022-10-28 09:39 |  | WCAPPR | Inspected water meter onsite, currently using 1.5L when no one onsite, we inspected all water fixtures within site and found 4 leaking cisterns, we replaced outlet washer & inlet valves to those cisterns. Advised by Iain to then close of work order
MSA-DFES | WA5307459 | 2 | Protek 24/7 Building & Maintenance | Female Toilet Block - Reception - see details | Building | General Building | 482.71 | Pass | Fail | -1 | 2 | 478.5 | 2022-04-07 13:32 | 2022-04-12 17:00 | 2022-04-08 13:30 | 2022-04-12 17:00 | 2022-04-28 12:00 |  | WACCES | Replace paper towel holder
MSA-DTWD | WA5100463 | 3 | Water2water Pty Ltd | Billi unit not working | Plumbing & Drainage | Water | 1540.36 | Pass | Fail | 0 | 3 | 478.25 | 2022-02-02 13:59 | 2022-02-09 17:00 | 2022-02-08 14:20 | 2022-02-09 17:00 | 2022-02-28 12:35 |  |  | Needs hot pump cold pump filter and zip fittings kit for startersWould not recommend repairs due to age 15 years oldInstalled new capex assets Maxiflow Filter System + IC8 Undersink Chiller + Dual Faucet A401850485 removed old to tip. Manufacturers SN 21060282
MSA-DTAG | WA6383429 | 2 | Gilmour & Jooste Electrical | Ground - Ground - Roller Door - Door not working properly - See Notes Below | Building | Doors | 488.39 | Fail | Fail | 1 | 4 | 478.25 | 2022-12-20 10:20 | 2022-12-23 17:00 | 2022-12-28 12:00 | 2022-12-23 17:00 | 2023-01-17 10:15 |  | WACCES | Investigated fault to faulty door. Met sapio on site to fault find. Found loose connection in control box. Re terminated cable. Checked and tested, all in working order.
MSA-DTWD | WA6529165 | 2 | Precise Air Group | air con not working controller blank | Air Conditioning | Room Air Conditioners | 810.805 | Pass | Fail | -1 | 2 | 477.9 | 2023-02-02 16:20 | 2023-02-07 17:00 | 2023-02-03 09:30 | 2023-02-07 17:00 | 2023-02-23 07:24
MSA-DTWD | WA5570180 | 2 | AHS Services WA Pty Ltd (Anchor) | W101 Female toilet - Toilet not flushing partially blocking | Plumbing & Drainage | Toilets/Cisterns | 651.76 | Pass | Fail | 0 | 3 | 477.5333 | 2022-06-28 07:59 | 2022-06-30 17:00 | 2022-06-28 09:30 | 2022-06-30 17:00 | 2022-07-18 07:02 |  |  | Job completed
MSA-DTWD | WA6257950 | 3 | Techworks Electrical | Damaged Lights | Electrical | Lighting, Internal | 1017.22 | Pass | Fail | -1 | 2 | 477.5 | 2022-11-25 09:16 | 2022-12-02 17:00 | 2022-11-25 11:00 | 2022-12-02 17:00 | 2022-12-15 08:30 |  |  | Replaced lights in p block waiting on light fitting from wholesaler for broken light in hallway Led Panels x 2 + 1 frame.6x 36w 840 tubes6x S10 starters
MSA-DTWD | WA6291075 | 2 | Equans Mechanical Services Australia | Roof above room B7 - Hole in roof under vent - Mechanical Fan - (see pics attached) | Equipment | Electrical Equipment | 787.59 | Pass | Fail | 0 | 3 | 476.5 | 2022-11-28 12:12 | 2022-12-01 17:00 | 2022-12-01 14:00 | 2022-12-01 17:00 | 2022-12-21 10:30 |  | WACCES | Accessed the roof checked the fresh air vent cover has broken, checking availability with vendor. 19/22/22: Picked up parts from the suppliers 21/12/22: Accessed the roof working at heights replaced the cover .
MSA-DCA | WA5973890 | 0 | ACTION GLASS & ALUMINIUM | Shop 5 - Broken glass door window | Glazing | Door Glass | 672.38 | Pass | Fail | 0 | 3 | 474.8333 | 2022-09-22 15:12 | 2022-09-22 17:12 | 2022-09-22 16:10 | 2022-09-22 19:12 | 2022-10-12 11:00 |  |  | ATTENDED SITE AFTER HOURSREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-862 X 460RETURNED LATER DATE TO SUPPLY & FITSIGNAGE & FROST FILM AS PER APPROVED BRAF
MSA-DTAG | WA5460559 | 0 | Dormakaba Australia Pty Ltd | Magistrates Carpark Roller doors - have come down on a car with door closed ,car has been moved | Building | Automatic Doors | 538.9 | Pass | Fail | 0 | 3 | 473.1 | 2022-05-18 15:23 | 2022-05-18 17:23 | 2022-05-18 17:00 | 2022-05-18 19:23 | 2022-06-07 10:06 |  |  | 18/5/22 - Door had come down on top of car causing the door to come out of its guides, repositioned door back into place, door can only be opened half way on controls due to lost limits,door requires 10 new 3 pin slat clips, Dormakaba electrician to reset limits and assess safety beams, ip 10917517/6/22 - Arrived on site and found the door requires 6 new slats. These are 5030mm night sky (black).
MSA-DCA | WA5038526 | 0 | Dormakaba Australia Pty Ltd | RETROSPECTIVE WORK ORDER - Roller door at the docks has come off its tracks. | Building | Doors | 3171.8 | Pass | Fail | 0 | 3 | 469.1667 | 2022-01-12 22:00 | 2022-01-13 | 2022-01-12 22:00 | 2022-01-13 02:00 | 2022-02-01 11:10 | 1 |  | 12/12/21 - The door was out of its guides. Got a second man to get the door down and secure. The door is operating correctly but will require a revisit to replace broken clips and do a proper assessment.13/12/21 - Assessed shutter, lifting equipment cut out unable to go full height due to slope, upon assessment found 7 x slats damaged and unable fix new clips due damaged end of slats RHS V.I.L.O, also requires new key switch control box due to exposed buttons, ( refer to images) slat length 5140.lifting device with outriggers required to repair door1/2/22 - Repair damaged Curtin and test door job is complete , door tested and working well
MSA-DTWD | WA6257194 | 3 | Equans Mechanical Services Australia | Room N320/321 - Room temps too high can't be controlled by set points | Air Conditioning | Room Air Conditioners | 940.32 | Fail | Fail | 4 | 7 | 463 | 2022-11-24 12:46 | 2022-12-01 17:00 | 2022-12-28 08:00 | 2022-12-01 17:00 | 2023-01-16 15:00 |  |  | Attend site, Sign in and complete take.Checked BMS no faults, VAV's not making SA flow setpoint. Checked AHU pressure setpoint and VSD speed-ok.Inspected VAV's and ductwork for air leaks - ok.Inspected VAV pedo tube's -okAHU is a max speed and working as hard as it can.Will monitior.Completed paperwork.
MSA-DTWD | WA5567161 | 3 | AWB Co. | 3B4 - 10 Faulty lights | Electrical | Lighting, Internal | 1520.32 | Pass | Fail | 0 | 3 | 462.8667 | 2022-06-23 15:53 | 2022-06-30 17:00 | 2022-06-30 08:38 | 2022-06-30 17:00 | 2022-07-19 15:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located classroom and isolated lighting, removed old light fittings and replaced with new, removed light fitting behind a/c and blanked off , tested lights and all working as intended, disposed of lights , completed paperwork, packed up, signed out **job completed**
MSA-DTWD | WA5596683 | 0 | Techworks Plumbing | Hot water system leaking water - see notes | Plumbing & Drainage | HWS/Units Electric & Gas | 5158.55 | Pass | Fail | 0 | 3 | 461.5 | 2022-07-11 09:50 | 2022-07-11 11:50 | 2022-07-11 11:00 | 2022-07-11 13:50 | 2022-07-30 16:30 |  | WACCES | Removed excisting hwu and re installed new 315 litre hwu
MSA-DCA | WA5306327 | 1 | Techworks Electrical | External pole floodlight - Cover to pole floodlight is missing. | Electrical | Lighting, External | 995.6 | Pass | Fail | 0 | 3 | 461.5 | 2022-04-06 12:20 | 2022-04-07 17:00 | 2022-04-07 07:00 | 2022-04-07 17:00 | 2022-04-26 12:30 |  | WCAPPR | Picked up trailer mounted EWP and drove to site, set up EWP below light and created exclusion zone, replaced damaged light for new led flood light, packed up materials and EWP once job completed.
MSA-DFES | WA5546504 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - External near work shop - road drain (two connected) is full and overflows when it rains | Plumbing & Drainage | Drainage | 832.9 | Pass | Fail | 0 | 3 | 461.5 | 2022-06-17 07:03 | 2022-06-23 17:00 | 2022-06-22 07:20 | 2022-06-23 17:00 | 2022-07-11 12:50 |  |  | Soakwall near work shop they are full of water and need to be clean ou. Need to raise job.Arrived on site and singed in went to soakwall near work shop and sucked them out with a pump once the water had cleared cold see a lot of sludge in the bottom and noticed they're not soakwall problems needs to be fixed with a pump or redesigned 11/07/22.
MSA-DTWD | WA5976795 | 2 | AWB Co. | Client services office - light tubes not working | Electrical | Lighting, Internal | 820.4475 | Pass | Fail | 0 | 3 | 461.25 | 2022-09-27 11:29 | 2022-09-30 17:00 | 2022-09-29 10:15 | 2022-09-30 17:00 | 2022-10-18 15:30 |  | WACCES | Attended site and signed in, completed JSA,spoke with fm about job, isolated lighting circuits and removed old fittings, cut old lights to suit new fittings , retro fitted new fittings in enclosures, re mounted in ceiling and tested lights, working as intended, cleaned up, packed up, completed paperwork,signed out, job complete
MSA-DTWD | WA6523267 | 2 | AWB Co. | Lights out in various locations on library floor area -see notes | Electrical | Lighting, Internal | 2550.59 | Pass | Fail | 0 | 3 | 461.25 | 2023-01-31 13:54 | 2023-02-03 17:00 | 2023-02-03 08:30 | 2023-02-03 17:00 | 2023-02-22 13:45 |  | WCAPPR
MSA-DTWD | WA5289377 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Frances Street entrance - Rectify Faulty security cameras | Electrical | General Electrical | 1071.035 | Pass | Fail | 0 | 3 | 460.75 | 2022-03-24 08:56 | 2022-03-31 17:00 | 2022-03-31 11:00 | 2022-03-31 17:00 | 2022-04-19 15:45 |  | WACCES | Arrived on site at 11:07. To investigate security cameras not working, located the 2 effected cameras and removed them for bench testing. Left site to collect data tester from Welshpool. Arrived back on site and tested cable found fault on one of cameras, re-terminated both ends of cable and tested all okay. Will need to return to site to install cameras. Left site at 14:30
MSA-DTAG | WA5038239 | 3 | Dom's Total Grounds Maintenance | Courtside - All areas - Grounds - The reticulation appears to not be working - see details | Landscaping & Gardening | Grounds Maintenance | 2148 | Fail | Fail | 3 | 6 | 460.5 | 2022-01-17 11:22 | 2022-01-24 17:00 | 2022-02-17 07:00 | 2022-01-24 17:00 | 2022-03-08 11:30 |  |  | Dom inspected retic. BRAF was raised.Retic Contractor required.
MSA-DTWD | WA6361549 | 3 | AWB Co. | 3x glass doors not closing properly - dropping/rubbing on floors | Building | Doors | 1292.7675 | Fail | Fail | 0 | 3 | 460.5 | 2022-12-08 10:43 | 2022-12-15 17:00 | 2022-12-16 10:15 | 2022-12-15 17:00 | 2023-01-04 14:45 |  |  | Works completed
MSA-DTWD | WA5497029 | 2 | AWB Co. | AT Block - Main Foyer -Various lights inoperative - contact Facilities on arrival | Electrical | Lighting, Internal | 2729.5725 | Pass | Fail | -1 | 2 | 460.25 | 2022-06-09 13:49 | 2022-06-14 17:00 | 2022-06-10 07:30 | 2022-06-14 17:00 | 2022-06-29 11:45 |  |  | Attended site and signed in. Completed JSA. Went through and replaced 4x old lights with 4x new LED studio fittings. Replaced 3x lamp plus control gear on wall up lights. Replaced 1x electronic ballast. Tested to make sure working. Cleaned up site. **job complete**
MSA-DTWD | WA5189669 | 1 | Dormakaba Australia Pty Ltd | Level 2 - Main Entry door - Auto door faulty - not opening or closing | Building | Automatic Doors | 5289.87 | Pass | Fail | 0 | 3 | 459.7667 | 2022-02-24 07:41 | 2022-02-24 17:00 | 2022-02-24 09:10 | 2022-02-24 17:00 | 2022-03-15 12:56 |  |  | 24/2/22 - On inspection, unit in total failure of equipment due to aged equipment (more than 20 years old) see attached photos, adjusted settings and re terminated cables. Unable to temporarily fix unit.As recommended and agreed with David (management), turned unit off until further works have been quoted and accepted.Please quote es200 locking kit with 2x ixio sensors 1x standard floor guide 1 length track and 2x track wheels.15/3/22 - Removed existing faulty door equipment and replaced with new es200 locking upgrade kit, 2x track wheels, 1x length of track and 2x ixio sensors, setup and tested operation upon completion and left in good working order.
MSA-DTWD | WA4995443 | 3 | Water2water Pty Ltd | S105 Passage - Fountain in passage water has black particles | Plumbing & Drainage | Water | 2104.6275 | Pass | Fail | -1 | 2 | 459.0833 | 2022-01-10 13:01 | 2022-01-17 17:00 | 2022-01-12 10:50 | 2022-01-17 17:00 | 2022-01-31 13:55 |  |  | Unable to clear particles in water. Tank corroded and in general poor condition. Fountain requires replacing. Isolated water and ‘tagged off’ fountain. Replaced fountain and fitted a filter. Still no power at GPO, reported to site contact Steve bInstalled new maxiflow filter system A40421697M + Zip Sitemaster fountain A40421696L manufacturers serial number 2022011702006 - removed old to tip
MSA-DTWD | WA5569477 | 3 | AHS Services WA Pty Ltd (Anchor) | Middle Tap needs replacing Green Skills Male toilet | Plumbing & Drainage | Water | 496.475 | Pass | Fail | -1 | 2 | 459 | 2022-06-27 15:01 | 2022-07-04 17:00 | 2022-06-30 09:30 | 2022-07-04 17:00 | 2022-07-19 12:30 |  |  | Replaced faulty basin tap , required product to be ordered in.
MSA-DTAG | WA5101203 | 1 | Midolo Building Services | Old Court House - Front doors are damaged – cracked appears someone has kicked the doors | Building | Doors | 874.93 | Pass | Fail | 0 | 3 | 458.75 | 2022-02-03 10:39 | 2022-02-04 17:00 | 2022-02-03 11:45 | 2022-02-04 17:00 | 2022-02-22 14:30 |  | WACCES & WCAPPR | cracks repaired & doors re-painted
MSA-DTWD | WA5478921 | 1 | ACTION GLASS & ALUMINIUM | Block C - External Windows damaged - See notes below | Building | Windows | 1509.6 | Pass | Fail | 0 | 3 | 458.25 | 2022-05-26 14:56 | 2022-05-27 17:00 | 2022-05-27 10:30 | 2022-05-27 17:00 | 2022-06-15 12:45 |  |  | ATTENDED SITEPATCHED TO MAKE SAFE BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS 1-660 X 460PLUS BLACK SILICONE AND .5 SQM OF SAFETY FILMRETURNED LATER DATE TO REGLAZE5MM SPOTSWOOD TOUGHENED SAFETY GLASS 1-780 X 505PLUS 8 NAILS AND 1.2 L/M OF PUTTYALSO SUPPLIED & INSTALLED 2 NEW STAINLESS STEEL SECURITY SCREENS2-950 X 730
MSA-MRWA | WA6534377 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Asphalt lab - AC 1not working - requires constant resetting | Air Conditioning | Room Air Conditioners | 202.705 | Pass | Fail | 0 | 3 | 458.1167 | 2023-02-06 11:55 | 2023-02-09 17:00 | 2023-02-08 07:30 | 2023-02-09 17:00 | 2023-02-27 09:37
MSA-DFES | WA5504195 | 1 | Go Doors | front electric gate is broken error msg motor fault and drive fault | Building | Doors | 2646.58 | Pass | Fail | 0 | 2 | 458 | 2022-06-11 13:43 | 2022-06-13 17:00 | 2022-06-11 14:30 | 2022-06-13 17:00 | 2022-06-30 16:30 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5692212 | 1 | Protek 24/7 Building & Maintenance | Window in gallery needs re sealing, water and debris coming in through window. | Building | Windows | 951.17 | Pass | Fail | 0 | 3 | 457.75 | 2022-08-03 11:23 | 2022-08-04 17:00 | 2022-08-04 08:30 | 2022-08-04 17:00 | 2022-08-23 10:15 |  |  | cut away old silicon install new
MSA-DCA | WA5108511 | 2 | Techworks Plumbing | Hackett Hall - ground - male toilet - small hole to toilet pan bowl see notes | Plumbing & Drainage | Water | 1773.3 | Pass | Fail | 0 | 2 | 457.5 | 2022-02-08 14:57 | 2022-02-11 17:00 | 2022-02-09 07:00 | 2022-02-11 17:00 | 2022-02-28 08:30 |  | WACCES | Attended site and signed in at security deskLocated broken toilet, called reece for a new one and there is none in the state. Called Neil to see if he wanted to wait for the same pan or get a different one. He was happy to wait and leave toilet locked off. Informed Neil that I will remove broken pan from site and plug waste to stop smell so we can return to site and install new pan when it arrives. Have ordered the new pan to the yard thru reece Osborne Park. Cleaned site,Completed paper work,Completed work
MSA-DFES | WA6014158 | 2 | AWB Co. | Engine room into station door soft closer leaver is broken - see notes | Building | Doors | 447.885 | Pass | Fail | 0 | 3 | 457 | 2022-10-12 06:49 | 2022-10-14 17:00 | 2022-10-14 14:30 | 2022-10-14 17:00 | 2022-11-02 15:30 |  |  | Works completed
MSA-DTAG | WA5675698 | 3 | Bullant Security Pty Ltd | Group - Room 109 - Broken lock on door | Security | Locksmith | 311.18 | Pass | Fail | 0 | 2 | 456.5 | 2022-07-22 13:01 | 2022-07-29 17:00 | 2022-07-27 09:00 | 2022-07-29 17:00 | 2022-08-15 09:30 |  |  | Attended site, viewed and require a longer spindle to complete job.Date on site: 27/7/2022Time on site: 09:00 - 09:30Attended site, supplied and fitted new extended spindle for clients lockwood dx on door for room 109.Date on site: 15/8/2022Time on site: 09:00 - 09:30
MSA-DFES | WA6404760 | 3 | ACTION GLASS & ALUMINIUM | Ground - Rear gate - Domed mirror damaged - see notes | Glazing | Mirrors | 399.705 | Pass | Fail | -1 | 2 | 456.25 | 2023-01-09 08:44 | 2023-01-16 17:00 | 2023-01-11 12:15 | 2023-01-16 17:00 | 2023-01-30 12:30
MSA-DCA | WA5413567 | 2 | Techworks Electrical | Staircase - Lights on stairs are out - Fittings are old suggest replace with LED | Electrical | General Electrical | 2051.65 | Pass | Fail | -1 | 2 | 456 | 2022-05-12 12:02 | 2022-05-17 17:00 | 2022-05-12 14:00 | 2022-05-17 17:00 | 2022-05-31 14:00 |  | WACCES | Replaced 5x downlights with new LED ones using a scaffold.
MSA-DTWD | WA6088560 | 3 | Critical Fire Protection & Training | Aroma Cafe - 2x faulty EWIS speakers in Aroma Cafe | Fire Protection Services | Fire Protection - Monitor System | 208.26 | Pass | Fail | -1 | 2 | 456 | 2022-10-19 09:20 | 2022-10-26 17:00 | 2022-10-19 14:00 | 2022-10-26 17:00 | 2022-11-07 14:00 |  | WACCES | Supplied and installed 2x new speakers
MSA-DCA | WA6251137 | 2 | Critical Fire Protection & Training | Main Reception FIP - No signal from GFA, reported when testing | Fire Protection Services | Fire Protection - Monitor System | 583 | Pass | Fail | 0 | 3 | 456 | 2022-11-22 09:25 | 2022-11-25 17:00 | 2022-11-25 12:00 | 2022-11-25 17:00 | 2022-12-14 12:00 |  | WACCES | History:Issue with the fire relay 3 alarms a few weeks back and advised site it was responsibility of the mech side.Whilst they were onsite carrying out works to the AMPAC fire controller that had faulty outputs, they noticed while testing,the GFA (General Fire Alarm) output module activated but no signals received in the MSSB.They were unsure if the GFA has been bypassed for shutdowns to apply in effected zones only.Please investigate this issue.Attended 25th of November carried out checks of system and mech board- recommend download fire system config toanalyze fire system program / mech interface- to advise CFAttend site 14th of December provided site with config copy, carried out checks of configuration 59+ dedicated functions on program with various input output field devices.email sent for further review.
MSA-DTWD | WA5693088 | 3 | Protek 24/7 Building & Maintenance | E1 E2 & E3 - Determine Type of mould visible on ceilings - See notes below | Building | Ceiling | 871.27 | Pass | Fail | -1 | 2 | 455.75 | 2022-08-04 09:26 | 2022-08-11 17:00 | 2022-08-04 12:00 | 2022-08-11 17:00 | 2022-08-23 11:45 |  | WACCES | Determine type of Mould on ceilings
MSA-DFES | WA5478170 | 3 | Protek 24/7 Building & Maintenance | Main Admin - Staff Change rooms - damaged ceiling panels - see notes below | Roofing | Metal Roofing | 962.5 | Pass | Fail | 0 | 3 | 455.5 | 2022-05-26 09:50 | 2022-06-02 17:00 | 2022-06-02 09:00 | 2022-06-02 17:00 | 2022-06-21 08:30 |  | WACCES | replace water damaged ceiling tiles
MSA-DTWD | WA5216748 | 2 | M Construction (WA) | T-Block room T108 has broken privacy curtains | Building | Curtains & Blinds | 556 | Fail | Fail | 0 | 3 | 455.5 | 2022-03-11 12:31 | 2022-03-16 17:00 | 2022-03-17 14:30 | 2022-03-16 17:00 | 2022-04-05 14:00 |  |  | Replaced 4 broken privacy curtains.
MSA-DTWD | WA6145842 | 1 | Equans Mechanical Services Australia | Supply temporary portable air conditioner to cool server room while repairs are being carried out | Air Conditioning | Room Air Conditioners | 908.42 | Pass | Fail | 0 | 3 | 455.1667 | 2022-11-02 16:31 | 2022-11-03 17:00 | 2022-11-03 12:50 | 2022-11-03 17:00 | 2022-11-22 12:00 |  |  | SUPPLY AND COLLECTION OF PORTABLE UNITS
MSA-DTWD | WA5750048 | 3 | Protek 24/7 Building & Maintenance | 3E13 classroom - Mold on ceiling panels from water leak | Building | Ceiling | 1227.875 | Pass | Fail | -1 | 2 | 454.75 | 2022-08-17 09:31 | 2022-08-24 17:00 | 2022-08-17 14:30 | 2022-08-24 17:00 | 2022-09-05 13:15 |  |  | Removed and replaced 4 x water damaged mineral fibre ceiling tiles in classroom
MSA-DTWD | WA5010105 | 1 | Techworks Electrical | E-Block - lights not working in hallway, sk1, sk2 and store room and directors office | Electrical | Lighting, Internal | 1308.21 | Pass | Fail | 0 | 3 | 454.5 | 2022-01-12 10:13 | 2022-01-13 17:00 | 2022-01-12 16:00 | 2022-01-13 17:00 | 2022-01-31 14:30 |  | WACCES | Replaced failed tubes in E block.Waiting on parts as no stock in Perth.Parts arrived. Replaced remaining light fittings.
MSA-DTWD | WA5692029 | 2 | Australian Airconditioning Services Pty Ltd | ET04 -AC Unit on heat but only blows cold air | Air Conditioning | Room Air Conditioners | 865.1 | Pass | Fail | 0 | 2 | 454.5 | 2022-08-03 09:47 | 2022-08-08 17:00 | 2022-08-05 11:00 | 2022-08-08 17:00 | 2022-08-24 09:30 |  | WACCES | Checked unit and found wall controller faulty and needs replacing. Returned to site and replaced faulty controller. Ran and tested. All ok
MSA-DFES | WA5289480 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Main Office - lights in back of the office are not working | Electrical | General Electrical | 234.66 | Pass | Fail | 0 | 3 | 453.5 | 2022-03-24 09:50 | 2022-03-25 17:00 | 2022-03-25 12:45 | 2022-03-25 17:00 | 2022-04-13 10:15 |  | WACCES | Attend site 1245, proceed to investigate lights not working at back of office. Tubes found to be faulty and in need of replacement. Local supplier does not stock so will need to acquire tubes first before returning to site. Left site at 1315.
MSA-DTWD | WA5548747 | 3 | AWB Co. | N28 - 4 x lights out | Electrical | General Electrical | 990.4675 | Pass | Fail | 0 | 2 | 453.25 | 2022-06-17 09:16 | 2022-06-24 17:00 | 2022-06-22 13:00 | 2022-06-24 17:00 | 2022-07-11 10:15 |  | WACCES | Attended site and signed in,completed jsa,spoke with fm about job,went to n block and isolated lighting , removed old lights and replaced with new, re energised circuit and tested lights, working as 8ntend3d, disposed of old fittings in bin located on site , cleaned up, packed up, completed paperwork, signed out **job completed**
MSA-DFES | WA5796335 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Faulty Lighting - Multiple locations - see notes below | Electrical | General Electrical | 999.01 | Pass | Fail | 0 | 3 | 452.5 | 2022-08-26 10:25 | 2022-08-31 17:00 | 2022-08-31 15:00 | 2022-08-31 17:00 | 2022-09-19 11:30 |  |  | Arrived onsite, signed in.Replaced 36w batten lights with new LED weatherproof lights, performed function test.Replaced sensor on outside of outside amenities block at back of station performed function test.Informed site of completed works and continued onto next job onsite.
MSA-DTWD | WA5207651 | 2 | Milners Tree Solutions Pty Ltd | Garden area NW of cafeteria - Fault description A tree has split at its base and in need of removal | Landscaping & Gardening | Tree Lopping |  | Pass | Fail | 0 | 3 | 451.9 | 2022-03-08 15:11 | 2022-03-11 17:00 | 2022-03-10 12:10 | 2022-03-11 17:00 | 2022-03-29 08:04 |  |  | No action
MSA-DTWD | WA5837752 | 1 | AHS Services WA Pty Ltd (Anchor) | Water leak from roof space above dishwasher | Plumbing & Drainage | Water | 665.6075 | Pass | Fail | 0 | 3 | 451.75 | 2022-09-08 08:47 | 2022-09-09 17:00 | 2022-09-08 13:30 | 2022-09-09 17:00 | 2022-09-27 09:15 |  |  | .
MSA-DTWD | WA5216886 | 2 | Lane's Plumbing | Sample point MW02 - reinstall/repair sample point MW02 | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 2 | 439.5 | 2022-03-11 13:47 | 2022-03-16 17:00 | 2022-03-14 09:00 | 2022-03-16 17:00 | 2022-04-01 16:30 |  |  | REPAIR AND REINSTALL SAMPLE POINT
MSA-DTWD | WA5239018 | 2 | Protek 24/7 Building & Maintenance | E71 Asian Kitchens Entry - External - Water leak through eave lining | Building | General Building | 2025.17 | Pass | Fail | 0 | 2 | 437.25 | 2022-03-16 10:03 | 2022-03-21 17:00 | 2022-03-18 07:30 | 2022-03-21 17:00 | 2022-04-05 12:45 |  |  | Repair leaking eave lining
MSA-DTWD | WA5216885 | 2 | Lane's Plumbing | Ground water monitoring point MW03 - repair Sample point MW03 | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 2 | 437 | 2022-03-11 13:43 | 2022-03-16 17:00 | 2022-03-14 09:30 | 2022-03-16 17:00 | 2022-04-01 14:30 |  |  | REPAIR GROUND WATER MONITORING POINT MWO3
MSA-DTWD | WA5381703 | 2 | M Construction (WA) | Ground Floor - Stores Area - E-Block stores has a s/steel trolley with broken rail needs welding | Equipment | Building Equipment | 809 | Pass | Fail | 0 | 2 | 437 | 2022-04-26 10:45 | 2022-04-29 17:00 | 2022-04-28 09:30 | 2022-04-29 17:00 | 2022-05-16 14:30 |  |  | Attend site to investigate steel trolley, take stainless steel trolley to welder for welding in Osborne Park, needed to borrow a van, pick up trolley from welder and return to north metro TAFE.
MSA-DFES | WA6669199 | 2 | Australian HVAC Services Pty. Ltd. | Main dinning room - Aircon - Fault | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Fail | 0 | 2 | 436.85 | 2023-02-22 15:19 | 2023-02-27 17:00 | 2023-02-24 11:00 | 2023-02-27 17:00 | 2023-03-14 15:51 |  | WACCES
MSA-DFES | WA5108221 | 3 | Protek 24/7 Building & Maintenance | Applied training ground - ground - change room 2 - see details below | Building | General Building | 1491.78 | Pass | Fail | -1 | 2 | 436 | 2022-02-08 12:34 | 2022-02-15 17:00 | 2022-02-10 11:15 | 2022-02-15 17:00 | 2022-02-28 15:15 |  | WACCES | Replaced damaged external door hardware
MSA-DTWD | WA6255759 | 2 | COMMERCIAL PLUMBING AND GAS | Eye ash station flow is slow and isolating valve doesn't work | Plumbing & Drainage | Water | 354.015 | Pass | Fail | 0 | 3 | 436 | 2022-11-23 13:08 | 2022-11-28 17:00 | 2022-11-28 14:00 | 2022-11-28 17:00 | 2022-12-16 18:00 |  |  | installed new line and valve
MSA-DTWD | WA5094525 | 2 | AWB Co. | E block - Canteen - faulty GPO | Electrical | General Electrical | 432.595 | Pass | Fail | 0 | 3 | 435.75 | 2022-01-31 11:53 | 2022-02-03 17:00 | 2022-02-03 07:45 | 2022-02-03 17:00 | 2022-02-21 11:30 |  | WACCES | Attended site and signed in. Completed jsa. Liaised with fm about works going ahead. Went to canteen and spoke to lady. Supplied and replaced thermostat stat. Tested for correct operation. **job complete**
MSA-DTWD | WA6157089 | 2 | ECO PLUMBING AND GAS PTY LTD | Faulty Hot Water Tap in Loading Bay | Plumbing & Drainage | Water | 219.03 | Pass | Fail | -1 | 2 | 435.2 | 2022-11-09 12:46 | 2022-11-14 17:00 | 2022-11-10 11:56 | 2022-11-14 17:00 | 2022-11-28 15:08 |  |  | Replaced taps in wash area
MSA-DFES | WA5697948 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Various Lights needing replacement - See notes below | Electrical | Lighting, Internal | 797.25 | Fail | Fail | 0 | 3 | 434.9167 | 2022-08-09 13:09 | 2022-08-16 17:00 | 2022-08-18 06:50 | 2022-08-16 17:00 | 2022-09-05 09:45 |  | WACCES | Continued on site at 08:45. Located faulty light in store room 7 replaced for new led battern and tested all okay. Located fitting with blown globes in hallway 6, replaced 2 x globes. Left site at 09:45
MSA-DTWD | WA6126554 | 2 | Protek 24/7 Building & Maintenance | Cabin crew office-Water damage to Ceiling / investigate roof leak | Building | Ceiling | 2383.31 | Fail | Fail | 1 | 3 | 434.75 | 2022-10-25 12:13 | 2022-10-28 17:00 | 2022-11-03 12:45 | 2022-10-28 17:00 | 2022-11-21 15:30 |  | WACCES & WCAPPR | Receive scissor lift and setup exclusion zone for duration of worksCarry out inspection of roof and confirm location of water ingress Make repairs where possible to roof to make water-tightCarry out water testing once works complete to confirm water-tight Remove and replace 2x ceiling tiles once roof confirmed water-tight
MSA-DTAG | WA6450773 | 3 | Midolo Building Services | Level 4 - Custody Ceiling - Create an access hatch which would allow the removal of an exhaust fan | Building | Ceiling | 2174.56 | Fail | Fail | 1 | 3 | 434.5 | 2023-01-16 14:08 | 2023-01-23 17:00 | 2023-01-28 06:00 | 2023-01-23 17:00 | 2023-02-15 08:30
MSA-DTAG | WA5397328 | 1 | Bullant Security Pty Ltd | Level 10 - Door to micro fishe area - see notes below | Security | Locksmith | 689.79 | Pass | Fail | 0 | 3 | 434.3333 | 2022-05-06 15:08 | 2022-05-09 17:00 | 2022-05-09 10:10 | 2022-05-09 17:00 | 2022-05-27 12:30 |  |  | Attended site, door handle thread on one side is damaged causing handles to pull off. I have managed to make one side screw in but a replacement is needed or may have to seek an alternative option.Date on site: 9/5/2022Time on site: 10:10 - 11:40Attended site, fitted new handles and scare plates on level 10 door to microfiche area.Date on site: 27/5/2022Time on site: 12:00 - 12:30
MSA-DCA | WA5887974 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Opposite main stairs and boardwalk area - 3 x External PE cells faulty - see notes below | Electrical | Lighting, External | 1626.685 | Pass | Fail | 0 | 2 | 434.25 | 2022-09-16 11:44 | 2022-09-19 17:00 | 2022-09-16 13:45 | 2022-09-19 17:00 | 2022-10-04 16:00 |  | WCAPPR | Arrived on site at 1145 to attend 3x faulty PE Cells, identified all relative PE Cells. Left to wholesaler at 1230 to pick up parts. Returned to site at 1345, identified/obtained access to relative switchboard, replaced all faulty PE Cells and ensured operation. Informed staff of works and left site at 1600
MSA-DCA | WA5572737 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Air temperatures in many parts of building too hot while some areas too cold.- See notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 315.315 | Fail | Fail | 0 | 3 | 434 | 2022-06-30 10:08 | 2022-07-05 17:00 | 2022-07-07 08:00 | 2022-07-05 17:00 | 2022-07-25 10:00 |  |  | Attended site, signed in and accessed affected areas of concern. Checked and recorded the room temperatures around 22.8 - 24.5 degreese on level 2 North/West areas. Found the temperatures in this area intermittently changing during afternoons.Checked the Ahus, chilled/heating water valves, vavs and calibration of the thermostats serving the affected ares and found no faults evident. Lowered the vav setpoints in the affected area from 23.5 to 22.5. It is recommended having the open area sensors calibrated by Honeywell. Checked the North/West seminar room vavs for correct operation and setpoints. Was told by staff the room gets warm when there is 10+ people in the room at once. It is recommended a supplementary unit be installed as the base building vavs are unable to cope with the temperatures when the room has 8+ people using it. Lowered the setpoints on the vavs and increased airflow for the time being.
MSA-DFES | WA5839196 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Multiple faulty lights - see notes below | Electrical | Lighting, Internal | 1976.915 | Pass | Fail | 0 | 2 | 434 | 2022-09-09 10:09 | 2022-09-14 17:00 | 2022-09-12 12:00 | 2022-09-14 17:00 | 2022-09-30 14:00 |  |  | Arrived on site at 1200 to attend Multiple faulty lights - see notes below Dormitory 9, Dormitory 10, Dormitory 13, Tunic room, Training Tower. Located/replaced 3 x fluros in carport, 1 x fluro in storage shed and 2 x fluros in tunic rm.Will need to return to site WITH EWP to identify south-end floodlight type in carpark requiring replacement and replace oyster lights in dorms 1, 2,3. Informed staff and Left site at 1400
MSA-DFES | WA5693015 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Outisde - Undernearth Electronic Gate - Rear Training Yard - Drains are blocked and backfilling | Plumbing & Drainage | Drainage | 194.28 | Pass | Fail | 0 | 2 | 433.3333 | 2022-08-04 08:50 | 2022-08-05 17:00 | 2022-08-04 14:22 | 2022-08-05 17:00 | 2022-08-22 15:42 |  |  | Inspecting the overflowing stormwater drains at the station’s back yard. Firefighters have pumped out the water with their own equipment. Soakwell is full with sand and leaves. Will organise a TerraVac truck to suck the dirt from soakwell and then inspect pipes to see if they are blocked.
MSA-DTWD | WA5698165 | 3 | GRAFFITI FORCE PTY LTD | Lift lobby-Level 2 Ladies & men’s toilets requires graffiti removal | Cleaning | Graffiti | 486.5 | Pass | Fail | -1 | 2 | 433.25 | 2022-08-09 15:12 | 2022-08-16 17:00 | 2022-08-11 11:00 | 2022-08-16 17:00 | 2022-08-29 12:15 |  |  | REMOVAL OF GRAFFITI FROM LEVEL 2 MALE BLOCK TOILET AND FEMALE TOILETS
MSA-DFES | WA5203756 | 3 | AWB Co. | Male Toilet - Near Dining Room - Two tiles are missing from Basin | Flooring | Tiling | 801.25 | Pass | Fail | 0 | 2 | 433 | 2022-03-03 16:36 | 2022-03-11 17:00 | 2022-03-10 08:00 | 2022-03-11 17:00 | 2022-03-28 09:00 |  |  | Craig Adams (10/03/2022) - Work NoteAttended site, met with Dwayne and showed me the location of the tiles, measured up. They don’t have tiles that size in Bunnings. Must try a tile shop.Size - 2 white tiles x 152mm x 152mmPhoto attached.Attend site and replace tile sizes, approval to change to more current and stock standard tile
MSA-DTWD | WA5208795 | 2 | Precise Air Group | A Block - Level 3 - A308 -Repair Ice Machine in A308 | Refrigeration | Refrigerators | 1810.69 | Pass | Fail | -1 | 2 | 433 | 2022-03-09 11:03 | 2022-03-14 17:00 | 2022-03-10 14:00 | 2022-03-14 17:00 | 2022-03-28 15:00 |  |  | Collected part from supplier. Attended site and completed pre start paperwork and signed in. Removed and replaced 1x water pump and cleaned ice machine. Test ran system and left operating in good working order. Left all ok.
MSA-DTAG | WA6521706 | 2 | Australian HVAC Services Pty. Ltd. | Whole building - ground-Chiller 2 is on fault – screen non responsive - A40092582J | Air Conditioning | Room Air Conditioners | 9896.98 | Pass | Fail | 0 | 2 | 433 | 2023-01-30 12:41 | 2023-02-02 17:00 | 2023-01-30 14:00 | 2023-02-02 17:00 | 2023-02-17 15:00
MSA-DFES | WA5994943 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Printer Room - Data Points not working - See notes below | Electrical | General Electrical | 1160.66 | Fail | Fail | 0 | 3 | 432.75 | 2022-10-06 09:38 | 2022-10-11 17:00 | 2022-10-13 09:30 | 2022-10-11 17:00 | 2022-10-31 10:15 |  | WACCES | Adam Back (13/10/2022) - Work NoteArrived onsite at 9:30 to investigate data points not working located front office. Conducted continuity test from data points to corresponding points on server rack and found no continuity. Traced cables from points and found cable had been cut. Will need to re run cables, install and test. Documented all necessary information for data point repair, notified staff and left site at 11:45Cameron Vasey (31/10/2022) - Work NoteOnsite 700 removed old cables and ran new from noted points to comms rack, tested and cleaned up. These points were not a part of our original scope of works and never worked. Completed and Signed out 1015
MSA-DCA | WA6020694 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Submarine Electrical Conduits - Faulty Cables - See notes below | Electrical | General Electrical | 1590.19 | Pass | Fail | -1 | 2 | 432.75 | 2022-10-13 15:52 | 2022-10-18 17:00 | 2022-10-14 11:30 | 2022-10-18 17:00 | 2022-11-01 12:15 |  | WACCES | Fixed broken conduit by mechanically protecting with ducting.
MSA-DFES | WA5384195 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Main Admin - lower floor Male toilet - roof leaking through light fitting | Electrical | Lighting, Internal | 149.805 | Pass | Fail | 0 | 2 | 432.4167 | 2022-04-28 10:39 | 2022-04-29 17:00 | 2022-04-28 13:45 | 2022-04-29 17:00 | 2022-05-16 14:10 |  |  | Arrived onsite at 13:45 to investigate water leak affecting roof lights. Found 1 x light to be wet from a recent water leak. Disconnected light and reenergised circuit for works to be completed regarding fixing the leak. Will reconnect when required and made safe. Left site at 15:00
MSA-DTWD | WA5586771 | 3 | AWB Co. | Water leak above I beam at end of Balcony-( Future Proof ) | Roofing | Metal Roofing | 1908.27 | Pass | Fail | -1 | 2 | 432.25 | 2022-07-06 14:37 | 2022-07-13 17:00 | 2022-07-07 12:00 | 2022-07-13 17:00 | 2022-07-25 12:15 |  |  | Investigated leak - found rust patches on I beam, cleaned back rust and prepped area. Sealed join where flashing meetsI beam.Sealed gap in between wall and flashing to prevent water running into eaves board.BRAF required - to follow.
MSA-DTWD | WA6668870 | 3 | WESTERN IRRIGATION PTY LTD | Fault dialler isn’t working – not sending text messages to relevant staff when there is irrigation | Electrical | General Electrical |  | Pass | Fail | -1 | 2 | 432 | 2023-02-22 12:15 | 2023-03-01 17:00 | 2023-02-24 11:00 | 2023-03-01 17:00 | 2023-03-14 11:00
MSA-DTWD | WA5308767 | 3 | Dormakaba Australia Pty Ltd | Auto door arm has come away from motor | Building | Doors | 3759.58 | Pass | Fail | -1 | 1 | 431.8 | 2022-04-08 15:58 | 2022-04-19 17:00 | 2022-04-11 10:12 | 2022-04-19 17:00 | 2022-04-29 10:00 |  |  | 11/4/22 - Found that the unit has completely failed, operating erratically and not staying open, urgent upgrade required to replace unit with an ed10029/4/22 - Note new IP number 1141909 ED100 K block. Removed faulty unit and supplied and fitted new ED100 complete with standard arm and commissioned.
MSA-DCA | WA6113179 | 3 | Protek 24/7 Building & Maintenance | Alexander Library building - State library theatre - Leak from roof when it rains - see notes | Roofing | Tiled Roofing | 773.14 | Pass | Fail | -1 | 2 | 431.75 | 2022-10-24 09:25 | 2022-10-31 17:00 | 2022-10-24 13:15 | 2022-10-31 17:00 | 2022-11-11 13:00 |  | WCAPPR | Leak tested roof area above leak to ceiling in theatre, replaced various roof screws around the suspect area
MSA-DTAG | WA5478686 | 3 | Australian HVAC Services Pty. Ltd. | Level 15 - Plant room - Heater pump “B” has failed | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2365.13 | Pass | Fail | -1 | 2 | 430.9167 | 2022-05-26 13:03 | 2022-06-02 17:00 | 2022-05-26 13:05 | 2022-06-02 17:00 | 2022-06-13 12:00 |  |  | Pick up all parts required for works. Attend site afterhours. Access level 15 plantroom. Isolate boiler and heating water pumps. Access roof and isolate make-up tank. Drain down water from pipework. Drill rivots out of cladding and remove from pipework. Unbolt isolation valves and remove. On inspection of the isolation valves we found the valve on the suction side was seized shut. The handle wound move but the butterfly was seized. Install new butterfly valves. Unbolt water strainer and remove. Install new strainer and new rubber gaskets. Deisolate make-up tank and slowly fill the system. Access ball valve at highest point to remove air. Once full inspect for any water leaks, none found. Deisolate heating water pumps and test operation. Found pump to run and pump as normal. Pump still appears to be in good working condition. Deisolate isolate boiler and return plant to auto operation. Fix cladding back to pipework and clean up area
MSA-DFES | WA5694129 | 3 | SONTEC WA PTY LTD | Exit Boom Gate - Intercom - Microphone not working. Can’t hear from Security Desk | Building | Steel Fencing & Gates | 1969.97 | Pass | Fail | -1 | 2 | 430.75 | 2022-08-05 08:15 | 2022-08-12 17:00 | 2022-08-05 14:30 | 2022-08-12 17:00 | 2022-08-23 13:15 |  |  | 5/8/22 - Dylan ParslowFound microphone corroded and RJ45 partly corroded.Recommend replacement.BRAF submitted.23/8/22 - Dean Simpson, Dylan ParslowOnsite waiting for IT dept to setup.Left device for IT dept to setup.31/8/22 Deborah confirmed IT dept have setup and fitted intercom.
MSA-DTWD | WA5053100 | 2 | Dormakaba Australia Pty Ltd | G Block - Ground - GF16 - Large roller door to workshop jammed | Building | Doors | 495.8 | Pass | Fail | 0 | 3 | 430.05 | 2022-01-18 13:04 | 2022-01-21 17:00 | 2022-01-21 12:30 | 2022-01-21 17:00 | 2022-02-08 10:33 |  |  | 21/1/22 - Assessed door and found and left hand guide has been hit forklift, was told by customer that they used a forklift to get the door down which has wedged the door in the guide. Bent guide out to free slats, door has lost limits but can still be hand chainedRevisit by Dormakaba electrician to reset limitsPlease quote for new 12B chain and sprocket - BRAF was submitted but as works are under $1000, BRAF was not required. 8/2/22 - Drive train for roller shutter had completely warn and rusted out, replace all parts with new, adjusted limits and motor. Door has been tested and work.
MSA-DTWD | WA6402259 | 1 | Equans Mechanical Services Australia | No chillers working. Chiller 1 showing fault 70, Chiller 2 also in fault. | Refrigeration | Chiller | 820.915 | Pass | Fail | 0 | 2 | 429.75 | 2023-01-05 09:27 | 2023-01-06 17:00 | 2023-01-05 10:15 | 2023-01-06 17:00 | 2023-01-23 08:00 |  | WACCES
MSA-DTWD | WA6450539 | 1 | Water2water Pty Ltd | Boiling water unit has faulty tap | Plumbing & Drainage | HWS/Units Electric & Gas | 533.245 | Pass | Fail | 0 | 2 | 429.2 | 2023-01-16 11:39 | 2023-01-17 17:00 | 2023-01-16 13:20 | 2023-01-17 17:00 | 2023-02-03 10:32 |  | WACCES
MSA-DTWD | WA5797787 | 3 | AWB Co. | F 60 - Power switch LED light not working | Electrical | General Electrical | 737.36 | Pass | Fail | -1 | 2 | 428 | 2022-08-29 10:38 | 2022-09-05 17:00 | 2022-09-01 15:00 | 2022-09-05 17:00 | 2022-09-19 11:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Liaised with site about works. Located classrooms. Isolated. Installed 2x green indicator lights near A/C. Energised and tested. Packed up. Notified relevant personnel of works completed. **job complete**
MSA-DCA | WA5127772 | 1 | Critical Fire Protection & Training | stage door - Fire Panel started beeping. Yellow Audio Line Fault Button flashing-Auditorium/zone 7 | Fire Protection Services | Fire Protection - Monitor System | 1224.07 | Pass | Fail | 0 | 2 | 427 | 2022-02-14 14:13 | 2022-02-15 17:00 | 2022-02-14 15:00 | 2022-02-15 17:00 | 2022-03-04 10:00 |  |  | Attempted system reset on ewis with no change. Inspected areas amplifier’s no untoward damage15/02/2022 due to performance rehearsals could not get full access to required areas to find and resolve fault. Will require to reattend with 2 technicians, when auditorium is free/clear access.04/03/22 - Fault rectified. Carried out checks of all speakers. All operating as intended.
MSA-DFES | WA6294455 | 2 | AWB Co. | Main admin - Lower ground - North west door jamming - see notes | Building | Doors | 1456.51 | Pass | Fail | 0 | 2 | 415.5 | 2022-11-30 16:58 | 2022-12-05 17:00 | 2022-12-02 08:00 | 2022-12-05 17:00 | 2022-12-19 15:30 |  |  | Speak with Kim Weir to arrange accessRemove old leaky door closersInstall two new door closersAdjust operation and checkClear siteJob is now completeBRAF approval attached
MSA-DTWD | WA6521536 | 1 | Equans Mechanical Services Australia | T Block - South Side - Require 5-6 portable AC units for classrooms (See notes) | Air Conditioning | Room Air Conditioners | 4015 | Pass | Fail | 0 | 2 | 415 | 2023-01-30 11:32 | 2023-01-31 17:00 | 2023-01-31 08:00 | 2023-01-31 17:00 | 2023-02-17 15:00
MSA-MRWA | WA6522704 | 1 | SONTEC WA PTY LTD | All throughout building - Intercom failed | ICT/Audiovisual | Phone Data Lines |  | Pass | Fail | 0 | 2 | 414 | 2023-01-31 09:47 | 2023-02-01 17:00 | 2023-01-31 11:00 | 2023-02-01 17:00 | 2023-02-17 17:00
MSA-DTWD | WA5494446 | 3 | AWB Co. | E100 (Main workshop) - 10 x lights out | Electrical | Lighting, Internal | 773.9725 | Pass | Fail | -1 | 2 | 413.25 | 2022-06-07 15:18 | 2022-06-14 17:00 | 2022-06-10 09:15 | 2022-06-14 17:00 | 2022-06-27 14:30 |  | WCAPPR | . Attended site and signed in, completed jsa,spoke with fm about job, replaced all tubes and starters in area with ewp, disposed of tubes in allocated boxes on site, cleaned up work area, off hired ewp, completed paperwork, signed out, job completed
MSA-DCA | WA5109692 | 2 | GPS Plumbing & Gas Services PtyLtd | Main foyer - Male toilets - leaking and faulty urinals and urinal pipes - see notes | Plumbing & Drainage | Water | 1038.6025 | Pass | Fail | 0 | 2 | 412.9833 | 2022-02-09 12:29 | 2022-02-14 17:00 | 2022-02-14 09:15 | 2022-02-14 17:00 | 2022-03-03 14:14 |  | WACCES | Replaced urinal sensor trap and seals to 1st Urinal RHS ground floor male toilet.
MSA-DTAG | WA5217085 | 2 | Sapio Pty Ltd | Security Desk - Camera 41 still drops out and vision lags | Security | CCTV Surveillance | 430 | Pass | Fail | 0 | 2 | 412.5 | 2022-03-11 16:27 | 2022-03-16 17:00 | 2022-03-14 09:00 | 2022-03-16 17:00 | 2022-03-31 13:30 |  |  | Replaced axis camera number 41. using PFM stock.camera to given to convergint
MSA-DTWD | WA6467523 | 3 | Techworks Electrical | Hallway- Lights not working | Electrical | Lighting, Internal | 3194.49 | Pass | Fail | -1 | 2 | 411.6 | 2023-01-17 14:56 | 2023-01-24 17:00 | 2023-01-18 11:00 | 2023-01-24 17:00 | 2023-02-04 14:36
MSA-DTWD | WA5191878 | 3 | AWB Co. | Corridor outside room 310 - 3x lights not working | Electrical | Lighting, Internal | 1911.78 | Pass | Fail | 0 | 2 | 411.5 | 2022-02-25 10:06 | 2022-03-04 17:00 | 2022-03-01 07:00 | 2022-03-04 17:00 | 2022-03-18 10:30 |  | WCAPPR | Attended site and signed in. Completed JSA. Spoke to fm about job. Went to B2 and re located faulty lights that needed replacing. Located snorkel. Had to go and get key for snorkel from Warwick. Returned to snorkel. Snorkel would move forward and back but would not go up or down. Called Dave, him and Warwick came down to see if they could sort the issue out. Couldn’t be fixed. Went to office to pick up ladder and materials. Returned to site and replaced all faulty tubes. All lights are now working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA6450663 | 2 | Techworks Electrical | Level 1 & 2 - all lights blown in corridors and classrooms | Electrical | Lighting, Internal | 1004.03 | Pass | Fail | 0 | 2 | 411.5 | 2023-01-16 12:33 | 2023-01-19 17:00 | 2023-01-16 13:30 | 2023-01-19 17:00 | 2023-02-02 17:00
MSA-DFES | WA4985736 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Males toilets - Light globe blown. | Electrical | Lighting, Internal | 406.65 | Pass | Fail | 0 | 2 | 411 | 2021-12-30 10:35 | 2022-01-07 17:00 | 2022-01-04 09:15 | 2022-01-07 17:00 | 2022-01-21 12:15 |  |  | Continued on from last job at same site. Located blown fluro in level 1 male toilet. Replaced for new and tested. Continued onto next job at same site.
MSA-DCA | WA5513769 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Level 3 - Rare book room -CRAC #1 in fault- compressor overload message | Air Conditioning | Building HVAC Maintenance (Major Plant) | 895.675 | Fail | Fail | 0 | 3 | 411 | 2022-06-14 13:00 | 2022-06-17 17:00 | 2022-06-20 08:00 | 2022-06-17 17:00 | 2022-07-07 11:00 |  |  | Works carried out and completed by subcontractor. Fuse replaced and system rebooted.
MSA-DTWD | WA5080856 | 1 | BAKE-QUIP PTY LTD | E Block - Ground - Canteen kitchen room E6 - Hobart dishwasher not working | Equipment | Catering Equipment | 679.03 | Fail | Fail | 1 | 4 | 410.75 | 2022-01-20 09:20 | 2022-01-21 17:00 | 2022-01-31 11:00 | 2022-01-21 17:00 | 2022-02-17 13:45 |  |  | See service report
MSA-DTWD | WA5976805 | 2 | WESTERN IRRIGATION PTY LTD | Grounds - Broken retic sprinklers on all stations | Landscaping & Gardening | Grounds Maintenance | 2516.16 | Fail | Fail | 2 | 4 | 410.75 | 2022-09-27 11:37 | 2022-09-30 17:00 | 2022-10-11 08:15 | 2022-09-30 17:00 | 2022-10-28 11:00 |  | WACCES | Attend site and repair / replace retic items as required.
MSA-DTWD | WA5101868 | 1 | Damian Rak Electrical Pty Ltd | Various security lights in front of lab | Electrical | General Electrical |  | Pass | Fail | 0 | 2 | 410.5 | 2022-02-03 15:58 | 2022-02-04 17:00 | 2022-02-04 11:00 | 2022-02-04 17:00 | 2022-02-21 13:30 |  |  | job completed - replace bunker lights
MSA-DTAG | WA6108865 | 1 | Sapio Pty Ltd | door leading into the custody control room has a damaged cabled and intermittent mortice lock-notes | Security | Security Management System | 3250.59 | Fail | Fail | 1 | 3 | 410.5 | 2022-10-20 11:54 | 2022-10-21 17:00 | 2022-10-25 13:30 | 2022-10-21 17:00 | 2022-11-11 16:00 |  |  | Replaced faulty mortice lock and recabled
MSA-DTAG | WA6381300 | 1 | Sapio Pty Ltd | Ground - Courtroom 1 - public exit door into main area – green button release not responding | Security | Access Control | 223.05 | Pass | Fail | 0 | 2 | 410 | 2022-12-19 12:51 | 2022-12-20 17:00 | 2022-12-20 06:00 | 2022-12-20 17:00 | 2023-01-06 08:00 |  | WACCES | Work performed by Dirk Malan (20/12/2022)Attended site. Investigated reported issue. Replacement Push to Exit button needed.Work performed by Michael Tomlinson (06/01/2023)Replaced Push to Exit button and all okay.Job completed.
MSA-DTAG | WA5318177 | 1 | Australian HVAC Services Pty. Ltd. | Roof - AC plant - Airconditioning very cold Judicial area | Air Conditioning | Room Air Conditioners | 984.65 | Pass | Fail | 0 | 2 | 409.9167 | 2022-04-12 09:04 | 2022-04-13 17:00 | 2022-04-12 09:05 | 2022-04-13 17:00 | 2022-04-29 11:00 |  |  | Attend site with icon logic. Access BMS and check control issue. Found heating call for chillers not working correctly. Carry out program reset as heating point was locked out. Found heating call to now operate chillers and FCUs now have heating. Test operation of Valves at FCUs and found to work as normal. Temps in cold areas are now beginning to rise.
MSA-DFES | WA5681323 | 3 | Australian HVAC Services Pty. Ltd. | ground admin building-Air conditioning units located outside parcel delivery room making loud noise | Air Conditioning | Room Air Conditioners | 1717.11 | Pass | Fail | -1 | 2 | 409.75 | 2022-07-28 11:12 | 2022-08-04 17:00 | 2022-07-29 15:00 | 2022-08-04 17:00 | 2022-08-15 16:45 |  | WACCES | All works done
MSA-DCA | WA5381915 | 1 | Dormakaba Australia Pty Ltd | Carpark - faulty cable gate | Building | Security Doors | 554.1 | Pass | Fail | 0 | 2 | 408.7 | 2022-04-26 12:22 | 2022-04-27 17:00 | 2022-04-26 14:14 | 2022-04-27 17:00 | 2022-05-13 14:56 |  |  | 26/4/22 - Note new IP number 1141908, arrived onsite and signed in, inspected unit and found the controller in fault, reset and cleared fault and tested operation and went back into fault and noticed Safety beam not working, further investigation found no power going to beam, checked all control fuses and all ok indicating the power supply on the control board faulty, picture attached. Dormakaba to submit quote to replace control board, Cable Gate 3.4 type.Rang Ryan and explained outcome.13/5/22 - Replaced batteries with new. Adjusted and tightened safety beam. Lubricated knuckle and mouth piece. Operation ok.
MSA-DTAG | WA6108909 | 1 | Sapio Pty Ltd | The network switch that provides the security network in the custody control room has a faulty port | Security | Security Management System | 3832.01 | Fail | Fail | 1 | 3 | 408.5 | 2022-10-20 12:00 | 2022-10-21 17:00 | 2022-10-25 15:30 | 2022-10-21 17:00 | 2022-11-11 16:00 |  | WCAPPR | Cabled all cat6 cables to workstations and cutover
MSA-DTWD | WA6132207 | 2 | AWB Co. | replace/repair fluro acrylic covers and globes | Electrical | Lighting, Internal | 1404.98 | Pass | Fail | 0 | 2 | 408.5 | 2022-10-31 12:22 | 2022-11-03 17:00 | 2022-11-01 13:30 | 2022-11-03 17:00 | 2022-11-18 14:00 |  | WACCES | Attended site and signed in. Completed jsa. Spoke to fm. Located faulty lighting. Isolated and locked out lighting circuits. Took down all lights and kept good diffusers. Put good diffusers up in other room where diffusers needed to be replaced. Put all LED wide base battens up. Took lockout off and re energised. Working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6257385 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Roof Level - Plant Room - Repair leak on Hydrochem Pump filter - See Notes Below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 833.21 | Pass | Fail | -1 | 2 | 408.5 | 2022-11-24 14:55 | 2022-11-29 17:00 | 2022-11-25 14:30 | 2022-11-29 17:00 | 2022-12-12 15:00 |  | WACCES | Hydrochem resolved leak on filtration system.
MSA-DCA | WA5413406 | 2 | EQUANS Mechanical Services (WA) Pty Limited | First Floor - Plant room - Remote access to BMS not working - please investigate further | Air Conditioning | Building HVAC Maintenance (Major Plant) | 799.65 | Pass | Fail | -1 | 2 | 408.0667 | 2022-05-12 10:51 | 2022-05-17 17:00 | 2022-05-13 15:05 | 2022-05-17 17:00 | 2022-05-30 15:09 |  |  | BMS Tech attended site reset IP Address and has brought remote access back online. Confirmed access to bms. No further action required
MSA-DTWD | WA5681125 | 3 | AHS Services WA Pty Ltd (Anchor) | Electrical Workshops - Male Toilets - waterless urinal waste water cover requires replacing | Plumbing & Drainage | Toilets/Cisterns | 605.49 | Pass | Fail | 0 | 2 | 408 | 2022-07-28 09:16 | 2022-08-04 17:00 | 2022-08-01 12:00 | 2022-08-04 17:00 | 2022-08-18 12:00 |  | WACCES | Installed new urinal plug & waste
MSA-DTWD | WA6015090 | 2 | Water2water Pty Ltd | Water tasting foul from chilled water unit. Possible filter problem | Plumbing & Drainage | Water | 2106.455 | Pass | Fail | 0 | 2 | 408 | 2022-10-12 14:52 | 2022-10-17 17:00 | 2022-10-14 13:00 | 2022-10-17 17:00 | 2022-10-31 13:00 |  |  | New unit required, Replacement required.
MSA-DTAG | WA5271231 | 2 | SONTEC WA PTY LTD | Armadale Court - Custody - Sallyport - Electronic lock faulty Key barrel loose | Building | Automatic Doors | 830 | Pass | Fail | 0 | 2 | 407.75 | 2022-03-18 09:18 | 2022-03-23 17:00 | 2022-03-21 11:45 | 2022-03-23 17:00 | 2022-04-07 11:30 |  |  | 21/3/22 - Dean SimpsonLock not working and cable fault.More time required to investigate further.BRAF Submitted 7/4/22 - Dylan ParslowDisassembled, cleaned and lubricated lock and tested.Found fault on cable and reconnected.All tested ok
MSA-DTAG | WA5674643 | 1 | Midolo Building Services | L1-court 4-Leak from roof near door at back of courtroom | Roofing | Metal Roofing | 767.25 | Fail | Fail | 1 | 3 | 407.75 | 2022-07-21 13:02 | 2022-07-22 17:00 | 2022-07-26 10:15 | 2022-07-22 17:00 | 2022-08-12 10:00 |  | WACCES | source of leak located & repaired
MSA-DTWD | WA5379842 | 2 | De.mem-Capic Pty Ltd | Cooling towers dosing pump trips circuit breaker | Air Conditioning | Cooling Tower | 142.5 | Pass | Fail | -1 | 2 | 407.75 | 2022-04-21 15:49 | 2022-04-27 17:00 | 2022-04-22 11:15 | 2022-04-27 17:00 | 2022-05-09 11:00 |  |  | 22.04.22 - Technician attended site to inspected dosing equipment - Found that the ORP dosing pump squeeze tube had split causing the chemical to leak onto the power outlet. Technician isolated the dosing pump and will return to replace squeeze tube.Total hours: 1hr labour at $95.00 per hour ($95.00)27.04.22 - Technician attended site to replace squeeze tube with a spare. Technician to return to site with a new replacement squeeze tube (Under warranty)Total hours: 30min ($47.50)9.05.22 - Technician replaced squeeze tube and work order has been completed. This was completed during the monthly water treatment service.Total hours: 1:25min (No cost as this was completed during monthly service)Total amount $142.50
MSA-DFES | WA5291130 | 3 | Protek 24/7 Building & Maintenance | External Patio - see notes below | Roofing | Metal Roofing | 1618.27 | Pass | Fail | -1 | 2 | 407.5 | 2022-03-25 15:20 | 2022-04-01 17:00 | 2022-03-28 12:30 | 2022-04-01 17:00 | 2022-04-14 12:00 |  | WACCES | Replace Damaged Roof Sheets
MSA-DCA | WA5861555 | 0 | Techworks Electrical | First Floor - Balcony Area - Led Track Light is out - See notes below | Electrical | Lighting, Internal | 1028.975 | Pass | Fail | 0 | 2 | 407.5 | 2022-09-13 10:04 | 2022-09-13 12:04 | 2022-09-13 10:30 | 2022-09-13 14:04 | 2022-09-30 10:00 |  |  | Tasks completed 1. arrived and after a bit of searching found that two breakers on one of the dyna lite boards was tripped. Reset and all working well
MSA-DTWD | WA5752876 | 2 | GRONBEK SECURITY | Room/Office-E block aquaculture-2 door locks broken - see notes | Security | Locksmith |  | Pass | Fail | 0 | 2 | 407.0333 | 2022-08-17 12:30 | 2022-08-22 17:00 | 2022-08-22 13:20 | 2022-08-22 17:00 | 2022-09-08 12:22 |  |  | Completed as per attached.
MSA-DTWD | WA6463690 | 2 | AWB Co. | Recall - New heater recently replaced is tripping the RDC | Electrical | General Electrical | 443.315 | Pass | Fail | 0 | 2 | 407 | 2023-01-17 10:28 | 2023-01-20 17:00 | 2023-01-20 15:00 | 2023-01-20 17:00 | 2023-02-06 14:00 |  | WACCES
MSA-DTWD | WA6256894 | 3 | AWB Co. | Lights in workshop will require a large ladder or elevated workplatform. | Electrical | Lighting, Internal | 1897.895 | Pass | Fail | 0 | 2 | 406.5 | 2022-11-24 09:45 | 2022-12-01 17:00 | 2022-11-29 13:30 | 2022-12-01 17:00 | 2022-12-16 12:00 |  | WACCES | Attended site signed in jsa completed. Installed x4 hi bays to replace the 13 lights. removed 6 lights all together and disposed. Unplugged 7 more as site requested.Ewp offhiredJob completed
MSA-DTWD | WA5697631 | 3 | AWB Co. | Water leak L3 Lift lobby | Roofing | Metal Roofing | 525.945 | Pass | Fail | -1 | 1 | 406.4833 | 2022-08-09 10:54 | 2022-08-16 17:00 | 2022-08-09 15:31 | 2022-08-16 17:00 | 2022-08-26 14:00 |  |  | Sourced leaks found seal on for frame perished and all flashing on rsj beam that folds in to box gutter had all lifted
MSA-DTWD | WA5308112 | 1 | BAKE-QUIP PTY LTD | E-Block - SK1 Lecturers oven pilot light on but oven not burning | Equipment | Catering Equipment | 780.8 | Pass | Fail | 0 | 2 | 405.75 | 2022-04-08 08:58 | 2022-04-11 17:00 | 2022-04-11 10:45 | 2022-04-11 17:00 | 2022-04-28 08:30 |  | WACCES | REFER TO SERVICE REPORT.
MSA-DCA | WA5216584 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Archaeology Offices - Vault Stores - Investigated AHU-6A is leaking see notes | Air Conditioning | Room Air Conditioners | 345.35 | Pass | Fail | 0 | 2 | 405.6 | 2022-03-11 11:25 | 2022-03-14 17:00 | 2022-03-14 13:23 | 2022-03-14 17:00 | 2022-03-31 10:59 |  |  | Formal Quote has been submitted for equipment repairs. No further action required on this job. Confirmed work area left tidy.
MSA-DTWD | WA6467526 | 3 | Techworks Electrical | Hallway- Lights not working | Electrical | Lighting, Internal | 2993.4 | Pass | Fail | -1 | 2 | 404.8 | 2023-01-17 15:01 | 2023-01-24 17:00 | 2023-01-18 13:30 | 2023-01-24 17:00 | 2023-02-04 10:18
MSA-DFES | WA5780410 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | old applied training transportable, light blown | Electrical | Lighting, Internal | 886.665 | Pass | Fail | 0 | 2 | 404.75 | 2022-08-19 10:13 | 2022-08-22 17:00 | 2022-08-19 12:00 | 2022-08-22 17:00 | 2022-09-05 08:45 |  | WACCES | Arrived onsite 1200 to investigate light blown in old training transportable. Located transportable and awaited staff that were aware of issue to inform us of situation as room was smoked out due to exploded light fitting. When confirmed room was safe to enter. Lights affected were located. Discovered 2 x ballasts burnt & exposed copper on active coming into contact of metal base within fitting. Removed damaged ballast and reinstated insulation on cable. Assessed remaining lights in area and and discovered another 2 light fittings containing damaged components due to issue. Disconnected remaining lights requiring replacement. Will need to return to site to replace 3 x light fittings. Informed staff of works and left site at 1430.05/09/2022Collected parts from workshop at 06:30 and continued to site arrived at 07:00. Located faulty fluros in old training transportable, replaced all with new led batterns and tested all okay. Located faulty light switch controlling lights swapped for n
MSA-DTWD | WA6357712 | 1 | Securex Security Systems & Services | Zone 20 - Security zone is malfunctioning | Security | Monitoring | 768.42 | Pass | Fail | 0 | 2 | 404.25 | 2022-12-05 16:54 | 2022-12-06 17:00 | 2022-12-06 16:30 | 2022-12-06 17:00 | 2022-12-23 12:45 |  |  | (06/12/2022) - Work NoteRemoved cobwebs from detector, ceiling mount, may need replacing. Checked before leaving in permanent alarm.Deprogrammed and need to return to replace.(23/12/2022) - Work NoteLocated and replaced zone 20 motion sensor in canteen. Programmed back into system and walk tested.
MSA-DFES | WA5090568 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Locker 5, 7, Hallway and Carpark - 4 x lights faulty | Electrical | Lighting, Internal | 862.105 | Pass | Fail | -1 | 2 | 404 | 2022-01-25 13:52 | 2022-01-31 17:00 | 2022-01-25 15:15 | 2022-01-31 17:00 | 2022-02-11 11:15 |  |  | Continue on site at 9:30. Replaced 5 faulty weather battern in lower undercover car park. Tested all ok. Left site at 11:15
MSA-DTWD | WA6088671 | 1 | COMMERCIAL PLUMBING AND GAS | T, U & V Blocks-Intermittent interruption to potable water flow to each building | Plumbing & Drainage | Water | 810.7275 | Pass | Fail | 0 | 2 | 403 | 2022-10-19 09:55 | 2022-10-20 17:00 | 2022-10-20 15:00 | 2022-10-20 17:00 | 2022-11-06 10:00 |  | WCAPPR | restore flow, inspected float, installed access cover
MSA-DFES | WA6482551 | 2 | Protek 24/7 Building & Maintenance | Ground - Engine Room - Damaged roof space access covers in hallway and engine room | Roofing | Metal Roofing | 918.46 | Pass | Fail | 0 | 2 | 399 | 2023-01-18 11:13 | 2023-01-23 17:00 | 2023-01-23 15:30 | 2023-01-23 17:00 | 2023-02-09 06:30
MSA-DFES | WA5399237 | 2 | Protek 24/7 Building & Maintenance | Drying room TILES AROUND THE AIR CON DRAIN NEED REPAIRING / REPLACING | Building | Internal Walls | 316.75 | Pass | Fail | 0 | 2 | 391.25 | 2022-05-09 20:11 | 2022-05-12 17:00 | 2022-05-11 07:00 | 2022-05-12 17:00 | 2022-05-27 14:15 |  | WACCES | Repair Tiles in Drying room
MSA-DTWD | WA5018704 | 3 | Schneider Electric Australia Pty Ltd | Central Store - Repair software issues with A Block Swipe Doors Leederville | Security | Access Control |  | Pass | Fail | 0 | 2 | 391 | 2022-01-14 15:24 | 2022-01-21 17:00 | 2022-01-19 10:30 | 2022-01-21 17:00 | 2022-02-04 17:30 |  |  | Repairs
MSA-DTWD | WA5116188 | 1 | Precise Air Group | aircon unit vibrating very badly | Air Conditioning | Room Air Conditioners | 1428.2 | Pass | Fail | 0 | 2 | 391 | 2022-02-11 12:04 | 2022-02-14 17:00 | 2022-02-14 09:00 | 2022-02-14 17:00 | 2022-03-02 16:00 |  | WACCES | Fan blade removed unable to find suitable replacement. Possible one ordered inFan blade replaced
MSA-DTWD | WA5473469 | 1 | Milners Tree Solutions Pty Ltd | A1 - Tree branch fell on roof | Landscaping & Gardening | Tree Lopping | 2800 | Fail | Fail | 0 | 2 | 391 | 2022-05-24 15:34 | 2022-05-25 17:00 | 2022-05-26 06:30 | 2022-05-25 17:00 | 2022-06-11 13:30 |  |  | damaged part of tree removed
MSA-DFES | WA5839827 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Multiple faulty lights - see notes below | Electrical | Lighting, Internal | 499.96 | Pass | Fail | 0 | 2 | 390.5 | 2022-09-09 16:33 | 2022-09-16 17:00 | 2022-09-14 08:00 | 2022-09-16 17:00 | 2022-09-30 14:30 |  | WACCES | Arrived on site at 1300 to replace faulty oyster lights in dorm 2 bedroom and dorm4/5 bathroom. Replaced/reenergised 1 x 300mm oyster lt and 1 x 400mm. Informed staff of works and left site at 1430.
MSA-DTWD | WA5799266 | 3 | AWB Co. | 4 x structural beams starting to rust | Building | Foundations | 1820.7675 | Pass | Fail | 0 | 2 | 390 | 2022-08-30 10:44 | 2022-09-06 17:00 | 2022-09-05 07:00 | 2022-09-06 17:00 | 2022-09-21 13:00 |  |  | works completed1st attendance no works undertaken - only assessed works - nil sign slip
MSA-DTWD | WA5377673 | 0 | Techworks Plumbing | Water leaking from the urinal - major leak - struggling to isolate the water | Plumbing & Drainage | Toilets/Cisterns | 942.71 | Pass | Fail | 0 | 2 | 389 | 2022-04-20 08:25 | 2022-04-20 10:25 | 2022-04-20 08:30 | 2022-04-20 12:25 | 2022-05-06 13:30 |  | WACCES | Attended site and signed in at office, met with kristy who showed me where the toilets were that had the over flowing urinals, once there I grabbed a ladder and got into the ceiling to isolate the water, then I inspected the electronic flush valves to see what the issue was, I checked all power leads and plugs to make sure they were all connected properly, removed the solenoid to make sure there was no debri in them that would cause them not to operate correctly, then I tried swapping over the battery packs from the working urinals to the not working urinals and after I did that they were working fine, so I put 2 out of service signs over the urinals that aren’t working correctly , the other two work fine and can be used, I have ordered new battery packs for the urinals and we will be back to change them once they arrive Cleaned up and packed up tools then went and got a signature slip Completed paperwork Attended site with new power cells for the electronic urinals and signed in
MSA-DTWD | WA5679083 | 2 | Securex Security Systems & Services | West Block Arming Panel has faults on it when arming | Security | Security Management System | 645.91 | Pass | Fail | 0 | 2 | 388.75 | 2022-07-26 10:36 | 2022-07-29 17:00 | 2022-07-27 08:15 | 2022-07-29 17:00 | 2022-08-12 13:00 |  |  | 27/07/2022, 815-915Cable fault on zone 2 duress. Tested all pairs found high resistance on all will require recabling.Have looped out zone in panel in the meantime. Monitored other zones all appear ok sealing fine.Recable 2 techs 2-3hrs depending on roof space but plenty of manholes and pop up tiles along route,will more than likely have to use duct to come down into position however 1 length.Approx 40m run. 8ft ladder required also higher than usual roof.12/08/2022, 1000-1300Tested cores on zone 2 all cores showing open circuitRun new cable to duress button from panel. Tested duress button all okUsed 35-40meters 4core cable
MSA-DTWD | WA6401075 | 1 | Equans Mechanical Services Australia | Air conditioner turned off | Air Conditioning | Package | 743.42 | Pass | Fail | 0 | 2 | 388.3333 | 2023-01-04 08:53 | 2023-01-05 17:00 | 2023-01-04 11:32 | 2023-01-05 17:00 | 2023-01-20 15:52
MSA-DCA | WA6290295 | 0 | TK Elevator Australia Pty Ltd | Lift-not responding | Lifts | Lifts |  | Fail | Fail | 0 | 2 | 387.3333 | 2022-11-28 07:35 | 2022-11-28 09:35 | 2022-11-28 11:12 | 2022-11-28 11:35 | 2022-12-14 14:32 |  |  | Tried powering down salsis unit and disconnecting unit from top of car. Error still on top of car board.Further investigation required.
MSA-DTWD | WA5086891 | 2 | WESTERN IRRIGATION PTY LTD | Ground - T, U and V Block - Bore controller fan - Internal fan warning light is on bore controller | Landscaping & Gardening | Grounds Maintenance | 6898.2 | Pass | Fail | 0 | 2 | 387.25 | 2022-01-21 15:23 | 2022-01-27 17:00 | 2022-01-25 08:30 | 2022-01-27 17:00 | 2022-02-10 11:45 |  | WACCES | 25-1-2022 Attend to check out fault, replace 1 cubicle cooling fan, quote to complete works to be provided.
MSA-DTWD | WA5306076 | 1 | Dormakaba Australia Pty Ltd | D-Block - Main entrance - auto glass door not closing at times | Building | Automatic Doors | 5509.95 | Pass | Fail | 0 | 2 | 387.0667 | 2022-04-06 10:04 | 2022-04-07 17:00 | 2022-04-06 11:02 | 2022-04-07 17:00 | 2022-04-22 14:06 |  |  | 6/4/22 - Attended site and found doors where staying open after activation, on inspection found that the pe eye’s circuitry board and associated components are unstable, re calibrated circuitry for now. Secured unsafe ceiling panels, have advised client that all panels will need re- securing for long term safety. Recommend unit to be upgraded in the near future due to age of unit and components to prevent further unreliability. Please quote to supply and install new El301 upgrade kit, 2 x ixio sensors, 1 pib kit, no switches or buttons required. The works will require 2 technicians for safety due to large wooden ceiling panels that need removing, see attached photo.22/4/22 - Complete upgrade as per quote, tested and adjusted, all OK
MSA-DTWD | WA5306092 | 1 | AHS Services WA Pty Ltd (Anchor) | E'Cafe - has a blocked sinks and leaking into the cupboard and on the floor | Plumbing & Drainage | Drainage | 1371.81 | Pass | Fail | 0 | 2 | 387 | 2022-04-06 10:17 | 2022-04-07 17:00 | 2022-04-06 10:30 | 2022-04-07 17:00 | 2022-04-22 13:30 |  |  | Will need to return run waste to a drain. Completed
MSA-DTWD | WA5583309 | 2 | Protek 24/7 Building & Maintenance | Entry Foyer - water leak coming from ceiling - See notes below | Building | Ceiling | 1700.44 | Fail | Fail | 1 | 3 | 387 | 2022-07-04 11:39 | 2022-07-07 17:00 | 2022-07-11 10:00 | 2022-07-07 17:00 | 2022-07-27 13:00 |  | WACCES | repair roof leak reseal windows repair celling
MSA-DFES | WA6450359 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | North side carpark streetlight remains on - see notes | Electrical | General Electrical | 1390.29 | Pass | Fail | 0 | 2 | 386.5 | 2023-01-16 11:10 | 2023-01-19 17:00 | 2023-01-18 12:00 | 2023-01-19 17:00 | 2023-02-03 14:30 |  | WACCES
MSA-DTWD | WA5226970 | 2 | Equans Mechanical Services Australia | Building 5 - A357 - Evap cooler noisy on high speed | Air Conditioning | Room Air Conditioners | 881.17 | Pass | Fail | 0 | 2 | 386.1167 | 2022-03-14 16:51 | 2022-03-17 17:00 | 2022-03-15 10:00 | 2022-03-17 17:00 | 2022-03-31 12:07 |  |  | FAULTY SUMP DUMP AND PUMP
MSA-DTWD | WA6293836 | 1 | Damian Rak Electrical Pty Ltd | Mating Pen - faulty power point | Electrical | General Electrical |  | Pass | Fail | 0 | 2 | 385.75 | 2022-11-30 10:50 | 2022-12-01 17:00 | 2022-11-30 12:45 | 2022-12-01 17:00 | 2022-12-16 14:30 |  |  | Isolate, test, tag
MSA-DTAG | WA6108906 | 1 | Sapio Pty Ltd | The waiting room / bail reed switch is not working correctly and will need to be replaced | Security | Security Management System | 3575.99 | Fail | Fail | 1 | 3 | 385.5 | 2022-10-20 11:58 | 2022-10-21 17:00 | 2022-10-25 14:30 | 2022-10-21 17:00 | 2022-11-10 16:00 |  | WCAPPR | Installed new mortice lock and recabled
MSA-DFES | WA6503871 | 2 | ACTION GLASS & ALUMINIUM | Ground - Volunteers Front roller door -perspex in front volunteer engine bay roller door cracked | Glazing | Specialist Glass | 1249.53 | Pass | Fail | 0 | 2 | 384.5 | 2023-01-19 11:51 | 2023-01-24 17:00 | 2023-01-23 14:45 | 2023-01-24 17:00 | 2023-02-08 15:15
MSA-DCA | WA6509247 | 1 | Techworks Electrical | Festoon Lights are not working - Lighting control box is located in garden bed opposite Polly's | Electrical | Lighting, External | 916.665 | Pass | Fail | 0 | 2 | 384.5 | 2023-01-20 08:42 | 2023-01-23 17:00 | 2023-01-23 09:00 | 2023-01-23 17:00 | 2023-02-08 09:30
MSA-DCA | WA5692017 | 1 | Dormakaba Australia Pty Ltd | North entry automatic door-Door moulding/padding on edge of glass is missing | Building | Automatic Doors | 4333.96 | Pass | Fail | 0 | 2 | 384.15 | 2022-08-03 09:43 | 2022-08-04 17:00 | 2022-08-03 11:53 | 2022-08-04 17:00 | 2022-08-19 12:02 |  |  | 3/8/22 - On inspection, found clip edge damaged/broken due to vandalism overnight.Replaced faulty clip edge as required, tested unit, all ok19/8/22 - Removed existing faulty door equipment and replaced with new es200 locking upgrade kit as per quotation, setup and tested operation upon completion and left in good working order.
MSA-DTAG | WA5689182 | 2 | Australian HVAC Services Pty. Ltd. | Court 52 - Magistrate advised Court room is too warm, temperature check | Air Conditioning | Room Air Conditioners | 427.92 | Pass | Fail | 0 | 2 | 384 | 2022-08-02 11:23 | 2022-08-05 17:00 | 2022-08-03 08:30 | 2022-08-05 17:00 | 2022-08-19 08:30 |  |  | Attend site. Access bms and check operation of vav box serving court 52. Court 52 is served by VAV box 5.14. Check temps and found to be 22.5 degrees. Check operation of box, drive to min then max airflow and found to work as normal. Access court room and check calibration of wall sensor, ok. Monitor operation and found box working as normal. Box is supplying desired airflow and maintaining setpoint.
MSA-DFES | WA5880733 | 3 | ADVANCED LOCK & KEY | need to change the locks on the 2 x gates to gain access - see notes below | Security | Locksmith | 240 | Pass | Fail | 0 | 2 | 383.25 | 2022-09-15 16:22 | 2022-09-22 17:00 | 2022-09-20 13:45 | 2022-09-22 17:00 | 2022-10-06 13:00 |  |  | Cut off c4 padlock and replaced it with 50mm berg watcher combo
MSA-DTWD | WA6376047 | 3 | AWB Co. | Power point for Portable Profile Cutter not working. (3 phase) | Electrical | General Electrical | 1738.98 | Pass | Fail | 0 | 2 | 383 | 2022-12-15 12:44 | 2022-12-22 17:00 | 2022-12-19 13:30 | 2022-12-22 17:00 | 2023-01-04 12:30 |  | WACCES | Attended site signed in jsa completed. Installed changeover switch as site requested if replacing gpo. Put outlet near other machines as requested.Tested operationalJob completed
MSA-DTWD | WA5853861 | 3 | Equans Mechanical Services Australia | Investigate cavitation and faults Chiller 2 | Refrigeration | Chiller | 1536.43 | Pass | Fail | -1 | 1 | 382.9833 | 2022-09-12 11:40 | 2022-09-19 17:00 | 2022-09-12 11:56 | 2022-09-19 17:00 | 2022-09-28 10:55 |  |  | Requested to investigate knocking / vibrating sound in basement of B2. On investigation found source initially predominant in basement. Traced to chilled water pipes. Found the vibration was through the whole building from the plant room on level 5 to the basement level 1. From enquires this was not a new issues but one that had been occurring for approximately 10 years.Noted chilled water pipes vibrating and their movement noticeable to the eye of approximately 25 – 50 mm. Traced pipe vibration and movement along pipes to basement plants rooms and up pipe ducts to plant room, where it was also noticeable.Investigated pumps. Investigated if air in system.As part of maintenance, coupling and elements were checked for wear and movement. These were replaced as part of this job for maintenance reasons and also that they may impact on the noise / vibration from the pumps. This did have an minor impact on the frequency of the pump noise near the pump but did not eliminate the problem.
MSA-DFES | WA5199518 | 3 | Protek 24/7 Building & Maintenance | Outside Operational Delivery - Pavers need fixing, locations listed below | Paving & Roadworks | Paving | 1812.5 | Pass | Fail | -1 | 1 | 382.5 | 2022-03-01 10:01 | 2022-03-09 17:00 | 2022-03-01 13:00 | 2022-03-09 17:00 | 2022-03-17 11:30 |  | WACCES | Fixed Pavers
MSA-DTWD | WA5304145 | 2 | Falcetta Plumbing and Gas | Block 7 - Ground - Male Toilet - L/H urinal flush button not working | Plumbing & Drainage | Toilets/Cisterns | 964.45 | Pass | Fail | 0 | 2 | 382 | 2022-04-04 15:09 | 2022-04-07 17:00 | 2022-04-06 15:00 | 2022-04-07 17:00 | 2022-04-22 13:00 |  |  | replaced urinal cistern and button assembly
MSA-DTAG | WA5303403 | 1 | Sapio Pty Ltd | Level 6 - Room 6.01, 6.02, and 6.03 - see notes below | Security | Access Control | 2230.18 | Pass | Fail | 0 | 2 | 381.75 | 2022-04-04 09:54 | 2022-04-05 17:00 | 2022-04-05 13:00 | 2022-04-05 17:00 | 2022-04-21 10:45 |  |  | Work performed by Drake Van der Merwe (05/04/2022)Attended site. Found doors handles bouncing and unlocking intermittently. 3 x mortice locks required.Work performed by Drake Van der Merwe (19/04/2022):Replaced lock on Level 6 - Rooms 6.01 & 6.02, confirmed correct operation of mortice locks.Could not replace Room 6.03 lock as handle ring is stuck. Need to return with special tool.Work performed by Drake Van der Merwe (21/04/2022):Replaced lock on Level 6 - Room 6.03, confirmed correct operation of mortice lock.
MSA-DTWD | WA5627864 | 2 | AWB Co. | F Block - Outside F38 in corridor - Diffuser in skylight fell to ground and disintegrated | Electrical | Lighting, Internal | 403.9175 | Pass | Fail | 0 | 2 | 381.75 | 2022-07-15 08:39 | 2022-07-20 17:00 | 2022-07-18 13:15 | 2022-07-20 17:00 | 2022-08-03 11:00 |  | WACCES | Attended site signed in jsa completed. Found skylight broken. Put new diffuser in that was on order. Secured and safeJob completed
MSA-DFES | WA5961913 | 1 | Protek 24/7 Building & Maintenance | Ground Floor - Internal door stair 2 - Door handle is coming off | Building | Doors | 295.13 | Pass | Fail | 0 | 2 | 381.25 | 2022-09-19 10:52 | 2022-09-20 17:00 | 2022-09-19 15:00 | 2022-09-20 17:00 | 2022-10-05 12:15 |  | WACCES | Install new door handle
MSA-DTWD | WA6431059 | 2 | Techworks Electrical | Lecture Theater 1&2 interior side wall lights not working | Electrical | Lighting, Internal | 1506.135 | Pass | Fail | 0 | 2 | 381 | 2023-01-13 11:44 | 2023-01-18 17:00 | 2023-01-16 13:00 | 2023-01-18 17:00 | 2023-02-01 10:00
MSA-DCA | WA5993656 | 1 | ADVANCED LOCK & KEY | Old Gaol - External area, corner of Francis/Beaufort St - Electrical box lock is faulty - see notes | Security | Locksmith | 495 | Pass | Fail | 0 | 2 | 380.75 | 2022-10-05 11:39 | 2022-10-06 17:00 | 2022-10-05 15:55 | 2022-10-06 17:00 | 2022-10-21 12:40 |  | WACCES | Installed EVVA cam lock picked up from commercial locksmiths on electrical box on the corner of Francis and Beaufort st and modified the cam. 1x EVVA cam lock
MSA-DFES | WA5697735 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level 2 - Upstairs Northern Firefighters Bathroom - The hot water only luke warm - see notes | Electrical | General Electrical | 536.52 | Pass | Fail | 0 | 2 | 379.5 | 2022-08-09 11:33 | 2022-08-10 17:00 | 2022-08-09 14:30 | 2022-08-10 17:00 | 2022-08-25 10:00 |  | WCAPPR | Test various taps and found the bathrooms down stairs and upstairs did not have hot water. There was a circuit breaker off for one of the hot water units I turned the circuit breaker back on. There are 4 circuit breakers in the switchboard they all had 240 volts going out. I also did a load test three circuit breakers were only drawing 0.2 amps one was drawing 9 amps. I tired to find booster switches but could not find any and the staff on site did not know of any. Recommend sending some who specialise in solar hot water units they they can all be checked. To get access will need roof access gear and a extension ladder.The hot work may be back on after I re set the circuit breaker it may just take a day for the water to heat up. If we call them we can ask if the hot water is back.Complete
MSA-DCA | WA5695115 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Steam plant low level alarm | Plumbing & Drainage | Water | 259.01 | Pass | Fail | 0 | 2 | 371.5167 | 2022-08-06 21:16 | 2022-08-06 23:16 | 2022-08-06 23:15 | 2022-08-07 01:16 | 2022-08-22 10:46 |  | WACCES | Attended after hours call out and signed in. Enter plant room and find steam generators 1 & 2 on low water alarm. Found RO plant on low water pressure alarm. Found RO system offline, demineralised water tanks empty and demineralised water pump off. Isolate steam generators while RO system faults are identified. Carry out several tests and checks. Identified low incoming mains water pressure. Isolate water and remove 4x sediment filters. Found sediment filters blocked causing low water pressure and plant failures.Replace 4x sediment filters with site spares. Bleed air from system and remove water isolations. Check for leaks on sediment filter housings. All ok. Open RO bypass valve to quick fill the demineralised water tanks while fault finding is carried out. Checked over RO system and reset low water pressure alarm. Energised RO system and ran. RO system running and filling the water tanks as required. Identified two small water leaks on the RO system, 1 on a product flow indicator a
MSA-DTWD | WA5481470 | 1 | Techworks Plumbing | Water board has notified use that we have a water leak somewhere on Campus | Plumbing & Drainage | Water | 1838.69 | Pass | Fail | 0 | 2 | 370 | 2022-05-30 13:08 | 2022-05-31 17:00 | 2022-05-31 05:30 | 2022-05-31 17:00 | 2022-06-15 15:30 |  | WACCES | attended site, the cleaner opened the gate for us once we got there,located the water metre and inspection shaft had a look to see if there was any water running through the inspection shaft we couldn’t see any.we inspected each plumbing fixture for leaks then we proceeded to isolated different parts of the building and checking the water metre, to try find an approximate location of the leak, after Isolating every building and valve we could we found the water metre to constantly be running the whole time .a leak detector will be neededcreated a dilapidation report and signed out (see attached service report)completed paperwork Returned 15/6 and fixed leak.
MSA-DTWD | WA5495382 | 2 | JEM Carpentry | House 806 - Front veranda ballestrade faulty | Building | General Building |  | Fail | Fail | 22 | 25 | 369.5 | 2022-06-08 11:43 | 2022-06-13 17:00 | 2022-11-17 08:00 | 2022-06-13 17:00 | 2022-12-02 17:30 |  |  | replaced railings
MSA-DTAG | WA6540873 | 3 | Australian HVAC Services Pty. Ltd. | Basement - A/C drain pipe is leaking outside after hours security room | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1033.27 | Pass | Fail | 0 | 2 | 368 | 2023-02-09 15:31 | 2023-02-16 17:00 | 2023-02-13 08:00 | 2023-02-16 17:00 | 2023-02-28 16:00
MSA-DFES | WA4993473 | 1 | Australian HVAC Services Pty. Ltd. | Level 3 - Plant Room - BMS system advises chiller flow fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2253.23 | Fail | Fail | 1 | 3 | 367.9992 | 2022-01-07 14:33 | 2022-01-10 17:00 | 2022-01-18 07:34 | 2022-01-10 17:00 | 2022-02-02 15:34 |  | WACCES | Replaced both condenser water flow switches on chillers. Confirmed correct operation of both chillers and flow switches.
MSA-DTWD | WA6008510 | 2 | SCAVENGER SUPPLIES PTY LTD | faulty fire alarm speaker in F010 - see notes below | Fire Protection Services | Fire Protection - Monitor System | 622.78 | Pass | Fail | 0 | 2 | 366.6667 | 2022-10-11 15:54 | 2022-10-14 17:00 | 2022-10-12 08:20 | 2022-10-14 17:00 | 2022-10-27 15:00 |  | WACCES | 12/10/22 KR- attended P2 call outFURTHER INSTALLATION OF NEW SPEAKER TO F10- PARTS ON ORDERCompleted 27/10/2022
MSA-DTWD | WA5487377 | 3 | AWB Co. | Carpark 2 - Various Lights out | Electrical | Lighting, External | 587.89 | Pass | Fail | 0 | 2 | 366 | 2022-06-01 14:34 | 2022-06-09 17:00 | 2022-06-07 09:30 | 2022-06-09 17:00 | 2022-06-22 15:30 |  | WACCES | Attended site and signed in. Completed JSA. Located light pole needing pole top. Supply and replace with new led pole top supplied by site and installed reducer to top of pole. Connected up and tested all okay. Signed out. Job complete
MSA-DTWD | WA6132535 | 3 | Equans Mechanical Services Australia | Chiller plant room - chillers 2 and 3 in fault ( bad modus comms ) | Refrigeration | Chiller | 1067.37 | Pass | Fail | -1 | 2 | 365 | 2022-10-31 15:01 | 2022-11-07 17:00 | 2022-11-03 07:00 | 2022-11-07 17:00 | 2022-11-18 12:00 |  |  | ATTENDED SITE, INVESTIGATED CHILLER 2&3 TRIPPED OFF BECAUSE OF POWER SURGE. TRIEDTO RESET CHILLER BUT NO LUCK. CALLED AIRVISION AND CAME OUT AND FIXED THE PROBLEM.ALL OK.
MSA-DTWD | WA6526772 | 3 | AWB Co. | 5 x lights out | Electrical | Lighting, Internal | 2685.125 | Pass | Fail | 0 | 2 | 365 | 2023-02-01 10:44 | 2023-02-08 17:00 | 2023-02-08 10:00 | 2023-02-08 17:00 | 2023-02-23 15:00
MSA-DCA | WA6385712 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Ground - Epoch Cafe - Investigate BMS alarm - see notes | Building | General Building | 146.4 | Pass | Fail | -1 | 1 | 363.5 | 2022-12-21 09:57 | 2022-12-28 17:00 | 2022-12-21 12:00 | 2022-12-28 17:00 | 2023-01-05 15:30 |  |  | Attended site on the 21st Dec and was shown the wrong unit. Didn't see any faults. Engaged Honeywell to check over alarms. Revisited site. The job is for a Zip hydrotap unit. Unit is faulting on condenser overtemp in the peak times due to heavy usage when filling water jugs. Doesn't seem to be enough ventilation in cabinet. Job requires plumbers to attend and investigate Zip hydrotap. Completed paperwork Barcode number on unit A41191442F
MSA-DTAG | WA5204474 | 3 | Gilmour & Jooste Electrical | Court Registry - lights need replacing | Electrical | General Electrical | 4098.65 | Pass | Fail | 0 | 2 | 363 | 2022-03-04 10:56 | 2022-03-14 17:00 | 2022-03-14 11:00 | 2022-03-14 17:00 | 2022-03-29 14:00 |  | WCAPPR | Lighting repairs
MSA-DTWD | WA6155520 | 2 | Precise Air Group | Multiple A/C complaints from Staff and students - Faulty AC - See notes below | Air Conditioning | Room Air Conditioners | 253.38 | Pass | Fail | 0 | 2 | 363 | 2022-11-08 11:13 | 2022-11-11 17:00 | 2022-11-08 13:00 | 2022-11-11 17:00 | 2022-11-23 16:00 |  |  | attended site and found ahu/fcu 8 cooling call staying on 100% when rooms are well under set point and also when set pointvit adjusted well into heating and heating call is enabled. actuator in chilled water pipework appears to drive freely when manually worked but will not change on bms. controls tech required to assess.
MSA-DTWD | WA6155546 | 2 | Precise Air Group | Room B9 - Faulty AC - See notes below | Air Conditioning | Room Air Conditioners | 253.38 | Pass | Fail | 0 | 2 | 363 | 2022-11-08 11:17 | 2022-11-11 17:00 | 2022-11-08 13:00 | 2022-11-11 17:00 | 2022-11-23 16:00 |  |  | attended site and found ahu/fcu 8 cooling call staying on 100% when rooms are well under set point and also when set pointvit adjusted well into heating and heating call is enabled. actuator in chilled water pipework appears to drive freely when manually worked but will not change on bms. controls tech required to assessworks to be complete on WA5995565
MSA-DTWD | WA6537460 | 1 | WESTERN IRRIGATION PTY LTD | Main bore near Simpson Ave - Remote controller for bore has weak signal, maybe a loose wire | Electrical | General Electrical | 1510 | Pass | Fail | 0 | 2 | 362.5 | 2023-02-07 09:29 | 2023-02-08 17:00 | 2023-02-07 10:00 | 2023-02-08 17:00 | 2023-02-22 12:30
MSA-DTWD | WA6125771 | 3 | AWB Co. | 5 x lights faulty | Electrical | Lighting, Internal | 1477.18 | Pass | Fail | 0 | 2 | 362.25 | 2022-10-25 08:19 | 2022-11-01 17:00 | 2022-11-01 08:45 | 2022-11-01 17:00 | 2022-11-16 11:00 |  | WACCES | Attended site and signed in. Completed JSA. located faulty lighting in various locations. Went to wholesaler for parts. Returned to site. Replaced faulty tubes, starters and tombstones as per list. Need to return to do a classroom that had class in. Have also ordered diffusers and sent email to wholesaler with specifications to be delivered to office, lead time 14days. Took pics. Completed paperwork. Signed out.Follow up required
MSA-DTWD | WA5583437 | 3 | Boilertronics | Boiler 1 tripped | Mechanical Services | Boilers | 705.07 | Pass | Fail | -1 | 1 | 362.0167 | 2022-07-04 12:30 | 2022-07-11 17:00 | 2022-07-06 11:34 | 2022-07-11 17:00 | 2022-07-21 13:35 |  | WACCES | Travel to site.Checked over hotwater unit, found main control to have no power, checked over temp switch and it had tripped. Resetand monitored boiler while checking over boiler 1.Boiler requires new 1” flow switchReturn to site and replace flow switch
MSA-DCA | WA5306246 | 2 | Protek 24/7 Building & Maintenance | G Block - Bench slat repair/replacement | Building | General Building | 575.96 | Pass | Fail | -1 | 2 | 362 | 2022-04-06 11:31 | 2022-04-11 17:00 | 2022-04-07 13:00 | 2022-04-11 17:00 | 2022-04-22 15:00 |  | WACCES | Repair bench slat
MSA-DTWD | WA5583445 | 3 | Boilertronics | Boiler 2 in fault | Mechanical Services | Boilers | 705.07 | Pass | Fail | -1 | 1 | 362 | 2022-07-04 12:33 | 2022-07-11 17:00 | 2022-07-06 11:40 | 2022-07-11 17:00 | 2022-07-21 13:40 |  | WACCES | Checked over hot water unit 1Found it to already be running.Monitored unit and noticed it intermittently switching off, opened flow switch found it to be a bit sticky. Freed up as best Icould. unit requires replacement 1” flow switch.Return to site 14/7/2022 - Replace Flow Switch and Test
MSA-DTWD | WA6130846 | 3 | SCAVENGER SUPPLIES PTY LTD | Foyer-Faulty PA speaker | Fire Protection Services | Fire Protection - Monitor System | 429.855 | Pass | Fail | -1 | 2 | 362 | 2022-10-28 16:34 | 2022-11-04 17:00 | 2022-10-31 12:00 | 2022-11-04 17:00 | 2022-11-15 14:00 |  | WACCES | First initial visit 31/10/2022 - Waiting on Parts Second visit 15/11/22
MSA-DTWD | WA4993478 | 2 | Precise Air Group | Q-Block chiller not cooling and has a coms error | Air Conditioning | Room Air Conditioners | 4227.79 | Pass | Fail | 0 | 2 | 361.6667 | 2022-01-07 14:37 | 2022-01-12 17:00 | 2022-01-10 13:30 | 2022-01-12 17:00 | 2022-01-25 15:10 |  |  | Installed the CCN gateway inside the control panel of chiller 2 and connected both chillers on one CCN bus.Configured the gateway based on the required BACnet points that have been handled by the NRP technician. Forsome reason, the BMS couldn’t communicate with the gateway on the BACnet MS/TP configuration. So, we had tomove the gateway to the MSSB panel and run the CCN bus from the chillers to the MSSB. The gateway wasconfigured to work on BACnet IP and successfully communicated with the BMS. The NRP technician discovered allthe points and remapped the enable points for both chillers for testing and both chillers ran successfully.
MSA-DFES | WA5692073 | 0 | Australian HVAC Services Pty. Ltd. | Air con is very cold check BMS the heating hasn’t kicked off. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1029.86 | Pass | Fail | 0 | 2 | 361.5411 | 2022-08-03 10:09 | 2022-08-03 12:09 | 2022-08-03 10:59 | 2022-08-03 14:09 | 2022-08-18 12:31 |  |  | Attended site with mizco and inspected ahu 5 warm-up mode operation. Mizco advised the warm up mode is operating correctly and on the day it had not reached the warm-up mode cutoff temperature in the zone. Accessed vav 5.1.1 and isolated power. Replaced the solid state relay. Reinstated and confirmed heater operation. Confirmed all operating ok. Will monitor and raise setpoints if required on maintenance.
MSA-DFES | WA5677401 | 1 | Protek 24/7 Building & Maintenance | L1 Workshop Welding Bay-roof leak - see notes | Roofing | Metal Roofing | 780.78 | Pass | Fail | 0 | 2 | 361.5 | 2022-07-25 14:20 | 2022-07-26 17:00 | 2022-07-26 10:00 | 2022-07-26 17:00 | 2022-08-10 11:30 |  | WACCES | Replaced broken polycarbonate wall sheet
MSA-MRWA | WA6128273 | 3 | AWB Co. | Admin / kitchen / hallway - Repair various faulty lights | Electrical | Lighting, Internal | 959.515 | Pass | Fail | 0 | 2 | 361.5 | 2022-10-26 14:13 | 2022-11-02 17:00 | 2022-11-01 10:30 | 2022-11-02 17:00 | 2022-11-16 12:00 |  |  | Attended site signed in jsa completed. Replaced 4 ballast 4 globes and 1 led panel in buildingTested operational.Job completed
MSA-DTWD | WA6191345 | 2 | COMMERCIAL PLUMBING AND GAS | Faulty cistern - Full flush not working. Half flush – button slow to release | Plumbing & Drainage | Toilets/Cisterns | 3298.795 | Pass | Fail | -1 | 2 | 361.5 | 2022-11-16 15:32 | 2022-11-21 17:00 | 2022-11-17 17:30 | 2022-11-21 17:00 | 2022-12-02 19:00 |  |  | installed new care suite
MSA-DTWD | WA6518581 | 3 | Australian HVAC Services Pty. Ltd. | AC not working | Air Conditioning | Package | 1935.11 | Pass | Fail | 0 | 2 | 361.5 | 2023-01-25 09:38 | 2023-02-02 17:00 | 2023-02-02 14:30 | 2023-02-02 17:00 | 2023-02-17 16:00
MSA-DTWD | WA5578411 | 2 | Equans Mechanical Services Australia | Airconditioning AHU D2 not working (showing Fan Status Fault) | Air Conditioning | Room Air Conditioners | 452.2975 | Pass | Fail | 0 | 2 | 361.25 | 2022-07-01 11:30 | 2022-07-06 17:00 | 2022-07-04 14:15 | 2022-07-06 17:00 | 2022-07-19 15:30 |  | WACCES | INSTALLED PART - OK
MSA-DTWD | WA5790357 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 1 - 146b male Toilet area - Water leak under the trough - please see further notes below | Plumbing & Drainage | Water | 1269.7875 | Pass | Fail | 0 | 2 | 361 | 2022-08-22 10:09 | 2022-08-25 17:00 | 2022-08-22 13:30 | 2022-08-25 17:00 | 2022-09-06 14:30 |  |  | Attended site to investigate fault. Located source of leak, searched for isolation valve, replaced mixer tap with new, replaced rubbers in pipework, reinstated water and tested all work ok.
MSA-DTAG | WA5982829 | 3 | Midolo Building Services | Judicial Carpark door to Irwin Street - Door loose/slack - see notes below | Building | Doors | 670.62 | Pass | Fail | 0 | 2 | 361 | 2022-09-30 14:56 | 2022-10-07 17:00 | 2022-10-04 10:30 | 2022-10-07 17:00 | 2022-10-19 11:30 |  | WACCES | door repaired - new seals installed
MSA-DTWD | WA6600938 | 2 | AWB Co. | West end Wall - Flood light out | Electrical | Lighting, External | 1372.56 | Pass | Fail | 0 | 2 | 361 | 2023-02-17 09:56 | 2023-02-22 17:00 | 2023-02-21 10:30 | 2023-02-22 17:00 | 2023-03-08 11:30 |  | WACCES
MSA-DCA | WA5017146 | 3 | Techworks Electrical | Reception - faulty lights and faulty transformer - see notes below | Electrical | General Electrical | 674.74 | Pass | Fail | 0 | 2 | 361 | 2022-01-13 10:51 | 2022-01-20 17:00 | 2022-01-17 07:00 | 2022-01-20 17:00 | 2022-02-01 08:00 |  | WACCES | Rectified faulty lighting
MSA-DTWD | WA5793629 | 3 | Equans Mechanical Services Australia | Boiler going into fault | Mechanical Services | Boilers | 1481.85 | Pass | Fail | -1 | 1 | 361 | 2022-08-24 09:01 | 2022-08-31 17:00 | 2022-08-24 11:30 | 2022-08-31 17:00 | 2022-09-08 12:30 |  |  | Check over boiler found it in fault at start of sequence in LFL, reset unit went full cycle andfired up stopped and started found boiler to fault intermittently in all different parts of thesequence. Pulled out QRA2 reset unit, QRA2 occasionally flashed, replaced with newfired up boiler.Stopped and started unit and it fired up each time without fail.
MSA-DFES | WA5081154 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Pump Room - Engine Bay - lights are flickering and causing RCD to trip - see notes below | Electrical | General Electrical | 543.56 | Pass | Fail | 0 | 2 | 360.75 | 2022-01-20 11:27 | 2022-01-21 17:00 | 2022-01-20 13:15 | 2022-01-21 17:00 | 2022-02-04 14:00 |  |  | Arrived on site and proceeded to main SB. Found RCDs had been reset. Unable to recreate fault as issue only occurs intermittently. Investigated flickering light and found floodlight that needs replace. Will need to return with replacement fitting.
MSA-DTWD | WA5308053 | 3 | AWB Co. | D111 - Jewellery Workshop - Blown tubes & globes | Electrical | General Electrical | 884.5 | Pass | Fail | 0 | 2 | 360.75 | 2022-04-08 08:40 | 2022-04-19 17:00 | 2022-04-19 12:15 | 2022-04-19 17:00 | 2022-05-04 13:00 |  | WACCES | Attended site and signed in , completed jsa,spoke with fm about job, went to b4 and removed old diffusers , trimmed up new diffusers to fit lights, installed new diffusers, packed up , cleaned up, completed paperwork,signed outJob complete
MSA-DTWD | WA5107788 | 1 | AWB Co. | U024.8 - Power points constantly tripping | Electrical | General Electrical | 1745.45 | Pass | Fail | 0 | 2 | 360.5 | 2022-02-08 09:25 | 2022-02-09 17:00 | 2022-02-09 11:15 | 2022-02-09 17:00 | 2022-02-24 11:45 |  | WCAPPR | Attended site, signed in,reviewed JSA, called cleaner to let us in u block , shut down dB and installed rcd with cable going into jbox above , re energised and tested rcd, rcd working as intended, ran cable from dB to pendant GPOs located in room 24, isolated circuits and wired new feed into pendants, re energised and tested pendants , replaced remaining contactors that were damaged in isolation box and then tested operation of power in room , found that it was still cutting in and out, tacked 24v control circuit to ventilation fan in roof and found a pressure sensor, , this was causing circuits to cut out, removed old filters (filters very full and dirty)and tested circuits, circuits now working as intended , spoke to fm and he agreed to monitor the circuits over the next 2-3 weeks. Everything now working as intended , completed paperwork, packed up **Job completed**
MSA-DTWD | WA5687345 | 2 | Protek 24/7 Building & Maintenance | Roof leak – dripping through 3rd light fitting from left corner - See notes below | Roofing | Metal Roofing | 999.99 | Pass | Fail | 0 | 2 | 360.5 | 2022-08-01 16:32 | 2022-08-04 17:00 | 2022-08-03 08:30 | 2022-08-04 17:00 | 2022-08-18 09:00 |  | WCAPPR | Sealed openings between ridge & sheets, re fixed down screws
MSA-DTAG | WA5495605 | 3 | Sapio Pty Ltd | Custody Centre - Ground - Cell 2 & 4 - tv units have stopped working | ICT/Audiovisual | Hardware / Equipment | 800.71 | Pass | Fail | -1 | 1 | 360.25 | 2022-06-08 13:24 | 2022-06-15 17:00 | 2022-06-09 08:45 | 2022-06-15 17:00 | 2022-06-24 09:00 |  |  | Supplied and installed 2 x monitor/TV in cells 2 and 4, tested, OK.
MSA-DTWD | WA5697430 | 1 | Equans Mechanical Services Australia | A & L block - rooms AG06 & LG03-no heating | Air Conditioning | Room Air Conditioners | 1379.077 | Pass | Fail | 0 | 2 | 360.25 | 2022-08-09 09:23 | 2022-08-10 17:00 | 2022-08-09 11:45 | 2022-08-10 17:00 | 2022-08-24 12:00 |  |  | Arrived on site signed in, checked in with Janine gathered tools and equipment. Assisted Jeff from icon logic with Block LG room temps. Found outside air fan not correct operation. Set and continued with investigation. Found other issues. Jeff to complete report and send information through suggestions to improve operation. Cleaned up and completed paperwork.
MSA-DTWD | WA5656239 | 3 | AWB Co. | water leaking through disconnected light fitting | Roofing | Metal Roofing |  | Pass | Fail | -1 | 1 | 360.2 | 2022-07-18 12:38 | 2022-07-25 17:00 | 2022-07-18 13:21 | 2022-07-25 17:00 | 2022-08-02 13:33 |  |  | As discussed with Steve yesterday can we please get permission to close out the below work orders with costs to date as they are recurring issues to the waterproofing to the balcony which we have priced over the years; WA5656239WA5397017WA5589490
MSA-DTAG | WA5686520 | 0 | Midolo Building Services | Outside Court 5 - Public waiting area - Roof Leak - Square ceiling tiles are at risk of caving in | Roofing | Metal Roofing | 466.69 | Pass | Fail | 0 | 2 | 360 | 2022-08-01 09:02 | 2022-08-01 11:02 | 2022-08-01 09:30 | 2022-08-01 13:02 | 2022-08-16 09:30 |  | WCAPPR | LEAK REPAIRED & CEILING TILES REPLACED
MSA-DTWD | WA5673426 | 2 | Protek 24/7 Building & Maintenance | Possible Roof Leak - See notes below | Roofing | Metal Roofing | 1113.87 | Pass | Fail | -1 | 2 | 359.75 | 2022-07-20 15:09 | 2022-07-25 17:00 | 2022-07-21 12:00 | 2022-07-25 17:00 | 2022-08-05 11:45 |  | WACCES | Fix new tek screws in joins of flashing , clean and re seal joins on dry pan flashing
MSA-DTWD | WA5208471 | 3 | AHS Services WA Pty Ltd (Anchor) | A Block - A311 - Repair Tap to Fume Hood 3 | Plumbing & Drainage | Materials | 720.95 | Pass | Fail | -1 | 1 | 359.25 | 2022-03-09 08:56 | 2022-03-16 17:00 | 2022-03-10 10:15 | 2022-03-16 17:00 | 2022-03-25 09:30 |  | WACCES | Inspected tap issue, serviced isolation valve, removed tap found debris in line and calcium build up in in tap, unable to clear out as sealed, new tap ordered.Collected new tap accessed site, isolated and replaced tap tested all good
MSA-DTWD | WA5691806 | 2 | Protek 24/7 Building & Maintenance | E65 Restaurant Dining - Roof leak - See notes below | Roofing | Metal Roofing | 763.49 | Pass | Fail | -1 | 1 | 359.25 | 2022-08-03 08:09 | 2022-08-08 17:00 | 2022-08-03 11:45 | 2022-08-08 17:00 | 2022-08-18 11:00 |  | WCAPPR | Re-sealed flashing
MSA-DTWD | WA6431423 | 2 | AHS Services WA Pty Ltd (Anchor) | Ladies toilets- Hot water unit not working | Plumbing & Drainage | HWS/Units Electric & Gas | 436.18 | Fail | Fail | 0 | 2 | 359 | 2023-01-13 14:17 | 2023-01-18 17:00 | 2023-01-19 10:30 | 2023-01-18 17:00 | 2023-02-03 09:30
MSA-DFES | WA6532150 | 2 | ACTION GLASS & ALUMINIUM | Main Appliance Room – Murray St Side - Broken Glass in Bay Door Window - See Notes | Glazing | Window Glass | 656.67 | Pass | Fail | 0 | 2 | 359 | 2023-02-03 15:41 | 2023-02-08 17:00 | 2023-02-06 13:00 | 2023-02-08 17:00 | 2023-02-21 12:00
MSA-DTAG | WA5390014 | 3 | Sapio Pty Ltd | Custody - TV in Cell 1 is not working | ICT/Audiovisual | General AV works | 430.74 | Pass | Fail | -1 | 1 | 358.8667 | 2022-05-02 09:38 | 2022-05-09 17:00 | 2022-05-02 09:38 | 2022-05-09 17:00 | 2022-05-17 08:30 |  |  | Replaced TV, tuned TV, all channels tested OK.
MSA-DFES | WA5971710 | 2 | MALCO FLOORING PTY LTD | Ground floor - Outside Stairwell 4 - Mat is damaged outside in courtyard off stairwell floor | Flooring | Carpet | 125.7 | Pass | Fail | 0 | 2 | 358.75 | 2022-09-20 15:49 | 2022-09-23 17:00 | 2022-09-22 10:00 | 2022-09-23 17:00 | 2022-10-07 08:45 |  |  | Restuck matting edge
MSA-DTWD | WA5471292 | 2 | Protek 24/7 Building & Maintenance | Level 4 -Western Stairwell - Roof leak onto landing between L3 and L4 – North corner | Roofing | Metal Roofing | 704.25 | Pass | Fail | 0 | 2 | 358.25 | 2022-05-23 12:38 | 2022-05-26 17:00 | 2022-05-26 15:00 | 2022-05-26 17:00 | 2022-06-10 13:15 |  |  | Investigate roof leak - Level 4 -Western Stairwell - Roof leak onto landing between L3 and L4 – North corner
MSA-DTWD | WA5676872 | 3 | AWB Co. | Level 4 - East Fire Stairs - 2 x lights failed with burned and cracked wiring | Electrical | Lighting, Internal | 956.6275 | Pass | Fail | -1 | 2 | 358 | 2022-07-25 11:10 | 2022-08-01 17:00 | 2022-07-28 10:15 | 2022-08-01 17:00 | 2022-08-12 08:15 |  | WACCES & WCAPPR | Attended site and signed in, completed jsa,spoke with fm about job, walked 12ft ladder up 4 flights of stairs to faulty fitting , isolated lighting and removed old light, mounted new light , mounted emergency light to side of fitting, re Energised circuit and tested light, light working as intended , packed up, cleaned up, completed paperwork, signed out, job completed
MSA-DTWD | WA5306244 | 3 | AWB Co. | S Block - S123 - Clean diffusers and re tube broken lights | Electrical | General Electrical | 999.7 | Pass | Fail | -1 | 1 | 357.75 | 2022-04-06 11:28 | 2022-04-13 17:00 | 2022-04-06 12:00 | 2022-04-13 17:00 | 2022-04-21 09:45 |  | WACCES & WCAPPR | Attended site and signed in. Completed JSA. Spoke to fm about job. Located room with faulty light fitting. Pulled light fitting down. Wired in new LED driver and replaced panel. Panel now working as intended. Packed and cleaned up. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5993377 | 3 | Schneider Electric Australia Pty Ltd | Fire exit door 116 - Access control for door116 has no power and door not locking | Security | Access Control |  | Pass | Fail | -1 | 1 | 357.75 | 2022-10-05 10:04 | 2022-10-12 17:00 | 2022-10-05 10:15 | 2022-10-12 17:00 | 2022-10-20 08:00 |  |  | Completed
MSA-DTAG | WA5494055 | 0 | Sapio Pty Ltd | Level 4 - Room 404 - camera is faulty | Security | CCTV Surveillance | 1287.86 | Pass | Fail | 0 | 2 | 357.65 | 2022-06-07 12:20 | 2022-06-07 14:20 | 2022-06-07 12:21 | 2022-06-07 16:20 | 2022-06-22 10:00 |  | WACCES | Remove faulty camera, replaced with AXIS camera, programmed and commissioned.
MSA-DTWD | WA6675981 | 1 | Australian Airconditioning Services Pty Ltd | Room 8F2 - Condensation water flooding plantroom | Air Conditioning | Ducted Split System |  | Pass | Fail | 0 | 2 | 357 | 2023-02-28 10:58 | 2023-03-01 17:00 | 2023-02-28 11:30 | 2023-03-01 17:00 | 2023-03-15 08:30
MSA-DTAG | WA5800500 | 1 | Australian HVAC Services Pty. Ltd. | Level 1 - Courtroom 1 - Airconditioning is too warm in Courtroom 1 | Air Conditioning | Room Air Conditioners | 2428.84 | Pass | Fail | 0 | 2 | 356.5 | 2022-08-31 10:32 | 2022-09-01 17:00 | 2022-08-31 12:00 | 2022-09-01 17:00 | 2022-09-15 08:30 |  | WCAPPR | Attend site with Carrier. Access roof and check operation of HPWU5. Carrier logged in and checked faults. Common fault freeze protection. Freeze protection set to 1.1 degrees. Run unit and check operation. Found unit to work as normal. Found unit supply water temp to go way below setpoint. Carrier said this had something to do with the logic. Also the bypass valve is located very close to unit 5 and and possibly cold water coming back before bypass valve has time to shut. Best option for now is to increase the supply water temp setpoint. Check transducer fault on HPWU3. Found possible bad connection on printed circuit board due to a broken clip. Further DAS to be raised for work order relating to HPWU3 (SEPARATE WORK ORDER)
MSA-DTWD | WA5838016 | 2 | BAKE-QUIP PTY LTD | ground - Cafeteria kitchen - Dishwasher faulty, not completing wash cycles. | Electrical | General Electrical | 655.8 | Pass | Fail | 0 | 2 | 355.5 | 2022-09-08 10:21 | 2022-09-13 17:00 | 2022-09-13 14:30 | 2022-09-13 17:00 | 2022-09-28 10:00 |  |  | REFER TO SERVICE REPORTS
MSA-DTWD | WA6113439 | 1 | Australian Airconditioning Services Pty Ltd | Horizontal Display Fridge fault – Trips breaker when turned on | Refrigeration | Refrigerators | 1881.46 | Pass | Fail | 0 | 2 | 354.75 | 2022-10-24 11:39 | 2022-10-25 17:00 | 2022-10-24 13:45 | 2022-10-25 17:00 | 2022-11-08 08:30 |  |  | complete
MSA-DTWD | WA6578508 | 2 | AWB Co. | Fluro lights not working - Rooms S108/S115/S121 | Electrical | Lighting, Internal | 637.0125 | Pass | Fail | -1 | 2 | 353.75 | 2023-02-15 09:52 | 2023-02-20 17:00 | 2023-02-16 14:45 | 2023-02-20 17:00 | 2023-03-03 08:30
MSA-DTWD | WA5099136 | 1 | Total Security Systems Pty Ltd | T Block - Ground Level - alarm system - see details below | Security | Monitoring | 735 | Pass | Fail | 0 | 2 | 353.25 | 2022-02-01 14:56 | 2022-02-02 17:00 | 2022-02-01 16:00 | 2022-02-02 17:00 | 2022-02-16 09:15 |  |  | 1/2/2022 - Jose Pereira - 4pm to 4.30pmFaulty PIR in massage area. I have shunted the input and replacement needed.Need to provide training as new staff have taken over and aren't familiar with the system. 14/2/2022 - Michael Higginbotham - 12.30pm to 2pmCompleted onsite training with staff, checked PIR believed to be the faulty device, working correctly. Device located in massage room currently occupied with class will need to reattend site to access room when free.16/2/2022 - Michael Higginbotham - 7.15am to 9.15amReplaced faulty PIR, Fault fixed job complete.
MSA-DFES | WA6001065 | 2 | AWB Co. | Ground - Duty Room - Duty room fire door has a split again at the latch part of the door. | Building | Doors | 181.575 | Pass | Fail | 0 | 2 | 344.5 | 2022-10-10 12:12 | 2022-10-13 17:00 | 2022-10-13 07:00 | 2022-10-13 17:00 | 2022-10-27 15:30 |  |  | Inspect and measure door ready for replacementBRAF declined
MSA-DTAG | WA5981853 | 3 | Australian HVAC Services Pty. Ltd. | Victim Support Office - AC in meeting room 3 is unable to be regulated and is constantly cold | Air Conditioning | Room Air Conditioners | 2849.66 | Pass | Fail | 0 | 2 | 343 | 2022-09-30 09:10 | 2022-10-07 17:00 | 2022-10-04 08:00 | 2022-10-07 17:00 | 2022-10-18 15:00 |  |  | Attended service call, checked bms found areas setpoint too low , adjusted & found still no change. Tested condensors & gas pressures ok. Found branch box 2 not changing supply as expected, requires specialist tech to test
MSA-DTWD | WA6537603 | 1 | COMMERCIAL PLUMBING AND GAS | No hot water in men’s gym showers-see notes | Plumbing & Drainage | Water | 1885.8075 | Pass | Fail | 0 | 2 | 341.25 | 2023-02-07 10:21 | 2023-02-08 17:00 | 2023-02-07 13:00 | 2023-02-08 17:00 | 2023-02-21 18:15 |  | WACCES
MSA-DTAG | WA5100977 | 1 | Sapio Pty Ltd | Level 1 - Room 1.06 - in session button is faulty (no response / not turning off) | Security | Security Management System | 940 | Pass | Fail | 0 | 2 | 341 | 2022-02-03 08:19 | 2022-02-04 17:00 | 2022-02-03 10:30 | 2022-02-04 17:00 | 2022-02-17 15:30 |  | WACCES | Replaced Controller and confirmed correct firmware installed
MSA-DTAG | WA5978409 | 1 | Sapio Pty Ltd | Ground Floor - Courtroom 3 - Faulty Ceiling speakers - See notes below | ICT/Audiovisual | General AV works | 439.16 | Pass | Fail | 0 | 2 | 341 | 2022-09-28 10:38 | 2022-09-29 17:00 | 2022-09-29 07:30 | 2022-09-29 17:00 | 2022-10-13 12:30 |  |  | Replaced mic in court 3. Tested ok
MSA-DTAG | WA5151131 | 1 | Sapio Pty Ltd | Waiting area 1 left PIR in constant alarm | Security | Monitoring | 1367.78 | Pass | Fail | 0 | 2 | 340.75 | 2022-02-17 11:04 | 2022-02-18 17:00 | 2022-02-17 13:15 | 2022-02-18 17:00 | 2022-03-03 18:00 |  |  | Walk tested all alarm zones on site back to our Monitoring Centre.Job completed.
MSA-DCA | WA5696042 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Cold Temperatures - See notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 371.62 | Pass | Fail | 0 | 2 | 340.55 | 2022-08-08 09:15 | 2022-08-09 17:00 | 2022-08-08 10:35 | 2022-08-09 17:00 | 2022-08-22 15:08 |  |  | Attended site gained access and carried out inspection of reported cold areas in wear house. Issue is believed related to the the failed heating water valve for coils 5&6 as system is in full dehumidifier mode due to high humidity cooling and heating both active to reduce humidity. Adjustments has been made to cooling coil 5&6 as temporary fix until replacement heating water valves arrives into WA from supplier. Equipment has been kept under observation and confirmed to be stablizing. Ref valve repair WA5688066
MSA-DFES | WA5835324 | 2 | Australian HVAC Services Pty. Ltd. | Main Admin - Staff Dining Room - Air conditioners are showing error E4 - not blowing warm air | Air Conditioning | Room Air Conditioners | 9260.55 | Pass | Fail | -1 | 1 | 340.1667 | 2022-09-07 08:14 | 2022-09-12 17:00 | 2022-09-07 11:45 | 2022-09-12 17:00 | 2022-09-21 15:55 |  |  | Ac fault fixed new oil separator installed and gas leaks fixed.
MSA-DTWD | WA5206926 | 3 | Falcetta Plumbing and Gas | storeroom 1-06 & 1-07 - Hot Water System - tank split | Plumbing & Drainage | Water | 4477.24 | Pass | Fail | -1 | 1 | 340 | 2022-03-08 10:19 | 2022-03-15 17:00 | 2022-03-10 14:00 | 2022-03-15 17:00 | 2022-03-24 18:00 |  | WACCES | Replaced hot water unit
MSA-DFES | WA6165932 | 2 | Critical Fire Protection & Training | Fire Suppression water Tank - Outside yard area - See notes | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 6361.35 | Pass | Fail | 0 | 2 | 340 | 2022-11-11 10:37 | 2022-11-16 17:00 | 2022-11-16 08:00 | 2022-11-16 17:00 | 2022-11-30 12:00 |  | WACCES | -Attend site-Isolate and drain down fire systems-Remove faulty tank infill valve and couplings from both tanks-Supply and install 2x tank infill valves and associated couplings-Reinstate fire systems-Test and commission
MSA-DTWD | WA5392422 | 2 | Equans Mechanical Services Australia | Aircon Issues - Automatically on heating not cooling - See notes | Air Conditioning | Room Air Conditioners | 307.35 | Pass | Fail | 0 | 2 | 339.75 | 2022-05-03 09:52 | 2022-05-06 17:00 | 2022-05-04 07:00 | 2022-05-06 17:00 | 2022-05-18 10:45 |  |  | Need daikin to adjust settings so rooms are on cool only
MSA-DTAG | WA6503792 | 3 | Sapio Pty Ltd | Level 30-Wilsons Security access cards not working -see notes | Security | Access Control | 333.56 | Pass | Fail | 0 | 2 | 339.5 | 2023-01-19 11:22 | 2023-01-27 17:00 | 2023-01-24 08:00 | 2023-01-27 17:00 | 2023-02-07 11:30
MSA-DTWD | WA5105813 | 2 | AWB Co. | faulty submersible pump | Electrical | General Electrical | 1103.86 | Pass | Fail | 0 | 2 | 339.5 | 2022-02-04 14:26 | 2022-02-09 17:00 | 2022-02-09 07:30 | 2022-02-09 17:00 | 2022-02-23 11:00 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm about job, Went over to O block workshop and re located evap a/c. Removed old pump from aircon unit. Went to wholesaler in Wangara and replaced for exact like for like pump. Emailed through paperwork for new pump. Returned to site and set up. Chopped all cable ties that were holding internal cabling together. Put new pump into position and cable tied all cables internally onto framework as it was before. Connected up new pump in connections box. Filled up a/c unit with water to suitable line. Put cardboard filters on back of unit back in position. Turned on a/c unit and it ran as intended. Spoke to lecturer and he was happy with it. Took pictures. Packed up. Completed paperwork. Signed out.*** Job complete ***
MSA-DFES | WA4986181 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | External Roof - Water leaking from the roof going externally down the wall | Plumbing & Drainage | Water | 4616.05 | Pass | Fail | 0 | 2 | 339.4167 | 2021-12-31 11:09 | 2022-01-06 17:00 | 2022-01-04 08:11 | 2022-01-06 17:00 | 2022-01-18 11:36 |  |  | Located to site to inspect a leak on old building at the front of the property and found it was the solar tank that has split and will need to be replacedReturned back to site and inspected the hot water unit that has been installed tested all the hot taps and all working correctly.
MSA-DTAG | WA6414779 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 1 - G4S - Female staff toilets - Water flow from mixer tap is low | Plumbing & Drainage | Water | 193.295 | Fail | Fail | 0 | 2 | 339.2667 | 2023-01-11 09:56 | 2023-01-18 17:00 | 2023-01-19 10:14 | 2023-01-18 17:00 | 2023-02-02 13:30 |  | WCAPPR
MSA-DFES | WA6401273 | 2 | Critical Fire Protection & Training | Fire alarm activating intermittently | Fire Protection Services | Fire Protection - Monitor System | 303.9 | Fail | Fail | 1 | 3 | 339.25 | 2023-01-04 10:42 | 2023-01-09 17:00 | 2023-01-19 11:00 | 2023-01-09 17:00 | 2023-02-02 14:15 |  | WACCES
MSA-DTWD | WA5976762 | 3 | AWB Co. | Garden Bend - Pole light in grassed area rusted and fallen over. Wires exposed. | Electrical | General Electrical | 1483.48 | Pass | Fail | -1 | 1 | 339 | 2022-09-27 11:19 | 2022-10-04 17:00 | 2022-09-28 13:00 | 2022-10-04 17:00 | 2022-10-12 16:00 |  | WACCES | Attended site signed in jsa completed. Dug pole out found its rag bolts so dug a pit over the top of it. Dug next to pit and cemented new pole in. Tested operational and passedJob completed
MSA-DFES | WA5869641 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Kitchen - Power supply to oven is tripping - See notes below | Electrical | General Electrical | 691.215 | Pass | Fail | 0 | 2 | 338.75 | 2022-09-14 15:27 | 2022-09-19 17:00 | 2022-09-16 13:30 | 2022-09-19 17:00 | 2022-09-30 16:15 |  |  | Arrived on site at 1330 to investigate Ground Floor - Kitchen - Power supply to oven is tripping. Assessed surrounding areas and conducted all necessary compliance testing on circuit, did not discover anything of concern. Discovered faulty heating element within oven while testing. Will need to return to site with parts. Informed staff and left site at 1615.Onsite to repair faulty oven with 2x new elements. Found that the elements were not the cause of the problem after installing and that a faulty globe that had melted was shorting out the circuit causing it to trip. Notified staff of works done and works required on next visit and left site at 17:00.Onsite to replace oven light globe and checked that it was working as it should. Notified staff of works and left site
MSA-DTWD | WA6360187 | 1 | AWB Co. | Tool Store hot water heater - Unit switch has burnt out - Smoking & RCD tripped | Electrical | General Electrical | 1540.8 | Pass | Fail | 0 | 2 | 338.5 | 2022-12-07 09:23 | 2022-12-08 17:00 | 2022-12-07 13:00 | 2022-12-08 17:00 | 2022-12-21 15:30 |  |  | Attended site signed in jsa completed. Connected HWS. Replaced CB to RCD in board. Tested operational.Job completed
MSA-DTAG | WA5570439 | 2 | AAA Ability Locksmiths | CBU/IDDP office - Handle sticking sometimes when using digilock | Security | Locksmith | 1825 | Pass | Fail | 0 | 2 | 338.25 | 2022-06-28 11:10 | 2022-07-01 17:00 | 2022-06-30 06:30 | 2022-07-01 17:00 | 2022-07-14 08:45 |  |  | 30/06/2022- Attend site, temporarily repair digital lock require replacement. Current model is no longer available.14/07/2022- On site, supply and install replacement digital lock.
MSA-DCA | WA5698160 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 1-Chester building/ VMO & BSSTC offices- Aircon in offices not turning on after FIP isolatatio | Air Conditioning | Room Air Conditioners | 259.01 | Pass | Fail | 0 | 2 | 338 | 2022-08-09 15:09 | 2022-08-10 17:00 | 2022-08-09 15:30 | 2022-08-10 17:00 | 2022-08-23 17:30 |  |  | Attended site. Checked over bms. Found FIP was still in alarm and indicating it's isolated. Found vmo office wasn't showing occupied but schedule was enabled. Switched to occupied and tested operation, all ok. Investigated black Swan offices. Found all showing occupied but only 1 unit running. Checked over units and pushed the on button, tested operation of the 3 units that were off, all ok. Completed paperwork
MSA-DTAG | WA5226924 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground - Kitchen near Mitchell JA chambers - Hot water tap runs water, however does not run hot. | Plumbing & Drainage | HWS/Units Electric & Gas | 1890.9 | Pass | Fail | 0 | 2 | 338 | 2022-03-14 15:25 | 2022-03-15 17:00 | 2022-03-15 09:11 | 2022-03-15 17:00 | 2022-03-29 11:11 |  |  | Install new steibel to replace faulty
MSA-DTWD | WA6145753 | 3 | COMMERCIAL PLUMBING AND GAS | First cubicle - cistern faulty | Plumbing & Drainage | Toilets/Cisterns | 1076.185 | Pass | Fail | -1 | 1 | 338 | 2022-11-02 14:34 | 2022-11-09 17:00 | 2022-11-04 16:00 | 2022-11-09 17:00 | 2022-11-18 18:00 |  |  | Replaced in duct cistern with invisi
MSA-DCA | WA5293952 | 1 | ACTION GLASS & ALUMINIUM | Outside / front entrance - Cracked windowpane (glass) - see notes below | Glazing | Window Glass | 480 | Pass | Fail | 0 | 2 | 337.85 | 2022-03-28 11:33 | 2022-03-29 17:00 | 2022-03-28 13:09 | 2022-03-29 17:00 | 2022-04-11 15:00 |  |  | ATTENDED SITE AND ASSESSED, RETURNED TO SITE WITH 2 MEN, INSTALLED NEW GLASS AND FRAME
MSA-DFES | WA5832397 | 0 | Protek 24/7 Building & Maintenance | Ground Floor - Male Toilets - Ceiling has collapsed due to a burst pipe on the weekend | Building | Ceiling | 6431.07 | Pass | Fail | 0 | 2 | 337.75 | 2022-09-05 12:41 | 2022-09-05 14:41 | 2022-09-05 13:15 | 2022-09-05 16:41 | 2022-09-19 15:00 |  |  | ? Lay floor protection and cover any fixed items in bathroom as required? Supply and install new ceiling and make flush? Pull through wires and mark out services as per existing? Sand, Prime, and paint ceiling to suit standard 'ceiling white'
MSA-DFES | WA6394376 | 3 | Water2water Pty Ltd | Ground Level-Safety Tower 1- Practical Training Ground - Drinking fountain has no power- (See notes) | Plumbing & Drainage | HWS/Units Electric & Gas | 2104.985 | Pass | Fail | 0 | 2 | 337.5833 | 2022-12-30 14:04 | 2023-01-09 17:00 | 2023-01-06 14:40 | 2023-01-09 17:00 | 2023-01-20 16:15
MSA-DCA | WA5727650 | 2 | Techworks Electrical | Light out on Alarm at Stage Door for Stalls Foyer Accessible Toilet - see notes below | Electrical | Lighting, Internal | 634.47 | Pass | Fail | 0 | 2 | 337.5 | 2022-08-15 11:02 | 2022-08-18 17:00 | 2022-08-16 13:30 | 2022-08-18 17:00 | 2022-08-30 15:00 |  | WACCES | Inspected disabled duress alarm light. Alarm does not light up on unit. Ordered replacement alarm light. Waiting on partsPicked up parts from Wangara. tasks completed 1. found light that was faulty. 2. Replaced with new, having to re wire as the plug was also wired the wrong way around. 3. tested and all working well.
MSA-DTAG | WA6509927 | 2 | Sapio Pty Ltd | Levels 1-6 - Cameras not working (see notes) | Security | Monitoring | 656.36 | Pass | Fail | 0 | 2 | 337.5 | 2023-01-20 16:34 | 2023-01-25 17:00 | 2023-01-23 13:00 | 2023-01-25 17:00 | 2023-02-06 14:30
MSA-DTWD | WA5697482 | 0 | Precise Air Group | FCU 44 in fault. Requires repair-A and C block-need to engage controller company | Air Conditioning | Room Air Conditioners | 738.18 | Pass | Fail | 0 | 2 | 337.4 | 2022-08-09 09:51 | 2022-08-09 11:51 | 2022-08-09 11:29 | 2022-08-09 13:51 | 2022-08-23 12:53 |  |  | Subcontractor attended and completed
MSA-DCA | WA6578781 | 3 | Property Fire Maintenance | Fire door rear stage door side - Fire door requires new handle | Building | Fire Door | 1190.14 | Pass | Fail | -1 | 1 | 337.3 | 2023-02-15 12:04 | 2023-02-22 17:00 | 2023-02-15 12:28 | 2023-02-22 17:00 | 2023-03-01 13:46 |  | WACCES
MSA-DTWD | WA5694810 | 2 | AWB Co. | Wall and passageways-security and grounds lights not working.RCD in switchboard tripped & wont reset | Electrical | General Electrical | 1661.105 | Pass | Fail | 0 | 2 | 337 | 2022-08-05 13:36 | 2022-08-10 17:00 | 2022-08-09 09:00 | 2022-08-10 17:00 | 2022-08-23 10:00 |  | WACCES & WCAPPR | Attended site and signed in. Completed JSA. Located 3 x lights faulty. Supply and replaced with new led fittings as required. Supply and replaced 6x lamps to fittings around the walkways of block 6. Bypassed old faulty ballasts to work on new led lamps. Tested all okay. Signed out. Job complete
MSA-DTAG | WA6503811 | 3 | Sapio Pty Ltd | Level L31- Pacom Licencing / Milestone software update- see notes | Security | Security Management System | 258.24 | Pass | Fail | 0 | 2 | 337 | 2023-01-19 11:36 | 2023-01-27 17:00 | 2023-01-24 09:00 | 2023-01-27 17:00 | 2023-02-07 10:00
MSA-DTWD | WA5549046 | 3 | Falcetta Plumbing and Gas | Block 3 - Ground - Metal Fabrication - Faulty floor waste to quench tank | Plumbing & Drainage | Drainage | 704.39 | Pass | Fail | 0 | 2 | 337 | 2022-06-17 12:19 | 2022-06-24 17:00 | 2022-06-24 13:00 | 2022-06-24 17:00 | 2022-07-08 14:00 |  |  | modified and re-installed quench tank
MSA-DFES | WA5998397 | 2 | Protek 24/7 Building & Maintenance | Ground Floor - Cleaners Cupboard - Broken Broom Holder | Building | General Building | 288.18 | Pass | Fail | 0 | 2 | 336.5 | 2022-10-07 15:35 | 2022-10-12 17:00 | 2022-10-10 09:30 | 2022-10-12 17:00 | 2022-10-24 10:00 |  | WACCES | Supply and install 1 x broom / mop holder to cleaners store wall
MSA-DFES | WA5215346 | 0 | Australian HVAC Services Pty. Ltd. | TV - Kitchen area - Air Con 5 - not working or turning on | Air Conditioning | Room Air Conditioners | 1361.94 | Pass | Fail | 0 | 2 | 336.5 | 2022-03-10 11:22 | 2022-03-10 13:22 | 2022-03-10 11:30 | 2022-03-10 15:22 | 2022-03-24 12:00 |  |  | Jean-Pierre Richards-Shaw (10/03/2022) Arrived on-site, signed in & located unit that was not turning on, set up roof access and began operational testing, found condenser fan as well as evaporator fan to run for about 40 seconds then unit would cut out before compressor could run. Began electrical testing & found power was going into compressor, tested windings, compressor ok. Proceeded to indoor unit and began removing filter door, fascia panels & disconnected louver & LCD screen cabling. Removed drain plug & found drain sump to be full of water, these MDV Cassette units have a water height sensor, meaning when it fails and the sump is full, it will not allow unit to run, drained old dirty water out and flushed pipework with hot water to free up any blockages, poured 4L of water into sump and re-eneegised unit, no leaks and unit started immediately, reassembled unit and allowed indoor to run on 17c set point for 60 minutes, no leaks and unit continued to run. Carried out operationa
MSA-DTWD | WA5287127 | 2 | Techworks Electrical | Workshop 3 carpentry machine shop, loose cable duct covers | Electrical | General Electrical | 847.26 | Pass | Fail | 0 | 2 | 336.5 | 2022-03-22 10:17 | 2022-03-25 17:00 | 2022-03-23 14:30 | 2022-03-25 17:00 | 2022-04-06 15:00 |  | WACCES | Put back all covers that were available. Replaced damaged section of electrical duct and installed lid.installed new lid in carpentry machine workshop are.
MSA-DTWD | WA5698083 | 2 | Protek 24/7 Building & Maintenance | E50 Bistro Service Counter - Roof leak over Bistro counter/coffee machine | Roofing | Metal Roofing | 362.68 | Pass | Fail | 0 | 2 | 336.5 | 2022-08-09 14:22 | 2022-08-12 17:00 | 2022-08-11 14:15 | 2022-08-12 17:00 | 2022-08-25 14:45 |  |  | Leak tested previously patched sections of roof above bistroNo leaks present
MSA-DTWD | WA4991093 | 1 | Dormakaba Australia Pty Ltd | Auto door closer broken | Building | Automatic Doors | 3638.9 | Pass | Fail | 0 | 2 | 336.4167 | 2022-01-04 15:11 | 2022-01-05 17:00 | 2022-01-04 16:05 | 2022-01-05 17:00 | 2022-01-18 16:30 |  |  | 4/1/22 - Inspected door and found intermittent fault of unit, tested Mag lock and privacy kit, all ok, operator is faulty.Please quote to supply and install a new ED 100BRAF raised and accepted - returning to complete 18/1/2218/1/22 - Note new IP number is 1141892, removed faulty ED800 and supplied and installed new ED100 and commissioned.
MSA-DTWD | WA6048958 | 2 | M Construction (WA) | Two window fly screens are broken | Building | Internal Screens | 655.61 | Fail | Fail | 1 | 3 | 336.0333 | 2022-10-17 13:54 | 2022-10-20 17:00 | 2022-10-28 16:15 | 2022-10-20 17:00 | 2022-11-11 16:17 |  |  | Measure up new flyscreen install flyscreens. Fixed in placed and sealed
MSA-DTWD | WA5676403 | 3 | M Construction (WA) | C112 requires wall to be repaired and door stop fixed in place | Building | Internal Walls | 605.12 | Pass | Fail | -1 | 1 | 336 | 2022-07-25 08:18 | 2022-08-01 17:00 | 2022-07-25 09:00 | 2022-08-01 17:00 | 2022-08-08 09:00 |  |  | Attended site to inspect job, left site to source materials, returned back to site and installed new door stop, repaired gyprock. Applied 1 coat base and 1 coat of top. will return to apply additional coats. Applied additional coat of plaster. Will return to paint. Sanded patch and painted wall to match existing.
MSA-DTWD | WA6156586 | 2 | Precise Air Group | Room B10 - Faulty AC - See notes below | Air Conditioning | Room Air Conditioners | 152.03 | Pass | Fail | -1 | 1 | 336 | 2022-11-09 09:05 | 2022-11-14 17:00 | 2022-11-09 14:00 | 2022-11-14 17:00 | 2022-11-23 14:00 |  |  | attended site signed in and located reported area. similar issues with classrooms related to AHU 8 B10 is served by AHU 9 which the chilled water supply is set to 85% and does not change depending on space temp or changing setpoint. will need controls tech to attend to assessworks to be completed on WA6156586
MSA-DTWD | WA6534447 | 2 | WESTERN IRRIGATION PTY LTD | External - Break in retic line | Plumbing & Drainage | Drainage | 2175.34 | Pass | Fail | 0 | 2 | 336 | 2023-02-06 12:33 | 2023-02-09 17:00 | 2023-02-09 13:00 | 2023-02-09 17:00 | 2023-02-23 13:00
MSA-DTWD | WA6673502 | 2 | AWB Co. | Faulty Light fittings | Electrical | Lighting, Internal | 2334.56 | Pass | Fail | 0 | 2 | 335.75 | 2023-02-24 15:41 | 2023-03-01 17:00 | 2023-02-27 14:00 | 2023-03-01 17:00 | 2023-03-13 13:45 |  | WACCES
MSA-DTAG | WA5800643 | 1 | Midolo Building Services | Lower custody interview room - damaged wall - see notes below | Building | Internal Walls | 1213.55 | Pass | Fail | 0 | 2 | 335.5 | 2022-08-31 11:27 | 2022-09-01 17:00 | 2022-09-01 08:15 | 2022-09-01 17:00 | 2022-09-15 07:45 |  | WACCES | render repaired damaged wall & painted
MSA-DTWD | WA5972637 | 3 | COMMERCIAL PLUMBING AND GAS | L2-ladies toilet-loose tap | Plumbing & Drainage | Toilets/Cisterns | 843.665 | Pass | Fail | -1 | 1 | 335.5 | 2022-09-21 07:27 | 2022-09-28 17:00 | 2022-09-21 19:00 | 2022-09-28 17:00 | 2022-10-05 18:30 |  | WACCES | replaced 3x basin mixers
MSA-DTAG | WA5987204 | 2 | Water2water Pty Ltd | Level 2-Ground Floor - Registry Staff Kitchen - BILLI hot water unit not working - See notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 5362.185 | Pass | Fail | 0 | 2 | 335.4833 | 2022-10-03 09:07 | 2022-10-06 17:00 | 2022-10-04 10:00 | 2022-10-06 17:00 | 2022-10-18 09:29 |  |  | Installed new quad420 as per quote. All tested and calibration
MSA-DTWD | WA6523306 | 2 | AWB Co. | Faulty Circuit Breaker | Electrical | Distribution Board | 194.275 | Pass | Fail | 0 | 2 | 335.25 | 2023-01-31 14:20 | 2023-02-03 17:00 | 2023-02-01 14:00 | 2023-02-03 17:00 | 2023-02-15 13:15 |  | WCAPPR
MSA-DTWD | WA5679064 | 3 | AWB Co. | 2 walkway - Lights not working | Electrical | Lighting, External | 937.82 | Pass | Fail | -1 | 1 | 335 | 2022-07-26 10:25 | 2022-08-02 17:00 | 2022-07-29 11:30 | 2022-08-02 17:00 | 2022-08-12 10:30 |  | WCAPPR | Attended site signed in jsa completed. Removed remaining 4 lights in block 2 and replaced with 3 lights john had on site and one i sourced from wholesaler. Tested and all working.Job completed
MSA-DTWD | WA6376036 | 3 | AWB Co. | ground-Metal Fab 2 6A1 workshop-Cable to Swage Jenny machine damaged. (3 phase) | Electrical | General Electrical | 576.62 | Pass | Fail | 0 | 2 | 335 | 2022-12-15 12:39 | 2022-12-22 17:00 | 2022-12-21 10:00 | 2022-12-22 17:00 | 2023-01-04 09:00 |  | WCAPPR | Attended site signed in jsa completed. Installed new plug and lead for genny, wired up into machine. Tested operational.Job completed
MSA-DTAG | WA5980425 | 2 | AHS Services WA Pty Ltd (Anchor) | Courtroom 32 - No Hot Water - See notes below | Plumbing & Drainage | Water | 910.695 | Pass | Fail | -1 | 1 | 334.95 | 2022-09-29 14:49 | 2022-10-04 17:00 | 2022-09-30 10:33 | 2022-10-04 17:00 | 2022-10-14 09:30 |  |  | Found no power going to hot water unit.Left message for Ian to recommend electrician to check over unit14/10 picked up and replaced hwu
MSA-DFES | WA5477972 | 3 | Protek 24/7 Building & Maintenance | Main Foyer - Roof - Whirly Bird is squeaking | Roofing | Metal Roofing | 576.01 | Pass | Fail | -1 | 1 | 334.75 | 2022-05-26 07:33 | 2022-06-01 17:00 | 2022-05-27 10:15 | 2022-06-01 17:00 | 2022-06-10 09:00 |  | WACCES | Replace Squeaking whirly bird
MSA-DFES | WA5106625 | 3 | Protek 24/7 Building & Maintenance | Ground - Hose store - Replace hand towel dispenser in hose store | Building | General Building | 295.47 | Pass | Fail | -1 | 1 | 334.5 | 2022-02-07 09:49 | 2022-02-14 17:00 | 2022-02-09 11:30 | 2022-02-14 17:00 | 2022-02-23 10:00 |  | WACCES | Replace hand towel dispenser in hose store
MSA-DCA | WA6391647 | 0 | Techworks Plumbing | Hackett hall-Mez level-male toilet flush button is not working | Plumbing & Drainage | Water | 207.79 | Pass | Fail | 0 | 2 | 334.5 | 2022-12-22 14:40 | 2022-12-22 16:40 | 2022-12-22 16:00 | 2022-12-22 18:40 | 2023-01-05 14:30 |  |  | male toilet flush button is not working - Repaired
MSA-DCA | WA5566553 | 3 | Techworks Electrical | Admin Building - Ground - Distribution board on contactor making loud noise | Electrical | General Electrical | 281.73 | Pass | Fail | -1 | 1 | 334.4333 | 2022-06-23 09:33 | 2022-06-30 17:00 | 2022-06-23 09:34 | 2022-06-30 17:00 | 2022-07-07 08:00 |  | WACCES | Replaced faulty contactor
MSA-DTAG | WA6540783 | 3 | Australian HVAC Services Pty. Ltd. | Level 7 - BMS faulty - Showing errors | Air Conditioning | Room Air Conditioners | 427.92 | Pass | Fail | -1 | 1 | 333.9333 | 2023-02-09 14:01 | 2023-02-16 17:00 | 2023-02-09 14:30 | 2023-02-16 17:00 | 2023-02-23 12:26
MSA-DTWD | WA5473291 | 3 | AWB Co. | J.107 - Gutters overwhelmed and water has damaged awning | Roofing | Metal Roofing | 657.42 | Pass | Fail | -1 | 1 | 333.8 | 2022-05-24 13:41 | 2022-05-31 17:00 | 2022-05-26 14:42 | 2022-05-31 17:00 | 2022-06-09 12:30 |  |  | Investigated leak.need to return to remove cladding in order to view downpipesRemoved cladding for investigationCleaned and Sealed section of sumpRefixed downpipe on to pop/outlet
MSA-DCA | WA5286006 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Main Building - Ground floor - Gallery AHU is leaking again - see details below | Air Conditioning | Room Air Conditioners | 397.675 | Pass | Fail | 0 | 2 | 333.6167 | 2022-03-21 11:49 | 2022-03-24 17:00 | 2022-03-23 14:28 | 2022-03-24 17:00 | 2022-04-06 12:05 |  |  | Returned to site. Carried out inspection of AHU 8 critical equipment. Confirmed unit no longer leaking water. Confirmed equipment operating correctly and providing cooling to Batavia gallery. No further action required
MSA-DTWD | WA5693198 | 3 | Equans Mechanical Services Australia | Investigate faults & staging with Chillers/Boilers in relation to the BMS | Mechanical Services | Boilers | 963.77 | Pass | Fail | -1 | 1 | 333.1667 | 2022-08-04 10:17 | 2022-08-11 17:00 | 2022-08-04 11:20 | 2022-08-11 17:00 | 2022-08-18 08:30 |  |  | Boiler and chiller make up water was turned off causing cavitation. Opened and monitored.Boiler 2 has control fault. - will quoteBoiler one has control fault - flow switch needs replaced. -will quoteBoiler return temp was set too high at 80C on BMS. Reset. Monitored. System stabilized. Chiller 1 override manualed ON causing pump no 1 to run. Very dangerous. Turned off.Chiller No 2 showing fault on BMS. Checked and manually reset chiller stage 3. Chillers faulted on BMS on Tuesday 16th Aug. D Gaff reset. Checked chillers fault no with chillers.BMS needs attention and maintenance as there are a number of on-going issues and refinements to be made- will quote.
MSA-DTAG | WA5688074 | 3 | Australian HVAC Services Pty. Ltd. | Level 1 - Outside Lift - Debris is being pushed out of the Airconditionin vent from outside on floor | Air Conditioning | Room Air Conditioners | 711.19 | Pass | Fail | -1 | 1 | 332.5 | 2022-08-02 09:35 | 2022-08-09 17:00 | 2022-08-02 14:30 | 2022-08-09 17:00 | 2022-08-16 11:00 |  |  | Pick up section of sheetmetal from office. Attend site. Access first floor ceiling and remove all debris from ceiling space. Vacuum ceiling until clean. Fit sheet metal in roof gutter to prevent further debris blowing under gap. Clean up area and dispose of debris.
MSA-DTWD | WA6166249 | 3 | Australian Airconditioning Services Pty Ltd | Plant Room - Stage 1 Compressor Faulty | Equipment | Compressors, Generators | 4610.16 | Pass | Fail | -1 | 1 | 332 | 2022-11-11 13:04 | 2022-11-18 17:00 | 2022-11-14 07:30 | 2022-11-18 17:00 | 2022-11-28 03:30 |  | WACCES | complete
MSA-DTWD | WA5869657 | 2 | Equans Mechanical Services Australia | HtgW pump failed coupling and flow switch | Mechanical Services | Pumps | 2000 | Pass | Fail | -1 | 1 | 331.35 | 2022-09-14 15:39 | 2022-09-19 17:00 | 2022-09-14 15:40 | 2022-09-19 17:00 | 2022-09-28 11:01 |  |  | During maintenance inspection Chilled and heating water pump couplings and elements were inspected. Elements on all show signs of wear and the coupling on HW pump 2 showed wear. Systems were systematically shut down and all elements and one coupling was sourced and replaced. An intermittent fault on the boiler circuits 1 and 2 was causing issues with the BMS. A fault for No 2 boiler was also showing on the MSSB board, even though the boiler and pump were operating normally. To eliminate the pressure switches from the problem they were both replaced.Fault issue on BMS and MSSB still occurs. Boiler 2 fault although boiler 2 and pump are operating normally.The next step is to further investigate control / BMS logic /setup as a separate job. Also schedule and sequence of boiler 1 and pump need to be checked as circuit one is rarely observed operating.
MSA-DTWD | WA5683088 | 2 | AWB Co. | 8x light globes out in U015 can we have them replaced | Electrical | Lighting, Internal | 510.7475 | Pass | Fail | 0 | 2 | 331.25 | 2022-07-29 16:13 | 2022-08-03 17:00 | 2022-08-02 13:30 | 2022-08-03 17:00 | 2022-08-16 08:45 |  | WACCES | Attended site and signed in, completed jsa,isolated lighting circuits and removed old faulty light, removed clips and cable, installed on new fitting, mounted new fitting to bar, plugged in, re energised lighting circuit and tested light , now working as intended, completed paperwork,packed up, signed out **job completed*
MSA-DFES | WA5567921 | 0 | Protek 24/7 Building & Maintenance | External Fence - Near North gate - on Leak street - fence is damage | Building | General Building | 850.625 | Pass | Fail | 0 | 2 | 331 | 2022-06-24 13:40 | 2022-06-24 15:40 | 2022-06-24 15:15 | 2022-06-24 17:40 | 2022-07-08 10:15 |  |  | repair damaged fence
MSA-DCA | WA5289531 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Shipwrecks Museum - Courtyard - Chiller Plant Room - see details below | Refrigeration | Chiller | 930.875 | Pass | Fail | -1 | 1 | 330.95 | 2022-03-24 10:19 | 2022-03-29 17:00 | 2022-03-25 15:34 | 2022-03-29 17:00 | 2022-04-08 10:31 |  |  | Returned to site with Mech plumber and replacement of faulty valve carried out. New isolation point installed. Confirmed water pressure setting. Confirmed mains pressure resorted to cooling plant. No further action required. Work area left tidy.
MSA-DTWD | WA6077276 | 3 | AWB Co. | Several light fittings on high ceiling have faulty lamps-see notes | Electrical | Lighting, Internal | 2562.6375 | Fail | Fail | 0 | 2 | 326.5911 | 2022-10-18 11:30 | 2022-10-25 17:00 | 2022-10-26 17:25 | 2022-10-25 17:00 | 2022-11-09 08:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed, replaced remaining tubes in lights.All working correctly.Job completed
MSA-DTWD | WA6408155 | 1 | AWB Co. | U Block south side compressor shed - Faulty power at U Block receiver dryer | Electrical | General Electrical | 716.29 | Pass | Fail | 0 | 2 | 321.25 | 2023-01-10 15:26 | 2023-01-11 17:00 | 2023-01-11 07:00 | 2023-01-11 17:00 | 2023-01-24 16:15 |  | WCAPPR
MSA-DTWD | WA5680949 | 3 | Falcetta Plumbing and Gas | Plumbing duct to staff toilets - Hot water system failed (Instantaneous electric) | Plumbing & Drainage | Water | 1284.53 | Pass | Fail | 0 | 2 | 321 | 2022-07-28 07:30 | 2022-08-03 17:00 | 2022-08-03 10:00 | 2022-08-03 17:00 | 2022-08-16 19:00 |  | WACCES | Replaced hot water unit
MSA-DFES | WA5289874 | 3 | Australian HVAC Services Pty. Ltd. | Media and Corporate Comms - Level 2 - Video Editing Room - see details below | Air Conditioning | Room Air Conditioners | 328.89 | Pass | Fail | 0 | 2 | 319.6656 | 2022-03-24 13:38 | 2022-03-31 17:00 | 2022-03-31 07:21 | 2022-03-31 17:00 | 2022-04-13 15:01 |  |  | Inspected vav serving area. Found as cooling load is changing the vav will require redesign and balance. Braf submitted for works. Braf declined.
MSA-DFES | WA5687331 | 3 | Protek 24/7 Building & Maintenance | Ground - Workshop - Leak from roof in Applied Training Workshop. Possibly from whirlybird. | Roofing | Metal Roofing | 925.72 | Pass | Fail | -1 | 1 | 318 | 2022-08-01 16:07 | 2022-08-08 17:00 | 2022-08-04 07:00 | 2022-08-08 17:00 | 2022-08-17 13:00 |  |  | Re sealed the ridge capping on the overlap join
MSA-DTAG | WA6129958 | 1 | Sapio Pty Ltd | Duress alarm in President’s chambers has faulted - see notes below | Security | Security Management System | 1417.76 | Pass | Fail | 0 | 2 | 317.5 | 2022-10-28 08:35 | 2022-10-29 08:35 | 2022-10-28 10:00 | 2022-10-29 08:35 | 2022-11-10 15:30 |  | WCAPPR | Install 2x wireless duress buttons and replaced 1x wall mount duress button and tested.
MSA-DFES | WA5367657 | 1 | Australian HVAC Services Pty. Ltd. | Plant Room - chiller 1 - fault | Refrigeration | Chiller | 3035.48 | Pass | Fail | 0 | 2 | 317.4058 | 2022-04-19 09:34 | 2022-04-20 17:00 | 2022-04-19 10:36 | 2022-04-20 17:00 | 2022-05-02 16:00 |  | WACCES | Cooling Tower 1 fan motor has been replaced and Cooling Tower 2 Shaft seal on condenser water pump has been replaced.
MSA-DFES | WA5305425 | 2 | AWB Co. | Station Officers Bathroom - see notes below | Building | Ceiling | 897.5 | Pass | Fail | 0 | 2 | 317 | 2022-04-05 16:05 | 2022-04-08 17:00 | 2022-04-08 08:00 | 2022-04-08 17:00 | 2022-04-21 13:00 |  |  | Graham Coxhill (08/04/2022) - Work NoteAttended site to measure ceiling. Lights have 3 small gaps around them that can just be no more gapped by painter. Room is 3400x1900
MSA-DFES | WA5682622 | 0 | Australian HVAC Services Pty. Ltd. | roof-air con leaking gas | Air Conditioning | Room Air Conditioners | 2553.61 | Pass | Fail | 0 | 2 | 317 | 2022-07-29 10:16 | 2022-07-29 12:16 | 2022-07-29 11:00 | 2022-07-29 14:16 | 2022-08-11 16:00 |  |  | AC1 is low on gas, Reversing valve is leaking. Requires a replacement. Requires a gas repair. 6.1kgs of R410a
MSA-DTWD | WA5126918 | 3 | AWB Co. | Level 2 - Entry foyer/ corridor - Blown fluoros | Electrical | Lighting, Internal | 1200.29 | Pass | Fail | -1 | 1 | 316.5 | 2022-02-14 10:31 | 2022-02-21 17:00 | 2022-02-17 07:00 | 2022-02-21 17:00 | 2022-03-02 11:30 |  | WACCES | Attended site signed in completed jsa.Got keys for b4 and replaced x4 diffusers in ground floor.***job completed***
MSA-DTWD | WA5694431 | 2 | AWB Co. | B Block - Water leak above stairwell | Roofing | Metal Roofing | 688 | Pass | Fail | 0 | 2 | 316.5 | 2022-08-05 10:06 | 2022-08-10 17:00 | 2022-08-09 10:15 | 2022-08-10 17:00 | 2022-08-22 14:45 |  |  | Soursed leak found it to be coming in around glass sealed as best we could will need to return dry day to complete as got rained offResealed skylight as was dripping around frame
MSA-DCA | WA6361930 | 2 | Protek 24/7 Building & Maintenance | Wooden Steps to east of SLWA - Damaged step | Building | External Walls | 1538.47 | Pass | Fail | -1 | 1 | 316.5 | 2022-12-08 16:22 | 2022-12-13 17:00 | 2022-12-09 09:00 | 2022-12-13 17:00 | 2022-12-22 13:30 |  |  | Remove boards and skew screwed frame work back together as a temp make safe fix.bunted off area, approx. 2m fall under deckReframe braces underneath the seat
MSA-DFES | WA5090111 | 3 | Dom's Total Grounds Maintenance | Administration - Ground - Lawns - Reticulation station error 15 left hand administration lawn faulty | Landscaping & Gardening | Grounds Maintenance | 1730 | Fail | Fail | 0 | 2 | 316 | 2022-01-25 09:42 | 2022-02-02 17:00 | 2022-02-04 09:00 | 2022-02-02 17:00 | 2022-02-17 13:00 |  |  | Excavator required to locate Station 15Retic Solenoid & Fittings
MSA-DTAG | WA5308473 | 1 | Australian HVAC Services Pty. Ltd. | Roof - AC plant - Office of DPP – AC very hot | Air Conditioning | Building HVAC Maintenance (Major Plant) | 745.65 | Pass | Fail | 0 | 1 | 316 | 2022-04-08 12:24 | 2022-04-11 17:00 | 2022-04-08 12:30 | 2022-04-11 17:00 | 2022-04-21 16:30 |  |  | Attend site. Access bms and and manual setpoint to bring on two stages of cooling. Access roof and check operation of unit. Found compressor 1 to start and run as normal. Found call for compressor 2 but unit not running. Trace wiring through control circuit and found no call comming out of printed circuit board. Trace wiring issue to Low pressure switchtest switch and found circuit to be closed. Remove pressure switch connectors and clean up. Replace connector and power cycle unit. Found unit to start and stage 1 to operate. Found stage 2 to now start and operate as normal. Found issue to be a bad low pressure switch connection. Cycle unit on and of and found to now work as normal.
MSA-DTWD | WA5549064 | 3 | Falcetta Plumbing and Gas | Block 7 - Kitchen wash room - Faulty delivery hose/pipe to dish washer | Plumbing & Drainage | Materials | 399.06 | Pass | Fail | 0 | 2 | 316 | 2022-06-17 12:31 | 2022-06-24 17:00 | 2022-06-24 13:30 | 2022-06-24 17:00 | 2022-07-07 17:30 |  |  | replace inlet piping and re-run
MSA-MRWA | WA5238777 | 3 | AWB Co. | Basement change rooms AHU - Emergency light not working | Electrical | General Electrical | 568.41 | Pass | Fail | 0 | 2 | 315.25 | 2022-03-16 08:56 | 2022-03-23 17:00 | 2022-03-23 06:00 | 2022-03-23 17:00 | 2022-04-05 09:15 |  |  | Attended site and signed in, reviewed jsa, went to basement airlock and set up work area, isolated lighting circuits, removed exit light, drilled holes in new light to suit existing cables , mounted new light and wired it in , used 1x CLEVERTRONIC exit light, 2x saddles and 1x adaptor, re energised light circuit and tested light, light working as intended, packed up, cleaned up, completed paperwork, signed out Job completed
MSA-DTWD | WA5586799 | 3 | Protek 24/7 Building & Maintenance | Front of Elevator - Hole in Floor in front of elevator | Flooring | Vinyl | 1289.42 | Pass | Fail | 0 | 2 | 315.25 | 2022-07-06 14:50 | 2022-07-13 17:00 | 2022-07-12 08:45 | 2022-07-13 17:00 | 2022-07-25 12:00 |  | WACCES | repair damaged concrete - replace damaged vinyl
MSA-DTWD | WA5655840 | 1 | Equans Mechanical Services Australia | BG14, BG17 , BF14 and BF15 - AHUB1 not heating | Air Conditioning | Building HVAC Maintenance (Major Plant) | 985.365 | Pass | Fail | 0 | 2 | 315.2 | 2022-07-18 10:45 | 2022-07-19 17:00 | 2022-07-19 12:30 | 2022-07-19 17:00 | 2022-08-01 15:42 |  |  | TESTING AND MONITORING OF ROOM TEMPERATURE CALIBRATE INLINE WITH BMSREADINGS.CHECK HEATERS ALL OK.CHECK HEATER AUTOMATION IF OPERATING WITHINTEMPERATURE SET POINTS ALL OK
MSA-DTWD | WA5086894 | 2 | Protek 24/7 Building & Maintenance | D Block - D1 Pastry Lab External - Brick Paving Damage to footpath due to burst retic | Paving & Roadworks | Paving | 985.23 | Pass | Fail | 0 | 2 | 315 | 2022-01-21 15:30 | 2022-01-27 17:00 | 2022-01-27 12:45 | 2022-01-27 17:00 | 2022-02-09 15:45 |  | WACCES | Brick Paving Damage to footpath due to burst retic
MSA-DTWD | WA6403744 | 2 | AWB Co. | Room C705, 706, 707 - Wall and skirtings damaged - Executive offices | Painting | Internal | 1574.95 | Pass | Fail | 0 | 2 | 315 | 2023-01-06 14:40 | 2023-01-11 17:00 | 2023-01-10 13:30 | 2023-01-11 17:00 | 2023-01-23 16:30
MSA-DCA | WA6178100 | 2 | Protek 24/7 Building & Maintenance | External Ground - Northern Side of State Theatre -Broken paving | Flooring | Concrete | 1177.21 | Pass | Fail | 0 | 2 | 314.75 | 2022-11-14 09:27 | 2022-11-17 17:00 | 2022-11-16 08:30 | 2022-11-17 17:00 | 2022-11-29 11:15 |  |  | measure up for replacement pavingRemoving trip hazards from paving
MSA-DTWD | WA5100912 | 3 | AWB Co. | 2 x hanging GPO that are faulty | Electrical | General Electrical | 1000.71 | Pass | Fail | -1 | 1 | 314.5 | 2022-02-03 08:04 | 2022-02-10 17:00 | 2022-02-03 14:15 | 2022-02-10 17:00 | 2022-02-16 16:45 |  | WACCES & WCAPPR | Attended site and signed in. Completed JSA. spoke to fm about job. Set up work area. Got 12ft platform ladder , mounted j boxes to roof frame, ran cables from both GPOs to existing gpo, put cable in conduit and cable tied it to round frame , isolated power and joined new GPOs into existing circuit , Re energised circuit and tested gpos , everything working as intended , cleaned up , packed up, completed paperwork, signed out Job completed
MSA-DFES | WA5879850 | 2 | Go Doors | SW Carpark Automatic Gates - Gate is not working via remote controller - Keypad fucntion works | Building | Steel Fencing & Gates | 1275.31 | Pass | Fail | -1 | 1 | 314.5 | 2022-09-15 09:45 | 2022-09-20 17:00 | 2022-09-15 14:00 | 2022-09-20 17:00 | 2022-09-28 16:30 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5295591 | 2 | ACTION GLASS & ALUMINIUM | Aluminium/Glass Bi-fold doors not closing properly and flush bolt is broken | Building | Doors | 473.75 | Pass | Fail | 0 | 2 | 314.5 | 2022-03-29 16:25 | 2022-04-01 17:00 | 2022-04-01 10:00 | 2022-04-01 17:00 | 2022-04-14 12:30 |  |  | ATTENDED SITE AND ASSESSED, RETURNED TO SITE AT LATER DATE WITH 2 MEN, INSTALLED NEW BOLT AND ADJUSTED DOORS
MSA-DFES | WA5289563 | 2 | Australian HVAC Services Pty. Ltd. | Main admin - SES/MR training office - Air conditioning displaying error code H3 for a filter problem | Air Conditioning | Room Air Conditioners | 815.57 | Pass | Fail | -1 | 1 | 314.25 | 2022-03-24 10:40 | 2022-03-29 17:00 | 2022-03-25 13:15 | 2022-03-29 17:00 | 2022-04-07 15:30 |  |  | Obtained new terminals & heartshrink cable insulation from suppliers, arrived on-site, spoke with on-site representative & informed of repairs to be carried out, signed in & proceeded to condensing unit, dismantled condenser fascia panelling, isolated unit and removed chewed H/P switch cabling, using new cable soldered terminals on cabling, reconnected all cabling and carried out operational tasting, found unit to be fully functional. Informed client of completed works & left site.
MSA-DCA | WA6074886 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - AHU6B alarm-controls fault. | Building | General Building | 468.01 | Pass | Fail | 0 | 2 | 314.0833 | 2022-10-18 09:53 | 2022-10-19 17:00 | 2022-10-18 09:55 | 2022-10-19 17:00 | 2022-10-31 12:00 |  |  | Purchase order sent to Schneider for controls issue with AHU 6B. Mechanical and electrical all OK.
MSA-DTWD | WA5835987 | 3 | AWB Co. | Level 1 - N129 - Failed Emergency Light | Electrical | Emergency & Exit Lighting | 1032.64 | Pass | Fail | 0 | 2 | 314 | 2022-09-07 09:37 | 2022-09-14 17:00 | 2022-09-14 07:00 | 2022-09-14 17:00 | 2022-09-27 09:00 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm. Set up work area. Installed seemless led light. Plugged in and cable tied excess cabling to conduit to make look neat. Cleaned up and packed up. Took picture. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5833497 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Local Plant cut out due to power loss | Air Conditioning | Building HVAC Maintenance (Major Plant) | 281.53 | Fail | Fail | 0 | 2 | 313.5 | 2022-09-06 10:12 | 2022-09-06 12:12 | 2022-09-06 14:30 | 2022-09-06 14:12 | 2022-09-19 16:00 |  |  | ATTENDED SITE AND CHECKED THE CENTRAL PLANT AFTER THE POWER SPIKE. CHECKED ALLCENTRAL PLANT EQUIPMENT FOR CORRECT OPERATION AND RESET ALL ALARMS ON THE BMS.RESET THE CENTENARY HUMIDIFIERS AND MONITORED FOR FURTHER FAULTS- ALL WORKING ASPER NORMAL.
MSA-DFES | WA6393427 | 3 | Dom's Total Grounds Maintenance | Grounds - Branches/leaves & saplings to be cleared - possible fire risk | Landscaping & Gardening | Grounds Maintenance | 790 | Fail | Fail | 1 | 3 | 313.5 | 2022-12-28 14:11 | 2023-01-05 17:00 | 2023-01-14 07:30 | 2023-01-05 17:00 | 2023-01-27 09:00
MSA-DTWD | WA5549073 | 3 | Falcetta Plumbing and Gas | Leaking tap in washing up sink | Plumbing & Drainage | Water | 238.925 | Pass | Fail | 0 | 2 | 313 | 2022-06-17 12:35 | 2022-06-24 17:00 | 2022-06-24 14:00 | 2022-06-24 17:00 | 2022-07-07 15:00 |  |  | replaced tap set and reseated
MSA-DTWD | WA6658617 | 2 | Swan Pest Control | Treat termites in cabinetry | Pest Control | General Pest | 1450 | Pass | Fail | 0 | 2 | 313 | 2023-02-21 11:39 | 2023-02-24 17:00 | 2023-02-24 14:30 | 2023-02-24 17:00 | 2023-03-09 15:30
MSA-DFES | WA5478934 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Dorm 8 Bathroom - Toilet seat broken | Plumbing & Drainage | Toilets/Cisterns | 251.2 | Pass | Fail | -1 | 1 | 312.7667 | 2022-05-26 15:20 | 2022-05-31 17:00 | 2022-05-27 10:59 | 2022-05-31 17:00 | 2022-06-09 11:45 |  | WCAPPR | Went back to room 8 at Perth fire station inspected toilet seat nothing was wrong with it. Took seat off and retighten everything to make sure spoke to fire guy in room 8 and l let him know what l did. He told me that there was no problem with the new seat.
MSA-DTWD | WA5478696 | 3 | AWB Co. | Ground - Student study area 9G23 - Water leak down window | Building | General Building | 457.5 | Pass | Fail | 0 | 2 | 312.6 | 2022-05-26 13:07 | 2022-06-02 17:00 | 2022-06-02 10:24 | 2022-06-02 17:00 | 2022-06-15 11:00 |  | WACCES | Investigated leak. Stripped section of roof. Found laps of sheets to be full of dirt causing water to breach.
MSA-DFES | WA5585652 | 2 | Protek 24/7 Building & Maintenance | Gym patio area-roof leaks-additional notes | Roofing | Metal Roofing | 1033.41 | Pass | Fail | 0 | 2 | 312.5 | 2022-07-06 07:01 | 2022-07-08 17:00 | 2022-07-08 11:00 | 2022-07-08 17:00 | 2022-07-21 11:30 |  |  | Supply & install new eave sheet
MSA-DFES | WA5195007 | 2 | Water2water Pty Ltd | Applied Training Ground - Water fountain ISFFT - see notes below | Plumbing & Drainage | Water | 2108.265 | Pass | Fail | 0 | 2 | 312.5 | 2022-02-28 10:08 | 2022-03-03 17:00 | 2022-03-01 10:30 | 2022-03-03 17:00 | 2022-03-14 11:00 |  | WACCES | 14.03 - tech replaced zip sitemaster. All okay on departureNEW UNIT REQUIRED. UNIT LEAKING AND TRIPPING POWER, UN-REPAIRABLE.
MSA-DTWD | WA5714836 | 2 | ACTION GLASS & ALUMINIUM | Level1 & 2 -A224 and Ground Floor -Two broken glass panels - See notes below | Glazing | Window Glass | 1369.83 | Pass | Fail | 0 | 2 | 312.4833 | 2022-08-12 08:53 | 2022-08-17 17:00 | 2022-08-17 13:55 | 2022-08-17 17:00 | 2022-08-30 14:24 |  | WACCES | ATTENDED SITEMADE SAFE 2 BROKEN OVERSIZE DOOR PANELS2 SQM OF SAFETY FILM USEDRETURNED LATER DATE TO REGLAZE 6.38 CLEAR LAMINATED SAFETY GLASS1-2190 X 7386.38 GREY LAMINATED SAFETY GLASS1-2172 X 692DECALS APPLIED6 L/M OF RUBBER REPLACEDAS PER APPROVED BRAF
MSA-DTWD | WA5287589 | 2 | Falcetta Plumbing and Gas | C-Block - CG10 - Oil separator not functioning correctly | Plumbing & Drainage | Materials | 784.33 | Pass | Fail | 0 | 2 | 312 | 2022-03-22 13:35 | 2022-03-25 17:00 | 2022-03-23 15:00 | 2022-03-25 17:00 | 2022-04-05 15:00 |  | WACCES | replaced floats and tested unit
MSA-DTAG | WA5990115 | 1 | Sapio Pty Ltd | Level 7, room 710 card reader on the secure door - see notes | Security | Access Control | 953.95 | Pass | Fail | 0 | 2 | 312 | 2022-10-04 13:19 | 2022-10-05 17:00 | 2022-10-04 14:30 | 2022-10-05 17:00 | 2022-10-17 14:30 |  |  | Replaced mortice lock and restored. All okay.Job completed
MSA-DCA | WA6394271 | 3 | EQUANS Mechanical Services (WA) Pty Limited | AHU unit above cannon at the top of the main stairs has started leaking intermittently (See notes) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1159.89 | Pass | Fail | -1 | 1 | 312 | 2022-12-30 10:20 | 2023-01-09 17:00 | 2023-01-03 10:00 | 2023-01-09 17:00 | 2023-01-16 10:00
MSA-DTWD | WA6256990 | 3 | M Construction (WA) | Drive way / Car Park - Repair pot holes. | Paving & Roadworks | Asphalt | 1489.47 | Pass | Fail | -1 | 1 | 311.25 | 2022-11-24 10:40 | 2022-12-01 17:00 | 2022-11-25 14:45 | 2022-12-01 17:00 | 2022-12-08 14:00 |  |  | Repaired Potholes in several locations (please see attached photo).
MSA-DTWD | WA5477570 | 1 | WESTERN IRRIGATION PTY LTD | Outside A25 - Retic station 2 solenoid valve needs replacing | Landscaping & Gardening | Grounds Maintenance | 1662.57 | Pass | Fail | 0 | 2 | 311 | 2022-05-25 14:46 | 2022-05-26 17:00 | 2022-05-26 11:00 | 2022-05-26 17:00 | 2022-06-08 10:00 |  |  | Replace faulty solenoid valve and run new solenoid wire to the valve.
MSA-DFES | WA4992527 | 1 | Anvil Doors | Rear Gate isnt opening automatically its jamming in the closing position | Building | Security Doors | 2691 | Pass | Fail | 0 | 2 | 311 | 2022-01-06 13:04 | 2022-01-07 17:00 | 2022-01-06 16:00 | 2022-01-07 17:00 | 2022-01-19 15:00 |  |  | Attended North Shore SES on P1 Call out to malfunctioning Auto Gate. Technician found that logic limit was faulty. The gate is unable to function and requires a replacement motor. Please see attached service report, BRAF, Signature Slip and Quote.Note, the motor requires urgent replacement.20/1/22 -- Gate Motor replaced BRAF works complete
MSA-DTAG | WA5188620 | 3 | Sapio Pty Ltd | NVR raid failure, remove unit for assessment | Security | Security Management System | 240 | Pass | Fail | -1 | 1 | 310.7833 | 2022-02-23 10:20 | 2022-03-02 17:00 | 2022-02-24 09:30 | 2022-03-02 17:00 | 2022-03-09 08:17 |  | WCAPPR | Checked raid on NVRs after the software upgrade. All OK.
MSA-DFES | WA6258219 | 1 | ACTION GLASS & ALUMINIUM | Ground - Front Engine Room Doors - 2 glass door panels broken - See Notes Below | Glazing | Door Glass | 755.61 | Pass | Fail | 0 | 1 | 310.6167 | 2022-11-25 11:01 | 2022-11-28 17:00 | 2022-11-25 13:03 | 2022-11-28 17:00 | 2022-12-08 11:40 |  |  | ATTENDED SITETEMP GLAZED 2 BROKEN PANELS6.38 CLEAR LAMINATED SAFETY GLASS2-444 X 1083PLUS SILICONERETURNED LATER DATE REMOVED TEMP GLASS & REFIT WITH 6.5 L/M OF NEW RUBBER(NO LABOUR CHARGE FOR SECOND VISIT)RETURNED LATER DATE TO SUPPLY & FIT TINT FILM
MSA-DTWD | WA5482640 | 1 | ECO PLUMBING AND GAS PTY LTD | C23 Café Eatery - Gas Heating System not working | Plumbing & Drainage | Gas | 389.83 | Fail | Fail | 0 | 2 | 310.1667 | 2022-05-31 13:45 | 2022-06-01 17:00 | 2022-06-02 14:50 | 2022-06-01 17:00 | 2022-06-15 13:00 |  | WCAPPR | Repaired issue with gas heating
MSA-DTWD | WA5468693 | 1 | Precise Air Group | Air con system managers 4 rooms is not working - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1416.04 | Pass | Fail | 0 | 1 | 309.5 | 2022-05-20 11:47 | 2022-05-23 17:00 | 2022-05-20 13:00 | 2022-05-23 17:00 | 2022-06-02 10:30 |  |  | Attended site and completed pre start paperwork and signed in. Acessed cu 2 on roof and inspected. Found system out on high pressure safety. Reset and checked drive belts/filters. Found ok. Test ran unit and found system to start and run with out fault. Left all ok.
MSA-DTAG | WA6184424 | 1 | Sapio Pty Ltd | Wilson security office – Dotag and SSO workstation – blank screen and monitor coming of the bracket | Security | Security Management System | 859.46 | Pass | Fail | 0 | 2 | 309 | 2022-11-15 12:13 | 2022-11-16 17:00 | 2022-11-15 13:00 | 2022-11-16 17:00 | 2022-11-28 10:00 |  | WACCES | Installed new monitor and removed old faulty one from site.
MSA-DTAG | WA5707000 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Bio Clean required - Custody area - Basement - see notes below | Cleaning | Cleaning | 300 | Fail | Fail | 2 | 4 | 307.5667 | 2022-08-11 15:36 | 2022-08-12 17:00 | 2022-08-24 14:56 | 2022-08-12 17:00 | 2022-09-06 10:30 |  |  | Please date this invoice on the 12th August 2022
MSA-DTWD | WA5216604 | 3 | AWB Co. | B2 - 314 - Brackets broken on base sheet roll holder | Building | General Building | 503.43 | Pass | Fail | -1 | 1 | 307.5 | 2022-03-11 11:30 | 2022-03-18 17:00 | 2022-03-11 13:30 | 2022-03-18 17:00 | 2022-03-24 09:00 |  |  | Replaced broken brackets in the massage store room
MSA-DCA | WA6537874 | 2 | Techworks Electrical | Balloon Light needs changing (see notes) | Electrical | General Electrical | 1951.705 | Pass | Fail | 0 | 2 | 307.5 | 2023-02-07 12:28 | 2023-02-10 17:00 | 2023-02-08 13:00 | 2023-02-10 17:00 | 2023-02-21 08:30
MSA-DFES | WA5994341 | 2 | ACTION GLASS & ALUMINIUM | External window seal fallen out of first floor window facing Stockton Road | Building | Windows | 314.935 | Pass | Fail | 0 | 1 | 307.1667 | 2022-10-05 15:25 | 2022-10-10 17:00 | 2022-10-07 15:05 | 2022-10-10 17:00 | 2022-10-20 10:15 |  |  | ATTENDED SITE TO ASSESS WINDOWRETURNED LATER DATE WITH 2 MEN & PLATFORM LADDERREFIT RUBBER AND SILICONE SEALED IN
MSA-DCA | WA5479569 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground Level - Staff Mens Bathroom - Tap leaking on sides when pressed | Plumbing & Drainage | Water | 621.405 | Pass | Fail | 0 | 1 | 304.9167 | 2022-05-27 10:17 | 2022-06-03 17:00 | 2022-05-31 15:20 | 2022-06-03 17:00 | 2022-06-13 08:15 |  | WACCES | Replaced daulty and leaking rhs tap
MSA-DFES | WA5087009 | 1 | Australian HVAC Services Pty. Ltd. | Front side of the bay - Aircondition system is not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 792.285 | Pass | Fail | 0 | 2 | 301 | 2022-01-22 12:36 | 2022-01-23 12:36 | 2022-01-22 13:00 | 2022-01-23 12:36 | 2022-02-04 02:00 |  |  | TBA
MSA-DTWD | WA6255904 | 2 | Australian Airconditioning Services Pty Ltd | AC Unit 7 - completely clogged, pressure gauge reading over 300 Pascals | Air Conditioning | Room Air Conditioners | 974.1 | Pass | Fail | -1 | 1 | 298.4511 | 2022-11-23 14:32 | 2022-11-28 17:00 | 2022-11-24 13:33 | 2022-11-28 17:00 | 2022-12-07 |  |  | Replaced filters and all ok.
MSA-DTWD | WA6650971 | 2 | AWB Co. | LED strip lighting/controller not working | Electrical | Lighting, External | 692.8225 | Pass | Fail | 0 | 2 | 298 | 2023-02-20 15:21 | 2023-02-23 17:00 | 2023-02-23 13:00 | 2023-02-23 17:00 | 2023-03-07 23:00 |  | WACCES
MSA-DTWD | WA5568151 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire pumps are activated no fire | Fire Protection Services | Fire Protection - Monitor System | 5020.34 | Pass | Fail | 0 | 2 | 294.8333 | 2022-06-25 05:15 | 2022-06-25 07:15 | 2022-06-25 07:10 | 2022-06-25 09:15 | 2022-07-07 14:00 |  | WACCES | COMPLETED 07/07/2022-DENNIS JARDINE TO AUTHORISE SIG SLIP-.07/07/2022 ***BRAF value reduce as less hours required to complete the install of pump***BRAF submitted 05/07/2022PRIORITY 0 CALL-OUT 25/06 -ONSITE 5.15AM ONSITE-#1 25/6 5.40AM TO 7.10AM-INVESTIGATEONSITE-#2 28/06 10.00AM TO 2.00PM-PARTS REQUIREDONSITE #3 28/06 5.30PM TO 6.30PMBRAF APPROVED- 06/07/2022
MSA-DTAG | WA5090670 | 3 | Midolo Building Services | Level 1 - passageway & storeroom - Holes in plasterboard ceilings | Building | Ceiling | 1547.25 | Fail | Fail | 1 | 3 | 294.25 | 2022-01-25 14:51 | 2022-02-02 17:00 | 2022-02-09 07:00 | 2022-02-02 17:00 | 2022-02-21 13:15 |  | WACCES | Patched and painted
MSA-DFES | WA5693806 | 3 | AWB Co. | fence ground-Tree has caused the fence to buckle and bottom bar to break | Building | Steel Fencing & Gates | 873.42 | Pass | Fail | -1 | 1 | 294.0667 | 2022-08-04 15:27 | 2022-08-11 17:00 | 2022-08-05 10:26 | 2022-08-11 17:00 | 2022-08-17 16:30 |  |  | remove damaged section of fencedig out rootsreplace fencing and install crossbar
MSA-DTAG | WA5111732 | 1 | Australian HVAC Services Pty. Ltd. | Detention warm - warm air going in, 4 out of 5 roof systems not running cold | Air Conditioning | Room Air Conditioners | 886.28 | Pass | Fail | 0 | 2 | 293.8833 | 2022-02-10 10:37 | 2022-02-11 17:00 | 2022-02-10 10:37 | 2022-02-11 17:00 | 2022-02-22 16:30 |  | WACCES | Pick up filters from supplier. Attend site. Access Basement carpark isolate AC unit and remove old filters. Carry out coil clean. Install new filters. Deisolate and test operation, working as normal.
MSA-DTWD | WA5869310 | 3 | Dormakaba Australia Pty Ltd | Art Gallery - Auto Door West L3 Gallery not operating | Building | Automatic Doors | 3899.48 | Pass | Fail | -1 | 1 | 292.6667 | 2022-09-14 12:57 | 2022-09-21 17:00 | 2022-09-15 08:00 | 2022-09-21 17:00 | 2022-09-27 12:40 |  |  | 15/9/22 - On arrival found door working ok, site complain of door intermittently failing, door failed whilst on site, checked over operator etc and tested, will recommend upgrade as current model is obsolete.1x ed1001x cover1x slide channel kit27/9/22 - 1091669, Programmed asset A40299730N. Arrived onsite and signed in .,removed existing unit and installed one new ED100 complete with slide arm and cover, wired in activation sensor and push button. Commissioned and tested operation all correct.
MSA-DTAG | WA5887446 | 1 | Sapio Pty Ltd | Duress not working inside the following rooms - see notes | Security | Security Management System | 418.88 | Pass | Fail | 0 | 2 | 292.5 | 2022-09-16 07:43 | 2022-09-16 17:00 | 2022-09-16 10:00 | 2022-09-16 17:00 | 2022-09-28 14:30 |  |  | Replaced batteries in duress buttons on Level 4, Room 46 and Level 7 Rooms 7.08 & 7.12, tested,reporting OKReplaced battery in duress button on Level 8, Room 8.11, tested, OK.
MSA-DTWD | WA6534155 | 1 | Australian Airconditioning Services Pty Ltd | Chiller 1 & 2 Fault Light is on | Refrigeration | Chiller | 2907 | Fail | Fail | 0 | 2 | 292.3667 | 2023-02-06 09:58 | 2023-02-07 17:00 | 2023-02-09 07:52 | 2023-02-07 17:00 | 2023-02-21 12:14
MSA-DCA | WA5571099 | 1 | Protek 24/7 Building & Maintenance | Ground Floor - Plant room number 3 - wall is damaged from water - needs to be dried | Building | Internal Walls | 405.32 | Pass | Fail | 0 | 2 | 292 | 2022-06-29 08:37 | 2022-06-30 17:00 | 2022-06-29 12:00 | 2022-06-30 17:00 | 2022-07-11 16:00 |  | WACCES | Carpet drying
MSA-DTAG | WA5085670 | 2 | Dormakaba Australia Pty Ltd | Ground Floor - Revolving door is noisy | Building | Automatic Doors | 365.65 | Pass | Fail | -1 | 1 | 290.9833 | 2022-01-21 09:55 | 2022-01-27 17:00 | 2022-01-21 11:08 | 2022-01-27 17:00 | 2022-02-02 14:07 |  |  | 21/1/22 - Inspected and tested door and found that the o rings were badly worn and that the bottom bearing was making a noise. 2x o rings required and 2x men to try and lift door and lubricated bottom bearing.2/2/22 - Replaced damaged O rings as required, tested and adjusted, all OK
MSA-DCA | WA5087960 | 2 | ACTION GLASS & ALUMINIUM | Admin Office 2 - broken window in admin office | Glazing | Window Glass | 668.3 | Pass | Fail | 0 | 2 | 290.5 | 2022-01-24 15:42 | 2022-01-28 17:00 | 2022-01-27 08:30 | 2022-01-28 17:00 | 2022-02-08 11:00 |  | WACCES | Made safe glass panel, returned to site at later date and reglazed
MSA-DTWD | WA6404871 | 2 | Precise Air Group | Aircon not running | Air Conditioning | Room Air Conditioners | 304.055 | Pass | Fail | 0 | 2 | 290.5 | 2023-01-09 09:48 | 2023-01-12 17:00 | 2023-01-11 07:00 | 2023-01-12 17:00 | 2023-01-23 09:30
MSA-DTWD | WA5674186 | 1 | AWB Co. | No lights in Workshop, unable to find cause. | Electrical | Lighting, Internal | 1521.2275 | Pass | Fail | 0 | 2 | 289.75 | 2022-07-21 09:35 | 2022-07-22 17:00 | 2022-07-21 11:30 | 2022-07-22 17:00 | 2022-08-02 13:15 |  |  | Attended site signed in jsa completed. located box in corner of room up high with ewp got there safely and removed old contactor as it was burnt out. replaced with new and tested all lights working.Ewp offhired and job completed
MSA-DFES | WA5790926 | 2 | Protek 24/7 Building & Maintenance | Ground Floor - Kitchen - Cupboard hinges are broken - See notes below | Carpentry | Joinery | 231.99 | Pass | Fail | 0 | 2 | 289.5 | 2022-08-22 13:29 | 2022-08-25 17:00 | 2022-08-24 07:00 | 2022-08-25 17:00 | 2022-09-05 08:30 |  | WACCES | replace broken hinges
MSA-DTWD | WA5518606 | 3 | Falcetta Plumbing and Gas | Water leak between floor waste & slab penetrations | Plumbing & Drainage | Water | 810.83 | Fail | Fail | 0 | 2 | 289 | 2022-06-15 07:43 | 2022-06-21 17:00 | 2022-06-23 16:00 | 2022-06-21 17:00 | 2022-07-05 17:00 |  |  | sealed around floor waste and pipe penetration hole
MSA-DTWD | WA5289472 | 2 | LIGHTHOUSE LOCKSMITHS | Whole Block - faulty keys x 6 | Security | Locksmith | 180 | Pass | Fail | -1 | 1 | 288.75 | 2022-03-24 09:45 | 2022-03-29 17:00 | 2022-03-25 08:30 | 2022-03-29 17:00 | 2022-04-06 09:15 |  |  | Replaced 6 damaged keys for M block
MSA-DFES | WA5869330 | 3 | Protek 24/7 Building & Maintenance | SOC Catering cupboard - shelf has fallen down/broken | Furniture | Domestic Furniture | 533.49 | Pass | Fail | -1 | 1 | 288.5 | 2022-09-14 13:08 | 2022-09-21 17:00 | 2022-09-15 09:00 | 2022-09-21 17:00 | 2022-09-27 09:30 |  | WACCES | Remove damaged shelf and replace
MSA-DTAG | WA5390961 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Lower - Cell 2 - requires a bio-clean – prisoner blowing nose mucus on walls and floor | Cleaning | Emergency Cleans | 500 | Fail | Fail | 1 | 3 | 288.0333 | 2022-05-02 15:30 | 2022-05-03 17:00 | 2022-05-11 12:16 | 2022-05-03 17:00 | 2022-05-23 12:18 |  |  | As per Work Order No# 5390961
MSA-DCA | WA5392654 | 2 | GPS Plumbing & Gas Services PtyLtd | Leaking flusher valve in a cubicle in ladies’ toilets, HLT foyer | Plumbing & Drainage | Toilets/Cisterns | 484.11 | Pass | Fail | 0 | 1 | 287.7667 | 2022-05-03 11:14 | 2022-05-06 17:00 | 2022-05-04 16:00 | 2022-05-06 17:00 | 2022-05-16 15:46 |  | WACCES | Attend the leak cistern. Found leaking flush valve. Schell brand. Looking into getting replacement. Return and replace valve
MSA-DFES | WA6390513 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Staff Change Room -Lighting needing replacement | Electrical | General Electrical | 562.63 | Pass | Fail | -1 | 1 | 287.75 | 2022-12-22 10:02 | 2022-12-29 17:00 | 2022-12-22 14:00 | 2022-12-29 17:00 | 2023-01-03 13:45 |  | WACCES | Located faulty light in the male locker room replaced the light with new. Located other faulty light and replaced with new.
MSA-DTWD | WA5791467 | 3 | AWB Co. | Laneway garden, west of building-Security lighting bollard kicked over, wiring exposed | Electrical | General Electrical | 1236.16 | Pass | Fail | 0 | 1 | 287.75 | 2022-08-23 07:39 | 2022-08-29 17:00 | 2022-08-26 10:45 | 2022-08-29 17:00 | 2022-09-07 10:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located bollard. Isolated circuit. Replaced bollard. Re energised. Working as intended, completed paperwork. Signed out. Job complete
MSA-DTAG | WA5398378 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Various locations - Covid clean required - see notes below | Cleaning | Emergency Cleans | 500 | Fail | Fail | 0 | 2 | 287.7333 | 2022-05-09 09:55 | 2022-05-09 11:55 | 2022-05-11 12:21 | 2022-05-09 13:55 | 2022-05-23 12:05 |  |  | As per Work Order No# WA5398378
MSA-DTAG | WA5400478 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground - various locations - covid clean - see notes below | Cleaning | Emergency Cleans | 500 | Fail | Fail | 0 | 2 | 287.7 | 2022-05-10 11:00 | 2022-05-10 13:00 | 2022-05-11 12:23 | 2022-05-10 15:00 | 2022-05-23 12:05 |  |  | As per WA5400478
MSA-DTAG | WA5395141 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground - Chambers of President Buss - see details below | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 3 | 287.6667 | 2022-05-05 10:52 | 2022-05-05 12:52 | 2022-05-11 12:31 | 2022-05-05 14:52 | 2022-05-23 12:11 |  |  | As per Work Order No# WA5395141
MSA-DTAG | WA5396741 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground Level - Court 2 - Covid clean required - See notes | Cleaning | Cleaning | 500 | Fail | Fail | 0 | 2 | 287.65 | 2022-05-06 11:11 | 2022-05-09 17:00 | 2022-05-11 12:26 | 2022-05-09 17:00 | 2022-05-23 12:05 |  |  | As per work order no# WA5396741
MSA-DFES | WA6560402 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Yard - Drain closest to engine room - strong odour | Plumbing & Drainage | Sewer Drains & Septic Systems | 2258.36 | Pass | Fail | 0 | 2 | 287.25 | 2023-02-13 09:57 | 2023-02-16 17:00 | 2023-02-16 11:30 | 2023-02-16 17:00 | 2023-02-28 10:45 |  | WCAPPR
MSA-DTWD | WA6538917 | 1 | BAKE-QUIP PTY LTD | Damaged function knob on Convotherm oven | Equipment | Catering Equipment | 529.35 | Fail | Fail | 1 | 3 | 287 | 2023-02-08 08:58 | 2023-02-09 17:00 | 2023-02-16 11:00 | 2023-02-09 17:00 | 2023-02-28 10:00
MSA-DTWD | WA5567047 | 3 | Falcetta Plumbing and Gas | 207 - DHW unit not working | Plumbing & Drainage | HWS/Units Electric & Gas | 994.34 | Pass | Fail | -1 | 1 | 287 | 2022-06-23 14:05 | 2022-06-30 17:00 | 2022-06-23 19:00 | 2022-06-30 17:00 | 2022-07-05 18:00 |  |  | replaced hot water unit, reset circuit breaker, holesawed cabinet to route power and water
MSA-DTWD | WA5683084 | 2 | AWB Co. | Water leak in the U017 | Roofing | Metal Roofing | 381.115 | Pass | Fail | 0 | 2 | 287 | 2022-07-29 16:08 | 2022-08-03 17:00 | 2022-08-03 13:45 | 2022-08-03 17:00 | 2022-08-15 12:45 |  |  | Found aircon flashings with split silicone.carried out repair
MSA-DFES | WA6675100 | 2 | Australian HVAC Services Pty. Ltd. | Stations Officer's room - Air Con is leaking water from unit onto wall | Air Conditioning | Room Air Conditioners | 1184.4 | Pass | Fail | 0 | 2 | 287 | 2023-02-27 15:23 | 2023-03-02 17:00 | 2023-03-01 13:00 | 2023-03-02 17:00 | 2023-03-13 12:00
MSA-DCA | WA6599913 | 0 | Protek 24/7 Building & Maintenance | Fence has been broken - security issue | Building | Steel Fencing & Gates | 1235.45 | Fail | Fail | 0 | 2 | 286.5 | 2023-02-17 08:57 | 2023-02-17 10:57 | 2023-02-17 11:30 | 2023-02-17 12:57 | 2023-03-01 10:00 |  | WACCES
MSA-DTWD | WA5586780 | 2 | Protek 24/7 Building & Maintenance | Passageway outside 5F12 - Water leak through light | Building | Ceiling | 473.94 | Pass | Fail | -1 | 1 | 286.25 | 2022-07-06 14:45 | 2022-07-11 17:00 | 2022-07-07 15:15 | 2022-07-11 17:00 | 2022-07-19 13:30 |  |  | Repaired leak to roof
MSA-DFES | WA4990817 | 1 | Critical Fire Protection & Training | Hydrant - ground floor - hydrant has damaged | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 2370 | Pass | Fail | 0 | 2 | 286 | 2022-01-04 11:58 | 2022-01-05 17:00 | 2022-01-05 14:00 | 2022-01-05 17:00 | 2022-01-17 12:00 |  |  | Brigade has driven off whilst hose attached to hydrant.We will need to rebuild the hydrant riser from the fence and up to the new hydrant head.
MSA-DTWD | WA5188872 | 2 | M Construction (WA) | hand wash dispensers have come away from their wall fittings | Building | Internal Walls | 412.65 | Pass | Fail | -1 | 1 | 286 | 2022-02-23 12:10 | 2022-02-28 17:00 | 2022-02-24 13:30 | 2022-02-28 17:00 | 2022-03-08 11:30 |  |  | Remove adhesive from wall and install soap dispenser.
MSA-DTWD | WA6131631 | 2 | AWB Co. | AG09 - Several Lights not working in classroom | Electrical | Lighting, Internal | 404.12 | Pass | Fail | 0 | 2 | 286 | 2022-10-31 08:41 | 2022-11-03 17:00 | 2022-11-02 09:00 | 2022-11-03 17:00 | 2022-11-14 07:00 |  | WCAPPR | Attended site signed in jsa completed. Found 6 tubes broken and s10 starters. Replaced with new and tested operationalJob completed
MSA-DTWD | WA5587366 | 3 | AWB Co. | Two Fluro light & two spot lights out | Electrical | Lighting, Internal | 568.4875 | Pass | Fail | -1 | 1 | 286 | 2022-07-07 07:27 | 2022-07-13 17:00 | 2022-07-07 10:00 | 2022-07-13 17:00 | 2022-07-19 08:00 |  |  | Attended site signed in jsa completed. replaced new drivers for two dali downlights and confirmed operational. also replaced electronic ballast in massage T52 classroom. Job completed
MSA-DFES | WA6389777 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Conference room - LED Lights faulty causing issues for other room uses - see notes below | Electrical | General Electrical | 334.65 | Pass | Fail | -1 | 1 | 285.75 | 2022-12-21 16:10 | 2022-12-28 17:00 | 2022-12-22 14:00 | 2022-12-28 17:00 | 2023-01-03 11:45 |  | WACCES | Located faulty light in the conference room. It is a led panel light that is flashing it will need replacement. Site add two extra lights onto the Job. They were in a office area with faulty tubes and starters. Replaced faulty tubes and starters with new. Will need to return with a new light and replace the one in the conference room. I have unplugged the light so the other lights can still be used.
MSA-DTWD | WA5681438 | 2 | BAKE-QUIP PTY LTD | SK3 4 x under bench gas ovens 5,6.7 & 8 on R/H side not lighting | Equipment | Catering Equipment | 1403.6 | Pass | Fail | -1 | 1 | 285.5 | 2022-07-28 11:56 | 2022-08-02 17:00 | 2022-07-29 15:30 | 2022-08-02 17:00 | 2022-08-10 13:00 |  |  | NOTE, MULIPLE OVENS. REFER TO SERVICE REPORT FOR DETAILS.
MSA-DTWD | WA5101850 | 2 | Damian Rak Electrical Pty Ltd | Faulty security light | Electrical | Lighting, External |  | Pass | Fail | -1 | 1 | 285.5 | 2022-02-03 15:41 | 2022-02-08 17:00 | 2022-02-04 13:00 | 2022-02-08 17:00 | 2022-02-16 10:30 |  |  | job copmleted - replaced faulty light lamp
MSA-DFES | WA5286320 | 2 | Water2water Pty Ltd | Unit 21 - Ground - Kitchen -Under sink filtered water system not working | Plumbing & Drainage | Water | 5485.31 | Pass | Fail | 0 | 2 | 285 | 2022-03-21 14:38 | 2022-03-24 17:00 | 2022-03-23 12:20 | 2022-03-24 17:00 | 2022-04-04 09:20 |  |  | Unit needs replacing New Zip unit installed. All tested & running to specs.
MSA-DCA | WA6376380 | 3 | Protek 24/7 Building & Maintenance | Level G-front desk UAT-lock mechanism is broken - see notes | Building | Doors | 410.94 | Pass | Fail | -1 | 1 | 285 | 2022-12-15 14:35 | 2022-12-22 17:00 | 2022-12-16 12:30 | 2022-12-22 17:00 | 2022-12-28 09:30 |  | WACCES | Replaced lock mechanism in door
MSA-DTWD | WA5188875 | 2 | M Construction (WA) | hand wash dispensers have come away from their wall fittings........................................ | Building | Internal Walls | 251.79 | Pass | Fail | -1 | 1 | 284.5 | 2022-02-23 12:15 | 2022-02-28 17:00 | 2022-02-24 12:30 | 2022-02-28 17:00 | 2022-03-08 09:00 |  |  | Removed adhesive off the wall and installed soap dispenser.
MSA-DFES | WA5478953 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Male FF Toilets - Industrial type extraction fan above male toilets - not working | Electrical | General Electrical | 934.08 | Pass | Fail | -1 | 1 | 284.5 | 2022-05-26 15:42 | 2022-05-31 17:00 | 2022-05-27 13:45 | 2022-05-31 17:00 | 2022-06-08 10:15 |  | WACCES | Arrived on site at 0900 to replace Industrial type extraction fan above male toilets. Replaced & reenergised ex fan, informed staff and left site at 1015.
MSA-DTAG | WA6393598 | 1 | Sapio Pty Ltd | Level 1 - Comms room - Lock not working | Security | Locksmith | 970.07 | Pass | Fail | 0 | 2 | 284 | 2022-12-29 07:07 | 2022-12-29 17:00 | 2022-12-29 15:00 | 2022-12-29 17:00 | 2023-01-10 11:00 |  |  | Work performed by Ryan Craven (29/12/2022):Attended site. Inspected mortice lock for Level 1 Comms Room, took photos for ordering new lock.Work performed by Michael Tomlinson (10/01/2023)Replaced lock on Comms Room Door on Level 1. Doors being cut over to Gallagher.
MSA-DTWD | WA5495212 | 3 | AWB Co. | 3B3 - 5 lights not working in class room | Electrical | Lighting, Internal | 1057.14 | Pass | Fail | -1 | 1 | 283.75 | 2022-06-08 10:16 | 2022-06-15 17:00 | 2022-06-09 14:00 | 2022-06-15 17:00 | 2022-06-21 09:45 |  | WACCES | Attended site and signed in. Completed JSA. Located 3b3. Disconnect and removed old lights. Supply and replace with new lights. Tested all okay. Signed out. Job complete
MSA-DFES | WA6249850 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | DO Applied Training office - 1 x down light not working-see notes | Electrical | Lighting, Internal | 588.24 | Pass | Fail | -1 | 1 | 283.75 | 2022-11-21 15:42 | 2022-11-28 17:00 | 2022-11-23 12:00 | 2022-11-28 17:00 | 2022-12-05 07:45 |  | WACCES | Continued work on site at 1200 to attend multiple faulty fluros around academy. Located 2 x faulty fluros in TDSC Office, 1 x faulty led panel in male locker and 1 x faulty downlight in DO Training Office. Replaced 2 x faulty fluro’s in TDSC Office. Surrounding wholesalers did not have parts required. Will need to return to site with parts to complete works in male locker and DO Applied Training office. Informed staff of works and left site at 1430.Matthew Kenney (02/12/2022) - Work NoteArrived onsite at 13:30 to replace downlight in DO office and led panel light in male locker, replaced downlight in DO office, all lights in DO office now working, went to replace LED panel light in locker room but was given a 1200x300 panel, but require 1200x600, will need to return with appropriate panel light to complete, advised staff of works and left site at 14:15.Matthew Kenney (05/12/2022) - Work NoteArrived onsite at 7:00 to replace faulty led panel in male locker, replaced faulty led
MSA-DTWD | WA6178856 | 2 | AWB Co. | Two DC outlet switches faulty on test bench | Electrical | General Electrical | 284.34 | Pass | Fail | 0 | 2 | 283 | 2022-11-14 14:07 | 2022-11-17 17:00 | 2022-11-17 14:15 | 2022-11-17 17:00 | 2022-11-29 09:15 |  | WACCES | Attended site and signed in. Liaised with site about works. Heard back from supplier, cannot source required outlet. Have advised site to change to 32v DC outlets. Not further works can be done. Silvio has advised me to keep it open until further notice. **job not complete**
MSA-DTAG | WA5834100 | 3 | Sapio Pty Ltd | Retrospective W/O- Ground - Magistrate office 6 glass break has changed state to open. See no | Security | Access Control | 489.9 | Pass | Fail | 0 | 1 | 282.5 | 2022-09-04 16:30 | 2022-09-09 17:00 | 2022-09-07 15:30 | 2022-09-09 17:00 | 2022-09-19 10:00 | 1 |  | Installed new glass break for Magistrates Office 6. Unshunted in Gallagher.
MSA-DFES | WA6426118 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Second Floor - Outside Men's toilet - Investigate sound of water | Plumbing & Drainage | Drainage | 264.4325 | Pass | Fail | -1 | 1 | 281.75 | 2023-01-12 14:41 | 2023-01-17 17:00 | 2023-01-12 14:45 | 2023-01-17 17:00 | 2023-01-24 08:30
MSA-DTWD | WA5163693 | 3 | Equans Mechanical Services Australia | B Block - Level 1 - BF9 - Air con not working | Air Conditioning | Room Air Conditioners | 455.23 | Pass | Fail | 0 | 2 | 280.55 | 2022-02-18 11:10 | 2022-02-25 17:00 | 2022-02-24 13:30 | 2022-02-25 17:00 | 2022-03-08 06:03 |  |  | Found the system stuck on heating, reset the air-conditioning system and the remote restarted on 21deg cooling. Test ran through several cycles all ok
MSA-DFES | WA5216458 | 1 | Australian HVAC Services Pty. Ltd. | BMS - in fault (fault alarm on chiller 1) | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Fail | 0 | 1 | 280.5 | 2022-03-11 10:29 | 2022-03-14 17:00 | 2022-03-11 11:30 | 2022-03-14 17:00 | 2022-03-23 04:00 |  |  | Found chiller 1 in condenser water flow loss fault. Swapped flow switch between chiller to confirm if switch is faulty. Returned to site and found no fault has occured. Will carry out further tests if fault occurs again.
MSA-DTWD | WA6131751 | 3 | Equans Mechanical Services Australia | Boiler 1 in fault - Boiler 2 not coming on | Mechanical Services | Boilers | 678.41 | Pass | Fail | -1 | 1 | 274.5 | 2022-10-31 09:33 | 2022-11-07 17:00 | 2022-11-03 | 2022-11-07 17:00 | 2022-11-14 10:30 |  |  | BOILER CHECKED. BMS NEEDS TO BE INVESTIGATED - HAVE ASKED BOILERTRONICS TO ATTEND
MSA-DTWD | WA6519322 | 2 | WESTERN IRRIGATION PTY LTD | Kendrew Grounds Retic not working to all stations | Landscaping & Gardening | Grounds Maintenance | 4524.69 | Pass | Fail | -1 | 1 | 274 | 2023-01-25 15:16 | 2023-01-31 17:00 | 2023-01-27 05:30 | 2023-01-31 17:00 | 2023-02-07 15:30
MSA-DTWD | WA5116296 | 2 | Equans Mechanical Services Australia | L Block - LG12B - Air conditioning unit FCUG.05 heating instead of cooling | Air Conditioning | Room Air Conditioners | 457.07 | Pass | Fail | 0 | 1 | 272 | 2022-02-11 13:16 | 2022-02-16 17:00 | 2022-02-14 08:00 | 2022-02-16 17:00 | 2022-02-25 16:00 |  |  | Found LG12B stuck on heating, LG05 LG02 & LF12 are stuck on fan only. Rebooted the system to see if it would reset back to normal, system didn't go back to normal will need to get controls tech in .
MSA-DTAG | WA6535117 | 3 | Australian HVAC Services Pty. Ltd. | L4-plantroom-Pump 1 indicates failure | Air Conditioning | Room Air Conditioners | 1646.16 | Pass | Fail | -1 | 1 | 270.5 | 2023-02-06 14:24 | 2023-02-13 17:00 | 2023-02-07 08:00 | 2023-02-13 17:00 | 2023-02-18 14:30
MSA-DTWD | WA5761804 | 1 | Precise Air Group | AC4 A Block South Wing - Not reaching temp; always too cold-see notes | Air Conditioning | Room Air Conditioners | 2590.5 | Pass | Fail | 0 | 2 | 270.2333 | 2022-08-18 11:53 | 2022-08-19 17:00 | 2022-08-19 07:44 | 2022-08-19 17:00 | 2022-08-30 13:58 |  |  | Carried out site inspection, carried out required gas leak repair. Charged system all running to specs
MSA-DFES | WA5393035 | 2 | Seme Solutions Pty Ltd | CCTV Camera 8 - no camera recordings | Security | CCTV Surveillance | 650 | Pass | Fail | 0 | 1 | 269.75 | 2022-05-03 14:13 | 2022-05-06 17:00 | 2022-05-04 09:30 | 2022-05-06 17:00 | 2022-05-15 15:15 |  | WCAPPR | Camera 8 wasn't working, Changed resolution and frame rate, camera 8 is different to all the other cameras so it doesn't match up to the others.
MSA-DTWD | WA5115541 | 1 | Precise Air Group | Block G - room G204 - Air Con not working | Air Conditioning | Room Air Conditioners | 2026.5 | Fail | Fail | 0 | 2 | 269.35 | 2022-02-11 07:21 | 2022-02-11 17:00 | 2022-02-14 07:39 | 2022-02-11 17:00 | 2022-02-25 13:00 |  | WACCES | Attended site and completed pre start paperwork andsigned in.Completed working at heights permit. Accessed unit and inspected. Found condenser fan motor to have failed. Fan motor + Outdoor pcb to be replaced Submitted details for braf.25/02/22Attended site and completed pre start paperwork and signed in. Completed working at heights permit. Set up work equipment and isolated /locked out unit. Removed and replaced 1x outdoor pcb , 1x outdoor fan motor. Applied new heat transfer paste on pcb. Checked over connections and reassembled unit. Test ran system. Found unit to start and run with out fault. No further works required. Packed up work equipment and completed paperwork.
MSA-DTAG | WA5216379 | 3 | Sapio Pty Ltd | Investigate SCN and record online devices and possible unwanted guests | Security | Access Control | 2050 | Pass | Fail | -1 | 1 | 268.7667 | 2022-03-11 09:44 | 2022-03-18 17:00 | 2022-03-11 09:44 | 2022-03-18 17:00 | 2022-03-22 14:30 |  | WCAPPR | carried out SCN audit
MSA-MRWA | WA6676302 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Roof - Aircon not starting | Air Conditioning | Room Air Conditioners |  | Pass | Fail | 0 | 2 | 268.5 | 2023-02-28 13:28 | 2023-03-03 17:00 | 2023-03-03 07:30 | 2023-03-03 17:00 | 2023-03-14 12:00
MSA-DTWD | WA5838926 | 3 | AWB Co. | Campus Grounds External - There are several external grounds lights not working- See notes below | Electrical | Lighting, External | 1205.4575 | Pass | Fail | 0 | 1 | 267.75 | 2022-09-09 07:30 | 2022-09-15 17:00 | 2022-09-12 09:00 | 2022-09-15 17:00 | 2022-09-23 12:45 |  | WCAPPR | .
MSA-DCA | WA6414962 | 3 | Protek 24/7 Building & Maintenance | Alexander Library Building - External area off Francis St - G Level - Concrete Slab (see notes) | Paving & Roadworks | Paving | 683.33 | Pass | Fail | -1 | 1 | 267.5 | 2023-01-11 11:16 | 2023-01-18 17:00 | 2023-01-13 08:15 | 2023-01-18 17:00 | 2023-01-24 11:45
MSA-DCA | WA5796396 | 2 | Precise Air Group | Chillers 1 & 2 continuously in alarm despite resetting | Refrigeration | Chiller | 253.38 | Pass | Fail | 0 | 1 | 266.9167 | 2022-08-26 10:59 | 2022-08-31 17:00 | 2022-08-29 08:00 | 2022-08-31 17:00 | 2022-09-09 10:55 |  |  | Attended site and signed in. Gained access to plantroom where chillers are located. Checked chiller 1 and found it was out on low evap temp alarm. This is an ongoing issue that is being monitored still. Checked chiller 2 and found it had tripped on high temp alarm, after investigation found that the condensing water pump had tripped. Reset and tested pump, found amps slightly high but still in the operating range. Suspect due to age of pump this was a nuisance trip, we will continue to monitor pump on maintenance. Recommend budgeting for repairs/ replacement of pump.
MSA-DTAG | WA5288628 | 1 | Midolo Building Services | Old Court House - Ground - Sir Lawrence Jackson Room - see details below | Building | General Building | 454.57 | Pass | Fail | 0 | 2 | 266.75 | 2022-03-23 11:58 | 2022-03-24 17:00 | 2022-03-24 09:00 | 2022-03-24 17:00 | 2022-04-04 11:45 |  | WACCES | Cancelled request by Natasha Leam - work not being approvedPainter has completed half the work - invoicing costs to date.
MSA-DTWD | WA5413323 | 3 | M Construction (WA) | External Pagola outside of D009 - BROKEN SHEETING ON TOP OF PAGOLA - 2-3 SHEETS | Building | General Building | 924.99 | Fail | Fail | 1 | 2 | 266.75 | 2022-05-12 10:14 | 2022-05-19 17:00 | 2022-05-23 12:45 | 2022-05-19 17:00 | 2022-06-03 15:30 |  | WACCES | Attended site and replaced damaged roof sheets as required.
MSA-DTWD | WA5880349 | 1 | AHS Services WA Pty Ltd (Anchor) | B208 female toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 1006.82 | Pass | Fail | 0 | 2 | 266.6333 | 2022-09-15 12:26 | 2022-09-16 17:00 | 2022-09-16 07:00 | 2022-09-16 17:00 | 2022-09-27 09:38 |  |  | Replaced with new one
MSA-DFES | WA5173225 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Water main burst on the property side | Plumbing & Drainage | Water | 1555.94 | Pass | Fail | 0 | 2 | 266.5167 | 2022-02-20 11:43 | 2022-02-20 13:43 | 2022-02-20 12:00 | 2022-02-20 15:43 | 2022-03-03 14:31 |  |  | Located to site after hours for a burst pipe found it was coming from the re-tick line caped it off to make safe will return to replace the pipe work.Returned back to site and dig up the old pipe work and removed the old line and solarnoid and ball valve redid the hole thing tested and working packed up and cleaned up.
MSA-DTWD | WA5111708 | 2 | Water2water Pty Ltd | FG39 kitchen - boiling water unit | Plumbing & Drainage | Water | 1820.94 | Pass | Fail | -1 | 1 | 265.9833 | 2022-02-10 10:19 | 2022-02-15 17:00 | 2022-02-11 12:01 | 2022-02-15 17:00 | 2022-02-22 14:00 |  | WACCES | Unit installed to specs.Attended diagnosed, Rheem not repairable must be replaced. Quoted to replace with new capex assets Quote approved to replace - returned and installed new Zip Econoboil 5 Litre Boiling Wallmount Unit SN 2021120905073 Prog No A40184359N
MSA-DTAG | WA5384183 | 2 | Midolo Building Services | Near Chief Justice’s Chambers/Judges Corridor on Ground Floor - Significant water leak - see notes | Roofing | Concrete Roof Construction | 479.4 | Pass | Fail | -1 | 1 | 265.5 | 2022-04-28 10:26 | 2022-05-03 17:00 | 2022-04-29 09:00 | 2022-05-03 17:00 | 2022-05-10 10:30 |  |  | SOURCE OF LEAK RESEALED & down pipes re secured
MSA-DTAG | WA5887936 | 3 | Midolo Building Services | Detention - Cell Door 2 - Window tinting is bubbled and peeled off | Building | Windows | 350.32 | Fail | Fail | 2 | 3 | 265.5 | 2022-09-16 11:27 | 2022-09-23 17:00 | 2022-10-06 07:00 | 2022-09-23 17:00 | 2022-10-17 08:30 |  | WACCES | New tinting installed to cell door window
MSA-DTAG | WA5308259 | 1 | Sapio Pty Ltd | Supreme Court Building - Intercom in cell 4 not working | Security | Monitoring | 722.22 | Pass | Fail | 0 | 1 | 265.25 | 2022-04-08 10:08 | 2022-04-11 17:00 | 2022-04-08 11:15 | 2022-04-11 17:00 | 2022-04-19 12:30 |  |  | Removed faulty intercom and installed replacement CI-CC. Tested and confirmed two way audio on intercom and CI3210.
MSA-DCA | WA5304815 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Main building - Basement - Freezer room -Investigate the ice build-up on the evaporator coil | Refrigeration | Freezers | 402.915 | Fail | Fail | 0 | 2 | 265 | 2022-04-05 10:00 | 2022-04-08 17:00 | 2022-04-11 08:00 | 2022-04-08 17:00 | 2022-04-22 09:00 |  |  | Attended site, signed in and accessed the freezer room. Identified a large ice build up on the floor and art work in quarantine. Returned the following week when art work was out of quarantine. The unit had been switched off and the ice removed. Switched the unit back on and found the condensate drain heating element faulty. Part required will be sent through as a quote.
MSA-DTWD | WA5714735 | 1 | Protek 24/7 Building & Maintenance | Drive way entry to car park 2 - Grate over drain has collapsed in road. | Building | Internal Walls | 337.595 | Pass | Fail | 0 | 1 | 265 | 2022-08-12 08:10 | 2022-08-15 17:00 | 2022-08-12 13:30 | 2022-08-15 17:00 | 2022-08-23 14:30 |  | WACCES | placed the grate back in position but the cones there as a warningplaced the grate back in position but left the cones there as a warningBraf Declined
MSA-DCA | WA5204948 | 2 | ADVANCED LOCK & KEY | Basement - Central stairwell - see details below | Security | Locksmith | 560 | Pass | Fail | 0 | 2 | 264.9167 | 2022-03-04 15:49 | 2022-03-10 17:00 | 2022-03-10 10:10 | 2022-03-10 17:00 | 2022-03-21 11:05 |  |  | Replace locks
MSA-DTWD | WA5499799 | 2 | AWB Co. | Campus passage ways and walk ways - Many lights not coming on at night | Electrical | General Electrical | 1374.72 | Pass | Fail | 0 | 1 | 264.5 | 2022-06-10 14:15 | 2022-06-15 17:00 | 2022-06-13 12:30 | 2022-06-15 17:00 | 2022-06-24 13:00 |  | WCAPPR | Attended site signed in jsa completed. Fixed various lights in walk ways. *** job completed ***
MSA-DFES | WA6249267 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Apron of Engine Room - Vertical feature lights in between each engine bay are u/s | Electrical | Lighting, Internal | 846.71 | Pass | Fail | -1 | 1 | 264.25 | 2022-11-21 11:02 | 2022-11-28 17:00 | 2022-11-21 14:30 | 2022-11-28 17:00 | 2022-12-02 14:45 |  | WACCES & WCAPPR | Replaced faulty tubes and ballast with new
MSA-DCA | WA6680760 | 0 | Precise Air Group | ground air con blowing hot air-L1 green room no cold air - see notes | Air Conditioning | Room Air Conditioners |  | Fail | Fail | 0 | 2 | 264.0167 | 2023-03-01 14:07 | 2023-03-01 16:07 | 2023-03-02 18:28 | 2023-03-01 18:07 | 2023-03-13 18:29
MSA-DFES | WA5568854 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Bay - Ground Level - Four tubed lights in the engine bay are not working | Electrical | Lighting, Internal | 487.95 | Pass | Fail | 0 | 2 | 264 | 2022-06-27 09:28 | 2022-07-04 17:00 | 2022-07-04 12:45 | 2022-07-04 17:00 | 2022-07-15 12:45 |  | WCAPPR | Arrived onsite at 10:45 to get keys for metro VFRS from the DFES academy, gained acess to site and found the engine bay was full of trucks and unable to erect 12ft ladder required to replace tubes and starters. Organised someone with a truck license to move all vehicles out to complete job as station is unmanned. Replaced tubes and starters inside lights and tested all good. Organised to have vehicles moved back in and site locked up. Left site at 12:45
MSA-DFES | WA6603897 | 3 | Protek 24/7 Building & Maintenance | External Fencing - two fencing sheets have partially seperated from support poles (see not | Building | Steel Fencing & Gates | 1318.99 | Pass | Fail | -1 | 1 | 263.75 | 2023-02-17 13:05 | 2023-02-24 17:00 | 2023-02-20 13:00 | 2023-02-24 17:00 | 2023-03-03 12:45 |  | WACCES
MSA-DTWD | WA6394029 | 1 | WESTERN IRRIGATION PTY LTD | Lost power to Irrigation system | Plumbing & Drainage | Water | 1859.4 | Pass | Fail | 0 | 2 | 263.5 | 2022-12-29 20:30 | 2022-12-30 17:00 | 2022-12-30 10:30 | 2022-12-30 17:00 | 2023-01-10 10:00 |  |  | 30/12/2022 Electrician attended to assess power issue but turned out to be leaking irrigation mainline.10/1/2023 Attempts to repair were unsuccessful. Returned to site with excavator and replaced components outright to eliminate possible future issues.
MSA-DTWD | WA6020038 | 2 | Techworks Plumbing | Drain near the plastering mixing area is full up and needs cleaning out.-see notes | Plumbing & Drainage | Drainage | 1477.32 | Pass | Fail | -1 | 1 | 263.45 | 2022-10-13 10:06 | 2022-10-18 17:00 | 2022-10-14 10:00 | 2022-10-18 17:00 | 2022-10-25 09:27 |  |  | Used a jetter machine after the suck truck came in to clean out the drains in the tiling area pit
MSA-DTWD | WA6109157 | 2 | AHS Services WA Pty Ltd (Anchor) | All of the floor wastes are holding water and slow to subside, partially blocked | Plumbing & Drainage | Drainage | 685.23 | Pass | Fail | 0 | 1 | 262.9833 | 2022-10-20 14:25 | 2022-10-25 17:00 | 2022-10-24 13:02 | 2022-10-25 17:00 | 2022-11-04 12:01 |  | WACCES | 24/10..unable to clear drains with plunger or hand snake4/11 picked up mini drain machine and used to clear drains
MSA-DTWD | WA5493548 | 2 | Equans Mechanical Services Australia | Secondary Htg W pump No 1 leaking - Plantroom flooded | Air Conditioning | Building HVAC Maintenance (Major Plant) | 3142.26 | Pass | Fail | 0 | 1 | 262.45 | 2022-06-07 09:04 | 2022-06-10 17:00 | 2022-06-09 12:32 | 2022-06-10 17:00 | 2022-06-20 10:59 |  | WACCES | Picked up repaired pump, Return back to site fitted pump and tested it. All OK no leaks
MSA-DTWD | WA5494961 | 3 | M Construction (WA) | Ground Floor - B Block Electrical - Gutters blocked please clear debris | Building | General Building | 523.05 | Pass | Fail | 0 | 1 | 262.25 | 2022-06-08 08:35 | 2022-06-15 17:00 | 2022-06-13 12:00 | 2022-06-15 17:00 | 2022-06-24 10:15 |  |  | Attended site to inspect reported blocked area. Returned to site during better weather to clean roof and gutter.
MSA-DTWD | WA6572946 | 3 | AWB Co. | Newcastle St Carpark - Signage vandalised requires replacement | Signage | General Signage | 886.9225 | Pass | Fail | 0 | 1 | 261.5 | 2023-02-14 09:50 | 2023-02-21 17:00 | 2023-02-20 11:30 | 2023-02-21 17:00 | 2023-03-03 09:00
MSA-DTWD | WA6256899 | 3 | AHS Services WA Pty Ltd (Anchor) | damaged toilet seats in the female toilets - multiple levels - see notes | Plumbing & Drainage | Toilets/Cisterns | 3930.0975 | Pass | Fail | -1 | 1 | 261.2333 | 2022-11-24 09:47 | 2022-12-01 17:00 | 2022-11-25 14:30 | 2022-12-01 17:00 | 2022-12-06 11:44 |  |  | Completed
MSA-DFES | WA6112316 | 0 | ACTION GLASS & ALUMINIUM | Rear smashed window will need to be boarded up | Glazing | Window Glass | 1030.12 | Pass | Fail | 0 | 2 | 261.0667 | 2022-10-21 15:38 | 2022-10-21 17:38 | 2022-10-21 17:26 | 2022-10-21 19:38 | 2022-11-01 14:30 |  |  | ATTENDED SITE AFTER HOURSBOARDED UP BROKEN WINDOW1-1440 X 1080PLUS SILICONE AND 12 SCREWS RETURNED LATER DATE WITH 2 MEN REMOVED BOARD, SECURITY SCREENS AND FIXED PANEL REGLAZED WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-1380 X 1047REFIT FIXED PANEL AND SECURITY SCREENS 32 RIVETS USEDAS PER APPROVED BRAF
MSA-DFES | WA5472234 | 3 | SONTEC WA PTY LTD | Server Room - SEE DETAILS BELOW | Security | CCTV Surveillance | 705.5 | Fail | Fail | 1 | 2 | 260.75 | 2022-05-23 16:15 | 2022-05-30 17:00 | 2022-06-03 15:15 | 2022-05-30 17:00 | 2022-06-14 12:00 |  |  | 3/6/22 - Dean SimpsonTested Power supply 3 for CCTV cameras.No voltage, replacement required. 14/6/22 - Dean SimpsonReplaced power supply.Tested all working correctly.
MSA-DTWD | WA5696776 | 3 | Equans Mechanical Services Australia | Investigate Coolant leak Chiller 2 | Refrigeration | Chiller | 945.945 | Pass | Fail | -1 | 1 | 260.6 | 2022-08-08 14:28 | 2022-08-15 17:00 | 2022-08-08 15:00 | 2022-08-15 17:00 | 2022-08-19 11:36 |  |  | On inspection of chillers noted a small oil patch with indication of a refrigerant leak. Further investigation determined ends of multiple coils copper pitted and corroded. Investigated further for potential leaks and found refrigerant leaks on several coils on various condensers coils of multiple stages of both chillers. At the time only two stages were available, one of which had a refrigerant leak, as chiller 1 was locked out due to sensor issues, and no 2 C stage was locked out due to valve issues. Found up on sensors and had them expedited to bring at least one other stage on line. As one also has a refrigerant leak. Investigated assessed and options and liaised with various techs and contractors to facilated options. Options need to be considered as short term - summer is around the corner. Long term replacing coils is a good option but may not be financially viable as against new chiller.
MSA-DCA | WA6675884 | 2 | Critical Fire Protection & Training | Level 1 - Stage door/FOHM desk - Various panel alarm & fault issues reported over the weekend | Fire Protection Services | Fire Protection - Monitor System | 1873.45 | Pass | Fail | 0 | 1 | 260 | 2023-02-28 10:14 | 2023-03-03 17:00 | 2023-03-01 14:00 | 2023-03-03 17:00 | 2023-03-12 10:00
MSA-DTWD | WA5217078 | 1 | AWB Co. | From Simpson Avenue entrance to F Block - Car park lights - see notes below | Electrical | Lighting, External | 2482.78 | Pass | Fail | 0 | 2 | 260 | 2022-03-11 16:12 | 2022-03-14 17:00 | 2022-03-14 11:30 | 2022-03-14 17:00 | 2022-03-25 07:30 |  | WCAPPR | Attended site signed in completed jsa. Peformed all pre start checks on mobile plant. Installed new led head on pole in car park. Tested and works fine. ** job completed ****under charged for works - charged as per BRAF**
MSA-DFES | WA5674703 | 0 | Protek 24/7 Building & Maintenance | Dormitories-Water leaking into dormitories along base of southern wall, when raining, - see notes | Roofing | Metal Roofing | 318.1 | Pass | Fail | 0 | 2 | 258.75 | 2022-07-21 13:24 | 2022-07-21 15:24 | 2022-07-21 14:30 | 2022-07-21 17:24 | 2022-08-01 09:15 |  |  | Water ingress to internal dorm rooms carpet tiles are wet and may require replacement at later date Bottom skirting boards may require replacement at later date
MSA-DCA | WA6560442 | 1 | ACTION GLASS & ALUMINIUM | Percussion Room - Broken window | Glazing | Window Glass | 889.7 | Pass | Fail | 0 | 1 | 258.5833 | 2023-02-13 10:09 | 2023-02-14 17:00 | 2023-02-13 14:45 | 2023-02-14 17:00 | 2023-02-24 09:20
MSA-DTWD | WA5089825 | 2 | AWB Co. | GPO's and Conduit damaged along East wall of laboratory | Electrical | General Electrical | 787.44 | Pass | Fail | 0 | 2 | 258.5 | 2022-01-25 06:57 | 2022-01-28 17:00 | 2022-01-28 15:00 | 2022-01-28 17:00 | 2022-02-08 09:30 |  |  | Attended site and signed in. Reviewed JSA. re located room b27. Set up work area. Repeated steps from last desk onto this desk. Fit off everything. Took pictures. Packed and cleaned up. Completed paperwork. Signed out.*** job complete ***
MSA-DTWD | WA5289330 | 2 | AWB Co. | faulty exhaust fan | Electrical | General Electrical | 899.68 | Pass | Fail | -1 | 1 | 258.5 | 2022-03-24 08:34 | 2022-03-29 17:00 | 2022-03-24 14:30 | 2022-03-29 17:00 | 2022-04-04 09:00 |  |  | Attended site and signed in, reviewed JSA, set up work area, removed access hole cover , fitted mounting gear, remounted fan, re attached flumes to both sides, wired in cables to isolators, re energised circuit, tested fan and is working as intended, cleaned up work area, completed paperwork replaced access hole cover , signed outJob completed
MSA-DFES | WA5656588 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - six lights out in Information Resources work area very dark | Electrical | Lighting, Internal | 226.2 | Pass | Fail | -1 | 1 | 257.5833 | 2022-07-18 15:05 | 2022-07-25 17:00 | 2022-07-18 15:10 | 2022-07-25 17:00 | 2022-07-29 08:45 |  |  | Arrived on site at 08:15. Went to resource work area and located 6 x lights out, replaced tube in each and tested all okay, left site at 08:45
MSA-MRWA | WA5368718 | 2 | Dormakaba Australia Pty Ltd | Door close not remaining open, broken nylon part / slider - see notes below | Building | Doors | 1195.06 | Pass | Fail | 0 | 1 | 257.4167 | 2022-04-19 12:29 | 2022-04-22 17:00 | 2022-04-19 15:55 | 2022-04-22 17:00 | 2022-04-30 09:20 |  |  | 19/4/22 - Found old Yale closer slide block has snapped and the closer no longer holds opens. Requires Dorma ts93G Push with hold open slide block.30/4/22 - Removed existing faulty door closer and supplied and fitted new ts93 closer complete with hold open device, adjusted and tested operation upon completion and left in good working order.
MSA-DTWD | WA5394253 | 2 | M Construction (WA) | U024.3 - Door closer faulty | Building | General Building | 1109.38 | Fail | Fail | 0 | 2 | 256 | 2022-05-04 14:22 | 2022-05-09 17:00 | 2022-05-12 08:15 | 2022-05-09 17:00 | 2022-05-23 00:15 |  |  | Attended site to investigate, found door closer to be broken, left site to source parts, returned to replace.
MSA-DTAG | WA5795040 | 2 | Sapio Pty Ltd | Court 2 Court 3 ALS office-Incorrect alarm in Courts 2 & 3 ALS office duress alarm cable not fixed | Security | Security Management System | 1854.33 | Pass | Fail | 0 | 1 | 253.5 | 2022-08-25 09:19 | 2022-08-30 17:00 | 2022-08-29 13:30 | 2022-08-30 17:00 | 2022-09-09 03:00 |  |  | Replaced all duress buttons and recabled
MSA-DTWD | WA6600173 | 2 | AWB Co. | Oil and Gas Plant compressor shed - Wires hanging down from ceiling (see notes - cherry picket req.) | Electrical | Distribution Board | 664.9 | Pass | Fail | 0 | 1 | 246.5 | 2023-02-17 09:12 | 2023-02-22 17:00 | 2023-02-20 08:30 | 2023-02-22 17:00 | 2023-03-02 15:00 |  | WACCES
MSA-DCA | WA5087968 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Commercial Kitchen - Replace broken 3Phase RCD Socket outlet | Electrical | General Electrical | 900.4825 | Pass | Fail | 0 | 1 | 246 | 2022-01-24 15:49 | 2022-02-01 17:00 | 2022-02-01 07:30 | 2022-02-01 17:00 | 2022-02-11 13:30 |  |  | Arrived on site at 730am. Bruce was not on site yet. I was able to get in and was taken to the kitchen. I found a damaged 3 phase GPO with a RCD. Confirmed with Bruce once he arrived. I called the local wholesalers but the part was not on the shelf. Will need to order new parts and return to install. I have taped the GPO so it is held together. Please call Bruce to arrange a suitable time to replace the parts.
MSA-DTWD | WA5468536 | 2 | Damian Rak Electrical Pty Ltd | BLD 822A - Reception - Faulty Lights buzzing | Electrical | Lighting, Internal |  | Pass | Fail | 0 | 1 | 246 | 2022-05-20 10:22 | 2022-05-25 17:00 | 2022-05-23 11:00 | 2022-05-25 17:00 | 2022-06-02 17:00 |  |  | Job completed
MSA-DCA | WA5494370 | 2 | Protek 24/7 Building & Maintenance | Level 5 - External Doors - new coat of paint needed for doors | Building | General Building | 1000 | Fail | Fail | 1 | 2 | 245.5 | 2022-06-07 14:31 | 2022-06-10 17:00 | 2022-06-14 09:30 | 2022-06-10 17:00 | 2022-06-24 15:00 |  |  | paint doors
MSA-DCA | WA5696599 | 3 | Techworks Electrical | First Floor - Administration Building - Exterior Light over door- Security Lights not working | Electrical | Lighting, Internal | 2677.34 | Pass | Fail | 0 | 1 | 245.5 | 2022-08-08 13:13 | 2022-08-15 17:00 | 2022-08-15 08:30 | 2022-08-15 17:00 | 2022-08-25 14:00 |  | WACCES | Inspected security lights out. Sourced boom and lights. Replaced x3 floods at high level and x2 emergency batten lights job not assigned to me on promapmaterials:x3 100w led floodsx2 4 foot weather proof emergency battens
MSA-DTWD | WA6178874 | 2 | SCAVENGER SUPPLIES PTY LTD | B32 - Smoke alarm attached to ceiling is faulty | Fire Protection Services | Smoke and Heat Detection | 418.53 | Pass | Fail | 0 | 1 | 244.8333 | 2022-11-14 14:21 | 2022-11-17 17:00 | 2022-11-15 09:00 | 2022-11-17 17:00 | 2022-11-25 13:50 |  | WACCES | attended 15/11/2022 investigate-materials to be orderedcomplete 25/11/2022
MSA-DTAG | WA6129235 | 3 | Midolo Building Services | 1987-external-footpath-Pavers in south east walkway leading to staff car park are uneven – trip haza | Paving & Roadworks | Paving | 985.59 | Pass | Fail | -1 | 1 | 244.5 | 2022-10-27 12:40 | 2022-11-03 17:00 | 2022-10-28 09:30 | 2022-11-03 17:00 | 2022-11-07 14:00 |  |  | closing off ctd - we have solved one issue however tree roots are a bigger issue and require resolving before we can repair. Iain has advised to close off - see email attached
MSA-DTWD | WA6129230 | 1 | Australian Airconditioning Services Pty Ltd | ground-Painting and Decorating Spray Booth- Exhaust fans noisy and smell of rubber burning | Air Conditioning | Room Air Conditioners | 1450.47 | Fail | Fail | 0 | 2 | 243.5 | 2022-10-27 12:35 | 2022-10-28 17:00 | 2022-10-31 10:00 | 2022-10-28 17:00 | 2022-11-10 13:30 |  |  | Picked up and fitted new cover plate for belts on spray booth ventilation. Tested operation. All ok
MSA-DTWD | WA6148387 | 2 | Australian Airconditioning Services Pty Ltd | AC Faulty - LG Split AC – Turns itself off and light flashes 5 times, indicating comms fault | Air Conditioning | Room Air Conditioners | 1254.65 | Pass | Fail | -1 | 1 | 243.5 | 2022-11-03 16:49 | 2022-11-08 17:00 | 2022-11-04 12:00 | 2022-11-08 17:00 | 2022-11-14 15:30 |  |  | Found LG wall split displaying fault lights that indicate communication error. Investigated outdoor unit and found gecko had short circuited pcb. New pcb assembly required.
MSA-DFES | WA5839228 | 2 | Protek 24/7 Building & Maintenance | Kitchen - Crack in ceiling and cornice | Building | Ceiling | 506.36 | Pass | Fail | 0 | 1 | 243.25 | 2022-09-09 10:35 | 2022-09-14 17:00 | 2022-09-13 09:15 | 2022-09-14 17:00 | 2022-09-23 12:30 |  |  | Apply adhesive to cornice and walls, patched and painted ceiling
MSA-DTAG | WA5460485 | 1 | High Tech Maintenance | Roof - Gutter - Blocked Gutter causing flooding in Mag 2 office | Building | General Building |  | Fail | Fail | 0 | 2 | 243.1167 | 2022-05-18 14:25 | 2022-05-19 17:00 | 2022-05-20 08:53 | 2022-05-19 17:00 | 2022-05-30 12:00 |  |  | 20.5.22 Two Gutter cleaning team members arrived and went to the roof to assess the condition where the down pipe had blocked.Overall, other areas of the roof had been cleaned well and there were little signs of leaves,given that there had been recent rainfall. the reason why this area wasnt cleaned well is that the grid mesh blocks access to the area for inspection and access to cleaning.This is also the reason why it wasnt reported on 12.5.22, because the built up excrement whicheventually slid down the roof with the rainfall to block the gutter was concealled under the framework supporting the air conditionsing units. The mesh ontop prevents visual inspection and access with anything other than water to clean the area.In the Aircon area, we could see the blocked downpipe, but couldnt remove the blockageof bird excrement by hand because the mesh was in the way. This had moved from under the AC unitsto the downpipe in the gutter, since the heavy rain after the full gut
MSA-DTWD | WA5017056 | 2 | Techworks Electrical | E-Block - SK2 - tagged out oven needs fixing it keeps tripping the RCD | Electrical | General Electrical | 396.805 | Pass | Fail | -1 | 1 | 243 | 2022-01-13 09:50 | 2022-01-18 17:00 | 2022-01-14 12:30 | 2022-01-18 17:00 | 2022-01-24 15:30 |  | WACCES | Replaced faulty thermostat in oven
MSA-DTAG | WA5838637 | 3 | Sapio Pty Ltd | Level 11 - sliding door faulty - see notes below | Building | Security Doors | 269 | Pass | Fail | -1 | 1 | 243 | 2022-09-08 16:28 | 2022-09-15 17:00 | 2022-09-09 11:30 | 2022-09-15 17:00 | 2022-09-19 14:30 |  |  | Rectified fault
MSA-DFES | WA6528739 | 2 | Protek 24/7 Building & Maintenance | Level 1 - Please see notes | Building | General Building | 469.51 | Pass | Fail | 0 | 1 | 243 | 2023-02-02 12:05 | 2023-02-07 17:00 | 2023-02-06 09:00 | 2023-02-07 17:00 | 2023-02-16 12:00 |  | WACCES
MSA-DCA | WA5978621 | 3 | FCT SURFACE CLEANING | Ground Floor - PCC Exterior - Urban Orchard – Northern End - Graffiti | Cleaning | Graffiti |  | Pass | Fail | -1 | 1 | 242.5 | 2022-09-28 11:53 | 2022-10-05 17:00 | 2022-09-30 11:00 | 2022-10-05 17:00 | 2022-10-10 13:30 |  |  | Removal of graffiti
MSA-DTWD | WA5994853 | 2 | BAKE-QUIP PTY LTD | Canteen -temperature switch on hot box not working – spinning around- See notes | Equipment | Catering Equipment | 504.19 | Pass | Fail | 0 | 1 | 242.25 | 2022-10-06 09:18 | 2022-10-11 17:00 | 2022-10-10 13:00 | 2022-10-11 17:00 | 2022-10-20 15:15 |  | WACCES | REFER TO SERVICE REPORT.
MSA-DTAG | WA5392189 | 3 | AHS Services WA Pty Ltd (Anchor) | Remove roof penetration through the airconditioning system to allow repair of membrane. | Roofing | Metal Roofing | 494.91 | Pass | Fail | -1 | 1 | 242.1 | 2022-05-03 08:22 | 2022-05-10 17:00 | 2022-05-06 06:44 | 2022-05-10 17:00 | 2022-05-16 08:50 |  |  | Completed
MSA-DTWD | WA5998009 | 2 | Techworks Plumbing | M Block - Floor Drain is blocked | Plumbing & Drainage | Drainage | 3411.48 | Pass | Fail | 0 | 1 | 242 | 2022-10-07 11:22 | 2022-10-12 17:00 | 2022-10-10 06:30 | 2022-10-12 17:00 | 2022-10-20 08:30 |  |  | attended site at balga tafe and contacted Darren, he wasn’t on site when we got here but he said the blocked floor drain was in m block and he would get someone to meet us down there, we got there and couldn’t find a blocked floor drain and none of the lecturers knew where it was, so we waited for Darren to get to site and he showed us where they were.they actually ended up being soak wells that were full of water and sand because of all the bricklaying in that block, they had dug it out as far as they could with shovels. and now they want us to get a truck to come and suck the pits out.left site and completed paperwork
MSA-DTWD | WA6450285 | 2 | Equans Mechanical Services Australia | Chiller 2 compressor 2 bearing fault | Refrigeration | Chiller | 1414.42 | Fail | Fail | 3 | 5 | 242 | 2023-01-16 10:34 | 2023-01-19 17:00 | 2023-02-10 12:00 | 2023-01-19 17:00 | 2023-02-20 14:00
MSA-DTWD | WA5795190 | 3 | AWB Co. | 6 x lights out Light panel hanging - 601 | Electrical | Lighting, Internal | 838.185 | Pass | Fail | -1 | 1 | 241.75 | 2022-08-25 09:44 | 2022-09-01 17:00 | 2022-08-26 13:15 | 2022-09-01 17:00 | 2022-09-05 15:00 |  | WCAPPR | Attended site and signed in, completed JSA,spoke with fm about job,isolated lighting circuits on level 6 and removed faulty fittings, replaced with new , tested lights and working as intended, cleaned up, packed up, completed paperwork, signed out**job completed**
MSA-DTWD | WA5289934 | 1 | Equans Mechanical Services Australia | Room 208,209,211,212, & 214 - BMS aircon - aircon not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2900.39 | Pass | Fail | 0 | 1 | 241.5 | 2022-03-24 14:31 | 2022-03-25 17:00 | 2022-03-25 08:30 | 2022-03-25 17:00 | 2022-04-04 10:00 |  |  | REPAIR LEAK BY REPLACING BROKEN CAPILLARY LINE, EVACUATE, PRESSURE TEST AND CHARGE UNIT WITH R410A. TURN UNIT ON, MONITOR RUNNING PRESSURES AND CHECK TEMPERATURE DIFFERENCE ACROSS EVAPORATOR COIL FOR A PERIOD OF TIME, ALL OK AT THIS TIME.
MSA-DFES | WA5304766 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Front of station - All rooms - Blocked soak wells (all) front of station | Plumbing & Drainage | Drainage | 1542.7 | Pass | Fail | 0 | 1 | 241.5 | 2022-04-05 09:40 | 2022-04-12 17:00 | 2022-04-12 10:30 | 2022-04-12 17:00 | 2022-04-22 12:00 |  |  | Located to site cause the storm water drains are slow to drain found they are blocked tried running the drain machine down and wasn’t moving will need a jetter and suck truck to do the job 22/4/22 Returned back to site with tunnel vision and cleared 3 out of the 4 the fourth drain is running to no where. Due to its an open ended pipe will await further instructions.
MSA-DFES | WA4990888 | 1 | SONTEC WA PTY LTD | Back Gate - unable to use any fobs or swip cards to access the gate - see notes below | Security | Access Control | 2186.13 | Pass | Fail | 0 | 1 | 241.25 | 2022-01-04 12:49 | 2022-01-05 17:00 | 2022-01-04 14:30 | 2022-01-05 17:00 | 2022-01-14 15:45 |  |  | 4/1/22 - Dylan ParslowReset door controller.Recommend relocating and replacing door controller. BRAF submitted.14/1/22 - Dean Simpson, Dylan ParslowRelocated and replaced door controller in new enclosure.
MSA-DTWD | WA5413833 | 2 | AWB Co. | Stairwell - Block D - Level 1 & G - South Side - glass windows leaking again | Building | Windows | 375 | Pass | Fail | 0 | 1 | 241 | 2022-05-12 13:59 | 2022-05-17 17:00 | 2022-05-17 08:00 | 2022-05-17 17:00 | 2022-05-27 09:00 |  |  | ATTENDED SITE TWICEFOR ASSESSING WORKS TO BE QUOTED
MSA-DCA | WA5534623 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - please see details below | Air Conditioning | Room Air Conditioners | 686.05 | Pass | Fail | -1 | 1 | 241 | 2022-06-16 12:28 | 2022-06-21 17:00 | 2022-06-17 15:00 | 2022-06-21 17:00 | 2022-06-27 16:00 |  |  | Attended site signed in and found supply air temperature setpoints on all ahus not adjusting automatically - Honeywell to attend site and rectify controlls issues.HoneywellSA-702447 - Dmitriy Chudaev - 17/06/2022 8:00 PM - Reconfigure terminal load calculations and SAT SP reset functions
MSA-DTAG | WA6362863 | 2 | Schindler Lifts Australia | Ground floor - lift 10 - showing out of service | Lifts | Lifts |  | Pass | Fail | -1 | 1 | 241 | 2022-12-09 14:09 | 2022-12-14 17:00 | 2022-12-09 14:30 | 2022-12-14 17:00 | 2022-12-19 15:30 |  |  | T1 errors on multiple days this week due to power outages in the CBD. T4 errors due to clutch not compressed as needs a reference run. Carried out same. Tested lift no issues clipping locks. Lift back in service.
MSA-MRWA | WA5177088 | 1 | Water2water Pty Ltd | Alfresco area - Ice Machine - faulty machine | Plumbing & Drainage | Water | 1226.0775 | Pass | Fail | 0 | 1 | 240.8333 | 2022-02-21 14:56 | 2022-02-22 17:00 | 2022-02-22 08:55 | 2022-02-22 17:00 | 2022-03-04 09:45 |  | WACCES | Replaced circulating pump and float assembly A40191157H
MSA-DTAG | WA5887956 | 2 | Water2water Pty Ltd | Admin Services Kitchen - Billi tap flashing orange (both hot and cold) | Plumbing & Drainage | HWS/Units Electric & Gas | 844.73 | Pass | Fail | 0 | 1 | 240.4167 | 2022-09-16 11:37 | 2022-09-21 17:00 | 2022-09-19 14:20 | 2022-09-21 17:00 | 2022-09-29 14:45 |  |  | BRAF Submitted, additional works required. Iain to approve. All repairs and testing completed as per BRAF quoted, all okay on departure.
MSA-DCA | WA5290370 | 0 | Automatic Fire Protection (ARA) | Ground - admin area - fire panel - fault code red | Fire Protection Services | Fire Protection - Monitor System | 758.35 | Pass | Fail | 0 | 1 | 240.25 | 2022-03-25 08:26 | 2022-03-25 10:26 | 2022-03-25 10:00 | 2022-03-25 12:26 | 2022-04-04 10:15 |  | WCAPPR | 25/03/2022Attended site intermittent fault on Wagner system zone 42 auditorium MASDS in history. Checked Wagner in plantroom and found from fault code it is in low airflow fault. As auditorium was being used for recording unable to clear out pipes and sampling tubes. Spoke with Bruce onsite and we have booked in for the 4/4/22 for 2-4hrs with 2 techs to vacuum out pipes and clear out sampling tubes and points that are all accessible from catwalk above auditorium. Advised code red monitoring that there will be a fault on the system till the above date.4/4 KS Attended site and checked and cleaned all sample points where possible and also adjusted flow fault setting to next setting up to large.Checked and left system normal.
MSA-DFES | WA5687321 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Outside Roof - 1 Glass tube on Solar Hot water system smashed on the Western side of the roof | Plumbing & Drainage | Water | 842.4 | Pass | Fail | 0 | 1 | 240.25 | 2022-08-01 15:46 | 2022-08-02 17:00 | 2022-08-02 09:15 | 2022-08-02 17:00 | 2022-08-12 09:30 |  | WACCES | Broken Solar Tubes on roof, sorced, ordered and replaced.
MSA-DCA | WA5081490 | 1 | Protek 24/7 Building & Maintenance | Fiji Room – vandalism panel to be removed to access extractor fan - see notes below | Building | External Walls | 481.5 | Pass | Fail | 0 | 1 | 240.0167 | 2022-01-20 14:34 | 2022-01-21 17:00 | 2022-01-21 11:15 | 2022-01-21 17:00 | 2022-01-31 11:16 |  | WACCES | Installed fan mount and fly screen
MSA-DFES | WA6405392 | 2 | AWB Co. | Dorms - External door handle to the toilet in the ensuite between dorms 17 & 18 is broken off | Building | Doors | 658.765 | Pass | Fail | 0 | 1 | 240 | 2023-01-09 12:39 | 2023-01-12 17:00 | 2023-01-10 09:00 | 2023-01-12 17:00 | 2023-01-20 09:00
MSA-DTWD | WA6540639 | 3 | Australian Airconditioning Services Pty Ltd | AC drainage needs to be fized. 2 techs required for roof access | Air Conditioning | Ducted Split System | 1471.64 | Pass | Fail | 0 | 1 | 240 | 2023-02-09 12:19 | 2023-02-16 17:00 | 2023-02-14 10:30 | 2023-02-16 17:00 | 2023-02-24 10:30 |  | WACCES
MSA-DTWD | WA5796241 | 3 | Equans Mechanical Services Australia | C800- Cavitation in Chilled water pipes, investigation of expansion tanks required | Refrigeration | Chiller | 670.05 | Pass | Fail | -1 | 1 | 239.75 | 2022-08-26 09:03 | 2022-09-02 17:00 | 2022-08-29 13:15 | 2022-09-02 17:00 | 2022-09-08 13:00 |  |  | Attended site, found chiller 3 in fault.Chilled water pipes have a lot of movement and there is flow faults on the chiller.Reset fault on CH-3 and chiller started.Located Expansion/Header tank on level 8 plantroom no safe access to check the float levels.Returned to site on Monday morning and chiller was in fault again.Looked at expansion tank access with supervisor and site FM.Air in CHW circuit appears to have dissipated.BMS wasn’t enabling CHW pumps or chiller.Manual enable and pump speeds and bypass position to start the system.Notified the Tafe to contact the BMS contractor to investigate BMS fault.
MSA-DFES | WA6402680 | 2 | Australian HVAC Services Pty. Ltd. | office and training room - air con not working - see notes | Air Conditioning | Ducted Split System | 1215.4 | Pass | Fail | -1 | 1 | 239.5 | 2023-01-05 14:51 | 2023-01-10 17:00 | 2023-01-06 13:30 | 2023-01-10 17:00 | 2023-01-16 13:00
MSA-MRWA | WA5838642 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Aircon is faulty - due to power failure | Air Conditioning | Building HVAC Maintenance (Major Plant) | 202.705 | Pass | Fail | 0 | 1 | 239.35 | 2022-09-08 16:44 | 2022-09-09 17:00 | 2022-09-09 13:30 | 2022-09-09 17:00 | 2022-09-19 12:51 |  |  | Attended job, checked ACs for control room and CRAC. All operating normally. Monitored. No further issues.
MSA-DFES | WA6431031 | 3 | AWB Co. | Ground - Concrete pit cover is broken | Paving & Roadworks | Concreting | 1317.6525 | Pass | Fail | 0 | 1 | 239.25 | 2023-01-13 11:18 | 2023-01-20 17:00 | 2023-01-20 13:00 | 2023-01-20 17:00 | 2023-01-30 12:15 |  | WACCES
MSA-DFES | WA5274076 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Station Officers Bathroom - Small leak from “Flick Mixer” in Station Officers Bathroom/Shower | Plumbing & Drainage | Water | 283.2 | Pass | Fail | -1 | 0 | 239 | 2022-03-18 11:14 | 2022-03-25 17:00 | 2022-03-18 14:30 | 2022-03-25 17:00 | 2022-03-28 13:30 |  | WACCES | Replaced cartridge on mixer tap.
MSA-DCA | WA6415263 | 2 | GPS Plumbing & Gas Services PtyLtd | Mezzanine - Men's Toilet - Men’s Toilets, 3rd cubicle along, toilet button broken | Plumbing & Drainage | Toilets/Cisterns | 432.5875 | Pass | Fail | 0 | 1 | 238.9167 | 2023-01-11 14:40 | 2023-01-16 17:00 | 2023-01-13 12:35 | 2023-01-16 17:00 | 2023-01-23 11:30 |  | WACCES
MSA-DTWD | WA5190802 | 2 | Water2water Pty Ltd | M Block - Plastering workshop - Training floor - drink fountain is not cold | Plumbing & Drainage | Water | 1897.0775 | Pass | Fail | 0 | 1 | 238.9 | 2022-02-24 14:45 | 2022-03-01 17:00 | 2022-02-28 12:36 | 2022-03-01 17:00 | 2022-03-10 11:30 |  |  | Found compressor is blown replacement required. Quote submitted New fountain installed as per capex asset
MSA-DTWD | WA5490609 | 2 | ACTION GLASS & ALUMINIUM | North facing, the glass door has been smashed | Building | Windows | 745.9 | Pass | Fail | 0 | 1 | 238.85 | 2022-06-03 07:44 | 2022-06-08 17:00 | 2022-06-07 11:45 | 2022-06-08 17:00 | 2022-06-17 10:36 |  |  | ATTENDED SITE WITH 2 MEN REGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-1297 X 703RETURNED LATER DATE TO SUPPLY & FIT TINT FILM1-1297 X 703
MSA-DFES | WA5488319 | 2 | Water2water Pty Ltd | Level 1 - Kitchen - Hot/Cold water dispenser has a continuous leak | Plumbing & Drainage | HWS/Units Electric & Gas | 96.1175 | Pass | Fail | -1 | 1 | 238.8167 | 2022-06-02 11:56 | 2022-06-08 17:00 | 2022-06-03 13:00 | 2022-06-08 17:00 | 2022-06-13 11:49 |  | WACCES | TECHNICIAN TO RETURN AND SWAP OVER UNIT. CURRENT UNIT IS LEAKING. Replaced unit. Work restarted 8/6/22 15:30. Completed work 8/6/22 15:50
MSA-DTWD | WA4990978 | 2 | Protek 24/7 Building & Maintenance | D32 Commercial Kitchen External - Burst retic has lifted brick paving in 2 areas | Paving & Roadworks | Paving | 606.25 | Pass | Fail | 0 | 1 | 238.6667 | 2022-01-04 13:57 | 2022-01-07 17:00 | 2022-01-07 13:50 | 2022-01-07 17:00 | 2022-01-17 12:30 |  |  | Cut out tree roots, reset pavers
MSA-DTWD | WA5384337 | 1 | UNIVERSAL DOORS | L Block - Roller door - electric roller door stuck in up position wont close | Building | Roller Shutters |  | Fail | Fail | 4 | 5 | 238.5833 | 2022-04-28 12:00 | 2022-04-29 17:00 | 2022-05-24 13:50 | 2022-04-29 17:00 | 2022-06-03 12:25 |  |  | job completed - Supply and install 1 x Grifco thp, 3ph roller shutter operator and controller to replacethe existing faulty operator
MSA-DCA | WA6130337 | 1 | Techworks Electrical | Level B2 - Studio Underground Stage - 3 phase outlet is not locking - See notes below | Electrical | General Electrical | 843.085 | Pass | Fail | 0 | 1 | 238.5 | 2022-10-28 11:26 | 2022-10-31 17:00 | 2022-10-28 12:30 | 2022-10-31 17:00 | 2022-11-07 11:00 |  |  | 28/10/22Found switch continually rotating and not switching. Ordered colour replacement and orderd in a temp replacement for Monday. 31/10/22Replaced isolator with temp one as the required colour is special order.
MSA-DTWD | WA6539120 | 2 | Equans Mechanical Services Australia | T Block - Level 2 - Loud noise through various a/c vents | Air Conditioning | Room Air Conditioners | 1491.95 | Fail | Fail | 1 | 3 | 238.5 | 2023-02-08 10:40 | 2023-02-13 17:00 | 2023-02-21 15:00 | 2023-02-13 17:00 | 2023-03-03 13:30 |  | WACCES
MSA-MRWA | WA6113500 | 3 | GPS Plumbing & Gas Services PtyLtd | HWS Plant room - Domestic hot water system fault unit 1 left hand side | Plumbing & Drainage | HWS/Units Electric & Gas | 729.14 | Pass | Fail | -1 | 1 | 238.0833 | 2022-10-24 12:05 | 2022-10-31 17:00 | 2022-10-25 14:00 | 2022-10-31 17:00 | 2022-11-04 12:05 |  | WACCES | lodged a service call and the manufacturer replaced water body and installed inlet filter
MSA-DFES | WA6650048 | 2 | Australian HVAC Services Pty. Ltd. | Study - Split system air con unit - noisy/rattling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 883.6 | Pass | Fail | 0 | 1 | 237.75 | 2023-02-20 09:03 | 2023-02-23 17:00 | 2023-02-20 14:00 | 2023-02-23 17:00 | 2023-03-02 11:45
MSA-DTWD | WA5407669 | 2 | Techworks Electrical | Kendrew- A - Block room A235 has a noisy and flickering light | Electrical | General Electrical | 380.46 | Pass | Fail | 0 | 1 | 236.7833 | 2022-05-11 13:08 | 2022-05-16 17:00 | 2022-05-13 10:00 | 2022-05-16 17:00 | 2022-05-23 06:47 |  |  | Repaired 8x lights in room
MSA-DTWD | WA6020693 | 1 | Ronley Holdings Pty Ltd | E Block Light fabrication compound - Plazma Cutter Extraction fan very noisy. | Equipment | Power Tools | 2940 | Fail | Fail | 0 | 2 | 236.25 | 2022-10-13 15:50 | 2022-10-14 17:00 | 2022-10-17 13:30 | 2022-10-14 17:00 | 2022-10-27 09:45 |  |  | We attended site 17/10/2022 for the initial inspection and diagnosis and determined that the bearing required replacement.We attended site 26/10/2022 and disconnected and removed the fan and motor. The motor was taken to a rewinder and the bearings were replaced and the motor spun to dry out the windings.We attended site 27/10/2022 and reinstalled fan and motor, reconnected electrically and test ran.
MSA-DCA | WA5396131 | 2 | EQUANS Mechanical Services (WA) Pty Limited | External Grounds(front carpark)-Maritime Conservation Workshop- Air-con pipe leak- See notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 862.475 | Pass | Fail | 0 | 1 | 236 | 2022-05-06 08:34 | 2022-05-11 17:00 | 2022-05-09 13:59 | 2022-05-11 17:00 | 2022-05-19 09:59 |  |  | Cancelled as no vendor
MSA-DTWD | WA5101853 | 2 | Precise Air Group | H001 - Evap air-con above cafe counter blowing hot air | Air Conditioning | Room Air Conditioners | 999.96 | Pass | Fail | -1 | 1 | 235.85 | 2022-02-03 15:40 | 2022-02-08 17:00 | 2022-02-04 12:09 | 2022-02-08 17:00 | 2022-02-14 08:00 |  | WACCES | Found unit requires new sump dum kit to get stystme up and running
MSA-DTWD | WA5972597 | 2 | AWB Co. | lights keep tripping | Electrical | Lighting, Internal | 942.305 | Pass | Fail | 0 | 1 | 235.75 | 2022-09-21 07:06 | 2022-09-23 17:00 | 2022-09-23 14:15 | 2022-09-23 17:00 | 2022-10-03 10:00 |  |  | Attended site signed in jsa completed. Found 4 faulty batterns isolated. Removed and disposed of in bin. Installed new led batterns in class d003all tested and working.Job completed
MSA-DFES | WA6522291 | 1 | SONTEC WA PTY LTD | Main steel gates - Damage to the exit boom gate reader. | Building | Materials | 1773.88 | Pass | Fail | 0 | 1 | 235.1667 | 2023-01-31 06:48 | 2023-01-31 17:00 | 2023-01-31 15:00 | 2023-01-31 17:00 | 2023-02-10 10:10
MSA-DTWD | WA5974395 | 1 | Equans Mechanical Services Australia | The Freezer has failed | Refrigeration | Freezers | 1337.765 | Pass | Fail | -1 | 1 | 235 | 2022-09-23 11:11 | 2022-09-27 17:00 | 2022-09-23 14:00 | 2022-09-27 17:00 | 2022-10-03 09:00 |  | WACCES | FREEZER has created another leak in system, informed Sharyn, beleive on age and history on unit not worth repairing. Cleaned up and completed paperwork and signed out.
MSA-DFES | WA5566331 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Hot water storage area - External storage area - leak in the hot water pipe system | Plumbing & Drainage | HWS/Units Electric & Gas | 428 | Pass | Fail | 0 | 1 | 235 | 2022-06-23 07:24 | 2022-06-29 17:00 | 2022-06-27 13:56 | 2022-06-29 17:00 | 2022-07-07 08:56 |  | WACCES | Installed drain for RPZD
MSA-DTWD | WA5570686 | 2 | BAKE-QUIP PTY LTD | Convotherm oven wiring sheath broken causing shorting | Equipment | Catering Equipment | 999 | Fail | Fail | 4 | 5 | 235 | 2022-06-28 13:38 | 2022-07-01 17:00 | 2022-07-29 14:30 | 2022-07-01 17:00 | 2022-08-08 09:30 |  | WACCES | Refer to service report
MSA-DTWD | WA5869594 | 2 | Protek 24/7 Building & Maintenance | Passage door has faulty hinge | Building | Doors | 603.625 | Pass | Fail | 0 | 1 | 234 | 2022-09-14 14:55 | 2022-09-19 17:00 | 2022-09-19 14:00 | 2022-09-19 17:00 | 2022-09-29 08:00 |  |  | Braf Declined Repaired broken swing door . Fitted new 75mm screws to bottom pivot hinge .
MSA-DTWD | WA5582815 | 1 | Securex Security Systems & Services | entry foyer-Intruder Alarm system will not arm | Security | Security Management System | 360 | Pass | Fail | 0 | 1 | 233.75 | 2022-07-04 08:38 | 2022-07-05 17:00 | 2022-07-04 15:00 | 2022-07-05 17:00 | 2022-07-14 08:45 |  |  | 04/07/2022, 1500-1600Found zone 4 can’t seal it is fault from the access control system.Need access control contractor to fix their fault.Isolated zone for now14/07/2022, 745-845Replaced cabinet tamper switch zone 4, tested arming ok.
MSA-DCA | WA5381770 | 0 | EQUANS Mechanical Services (WA) Pty Limited | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 486.65 | Fail | Fail | 0 | 1 | 229.35 | 2022-04-22 20:47 | 2022-04-22 22:47 | 2022-04-22 23:00 | 2022-04-23 00:47 | 2022-05-02 12:21 | 1 |  | Found ac6 humidifier tripped on water conductivity sensor fault. Blew down system checked sensors, all ok. Reset unit, ran up, all ok.
MSA-DTWD | WA5588804 | 3 | Falcetta Plumbing and Gas | Carpark-Tap vandalised | Plumbing & Drainage | Water | 243.97 | Pass | Fail | 0 | 1 | 227 | 2022-07-08 07:11 | 2022-07-14 17:00 | 2022-07-11 08:00 | 2022-07-14 17:00 | 2022-07-20 19:00 |  | WACCES | replaced barrel union and tested rpzd
MSA-DCA | WA5094891 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground - Cafe Male Toilet - Toilet flusher does not stop flushing | Plumbing & Drainage | Toilets/Cisterns | 1497.92 | Pass | Fail | 0 | 1 | 225 | 2022-01-31 15:02 | 2022-02-03 17:00 | 2022-02-01 07:25 | 2022-02-03 17:00 | 2022-02-10 16:25 |  | WACCES | Replaced Valve
MSA-DTAG | WA5298054 | 3 | Sapio Pty Ltd | Level 31 - Server Room - Milestone client slow to load into system | Security | CCTV Surveillance | 490 | Pass | Fail | 0 | 1 | 225 | 2022-03-31 14:56 | 2022-04-07 17:00 | 2022-04-04 12:30 | 2022-04-07 17:00 | 2022-04-13 21:30 |  |  | Attended site after hours and modified IP configuration no workstation and CCTV system. Restored cameras andconfirmed system running correctly
MSA-DTWD | WA5706040 | 3 | COMMERCIAL PLUMBING AND GAS | VBB Wash room - 6b15 - Water leaking from hot water unit | Plumbing & Drainage | Water | 1420.75 | Fail | Fail | 1 | 2 | 225 | 2022-08-11 08:19 | 2022-08-18 17:00 | 2022-08-24 09:00 | 2022-08-18 17:00 | 2022-09-02 18:00 |  |  | Replaced hot water unit
MSA-DFES | WA6113542 | 3 | AWB Co. | Simcentre - North East Corner - Electrical Brick box broken away from wall - See notes | Building | External Walls | 1311.365 | Pass | Fail | 0 | 1 | 224.5 | 2022-10-24 12:30 | 2022-10-31 17:00 | 2022-10-31 07:00 | 2022-10-31 17:00 | 2022-11-09 15:30 |  | WACCES & WCAPPR | Work NoteAttended site and signed in. Completed JSA. Loaded with site contact. He explained issue and where it was. Investigate issue further and he’s asked for flashing to be installed around brick pillar that’s come away from wall to make it water tight. Will need roof plumbers to attend.Materials required:3.5 metres of flashing required2x tubes of siliconeFixingsFollow up required for roof plumber to attend!Attended site. Measured flashing to be ordered and installed at a later date. Installed temporary Flexi flashing to prevent water entering.Attended site with materials and set up work area. Cut and fit flashing around electrical box to stop water entering. Fixed and made waterproof. Cleaned and packed up site.BRAF approval attached
MSA-DTWD | WA6292957 | 1 | Australian HVAC Services Pty. Ltd. | Split System Aircon isn't working | Air Conditioning | Ducted Split System | 2034.99 | Pass | Fail | 0 | 1 | 224 | 2022-11-29 15:12 | 2022-11-30 17:00 | 2022-11-30 08:00 | 2022-11-30 17:00 | 2022-12-09 16:00 |  |  | Douglas Posthuma (09/12/2022) - Work Notearrived on site, accessed condensing unit.disassembled condensing unit and removed the main power board and main control boardfitted new boards.removed and replaced electrical isolator.ran and tested system, all ok
MSA-DTWD | WA5588392 | 3 | Falcetta Plumbing and Gas | Wall mounted HW unit leaking rusty water onto benchtop iso valve stuck | Plumbing & Drainage | HWS/Units Electric & Gas | 1402.2 | Pass | Fail | 0 | 1 | 224 | 2022-07-07 15:35 | 2022-07-14 17:00 | 2022-07-11 09:00 | 2022-07-14 17:00 | 2022-07-20 17:00 |  | WACCES | replaced autoboil with new unit
MSA-DTAG | WA6667822 | 3 | Australian HVAC Services Pty. Ltd. | Ground - Stair Well - FCU 7 drain leaking | Air Conditioning | Ducted Split System |  | Pass | Fail | -1 | 1 | 223 | 2023-02-21 15:13 | 2023-02-28 17:00 | 2023-02-23 08:00 | 2023-02-28 17:00 | 2023-03-04 15:00
MSA-DCA | WA5961545 | 1 | Dormakaba Australia Pty Ltd | Fire doors - Fault description…..Doors not shutting | Building | Fire Door | 2751.99 | Pass | Fail | 0 | 1 | 222.5 | 2022-09-19 08:27 | 2022-09-20 17:00 | 2022-09-19 10:00 | 2022-09-20 17:00 | 2022-09-28 16:30 |  |  | 19/9/22 - Inspected door and found that the fire closer mechanism was jamming and this was causing the doors to not close properly, attempted to carry out tempt repair but door still not functioning correctly. Please quote for 1x gsr-emf door mechanism. 2x hours on site.28/9/22 - Supplied and fitted new ts93 emf door selector as per quotation, setup and tested operation upon completion. Upon completion we don’t appear to have any voltage coming from the fire system. Site will look into this and let us know if we need to reattend etc
MSA-DCA | WA6364787 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground floor - External Building - Toilet seat snapped and toilet has come loose. | Plumbing & Drainage | Toilets/Cisterns | 904.665 | Pass | Fail | 0 | 1 | 222.1667 | 2022-12-12 14:49 | 2022-12-13 17:00 | 2022-12-13 08:15 | 2022-12-13 17:00 | 2022-12-22 14:25 |  | WACCES | Job requires two new toilet seats ones cracked and in the other toilet the seat is loose it has been put back and tighten as much as possible but screws are worn and requires new one. We will try and supply grey ones but given permission by management to provide white if only ones supplier called and parts ready to order.Forgot to start timer arrived at 12:30pm replaced two toilet seats both from reece wolfen grey seats tightend aligned as install.
MSA-DTWD | WA6022887 | 3 | AWB Co. | Patch wall where pipes exposed paint one wall Antique White USA | Plastering | Plastering | 995.575 | Pass | Fail | 0 | 1 | 222 | 2022-10-14 12:40 | 2022-10-21 17:00 | 2022-10-19 07:00 | 2022-10-21 17:00 | 2022-10-28 13:00 |  |  | Works completed
MSA-DTWD | WA6041554 | 2 | Critical Fire Protection & Training | Entry Foyer EWIS Panel-panel still in alarm | Fire Protection Services | Fire Protection - Monitor System | 700.95 | Pass | Fail | 0 | 1 | 222 | 2022-10-17 07:44 | 2022-10-19 17:00 | 2022-10-19 08:00 | 2022-10-19 17:00 | 2022-10-28 14:00 |  |  | Attended site to investigate intermittent fault to EWIS panel.After placing faulty zone 3 into alert and listening for speaker operation found all but 2 speakers in cafe functioning and checked connections at each cafe speaker.It was found both speakers need to be replaced however connections at these speakers are not the cause of the fault as the EWIS cabling is fully intact and connected correctly. Further investigation is required as all other speakers in faulty zone function as intended.
MSA-DTWD | WA5694237 | 2 | Australian Airconditioning Services Pty Ltd | 3B5 Hydraulics class room -Building Management System (INNOTECH) for Block 9 showing multiple sensor | Air Conditioning | Building HVAC Maintenance (Major Plant) | 700.26 | Pass | Fail | 0 | 1 | 221.75 | 2022-08-05 08:35 | 2022-08-10 17:00 | 2022-08-08 07:15 | 2022-08-10 17:00 | 2022-08-17 13:00 |  |  | BMS sensor fault rectified by icon logic subcontractor. All ok
MSA-DTWD | WA5226536 | 1 | Lane's Plumbing | Outside BLD 839 - Burst Water Pipe | Plumbing & Drainage | Drainage |  | Pass | Fail | 0 | 1 | 221.5 | 2022-03-14 09:58 | 2022-03-15 17:00 | 2022-03-14 11:00 | 2022-03-15 17:00 | 2022-03-23 16:30 |  |  | job completed - REPAIR BURST WATER MAIN OUTSIDE BLD 839
MSA-DTWD | WA6528940 | 3 | AWB Co. | Aberdeen St entrance -5 out of 10 bollards lights out | Electrical | Lighting, External | 1715.6625 | Pass | Fail | 0 | 1 | 221.5 | 2023-02-02 13:08 | 2023-02-09 17:00 | 2023-02-07 09:15 | 2023-02-09 17:00 | 2023-02-16 14:45 |  | WACCES
MSA-DTAG | WA5090640 | 1 | Sapio Pty Ltd | Basement - Custody Hallway - Custody door connecting stairway to records area not working - | Security | Access Control | 1831.55 | Pass | Fail | 0 | 1 | 221 | 2022-01-25 14:33 | 2022-01-27 17:00 | 2022-01-27 08:00 | 2022-01-27 17:00 | 2022-02-05 13:00 |  | WCAPPR | Replaced cable and tested
MSA-DTWD | WA5380578 | 2 | AWB Co. | V Block - Ground - internal lights - Press all lights off button and some still stay on | Electrical | General Electrical | 876.625 | Pass | Fail | 0 | 1 | 221 | 2022-04-22 13:49 | 2022-04-28 17:00 | 2022-04-26 07:00 | 2022-04-28 17:00 | 2022-05-05 12:00 |  |  | Attended site signed in jsa completed. Got keys for site, met dean on site who does dynalite programing to find fault on lights. Found lights had been replaced but not put in the system via programming, made sure dean was able to program the lights to turn on and off via the two way dynalite switches. All tested ok and passed**** job completed *****
MSA-DTWD | WA5066149 | 2 | AWB Co. | Carpark - footpath down by A Block have no lights working | Electrical | General Electrical | 755.73 | Pass | Fail | 0 | 1 | 220.5 | 2022-01-19 08:41 | 2022-01-24 17:00 | 2022-01-24 10:30 | 2022-01-24 17:00 | 2022-02-02 15:00 |  | WACCES | Attended site and signed in. Completed jsa. Located exterior lights along veranda of A block. Supplied and replaced igniter and lamps for 4x walkway lights. Tested for correct operation. All working properly. Notified relevant personal of works completed. **job complete**
MSA-DCA | WA5080940 | 1 | Techworks Electrical | Fiji Room - Office - Extractor fan is not working | Electrical | General Electrical | 991.115 | Pass | Fail | 0 | 1 | 220.5 | 2022-01-20 09:14 | 2022-01-21 17:00 | 2022-01-20 11:00 | 2022-01-21 17:00 | 2022-01-29 15:30 |  | WCAPPR | Changed exhaust fan for new fitting
MSA-DCA | WA5140797 | 1 | Critical Fire Protection & Training | Plant room - Fire alarm - activated last night - L4 D40 - plant ac2 Z52 - in fault | Fire Protection Services | Fire Protection - Monitor System | 1059.71 | Pass | Fail | 0 | 1 | 220.5 | 2022-02-16 07:18 | 2022-02-16 17:00 | 2022-02-16 08:30 | 2022-02-16 17:00 | 2022-02-25 13:00 |  |  | Plant room - Fire alarm - activated - L4 D40 - plant ac2 Z52 - in faultTech has investigated false alarm and found 2x conventional duct probes hanging off an addressable zone monitor ( L4 D40 - plant ac2 Z52 )Both duct probes appear to be in poor condition and have been recommended that these are replacedBRAF approved: 17/02/20222x Duct Probes Replaced
MSA-DCA | WA5488314 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Mezzanine - office cold due to air conditioner | Air Conditioning | Room Air Conditioners | 1758.225 | Fail | Fail | 1 | 2 | 220.5 | 2022-06-02 11:51 | 2022-06-03 17:00 | 2022-06-07 08:00 | 2022-06-03 17:00 | 2022-06-16 12:30 |  |  | Attended site, signed in and loged on to the State Library BMS. Checked the building floor temperatures and all were reading around 20 to 21 degreese. Checked the boilers and ahus for correct operation. Found all the ahus supply air temperature setpoint set at 18.0 degrees and not adjusting automatically. Manually adjusted the the setpoints higher to allow heating into the ahu coils. Sent a work order to Honeywell to investigate all ahus setpoints not adjusting automatically. (Honeywell rectified controll issues).
MSA-DFES | WA5291018 | 2 | Seme Solutions Pty Ltd | Ground - Communications cupboard room 29, alarm panel in Room 22- see details | Security | Monitoring | 747.5 | Pass | Fail | 0 | 1 | 220.25 | 2022-03-25 13:52 | 2022-03-30 17:00 | 2022-03-28 09:00 | 2022-03-30 17:00 | 2022-04-06 13:15 |  | WCAPPR | Download existing panel system to titan software.Replace alarm board with another.Power up but board faulty.Replace faulty capacitor on original board and refit.Board had defaulted itself.Connect laptop to system but couldn’t connect,faulty comms on board.Reprogamme board through keypad and test alarm ok.
MSA-DTWD | WA5672961 | 3 | AWB Co. | Repair Patch and paint over large water damage hole in wall | Building | Ceiling | 368.41 | Pass | Fail | 0 | 1 | 220 | 2022-07-20 11:04 | 2022-07-27 17:00 | 2022-07-26 09:00 | 2022-07-27 17:00 | 2022-08-04 13:00 |  |  | Visited job and took measurement s to completeInspect wall damage due to leak caused by rain. ? Attended to room 303.? Found water damage to gyprock wall on the adjacent wall to external wall.? Put a piece of paper on the window to identify the area outside.? We suspect that the cladding or joins on cladding must be allowing rainwater through.? Area is approx 15m-20m high.? Will need a boom lift to assess it, as well as council approval to block off the path. Maybe even traffic control. ? Advised client that their roofers will need to investigate furtherclose costs to date
MSA-DTAG | WA5834368 | 1 | Australian HVAC Services Pty. Ltd. | Stirling Gardens Complex - Level 1 - Office of the Associate to President Buss - See notes | Air Conditioning | Room Air Conditioners | 1243.54 | Pass | Fail | 0 | 1 | 220 | 2022-09-06 15:37 | 2022-09-07 17:00 | 2022-09-07 08:00 | 2022-09-07 17:00 | 2022-09-16 12:00 |  |  | ttend site. Access plantroom and monitor damper operation. Also access BMS at the same time and carry out damper operation for each zone to confirm working correctly. Each zone as 2 damper actuators, heating and cooling. The damper actuators are opposing, confirm correct direction. Found zone 1 heat damper to be slipping on the shaft. Stoke correct positioning and tighten. All other zone dampers and actuators working correctly.
MSA-DTWD | WA6400130 | 1 | SCAVENGER SUPPLIES PTY LTD | Ground floor - Fire pumps behind shed - Water leaking out of piping - see notes | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 956.209 | Pass | Fail | 0 | 1 | 219.8333 | 2023-01-03 09:51 | 2023-01-04 17:00 | 2023-01-03 10:10 | 2023-01-04 17:00 | 2023-01-12 14:00 |  | WACCES
MSA-DTWD | WA6293478 | 1 | Australian Airconditioning Services Pty Ltd | 6G51 - Painting and Decorating spray booth - Water in spray booth filter system | Air Conditioning | Evaporative Coolers | 1024.89 | Pass | Fail | 0 | 1 | 219.75 | 2022-11-30 09:02 | 2022-12-01 17:00 | 2022-11-30 12:00 | 2022-12-01 17:00 | 2022-12-09 15:45 |  |  | complete
MSA-DFES | WA6393277 | 2 | Complete Pest Management Services | Pidgeons nesting in warehouse and making mess pest control required to get rid on them. | Pest Control | General Pest | 3042.91 | Fail | Fail | 0 | 1 | 219.5 | 2022-12-28 12:10 | 2023-01-03 17:00 | 2023-01-04 12:00 | 2023-01-03 17:00 | 2023-01-13 15:30
MSA-DTWD | WA5204769 | 3 | Protek 24/7 Building & Maintenance | Block G - 1sr floor - GF30 - Roof leak in classroom GF30 | Roofing | Metal Roofing | 808.5 | Pass | Fail | -1 | 0 | 219.25 | 2022-03-04 13:08 | 2022-03-14 17:00 | 2022-03-08 12:45 | 2022-03-14 17:00 | 2022-03-17 16:00 |  |  | Repair roof leak in classroom
MSA-DTWD | WA5495166 | 3 | AWB Co. | 3G42 - Faulty wiring in battery charging room | Electrical | General Electrical | 459.92 | Pass | Fail | 0 | 1 | 219 | 2022-06-08 09:31 | 2022-06-15 17:00 | 2022-06-14 09:30 | 2022-06-15 17:00 | 2022-06-23 12:30 |  | WACCES | Attended site signed in jsa completed. Picked up parts from jaycar. Installed all battery links between plug and battery and put 5a 3ga fuses in.*** job completed ***
MSA-DTWD | WA5976814 | 3 | Australian Airconditioning Services Pty Ltd | E65-pines restaurant-Faulty temp sensor on Pines Restaurant AC4 | Air Conditioning | Room Air Conditioners | 993.59 | Pass | Fail | -1 | 0 | 218.75 | 2022-09-27 11:39 | 2022-10-04 17:00 | 2022-09-28 08:00 | 2022-10-04 17:00 | 2022-10-07 10:45 |  | WACCES | complete
MSA-DFES | WA6158589 | 1 | Go Doors | Front entry Car Park Boom gates Stuck -Not opertaing | Building | Materials | 2983.65 | Pass | Fail | 0 | 1 | 218.5 | 2022-11-10 06:57 | 2022-11-11 06:57 | 2022-11-10 07:30 | 2022-11-11 06:57 | 2022-11-19 10:00 |  |  | Completed
MSA-DTWD | WA5195569 | 2 | ECO PLUMBING AND GAS PTY LTD | Blocked Drain | Plumbing & Drainage | Water | 554.83 | Pass | Fail | 0 | 1 | 218 | 2022-02-28 12:56 | 2022-03-03 17:00 | 2022-03-02 15:00 | 2022-03-03 17:00 | 2022-03-11 17:00 |  | WCAPPR | Cleared blockage using jetter
MSA-DTWD | WA5519468 | 2 | AWB Co. | Room F001 - 3 x high bay workshops lights out on the fabrication side of the workshop - See notes | Electrical | Lighting, External | 1421.755 | Pass | Fail | 0 | 1 | 217.5 | 2022-06-15 09:09 | 2022-06-20 17:00 | 2022-06-20 08:00 | 2022-06-20 17:00 | 2022-06-29 09:30 |  |  | Attended site and signed in. Completed JSA and relevant paperwork required for EWP. Drove EWP to work area. Set up cones to block off drop zone. Removed 3x old highways and replaced them with new LED highbays. Tested to make sure all working correctly. Packed up area. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6108943 | 3 | AWB Co. | J100-Faulty overhead GPOs x 2 | Electrical | Lighting, Internal | 1003.34 | Pass | Fail | 0 | 1 | 217.5 | 2022-10-20 12:20 | 2022-10-27 17:00 | 2022-10-25 11:00 | 2022-10-27 17:00 | 2022-11-03 12:30 |  |  | Attended site and signed in. Completed jsa. Completed rescue plan. Completed ewp pre start checklist. Located EWP and drove over to work area. Went to wholesaler for parts. Returned to site. De energised circuit. Reterminated cables in ceiling rose. Adjusted jack chain so that no stress was put on cable. Re energised circuit. Tested. Found fault. De energised circuit. Opened up inside of pendant gpo and found that the earth had not been terminated correctly and was hanging freely. Re terminated earth cable. Re energised circuit. Tested. Everything is now working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5382190 | 1 | Codee Cleaning Services | Level 1 - Transit Cell 1 - Bio Clean - PIC could have also spat on the floor | Cleaning | Emergency Cleans | 280 | Pass | Fail | 0 | 1 | 217.35 | 2022-04-26 15:09 | 2022-04-27 17:00 | 2022-04-26 17:53 | 2022-04-27 17:00 | 2022-05-05 19:14 |  |  | COMPLETED 26/04/2022
MSA-DTAG | WA5382065 | 1 | Codee Cleaning Services | Ground - Custody Cell 3 - Bio Clean | Cleaning | Emergency Cleans | 280 | Pass | Fail | 0 | 1 | 217.3167 | 2022-04-26 13:29 | 2022-04-27 17:00 | 2022-04-26 17:52 | 2022-04-27 17:00 | 2022-05-05 19:11 |  |  | COMPLETED 26/04/2022
MSA-DCA | WA5141521 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Temporary Exhibition Gallery (TEG) - Only half the house lights in the TEG are coming on | Electrical | General Electrical | 990.0375 | Pass | Fail | 0 | 1 | 216.75 | 2022-02-16 10:49 | 2022-02-17 17:00 | 2022-02-16 12:15 | 2022-02-17 17:00 | 2022-02-25 13:00 |  | WCAPPR | Arrived on site at located faulty lights. Check the switchboards for any tripped circuit breakers. I didn’t find any tripped circuit breakers. Stu from light application advised the lighting system was good when he connected remotely. We used the on site sissor lift the check if there was power to one of the lights not working. Removed the globe and there was power at the light. Removed a working globe and installed it in a faulty light and the light works. Will need to replace faulty globes with new. Will need to arrange a suitable time to return so we can use the onsite sissor lift and when at time the room is not in use. The new show in the room starts on the 28 of February. Pet- sue advised they are planning to finish the set up of the show by the 23rd of February. 25/02/2022Collect globes from lamp replacements O’Connor at 10:15. Continued to site arrived at 10:28. Using scissor lift on site replaced 11 x blown globes in the temporary display. 3 x globes are unaccessible as t
MSA-DTWD | WA5697845 | 2 | Protek 24/7 Building & Maintenance | Roof leak near window of classroom. Possible box gutter leak/blockage | Roofing | Metal Roofing | 218.14 | Pass | Fail | 0 | 1 | 216.75 | 2022-08-09 12:18 | 2022-08-12 17:00 | 2022-08-10 12:00 | 2022-08-12 17:00 | 2022-08-19 12:45 |  |  | Reported Findings OnlySilicone appears to be failing around Flashings / Dektites and Gutter join and sump
MSA-DTWD | WA6521747 | 1 | AWB Co. | Wall Data Port P3-3 broken - requires fixing | ICT/Audiovisual | Telephony | 497.665 | Pass | Fail | 0 | 1 | 216.5 | 2023-01-30 12:59 | 2023-01-31 17:00 | 2023-01-30 14:00 | 2023-01-31 17:00 | 2023-02-08 14:30 |  | WCAPPR
MSA-DTWD | WA5697841 | 2 | Protek 24/7 Building & Maintenance | 3 x Roof leaks in centre of classroom | Roofing | Metal Roofing | 257.27 | Pass | Fail | 0 | 1 | 216.5 | 2022-08-09 12:08 | 2022-08-12 17:00 | 2022-08-10 13:00 | 2022-08-12 17:00 | 2022-08-19 13:30 |  |  | Silicone around Fan flashings / Tray flashings /Apron Flashings / Dektites
MSA-DTWD | WA6130584 | 2 | AWB Co. | EG22 – AMEP Reception -Fluro light not working - See notes | Electrical | Lighting, Internal | 963.03 | Pass | Fail | 0 | 1 | 216.5 | 2022-10-28 13:11 | 2022-11-02 17:00 | 2022-10-31 13:30 | 2022-11-02 17:00 | 2022-11-09 14:00 |  | WACCES | Attended site signed in jsa completed.. Installed lights as per glenns request as faulty. Tested and checked operation.Job completed
MSA-DTAG | WA6573038 | 1 | Sapio Pty Ltd | : Treasury levels experiencing issue with REX buttons when operated. Multiple requests to exit befo | Security | Access Control | 241.66 | Pass | Fail | 0 | 1 | 216.5 | 2023-02-14 10:27 | 2023-02-15 17:00 | 2023-02-15 11:30 | 2023-02-15 17:00 | 2023-02-24 12:00
MSA-DFES | WA5976939 | 2 | Water2water Pty Ltd | Kitchen - Zip Hydro tap tripping out circuit breaker - No hot/cold water | Plumbing & Drainage | Water | 1395.545 | Pass | Fail | 0 | 1 | 216.4167 | 2022-09-27 12:28 | 2022-09-30 17:00 | 2022-09-28 09:00 | 2022-09-30 17:00 | 2022-10-07 09:25 |  | WACCES | Replaced failed element due to corrosion Replaced tap head due to faultReplaced hot tank gasket due to corrosion Removed unit back to workshop for safe testing and observation. All ok + reinstalled
MSA-DTWD | WA6518673 | 1 | AWB Co. | Level 1- Room B10 - corridor - 6-foot LED fluorescent light is flickering really fast | Electrical | Lighting, Internal | 366.17 | Pass | Fail | 0 | 1 | 216 | 2023-01-25 10:21 | 2023-01-27 17:00 | 2023-01-25 13:00 | 2023-01-27 17:00 | 2023-02-03 13:00 |  | WACCES
MSA-DTAG | WA5386081 | 1 | Midolo Building Services | Criminal file room - Rear - Roof leak (dripping) from ceiling and corner of light fitting | Building | General Building | 538.25 | Pass | Fail | 0 | 1 | 215.75 | 2022-04-29 15:40 | 2022-05-02 17:00 | 2022-05-02 08:15 | 2022-05-02 17:00 | 2022-05-11 08:00 |  | WACCES & WCAPPR | ceiling repaired & roof cleaned/repaired for potential leak spots
MSA-DTWD | WA5294279 | 2 | M Construction (WA) | Workshop 4 emergency exit door handle broken and fixing loose | Building | Doors | 652.31 | Pass | Fail | 0 | 1 | 215 | 2022-03-28 15:33 | 2022-03-31 17:00 | 2022-03-29 13:00 | 2022-03-31 17:00 | 2022-04-07 12:00 |  |  | Replace door handle.
MSA-DCA | WA6359612 | 3 | Precise Air Group | Carpark -Air conditioning cover in carpark area has been forced open and not locking well - See Note | Air Conditioning | Room Air Conditioners | 437.975 | Pass | Fail | 0 | 1 | 214.9 | 2022-12-06 16:32 | 2022-12-13 17:00 | 2022-12-12 11:30 | 2022-12-13 17:00 | 2022-12-21 10:24 |  |  | Arrived on siteI didn't find myself to staff at front deskIdentified which air conditioning unit was having the issueGained access to platform and investigated possible solutionsIt appears homeless have been opening The doors aren't getting access to the unit and wiring insidediscussed with Bryce a possible solution is a harsp and staple along with a padlock and he approvesReturned ladder to vehicle signed out and exit site2nd visitattended supplier for materialsarrived on sitegained access to parking beyond electronic bollardsgained access to unitinstalled hasp and staplecoded padlock 2185removed tools and ladder from work areaExit site
MSA-DCA | WA5290896 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Admin - Level 1 - Open office area top of stairs near library - warm - see notes | Air Conditioning | Room Air Conditioners | 397.675 | Pass | Fail | 0 | 1 | 214.8833 | 2022-03-25 12:32 | 2022-03-30 17:00 | 2022-03-28 14:26 | 2022-03-30 17:00 | 2022-04-06 13:19 |  |  | Condenser fans have failed on the unit due to fan cowling becoming sun damages and leading to fan faults. No further action required on this job. Quote has been submitted for repairs.
MSA-DFES | WA4991627 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Roof - Engine Room - TV antenna installation moves around and faulty | ICT/Audiovisual | Hardware / Equipment | 542.255 | Pass | Fail | 0 | 1 | 214.75 | 2022-01-05 10:01 | 2022-01-12 17:00 | 2022-01-12 15:45 | 2022-01-12 17:00 | 2022-01-21 14:30 |  | WCAPPR | Attended site to investigate Roof - Engine Room - TV antenna installation moves around and faulty. Wall that antenna was fixed to was weathered and soft, allowing the antenna mount to move.Installed plywood to wall to create a more solid surface and fixed antenna mount to it. All okay.
MSA-DTWD | WA5752415 | 3 | AWB Co. | H200 - Water leak in Workshop | Roofing | Metal Roofing | 999.75 | Pass | Fail | -1 | 0 | 214.65 | 2022-08-17 11:47 | 2022-08-24 17:00 | 2022-08-17 12:36 | 2022-08-24 17:00 | 2022-08-26 11:15 |  |  | Attended H200 Work shop leak around evap unit, riveted and re-sealed large dry pan system behind unit.
MSA-DCA | WA5512106 | 2 | Techworks Electrical | Admin F/F - Passage - Emergency lighting switch in distribution Board - no3 is humming very loud | Electrical | Distribution Board | 330.73 | Pass | Fail | 0 | 1 | 214.5 | 2022-06-13 13:44 | 2022-06-16 17:00 | 2022-06-14 08:00 | 2022-06-16 17:00 | 2022-06-23 06:30 |  |  | Replaced failed contactor with new unit
MSA-DTWD | WA5584830 | 1 | Lane's Plumbing | Boiler room-Faulty Pump . It is on the ring main. | Mechanical Services | Boilers |  | Pass | Fail | 0 | 1 | 214.5 | 2022-07-05 10:39 | 2022-07-06 17:00 | 2022-07-05 13:00 | 2022-07-06 17:00 | 2022-07-14 11:30 |  |  | Job completed
MSA-DTWD | WA6518705 | 1 | ECO PLUMBING AND GAS PTY LTD | Plastering Workshop - Floor Drain - Blocked floor drains Jetta required | Plumbing & Drainage | Drainage | 660.185 | Pass | Fail | 0 | 1 | 214.3833 | 2023-01-25 10:30 | 2023-01-27 17:00 | 2023-01-25 15:44 | 2023-01-27 17:00 | 2023-02-03 14:07
MSA-DFES | WA5585964 | 0 | SONTEC WA PTY LTD | Mutplie Secuirty panel - lost power and Secuirty panels have no back up power | Security | Security Management System | 2045 | Fail | Fail | 0 | 1 | 213 | 2022-07-06 09:35 | 2022-07-06 11:35 | 2022-07-06 13:30 | 2022-07-06 13:35 | 2022-07-15 10:30 |  |  | 6/7/22 - Dylan ParslowFound CCTV server offline.Restarted, and found camera displaysometimes freezing images.Found NUC processor running at 100% to be the likely cause.Recommend replacement.15/7/22 - Joshua ParkInstalled replacement NUC for CCTV.Tested all working.
MSA-DTAG | WA5239709 | 0 | Australian HVAC Services Pty. Ltd. | Courtside - court 2 - aircon is not operating correctly | Air Conditioning | Room Air Conditioners | 1164.12 | Pass | Fail | 0 | 1 | 212.5 | 2022-03-16 14:49 | 2022-03-16 16:49 | 2022-03-16 15:00 | 2022-03-16 18:49 | 2022-03-25 11:30 |  |  | Travelled to site to investigate Court 2 - FCU 4 not cooling properly.Accessed BMS and found fan Status on Fault.Accessed FCU plant room and found FCU-4 running, both chilled water valves closed.Checked new flow switch, flow switch made, checked all control wiring terminals all ok.All of a sudden both chilled water valves driving to 100% open Supply air temp 12 deg.There is a intermittent controls fault or broken wire. Braff to be raised and Icon logic to attend site to investigate problem further.Travelled to site with Jeff from Icon logic and investigated possible faults with FCU 4 stopping and starting g intermittently.Replaced run relay inside mechanical switch board. Monitored operation.All appears ok.
MSA-DFES | WA5798594 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - SOC - DOSS - 3x Fluros need replacing in the doss office | Electrical | Lighting, Internal | 434.22 | Pass | Fail | 0 | 1 | 212.5 | 2022-08-29 15:57 | 2022-08-30 17:00 | 2022-08-30 16:15 | 2022-08-30 17:00 | 2022-09-08 12:45 |  | WACCES | Arrived on site at 1615 to investigate Level 1 - SOC - DOSS - 3x Fluros need replacing in the doss office. Awaited acces to office and identified 6 x faulty fluros in office. Surrounding wholesalers were shut before parts could be picked up. Will need to return to site to replace 6 x faulty fluros. Informed staff and left site at 1630.
MSA-DFES | WA5290664 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Female Toilets - Second cubicle - wont flush | Plumbing & Drainage | Toilets/Cisterns | 953.4125 | Pass | Fail | 0 | 1 | 212.3833 | 2022-03-25 10:50 | 2022-03-30 17:00 | 2022-03-28 14:15 | 2022-03-30 17:00 | 2022-04-06 10:38 |  | WACCES | Returned back to site with in cistern replaced all the inturnals of the cistern put back together tested and working correctly now
MSA-DTWD | WA5088633 | 3 | AWB Co. | Client Services Reception - Repair and/or remove broken metal support leg to Client Services counter | Building | Steel Work | 468.13 | Pass | Fail | 0 | 1 | 212 | 2022-01-24 18:44 | 2022-02-01 17:00 | 2022-01-31 13:00 | 2022-02-01 17:00 | 2022-02-09 09:00 |  |  | Sourced legRemoved old leg shaved any sharp pointsFitted new legJob complete
MSA-DTWD | WA5563496 | 3 | AWB Co. | 3D30 - High bay lights not working over CNC machine | Electrical | Lighting, Internal | 574.82 | Pass | Fail | -1 | 0 | 212 | 2022-06-20 15:15 | 2022-06-27 17:00 | 2022-06-21 12:00 | 2022-06-27 17:00 | 2022-06-30 08:00 |  | WACCES & WCAPPR | Attended site signed in jsa completed. Found cleaner to open up work area. Removed x2 old hi bay lights and disposed. Installed new chain and hi bays in area above machine. All tested and workingjob completed.
MSA-DTWD | WA5831870 | 2 | BJ SYSTEMS | Faulty alarm keypad - not disarming | Security | Access Control | 495 | Pass | Fail | 0 | 1 | 211.75 | 2022-09-05 09:11 | 2022-09-08 17:00 | 2022-09-07 15:00 | 2022-09-08 17:00 | 2022-09-16 10:45 |  |  | 07/09/2022 - Investigated system, attended Rockingham for further investigation. Return required with spare controller as controller is o?ine and may require replacement16/09/2022 - Returned to site with replacement controller. Investigated network prior to replacement to ?nd blown port on the network switch. New port used for comms to controller. Testing has shown port is unlocked and available for use. System tested and functioning as intended. Thousands of alarms slowly coming through, alarms cleared, however they are taking far too long to come through so leaving site and Dennis can clear all at a later point in time
MSA-DTAG | WA6393812 | 3 | Midolo Building Services | Level 7 - Court 71 - Missing number ‘71’ on entry door | Building | Doors | 72.63 | Pass | Fail | 0 | 1 | 211.75 | 2022-12-29 10:31 | 2023-01-06 17:00 | 2023-01-04 14:30 | 2023-01-06 17:00 | 2023-01-13 10:15 |  | WACCES
MSA-DTWD | WA5797586 | 2 | M Construction (WA) | Opposite to main entrance - external down pipe broken opposite main entrance to building | Roofing | Guttering | 366.92 | Pass | Fail | 0 | 1 | 211 | 2022-08-29 09:20 | 2022-09-01 17:00 | 2022-08-30 15:00 | 2022-09-01 17:00 | 2022-09-08 10:00 |  |  | Attended site 30/8 and inspected broken downpipe, will need to return with materials to complete. Returned to site 8/9 andremoved broken section of downpipe and installed new PVC section, painted to suit existing. Job completed.
MSA-DCA | WA6403150 | 2 | Techworks Plumbing | Ground - Epoch Cafe - Zip tap fault - recurring alarm - see notes | Plumbing & Drainage | HWS/Units Electric & Gas | 326.58 | Pass | Fail | 0 | 1 | 210.5 | 2023-01-06 08:43 | 2023-01-11 17:00 | 2023-01-10 16:30 | 2023-01-11 17:00 | 2023-01-19 11:00
MSA-DFES | WA6539719 | 3 | Dom's Total Grounds Maintenance | garden-Reticulation not working correctly, Sprinklers need attention | Landscaping & Gardening | Grounds Maintenance | 685.7 | Fail | Fail | 1 | 2 | 210.5 | 2023-02-08 16:32 | 2023-02-15 17:00 | 2023-02-23 17:30 | 2023-02-15 17:00 | 2023-03-04 12:00
MSA-DTAG | WA5401035 | 1 | Codee Cleaning Services | Custody – Cell 3 - Blood on the wall of cell 3 from an accused in custody. | Cleaning | Emergency Cleans | 280 | Pass | Fail | 0 | 1 | 209.15 | 2022-05-10 15:03 | 2022-05-11 17:00 | 2022-05-11 00:45 | 2022-05-11 17:00 | 2022-05-19 17:54 |  |  | Completed 11/05/2022
MSA-DCA | WA5309908 | 0 | Precise Air Group | Level 5 Planet room Cooling Tower is leaking | Mechanical Services | Pumps | 502.32 | Fail | Fail | 0 | 1 | 208.75 | 2022-04-10 10:55 | 2022-04-10 12:55 | 2022-04-10 23:30 | 2022-04-10 14:55 | 2022-04-19 16:15 |  |  | Attended site found float stuck letting to much water in, adjusted and stopped water. Suggest replacing
MSA-DTWD | WA5700023 | 3 | Equans Mechanical Services Australia | F59 - Faulty aircon wall switch - Please repair | Air Conditioning | Room Air Conditioners | 470.57 | Fail | Fail | 0 | 1 | 205.5 | 2022-08-10 14:06 | 2022-08-17 17:00 | 2022-08-17 23:00 | 2022-08-17 17:00 | 2022-08-26 12:30 |  |  | Checked system and switches all operating correctly tried swapping switches for neon type unable due to swithch settings not correct only signal type. Lecturers confused when turning unit on weather it started and they continually pressing causing issues with unit operations.
MSA-DTAG | WA5297933 | 3 | Sapio Pty Ltd | LEVEL 31 - Server room - Paacom Taking longer than usual to search up users | Security | Security Management System | 490 | Pass | Fail | 0 | 1 | 201.5 | 2022-03-31 14:38 | 2022-04-07 17:00 | 2022-04-04 14:30 | 2022-04-07 17:00 | 2022-04-13 |  |  | Attended site after hours and modified IP configuration on workstation and CCTV system. Restored cameras andconfirmed system running correctly.
MSA-DTWD | WA5655792 | 2 | Damian Rak Electrical Pty Ltd | Building 857 - Sheep Shelter - Faulty Power Points Attacked by cocky’s | Electrical | General Electrical |  | Fail | Fail | 0 | 2 | 200 | 2022-07-18 10:28 | 2022-07-21 17:00 | 2022-07-24 08:00 | 2022-07-21 17:00 | 2022-08-01 16:00 |  |  | Cockatoos have destroyed all x3 15 amp power circuits in outside sheering areaEverything needs replacingFaulty powerpoints Attacked by cockysTradesman Labour Damian 24/7/22 9 hrs 25/7/22 8 hrs31/7/22 8 hrs7/8/22 8 hrsDamian 3 hrs off site----------Materials 1 x roll of 2.5mm power cable 1 x bundle 20mm conduit grey3 x 15 amp suspended Clipsal pendants
MSA-DTWD | WA5706129 | 3 | Protek 24/7 Building & Maintenance | Water leak from skylights | Roofing | Rooflights and Skylights | 658.09 | Pass | Fail | 0 | 1 | 200 | 2022-08-11 08:58 | 2022-08-18 17:00 | 2022-08-16 07:00 | 2022-08-18 17:00 | 2022-08-24 15:00 |  | WCAPPR | Fitted foam strips between flashing and roof sheet. Silicone in the troughs of sheet to stop water blow back. Silicone seal to screws and rivets on dry pan flashing on both skylights.
MSA-DTWD | WA5836354 | 3 | COMMERCIAL PLUMBING AND GAS | Level 4 - Ladies WC North - ladies toilet cistern running - L4 Nth | Plumbing & Drainage | Toilets/Cisterns | 699.255 | Pass | Fail | 0 | 1 | 199.5 | 2022-09-07 11:28 | 2022-09-14 17:00 | 2022-09-13 09:00 | 2022-09-14 17:00 | 2022-09-21 16:30 |  |  | Replaced invisi cistern
MSA-DTWD | WA5001244 | 2 | SCAVENGER SUPPLIES PTY LTD | Ground - Garden - Fire pump - Faulty pressure switch on firepump | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 617.14 | Pass | Fail | 0 | 1 | 199.2 | 2022-01-11 10:29 | 2022-01-14 17:00 | 2022-01-13 09:00 | 2022-01-14 17:00 | 2022-01-21 16:12 |  | WCAPPR | COMPLETED 16/02/2022 3 X SEPERATE SITE ATTENDANCE
MSA-DTWD | WA5727816 | 1 | Australian Airconditioning Services Pty Ltd | E Block - Noisy Airconditioner - Braemar aircon making grinding sound | Air Conditioning | Room Air Conditioners | 1856.72 | Pass | Fail | 0 | 1 | 199 | 2022-08-15 12:16 | 2022-08-16 17:00 | 2022-08-16 08:00 | 2022-08-16 17:00 | 2022-08-24 15:00 |  |  | complete
MSA-DCA | WA5100123 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 3 - Plumbing duct Executive area (enter via men’s bathroom in Exec) - Isolations taps corroded | Plumbing & Drainage | Water | 395.6175 | Pass | Fail | -1 | 0 | 198.8833 | 2022-02-02 11:05 | 2022-02-09 17:00 | 2022-02-03 07:30 | 2022-02-09 17:00 | 2022-02-11 14:23 |  | WACCES & WCAPPR | Investigate where to isolate water to level 3 executive area.Whole building will have to be isolated at night time.New work order to be raised.
MSA-DCA | WA5305124 | 2 | Protek 24/7 Building & Maintenance | Cracked paver requires replacing | Paving & Roadworks | Paving | 549.875 | Pass | Fail | 0 | 1 | 198.75 | 2022-04-05 12:21 | 2022-04-08 17:00 | 2022-04-06 07:00 | 2022-04-08 17:00 | 2022-04-14 13:45 |  | WACCES | Replace Cracked Paver
MSA-DTWD | WA6673081 | 2 | Complete Pest Management Services | L1-Outside AT06/07-Issues with birds leaving droppings on the balcony-see notes | Pest Control | General Pest | 1258.25 | Fail | Fail | 0 | 1 | 198.5 | 2023-02-24 10:44 | 2023-03-01 17:00 | 2023-03-02 13:00 | 2023-03-01 17:00 | 2023-03-10 19:30
MSA-DFES | WA5208657 | 1 | Dom's Total Grounds Maintenance | Retic not turning off | Plumbing & Drainage | Water | 1977.3 | Pass | Fail | 0 | 1 | 198.4167 | 2022-03-09 10:06 | 2022-03-10 17:00 | 2022-03-10 10:20 | 2022-03-10 17:00 | 2022-03-18 16:45 |  |  | Dom went out to inspect, BRAf was raised and then works completed
MSA-DTWD | WA6256860 | 2 | JEM Carpentry | Vent on flue faulty | Roofing | Metal Roofing |  | Pass | Fail | -1 | 0 | 197.75 | 2022-11-24 09:29 | 2022-11-29 17:00 | 2022-11-24 09:45 | 2022-11-29 17:00 | 2022-12-02 15:30 |  |  | Re installed correctly
MSA-DCA | WA5961583 | 2 | Protek 24/7 Building & Maintenance | Metal corner has been knocked off skirting edge, Damage to paintwork also. | Flooring | Timber | 339.49 | Pass | Fail | 0 | 1 | 197.5 | 2022-09-19 08:39 | 2022-09-22 17:00 | 2022-09-20 07:30 | 2022-09-22 17:00 | 2022-09-28 13:00 |  |  | Cleared away all lose materials and refixed edge protection, patched wall.Sand and painted
MSA-DCA | WA5513343 | 1 | Dormakaba Australia Pty Ltd | Ground Floor - GF Design Store/ Cafe - Doors not automatically opening and closing | Building | Automatic Doors | 6330.2 | Pass | Fail | 0 | 1 | 197.3833 | 2022-06-14 09:44 | 2022-06-15 17:00 | 2022-06-14 11:01 | 2022-06-15 17:00 | 2022-06-22 16:24 |  |  | 14/6/22 - On inspection, unit in total failure of equipment due to heavy corrosion and aged equipment, urgent quotation required to supply and install el301 non locking kit with 2 ixio sensors and 1 sk4 key switch, 2 techs required for this task due to large heavy pelmet, see attached photos.22/6/22 - Upgrade works as per quotation, tested all ok.
MSA-DTAG | WA5493587 | 3 | Australian HVAC Services Pty. Ltd. | Level 15 - Plant room - Copper flow valve pipe above water pumps is leaking | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1489.8 | Pass | Fail | -1 | 0 | 197.3 | 2022-06-07 09:12 | 2022-06-14 17:00 | 2022-06-07 09:12 | 2022-06-14 17:00 | 2022-06-15 14:30 |  |  | Pick up gear required for works. Attend site, access level 15 planroom. Clean all areas to be sealed. Seal around boiler plimths. Seal along existing water barriers. Seal all holes in floor and around fixings. Seal around drains. All possible leaking points now sealed. Clean up area.
MSA-DTWD | WA5990088 | 2 | Equans Mechanical Services Australia | Evaporative air conditioner dumping water whilst switched on | Air Conditioning | Room Air Conditioners | 836.8375 | Pass | Fail | 0 | 1 | 197 | 2022-10-04 13:03 | 2022-10-07 17:00 | 2022-10-06 10:00 | 2022-10-07 17:00 | 2022-10-14 15:00 |  |  | ARRIVED ON SITE SIGN IN CHECKED AND ISOLATE POWER TO EVAP. REMOVED FAULTY DUMP VALVE AND REPLACED WITH NEW ONE AND ADJUSTED FLOAT VALVE. TESTED WORKING FINE
MSA-DTWD | WA6082455 | 3 | AHS Services WA Pty Ltd (Anchor) | Room 1-30.1 Laboratory-Laboratory tap set not shutting off | Plumbing & Drainage | Water | 213.945 | Fail | Fail | 0 | 1 | 197 | 2022-10-18 15:39 | 2022-10-25 17:00 | 2022-10-27 02:30 | 2022-10-25 17:00 | 2022-11-04 07:30 |  | WACCES | Found cold tap leaking.Removed 1/2 turn spindle and fitted temporary spindle.Returned to site to find job completed by different contractor
MSA-DTAG | WA5761294 | 2 | Australian HVAC Services Pty. Ltd. | Level 9 - A/C flow is very low in Court rooms | Air Conditioning | Room Air Conditioners | 1067.82 | Pass | Fail | -1 | 1 | 196.8833 | 2022-08-18 07:56 | 2022-08-22 17:00 | 2022-08-18 11:07 | 2022-08-22 17:00 | 2022-08-26 16:00 |  |  | Attend site with icon logic. Access BMS and check issues on level 9 graphics. Icon carried out diagnostic checks and found issue with program. Carried out a reset and found floor to come back online. Airflows and temps now visible. Access level 9 and check temps across floor, ok. All boxes now working ok.
MSA-DTWD | WA5487465 | 2 | M Construction (WA) | Sawtooth roof openings leaking dust and water - see notes below | Roofing | Metal Roofing | 225 | Pass | Fail | -1 | 0 | 196.75 | 2022-06-01 15:58 | 2022-06-07 17:00 | 2022-06-02 10:00 | 2022-06-07 17:00 | 2022-06-10 14:45 |  |  | Attended site to investigated, submitted BRAF to conduct repairs. Client advised to close job.
MSA-DTWD | WA5961591 | 0 | Precise Air Group | aircon service duct - making loud noise and blowing out hot air | Air Conditioning | Room Air Conditioners | 1588.79 | Pass | Fail | 0 | 1 | 196.1 | 2022-09-19 08:48 | 2022-09-19 10:48 | 2022-09-19 09:30 | 2022-09-19 12:48 | 2022-09-27 13:36 |  |  | Loud bearing noise removed motor got new bearings installed put all back together aligned belts and turned back on all running very nice Asset no is A40315666k
MSA-DTAG | WA5589656 | 2 | Sapio Pty Ltd | Ground Level - MYBS office/ waiting room - camera not working Camera 41 in black and white only | Security | CCTV Surveillance | 398.12 | Pass | Fail | 0 | 1 | 196 | 2022-07-08 15:27 | 2022-07-13 17:00 | 2022-07-11 07:30 | 2022-07-13 17:00 | 2022-07-19 11:30 |  |  | Work performed by Ken Moore (11/07/2022)Attended site and checked system, located camera on system reset Indigo BX420 from software. Camera 41 appears tobe working correctly, located MYBS office camera and checked footage and unable to see camera on Indigo system.Work performed by Ken Moore (19/07/2022)Attended site and connected directly into camera and checked camera view and cross referenced with all cameras.Factory reset camera and programmed and attempted to add into system. IndigoPRO system has all 80 camera licencesused.20/07/2022 - BRAF submitted for approval.Closing job with works to date.No response from client
MSA-DTAG | WA6089146 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Custody - Split-system air conditioner in custody comms room is leaking/dripping water | Air Conditioning | Ducted Split System | 2549.62 | Pass | Fail | 0 | 1 | 196 | 2022-10-19 11:55 | 2022-10-20 17:00 | 2022-10-20 08:00 | 2022-10-20 17:00 | 2022-10-28 12:00 |  |  | Return to site. Check pressure and found not to have dropped. Release nitrogen and evacuate system. Charge system with R32. Reassemble indoor unit. Commission operation, working ok.
MSA-DFES | WA5546558 | 3 | Protek 24/7 Building & Maintenance | Admin Building - First Aid Room - Skirting boards have water damage - no water leaks found | Building | Internal Walls | 517.77 | Pass | Fail | 0 | 1 | 196 | 2022-06-17 07:08 | 2022-06-23 17:00 | 2022-06-22 10:00 | 2022-06-23 17:00 | 2022-06-30 14:00 |  | WACCES | Replace damaged skirting boards
MSA-DCA | WA6384755 | 1 | Techworks Plumbing | Ground - Jubilee building - Blocked toilets and sinks | Plumbing & Drainage | Toilets/Cisterns | 1013.34 | Pass | Fail | 0 | 1 | 196 | 2022-12-21 08:57 | 2022-12-22 17:00 | 2022-12-21 13:00 | 2022-12-22 17:00 | 2022-12-29 17:00 |  |  | Attended site and signed in located blocked toilets in jubilee attempted to plunge, was unsuccessful so used the drain machinecleared blockage, checked all openings and tested flushesScrubbed and mopped all surfaces exposed to ascended effluent returned keys, signed out, left site
MSA-DFES | WA5995762 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | WATER METER - Advised by water corp meter reader that the meter has a water leak. | Plumbing & Drainage | Water | 2099.0175 | Pass | Fail | 0 | 1 | 195.7667 | 2022-10-06 16:34 | 2022-10-11 17:00 | 2022-10-10 07:15 | 2022-10-11 17:00 | 2022-10-18 11:01 |  | WACCES | Arrived on site and singed in went to water meter out the front of building did a leak test getting 2 litres a minute. Isolated both hotwater systems did another test something 2 litres a minute, then lsocated retic something. Went inside and checked all tapware and toilets nothing was leaking. I also checked every garden tap they where fine also, no water visible on ground. Going to need leak detection. Arrived on site and singed in had to meet leak detection onsite to locate water leak had isolate water and fine leak with air, found leak out the front of the engine room ( Where they park the trucks). need to get job raised. As it is in bitumen and organise how thay are going to get the trucks out for a emergency.Arrived on site and singed, dug up and repair 20mm blue line in front of engine room cleaned up tested everything running fine.
MSA-DTWD | WA5112181 | 1 | Equans Mechanical Services Australia | D Block - Ground - D41 Cool room 2 - Cool room is sitting at 33 degrees | Refrigeration | Coolroom | 627.31 | Fail | Fail | 1 | 2 | 195.75 | 2022-02-10 14:12 | 2022-02-11 17:00 | 2022-02-16 08:30 | 2022-02-11 17:00 | 2022-02-24 12:15 |  |  | Found several electrical connections in condenser unit to be loose and causing system not to operate and found main isolator switch to have broken terminal from installation. Tightened loose connections and got system operating. Ordered and picked up new switch from suppliers. Returned to site and replaced faulty switch. Removed isolation and started unit. Checked operation and all ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5393562 | 2 | AWB Co. | Outside Lights - Lights not coming on during darker hours - safety concerns | Electrical | Lighting, External | 1614.8225 | Pass | Fail | 0 | 1 | 195.75 | 2022-05-04 08:53 | 2022-05-09 17:00 | 2022-05-09 07:00 | 2022-05-09 17:00 | 2022-05-17 10:45 |  |  | Attended site signed in jsa completed. Got keys from office at 8am after 1 hour wait. replaced 12 tubes and 9 ballasts in security lighting in G block. 3 lights tagged out of service with IR faults. all others replaced and working.*** job completed ***
MSA-DTWD | WA6672257 | 3 | AWB Co. | Numerous lights out in classroom | Electrical | Lighting, Internal | 616.66 | Pass | Fail | 0 | 1 | 195.5 | 2023-02-23 14:06 | 2023-03-02 17:00 | 2023-02-27 09:30 | 2023-03-02 17:00 | 2023-03-07 13:00 |  | WACCES
MSA-DFES | WA4994904 | 2 | Dom's Total Grounds Maintenance | back yard - retic - faulty | Plumbing & Drainage | Water | 885.5 | Pass | Fail | 0 | 1 | 195.3333 | 2022-01-10 08:50 | 2022-01-13 17:00 | 2022-01-11 08:30 | 2022-01-13 17:00 | 2022-01-19 11:50 |  |  | Repair Retic
MSA-DTWD | WA6572882 | 1 | Australian Airconditioning Services Pty Ltd | Indoor coil has iced over – Cool room running warm – Possible TX Valve fault | Air Conditioning | Evaporative Coolers | 1238.97 | Pass | Fail | 0 | 1 | 195.25 | 2023-02-14 09:24 | 2023-02-15 17:00 | 2023-02-14 12:15 | 2023-02-15 17:00 | 2023-02-22 15:30
MSA-DTWD | WA6402442 | 2 | AHS Services WA Pty Ltd (Anchor) | A237 - Ladies toilets - Leaking toilet cisterns x2 | Plumbing & Drainage | Toilets/Cisterns | 1523.46 | Fail | Fail | 0 | 1 | 195.0333 | 2023-01-05 11:37 | 2023-01-10 17:00 | 2023-01-11 10:30 | 2023-01-10 17:00 | 2023-01-19 13:32
MSA-DTWD | WA4994813 | 1 | Securex Security Systems & Services | L Block - all affected - alarms cannot be disabled | Security | Monitoring | 4528.5 | Pass | Fail | 0 | 1 | 195 | 2022-01-10 07:43 | 2022-01-10 17:00 | 2022-01-10 08:30 | 2022-01-10 17:00 | 2022-01-18 11:30 |  |  | 10/1/2022Gallagher controllers offline again. Rebooted controllers. Controllers not working.Need to replace.18/1/2022Replaced controllers. Got system working.
MSA-DTWD | WA5417575 | 2 | AWB Co. | Block 3 Heavy Plant - Faulty override switch for external lights facing into the undercover area | Electrical | General Electrical | 1342.57 | Pass | Fail | 0 | 1 | 195 | 2022-05-13 14:03 | 2022-05-18 17:00 | 2022-05-16 12:30 | 2022-05-18 17:00 | 2022-05-24 15:30 |  | WACCES | Attended site and signed in. Completed JSA and relevant paperwork required for EWP use. Located heavy diesel workshop. Set up work area. Located switch controlling outside lights removed and tested cable. Found to be fault going out to circuit. Found junction in girder. Split cables and tested again. Found to be fault going to external street style lights on outside wall of building. Removed cables that were causing faults (street style lights are now redundant and not in use). Retested cables all cables in use are now passing. Site requested PE cell to be made redundant. Ran new single cable from junction to pe cell to by pass it. Placed all cables back in junction box. Reinstated light switch to wall. Tested all. All working correctly. Notified fm of works completed. **job complete**
MSA-DTWD | WA5565554 | 2 | AWB Co. | Faulty ceiling lights need replacing | Electrical | Lighting, Internal | 999.77 | Pass | Fail | 0 | 1 | 195 | 2022-06-22 08:59 | 2022-06-27 17:00 | 2022-06-27 12:00 | 2022-06-27 17:00 | 2022-07-05 15:00 |  | WACCES | Attended site signed in jsa completed. Picked up new lights which were on order. Installed new lights in toilets/ showers. Also found wrong labels on switchboard circuits done by insight electrical brand new switchboard less than 2 months old. Fixed legend and tested. All tested fineJob completed
MSA-DTWD | WA5962479 | 2 | Protek 24/7 Building & Maintenance | roof leak - This is the area that was previously resheeted | Roofing | Metal Roofing | 698.16 | Pass | Fail | 0 | 1 | 194.75 | 2022-09-19 14:27 | 2022-09-22 17:00 | 2022-09-20 09:15 | 2022-09-22 17:00 | 2022-09-28 12:00 |  | WACCES | Replaced section of piping and fittings to make right, turned water back on and fitting are all secure
MSA-DCA | WA5583742 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Random loud beeping noise coming from plant room - may be to do with hot water system | Air Conditioning | Building HVAC Maintenance (Major Plant) | 830.655 | Fail | Fail | 1 | 2 | 194.7 | 2022-07-04 14:26 | 2022-07-07 17:00 | 2022-07-11 13:22 | 2022-07-07 17:00 | 2022-07-19 16:04 |  |  | Returned to site. Gained access and confirmed pump operation and hit water flow. Beeping is believed to be internal alarm related to temp loss on water line. Confirmed pump has not faulted again and running to building requirements providing hot water to labs. Work area has been left tidy. Sound has not reoccured.
MSA-DTAG | WA5141688 | 1 | Sapio Pty Ltd | Ground - Security - Court entry button to Court 1 is not working | Security | Keys & Access | 388.61 | Pass | Fail | 0 | 1 | 194.3167 | 2022-02-16 11:56 | 2022-02-17 17:00 | 2022-02-16 15:11 | 2022-02-17 17:00 | 2022-02-24 17:30 |  |  | Replaced REX on Court 1, tested, all OK.Job completed.
MSA-DTWD | WA5612366 | 2 | Protek 24/7 Building & Maintenance | Water leak from roof of bulk store | Roofing | Metal Roofing | 435.42 | Pass | Fail | 0 | 1 | 194.25 | 2022-07-14 11:42 | 2022-07-19 17:00 | 2022-07-19 09:00 | 2022-07-19 17:00 | 2022-07-27 11:15 |  | WCAPPR | Braf Declined New roof sheets need to be installed
MSA-DCA | WA5394611 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS- AC 3 - Room Humidity - Galleries 3, 4 and 9 - Level 2 - alarming | Air Conditioning | Building HVAC Maintenance (Major Plant) | 450 | Pass | Fail | 0 | 1 | 194 | 2022-05-05 07:44 | 2022-05-05 09:44 | 2022-05-05 08:00 | 2022-05-05 11:44 | 2022-05-13 10:00 |  |  | Attended site, signed in and checked the BMS. Found Gallery 3 humidity at 45 and 46%.Accessed the main plant room ahu 3 and checked running conditions and humidification. Checked and tested zone 225 and zone 214 heating water valve for correct operation - all ok. Accessed the chiller plant room and checked operation of both steam generators and reverse Osmosis plant and found running correctly with no faults. Will monitor zones humidity levels during the preventative hvac maintenance.
MSA-DTWD | WA5585373 | 3 | Protek 24/7 Building & Maintenance | stairwell - roof leak - Water leak on south side of stair well | Building | Ceiling | 558.92 | Pass | Fail | -1 | 0 | 193.75 | 2022-07-05 15:36 | 2022-07-12 17:00 | 2022-07-07 14:15 | 2022-07-12 17:00 | 2022-07-15 16:00 |  |  | cleaned and repaired gutters to prevent leaking
MSA-DTWD | WA5105872 | 2 | Damian Rak Electrical Pty Ltd | faulty light | Electrical | Lighting, Internal |  | Pass | Fail | 0 | 1 | 193.5 | 2022-02-04 15:55 | 2022-02-09 17:00 | 2022-02-08 07:00 | 2022-02-09 17:00 | 2022-02-16 08:30 |  |  | job completed - replaced light
MSA-DTAG | WA5379674 | 3 | Sapio Pty Ltd | Ground Level - Switch Board Room- Equipment rack storing PA system been broken-Glass door is smashed | Equipment | Security Equipment | 1778.33 | Fail | Fail | 2 | 4 | 193.5 | 2022-04-21 13:20 | 2022-04-29 17:00 | 2022-05-16 09:00 | 2022-04-29 17:00 | 2022-05-24 10:30 |  | WACCES | installed cooling system
MSA-DCA | WA6113041 | 1 | EQUANS Mechanical Services (WA) Pty Limited | External plant room - Chiller 2 in fault | Refrigeration | Chiller | 596.84 | Pass | Fail | 0 | 1 | 193.4167 | 2022-10-24 08:44 | 2022-10-25 17:00 | 2022-10-25 10:00 | 2022-10-25 17:00 | 2022-11-02 11:25 |  |  | Subcontractor has attended site and repaired fault with Chiller 2 and is now operational.
MSA-DTWD | WA5677930 | 2 | Securex Security Systems & Services | A 238 - Digital door lock not working | Security | Locksmith | 280 | Pass | Fail | 0 | 1 | 193.25 | 2022-07-26 08:31 | 2022-07-29 17:00 | 2022-07-28 11:00 | 2022-07-29 17:00 | 2022-08-05 12:15 |  |  | 28/07/2022, 1100-1115Door is inside classroom, unable to access due to class, return when empty05/08/2022, 1100-1215Located room A238 but no digital door lock. John Burns is sick.Facilities manager advised to close off job and new job will be submitted once they have clarification.
MSA-DTWD | WA6674205 | 3 | Protek 24/7 Building & Maintenance | Passageway - Ceiling slats fallen down to heavy plant | Roofing | Metal Roofing | 1495.495 | Pass | Pass | -1 | 0 | 193.25 | 2023-02-27 08:38 | 2023-03-07 17:00 | 2023-02-27 14:30 | 2023-03-07 17:00 | 2023-03-07 15:45
MSA-DTWD | WA5107222 | 1 | Water2water Pty Ltd | A6 staff kitchen - Wall boiler unit is discharging debris | Plumbing & Drainage | Water | 1705.7175 | Pass | Fail | 0 | 1 | 193.1667 | 2022-02-07 15:57 | 2022-02-08 17:00 | 2022-02-08 10:50 | 2022-02-08 17:00 | 2022-02-16 12:00 |  |  | Rheem Wallmounted BWU flaking inside - unit over 10 years in age cleaned and flushed but recommend replacing this as it will most likely have ongoing issues with old internal tank being flakey - quoted to replaced Asset A402011412New Assets installed Maxiflow Scale Filter System B21429 + Rheem 3L Boiling Wallmounted Unit SN10402 as quoted
MSA-DCA | WA6516212 | 3 | GPS Plumbing & Gas Services PtyLtd | Drain covers are broken and loose - see notes | Plumbing & Drainage | Drainage | 326.29 | Pass | Fail | -1 | 0 | 193.1333 | 2023-01-23 09:54 | 2023-01-31 17:00 | 2023-01-24 07:32 | 2023-01-31 17:00 | 2023-02-01 08:40 |  | WACCES
MSA-DTWD | WA6149226 | 2 | AHS Services WA Pty Ltd (Anchor) | D243 - Block D - Kendrew D Block - Executive Kitchen D243 Hot Tap leaking/very difficult to turn off | Plumbing & Drainage | Water | 1794.43 | Pass | Fail | 0 | 1 | 193.1167 | 2022-11-04 13:07 | 2022-11-09 17:00 | 2022-11-08 09:00 | 2022-11-09 17:00 | 2022-11-16 10:07 |  |  | Leaking tapset in kitchen, could not isolate the water feeds, had to replace entire tap set and seal all penotrations to floor below due to leaking to below and dry all roof tiles
MSA-DTWD | WA5493820 | 1 | Falcetta Plumbing and Gas | Whole Floor - No water | Plumbing & Drainage | Water | 1369.24 | Pass | Fail | 0 | 1 | 193 | 2022-06-07 10:35 | 2022-06-08 17:00 | 2022-06-07 15:30 | 2022-06-08 17:00 | 2022-06-15 16:30 |  | WACCES | restored water and replaced service valve
MSA-DCA | WA6393768 | 2 | Protek 24/7 Building & Maintenance | Alexander Library Building - Level 3 - Door handle has broken off (see notes) | Building | Doors | 327.32 | Pass | Fail | -1 | 0 | 193 | 2022-12-29 09:27 | 2023-01-04 17:00 | 2022-12-29 12:30 | 2023-01-04 17:00 | 2023-01-06 13:30
MSA-DTWD | WA6544577 | 2 | AWB Co. | EWS Cupboard - faulty GPO | Electrical | General Electrical | 682.65 | Pass | Fail | 0 | 1 | 193 | 2023-02-10 14:25 | 2023-02-15 17:00 | 2023-02-14 06:00 | 2023-02-15 17:00 | 2023-02-22 07:00 |  | WCAPPR
MSA-DTWD | WA5380147 | 3 | AWB Co. | Level 1 - Corridor - 5 sets of lights not working | Electrical | Lighting, Internal | 1153.98 | Pass | Fail | 0 | 1 | 193 | 2022-04-22 08:49 | 2022-05-02 17:00 | 2022-05-02 13:00 | 2022-05-02 17:00 | 2022-05-10 14:00 |  | WCAPPR | Attended site signed in jsa completed. Replaced various lights in b6 as per lighting list given by dave gaff. All lights working and operational.** job completed ***
MSA-DTAG | WA5707021 | 2 | Sapio Pty Ltd | Level 22 -Delays after swiping access cards & buzzing sound after you open door - See notes below | Security | Access Control | 333.56 | Pass | Fail | 0 | 1 | 192.9167 | 2022-08-11 16:14 | 2022-08-16 17:00 | 2022-08-16 09:50 | 2022-08-16 17:00 | 2022-08-24 10:45 |  |  | Found staff to be holding door handle when swiping card.there needs to be no pressure on the mortice lock for the release mechanism to work correctly
MSA-DTWD | WA5735713 | 1 | ACTION GLASS & ALUMINIUM | Broken window | Building | Windows | 2211.375 | Fail | Fail | 4 | 5 | 192.75 | 2022-08-16 14:45 | 2022-08-17 17:00 | 2022-09-12 08:00 | 2022-08-17 17:00 | 2022-09-20 08:45 |  | WACCES | ATTENDED SITEMEASURED & MADE SAFE BROKEN PANEL2 SQM OF SAFETY FILM USEDRETURNED LATER DATE WITH 4 MEN TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-1805 X 1630PLUS SILICONERETURNED LATER DATE TO SUPPLY & FIT TINT FILM1-1805 X 1630
MSA-DTAG | WA5109584 | 1 | Sapio Pty Ltd | Secure interlock door leading into police station corridor, cards will not grant access (possible wa | Security | Security Management System | 1435.55 | Pass | Fail | 0 | 1 | 192.5 | 2022-02-09 11:37 | 2022-02-10 17:00 | 2022-02-09 13:30 | 2022-02-10 17:00 | 2022-02-17 14:00 |  | WCAPPR | installed new lock and tested door interlocks
MSA-DTWD | WA5689735 | 3 | AWB Co. | Repair and patch hole in plaster wall outside Lift Level 3 A Block | Building | Internal Walls | 608.5 | Pass | Fail | 0 | 1 | 192.4833 | 2022-08-02 13:24 | 2022-08-09 17:00 | 2022-08-09 10:31 | 2022-08-09 17:00 | 2022-08-17 11:00 |  |  | attended site and completed works
MSA-DTWD | WA5686631 | 2 | M Construction (WA) | motor trimming WS-weather seal has been damaged nth facing glazed alumin door-see note | Building | Doors | 581.45 | Pass | Fail | 0 | 1 | 192.25 | 2022-08-01 09:52 | 2022-08-04 17:00 | 2022-08-03 09:15 | 2022-08-04 17:00 | 2022-08-11 09:30 |  |  | Attended site to investigate, found weather seal damaged, measured for new weather seal. Returned to fit seals but weather has changed. will have to complete when rain stops. Reattended to clean doors and cut and fit new weather seals to bottom of doors. No one onsite to sign off on the works. Reattended site to get paperwork signed off.
MSA-DTWD | WA5226857 | 1 | BAKE-QUIP PTY LTD | E-Block SK3 the prover oven keeps tripping out unit needed for delivery | Equipment | Catering Equipment | 954.2 | Pass | Fail | 0 | 1 | 191.75 | 2022-03-14 13:55 | 2022-03-15 17:00 | 2022-03-15 10:00 | 2022-03-15 17:00 | 2022-03-23 09:45 |  | WACCES | Refer to service report
MSA-DTWD | WA5377847 | 2 | AWB Co. | The intrinsically safe light in fuel store room has stopped working, looks like globes have blown. | Electrical | Emergency & Exit Lighting | 414.61 | Pass | Fail | -1 | 0 | 191.75 | 2022-04-20 09:33 | 2022-04-26 17:00 | 2022-04-21 13:30 | 2022-04-26 17:00 | 2022-04-29 13:15 |  | WCAPPR | Attended site signed in jsa completed. Got keys from nathan and unlocked room, replaced two tubes in paint room. Working well now*** job completed ***
MSA-DTWD | WA6516806 | 1 | Securex Security Systems & Services | Security Gate - gate is stuck open – see ntoes | Security | Security Management System | 710.91 | Pass | Fail | 0 | 1 | 191.75 | 2023-01-23 15:20 | 2023-01-24 17:00 | 2023-01-24 14:15 | 2023-01-24 17:00 | 2023-02-01 14:00 |  | WACCES
MSA-DTAG | WA5201274 | 1 | SONTEC WA PTY LTD | Custody - custody control room - Power surge has shut down CCTV screens | Security | Security Management System | 2800 | Pass | Fail | 0 | 1 | 191.3667 | 2022-03-02 09:51 | 2022-03-03 17:00 | 2022-03-02 11:48 | 2022-03-03 17:00 | 2022-03-10 11:10 |  |  | 2/3/22 - Dean SimpsonAfter power surge CCTV screens not working.Tested PC, not working, no output on HDMI plugs.BRAF submitted 10/3/22 - Dylan ParslowReplaced PC and tested, all working.
MSA-DTWD | WA6050529 | 2 | AWB Co. | U Block - C+J Workshop - blown light tubes and globes in the C+J workshop | Electrical | Lighting, Internal | 492.7625 | Pass | Fail | 0 | 1 | 191.25 | 2022-10-17 15:17 | 2022-10-20 17:00 | 2022-10-20 14:45 | 2022-10-20 17:00 | 2022-10-28 14:00 |  | WCAPPR | Attended site and signed in. Completed jsa. Spoke to fm. Drove EWP around to work area. Replaced faulty tubes and starters. All lighting working as intended in the workshop. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5888266 | 2 | AHS Services WA Pty Ltd (Anchor) | A Block Level 3 - East End Male toilets - Urinal button faulty | Plumbing & Drainage | Toilets/Cisterns | 83.725 | Pass | Fail | 0 | 1 | 191.1333 | 2022-09-16 14:40 | 2022-09-21 17:00 | 2022-09-19 10:27 | 2022-09-21 17:00 | 2022-09-27 09:35 |  |  | Urinal needed adjustment but now works fine
MSA-DTWD | WA5481256 | 1 | Precise Air Group | Room E18 to E21 - e -vap dumping water continuously | Air Conditioning | Room Air Conditioners | 1225.535 | Pass | Fail | 0 | 1 | 191 | 2022-05-30 11:48 | 2022-05-31 17:00 | 2022-05-30 12:30 | 2022-05-31 17:00 | 2022-06-07 11:30 |  |  | Attended site and completed pre start paperwork and singed in. Collected parts and returned to site. Acessed unit and repaired as per quotation. Leak checked all connections and test ran unit. Found to unit to start and run with out fault. Left all ok.
MSA-DFES | WA5393146 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Admin - Various water isolation taps need repair - See notes | Plumbing & Drainage | Water | 900.4475 | Fail | Fail | 0 | 1 | 190.9333 | 2022-05-03 15:16 | 2022-05-10 17:00 | 2022-05-12 12:49 | 2022-05-10 17:00 | 2022-05-20 11:45 |  |  | Arrived to site and tested 2 isolation taps to find where they are running found one isolates the toilets near the change room and the other isolated a water fountain will return to fix one of the valves due to it is leaking
MSA-DTAG | WA5973141 | 3 | Total Security Systems Pty Ltd | Videowall monitor on ground floor has no image (possible warranty) | Security | Monitoring |  | Pass | Pass | -1 | 0 | 190.75 | 2022-09-21 10:51 | 2022-09-29 17:00 | 2022-09-21 13:00 | 2022-09-29 17:00 | 2022-09-29 11:45 |  |  | WARRANTY20/9/2022 - Michael Higginbotham - 10.15am to 10.45am (no travel time as already on site for a different issue)Checked monitor, power and cabling ok. Need to test HDMI and pc, return visit with HDMI Extender kit for testing.29/9/2022 - Michael Higginbotham travel to site - 6.45am to 8.15amtime on site - 8.15am to 10.15travel from site - 10.15am to 11.45amReconfigured and reset site setup after upgrading faulty driver for the graphics card in the comms rack PC. Job complete.
MSA-DFES | WA5394164 | 0 | ACTION GLASS & ALUMINIUM | Main Office - Window has been smashed | Glazing | Window Glass | 999.99 | Pass | Fail | 0 | 1 | 190.5 | 2022-05-04 13:05 | 2022-05-04 15:05 | 2022-05-04 15:00 | 2022-05-04 17:05 | 2022-05-12 13:30 |  |  | ATTENDED SITEMADE SAFE BROKEN WINDOW5.38 CLEAR LAMINATED SAFETY GLASS1-500 X 190 PLUS SAFETY FILM 2-500 X 300RETURNED LATER DATE TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-1140 X 1120PLUS SILICONE AND 4 L/M OF RUBBER USEDRETURNED LATER DATE SUPPLIED & FIT TINT FILM 1-1120 X 1140
MSA-DTWD | WA5681708 | 3 | SCAVENGER SUPPLIES PTY LTD | Fire Extinguisher sign needs replacing | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 117.39 | Fail | Fail | 1 | 2 | 190.45 | 2022-07-28 14:15 | 2022-08-04 17:00 | 2022-08-10 10:24 | 2022-08-04 17:00 | 2022-08-18 08:51 |  |  | Completed 18/08/2022
MSA-DTWD | WA5188239 | 2 | AWB Co. | Light switch not working in Lecture Theatre | Electrical | Lighting, Internal | 336.22 | Pass | Fail | 0 | 1 | 190.25 | 2022-02-23 07:42 | 2022-02-25 17:00 | 2022-02-23 10:00 | 2022-02-25 17:00 | 2022-03-03 08:15 |  | WACCES | Attended site signed in completed jsa. Isolated B1 and found loose wire in switch. Connected up and seems to work. Also found master switches in projector booth. If turned on dimmers and light switches become redundant and dont work. Advised site of how to operate without master and showed dennis and mike FMs on site. ***job completed***
MSA-DFES | WA5091252 | 1 | Protek 24/7 Building & Maintenance | Undercorft to stairwell 4 - door handle has broken off on both sides of the door | Building | Doors | 442.59 | Pass | Fail | 0 | 1 | 190 | 2022-01-27 07:23 | 2022-01-27 17:00 | 2022-01-27 14:00 | 2022-01-27 17:00 | 2022-02-04 12:00 |  | WACCES | Replace internal and external door handle
MSA-DTAG | WA5368556 | 1 | Sapio Pty Ltd | Level 1 - Camera 43 - not displaying | Security | CCTV Surveillance | 1043.05 | Pass | Fail | 0 | 1 | 190 | 2022-04-19 11:29 | 2022-04-20 17:00 | 2022-04-19 15:00 | 2022-04-20 17:00 | 2022-04-27 13:00 |  |  | Replaced Camera 43, confirmed correct operation and recording schedule
MSA-DTAG | WA5834404 | 2 | Midolo Building Services | Female staff toilets - Broken toilet roll holder | Building | Internal Walls | 361.19 | Pass | Fail | 0 | 1 | 190 | 2022-09-06 16:35 | 2022-09-09 17:00 | 2022-09-07 13:45 | 2022-09-09 17:00 | 2022-09-15 11:45 |  | WACCES | New toilet roll holder installed
MSA-DTWD | WA5378370 | 2 | Water2water Pty Ltd | T Block - Level 2 - Staff Kitchen - Zip Hydrotap not operating - see notes | Plumbing & Drainage | Water | 774.36 | Pass | Fail | 0 | 1 | 189.9167 | 2022-04-20 13:25 | 2022-04-26 17:00 | 2022-04-26 15:30 | 2022-04-26 17:00 | 2022-05-04 13:25 |  | WACCES | Returned to factory for further repairs, had to leave site due to time constraints (5.45pm)Reinstalled unit. Started on site at 3/5/22 12.20pm and finished 3/5/22 12.55pm
MSA-DFES | WA5699808 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Applied Training Block - Ground floor old offices - Sensor light not working see notes | Electrical | Lighting, External | 570.84 | Pass | Fail | 0 | 1 | 189.75 | 2022-08-10 12:31 | 2022-08-17 17:00 | 2022-08-16 13:15 | 2022-08-17 17:00 | 2022-08-24 11:00 |  | WACCES | Arrived onsite at 13:15 to investigate lights not working located trailer shed. Found faulty sensor not allowing lights to work. Bypassed sensor to test lights and they work fine. Disconnected faulty sensor until replaced. Will need to return to site with parts to fix and reconnect lights. Left site at 15:00
MSA-DTAG | WA5987795 | 2 | Midolo Building Services | Pothole in driveway, in front of vehicle gate on Whitfield Street | Paving & Roadworks | Asphalt | 625.32 | Pass | Fail | 0 | 1 | 189.75 | 2022-10-03 14:42 | 2022-10-06 17:00 | 2022-10-05 14:15 | 2022-10-06 17:00 | 2022-10-13 12:00 |  | WACCES | pothole has been repaired
MSA-DTAG | WA5303708 | 1 | Australian HVAC Services Pty. Ltd. | Level 3 & 5 - Admin Services and Court 51 - Air con doesn’t seem to be working | Air Conditioning | Room Air Conditioners | 397.68 | Pass | Fail | 0 | 1 | 189.55 | 2022-04-04 12:02 | 2022-04-05 17:00 | 2022-04-04 12:02 | 2022-04-05 17:00 | 2022-04-12 09:35 |  |  | Attend site. Access BMS and check temps on floors. Found BMS to be again offline. Access level 3 and carry out BMS reset. Monitor and found BMS to come back online. Monitor operation and found temps to return to normal. Due to the building being half old and half new control equipment the old equipment intermittently brings down the new equipment for unknown reason. Will monitor over a few days and see if any more adjustments are required.
MSA-DTWD | WA6407220 | 1 | Protek 24/7 Building & Maintenance | Entrance gate near C-Block damaged - see notes | Building | Steel Fencing & Gates | 566.77 | Pass | Fail | 0 | 1 | 189.5 | 2023-01-10 07:10 | 2023-01-10 17:00 | 2023-01-10 09:30 | 2023-01-10 17:00 | 2023-01-18 07:00
MSA-DTWD | WA6654055 | 2 | Techworks Electrical | Room E21 - the perspex lock box containing the aircon temp switch has broken needs replacing | Electrical | General Electrical |  | Pass | Fail | 0 | 1 | 189.5 | 2023-02-21 09:12 | 2023-02-24 17:00 | 2023-02-22 10:30 | 2023-02-24 17:00 | 2023-03-02 08:00
MSA-DTWD | WA5888291 | 3 | AHS Services WA Pty Ltd (Anchor) | A126 - Female staff room - shower taps difficult to turn on and off | Plumbing & Drainage | Water | 459.995 | Pass | Fail | -1 | 1 | 189.05 | 2022-09-16 15:01 | 2022-09-23 17:00 | 2022-09-19 12:27 | 2022-09-23 17:00 | 2022-09-27 09:30 |  |  | Replaced with new one
MSA-DTWD | WA4992316 | 2 | Techworks Plumbing | D Block Reticulation in covered walkway - roof/gutter height - faulty see notes | Plumbing & Drainage | Water | 628.03 | Pass | Fail | 0 | 1 | 189.0333 | 2022-01-06 09:52 | 2022-01-11 17:00 | 2022-01-10 13:00 | 2022-01-11 17:00 | 2022-01-18 10:02 |  | WACCES | Attended site and inspected work, will need to order parts , extended retic to garden bed
MSA-DTWD | WA5797911 | 2 | Lane's Plumbing | Faulty water meter | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 1 | 189 | 2022-08-29 11:29 | 2022-09-01 17:00 | 2022-08-29 15:00 | 2022-09-01 17:00 | 2022-09-06 12:00 |  |  | REPLACE FAULTY WATERMETER TO CHEMICAL SHED
MSA-DTAG | WA5794347 | 1 | Midolo Building Services | Level 2(Ground) -Ladies staff toilet - Tile is chipped, slightly lifted & grout missing –trip hazard | Flooring | Tiling | 308.8 | Pass | Fail | 0 | 1 | 188.25 | 2022-08-24 14:13 | 2022-08-25 17:00 | 2022-08-25 13:15 | 2022-08-25 17:00 | 2022-09-02 09:30 |  | WACCES | tile re glued & grouted
MSA-DTAG | WA6000677 | 2 | Midolo Building Services | G4S Kitchen - Towel dispenser unit has detached from the wall | Building | Internal Walls | 374.49 | Pass | Fail | 0 | 1 | 188 | 2022-10-10 09:31 | 2022-10-13 17:00 | 2022-10-11 13:45 | 2022-10-13 17:00 | 2022-10-19 09:45 |  |  | NEW TOWEL DISPENSER INSTALLED
MSA-DTWD | WA6537334 | 2 | SCAVENGER SUPPLIES PTY LTD | FIP has a fault showing | Fire Protection Services | Fire Protection - Monitor System | 1889.855 | Pass | Fail | 0 | 1 | 187.8833 | 2023-02-07 08:48 | 2023-02-10 17:00 | 2023-02-09 15:06 | 2023-02-10 17:00 | 2023-02-17 10:59 |  | WACCES
MSA-DFES | WA5438771 | 2 | Dom's Total Grounds Maintenance | Front of station - 4 x palm trees dead/dying -tops of them are dropping off - may need to be removed | Landscaping & Gardening | General Tree Works | 3510 | Fail | Fail | 1 | 2 | 187.75 | 2022-05-16 16:09 | 2022-05-19 17:00 | 2022-05-24 15:15 | 2022-05-19 17:00 | 2022-06-01 11:00 |  |  | BRAF raised 25/5/22
MSA-DCA | WA5053344 | 3 | EQUANS Mechanical Services (WA) Pty Limited | HBRC - Ground - Plant Room - Ahu 7 internal fault registering a 038 fault - see details | Air Conditioning | Room Air Conditioners | 293.025 | Pass | Fail | -1 | 0 | 187.5 | 2022-01-18 16:30 | 2022-01-25 17:00 | 2022-01-19 16:30 | 2022-01-25 17:00 | 2022-01-27 12:00 |  |  | Returned to site gained access and rechecked equipment. No fault was noted to be active on VSD or at BMS. No further action required on this job. Equipment will be monitored during site PM inspection for signs of further fault. Work area left tidy.
MSA-DCA | WA5571174 | 1 | Protek 24/7 Building & Maintenance | Exterior grounds, Iris Road End. - Paddock Area 9 - Bollard has been removed, needs to be reset | Equipment | Electrical Equipment | 389.52 | Pass | Fail | 0 | 1 | 187.5 | 2022-06-29 09:29 | 2022-06-30 17:00 | 2022-06-29 13:45 | 2022-06-30 17:00 | 2022-07-07 09:15 |  | WACCES | Concrete bollards back in place
MSA-DTWD | WA6450268 | 1 | AWB Co. | Q008 and Q block toilets - Broken clear Skylight difusers | Electrical | Lighting, Internal | 1515.415 | Pass | Fail | 0 | 1 | 187.25 | 2023-01-16 10:17 | 2023-01-17 17:00 | 2023-01-16 14:00 | 2023-01-17 17:00 | 2023-01-24 09:15
MSA-DTWD | WA6674268 | 3 | Protek 24/7 Building & Maintenance | Window framed have broken spirals and wont close | Building | Windows | 489.55 | Pass | Pass | -1 | 0 | 187.25 | 2023-02-27 09:11 | 2023-03-07 17:00 | 2023-02-27 13:15 | 2023-03-07 17:00 | 2023-03-07 08:30 |  | WCAPPR
MSA-DTWD | WA5289442 | 3 | Precise Air Group | Plant Room 1 - Condensed water pump two noisy bearing | Air Conditioning | Room Air Conditioners | 2555.14 | Fail | Fail | 38 | 39 | 186.55 | 2022-03-24 09:25 | 2022-03-31 17:00 | 2022-12-19 13:27 | 2022-03-31 17:00 | 2022-12-27 08:00 |  |  | removed faulty pump, carry out overhaul on system, reinstate pump into system
MSA-DCA | WA6519096 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Cooling tower level-Lift motor room (lifts 6 & 7)-Plant room mech board fault light illum-notes | Air Conditioning | Room Air Conditioners | 698.2 | Pass | Fail | -1 | 0 | 186.5 | 2023-01-25 13:03 | 2023-01-31 17:00 | 2023-01-25 14:30 | 2023-01-31 17:00 | 2023-02-02 09:00
MSA-DTWD | WA6537199 | 3 | Protek 24/7 Building & Maintenance | C/Block retractable Ballard been run over by a truck and badly damaged | Building | Steel Fencing & Gates | 290.02 | Pass | Fail | -1 | 0 | 186 | 2023-02-07 07:39 | 2023-02-13 17:00 | 2023-02-07 12:30 | 2023-02-13 17:00 | 2023-02-15 06:30
MSA-DTWD | WA5687157 | 2 | AWB Co. | DGPO on ducting at floor level (below & to left of projector) is faulty- See notes below | Electrical | General Electrical | 687.025 | Pass | Fail | 0 | 1 | 185.5 | 2022-08-01 13:47 | 2022-08-04 17:00 | 2022-08-02 14:00 | 2022-08-04 17:00 | 2022-08-10 07:30 |  | WCAPPR | Attended site signed in jsa completed.replaced dgpo as per site request. All working now.Job completed
MSA-DTWD | WA5689976 | 1 | Falcetta Plumbing and Gas | Gas heater isnt working | Plumbing & Drainage | Gas | 974.23 | Pass | Fail | 0 | 1 | 185 | 2022-08-02 16:21 | 2022-08-03 17:00 | 2022-08-03 16:30 | 2022-08-03 17:00 | 2022-08-11 09:30 |  | WACCES | reset and recommissioned with network controller
MSA-DFES | WA5568334 | 0 | Critical Fire Protection & Training | the fire hydride for the water supply is broken, the main water been isolate but still leaking | Fire Protection Services | Fire Protection - Monitor System | 4161.49 | Pass | Fail | 0 | 1 | 184.75 | 2022-06-26 18:26 | 2022-06-26 20:26 | 2022-06-26 19:15 | 2022-06-26 22:26 | 2022-07-04 12:00 |  |  | Investigated system - found hydrant in rear yard adjacent flammable liquid stores completely damage with upright hydrant pole bent and hydrant heads missing. Exercised in ground valve on pedestrian footpath of Dixon Road in attempt to further isolate and reduce current flow of water. Plumbers required to fix hydrant.
MSA-DTWD | WA5675879 | 3 | Falcetta Plumbing and Gas | Gas Domestic HW unit in fault reset not holding | Plumbing & Drainage | Gas | 971.415 | Pass | Fail | 0 | 1 | 184.75 | 2022-07-22 15:10 | 2022-07-29 17:00 | 2022-07-28 19:30 | 2022-07-29 17:00 | 2022-08-05 12:15 |  |  | replaced gas control assembly
MSA-DTAG | WA6517927 | 1 | GPS Plumbing & Gas Services PtyLtd | Custody - Cell 4 - Toilet metal plate has been pulled out | Plumbing & Drainage | Toilets/Cisterns | 803.8525 | Pass | Fail | 0 | 1 | 184.65 | 2023-01-24 14:07 | 2023-01-25 17:00 | 2023-01-24 14:56 | 2023-01-25 17:00 | 2023-02-01 07:35 |  | WACCES
MSA-DFES | WA6247958 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Shower head is broken | Plumbing & Drainage | Materials | 945.35 | Pass | Fail | 0 | 1 | 183.75 | 2022-11-20 15:45 | 2022-11-21 15:45 | 2022-11-20 16:45 | 2022-11-21 15:45 | 2022-11-28 08:30 |  | WACCES | Re attend site to repair shower head in back bathroom. Removed old shower rail and wall fitting. Install new wall fittings and shower rail. Tested and checked all working correctly
MSA-DTWD | WA5761331 | 2 | COMMERCIAL PLUMBING AND GAS | Cistern fault - Flush is continually running | Plumbing & Drainage | Toilets/Cisterns | 1421.125 | Pass | Fail | 0 | 1 | 177.5 | 2022-08-18 08:21 | 2022-08-23 17:00 | 2022-08-22 09:00 | 2022-08-23 17:00 | 2022-08-29 18:30 |  | WACCES | replaced invisi cistern and 2 button assemblies
MSA-DFES | WA5578165 | 1 | SONTEC WA PTY LTD | Ground Floor - Main Entrance - Sacnner isn't allowing people to scan through past a certain number | Security | Access Control | 1474.47 | Pass | Fail | 0 | 1 | 177 | 2022-07-01 09:20 | 2022-07-04 17:00 | 2022-07-01 13:20 | 2022-07-04 17:00 | 2022-07-08 22:20 |  |  | 1/7/22 - Dylan ParslowInvestigated issues with main entry card reader.Recommend replacing reader.4/7/22 - Dylan ParslowReplaced reader and tested, all working.8/7/22 - Dylan ParslowFault reoccuring, after hours attendance requested.Reset controller, and rewired.Reprogrammed door in system and tested, all working.
MSA-DTWD | WA5833379 | 2 | Protek 24/7 Building & Maintenance | Hallway - external AF11 - Consistent roof leak. - see notes below | Roofing | Metal Roofing | 479.985 | Pass | Fail | 0 | 1 | 177 | 2022-09-06 09:19 | 2022-09-09 17:00 | 2022-09-08 07:00 | 2022-09-09 17:00 | 2022-09-15 16:00 |  |  | Removed screws sealed holes refit spreader, Cleaned ceiling space of water and refit ceiling tile
MSA-DFES | WA5977277 | 2 | AWB Co. | dorms various faults - see notes | Building | Foundations | 3621.845 | Pass | Fail | 0 | 1 | 177 | 2022-09-27 15:18 | 2022-09-30 17:00 | 2022-09-30 07:00 | 2022-09-30 17:00 | 2022-10-07 16:00 |  |  | Works completed
MSA-DTWD | WA5226341 | 1 | BAKE-QUIP PTY LTD | A block - Level 1 - A120 Café kitchen - Lights on the bain marie have tripped the circuit breaker | Equipment | Catering Equipment | 403.63 | Fail | Fail | 0 | 1 | 175.6833 | 2022-03-14 08:02 | 2022-03-15 17:00 | 2022-03-17 15:30 | 2022-03-15 17:00 | 2022-03-24 23:11 |  |  | Refer to service report
MSA-DTWD | WA5835491 | 1 | BAKE-QUIP PTY LTD | Oven Temperature Knob Broken - Temp Knob Broken (Possibly part # 5009320) | Equipment | Catering Equipment | 475.6 | Pass | Fail | 0 | 1 | 174.75 | 2022-09-07 09:06 | 2022-09-08 17:00 | 2022-09-08 09:30 | 2022-09-08 17:00 | 2022-09-15 16:15 |  | WACCES | REFER TO SERVICE REPORT.
MSA-DTWD | WA6258759 | 3 | AWB Co. | Walkway between buildings-Repair or replace walkway lights | Electrical | Lighting, Internal | 1651.3125 | Pass | Fail | 0 | 1 | 174.75 | 2022-11-25 16:48 | 2022-12-02 17:00 | 2022-11-29 09:15 | 2022-12-02 17:00 | 2022-12-06 16:00 |  | WACCES | Attended site, signed in,completed jsa , spoke with fm about job, located lighting in between R block , identified and isolated circuits, removed old lights and replaced with new, re energised circuits, tested lights , lights working as intended, cleaned up, packed up, completed paperwork,signed out **job completed**
MSA-DTWD | WA6361759 | 1 | High Tech Pest Control | External to building - Relocate beehive in comms pit in garden bed | Pest Control | Specialist Pest | 301.37 | Pass | Fail | 0 | 1 | 174.5833 | 2022-12-08 12:48 | 2022-12-09 17:00 | 2022-12-09 06:45 | 2022-12-09 17:00 | 2022-12-16 13:20 |  | WCAPPR | Moved honeycomb on 9.12.22 out of pit and into box. Wait.Revisited and removed box 16.12.22.Bees successfully relocated elsewhere.
MSA-DTWD | WA5100361 | 3 | Schneider Electric Australia Pty Ltd | Fault with missing access control system transaction database for 2021 - see notes below | Security | Access Control |  | Pass | Fail | 0 | 1 | 174.5 | 2022-02-02 12:53 | 2022-02-09 17:00 | 2022-02-07 09:30 | 2022-02-09 17:00 | 2022-02-14 16:00 |  |  | job copmleted - Received SQL database backups. Prepared virtual machine and MSSQL instance and restoreddatabase backups. Extracted data for required individual from all available data and emailed results to stakeholders. On receiptof a second individual need data, repeated data extract and email again to stakeholders.
MSA-DTWD | WA4991116 | 3 | ACTION GLASS & ALUMINIUM | Hole in window glass | Glazing | Window Glass | 647.3 | Pass | Fail | 0 | 1 | 174.0833 | 2022-01-04 15:24 | 2022-01-11 17:00 | 2022-01-10 09:50 | 2022-01-11 17:00 | 2022-01-17 15:55 |  |  | ATTENDED SITEMADE SAFE BROKEN WINDOW WITH .5 SQM OF SAFETY FILMRETURNED LATER DATE TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-928 X 8974 L/M OF RUBBER AND 2 RIVETS USED2 MEN AND LARGE PLATFORM LADDER REQUIRED
MSA-DTWD | WA6602431 | 1 | Equans Mechanical Services Australia | All of Level 1 - No Aircon - Daiken system | Air Conditioning | Room Air Conditioners |  | Pass | Fail | 0 | 1 | 174.05 | 2023-02-17 11:30 | 2023-02-20 17:00 | 2023-02-20 09:15 | 2023-02-20 17:00 | 2023-02-27 15:18
MSA-DTWD | WA6298977 | 2 | Precise Air Group | C006 - Air Con is not working in left hand salon (see notes) | Air Conditioning | Ducted Split System | 484.605 | Pass | Fail | 0 | 1 | 174 | 2022-12-01 15:57 | 2022-12-06 17:00 | 2022-12-05 09:00 | 2022-12-06 17:00 | 2022-12-12 15:00 |  |  | AC1&2 thermostats we’re set to high for summer conditions reset to 22c was 26c also both package units need new Evap and condenser fan belts ,picked up new belts and installed in Frigopol vertical package units out back of hair dresser C block all working fine again
MSA-DTWD | WA5215058 | 3 | AWB Co. | Ceiling strap has come loose - A tall ladder is required | Building | Ceiling | 1123.6 | Pass | Fail | 0 | 1 | 173.5 | 2022-03-10 09:05 | 2022-03-17 17:00 | 2022-03-16 07:00 | 2022-03-17 17:00 | 2022-03-23 12:30 |  |  | Mark Crewe (16/03/2022) - Work NoteInspected loose ceiling cover strip on second floor. I called safety supervisor due to the location of the job and the risk of falling over the safety barrier. I sent Sam some photos and after a discussion he recommended that the job be rescheduled. I have emailed Bree to inform her. Sam recommended the use of a aluminium mobile scaffolding and that it should be a two person job along with barricading off the walkway whilst the work is being done.Craig Adams (23/03/2022) - Work NotePicked up trailer with the scaffolding from yard, attended site, erected scaffolding and glued and pined cover strips in place on ceiling.Dropped off trailer to yard.
MSA-DFES | WA5831915 | 2 | Water2water Pty Ltd | Ground Floor - Kitchen - Zip Billi boil and chill dispenser not working | Plumbing & Drainage | Water | 3161.075 | Pass | Fail | 0 | 1 | 173.0833 | 2022-09-05 09:31 | 2022-09-08 17:00 | 2022-09-06 09:20 | 2022-09-08 17:00 | 2022-09-13 14:25 |  |  | All part quoted replaced and tested,then re installed and tested again.
MSA-DCA | WA5407356 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Level 3 - Executive area - see details below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 700.015 | Fail | Fail | 0 | 1 | 173 | 2022-05-11 11:11 | 2022-05-12 17:00 | 2022-05-13 11:00 | 2022-05-12 17:00 | 2022-05-20 16:00 |  | WACCES | Accessed level 3 and located vav 3.3.28. Removed ceiling grid and investigated the vav and found the relay and relay base for the fan faulty and burnt wiring to the heater contractor. Collected parts and materials from supplier. Returned to site and replaced faulty parts. Tested the fan and heaters amp draws and checked vav for correct operation .
MSA-DTAG | WA5569284 | 3 | Gilmour & Jooste Electrical | Upper custody, Court Rooms, Public Area and Outside -Lights needing replacement - See notes below | Electrical | Lighting, Internal | 1769.01 | Pass | Fail | -1 | 0 | 172.5 | 2022-06-27 13:24 | 2022-07-04 17:00 | 2022-06-28 07:30 | 2022-07-04 17:00 | 2022-07-05 12:00 |  | WCAPPR | Replaced faulty LED flood to rear car park. Inspected front car park lights - will return with parts.Inspected court lights - will return with parts.Inspected magistrates car park lights - will return with parts.Repaired interview room fluoro in upper custody.Repaired stairwell wall light.Repaired bunker light outside sallyport.Advised emergency lights will be tested again soon under different work order and where functioning correctly when last tested.
MSA-DTWD | WA6158839 | 2 | CONNECT SECURITY SYSTEMS | Faulty alarm panel - see note | Security | Security Management System | 1199.76 | Pass | Fail | -1 | 0 | 172.3167 | 2022-11-10 09:30 | 2022-11-15 17:00 | 2022-11-10 11:14 | 2022-11-15 17:00 | 2022-11-17 15:33 |  |  | Replaced failed alarm equipment in J Block to make system operational. Updated documentation off site as per requirement for monitoring.
MSA-DTWD | WA5407943 | 3 | AWB Co. | Block 2 - ground - Main staff room - Numerous faulty fluroes in office | Electrical | General Electrical | 956.145 | Pass | Fail | 0 | 1 | 172.25 | 2022-05-11 15:14 | 2022-05-18 17:00 | 2022-05-17 11:15 | 2022-05-18 17:00 | 2022-05-24 15:30 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Located staff room with multiple light failures. Went through and removed 8x old faulty fittings. Replaced with new LED panels. Tested to see if all were operating correctly. All are. Disposed of rubbish in bins. Notified fm of works completed. **job complete**
MSA-DCA | WA5289512 | 2 | EQUANS Mechanical Services (WA) Pty Limited | HMAS Ovens Submarine - Front lower deck air-conditioning on submarine - low air flow | Air Conditioning | Room Air Conditioners | 600.41 | Pass | Fail | -1 | 0 | 172.0333 | 2022-03-24 10:08 | 2022-03-29 17:00 | 2022-03-25 07:00 | 2022-03-29 17:00 | 2022-04-01 11:02 |  |  | Repairs completed on equipment. Air movement restored to front section of sub
MSA-DCA | WA5087540 | 2 | Earth & Water Pty Ltd | zone 14 - leak on main line | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 1 | 172 | 2022-01-24 10:37 | 2022-01-28 17:00 | 2022-01-27 08:00 | 2022-01-28 17:00 | 2022-02-03 12:00 |  |  | works completed - retic pipes repaired/replaced
MSA-DTWD | WA5584626 | 2 | AWB Co. | Student Toilets - exhaust fan is making a loud noise | Electrical | General Electrical | 662.9 | Pass | Fail | 0 | 1 | 171.75 | 2022-07-05 09:21 | 2022-07-08 17:00 | 2022-07-06 12:00 | 2022-07-08 17:00 | 2022-07-13 15:45 |  | WACCES | Attended site and signed in, completed jsa,spoke with fm about job, set up work area, replaced fan belts, re energised circuit, tested both motors , put cover back on and packed up , completed paperwork, signed out , job completed , signature slips sent through for signing
MSA-DTWD | WA5454650 | 3 | AWB Co. | E105 - Wall mounted fresh air fan is rattling and noisy | Electrical | General Electrical | 724.5575 | Pass | Fail | 0 | 1 | 171.25 | 2022-05-17 13:07 | 2022-05-24 17:00 | 2022-05-23 08:45 | 2022-05-24 17:00 | 2022-05-30 12:00 |  | WACCES | Attended site and signed in. Completed JSA. Located faulty exhaust fan. Removed cover. Removed old exhaust fan. Supplied and replaced with new fan. Tested to see if it was working correctly. Disposed of rubbish. Completed paperwork. **job complete**
MSA-DFES | WA6405071 | 2 | Protek 24/7 Building & Maintenance | Roof - flashing on SW gable is partially missing and sign of water leaking | Roofing | Metal Roofing | 571.99 | Pass | Fail | 0 | 1 | 171.2333 | 2023-01-09 11:13 | 2023-01-12 17:00 | 2023-01-10 11:00 | 2023-01-12 17:00 | 2023-01-17 14:14
MSA-DTWD | WA6155525 | 2 | Precise Air Group | A Block staff office area level 1 - AC Faulty - See notes | Air Conditioning | Room Air Conditioners | 2156.38 | Fail | Fail | 0 | 1 | 171.05 | 2022-11-08 11:15 | 2022-11-11 17:00 | 2022-11-14 12:47 | 2022-11-11 17:00 | 2022-11-21 15:50 |  |  | replacement of actuators works complete
MSA-DTWD | WA5094349 | 2 | AWB Co. | Broken concrete comm's pit lid South / East of Battery room H402. see notes | Electrical | General Electrical | 426.06 | Pass | Fail | 0 | 1 | 171 | 2022-01-31 10:25 | 2022-02-03 17:00 | 2022-02-02 07:00 | 2022-02-03 17:00 | 2022-02-09 10:00 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm about job. Re located damaged pit lids. Took out old lids and disposed of safely. Put new pit lids in. Cleaned up around work area. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5563245 | 2 | ACTION GLASS & ALUMINIUM | B/Block - west side - auto door glass panel - has slip down from the frame leaving a 10cm gap | Building | General Building | 230 | Pass | Fail | 0 | 1 | 170.7719 | 2022-06-20 13:11 | 2022-06-23 17:00 | 2022-06-23 11:30 | 2022-06-23 17:00 | 2022-06-30 14:16 |  |  | ATTENDED SITE TO ASSESS WORKS REQUIREDRETURNED LATER DATE WITH 2 MENREMOVED AND RFEFIT GLASS TO DOORREFIT RUBBERS AND SEALED WITH SILICONE
MSA-DTWD | WA5974130 | 1 | SCAVENGER SUPPLIES PTY LTD | B Block - Ground Floor Stairwell - Fire door break glass needs replacing | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 476.09 | Pass | Fail | -1 | 0 | 170.75 | 2022-09-23 08:13 | 2022-09-27 17:00 | 2022-09-23 10:45 | 2022-09-27 17:00 | 2022-09-30 13:30 |  | WACCES | 23/9/22 - INITIAL ATTENDANCE - Requires further time/ works. Parts on order.30/9/22 - New Press button emergency door release to be installed instead of replacement glass as will be a better long term solution.
MSA-DCA | WA6165753 | 3 | FCT SURFACE CLEANING | PCC Exterior - Ground - Graffiti in various locations - See notes | Cleaning | Graffiti |  | Pass | Fail | -1 | 0 | 170.5 | 2022-11-11 09:11 | 2022-11-18 17:00 | 2022-11-14 12:00 | 2022-11-18 17:00 | 2022-11-21 14:30 |  |  | Removal of graffiti
MSA-DTWD | WA6190540 | 1 | AWB Co. | Bain Maree heat globe faulty | Electrical | Lighting, Internal | 836.175 | Pass | Fail | 0 | 1 | 170.5 | 2022-11-16 09:11 | 2022-11-17 17:00 | 2022-11-16 12:30 | 2022-11-17 17:00 | 2022-11-23 15:00 |  | WACCES | Attended site signed in jsa completed. Replaced two globes as per safety standard in bain maree’s which says need to be double glazed if near food.Tested operational.Job completed
MSA-DTAG | WA5207486 | 3 | Midolo Building Services | ground court 09 - Create access to ceiling space in Court 9 for A/C techs for patch & paint | Building | Ceiling | 2639.48 | Pass | Fail | 0 | 1 | 170.4167 | 2022-03-08 13:26 | 2022-03-15 17:00 | 2022-03-12 07:00 | 2022-03-15 17:00 | 2022-03-19 09:25 |  | WACCES & WCAPPR | created access, patched and painted
MSA-DFES | WA5694475 | 3 | ADVANCED LOCK & KEY | Ground Floor- Store Room -storeroom manhole latch/lock broken. | Security | Locksmith | 252.5 | Pass | Pass | -1 | 0 | 170.1667 | 2022-08-05 10:40 | 2022-08-12 17:00 | 2022-08-05 14:15 | 2022-08-12 17:00 | 2022-08-12 16:25 |  |  | Replace lock
MSA-DCA | WA5586754 | 3 | Protek 24/7 Building & Maintenance | Ground - Main Theatre - Stairs into orchestra pit - Broken stair, needs replacement piece of wood. | Carpentry | Timber (all types) | 651.78 | Pass | Fail | 0 | 1 | 170 | 2022-07-06 14:25 | 2022-07-13 17:00 | 2022-07-11 08:00 | 2022-07-13 17:00 | 2022-07-18 10:00 |  | WACCES | Replaced broken step
MSA-DFES | WA6082531 | 3 | Dom's Total Grounds Maintenance | front gate-Water pooling on the driveway - Reticulation needs to be checked for leaks | Landscaping & Gardening | Grounds Maintenance | 233 | Pass | Fail | -1 | 0 | 170 | 2022-10-18 15:45 | 2022-10-25 17:00 | 2022-10-19 17:00 | 2022-10-25 17:00 | 2022-10-26 19:00 |  |  | 2 x Call Out, Labour & Parts
MSA-DTWD | WA6256873 | 2 | COMMERCIAL PLUMBING AND GAS | Toilet cubicle currently blocked & cover plate not secure | Plumbing & Drainage | Toilets/Cisterns | 422.79 | Pass | Fail | 0 | 1 | 170 | 2022-11-24 09:41 | 2022-11-29 17:00 | 2022-11-29 15:30 | 2022-11-29 17:00 | 2022-12-06 17:30 |  |  | repaired cover panel and replaced inlet
MSA-DCA | WA6672319 | 3 | Techworks Electrical | light timer fault | Electrical | General Electrical | 326.61 | Pass | Fail | 0 | 1 | 170 | 2023-02-23 14:58 | 2023-03-02 17:00 | 2023-02-28 08:30 | 2023-03-02 17:00 | 2023-03-07 10:30
MSA-DTWD | WA5676798 | 3 | Australian Airconditioning Services Pty Ltd | 3G60 electrical classroom - A/C not working | Air Conditioning | Room Air Conditioners | 422.5 | Pass | Pass | -1 | 0 | 169.75 | 2022-07-25 10:45 | 2022-08-01 17:00 | 2022-07-25 12:30 | 2022-08-01 17:00 | 2022-08-01 14:15 |  |  | Closing job as new wo was raised. Refer to WA5686985
MSA-DFES | WA5378450 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - External Hose reels for vehicle washing - damaged- see notes | Plumbing & Drainage | Water | 1681.89 | Pass | Fail | 0 | 1 | 169.55 | 2022-04-20 14:19 | 2022-04-28 17:00 | 2022-04-26 11:29 | 2022-04-28 17:00 | 2022-05-03 13:02 |  | WACCES | Returned back to side to inform the fire fighter that the new hose has been ordered in And have be told but the suppler that the original hose on the hose reels and not the right one and will could warranty on the units so have order the correct ones to suit the new reels and will not put strain on the retractor.Day 2Returned back to site with the new hoses installed the hoses tested mutable times to make sure they do not leak and all working correctly packed up all the old hoses and took them away.
MSA-DFES | WA5470350 | 1 | AWB Co. | Main Admin near plant room - Water leak coming from the roof | Roofing | Metal Roofing | 313.13 | Pass | Fail | 0 | 1 | 169.5 | 2022-05-23 09:45 | 2022-05-24 17:00 | 2022-05-23 11:15 | 2022-05-24 17:00 | 2022-05-30 12:45 |  |  | Attended, weather conditions hindered works, returned on dry day and sealed fixings and parapet flashing. Job complete
MSA-DTWD | WA5578225 | 2 | AWB Co. | Grounds and driveway -Timer control not working for grounds lighting | Electrical | General Electrical | 631.795 | Pass | Fail | 0 | 1 | 169.5 | 2022-07-01 09:54 | 2022-07-06 17:00 | 2022-07-06 13:00 | 2022-07-06 17:00 | 2022-07-13 14:30 |  | WCAPPR | Attended site signed in jsa completed. Proceded to test cables between lights, found timer was working correctly. Covered pe cell and only some came on. Found overide in the off position in block3 fitting and machining board. After switching that on all lights came on with block one testing kit.Job completed
MSA-MRWA | WA5696147 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Media Room- TV Signal Port pushed in and not receiving TV Signal | Electrical | General Electrical | 441.2325 | Pass | Fail | 0 | 1 | 169.5 | 2022-08-08 09:54 | 2022-08-11 17:00 | 2022-08-10 13:15 | 2022-08-11 17:00 | 2022-08-17 14:45 |  |  | complete
MSA-DTWD | WA5761326 | 2 | COMMERCIAL PLUMBING AND GAS | Leaking pan in cubicle toilet | Plumbing & Drainage | Toilets/Cisterns | 999.155 | Pass | Fail | 0 | 1 | 169.5 | 2022-08-18 08:08 | 2022-08-23 17:00 | 2022-08-22 10:00 | 2022-08-23 17:00 | 2022-08-29 11:30 |  | WACCES | repaired leaking pans x2, replaced cisterns x2
MSA-DTAG | WA5839780 | 2 | Sapio Pty Ltd | L30.12 Patch room camera is not available - see notes below | Security | CCTV Surveillance | 1217.27 | Pass | Fail | 0 | 1 | 169.5 | 2022-09-09 15:48 | 2022-09-14 17:00 | 2022-09-12 11:00 | 2022-09-14 17:00 | 2022-09-19 12:30 |  |  | Replaced camera
MSA-DCA | WA6390713 | 1 | Techworks Plumbing | Geology Building - Level 1 - Female Toilets - blocked toilet cubicle 2 | Plumbing & Drainage | Toilets/Cisterns | 143.3 | Pass | Fail | 0 | 1 | 169.45 | 2022-12-22 12:02 | 2022-12-23 17:00 | 2022-12-22 12:03 | 2022-12-23 17:00 | 2022-12-29 13:30 |  |  | Assessed blocked toilet in female toilets on level 1Cleared blockage with plunger and testedCleaned up work areaGerbrit pneumatic flush buttons are faulty causing blockage, therefore need to be replaced
MSA-DTWD | WA5699215 | 3 | High Tech Pest Control | L1-D102../. D103 Check floor board for White Ant infestation | Pest Control | General Pest | 216.5 | Pass | Fail | 0 | 1 | 169.4167 | 2022-08-10 07:55 | 2022-08-16 17:00 | 2022-08-16 07:20 | 2022-08-16 17:00 | 2022-08-23 08:45 |  |  | Inspect Room D102/103 for Termites, old damage in floor boards in 102, skirting damage, door frame has lead, kitchen had old damage.External inspection.No activity found.
MSA-DTWD | WA5379507 | 2 | Protek 24/7 Building & Maintenance | Ground Level - E Block Footpath - Pavers coming up uneven on pathway | Flooring | Concrete | 505.465 | Pass | Fail | -1 | 0 | 169.25 | 2022-04-21 11:54 | 2022-04-27 17:00 | 2022-04-21 13:45 | 2022-04-27 17:00 | 2022-04-28 15:00 |  | WACCES & WCAPPR | Replace Pavers
MSA-DTWD | WA6155642 | 3 | ACTION GLASS & ALUMINIUM | Level 1 - Carpentry Workshop - Door Glass Cracked | Glazing | Door Glass | 812.4 | Pass | Fail | -1 | 0 | 169.25 | 2022-11-08 12:03 | 2022-11-15 17:00 | 2022-11-10 09:15 | 2022-11-15 17:00 | 2022-11-17 10:30 |  |  | ATTENDED SITEMADE SAFE BROKEN WINDOW WITH 1 SQM OF SAFETY FILMRETURNED LATER DATE WITH 2 MEN TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-1128 X 15705.4 L/M OF DOUBLE SIDED TAPE USED
MSA-DCA | WA6425798 | 3 | Protek 24/7 Building & Maintenance | First Floor - Timber flooring- grout’/rubber seal joins worn - see notes | Flooring | Timber | 427.34 | Pass | Fail | -1 | 0 | 169.25 | 2023-01-12 11:49 | 2023-01-19 17:00 | 2023-01-13 10:45 | 2023-01-19 17:00 | 2023-01-20 12:00 |  | WACCES
MSA-DTWD | WA5086034 | 2 | WESTERN IRRIGATION PTY LTD | Grounds - Bore tripping out on low pressure | Landscaping & Gardening | Grounds Maintenance | 732.25 | Pass | Fail | 0 | 1 | 169 | 2022-01-21 10:12 | 2022-01-27 17:00 | 2022-01-24 14:00 | 2022-01-27 17:00 | 2022-01-31 15:00 |  |  | 24-1-2022 Attended site, located 3 faulty solenoid valves. Isolated the valves and liaised with Phil onsite and arranged to return on the 1 February 2022 to replace the valves.31-1-2022 Attend site and replace faulty solenoid valves, test system for correct operation.
MSA-DTWD | WA5188520 | 1 | AWB Co. | Atrium between East and West G block - see notes below | Electrical | Lighting, Internal | 1607.205 | Pass | Fail | 0 | 1 | 169 | 2022-02-23 09:29 | 2022-02-24 17:00 | 2022-02-23 14:30 | 2022-02-24 17:00 | 2022-03-02 15:30 |  | WCAPPR | Attended site and signed in. Completed JSA and required paperwork for EWP. Liaised with site about works going ahead. Drove scissor lift to g block undercover area. Investigated fault which was on circuit found to be cable earthing out to frame work (suspected cause when light fell). Rectified fault. Went through and resecured and retubed all lights which were accessible off EWP. Found to be 4x fittings on upper roof have faulty ballast. Spoke to fm and he wants all lights in upper area replaced to LED. FM advised us to close of job as he will raise new one for the faulty lights. Off hired scissor. Signed out. **job complete**
MSA-DCA | WA6519993 | 3 | GPS Plumbing & Gas Services PtyLtd | Front of building near late doors - No water flowing since the balcony reconstruction | Plumbing & Drainage | Water | 678.3525 | Pass | Pass | -1 | 0 | 168.9333 | 2023-01-27 09:35 | 2023-02-03 17:00 | 2023-01-27 11:24 | 2023-02-03 17:00 | 2023-02-03 12:20 |  | WCAPPR
MSA-MRWA | WA6178528 | 1 | GPS Plumbing & Gas Services PtyLtd | Main tap in the kitchen is leaking and jammed | Plumbing & Drainage | Water | 1100.18 | Pass | Fail | 0 | 1 | 168.8667 | 2022-11-14 12:01 | 2022-11-15 17:00 | 2022-11-14 12:55 | 2022-11-15 17:00 | 2022-11-21 13:47 |  |  | Replaced leaking billi mixer tap
MSA-DTAG | WA5679562 | 2 | Australian HVAC Services Pty. Ltd. | 14 and ground floor-Magistrates Chambers and ground floor-air con cold - see notes | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Fail | 0 | 1 | 168.5 | 2022-07-26 14:55 | 2022-07-29 17:00 | 2022-07-27 08:00 | 2022-07-29 17:00 | 2022-08-03 08:30 |  |  | Return to site and check temps on level 14 and ground. Found temp in room 14.05 to be 23.5 degrees. Found temps in ground floor registry to be 22.5 degrees. Ground floor is a difficult area to heat as the ceiling is two levels high and hot air rises, also the front sliding door is constantly opening letting the cold air from outside enter. The system is working the best it can at present
MSA-DCA | WA6391644 | 0 | Techworks Plumbing | Hackett hall ground-UAT-water spout has come out of the wall | Plumbing & Drainage | Water | 135.14 | Pass | Fail | 0 | 1 | 168.5 | 2022-12-22 14:38 | 2022-12-22 16:38 | 2022-12-22 15:30 | 2022-12-22 18:38 | 2022-12-29 16:00 |  |  | Repaired -water spout has come out of the wall
MSA-DFES | WA6520028 | 3 | Protek 24/7 Building & Maintenance | Car Park B - Ground level - Broken pit lid - near Lake Road see notes | Building | General Building | 497.91 | Pass | Fail | -1 | 0 | 168.5 | 2023-01-27 09:57 | 2023-02-03 17:00 | 2023-01-30 14:45 | 2023-02-03 17:00 | 2023-02-06 15:15 |  | WACCES
MSA-DFES | WA4992536 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | PA System emitting a loud buzzing/humming noise | Electrical | General Electrical | 367.33 | Pass | Fail | -1 | 0 | 168.5 | 2022-01-06 13:10 | 2022-01-11 17:00 | 2022-01-07 14:15 | 2022-01-11 17:00 | 2022-01-14 14:45 |  |  | Issue is caused by Call-Out system and outside scope of works. Informed Sharon Streatfield.
MSA-DFES | WA5699581 | 2 | WA BOILER SPARES & SERVICE | Operational Practice Ground-Tower 2 & 3 faults- see notes | Mechanical Services | Boilers | 610 | Pass | Fail | 0 | 1 | 168.5 | 2022-08-10 10:33 | 2022-08-15 17:00 | 2022-08-12 09:00 | 2022-08-15 17:00 | 2022-08-19 09:30 |  |  | Repaired 4 x leaking gas valves
MSA-DTAG | WA6668652 | 1 | AHS Services WA Pty Ltd (Anchor) | Gas box - Possible leakage | Plumbing & Drainage | Gas | 639.345 | Pass | Fail | 0 | 1 | 168.4167 | 2023-02-22 10:52 | 2023-02-23 17:00 | 2023-02-22 11:35 | 2023-02-23 17:00 | 2023-03-01 12:00
MSA-DTAG | WA5295575 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground - Male staff toilet - Left hand hinge broken on toilet lid/seat, last cubicle | Plumbing & Drainage | Water | 650.14 | Pass | Fail | 0 | 1 | 168.3167 | 2022-03-29 15:53 | 2022-04-01 17:00 | 2022-03-30 08:31 | 2022-04-01 17:00 | 2022-04-06 08:50 |  | WACCES | No Reece store have required replacement seat. Got 2 branch managers looking into it to see re- replacement seat and price.
MSA-DTAG | WA5834382 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Custody holding cell 1 - Bio clean - blood spilled on the floor | Cleaning | Cleaning | 300 | Fail | Fail | 1 | 2 | 168.0667 | 2022-09-06 15:53 | 2022-09-06 17:53 | 2022-09-13 15:17 | 2022-09-06 19:53 | 2022-09-20 15:21 |  |  | As per work order no# WA5834382
MSA-DTAG | WA5016806 | 1 | Sapio Pty Ltd | Lower Level - Custody Hallway Door Lock jamming | Electrical | General Electrical | 875.55 | Pass | Fail | 0 | 1 | 168.0333 | 2022-01-13 07:29 | 2022-01-13 17:00 | 2022-01-13 11:03 | 2022-01-13 17:00 | 2022-01-20 11:05 |  |  | Replaced Custody Entry Door strike. File both new lock & frame to fit as door no gap to frame. Advised site to call Locksmith and correct door gap.Job completed.
MSA-DTWD | WA6126219 | 2 | M Construction (WA) | Door hook for the door to stay open in the stores area has broken | Building | Doors | 169.57 | Pass | Fail | 0 | 1 | 168.0333 | 2022-10-25 10:58 | 2022-10-28 17:00 | 2022-10-28 08:16 | 2022-10-28 17:00 | 2022-11-04 08:18 |  |  | Block of wood supporting door hook had come away from wall. Install new piece of wood long enough to catch 2 studs for fixing.
MSA-DTAG | WA5089797 | 2 | Midolo Building Services | Ground - Front colorbond security door - security door has drop and is difficult to open and close | Building | Doors | 498.45 | Pass | Fail | 0 | 1 | 168 | 2022-01-25 06:31 | 2022-01-28 17:00 | 2022-01-25 12:45 | 2022-01-28 17:00 | 2022-02-01 12:45 |  | WACCES | NEW HINGE & DOOR CLOSER FITTED
MSA-DTAG | WA5175696 | 2 | Australian HVAC Services Pty. Ltd. | Level 3 - Court room 34 -Air con doesn’t appear to be working, courtroom is warm | Air Conditioning | Room Air Conditioners | 347.97 | Pass | Fail | 0 | 1 | 168 | 2022-02-21 12:53 | 2022-02-24 17:00 | 2022-02-21 13:30 | 2022-02-24 17:00 | 2022-02-28 13:30 |  |  | Attend site. Access level 3 court 34. Found court in session. Access bms and check temps. Found temps to be reading 23 degrees. Check vav box operation and found to be working as normal. Access court 34 and check sensor calibration, all ok. Unable to to determine cause of temperature issues as is working as normal.
MSA-DFES | WA5477660 | 2 | Protek 24/7 Building & Maintenance | Engine Room - Cornice broken and falling from ceiling in the Engine Room | Building | General Building | 575.48 | Pass | Fail | 0 | 1 | 168 | 2022-05-25 16:51 | 2022-05-30 17:00 | 2022-05-27 11:30 | 2022-05-30 17:00 | 2022-06-03 11:30 |  | WCAPPR | Repair Cornice in engine room
MSA-DTWD | WA5827354 | 3 | AWB Co. | Room C703 - Flickering light | Electrical | Lighting, Internal | 1191.02 | Pass | Fail | 0 | 1 | 168 | 2022-09-01 09:52 | 2022-09-08 17:00 | 2022-09-07 11:45 | 2022-09-08 17:00 | 2022-09-14 11:45 |  | WCAPPR | Attended site and signed in. Completed jsa. Set up ladder where flood light is going. Isolated lighting circuit. Added in Pe cell where junction to light was. Connected up light and made sure light and pe cell was water tight. Tested. Everything working as intended. Cleaned up. Completed paperwork. Signed out.Job completeBRAF approval attached
MSA-DTWD | WA6256841 | 3 | AWB Co. | Faulty ceiling lights, please repair. | Electrical | Lighting, Internal | 369.275 | Pass | Fail | 0 | 1 | 168 | 2022-11-24 09:21 | 2022-12-01 17:00 | 2022-11-29 13:00 | 2022-12-01 17:00 | 2022-12-06 13:00 |  | WACCES | Attended site signed in jsa completed. Removed of x3 old lights and replaced with new as non fixable. Tested operationalJob completed
MSA-DTWD | WA6358197 | 2 | WESTERN IRRIGATION PTY LTD | Main Retic - timing is out please contact Tracey | Landscaping & Gardening | Grounds Maintenance | 1792.5 | Pass | Fail | 0 | 1 | 168 | 2022-12-06 08:14 | 2022-12-09 17:00 | 2022-12-09 11:30 | 2022-12-09 17:00 | 2022-12-16 11:30 |  |  | Drain main retic, adjust timing and refill / commission.
MSA-DCA | WA6650186 | 0 | Critical Fire Protection & Training | Fire alarm has activated-needs to be reset | Fire Protection Services | Fire Protection - Monitor System | 535.915 | Pass | Fail | 0 | 1 | 167.9833 | 2023-02-20 09:51 | 2023-02-20 11:51 | 2023-02-20 10:01 | 2023-02-20 13:51 | 2023-02-27 10:00
MSA-DTWD | WA5306572 | 3 | AWB Co. | Block 3 - ground - room 3C34 - Lights not working F&M store | Electrical | Lighting, Internal | 990.58 | Pass | Fail | 0 | 1 | 167.5 | 2022-04-06 14:36 | 2022-04-13 17:00 | 2022-04-13 12:30 | 2022-04-13 17:00 | 2022-04-20 12:00 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty lights in store room. Pulled all lights down and put all new LED battens up. Got laser out to make sure they were straight before putting up. Packed and cleaned up. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-MRWA | WA5392255 | 2 | Automatic Fire Protection (ARA) | Level 6 - Fire Reel Cabinet - Fire Hose Leaking | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 720.7 | Pass | Fail | 0 | 1 | 167.5 | 2022-05-03 08:57 | 2022-05-06 17:00 | 2022-05-04 09:00 | 2022-05-06 17:00 | 2022-05-11 08:30 |  |  | 04/05 AMInvestigated leaking hose reel on level 6.Hose reel was leaking from centre hub. Overhauled O Rings in centre hub however hose reel continued to leak when under pressure. Drained all water out of hose reel to stop it dripping.Replacement swing hose reel required including pipe freeze.11/5 AMAttended site and installed new swing hose reel.
MSA-DTWD | WA6205448 | 3 | COMMERCIAL PLUMBING AND GAS | Toilet pans in both cubicles are damaged | Plumbing & Drainage | Toilets/Cisterns | 1693.21 | Pass | Fail | 0 | 1 | 167.5 | 2022-11-17 10:01 | 2022-11-24 17:00 | 2022-11-24 12:00 | 2022-11-24 17:00 | 2022-12-01 11:30 |  |  | replaced pan and flushpipe
MSA-DFES | WA5383814 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Building - Pressure problems with hot water system (Solarhart) | Plumbing & Drainage | HWS/Units Electric & Gas | 617.3 | Fail | Fail | 0 | 1 | 167.4833 | 2022-04-28 07:28 | 2022-05-02 17:00 | 2022-05-04 09:06 | 2022-05-02 17:00 | 2022-05-11 08:35 |  | WCAPPR | Arrived to site to inspect why there is low hot water pressure found there was good pressure on the solar Trole couldn’t get up due to didn’t have a second person and working at height will return with the right gear to fix the problems.Returned back to site with second person and big ladder replaced the temp valve due to it was faulty tested after replacing the temp valve and working correctly now
MSA-DTAG | WA5414127 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Cleaning and Grafitti Removal - Custody - Cell 5 requires Bio Clean Blood on walls | Cleaning | Emergency Cleans | 300 | Fail | Fail | 1 | 2 | 167.3667 | 2022-05-12 16:59 | 2022-05-12 18:59 | 2022-05-16 12:43 | 2022-05-12 20:59 | 2022-05-23 12:05 |  |  | As per Work Order No# WA5414127
MSA-DTAG | WA5413168 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground Level - Various Locations - Covid Clean Required - See notes below | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 2 | 167.2833 | 2022-05-12 09:31 | 2022-05-12 11:31 | 2022-05-16 12:47 | 2022-05-12 13:31 | 2022-05-23 12:04 |  |  | As per Work Order No# WA5413168
MSA-DTWD | WA5586858 | 2 | Lane's Plumbing | BLD 822 - ground floor - store room - faulty taps | Plumbing & Drainage | Water |  | Pass | Fail | -1 | 0 | 167 | 2022-07-06 15:36 | 2022-07-11 17:00 | 2022-07-07 15:00 | 2022-07-11 17:00 | 2022-07-14 14:00 |  |  | REPLACE FAULTY TAPS TO STORE ROOM BLD 822
MSA-DFES | WA5838377 | 3 | Critical Fire Protection & Training | Main Admin - Fire alarm panel is not activated when smoke alarm is active via security system | Fire Protection Services | Fire Protection - Monitor System | 635.25 | Pass | Fail | 0 | 1 | 167 | 2022-09-08 12:45 | 2022-09-15 17:00 | 2022-09-13 13:00 | 2022-09-15 17:00 | 2022-09-20 12:00 |  |  | Attend site review security connection, note cable in BOWS require reattend with security contractor onsite verify connection/type.Ows not physically interfacedRelay modification requiredSecurity contractor required
MSA-DFES | WA6361841 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - PA sound is unclear & white noise when volume turned up | Electrical | General Electrical | 543.5125 | Pass | Fail | -1 | 0 | 167 | 2022-12-08 13:57 | 2022-12-15 17:00 | 2022-12-09 10:30 | 2022-12-15 17:00 | 2022-12-16 09:30 |  | WACCES | Matthew Kenney (09/12/2022) - Work NoteArrived onsite at 10:30 to investigate PA, spoke to staff and was told that volume was set too low to hear when operating, and when turned up there is feedback coming from speakers especially older ones, collected details of speakers, there are 12x circle recessed ones throughout building and 1x box speaker in lockers, recommend changing old speakers and resetting amp to original settings to resolve issue, took details of newer speakers that have been installed so we can source replacements. Advised staff of works and left site at 11:45.Arrived onsite at 7:45 to replace speaker in officers bedroom, changed out old one for new speaker and tested, new speaker seems to have less feedback noise than old one, also lowered volume input slightly on input 3 (sleeping quarters) and did a proper test call through call center and found the volume was satisfactory and audio was clearer. Still need to sort replace remaining 11 old speakers and 1 wall box spe
MSA-DCA | WA5694917 | 2 | Protek 24/7 Building & Maintenance | Ground Learning Studio 3 Repair broken floorboard/s.- see notes | Flooring | Timber | 652.35 | Pass | Fail | 0 | 1 | 166.75 | 2022-08-05 14:45 | 2022-08-10 17:00 | 2022-08-08 13:00 | 2022-08-10 17:00 | 2022-08-15 11:45 |  |  | Sand back floor boards, patched and polished
MSA-DTWD | WA5833385 | 2 | Protek 24/7 Building & Maintenance | G10 foyer - Roof leak | Roofing | Metal Roofing | 668.57 | Pass | Fail | 0 | 1 | 166.75 | 2022-09-06 09:38 | 2022-09-09 17:00 | 2022-09-08 13:45 | 2022-09-09 17:00 | 2022-09-15 12:30 |  |  | Investigate and repair roof leaks
MSA-DTWD | WA5010017 | 2 | CAPS AUSTRALIA PTY LTD | compressor shed - South end - faulty receiver dryer | Equipment | Compressors, Generators |  | Pass | Fail | -1 | 0 | 166.5 | 2022-01-12 09:28 | 2022-01-17 17:00 | 2022-01-12 12:30 | 2022-01-17 17:00 | 2022-01-19 11:00 |  |  | job completed - The unit needs to be checked by a refrigeration company for gas and the high pressure switch
MSA-DTAG | WA5961689 | 2 | Midolo Building Services | Ground - Public waiting area - An evacuation sign was pulled from the wall - see notes below | Building | Internal Walls | 156.63 | Pass | Fail | 0 | 1 | 166.5 | 2022-09-19 09:17 | 2022-09-22 17:00 | 2022-09-20 10:00 | 2022-09-22 17:00 | 2022-09-27 08:30 |  | WACCES | Re attached sign to wall
MSA-DFES | WA6208133 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Front of Station - red strobe light its not operating properly | Electrical | Lighting, External | 1250.62 | Pass | Fail | 0 | 1 | 166.5 | 2022-11-17 13:27 | 2022-11-18 17:00 | 2022-11-17 14:30 | 2022-11-18 17:00 | 2022-11-24 13:00 |  | WACCES | Onsite at 11:00 replaced 1x siren with new and 1x strobe light with new and notified DO of works complete and moved onto the next job at 13:00.
MSA-DTAG | WA6232187 | 0 | GPS Plumbing & Gas Services PtyLtd | undercover carpark sewerage pipe cracked and leaking | Plumbing & Drainage | Materials | 3472.055 | Pass | Fail | 0 | 1 | 166.5 | 2022-11-19 12:41 | 2022-11-19 14:41 | 2022-11-19 13:30 | 2022-11-19 16:41 | 2022-11-26 12:00 |  |  | The copper pipe from the septic tank to the mains is corroded it needs to be replaced
MSA-MRWA | WA6148879 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - Room 119.2 - Investigate fault alarm on fume cupboards post power outage | Air Conditioning | Building HVAC Maintenance (Major Plant) | 484.23 | Pass | Fail | -1 | 0 | 166.4 | 2022-11-04 09:59 | 2022-11-09 17:00 | 2022-11-04 10:00 | 2022-11-09 17:00 | 2022-11-11 08:24 |  | WACCES | It was reported that several weekends ago the power to the site failed. Carried out time trails and investigated soil FC battery replacement.
MSA-DCA | WA5306084 | 2 | GPS Plumbing & Gas Services PtyLtd | Main Building - Level 1 - Public toilets - HWS valve not closing water constantly running through | Plumbing & Drainage | Drainage | 803.46 | Pass | Fail | -1 | 0 | 166.15 | 2022-04-06 10:13 | 2022-04-11 17:00 | 2022-04-07 11:06 | 2022-04-11 17:00 | 2022-04-14 09:15 |  | WCAPPR | Replaced corroded and jammed check valves to hot water unit.
MSA-DTWD | WA5488432 | 3 | Precise Air Group | Level 2 - D206 - Noisy aircon when fan motor starts up | Air Conditioning | Room Air Conditioners | 188.385 | Pass | Fail | 0 | 1 | 166.1167 | 2022-06-02 12:49 | 2022-06-10 17:00 | 2022-06-07 14:00 | 2022-06-10 17:00 | 2022-06-14 12:07 |  |  | Job rated under wrong site. Travelled to right campus signed in and located area. Found no major issues but filters do need to be replaced.
MSA-DTAG | WA5188616 | 3 | Sapio Pty Ltd | Upper basement B01 corridor double door mag lock full of water. | Security | Security Management System | 719.53 | Pass | Pass | -1 | 0 | 166 | 2022-02-23 10:16 | 2022-03-02 17:00 | 2022-02-23 15:00 | 2022-03-02 17:00 | 2022-03-02 13:00 |  | WACCES | Replaced maglock on B01 Corridor Double Door.
MSA-DTWD | WA5569399 | 3 | AWB Co. | 3 phase Blacksmith hammer has damaged lead | Equipment | Electrical Equipment | 352.505 | Pass | Fail | 0 | 1 | 166 | 2022-06-27 14:18 | 2022-07-04 17:00 | 2022-07-04 14:00 | 2022-07-04 17:00 | 2022-07-11 12:00 |  |  | Attended site and signed in. Completed jsa. Located black hammer in workshop. Inspected machine and load rating. Installed plug top to machine and required. Could not test rotation as the machine isn’t in it location to be working yet. Everything else okay and ready to use. Signed out. Job complete
MSA-DTWD | WA6504392 | 3 | AWB Co. | 3 x GPO on South wall not working | Electrical | Lighting, Internal | 764.99 | Pass | Fail | 0 | 1 | 166 | 2023-01-19 15:25 | 2023-01-27 17:00 | 2023-01-24 12:00 | 2023-01-27 17:00 | 2023-01-31 10:00 |  | WCAPPR
MSA-DTWD | WA5564224 | 3 | AWB Co. | 8G36 - Lights tripping on W2 RCD circuit | Electrical | General Electrical | 901.43 | Pass | Pass | -1 | 0 | 166 | 2022-06-21 09:07 | 2022-06-28 17:00 | 2022-06-21 13:00 | 2022-06-28 17:00 | 2022-06-28 11:00 |  |  | Attended site and signed in. Completed JSA. Located room 8g36. Supply and replace lights to middle of classroom. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5585379 | 3 | Protek 24/7 Building & Maintenance | Water leak on north side over table | Roofing | Metal Roofing | 496.88 | Pass | Fail | -1 | 0 | 166 | 2022-07-05 15:45 | 2022-07-12 17:00 | 2022-07-07 13:45 | 2022-07-12 17:00 | 2022-07-14 11:45 |  |  | Record & Report
MSA-DTWD | WA6158732 | 3 | AWB Co. | 6B VVB tool store - Light not working and missing diffuser. | Electrical | Lighting, Internal | 960.705 | Pass | Pass | -1 | 0 | 166 | 2022-11-10 08:24 | 2022-11-17 17:00 | 2022-11-10 13:00 | 2022-11-17 17:00 | 2022-11-17 11:00 |  | WACCES | Attended site signed in jsa completed.Removed 4x old fittings and replaced with new 40w integrated batterns.Tested operational.Job completed.
MSA-DFES | WA5099888 | 2 | Protek 24/7 Building & Maintenance | External front door to Room 2 SO Office - Front door needs repair & possible replacement (MDF blown) | Building | Doors | 747.645 | Pass | Fail | 0 | 1 | 165.75 | 2022-02-02 09:22 | 2022-02-07 17:00 | 2022-02-04 12:00 | 2022-02-07 17:00 | 2022-02-11 09:45 |  |  | Repair to Front Door
MSA-DCA | WA6292893 | 2 | Protek 24/7 Building & Maintenance | Building/Warehouse - Repairs to front gate (see notes) | Building | Steel Fencing & Gates | 562.98 | Pass | Fail | 0 | 1 | 165.75 | 2022-11-29 14:03 | 2022-12-02 17:00 | 2022-11-30 12:30 | 2022-12-02 17:00 | 2022-12-07 10:15 |  | WACCES | Bend back gate as temp, measured to replaceAdjust gate and install new spigots
MSA-DTAG | WA5697390 | 2 | Midolo Building Services | ground Court Room One Entry & Waiting Leak adjacent to Court one entry-see notes | Building | Ceiling | 302.41 | Fail | Fail | 1 | 2 | 165.5 | 2022-08-09 09:07 | 2022-08-12 17:00 | 2022-08-18 10:00 | 2022-08-12 17:00 | 2022-08-25 07:30 |  | WCAPPR | potential leak spots sealed/cleaned/repaired
MSA-DTWD | WA6151879 | 1 | Australian Airconditioning Services Pty Ltd | Cooling Tower leaking at waste connection | Air Conditioning | Building HVAC Maintenance (Major Plant) | 765.92 | Pass | Fail | 0 | 1 | 165.5 | 2022-11-07 09:33 | 2022-11-08 17:00 | 2022-11-07 12:00 | 2022-11-08 17:00 | 2022-11-14 09:30 |  | WACCES | Checked cooling tower and found water leaking from seal on main drain line. Unable to shut down system due to classes. Patched leak with tape to slow down untill we can get back on friday to shut down system and drain cooling tower and repair leak.11/11 Went to site, shut down system and drained cooling tower. Repaired leak and left over the weekend to dry.14/11 Went to site, filled cooling and no more leak. Swiched system back on and all ok.
MSA-DCA | WA5472981 | 1 | Protek 24/7 Building & Maintenance | Playground Area - Spinning wheels on playground equipment has come off - see notes below | Equipment | Recreation Equipment | 291.625 | Pass | Fail | 0 | 1 | 165.25 | 2022-05-24 12:04 | 2022-05-25 17:00 | 2022-05-24 14:00 | 2022-05-25 17:00 | 2022-05-31 11:15 |  |  | Repair Damaged spinning wheels on playground equipment
MSA-DCA | WA6390419 | 1 | Protek 24/7 Building & Maintenance | External ground - Outside PICA bar - Broken paving - see notes | Landscaping & Gardening | Landscaping | 837.78 | Pass | Fail | 0 | 1 | 165.25 | 2022-12-22 08:54 | 2022-12-23 17:00 | 2022-12-22 13:30 | 2022-12-23 17:00 | 2022-12-29 10:45 |  | WACCES | Relay the pavers around solenoid boxes
MSA-DTWD | WA5382631 | 3 | AWB Co. | Level 5 - Cooling Tower - GPO Damaged/Cracked - dosing pump | Electrical | General Electrical | 666.63 | Pass | Fail | 0 | 1 | 165 | 2022-04-27 08:13 | 2022-05-04 17:00 | 2022-05-03 13:00 | 2022-05-04 17:00 | 2022-05-10 10:00 |  | WACCES | -Attended site signed in jsa completed. De engergised b3 and commenced works. Removed gpo and put two way box. Extended cables 5m to get out of wet zone as requested.All tested and operational*** job completed ***
MSA-DTWD | WA5569394 | 3 | AWB Co. | Drill Press with Damaged 23 phase plug | Equipment | Electrical Equipment | 433.6 | Pass | Fail | 0 | 1 | 165 | 2022-06-27 14:15 | 2022-07-04 17:00 | 2022-07-04 13:30 | 2022-07-04 17:00 | 2022-07-11 10:30 |  |  | Attended site and signed in. Completed jsa. Located drill presses. Disconnect and removed cabling. Reinstalled cabling and plug tops. Checked phase rotations and adjusted correctly. All okay. Signed out. Job complete
MSA-DCA | WA5596930 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Preparation Lab - Door on Fume Cupboard 2 extremely difficult to raise and lower | Building | Doors | 517.67 | Pass | Fail | -1 | 0 | 165 | 2022-07-11 11:24 | 2022-07-18 17:00 | 2022-07-12 14:30 | 2022-07-18 17:00 | 2022-07-19 11:30 |  | WACCES | Fume cupboard sash was found to be difficult to move due to sashwire falling out the pulley groove. This generally occurs from roughhandling of the sash. It is encouraged to ensure sash is operatedwith 2 hands to prevent rough handling.
MSA-DTWD | WA5888156 | 2 | Lane's Plumbing | Level 1 - Fat D Bathroom - Faulty Cistern | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Fail | -1 | 0 | 165 | 2022-09-16 13:34 | 2022-09-21 17:00 | 2022-09-16 15:00 | 2022-09-21 17:00 | 2022-09-23 12:00 |  |  | Repairs to cistern
MSA-DTWD | WA5706105 | 3 | Protek 24/7 Building & Maintenance | Water leak above CNC machine | Roofing | Metal Roofing | 424.19 | Pass | Fail | 0 | 1 | 164.75 | 2022-08-11 08:47 | 2022-08-18 17:00 | 2022-08-17 12:30 | 2022-08-18 17:00 | 2022-08-24 09:15 |  | WCAPPR | Cleaned and sealed box gutter jointSealed crack in louvre
MSA-DTWD | WA5781333 | 2 | AWB Co. | ET01 – Classroom-Faulty light fitting | Electrical | Lighting, Internal | 468.915 | Pass | Fail | 0 | 1 | 164.75 | 2022-08-19 15:50 | 2022-08-24 17:00 | 2022-08-23 11:30 | 2022-08-24 17:00 | 2022-08-30 08:15 |  | WACCES | Attended site and signed in. Completed JSA. Located room. Set up work area. Isolated circuit requiring work. Removed old fitting and replaced with New LED panel. Energised circuit and tested for correct operation. Packed up work area. Notified relevant personnel. **job complete**
MSA-DCA | WA5978372 | 1 | Protek 24/7 Building & Maintenance | Sinking floorboard | Flooring | Timber | 485.51 | Pass | Fail | 0 | 1 | 164.75 | 2022-09-28 10:26 | 2022-09-29 17:00 | 2022-09-28 13:00 | 2022-09-29 17:00 | 2022-10-05 09:45 |  |  | Repaired Trip Hazard - sanded boards
MSA-DTWD | WA5978038 | 3 | Australian Airconditioning Services Pty Ltd | Toilets - Fans not working due to faulty timer | Air Conditioning | Materials | 622.1 | Pass | Pass | -1 | 0 | 164.5 | 2022-09-28 08:27 | 2022-10-05 17:00 | 2022-09-28 15:00 | 2022-10-05 17:00 | 2022-10-05 11:30 |  |  | complete
MSA-DFES | WA6672375 | 3 | Protek 24/7 Building & Maintenance | Service Training/FDP office - Screening panels have fallen and broken | Building | General Building | 1027.32 | Pass | Fail | -1 | 0 | 164.5 | 2023-02-23 15:52 | 2023-03-02 17:00 | 2023-02-24 14:30 | 2023-03-02 17:00 | 2023-03-03 11:00 |  | WACCES
MSA-DTWD | WA5488302 | 2 | M Construction (WA) | EG19 - Door Closer Faulty | Building | Doors | 695.84 | Pass | Fail | -1 | 0 | 164.4667 | 2022-06-02 11:48 | 2022-06-08 17:00 | 2022-06-02 14:17 | 2022-06-08 17:00 | 2022-06-09 10:45 |  |  | Attended site to investigate faulty door closer, replaced door closer with new as required.
MSA-DTWD | WA5295542 | 2 | Protek 24/7 Building & Maintenance | Block 3 – Heavy Auto – outside workshop - Re-attach wire fence to wall/anchor point | Building | General Building | 497 | Pass | Fail | 0 | 1 | 164.25 | 2022-03-29 15:14 | 2022-04-01 17:00 | 2022-03-30 12:45 | 2022-04-01 17:00 | 2022-04-06 09:00 |  |  | Reattach Wire fence to anchor point
MSA-DTWD | WA5790891 | 3 | AWB Co. | Foyer & stairs-Multiple Fluro lights out | Electrical | Lighting, Internal | 774.905 | Pass | Fail | -1 | 0 | 164.25 | 2022-08-22 13:19 | 2022-08-29 17:00 | 2022-08-25 13:30 | 2022-08-29 17:00 | 2022-09-01 09:45 |  | WCAPPR | Attended site and signed in. Completed JSA. Located t block foyer and stairs. Set up work area. Went through and replaced various tubes with the 8ft ladder. Placed ladder back onto car and got 12ft ladder off. Replaced various tubes on stairwell. Packed and cleaned up site. Notified relevant personnel of works completed. **job complete**
MSA-DTAG | WA6154707 | 3 | Seme Solutions Pty Ltd | CCTV1 - DISK 7 - FAILURE | Security | CCTV Surveillance | 460.16 | Pass | Pass | -1 | 0 | 164.0333 | 2022-11-07 16:28 | 2022-11-14 17:00 | 2022-11-07 16:30 | 2022-11-14 17:00 | 2022-11-14 12:32 |  | WACCES | ***SEE SIGSLIP FOR ACTUAL START TIME***Installed drive job complete
MSA-DTAG | WA5974370 | 0 | Sapio Pty Ltd | Basement of Building - Gate for entry and access for garage - Gate is not working - no cars entering | Security | Access Control | 1657.58 | Fail | Fail | 0 | 1 | 164 | 2022-09-23 10:56 | 2022-09-23 12:56 | 2022-09-23 13:30 | 2022-09-23 14:56 | 2022-09-30 09:30 |  |  | Work performed by Mitchell Watt (30/09/2022) UPS in Basement Gate Controller replaced. Tested, OK.Job completed.
MSA-DTWD | WA5468821 | 1 | Equans Mechanical Services Australia | E58 Kitchen - Upright Freezer running too hot and going into alarm - See notes below | Refrigeration | Freezers | 665.3 | Pass | Fail | 0 | 1 | 163.75 | 2022-05-20 12:42 | 2022-05-23 17:00 | 2022-05-20 14:15 | 2022-05-23 17:00 | 2022-05-27 10:00 |  | WACCES & WCAPPR | Freezer very iced up. Left off to defrost over weekend. Stock removed and was informed that kitchen not being used Monday. Returned to site. Started unit and checked operation. Condenser unit running as normal and unit cooling to set point. Unit reached set point but did cycle the compressor off. Investigated and found Dixall controller has failed and constantly runs compressor due to seized relay in controller. New controller ordered. ETA 24 hours as controller needs programming by Arcus to suit unit specifications.Picked up parts from suppliers. Returned to site. Fitted new controller and wired accordingly. Started unit and checked operation. Unit cycling off at -20 deg as per normal. All ok
MSA-DFES | WA5256527 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Administration - Ground - Eastern foyer Administration - | Electrical | General Electrical | 387.53 | Pass | Fail | 0 | 1 | 163.5167 | 2022-03-17 11:09 | 2022-03-24 17:00 | 2022-03-23 14:45 | 2022-03-24 17:00 | 2022-03-30 10:16 |  | WACCES | Attended site at 1445. Investigated light in parcel delivery room not working. Starter for faulty light has burnt out and fused with holder, part will need replacing or replace light with LED Batten. Investigated lights flickering in Eastern foyer Admin, fault was not present at the time however the lights are very old and the globes may flicker when first being switched on at start of day when cold. I recommend replacing lights to match other LED fittings in area. Left site at 1600.Onsite 1000 from previous job, replaced globe in light fittings g for flags, tested and cleaned up, informed staff all complete and signed out 1016.
MSA-DTAG | WA5305195 | 3 | Seme Solutions Pty Ltd | Alarm codes not working on panels | Security | Monitoring | 494 | Pass | Fail | -1 | 0 | 163.5 | 2022-04-05 12:57 | 2022-04-12 17:00 | 2022-04-06 14:30 | 2022-04-12 17:00 | 2022-04-13 10:00 |  |  | System fully operational
MSA-DTWD | WA5413959 | 2 | Protek 24/7 Building & Maintenance | G10 foyer - Roof leak | Building | General Building | 772.45 | Pass | Fail | -1 | 0 | 163.5 | 2022-05-12 15:42 | 2022-05-17 17:00 | 2022-05-13 14:00 | 2022-05-17 17:00 | 2022-05-20 09:30 |  |  | Repair Roof leak - G10 Foyer
MSA-DTWD | WA5472578 | 2 | AWB Co. | replace lights tubes not working in D107 | Electrical | Lighting, Internal | 174.5425 | Pass | Fail | 0 | 1 | 163.5 | 2022-05-24 08:53 | 2022-05-27 17:00 | 2022-05-26 12:45 | 2022-05-27 17:00 | 2022-06-02 08:15 |  | WCAPPR | Attended site and signed in. Completed jSA. Located cleaner to help me access classroom. Found to be faulty lamps In D107 & D106. Replaced multiple lamps in rooms. Packed up site. Completed paperwork. **job complete**
MSA-DTWD | WA5490987 | 3 | BAKE-QUIP PTY LTD | E Block - Ground Floor - SK3 - Lecturers oven not working | Equipment | Catering Equipment | 935 | Pass | Fail | -1 | 0 | 162.75 | 2022-06-03 11:01 | 2022-06-13 17:00 | 2022-06-08 13:30 | 2022-06-13 17:00 | 2022-06-15 08:15 |  |  | note, this was to actually remove an old oven and install a new one.
MSA-DCA | WA6402986 | 1 | Protek 24/7 Building & Maintenance | Amphitheatre Ramp (next to PICA bar) - Broken railing | Building | General Building | 371.07 | Pass | Fail | 0 | 1 | 162.75 | 2023-01-06 07:58 | 2023-01-06 17:00 | 2023-01-06 13:30 | 2023-01-06 17:00 | 2023-01-13 08:15 |  | WACCES
MSA-DFES | WA6538701 | 2 | Protek 24/7 Building & Maintenance | Ground rear yard - See notes | Paving & Roadworks | Concreting | 794.13 | Pass | Fail | 0 | 1 | 162.75 | 2023-02-08 07:22 | 2023-02-10 17:00 | 2023-02-08 12:15 | 2023-02-10 17:00 | 2023-02-15 07:00 |  | WACCES
MSA-DTAG | WA5413724 | 0 | Seme Solutions Pty Ltd | Sally Port - its jammed and electronics are not working but manually able to open | Security | Security Management System | 1012.85 | Pass | Fail | 0 | 1 | 162.15 | 2022-05-12 13:13 | 2022-05-12 15:13 | 2022-05-12 14:45 | 2022-05-12 17:13 | 2022-05-19 08:54 |  | WACCES | Attended site. Sally port roller door doesn’t operate properly. Checked power, checked connection, checked operation through software”Pacom”. Replaced intercom AIPHONE LEM-1DL. Checked functionality, everything is working fine.
MSA-DTWD | WA6526797 | 2 | AWB Co. | D2 Male public toilets - Broken/vandalised lights need repairing or replacing | Electrical | Lighting, Internal | 543 | Pass | Fail | -1 | 0 | 161.5 | 2023-02-01 10:58 | 2023-02-06 17:00 | 2023-02-01 14:30 | 2023-02-06 17:00 | 2023-02-08 08:00 |  | WACCES
MSA-DTWD | WA5995039 | 2 | M Construction (WA) | Eco 1& 2 - Broken signage on wall above basins and extinguishers - See notes | Signage | General Signage | 437.57 | Pass | Fail | 0 | 1 | 156.5167 | 2022-10-06 09:58 | 2022-10-11 17:00 | 2022-10-11 01:30 | 2022-10-11 17:00 | 2022-10-17 14:01 |  |  | Have fixed all signage that was possible will have to order new signs.
MSA-DTWD | WA5081550 | 2 | Equans Mechanical Services Australia | Splitting Beans Cafe - Display fridge & cool room not working | Refrigeration | Coolroom | 994.12 | Pass | Fail | 0 | 1 | 156.5 | 2022-01-20 15:37 | 2022-01-25 17:00 | 2022-01-25 15:00 | 2022-01-25 17:00 | 2022-02-01 03:30 |  |  | PICKED UP PARTS FROM SUPPLIER, ACCESSED CAFE AND OPENED CAKE FRIDGE PANELS.CHECKED UNIT HELD PRESSURE OVER NIGHT, RELEASED NITROGEN AND VAC OUT SYSTEM.CHARGE UP WITH 134A REFRIGERANT, OK
MSA-DTWD | WA5101462 | 1 | Equans Mechanical Services Australia | Due to delay in supplying replacement parts please supply portable A/C unit for classroom 3A60 | Air Conditioning | Room Air Conditioners | 412.5 | Pass | Fail | 0 | 1 | 154 | 2022-02-03 12:01 | 2022-02-04 17:00 | 2022-02-04 07:00 | 2022-02-04 17:00 | 2022-02-10 17:00 |  |  | DELVERY AND COLLECTION OF PORTABLE UNIT
MSA-DFES | WA6208054 | 2 | AWB Co. | kitchen-Cupboard door hinges in need of replacement - see notes | Furniture | Domestic Furniture | 422.485 | Pass | Fail | 0 | 1 | 154 | 2022-11-17 12:32 | 2022-11-22 17:00 | 2022-11-22 13:00 | 2022-11-22 17:00 | 2022-11-28 23:00 |  |  | Andy Lamble (28/11/2022) - Work NoteAttend site and inspect workAttempt to adjust old hinges but unable to Plug holes to take new screwsFit new hinges and check operation of doorsAll correct and site clearedJob is now complete
MSA-DCA | WA6393892 | 0 | ACTION GLASS & ALUMINIUM | glass panel in lift foyer broken - please make safe | Glazing | Window Glass | 414.26 | Pass | Fail | 0 | 1 | 153.9 | 2022-12-29 11:36 | 2022-12-29 13:36 | 2022-12-29 13:30 | 2022-12-29 15:36 | 2023-01-04 23:24 |  | WACCES | ATTENDED SITE TO ASSESS, FOUND THAT TWO MEN NEED TO RETURN.RETURNED WITH 2 MEN AND PLATFORM LADDER TO MEASURE & ASSESSSHATTERED ROOF CANOPYAS PER BRAF EMAILED TO REESE WITHEY
MSA-DTWD | WA6255787 | 2 | JEM Carpentry | Between BLD 815 /814 - Faulty ringlock fence | Building | Steel Fencing & Gates |  | Fail | Fail | 7 | 8 | 152.5 | 2022-11-23 13:53 | 2022-11-28 17:00 | 2023-01-19 07:30 | 2022-11-28 17:00 | 2023-01-25 16:00 |  |  | repair to fence
MSA-DTWD | WA6425860 | 2 | WESTERN IRRIGATION PTY LTD | Ground - Station 8 - Water leak near reticulation controller | Plumbing & Drainage | Water | 3323.79 | Pass | Fail | 0 | 1 | 152.5 | 2023-01-12 12:21 | 2023-01-17 17:00 | 2023-01-17 06:30 | 2023-01-17 17:00 | 2023-01-23 15:00
MSA-DTWD | WA6178625 | 3 | AWB Co. | Main entrance to AMEP - Broke light fitting | Electrical | Lighting, Internal | 582.315 | Pass | Fail | -1 | 0 | 151.5 | 2022-11-14 12:24 | 2022-11-21 17:00 | 2022-11-17 08:00 | 2022-11-21 17:00 | 2022-11-23 15:30 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located light out in AMeL. Isolated circuit. Supplied and replaced with new LED panel. Energised. Tested for correct operation. **job complete**
MSA-DTAG | WA5294514 | 1 | Sapio Pty Ltd | Level 10 - control room - one of the big CCTV screens is flickering | Security | CCTV Surveillance | 558.58 | Pass | Fail | 0 | 1 | 151 | 2022-03-29 07:08 | 2022-03-29 17:00 | 2022-03-29 08:00 | 2022-03-29 17:00 | 2022-04-04 15:00 |  |  | Replaced monitor with Samsung Q75T from PFM stock
MSA-DTWD | WA5303930 | 2 | Techworks Electrical | A-Block - A104 - lights not working | Electrical | General Electrical | 1263.65 | Pass | Fail | 0 | 1 | 151 | 2022-04-04 13:23 | 2022-04-07 17:00 | 2022-04-05 10:00 | 2022-04-07 17:00 | 2022-04-11 17:00 |  | WACCES | Replaced faulty fluro panels with new led panel lights
MSA-DTWD | WA5478719 | 3 | AWB Co. | Under cover area south east - Low gutter blocked with leaves. | Roofing | Guttering | 610.71 | Pass | Fail | 0 | 1 | 151 | 2022-05-26 13:14 | 2022-06-02 17:00 | 2022-06-02 07:00 | 2022-06-02 17:00 | 2022-06-08 14:00 |  |  | Attended and investigated, return required. Cleaned out gutter fitted gutter mesh to section of gutter. Job complete
MSA-DTWD | WA5478728 | 3 | AWB Co. | 7G14 dish washing room - Water leaking from ceiling in various places around dish washing exhaust | Building | General Building | 395.63 | Pass | Fail | 0 | 1 | 151 | 2022-05-26 13:18 | 2022-06-02 17:00 | 2022-06-02 08:30 | 2022-06-02 17:00 | 2022-06-08 15:30 |  |  | Attended leak, required return in better weather to carry out repairs. Found splits in silicone and small holes around extraction unit made repairs may need to be reflashed in near future if issue continues.
MSA-DTWD | WA5127795 | 1 | Equans Mechanical Services Australia | F58 & F59 - Aircon not cooling (same unit for both rooms) | Air Conditioning | Room Air Conditioners | 790.11 | Fail | Fail | 0 | 1 | 150.5 | 2022-02-14 14:19 | 2022-02-15 17:00 | 2022-02-16 08:00 | 2022-02-15 17:00 | 2022-02-22 14:30 |  |  | Arrived on site signed in gathered tools and equipment rechecked for fault found fuse blown, replaced with new from van stock. Miscellaneous charge. Checker operation and adjusted run time tested all ok cleaned up completed paperwork.
MSA-DCA | WA5301956 | 2 | Techworks Electrical | Basement 2 - Rehearsal room -Lights in Rehearsal Room 1 were tripped multiple times. see notes | Electrical | Lighting, Internal | 1809.79 | Pass | Fail | 0 | 1 | 150.5 | 2022-04-01 15:24 | 2022-04-06 17:00 | 2022-04-05 08:00 | 2022-04-06 17:00 | 2022-04-11 14:30 |  |  | Investigated tripping lights, circuit was on and working fine the whole time we were there, all tests came back good, some lights were just some globes out so we replaced these with stock from STC, 3 lights were ballests, one of which is likely causing the intermittent tripping, we replaced these 3 lights with LED downlights.
MSA-DFES | WA6579077 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Wood Shed - Fan not Working | Electrical | General Electrical | 999.6275 | Pass | Fail | 0 | 1 | 150.5 | 2023-02-15 14:06 | 2023-02-22 17:00 | 2023-02-21 08:45 | 2023-02-22 17:00 | 2023-02-27 15:15 |  | WACCES
MSA-DTWD | WA6184654 | 2 | AWB Co. | Level 5 - Chiller Floor -During hydrant testing water leaks between floor and wall - See notes | Building | Internal Walls | 693.54 | Pass | Fail | 0 | 1 | 150 | 2022-11-15 14:18 | 2022-11-18 17:00 | 2022-11-18 07:00 | 2022-11-18 17:00 | 2022-11-24 13:00 |  |  | Works completed
MSA-DTWD | WA5691748 | 3 | AWB Co. | Main Entry -Repair broken LED light on A Block Exterior | Electrical | Lighting, External | 566.2675 | Pass | Fail | 0 | 1 | 149.75 | 2022-08-03 07:43 | 2022-08-09 17:00 | 2022-08-09 09:15 | 2022-08-09 17:00 | 2022-08-15 15:00 |  | WACCES | Attended site and signed in. Lockated faulty lights and replaced with led. Check and tested all now working. Informed site of Job completion
MSA-DTWD | WA5289545 | 2 | AWB Co. | U block - U block garden bed - Damaged electrical pit | Electrical | General Electrical | 529.72 | Pass | Fail | -1 | 0 | 149.5 | 2022-03-24 10:21 | 2022-03-29 17:00 | 2022-03-25 07:30 | 2022-03-29 17:00 | 2022-03-31 13:00 |  | WACCES | Attended site signed in completed jsa. Located old electrical pit. No cables inside were live. Removed old pit in pieces and replaced with new p5 pit. Leveled off to ground level as there is bushes in the way.*** job completed ***
MSA-DTWD | WA5291029 | 2 | WESTERN IRRIGATION PTY LTD | T U & V Blocks - Grounds - Reticulation break - see notes below | Landscaping & Gardening | Grounds Maintenance | 1315.84 | Pass | Fail | 0 | 1 | 149.5 | 2022-03-25 14:03 | 2022-03-30 17:00 | 2022-03-30 08:00 | 2022-03-30 17:00 | 2022-04-05 13:30 |  |  | Checked system and replaced damaged solenoid wiring and conduit.
MSA-DTWD | WA5106767 | 2 | Securex Security Systems & Services | Main front entry door - The swipe card access to the main front door is faulty see notes | Security | Security Management System | 698.18 | Pass | Fail | 0 | 1 | 149.5 | 2022-02-07 11:08 | 2022-02-10 17:00 | 2022-02-10 10:00 | 2022-02-10 17:00 | 2022-02-16 15:30 |  |  | 10/02/2022Attended site. No one onsiteReturned later in day, confirmed electric strike faulty.16/02/2022Replaced electic strike.Tested ok.
MSA-DFES | WA5589116 | 3 | ADVANCED LOCK & KEY | Locked out of safe – Safe locked in open position -bolt will not move tried new batteries and reset | Security | Locksmith | 1163.5 | Pass | Fail | 0 | 0 | 148.75 | 2022-07-08 10:02 | 2022-07-15 17:00 | 2022-07-12 10:15 | 2022-07-15 17:00 | 2022-07-18 15:00 |  |  | Attend site to remove damaged safe and install new safe
MSA-DTWD | WA5094744 | 2 | Dormakaba Australia Pty Ltd | F1 auto door not working - Automatic door not opening | Building | Automatic Doors | 4235.48 | Pass | Fail | 0 | 1 | 148.5333 | 2022-01-31 13:10 | 2022-02-03 17:00 | 2022-02-01 07:52 | 2022-02-03 17:00 | 2022-02-07 12:24 |  |  | 1/2/22 - On inspection found neither sensor was activating to open door, after testing found that 27 volts was coming from controller but less than 2 volts where coming from ports for sensors. The main control board is faulty, due to age there is no replacement parts for this unit, recommend upgrade to new improved ed100 unit. Please quote to supply and install 1 x Ed100 push arm unit & 1 times Microhead sensor to external to replace existing older one, see attached photos. Note no extension needed for arm spacing.The IP address for this door is 608638.7/2/22 - Attend site to replace and commission ED100 operator with push arm configuration. Door triggered by motion sensor on each side of door. External Eagle one motion sensor replaced. Door programmed and tested with door left active and operational on departure from job.
MSA-DTWD | WA6521448 | 2 | AWB Co. | Lights not turning on | Electrical | Lighting, Internal | 656.4925 | Pass | Fail | 0 | 1 | 148.5 | 2023-01-30 10:55 | 2023-02-02 17:00 | 2023-01-31 10:00 | 2023-02-02 17:00 | 2023-02-06 14:30
MSA-DFES | WA5115815 | 2 | Australian HVAC Services Pty. Ltd. | **Retrospective WO - BMS Offline – attended 10/02/22 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2114.66 | Pass | Fail | -1 | 0 | 148.4689 | 2022-02-10 09:45 | 2022-02-15 17:00 | 2022-02-10 09:59 | 2022-02-15 17:00 | 2022-02-16 14:27 | 1 |  | Attended site and found bms controllers offline. Reset bms controllers. Replaced battery backups as per recommendation.
MSA-DFES | WA6255921 | 2 | Go Doors | Engine room - North end middle roller door does not open with the controller. | Building | Roller Shutters | 667.12 | Pass | Fail | 0 | 0 | 148.25 | 2022-11-23 15:41 | 2022-11-28 17:00 | 2022-11-25 08:00 | 2022-11-28 17:00 | 2022-12-01 12:15 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5478699 | 3 | AWB Co. | Workroom kitchen 9G15 - Water leak above window | Building | General Building | 498.75 | Pass | Fail | 0 | 1 | 148.25 | 2022-05-26 13:12 | 2022-06-02 17:00 | 2022-06-02 07:30 | 2022-06-02 17:00 | 2022-06-08 11:45 |  |  | Investigated, required re-attendance. Found box gutter joint silicone perished overflow silicone perished found small splits on parapet flashing carried out all repairs. This parapet wall would benefit from parapet capping and gutter guard in future. Box gutter showing signs of rust also which may require replacement in near future.
MSA-DTAG | WA6155455 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Comms Room - Air conditioner leaking - See notes below | Air Conditioning | Room Air Conditioners | 1088.79 | Pass | Fail | 0 | 1 | 148 | 2022-11-08 10:41 | 2022-11-09 17:00 | 2022-11-08 12:00 | 2022-11-09 17:00 | 2022-11-14 16:00 |  |  | Gary McAndrew (14/11/2022) - Work Note Picked up parts from suppliers, attended site, accessed roof and isolated ac 16. Replaced pump in ceiling space, rewired to indoor unit & secured probes in place control pump. Re instated power to unit and tested operation ok. Cleared work area.
MSA-DFES | WA6683876 | 2 | Protek 24/7 Building & Maintenance | engine-ground-engine room 4-Broken soap holder in first shower cubicle | Building | Internal Walls | 356.25 | Pass | Fail | 0 | 1 | 148 | 2023-03-03 13:05 | 2023-03-09 17:00 | 2023-03-08 10:30 | 2023-03-09 17:00 | 2023-03-14 14:30 |  | WACCES
MSA-DTAG | WA5473355 | 1 | Sapio Pty Ltd | L10 Glass Door to Marriage room - is beeping | Security | Access Control | 255 | Pass | Fail | 0 | 1 | 148 | 2022-05-24 14:09 | 2022-05-25 17:00 | 2022-05-25 10:00 | 2022-05-25 17:00 | 2022-05-31 14:00 |  | WACCES | Investigated sliding door and found reed switch not sealing after door repaired. Advised client need to open sliding doorand client advised he will get the other contractor back. Inverted input to stop beeping on door. Technician to return andcheck.Arranged with site to attend. Arrived onsite to find another Security Contractor working on door.
MSA-DTWD | WA5495149 | 1 | AWB Co. | 6F45 - No lights or heaters in main workshop | Electrical | General Electrical | 841.16 | Pass | Fail | 0 | 1 | 148 | 2022-06-08 09:49 | 2022-06-09 17:00 | 2022-06-09 07:00 | 2022-06-09 17:00 | 2022-06-15 11:00 |  | WACCES | Attended site and signed in. Completed JSA. Located painting workshop, found faulty switch for heaters. Supply and replace with new switch. Replaced faulty contactor. Tested all okay, signed out. Job complete
MSA-DTWD | WA6159159 | 1 | CDA Air & Solar | Small Cool Room - Faulty Cool Room | Refrigeration | Coolroom | 562.2 | Pass | Fail | 0 | 1 | 147.5 | 2022-11-10 12:21 | 2022-11-11 17:00 | 2022-11-10 12:30 | 2022-11-11 17:00 | 2022-11-16 16:00 |  | WACCES | Install replacement fan motor and test all okcorroded suction filter likely would need replacement
MSA-DTAG | WA5294522 | 0 | Sapio Pty Ltd | Level 10 - control room - cameras not working for visual for SAT building | Security | CCTV Surveillance | 610 | Fail | Fail | 0 | 1 | 147.5 | 2022-03-29 07:17 | 2022-03-29 09:17 | 2022-03-29 12:00 | 2022-03-29 11:17 | 2022-04-04 15:30 |  |  | Reattended site with new license file supplied by Milestone, Uploaded new file to server and restarted all CCTVWorkstations and Server in both DMJC and SAT. Checked all workstations and confirmed all operating correctly
MSA-DCA | WA5792309 | 3 | FCT SURFACE CLEANING | PCC Exterior-ground-Graffiti various locations | Cleaning | Graffiti |  | Pass | Fail | -1 | 0 | 147.5 | 2022-08-23 12:54 | 2022-08-30 17:00 | 2022-08-25 11:30 | 2022-08-30 17:00 | 2022-08-31 15:00 |  |  | Removal of graffiti
MSA-DCA | WA6405396 | 3 | Protek 24/7 Building & Maintenance | External Ground - Planters next to Livingstones - Planter boxes require new wood planks to top. | Landscaping & Gardening | Grounds Maintenance | 336.78 | Pass | Fail | 0 | 0 | 147.5 | 2023-01-09 13:17 | 2023-01-16 17:00 | 2023-01-13 07:00 | 2023-01-16 17:00 | 2023-01-19 10:30
MSA-DTWD | WA6521933 | 1 | Precise Air Group | air-con failure and push button broken | Air Conditioning | Room Air Conditioners | 1147.85 | Pass | Fail | 0 | 1 | 147.0333 | 2023-01-30 14:45 | 2023-01-31 17:00 | 2023-01-31 11:00 | 2023-01-31 17:00 | 2023-02-06 14:02
MSA-DTWD | WA6248709 | 2 | COMMERCIAL PLUMBING AND GAS | Cell C7 - Water leaking from HWU | Plumbing & Drainage | HWS/Units Electric & Gas | 628.44 | Pass | Fail | 0 | 1 | 147 | 2022-11-21 07:31 | 2022-11-23 17:00 | 2022-11-22 14:00 | 2022-11-23 17:00 | 2022-11-28 17:00 |  |  | replaced reliefs, adjusted temps, disassembled and serviced burner assembly
MSA-DTAG | WA6431055 | 1 | Australian HVAC Services Pty. Ltd. | Court 1, Library & Magistrates area - Airconditioning too warm | Air Conditioning | Package | 1276.69 | Pass | Fail | 0 | 0 | 147 | 2023-01-13 11:41 | 2023-01-16 17:00 | 2023-01-13 12:30 | 2023-01-16 17:00 | 2023-01-19 15:30
MSA-DTWD | WA6531891 | 3 | COMMERCIAL PLUMBING AND GAS | Kitchen - Vegetable spray tap on kitchen sink is faulty | Plumbing & Drainage | Water | 574.715 | Pass | Fail | 0 | 1 | 147 | 2023-02-03 15:01 | 2023-02-10 17:00 | 2023-02-09 12:00 | 2023-02-10 17:00 | 2023-02-15 15:00
MSA-DTWD | WA6130222 | 3 | AWB Co. | D117-Exit Door fire release not working ( not locking ) | Building | Fire Door | 416.58 | Pass | Fail | 0 | 1 | 146.75 | 2022-10-28 10:46 | 2022-11-04 17:00 | 2022-11-03 09:00 | 2022-11-04 17:00 | 2022-11-09 11:45 |  |  | Attended site and signed in. Completed jsa. Spoke to fm , went b4 and located door , traced cable to access security panel located next to dB on ground floor, told fm and he notified Schneider, fm happy, completed paperwork,signed out, **job completed**
MSA-DFES | WA5583356 | 2 | Anvil Doors | Engine room - Rear roller door of second pump bay is not opening fully | Building | Automatic Doors | 1435.3 | Pass | Fail | 0 | 1 | 146.6333 | 2022-07-04 11:55 | 2022-07-07 17:00 | 2022-07-06 11:40 | 2022-07-07 17:00 | 2022-07-12 14:18 |  |  | Technician Attended Site and ran diagnostics. Old electrical connections. Recon figured and re--connected. If problem persists, Electrical loom (If not obsolete) or Whole new system replacement.RE-Attended Check door 4 found after repairing logic still had to same issue eventually found limits faulty replacelimits test all ok.
MSA-DTAG | WA5141499 | 1 | Midolo Building Services | Entrance hallway – repair holes left by relocation of cameras | Building | General Building | 673.62 | Pass | Fail | 0 | 1 | 146.5 | 2022-02-16 10:40 | 2022-02-17 17:00 | 2022-02-17 06:00 | 2022-02-17 17:00 | 2022-02-23 08:30 |  | WACCES & WCAPPR | HOLES REPAIRED AND PAINTED
MSA-DCA | WA5679717 | 0 | ADVANCED LOCK & KEY | Locksmith - Gain access | Security | Locksmith | 1216 | Pass | Fail | 0 | 1 | 146.5 | 2022-07-27 06:24 | 2022-07-27 08:24 | 2022-07-27 07:30 | 2022-07-27 10:24 | 2022-08-02 10:00 |  |  | Removed broken key out of oval cylinder after glaziers removed the door.
MSA-DTWD | WA5977903 | 3 | COMMERCIAL PLUMBING AND GAS | Men's Toilet water running | Plumbing & Drainage | Toilets/Cisterns | 681.14 | Pass | Fail | 0 | 1 | 146.5 | 2022-09-28 07:15 | 2022-10-04 17:00 | 2022-10-04 15:30 | 2022-10-04 17:00 | 2022-10-10 18:00 |  |  | repaired water leak/flow
MSA-DTWD | WA6521995 | 2 | Techworks Plumbing | Male toilets in A/block Auto flush not working | Plumbing & Drainage | Toilets/Cisterns | 1548.2 | Pass | Fail | 0 | 1 | 146.5 | 2023-01-30 15:47 | 2023-02-02 17:00 | 2023-01-31 15:00 | 2023-02-02 17:00 | 2023-02-06 17:30
MSA-DTWD | WA6539690 | 2 | AWB Co. | L2-fire stairs-2 x lights out | Electrical | Lighting, Internal | 895.75 | Pass | Fail | -1 | 0 | 146.5 | 2023-02-08 16:11 | 2023-02-13 17:00 | 2023-02-09 09:30 | 2023-02-13 17:00 | 2023-02-15 12:00 |  | WACCES
MSA-DTWD | WA5142141 | 1 | WESTERN IRRIGATION PTY LTD | B Block northern side - Reticulation mainline - Mainline damaged water leaking out | Landscaping & Gardening | Grounds Maintenance | 2382.99 | Pass | Fail | 0 | 1 | 146.5 | 2022-02-16 13:45 | 2022-02-17 17:00 | 2022-02-17 07:00 | 2022-02-17 17:00 | 2022-02-23 09:30 |  |  | Located two broken 40mm laterals under a tree, redirect the 40mm PVC pipes around the tree.Return to cap off a broken sprinkler in the bush land then again to replace a broken tee 2 meters away from the original leak.
MSA-DTWD | WA5195749 | 2 | Falcetta Plumbing and Gas | Ladies toilet - Cistern leaking | Plumbing & Drainage | Toilets/Cisterns | 965.25 | Pass | Fail | 0 | 1 | 146.25 | 2022-02-28 15:15 | 2022-03-03 17:00 | 2022-03-02 14:45 | 2022-03-03 17:00 | 2022-03-08 17:00 |  | WACCES | replaced cistern w/invisi and button to suit existing
MSA-DFES | WA5286324 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Station officers bathroom - see details below | Electrical | Lighting, Internal | 540.44 | Pass | Fail | 0 | 1 | 146.25 | 2022-03-21 14:46 | 2022-03-24 17:00 | 2022-03-23 10:45 | 2022-03-24 17:00 | 2022-03-29 13:00 |  | WACCES | Located faulty lights. I found one light not working and one light dull. Left site to get new globes. Installed new globes. One light the lamp holder is damaged and in the other light only one globe will work. Both lights are damaged inside and will need replacement. The hole size is 230mm. Staff needed to leave the station so we will need to order parts and return to install.
MSA-DTAG | WA5472176 | 1 | Midolo Building Services | 1 – Upstairs -DCP Office - Water marks on two more ceiling tiles – Two new roof leaks | Building | General Building | 459.38 | Fail | Fail | 0 | 1 | 146.25 | 2022-05-23 15:07 | 2022-05-24 17:00 | 2022-05-25 12:45 | 2022-05-24 17:00 | 2022-05-31 15:00 |  | WACCES | damaged ceiling tiles removed - replaced with new
MSA-DTWD | WA6298392 | 2 | Protek 24/7 Building & Maintenance | Block E - Fluid Power Compound - Break-in to North Cyclone Fence | Building | Steel Fencing & Gates | 925.56 | Pass | Fail | -1 | 0 | 146.25 | 2022-12-01 09:41 | 2022-12-06 17:00 | 2022-12-02 09:15 | 2022-12-06 17:00 | 2022-12-08 11:30 |  | WACCES | Repaired damaged to fence
MSA-DTWD | WA5226869 | 1 | Dormakaba Australia Pty Ltd | E-Block - S/W end of building - Auto door not working – wont shut or open properly | Building | Automatic Doors | 3505.2 | Fail | Fail | 1 | 2 | 146.15 | 2022-03-14 14:10 | 2022-03-15 17:00 | 2022-03-22 09:23 | 2022-03-15 17:00 | 2022-03-28 11:32 |  |  | 22/3/22 - Inspected door and found that the door had failed again, checked the door controller history and there is a multiple of errors and the gearbox is also badly worn. Spoke with site and advised we carry out an upgrade as this door is 18 years old and beyond economical repair. Please quote for 1x es200 locking upgrade kit, reuse existing sensors/ switches.28/3/22 - Removed existing faulty door equipment and replaced with new es200 upgrade kit, reused existing sensors and switches, setup and tested operation upon completion and left in good working order.
MSA-DCA | WA5093671 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS air condition alarm for the chilled water plant temp alarm | Air Conditioning | Room Air Conditioners | 970.675 | Fail | Fail | 0 | 1 | 146 | 2022-01-29 14:58 | 2022-01-29 16:58 | 2022-02-01 08:00 | 2022-01-29 18:58 | 2022-02-07 10:00 |  |  | Cooling Tower 1 Variable speed drive generates an earth fault intermittently even when not running. Quote is being prepared to replace the vsd.
MSA-DTAG | WA5995070 | 3 | Midolo Building Services | Registry - Glass Barrier Door is not remaining in full open state - See notes below | Building | Doors | 912.16 | Pass | Pass | -1 | 0 | 146 | 2022-10-06 10:25 | 2022-10-13 17:00 | 2022-10-07 08:00 | 2022-10-13 17:00 | 2022-10-13 10:00 |  | WACCES | adjustments made to door & closer. New cabin hook installed
MSA-DTWD | WA5215250 | 3 | Falcetta Plumbing and Gas | B2 - Level 3 - Male toilet - Tap leaking | Plumbing & Drainage | Materials | 865.91 | Pass | Pass | -1 | 0 | 146 | 2022-03-10 10:42 | 2022-03-17 17:00 | 2022-03-10 16:00 | 2022-03-17 17:00 | 2022-03-16 18:00 |  | WACCES | Repaired tap and urinals
MSA-DTWD | WA5215265 | 3 | Falcetta Plumbing and Gas | B2 - 143 cleaners - Backflow valve hammering | Plumbing & Drainage | Drainage | 581.1 | Pass | Pass | -1 | 0 | 146 | 2022-03-10 10:50 | 2022-03-17 17:00 | 2022-03-10 15:00 | 2022-03-17 17:00 | 2022-03-16 17:00 |  | WACCES | replaced rpzd with dcv
MSA-DTWD | WA5584783 | 2 | Protek 24/7 Building & Maintenance | Reception Area - roof leaking | Roofing | Metal Roofing | 821.68 | Pass | Fail | 0 | 1 | 146 | 2022-07-05 10:26 | 2022-07-08 17:00 | 2022-07-07 10:00 | 2022-07-08 17:00 | 2022-07-13 12:00 |  |  | Patch & Paint
MSA-DTWD | WA6519951 | 2 | Australian Airconditioning Services Pty Ltd | LG AC not cooling | Air Conditioning | Room Air Conditioners | 2947.06 | Pass | Fail | 0 | 1 | 146 | 2023-01-27 08:55 | 2023-02-01 17:00 | 2023-02-01 10:00 | 2023-02-01 17:00 | 2023-02-07 12:00
MSA-DTWD | WA5478159 | 1 | ECO PLUMBING AND GAS PTY LTD | E40 Male Toilets - Urinals Blocked - Taking a long time to drain | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Fail | 0 | 1 | 145.8667 | 2022-05-26 09:46 | 2022-05-27 17:00 | 2022-05-27 15:00 | 2022-05-27 17:00 | 2022-06-02 16:52 |  |  | cleared blockage
MSA-DTWD | WA6183873 | 2 | Protek 24/7 Building & Maintenance | Block T - Level 1 - Male Toilets - Ceiling water damaged | Building | Ceiling | 1227.805 | Pass | Fail | 0 | 1 | 145.5 | 2022-11-15 08:57 | 2022-11-18 17:00 | 2022-11-17 11:30 | 2022-11-18 17:00 | 2022-11-23 13:00 |  |  | Scraped back flaking paint and gyprock , patched holes with a repair kit , applied one coat of base coatScrape back base, base again. Top coat. Sand back previously patched ceiling, undercoat, then paint in ceiling white
MSA-DTWD | WA6407612 | 3 | Protek 24/7 Building & Maintenance | Courtyard area - Gutter and roof clean - Remove leaf and debris material from gutters and sumps | Plumbing & Drainage | Drainage | 670.2 | Pass | Pass | -1 | 0 | 145.5 | 2023-01-10 10:12 | 2023-01-17 17:00 | 2023-01-10 13:00 | 2023-01-17 17:00 | 2023-01-16 14:30
MSA-DFES | WA5304899 | 2 | Australian HVAC Services Pty. Ltd. | Front admin building - Female toilets - fan is not working | Air Conditioning | Room Air Conditioners | 605.82 | Pass | Fail | 0 | 1 | 145 | 2022-04-05 10:38 | 2022-04-08 17:00 | 2022-04-06 11:00 | 2022-04-08 17:00 | 2022-04-12 12:00 |  |  | Obtained parts from supplier, arrived on-site, spoke with on-site representative and informed client of works to be carried out. Signed in & obtained keys, proceeded to.admin bathroom.work.area, isolated fan electrically and tested for power, began removing power lead from old exhaust fan and dismantling exhaust fan assembly, removed old exhaust fan & proceeded to install new exhaust into window but found original hole to have been cut to short, inspected old exhaust fan assembly and upon visual inspection found that old assembly had not used bolts but had screwed the two seating plates together using self drilling impact screws, installed new exhaust fan using same method & sealed all edges on window using clear silicone to prevent any water being able to seep through to fan motor, this may be what caused previous fan to have electrically seized at motor. Re-energised exhaust fan GPO outlet and found there to still be no power, obtained keys to distribution board 7 & found main fuse h
MSA-DTWD | WA6527065 | 3 | AWB Co. | Heavy Picture bolted to the brick wall is hanging from one side | Building | Internal Walls | 314.73 | Pass | Fail | -1 | 0 | 145 | 2023-02-01 13:18 | 2023-02-08 17:00 | 2023-02-03 09:30 | 2023-02-08 17:00 | 2023-02-09 10:30
MSA-DTWD | WA5215512 | 2 | Lane's Plumbing | BLD 822 - Flat C- Bathroom- Toilets faulty cisterns | Plumbing & Drainage | Water |  | Pass | Fail | -1 | 0 | 145 | 2022-03-10 12:59 | 2022-03-15 17:00 | 2022-03-11 10:00 | 2022-03-15 17:00 | 2022-03-17 11:00 |  |  | job completed - REPLACE TWO FAULTY TOILET CISTERNS TO FLAT C BLD 822
MSA-DFES | WA5323464 | 1 | Dom's Total Grounds Maintenance | Applied Training - Near new store area - see details below | Landscaping & Gardening | Grounds Maintenance | 714 | Pass | Fail | 0 | 1 | 144.8333 | 2022-04-13 08:25 | 2022-04-14 17:00 | 2022-04-13 09:40 | 2022-04-14 17:00 | 2022-04-19 10:30 |  |  | 3 x Call Outs & Parts & Labour
MSA-DCA | WA6020555 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Earth Sciences Fume Hood - Fan not working - see notes | Electrical | General Electrical | 484.23 | Pass | Fail | 0 | 1 | 144.8333 | 2022-10-13 14:08 | 2022-10-14 17:00 | 2022-10-13 14:10 | 2022-10-14 17:00 | 2022-10-19 15:00 |  |  | Subcontractor to attend site and access fume cupboard fan motor and repair.
MSA-DCA | WA5398956 | 1 | Protek 24/7 Building & Maintenance | Café door closer needs to be tightened - Photo's to follow in email | Building | Doors | 1296 | Pass | Fail | 0 | 1 | 144.75 | 2022-05-09 13:33 | 2022-05-10 17:00 | 2022-05-10 11:15 | 2022-05-10 17:00 | 2022-05-16 12:00 |  | WACCES | Replace Damaged door
MSA-DTAG | WA5200886 | 1 | Midolo Building Services | Courtroom 1 - Leak in roof right above the step to the witness box - see notes below | Roofing | Metal Roofing | 358.31 | Pass | Fail | 0 | 1 | 144.5 | 2022-03-02 09:57 | 2022-03-03 17:00 | 2022-03-02 14:00 | 2022-03-03 17:00 | 2022-03-08 14:30 |  | WACCES | ROOF LEAK REPAIRED
MSA-DTWD | WA5323842 | 1 | Protek 24/7 Building & Maintenance | 10G68 - Lower weather strip on emergency exit door has fallen off | Building | General Building | 384.875 | Pass | Fail | 0 | 1 | 144.5 | 2022-04-13 11:30 | 2022-04-14 17:00 | 2022-04-13 12:30 | 2022-04-14 17:00 | 2022-04-19 13:00 |  | WACCES | Replace With strip on emergency exit
MSA-DTWD | WA5392079 | 2 | AWB Co. | T Block Executive car park - Executive Car park -One of the Hinged LED lights requires replacing | Electrical | General Electrical | 750.1275 | Pass | Fail | 0 | 1 | 144.5 | 2022-05-03 07:32 | 2022-05-05 17:00 | 2022-05-05 15:00 | 2022-05-05 17:00 | 2022-05-11 15:30 |  |  | Attended site signed in jsa completed. light pole head was faulty and just needed to be replaced. Had replacement on board and just installed it. Works fine now and operational in photos. *** job completed ***
MSA-DTAG | WA5972882 | 2 | Midolo Building Services | Ground floor Court room 6 - 2 x lecterns are not secured on the bench - see notes below | Furniture | Office Furniture | 96.84 | Pass | Fail | 0 | 1 | 144.5 | 2022-09-21 09:10 | 2022-09-27 17:00 | 2022-09-27 08:30 | 2022-09-27 17:00 | 2022-10-03 09:00 |  | WACCES | WORK ORDER CANCELLED BY SITE - REFER EMAIL ATTACHED KPI EVIDENCE 5-10-2022
MSA-DTWD | WA6290659 | 2 | WESTERN IRRIGATION PTY LTD | Glasshouse - Water Recycling Plant - water tanks not filling - see notes | Plumbing & Drainage | Water | 371 | Pass | Fail | 0 | 1 | 144.5 | 2022-11-28 10:14 | 2022-12-01 17:00 | 2022-11-29 07:30 | 2022-12-01 17:00 | 2022-12-05 08:00 |  |  | Reset probes and tested for correct operation. Returned to site and confirmed correct operation.
MSA-DTWD | WA5478739 | 3 | AWB Co. | Block 3 - Ground - Passage way outside 3D Heavy Plant work shop | Building | General Building | 416.25 | Pass | Fail | 0 | 1 | 144.25 | 2022-05-26 13:23 | 2022-06-02 17:00 | 2022-06-02 09:30 | 2022-06-02 17:00 | 2022-06-08 09:45 |  | WACCES | Attended, required return due to weather. Found 2 banks of skylights that were overlapped without any sealant. Stripped sheets and applied sealant re-fixed sheets.
MSA-DTWD | WA5585394 | 3 | Protek 24/7 Building & Maintenance | Down pipe detached from gutter next to roller door. | Roofing | Guttering | 307.58 | Pass | Fail | -1 | 0 | 144.25 | 2022-07-05 16:07 | 2022-07-12 17:00 | 2022-07-07 14:45 | 2022-07-12 17:00 | 2022-07-13 15:00 |  |  | Reattach downpipe
MSA-DCA | WA5306654 | 2 | EQUANS Mechanical Services (WA) Pty Limited | RO plant is in alarm with low pressure light on. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 831.51 | Pass | Fail | 0 | 0 | 144.15 | 2022-04-06 16:07 | 2022-04-11 17:00 | 2022-04-08 11:00 | 2022-04-11 17:00 | 2022-04-14 11:09 |  |  | Returned and rechecked equipment operation all OK. No water leaks present. Pump running as requered. Quote will be submitted for replacement spare change over pump. Confirmed left I auto operation. No further action required
MSA-DTWD | WA6049040 | 2 | M Construction (WA) | Stores area - Hole in wall | Building | Internal Walls | 202.26 | Pass | Fail | 0 | 1 | 144.0833 | 2022-10-17 13:59 | 2022-10-20 17:00 | 2022-10-20 13:29 | 2022-10-20 17:00 | 2022-10-26 13:34
MSA-DTAG | WA5386050 | 2 | Sapio Pty Ltd | Level 31 - Paacom taking long time to search users / often screen just loading | Security | CCTV Surveillance | 4199.96 | Fail | Fail | 0 | 1 | 144 | 2022-04-29 15:12 | 2022-05-04 17:00 | 2022-05-05 13:00 | 2022-05-04 17:00 | 2022-05-11 13:00 |  |  | Replaced workstation with Custom micro PC with PFM specifications. Installed and programmed Milestone and Pacom.Confirmed correct operation.
MSA-DTAG | WA5459923 | 2 | Midolo Building Services | 1 – Upstairs - DCP Office - Roof Leak | Roofing | Tiled Roofing | 246.89 | Fail | Fail | 0 | 1 | 144 | 2022-05-18 09:57 | 2022-05-23 17:00 | 2022-05-25 13:30 | 2022-05-23 17:00 | 2022-05-31 13:30 |  | WACCES | roof resealed - ceiling tiles replaced
MSA-DTWD | WA5981397 | 2 | Jako Industries Pty Ltd | Hopper 5-Clear the blockage in unit 5 dust extraction hopper. | Electrical | General Electrical |  | Pass | Fail | 0 | 1 | 144 | 2022-09-29 15:51 | 2022-10-04 17:00 | 2022-10-04 07:30 | 2022-10-04 17:00 | 2022-10-10 07:30 |  |  | Removed filters and found supply air duct partially blocked, unblocked all now happy with suction on inlets.
MSA-DCA | WA6149291 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Fire panel-Issues with fire panel-see notes | Fire Protection Services | Fire Protection - Monitor System | 994.09 | Pass | Fail | 0 | 1 | 144 | 2022-11-04 13:54 | 2022-11-11 17:00 | 2022-11-09 11:00 | 2022-11-11 17:00 | 2022-11-15 11:00 |  |  | Engaged Alerton to investigate fire relay control in MSSB-1ATTENDED SITE TO INVESTIGATE FSR3 INTERMITTENTLY ALARMING IN MSSB, FSR3 WAS BEING ACTIVATED BY LOOP 4 S2 OUTPUT 1. TECHNICIAN HAS NOW MOVED TO LOOP 4 S3 OUTPUT 2. RE-PROGRAMMED FIP AND TESTED OUTPUT ACTIVATION, ALL OK UPONDEPARTURE. PLEASE NOTE WHILE TESTING, FOUND GFA OUTPUT MODULE ACTIVATED BUT NO SIGALS HAVE BEEN RECEIVED IN MSSB. TECHNICIAN HAD NO ACCESS TO THE FIRE MATRIX. POSSIBLY BYPASSED FOR SHUTDOWNS TO APPLY IN EFFECTED ZONES ONLY. MADE NO CHANGES AND LEFT AS FOUND.
MSA-DTWD | WA6294021 | 2 | Protek 24/7 Building & Maintenance | D2 - Gyprock wall damaged needs repair | Building | Internal Walls | 658.655 | Pass | Fail | 0 | 0 | 144 | 2022-11-30 11:50 | 2022-12-05 17:00 | 2022-12-02 13:30 | 2022-12-05 17:00 | 2022-12-08 13:30 |  | WACCES | Cut out damage, install stud, install new gyprock and baseSand and paint wall
MSA-DTWD | WA6560370 | 2 | COMMERCIAL PLUMBING AND GAS | L1-female toilet first cubicle water keeps running after flushing-see notes | Plumbing & Drainage | Toilets/Cisterns | 686.9825 | Pass | Fail | 0 | 1 | 143.75 | 2023-02-13 09:41 | 2023-02-16 17:00 | 2023-02-15 15:15 | 2023-02-16 17:00 | 2023-02-21 15:00
MSA-DFES | WA5699690 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - all female toilets are drains are blocked - see notes below | Plumbing & Drainage | Toilets/Cisterns | 1470.7 | Pass | Fail | 0 | 1 | 143.7333 | 2022-08-10 11:24 | 2022-08-10 13:24 | 2022-08-10 12:31 | 2022-08-10 15:24 | 2022-08-16 12:15 |  |  | Arrived on site and singed in went to level 2 toilets and removed the end toilet in female toilets and had to use camera down drain to see if we could work out why the drain was backing up. Once we put the camera down we could see that the pipe was very dirty which indicated there's a lot of blockages, and the water was not pushing the paper through. Once we got the paper through we did another paper test reuse the camera and work out that the drain has a couple of flat spots in the system, and this is going to be a on going issue. The only way to fix the problem is see if you can get the pipes clean or have to repair the hole drain on the second floor. put back toilet and cleaned up
MSA-DTWD | WA5680396 | 1 | SCAVENGER SUPPLIES PTY LTD | North-B8 staff office-Fault description Fault on manual call point at the FIP | Fire Protection Services | Fire Protection - Monitor System | 253.09 | Pass | Fail | 0 | 1 | 143.5667 | 2022-07-27 11:57 | 2022-07-28 17:00 | 2022-07-28 11:56 | 2022-07-28 17:00 | 2022-08-03 11:30 |  | WACCES | INITIAL ATTENDANCE - 27/7/22 - Manual Call Point front panel is causing FIP to go into Alarm. Unscrewed Core Point and removed break glass to determine any visual defects.DFES informed and Zone isolated.03/08/2022-New Core Point to be ordered and will return to complete job once part has arrived. COMPLETED 03/08/2022
MSA-DCA | WA5566547 | 1 | Techworks Electrical | Ground – external - Urban Orchard -New light fitting cover has been removed (vandals). | Electrical | General Electrical | 810.04 | Pass | Fail | 0 | 1 | 143.5 | 2022-06-23 09:25 | 2022-06-24 17:00 | 2022-06-24 07:30 | 2022-06-24 17:00 | 2022-06-30 07:00 |  | WACCES | Supplied and installed 1x new LED PT4 fitting and bolted to pole to eliminate head frame being "shaken" off by patrons
MSA-DTWD | WA6407494 | 3 | Protek 24/7 Building & Maintenance | Courtyard - Gutter and roof clean | Roofing | Guttering | 474.55 | Pass | Pass | -1 | 0 | 143.5 | 2023-01-10 09:14 | 2023-01-17 17:00 | 2023-01-10 12:30 | 2023-01-17 17:00 | 2023-01-16 12:00
MSA-DTWD | WA6537843 | 2 | AWB Co. | Sensor lighting cuts off every 15 minutes , needs to be extended to 60 minutes | Electrical | Lighting, Internal | 421.34 | Pass | Fail | 0 | 1 | 143.5 | 2023-02-07 12:08 | 2023-02-10 17:00 | 2023-02-08 12:00 | 2023-02-10 17:00 | 2023-02-14 11:30
MSA-DFES | WA4990961 | 3 | AWB Co. | Ground - Engine Room - damaged gyprock - see notes below | Building | External Walls | 341.35 | Pass | Fail | -1 | 0 | 143.25 | 2022-01-04 13:45 | 2022-01-11 17:00 | 2022-01-06 08:30 | 2022-01-11 17:00 | 2022-01-12 07:45 |  |  | Inspected damaged gyprock wall then filled it with rapid set plaster. Once dried out enough applied topcoat plaster. Sanded and painted wall job complete
MSA-DTWD | WA6601273 | 2 | AWB Co. | Museum St entrance - All Museum St entrance lights not working - (see notes) | Electrical | Lighting, External | 596.0425 | Pass | Fail | 0 | 1 | 143.25 | 2023-02-17 10:12 | 2023-02-22 17:00 | 2023-02-21 14:00 | 2023-02-22 17:00 | 2023-02-27 13:15
MSA-DFES | WA5888360 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Media & Corporate Communications - Multiple lights in the NE corner, facing Stockton are faulty | Electrical | Lighting, Internal | 468.57 | Pass | Fail | 0 | 1 | 143 | 2022-09-16 16:31 | 2022-09-23 17:00 | 2022-09-23 14:45 | 2022-09-23 17:00 | 2022-09-29 13:45 |  | WACCES | Collected gear from wholesaler at 13:00 and continued to site arrived at 13:15. Went to level 2 and spoke with staff, lights are not wanted on due to headaches with staff. No action needed. Left site at 13:45
MSA-DTWD | WA6509386 | 2 | AWB Co. | Office B207 - Light out | Electrical | Lighting, Internal | 378.4275 | Pass | Fail | 0 | 1 | 143 | 2023-01-20 10:16 | 2023-01-25 17:00 | 2023-01-24 15:00 | 2023-01-25 17:00 | 2023-01-30 14:00 |  | WACCES
MSA-DTWD | WA5324303 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block - Outside kitchen door - broken down pipe outside restaurant kitchen door | Plumbing & Drainage | Drainage | 982.415 | Pass | Pass | -1 | 0 | 142.75 | 2022-04-13 13:40 | 2022-04-20 17:00 | 2022-04-13 14:00 | 2022-04-20 17:00 | 2022-04-19 12:45 |  |  | Completed
MSA-DCA | WA5603356 | 1 | ADVANCED LOCK & KEY | Alexander Library Building -Door to electrical riser DB-G-B (opposite reception)- door cant lock | Security | Locksmith | 305.62 | Pass | Fail | 0 | 1 | 142.7172 | 2022-07-12 10:08 | 2022-07-13 17:00 | 2022-07-12 14:10 | 2022-07-13 17:00 | 2022-07-18 12:53
MSA-DCA | WA5188185 | 2 | Protek 24/7 Building & Maintenance | Alexander Library Building - Door Handle Tongue faulty - Disabled cubicle | Building | Doors | 741.04 | Pass | Fail | 0 | 1 | 142.5 | 2022-02-23 07:04 | 2022-02-25 17:00 | 2022-02-25 15:00 | 2022-02-25 17:00 | 2022-03-03 13:30 |  | WACCES | Replace door handle
MSA-DTAG | WA5472666 | 1 | Midolo Building Services | Level 1 - Upstairs - DPP Office & Youth Justice Office- Ceiling tile on floor - see notes below | Roofing | Tiled Roofing | 276.81 | Pass | Fail | 0 | 1 | 142.5 | 2022-05-24 09:31 | 2022-05-25 17:00 | 2022-05-25 14:15 | 2022-05-25 17:00 | 2022-05-31 12:45 |  | WACCES | roof leak repaired & ceiling tile replaced
MSA-DTAG | WA5494337 | 2 | Sapio Pty Ltd | Ground Level - Court 2 -Door not automatically locking when closing - See notes below | Security | Access Control | 257.44 | Pass | Fail | 0 | 1 | 142.5 | 2022-06-07 14:09 | 2022-06-10 17:00 | 2022-06-09 10:00 | 2022-06-10 17:00 | 2022-06-15 08:30 |  | WACCES | Replaced Egress button and tested.
MSA-DTWD | WA5478939 | 3 | AWB Co. | Block 8 - Ground - Internal passage way outside AMP office 8G64 - water leak in passage | Building | General Building | 354.38 | Pass | Fail | 0 | 1 | 142.25 | 2022-05-26 15:27 | 2022-06-02 17:00 | 2022-06-02 10:00 | 2022-06-02 17:00 | 2022-06-08 08:15 |  | WACCES | Attended, required return due to weather.Traced leak to sump box. Found perished silicone around outlet. Worth noting that pipe for box gutter runs internally and is not visible without removing cover, advise to monitor in next rain
MSA-DTAG | WA6144429 | 2 | Sapio Pty Ltd | Director Generals Suite – L31-13-sliding door showing event active / inactive event-see notes | Security | Access Control | 204.44 | Pass | Fail | 0 | 1 | 142.25 | 2022-11-02 06:53 | 2022-11-04 17:00 | 2022-11-04 16:45 | 2022-11-04 17:00 | 2022-11-10 15:00 |  | WACCES | Rectified fault and adjusted programming
MSA-DCA | WA5761708 | 3 | Techworks Electrical | Track Lights in foyers-no longer functioning - see notes | Electrical | Lighting, Internal | 878.26 | Pass | Pass | -1 | 0 | 142 | 2022-08-18 11:20 | 2022-08-25 17:00 | 2022-08-19 11:00 | 2022-08-25 17:00 | 2022-08-25 09:00 |  | WACCES | Tasks completed 1. found the box that had the lights left in, there was 6 in there, 3x plastic that help the fitting up was spanned and un fixable. 2. fixed the 3x lights that didn’t have snapped plastic by bending the contacts in the fitting back into place. 3. simone found another one as I was leaving so fixed that as well meaning they have 4x working lights now in total. no parts used
MSA-DTAG | WA5394243 | 2 | Midolo Building Services | Level 5 - Family Violence - Top drawer in staff kitchen is stiff to open | Building | General Building | 457.42 | Pass | Fail | -1 | 0 | 142 | 2022-05-04 14:10 | 2022-05-09 17:00 | 2022-05-05 13:45 | 2022-05-09 17:00 | 2022-05-11 11:45 |  | WACCES | new draw runners installed. Draw repaired
MSA-DTWD | WA5792500 | 3 | ADVANCED LOCK & KEY | lB314.1 - Lock and handle faulty | Security | Locksmith | 1590.84 | Pass | Fail | -1 | 0 | 141.4167 | 2022-08-23 14:58 | 2022-08-30 17:00 | 2022-08-25 14:05 | 2022-08-30 17:00 | 2022-08-31 11:30 |  |  | 25/8/22 attend site, requires electric mortice lock. 31/8/22 replaced faulty mortice lock with new on B314.1
MSA-DTAG | WA6519240 | 2 | Australian HVAC Services Pty. Ltd. | Level 1- 1987 Wing - Aircon making loud noises -see notes | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Pass | -1 | 0 | 141.25 | 2023-01-25 14:13 | 2023-01-31 17:00 | 2023-01-25 14:15 | 2023-01-31 17:00 | 2023-01-31 11:30
MSA-DTWD | WA5487380 | 2 | AWB Co. | Ground Level - Whole Ground - Ground lights not working | Electrical | Lighting, External | 999.5 | Pass | Fail | 0 | 1 | 141 | 2022-06-01 14:38 | 2022-06-07 17:00 | 2022-06-07 13:30 | 2022-06-07 17:00 | 2022-06-13 10:30 |  | WCAPPR | Attended site signed in jsa completed.Hired ladder and roofers harness kit from kennards to do job safely. Had dan spot me to get on roof and locate pe cell for block 1. Found it after somentime and tested it. Was faulty had one on hand and replaced with new. Tested and works fine now lights come on. *** job completed ***
MSA-DCA | WA5681850 | 0 | Dormakaba Australia Pty Ltd | Studio dock 1 gate on 6 Roe St - is not closing. | Building | Doors | 712.5 | Pass | Fail | 0 | 1 | 141 | 2022-07-28 19:03 | 2022-07-28 21:03 | 2022-07-28 20:00 | 2022-07-28 23:03 | 2022-08-03 17:00 |  |  | 28/7/22 - Attended site and found gates not closing, on inspection found internal safety beams to be faulting, replaced batteries but still faulting, will need revisit to install new set of cents safety beams see attached photo,. Joined wires together to bypass beams and gate is now closed and secure for the night.3/8/22 - Replaced faulty internal safety beams tested gate. All good.
MSA-DTWD | WA6015110 | 0 | Securex Security Systems & Services | Central Foyer - zone alarm is activating on zone 263 | Security | Monitoring | 250 | Pass | Fail | 0 | 1 | 141 | 2022-10-12 15:11 | 2022-10-12 17:11 | 2022-10-12 16:00 | 2022-10-12 19:11 | 2022-10-18 13:00 |  |  | (12/10/2022, 1600-1645) - Work NoteDuress button is one of 4 on the centre desk.None were in alarm on arrival, but, the system had reported an alarm which through testing proved to still be in alarm. Either one of the duress buttons is faulty or there is a cable fault on the system. There is also an un- resolved dgp 17 tamper on the site. (18/10/2022, 1230-1300) - Work NoteReset all duress buttons, found 2 on other desk. Clear zone all good.Seems like more than just centre desk on duress loop.
MSA-DCA | WA6390584 | 2 | FCT SURFACE CLEANING | Ground - PCC Exterior - Graffiti - Various Locations - See Notes Below | Cleaning | Graffiti |  | Pass | Pass | -1 | 0 | 141 | 2022-12-22 10:47 | 2022-12-29 17:00 | 2022-12-22 13:30 | 2022-12-29 17:00 | 2022-12-28 10:30 |  |  | Removed graffiti from various locations: STC exterior wall (James St side) SLWA HV control room SLWA rear staff car park SLWA bench By Fringe Box Office Rear of PICA car park.
MSA-DCA | WA6537403 | 2 | Protek 24/7 Building & Maintenance | Bay above cleaners room (off Francis St)-Broken paving in two spots. | Paving & Roadworks | Paving | 255.07 | Pass | Fail | 0 | 0 | 141 | 2023-02-07 09:14 | 2023-02-10 17:00 | 2023-02-07 11:30 | 2023-02-10 17:00 | 2023-02-13 08:30 |  | WACCES
MSA-DCA | WA6573284 | 2 | ACTION GLASS & ALUMINIUM | Kitchen - Cracked window - Retrospective WO for Action Glass - already measured for new glass | Glazing | Window Glass | 279.27 | Pass | Fail | 0 | 1 | 140.8333 | 2023-02-14 12:19 | 2023-02-17 17:00 | 2023-02-17 14:25 | 2023-02-17 17:00 | 2023-02-23 11:15 | 1
MSA-DTWD | WA6156994 | 3 | Schneider Electric Australia Pty Ltd | Room D117 - Door is not locking Electrician traced cable back to access control panel | Building | Doors |  | Pass | Pass | -1 | 0 | 140.75 | 2022-11-09 12:04 | 2022-11-16 17:00 | 2022-11-09 12:15 | 2022-11-16 17:00 | 2022-11-15 09:00 |  |  | Completed
MSA-DFES | WA6540811 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room-Fluro light in engine bay is not working | Electrical | Lighting, Internal | 704.855 | Pass | Fail | 0 | 1 | 140.75 | 2023-02-09 14:18 | 2023-02-16 17:00 | 2023-02-14 13:30 | 2023-02-16 17:00 | 2023-02-20 10:15
MSA-DTWD | WA6256944 | 3 | ACTION GLASS & ALUMINIUM | Cafe North - Seal for glass (hinged) door has perished/cracked and needs replacing | Glazing | Door Glass | 191.745 | Pass | Pass | -1 | 0 | 140.6 | 2022-11-24 10:22 | 2022-12-01 17:00 | 2022-11-24 13:39 | 2022-12-01 17:00 | 2022-11-30 10:15 |  |  | ATTENDED SITE TO ASSESSRETURNED LATER DATE SUPPLIED & FIT NEW BUG STRIP TO DOOR
MSA-MRWA | WA5018664 | 1 | Dormakaba Australia Pty Ltd | Second Floor - Entrance - auto slide door not closing | Building | Automatic Doors | 1148.96 | Pass | Fail | 0 | 0 | 140.55 | 2022-01-14 14:17 | 2022-01-17 17:00 | 2022-01-14 15:48 | 2022-01-17 17:00 | 2022-01-20 12:21 |  |  | 14/1/22 - Found that the internal sensor has failed, quotation required to replace with an ixio sensor and ceiling mount bracket.20/1/22 - Installed new sensor as per quotation, tested all ok.
MSA-DTWD | WA5324342 | 2 | Protek 24/7 Building & Maintenance | Block 10 - 10G66 - Finishing tiles above laundry trough have fallen off | Flooring | Tiling | 366 | Pass | Pass | -1 | 0 | 140.5 | 2022-04-13 14:12 | 2022-04-20 17:00 | 2022-04-14 13:30 | 2022-04-20 17:00 | 2022-04-20 10:00 |  |  | Laundry trough Tiles replaced
MSA-DTWD | WA6208213 | 1 | AWB Co. | ground-3B 8 classroom-Half the lights tripping off after a few seconds. | Electrical | Lighting, Internal | 659.485 | Pass | Fail | 0 | 1 | 140.5 | 2022-11-17 14:31 | 2022-11-18 17:00 | 2022-11-18 12:30 | 2022-11-18 17:00 | 2022-11-24 09:00 |  | WACCES | Attended site signed in jsa completed. Replaced panel lights as per request. Tested operational.Job completed
MSA-DCA | WA6526718 | 1 | Protek 24/7 Building & Maintenance | Public Concourse (box office) - Door mat into the box office foyer are lifting causing trip hazard | Flooring | Carpet | 354.36 | Pass | Fail | 0 | 1 | 140.5 | 2023-02-01 10:11 | 2023-02-02 17:00 | 2023-02-01 14:00 | 2023-02-02 17:00 | 2023-02-07 10:30
MSA-DFES | WA5231310 | 2 | ADVANCED LOCK & KEY | Dining Room Door to outside - see details below | Security | Locksmith | 325 | Pass | Fail | 0 | 1 | 140.4167 | 2022-03-15 10:23 | 2022-03-18 17:00 | 2022-03-18 14:15 | 2022-03-18 17:00 | 2022-03-24 10:40 |  |  | Attend site to replace digital on entry door to firefighters car park entryBL2301 used and 2x flat steel keys cut
MSA-DTWD | WA5562690 | 2 | AWB Co. | K Block - Shed - roof leak | Building | General Building | 1162.38 | Pass | Fail | 0 | 1 | 140 | 2022-06-20 09:12 | 2022-06-23 17:00 | 2022-06-23 14:00 | 2022-06-23 17:00 | 2022-06-29 10:00 |  |  | Measured up to block off openings of shedWork Performed:Set up exclusion zoneRemoved screws from roof sheetsInstalled timberReinstalled screws into sheetsCleaned and packed up
MSA-DFES | WA6450869 | 1 | Protek 24/7 Building & Maintenance | Electric fence and other fences damaged due to fallen tree | Building | Steel Fencing & Gates | 372.24 | Pass | Fail | 0 | 1 | 140 | 2023-01-16 15:35 | 2023-01-17 17:00 | 2023-01-17 12:30 | 2023-01-17 17:00 | 2023-01-23 08:30 |  | WCAPPR
MSA-DTWD | WA5451186 | 3 | AWB Co. | A350.2 - floor track needs re securing | Building | General Building | 230.625 | Pass | Fail | -1 | 0 | 140 | 2022-05-17 07:43 | 2022-05-23 17:00 | 2022-05-18 12:15 | 2022-05-23 17:00 | 2022-05-24 08:15 |  |  | WORK COMPLETED
MSA-DTWD | WA5495164 | 3 | AWB Co. | Block 10 - 10G3 - Light out over desk | Electrical | General Electrical | 225.02 | Pass | Pass | -1 | 0 | 140 | 2022-06-08 09:53 | 2022-06-15 17:00 | 2022-06-09 12:00 | 2022-06-15 17:00 | 2022-06-15 08:00 |  | WACCES | Attended site and signed in. Completed JSA. Located faulty lights. Supply and replace with new. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5495178 | 3 | AWB Co. | 10G65 - x 2 lights out | Electrical | General Electrical | 225.02 | Pass | Pass | -1 | 0 | 140 | 2022-06-08 09:58 | 2022-06-15 17:00 | 2022-06-09 13:00 | 2022-06-15 17:00 | 2022-06-15 09:00 |  | WACCES | Attended site and signed in. Completed JSA. Located faulty lights. Supply and replace with new. Tested all okay. Signed out. Job complete
MSA-DTWD | WA6407872 | 3 | Protek 24/7 Building & Maintenance | Roof leaking into classroom | Plumbing & Drainage | Drainage | 433.79 | Pass | Pass | -1 | 0 | 140 | 2023-01-10 12:37 | 2023-01-17 17:00 | 2023-01-10 13:30 | 2023-01-17 17:00 | 2023-01-16 09:30
MSA-DFES | WA6392205 | 2 | Securex Security Systems & Services | Ground - Door to BA Room - Key pad for lock is faulty. Difficult to unlock to access BA room | Security | Access Control | 1135 | Pass | Fail | 0 | 1 | 139.75 | 2022-12-23 11:03 | 2022-12-30 17:00 | 2022-12-28 14:15 | 2022-12-30 17:00 | 2023-01-03 10:00 |  |  | 28/12/2022, 1415-1430Digital lock requires replacement. Numerous keys faulty and none responsive. Revisit required.03/01/2023, 930-1000Installed new digital DX lock and set the code to same as existing.Tested ok
MSA-DTWD | WA5660774 | 1 | AWB Co. | Kitchen E74-convi oven not working | Electrical | General Electrical | 707.045 | Pass | Fail | 0 | 1 | 139.75 | 2022-07-19 12:31 | 2022-07-20 17:00 | 2022-07-20 15:15 | 2022-07-20 17:00 | 2022-07-26 11:00 |  | WACCES | Attended site and signed in. Completed JSA. Supply and replace 1 x dimmer to restaurant lights repaired by Milan. Supply and replace 3 gang plate to light switch as required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5473877 | 3 | AWB Co. | 2x merc vap globes faulty | Electrical | Lighting, Internal | 1382.1525 | Pass | Fail | -1 | 0 | 139.5 | 2022-05-25 07:47 | 2022-05-31 17:00 | 2022-05-27 15:15 | 2022-05-31 17:00 | 2022-06-02 10:45 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located Gym storeroom. Went through and replaced multiple lamps and ballast in lights that were not operating correctly. Also changed 2x 58ws under range hood in canteen kitchen to match others as directed by site. Notified relevant personal of works completed. Completed paperwork. **job complete**
MSA-DTAG | WA5203438 | 1 | Codee Cleaning Services | Ground & Level 1 - Custody cells - Bio clean - see notes below | Cleaning | Cleaning | 500 | Pass | Fail | 0 | 1 | 138.7333 | 2022-03-03 12:55 | 2022-03-04 17:00 | 2022-03-03 17:39 | 2022-03-04 17:00 | 2022-03-09 12:23 |  |  | complete
MSA-DTWD | WA5995415 | 2 | AWB Co. | K006 - Fluorescent light covers are degrading and look likely to fall | Electrical | General Electrical | 490.575 | Pass | Fail | -1 | 0 | 138.25 | 2022-10-06 12:05 | 2022-10-11 17:00 | 2022-10-07 14:15 | 2022-10-11 17:00 | 2022-10-13 08:30 |  | WACCES | Attended site signed in jsa completed. Located light in store and replaced with new light. Tested and working.Job completed
MSA-DTWD | WA6361201 | 1 | AWB Co. | power and lighting needs to be isolated | Electrical | Lighting, Internal | 290.005 | Pass | Fail | 0 | 1 | 138 | 2022-12-08 08:06 | 2022-12-09 17:00 | 2022-12-08 14:00 | 2022-12-09 17:00 | 2022-12-14 08:00 |  | WCAPPR | Attended site signed in jsa completed. Re energised circuits as per scopes.Job completed
MSA-DFES | WA5695714 | 3 | MALCOLM THOMPSON PUMPS PTY LTD | Applied training-ground-Storm Water Pump (near USAR undercover parking) isn't working | Plumbing & Drainage | Water |  | Fail | Fail | 1 | 2 | 135 | 2022-08-08 07:15 | 2022-08-12 17:00 | 2022-08-18 06:00 | 2022-08-12 17:00 | 2022-08-23 21:00 |  |  | Job is completed - Storm water pump has been replaced
MSA-DCA | WA6298982 | 1 | Earth & Water Pty Ltd | External Grounds - Gardens - Zone 14 Retic - Retic to be turned back on and activated daily | Plumbing & Drainage | Water |  | Fail | Fail | 4 | 5 | 134.5 | 2022-12-01 16:26 | 2022-12-02 17:00 | 2023-01-01 16:30 | 2022-12-02 17:00 | 2023-01-07 07:00 |  |  | Completed
MSA-DFES | WA6504006 | 3 | Dom's Total Grounds Maintenance | Side Garden - reticulation needs to be changed - Plant dying | Plumbing & Drainage | Water | 273 | Pass | Pass | -1 | 0 | 134.4167 | 2023-01-19 12:42 | 2023-01-27 17:00 | 2023-01-20 17:05 | 2023-01-27 17:00 | 2023-01-26 07:30
MSA-DTWD | WA5186960 | 1 | ECO PLUMBING AND GAS PTY LTD | Damaged spout/mixer combo at dishwashing station | Plumbing & Drainage | Water | 318.21 | Pass | Fail | 0 | 1 | 134.3667 | 2022-02-22 10:10 | 2022-02-23 17:00 | 2022-02-22 23:45 | 2022-02-23 17:00 | 2022-02-28 14:07 |  | WACCES | Installed new spindle
MSA-DTWD | WA5677907 | 2 | AWB Co. | E58 LSK - 3x LED Panels Not Working - High Raked Ceilings. Will need a large platform ladder | Electrical | Lighting, Internal | 468.555 | Pass | Fail | 0 | 0 | 129 | 2022-07-26 08:24 | 2022-07-29 17:00 | 2022-07-27 08:00 | 2022-07-29 17:00 | 2022-08-01 17:00 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Set up work area. Investigated lights not working. Found to be driver. Replaced with warranty parts. Notified relevant personnel of works completed. Packed up. **job complete**
MSA-DTWD | WA5187618 | 1 | Precise Air Group | Air con wont working - see notes | Air Conditioning | Room Air Conditioners | 986.22 | Pass | Fail | 0 | 1 | 128.5 | 2022-02-22 13:54 | 2022-02-23 17:00 | 2022-02-23 07:30 | 2022-02-23 17:00 | 2022-02-28 16:00 |  |  | Attended site and completed pre start paperwork and signed in. Acessed a/c in room j006. Found system out on a u4 fault(failed communication between indoor and outdoor unit ). Lecture advised that once push button timer releases unit fails to start. Reset system and inspected timer. Set timer to 30 second operation to test timer. Found to operate as required. Once push button pressed unit starts and runs with out fault. Set timer to 10 minutes and tested. Found all ok. Put timer back to 2hours and test ran. Unit ran with out fault . When the unit switches off on timer, button on the wall must be pressed before operating a/c as I suspect this is what is causing the u4 fault as timer drops out the communication line. Maintenance to monitor. If system fails again timer set-up / relays to be replaced.
MSA-DTAG | WA5866696 | 3 | Australian HVAC Services Pty. Ltd. | HPWU2 pump is not responding correctly | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2626.86 | Pass | Pass | -1 | 0 | 128 | 2022-09-14 08:54 | 2022-09-21 17:00 | 2022-09-15 08:30 | 2022-09-21 17:00 | 2022-09-20 16:30 |  |  | Pick up new pump from supplier. Attend site. Access roof and isolate HPWU2. Remove panels to access pump. Isolated supply and return water valves. Drain water from system. Remove electrical box cover and disconnect electrical wiring. Disconnect water pipework from pump. Unbolt pump mounts and remove old pump from unit. Swap over brass fittings to new pump for pipework connections. Install new pump and bolt up mounts. Connect water pipework and tighten. Connect electrical wiring and fit cover. Open water pipework and bleed air from system. New pump is longer than original so panel cut out required. Remove panel from roof and cut in rear carpark. Return to roof and fit modified panel. Deisolate unit and test operation of pump, found to start and operate as normal. Check pump amp draws and found to be 1.8 on each phase. Replace front panel and test operation of unit. Found unit to work as normal.
MSA-DTWD | WA6370028 | 2 | Lane's Plumbing | Paddock - Near Blue Valves - 2 x faulty valves near main water bank | Plumbing & Drainage | Water |  | Pass | Fail | -1 | 0 | 128 | 2022-12-14 09:21 | 2022-12-19 17:00 | 2022-12-14 10:30 | 2022-12-19 17:00 | 2022-12-19 18:30 |  |  | Completed
MSA-DTWD | WA5270661 | 2 | Protek 24/7 Building & Maintenance | LF.03 - Plaster is coming away from wall behind door, possibly water damage | Building | General Building | 884.91 | Pass | Fail | 0 | 1 | 127.75 | 2022-03-18 08:36 | 2022-03-23 17:00 | 2022-03-23 07:00 | 2022-03-23 17:00 | 2022-03-28 14:45 |  | WACCES | Repair plaster coming away from the wall
MSA-DTWD | WA5688149 | 3 | GRAFFITI FORCE PTY LTD | Ground Floor - External - 25Ab:Graffiti tagging at various points around perimeter | Cleaning | Graffiti | 588 | Pass | Fail | -1 | 0 | 127.0833 | 2022-08-02 10:09 | 2022-08-09 17:00 | 2022-08-05 07:00 | 2022-08-09 17:00 | 2022-08-10 14:05 |  |  | REMOVAL OF GRAFFITI FROM VARIOUS LOCATIONS AROUND THE TAFE
MSA-DTWD | WA5209009 | 1 | AHS Services WA Pty Ltd (Anchor) | B Block -Level 2 - Female Toilet - Leak from light female toilet | Plumbing & Drainage | Drainage | 568.6275 | Pass | Fail | 0 | 1 | 127 | 2022-03-09 12:38 | 2022-03-10 17:00 | 2022-03-10 08:00 | 2022-03-10 17:00 | 2022-03-15 15:00 |  |  | Investigated all areas water leaking through slab, located leak from end toilet, isolated water from pan, will reinsepect in few days to confirm 100 percent and repair. Returned inspected found dried out repaired last toilet , replaced flushpipe rubber and rubber connector.
MSA-DCA | WA6405482 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - AHU 6B Supply Fan Unit status fault on the BMS system - Possibly sensor switch issue | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1121.67 | Pass | Fail | 0 | 1 | 127 | 2023-01-09 14:18 | 2023-01-10 17:00 | 2023-01-10 08:00 | 2023-01-10 17:00 | 2023-01-15 15:00
MSA-DTWD | WA5795848 | 1 | BAKE-QUIP PTY LTD | Handle on Unox oven (opposite lecturer’s station) is broken-see notes | Electrical | General Electrical | 548.57 | Fail | Fail | 1 | 2 | 126.5 | 2022-08-26 06:37 | 2022-08-26 17:00 | 2022-09-01 08:45 | 2022-08-26 17:00 | 2022-09-06 15:15 |  | WACCES | Refer to service report
MSA-DTWD | WA6294260 | 3 | Protek 24/7 Building & Maintenance | A Block - Repair damaged & missing facia to external ceiling east side | Building | External Walls | 1494.96 | Pass | Pass | -1 | 0 | 126.5 | 2022-11-30 14:04 | 2022-12-07 17:00 | 2022-12-02 07:00 | 2022-12-07 17:00 | 2022-12-07 13:30 |  | WACCES | Replaced missing and damaged FC facia
MSA-DTWD | WA6534906 | 2 | AWB Co. | Faulty wall mounted fans | Electrical | General Electrical | 1572.555 | Pass | Fail | 0 | 1 | 126 | 2023-02-06 13:47 | 2023-02-09 17:00 | 2023-02-08 10:00 | 2023-02-09 17:00 | 2023-02-13 16:00 |  | WACCES
MSA-DFES | WA6603930 | 3 | Dom's Total Grounds Maintenance | Rectify master valve issues as advised by Deb @ PFM | Plumbing & Drainage | Drainage | 575 | Pass | Pass | -1 | 0 | 126 | 2023-02-17 13:19 | 2023-02-24 17:00 | 2023-02-18 06:30 | 2023-02-24 17:00 | 2023-02-23 12:30
MSA-DFES | WA4990035 | 0 | Australian HVAC Services Pty. Ltd. | WAter leaking through the ceiling on the second level - centre stariways near lifts. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 3159.41 | Pass | Fail | 0 | 1 | 125.0333 | 2022-01-02 10:43 | 2022-01-02 12:43 | 2022-01-02 10:45 | 2022-01-02 14:43 | 2022-01-07 15:47 |  | WACCES | Repaired leaking mechanical seal on condenser water pump 2
MSA-DTWD | WA6689163 | 2 | AWB Co. | Faulty lights | Electrical | Lighting, Internal |  | Pass | Fail | 0 | 0 | 125 | 2023-03-08 09:58 | 2023-03-13 17:00 | 2023-03-10 10:00 | 2023-03-13 17:00 | 2023-03-15 15:00
MSA-DTWD | WA5175419 | 2 | Precise Air Group | Noise in Aircon in middle of room | Air Conditioning | Room Air Conditioners | 554.685 | Pass | Fail | 0 | 1 | 124.95 | 2022-02-21 11:37 | 2022-02-24 17:00 | 2022-02-23 09:00 | 2022-02-24 17:00 | 2022-02-28 13:57 |  | WCAPPR | Was unable to gain access into class room, waited for class to finish. Will reschedule for Monday Returned to site, gained access to area with noisy fan coil unit, found frame of unit has come loose from fan and causing fan bracket to knock against the frame. Isolated unit, reattached bracket. Ran system checked operation all systems running to specs. Cleared debris from site
MSA-DFES | WA5204951 | 3 | ADVANCED LOCK & KEY | Warehouse door lock is incorrectly installed - further notes below | Security | Locksmith | 544.94 | Pass | Pass | -1 | 0 | 124.5833 | 2022-03-04 15:55 | 2022-03-14 17:00 | 2022-03-09 10:50 | 2022-03-14 17:00 | 2022-03-14 15:25 |  |  | Installed 002Lsc with 2 3mm 001 packers keyed to sample (1 c4 rekey for outside cyl) on warehouse entry door and removed old 303 that was installed higher as it wasn’t fire code
MSA-DTWD | WA5106783 | 2 | ADVANCED LOCK & KEY | Door lock is not working - see note below | Security | Locksmith | 1295 | Pass | Fail | 0 | 1 | 124.25 | 2022-02-07 11:22 | 2022-02-10 17:00 | 2022-02-10 11:05 | 2022-02-10 17:00 | 2022-02-15 15:20 |  |  | Replace lock
MSA-DTAG | WA5801304 | 1 | Australian HVAC Services Pty. Ltd. | Air con faulty in Court 2 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1071.76 | Pass | Fail | 0 | 1 | 124 | 2022-08-31 15:12 | 2022-09-01 17:00 | 2022-09-01 07:30 | 2022-09-01 17:00 | 2022-09-06 11:30 |  |  | Travelled to site with Icon logic.Investigated no airflow Status on FCU 4 , and 6.Found FCU 4 running, status relay not energized.After checking and going through wiring found On/Off switch in court room desk control panel has been switched off. Switched on unit from switch, unit has run status. All ok.FCU 6 found air flow switch open.Adjusted airflow switch and now we have status. Will monitor flow switch for FCU 6.Both units have now status.
MSA-DTWD | WA4992272 | 2 | Equans Mechanical Services Australia | Chiller 1 continuously tripping out - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 517.21 | Fail | Fail | 0 | 1 | 124 | 2022-01-06 09:22 | 2022-01-11 17:00 | 2022-01-13 11:30 | 2022-01-11 17:00 | 2022-01-18 15:30 |  |  | A40328248K Daikin Chiller 1. 13/1/22 Carried out investigations and found cranck case heater to have failed causing equipment to go into fault. Isolated staged and 18/1/22 sourced new heater from supplier. Brought to site isolated chiller and carried out replacement. Confirmed operation. Chiller placed back into remote operation mode. Work area left tidy. Confirmed no further active faults.
MSA-DCA | WA6516839 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Air con fault - Gas shutoff button on -see notes | Air Conditioning | Ducted Split System | 712.21 | Fail | Fail | 0 | 1 | 123.5 | 2023-01-23 16:00 | 2023-01-24 17:00 | 2023-01-25 12:30 | 2023-01-24 17:00 | 2023-01-30 16:00
MSA-DTWD | WA6560660 | 2 | M Construction (WA) | Female Restaurant toilets - Entry door has sagged and does not close properly | Building | Doors | 374.91 | Pass | Fail | 0 | 1 | 123.5 | 2023-02-13 11:45 | 2023-02-16 17:00 | 2023-02-15 09:00 | 2023-02-16 17:00 | 2023-02-20 12:30
MSA-DCA | WA6369584 | 2 | Protek 24/7 Building & Maintenance | East of State Library-Broken paving in two spots.-see notes | Paving & Roadworks | Paving | 374.07 | Pass | Fail | 0 | 0 | 123.25 | 2022-12-14 08:41 | 2022-12-19 17:00 | 2022-12-16 09:30 | 2022-12-19 17:00 | 2022-12-21 12:45 |  | WACCES | Remove 2 x damaged concrete slabs and replace with new , cut to size to match existing
MSA-DTAG | WA6393801 | 3 | Midolo Building Services | Levels 7, 8 & 9 - Loose seating which needs to be tightened (see notes) | Furniture | Office Furniture | 413.56 | Pass | Fail | 0 | 0 | 123 | 2022-12-29 10:19 | 2023-01-06 17:00 | 2023-01-04 07:30 | 2023-01-06 17:00 | 2023-01-09 10:30
MSA-DFES | WA5107248 | 1 | Anvil Doors | Engine Room - Door 2 - Cut cord | Building | Fire Door | 3462 | Fail | Fail | 1 | 2 | 122.75 | 2022-02-07 16:26 | 2022-02-08 17:00 | 2022-02-14 09:45 | 2022-02-08 17:00 | 2022-02-19 12:30 |  |  | Attended Duncraig Fire Station and replaced 4 x retractable cable to bifold doors. Please see attached service report and signature slip.Thank you
MSA-DTWD | WA6364573 | 2 | BAKE-QUIP PTY LTD | The hot plate is not heating evenly | Equipment | Catering Equipment | 1449.9 | Pass | Fail | 0 | 1 | 122.75 | 2022-12-12 12:47 | 2022-12-15 17:00 | 2022-12-14 07:30 | 2022-12-15 17:00 | 2022-12-19 10:15 |  |  | Refer to service report
MSA-DTWD | WA6540567 | 2 | AHS Services WA Pty Ltd (Anchor) | Student female toilets - wont flush | Plumbing & Drainage | Drainage | 269.5075 | Pass | Fail | -1 | 0 | 122.6667 | 2023-02-09 11:47 | 2023-02-14 17:00 | 2023-02-10 12:15 | 2023-02-14 17:00 | 2023-02-15 14:55
MSA-MRWA | WA5482186 | 2 | Water2water Pty Ltd | Alfresco Area - Ice machine is faulty - Ice is melting | Refrigeration | Ice machine | 307.715 | Pass | Fail | 0 | 1 | 122.5833 | 2022-05-31 09:47 | 2022-06-03 17:00 | 2022-06-02 13:45 | 2022-06-03 17:00 | 2022-06-07 16:20 |  |  | TECH REPLACED 10" MAXIFLOW SCALE WITH 15" MAXIFLOW SCALE. LEFT OVER WEEKEND TO DEFROST. RAN CYCLE, ALL OKAY ON DEPARTURE
MSA-DTWD | WA5835544 | 3 | Protek 24/7 Building & Maintenance | D102 & D103 - floor boards damaged by white ant infestation | Flooring | Timber | 979.59 | Pass | Pass | -1 | 0 | 122.5 | 2022-09-07 09:22 | 2022-09-14 17:00 | 2022-09-08 12:00 | 2022-09-14 17:00 | 2022-09-13 14:30 |  |  | Removed rotten flooring. Sprayed insecticide across timber and under flooring. Replaced flooring with new planks.
MSA-DTWD | WA5287770 | 3 | Falcetta Plumbing and Gas | Level 2 - W204 - sink waste pipe runs slow or has blockage | Plumbing & Drainage | Water | 315.7 | Pass | Pass | -1 | 0 | 122.5 | 2022-03-22 15:47 | 2022-03-29 17:00 | 2022-03-24 13:00 | 2022-03-29 17:00 | 2022-03-29 15:30 |  | WACCES | removed old safe tray waste and installed new
MSA-DTWD | WA6082031 | 3 | CONNECT SECURITY SYSTEMS | No CCTV vision to staff computers in reception | Security | Security Management System | 1061.44 | Pass | Pass | -1 | 0 | 122.35 | 2022-10-18 15:11 | 2022-10-25 17:00 | 2022-10-20 11:18 | 2022-10-25 17:00 | 2022-10-25 13:39 |  |  | Reprogrammed CCTV to get operating on PCs again
MSA-DCA | WA5459938 | 2 | GPS Plumbing & Gas Services PtyLtd | Conservation Labs - Level 1 - Leak, possibly from PVS piping | Plumbing & Drainage | Water | 860.795 | Pass | Fail | 0 | 0 | 122.3167 | 2022-05-18 10:03 | 2022-05-23 17:00 | 2022-05-20 08:50 | 2022-05-23 17:00 | 2022-05-25 11:09 |  | WCAPPR | Replaced section of leaking storm water pipe near the ceilingDrained storm water pipe was full of water.
MSA-DTWD | WA5133448 | 2 | AWB Co. | C Block - Ground - Child Care Centre - Various lighting not working | Electrical | General Electrical | 327.305 | Pass | Fail | 0 | 0 | 122.25 | 2022-02-15 10:55 | 2022-02-18 17:00 | 2022-02-16 13:30 | 2022-02-18 17:00 | 2022-02-21 15:45 |  | WCAPPR | Attended site and signed in. Completed JSA. Went through and replaced various fluros in childcare centre. Notified site of works. **job complete**
MSA-DTWD | WA6129424 | 3 | COMMERCIAL PLUMBING AND GAS | Staff disabled toilet - Leaking Tap | Plumbing & Drainage | Water | 428.685 | Pass | Fail | 0 | 1 | 122 | 2022-10-27 14:55 | 2022-11-03 17:00 | 2022-11-03 14:00 | 2022-11-03 17:00 | 2022-11-08 16:00 |  |  | replaced basin set, installed mini stops
MSA-DTWD | WA5141455 | 1 | Equans Mechanical Services Australia | Ground - AG06 - Air Conditioner Cassette just blowing air | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Fail | 0 | 1 | 122 | 2022-02-16 10:24 | 2022-02-17 17:00 | 2022-02-17 10:00 | 2022-02-17 17:00 | 2022-02-22 12:00 |  |  | Gathered tools and equipment, checked controls and operation all ok. No fault located. Only fault found door open to room may cause unit to over work. Cleaned up and completed paperwork. 22.2 RETURNED TO SITE FOUND UNIT HAD A FAULT CODE WHICH A OLD CODE RETESTED FOUND ALL OK. RESET UNIT MONITORED AND TESTED ALL OK. DOOR CONTINUALLY LEFTOPEN AND TEMP SETTINGS AT 20C. CONDENSER UNIT ON ROOF IN DIRECT SUN. GOING OUT ON HIGH HEAD PRESSURE. REPORTED FINDINGS CLEANED UP AND COMPLETED PAPERWORK AND SIGNED OUT
MSA-DTWD | WA5460575 | 1 | Protek 24/7 Building & Maintenance | DG01 - Roof leak in classroom, has caused ceiling to collapse - see details below | Building | General Building | 628.75 | Fail | Fail | 0 | 1 | 122 | 2022-05-18 15:36 | 2022-05-19 17:00 | 2022-05-20 13:00 | 2022-05-19 17:00 | 2022-05-25 15:00 |  |  | BRAF declined Investigate breakdown report per above workorder details and report to Protek247 OperationsPerform make safe, make good or repair as instructed to prevent further damage or harm to persons and property
MSA-DTWD | WA5192346 | 3 | AWB Co. | N17 east yard - Damaged paving due to heavy vehicle | Paving & Roadworks | Paving | 925 | Pass | Fail | 0 | 1 | 121.8333 | 2022-02-25 11:30 | 2022-03-04 17:00 | 2022-03-03 07:17 | 2022-03-04 17:00 | 2022-03-08 09:07 |  |  | Repaired paving area damaged by heavy vehicles
MSA-DCA | WA4991112 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Back-of house office area (Kalle’s Office located back, far left of Conservation labs)-see notes | Air Conditioning | Room Air Conditioners | 868.6 | Pass | Fail | 0 | 0 | 121.6333 | 2022-01-04 15:18 | 2022-01-07 17:00 | 2022-01-05 14:16 | 2022-01-07 17:00 | 2022-01-10 15:54 |  |  | Returned to site to recheck. Confirmed no further water leaking present. Confirmed unit drip tray and base were dry and had no pooling water. Work area left tidy. All switches left in auto.
MSA-DTWD | WA5189201 | 1 | AWB Co. | faulty power point coming away from the wall | Electrical | General Electrical | 673.38 | Pass | Fail | 0 | 1 | 121.5 | 2022-02-23 15:34 | 2022-02-24 17:00 | 2022-02-24 12:30 | 2022-02-24 17:00 | 2022-03-01 14:00 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm about job. Re located damaged rcd gpo. De energised circuit from distribution board. Double checked to ensure rcd gpo was dead. Took off old rcd gpo and base. Marked out new holes for new base to go onto. Drilled new holes and put green plugs in wall. Fixed base to wall and made sure it was level. Fit off rcd gpo. Put back together. Re energised circuit. Tested rcd gpo operation. Everything working as intended. Took pictures before and after. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5499415 | 2 | AWB Co. | D 30 - Faulty bench lights | Electrical | General Electrical | 695.96 | Pass | Fail | 0 | 1 | 121.5 | 2022-06-10 12:58 | 2022-06-15 17:00 | 2022-06-15 10:30 | 2022-06-15 17:00 | 2022-06-20 12:00 |  | WACCES | Attended site signed in jsa completed. Installed new led lights in d30 classroom. *** job completed ***
MSA-DFES | WA6293244 | 2 | Australian HVAC Services Pty. Ltd. | Level 1 & 6-air con issues - see notes | Air Conditioning | Room Air Conditioners | 477.78 | Pass | Fail | 0 | 1 | 121.5 | 2022-11-30 07:13 | 2022-12-02 17:00 | 2022-12-01 08:00 | 2022-12-02 17:00 | 2022-12-06 09:30 |  |  | Gary McAndrew (01/12/2022) - Work NoteFaulty outside board, possibly fan motor, tech support recommends replacing both board and fan motor, compressor tests ok electrically but could be seized, will not know until parts replaced.Parts are not available until the end of the month. The condition of the outdoor unit I would recommend that the AC is replaced. Bill Clarke (06/12/2022 - Work NoteAttended site to get details to quote new AC Unit
MSA-DCA | WA6393766 | 2 | Protek 24/7 Building & Maintenance | Alexander Library Building - Server room - Door latch stuck, door unable to be secured | Building | Doors | 259.39 | Pass | Pass | -1 | 0 | 121.5 | 2022-12-29 09:26 | 2023-01-04 17:00 | 2022-12-29 10:45 | 2023-01-04 17:00 | 2023-01-03 12:15
MSA-DCA | WA5687148 | 2 | FCT SURFACE CLEANING | First Floor - graffiti on almost all sides of the site except the front | Cleaning | Graffiti |  | Pass | Fail | 0 | 1 | 121.25 | 2022-08-01 13:22 | 2022-08-04 17:00 | 2022-08-03 11:45 | 2022-08-04 17:00 | 2022-08-08 13:00 |  |  | Removal of graffiti
MSA-MRWA | WA5368990 | 2 | Water2water Pty Ltd | Marri room kitchen - Zip hydro-tap tap not working - see notes below | Plumbing & Drainage | Water | 690.995 | Pass | Fail | 0 | 1 | 121.2 | 2022-04-19 14:45 | 2022-04-22 17:00 | 2022-04-22 12:30 | 2022-04-22 17:00 | 2022-04-27 13:42 |  | WACCES | Replaced zip tap loom to main pcb board and also replaced leaking tap head with a zip converter head and filter system combo. Tested, normal operation
MSA-DFES | WA5133233 | 2 | ADVANCED LOCK & KEY | engine bay room - locker rooms - broken locking mechanisms on lockers | Security | Locksmith | 507.5 | Pass | Fail | 0 | 1 | 121 | 2022-02-15 08:46 | 2022-02-18 17:00 | 2022-02-17 14:00 | 2022-02-18 17:00 | 2022-02-22 15:00 |  |  | Replaced 7 cam locks with 7 new 19mm l&f cam locks and 1 new rectangular black plastic locker lock to replace broken one
MSA-DTWD | WA6516808 | 2 | AWB Co. | Three ceiling fans are loose and unstable for use | Electrical | General Electrical | 894.24 | Pass | Fail | 0 | 0 | 121 | 2023-01-23 15:28 | 2023-01-27 17:00 | 2023-01-25 14:00 | 2023-01-27 17:00 | 2023-01-30 15:00 |  | WACCES
MSA-DTAG | WA5209103 | 2 | Australian HVAC Services Pty. Ltd. | Level 10 - Doctor's office -Rattling noise in the roof above workstation see notes | Air Conditioning | Room Air Conditioners | 1003.47 | Pass | Fail | 0 | 1 | 121 | 2022-03-09 13:33 | 2022-03-14 17:00 | 2022-03-14 10:00 | 2022-03-14 17:00 | 2022-03-19 11:00 |  |  | Attend site. Access bms level 6 and override level 15 AHU off. Access level 15 and isolate AHU and tag out. Access level 10 supply ductwork and remove access panel. Locate fire damper and found and found to have play causing movement under high airflow. Found threaded rivot to have come loose in the joining tab. Cut out rivot and screw as was seized. Replace with nut and bolt. Tighten and now damper has no play. Access level 15 and deisolate AHU. Access level 6 and change AHU to manual operation. Return to level 10 and check for noise. No noise or vibrations found. Access level 6 and return AHU to automatic operation. Clean up area.
MSA-DCA | WA5578414 | 3 | Techworks Electrical | The lamp that notifies if power is supplying the fire sprinkler pumps is out | Electrical | General Electrical | 356.7 | Pass | Fail | 0 | 1 | 121 | 2022-07-01 11:32 | 2022-07-08 17:00 | 2022-07-08 07:00 | 2022-07-08 17:00 | 2022-07-13 08:00 |  |  | Completed replacement of 240v coil 3pole contactor.
MSA-DTWD | WA5108499 | 1 | Equans Mechanical Services Australia | T Block - L1 - t114 - T114 A/c isn’t working - Have tried to correct using BMS | Air Conditioning | Room Air Conditioners | 1000 | Fail | Fail | 0 | 1 | 120.75 | 2022-02-08 14:42 | 2022-02-09 17:00 | 2022-02-10 11:45 | 2022-02-09 17:00 | 2022-02-15 12:30 |  |  | Checked issue and found second person required To be continued 11/2 amRe attended and found issue to be with BMS. Controls tech to attend Controls tech attended and fixed problem
MSA-DTAG | WA5796224 | 2 | Midolo Building Services | 1987 Wing - Justice Beech Chambers - Black skirting board damaged - See notes | Building | Internal Walls | 185.36 | Pass | Pass | -1 | 0 | 120.75 | 2022-08-26 09:29 | 2022-08-31 17:00 | 2022-08-26 14:00 | 2022-08-31 17:00 | 2022-08-31 14:45 |  |  | skirting re attached to wall & cut down carpet tile for door clearance
MSA-DCA | WA6159022 | 1 | Protek 24/7 Building & Maintenance | Ground Level - Loading Bay - Replace Dead Bolt - See notes below | Building | Doors | 178.57 | Pass | Fail | 0 | 1 | 120.5 | 2022-11-10 11:03 | 2022-11-11 17:00 | 2022-11-11 08:00 | 2022-11-11 17:00 | 2022-11-16 08:30 |  | WACCES | Supply and install a long throw shoot bolt to loading dock door
MSA-DCA | WA5495672 | 3 | Protek 24/7 Building & Maintenance | Regional Arts Office - Sash Window Cord Replacement | Building | General Building | 659.26 | Pass | Pass | -1 | 0 | 120.5 | 2022-06-08 14:00 | 2022-06-15 17:00 | 2022-06-09 13:30 | 2022-06-15 17:00 | 2022-06-14 14:00 |  | WACCES | Replace cords on 2 sash windows
MSA-DTWD | WA5568996 | 2 | BAKE-QUIP PTY LTD | Faulty Combi oven | Equipment | Catering Equipment | 1958.1 | Fail | Fail | 1 | 2 | 120.5 | 2022-06-27 11:03 | 2022-06-30 17:00 | 2022-07-06 10:30 | 2022-06-30 17:00 | 2022-07-11 11:00 |  | WACCES | WRONG CLEANING CHEMICAL BEING USED. REFER TO SERVICE REPORT
MSA-DTWD | WA6184795 | 3 | M Construction (WA) | Library Male toilets - Vanity bench coming away from wall | Carpentry | Timber (all types) | 1176.58 | Pass | Pass | -1 | 0 | 120.0333 | 2022-11-15 16:10 | 2022-11-22 17:00 | 2022-11-16 16:33 | 2022-11-22 17:00 | 2022-11-21 16:35 |  |  | Support vanity unit with timber remove brackets. Re fit unit fit brackets. new legs clean up.
MSA-DCA | WA5499017 | 3 | Protek 24/7 Building & Maintenance | Door between café and theatre foyer - Door wonky and at risk of striking glass | Building | Doors | 978 | Pass | Pass | -1 | 0 | 120 | 2022-06-10 09:25 | 2022-06-17 17:00 | 2022-06-10 12:00 | 2022-06-17 17:00 | 2022-06-15 12:00 |  | WACCES | Repair wonky door
MSA-DFES | WA5868627 | 3 | Protek 24/7 Building & Maintenance | Ground floor - between foyer and mailroom - door not closing properly, getting jammed | Building | Doors | 165.3 | Pass | Pass | -1 | 0 | 120 | 2022-09-14 11:19 | 2022-09-21 17:00 | 2022-09-15 08:30 | 2022-09-21 17:00 | 2022-09-20 08:30 |  |  | Repaired door handle
MSA-DTWD | WA6126167 | 2 | M Construction (WA) | The soft door close has broken, so the door is heavy and slams shut | Building | Doors | 910.92 | Pass | Fail | 0 | 1 | 120 | 2022-10-25 10:33 | 2022-10-28 17:00 | 2022-10-28 11:00 | 2022-10-28 17:00 | 2022-11-02 11:00 |  |  | Door Closer was in need of replacement. Replaced on 02/11/2022
MSA-DTWD | WA6687615 | 1 | Precise Air Group | aircon not working | Air Conditioning | Room Air Conditioners | 366 | Pass | Fail | 0 | 1 | 119.95 | 2023-03-07 08:47 | 2023-03-08 17:00 | 2023-03-08 08:04 | 2023-03-08 17:00 | 2023-03-13 08:01 |  | WACCES
MSA-DTWD | WA5692581 | 2 | Protek 24/7 Building & Maintenance | External stair case - Down pipe detached from gutter | Roofing | Guttering | 548.57 | Pass | Fail | -1 | 0 | 119.5 | 2022-08-03 15:01 | 2022-08-08 17:00 | 2022-08-04 10:15 | 2022-08-08 17:00 | 2022-08-09 09:45 |  | WACCES | Re install down pipe
MSA-DTWD | WA6298629 | 2 | Precise Air Group | Evap aircon is leaking water into the room on the floor | Air Conditioning | Evaporative Coolers | 1019.14 | Pass | Fail | -1 | 0 | 119.4833 | 2022-12-01 11:42 | 2022-12-06 17:00 | 2022-12-02 13:00 | 2022-12-06 17:00 | 2022-12-07 12:29 |  |  | Turned unit on and let run and checked for leaks.No leaks found.Silicone around all screws and seams has held.Unit working 100%
MSA-DFES | WA5201488 | 3 | Protek 24/7 Building & Maintenance | Dining Rooms - Kitchen cupboards broken, see notes below | Furniture | Indoor Furniture | 698.38 | Pass | Pass | -1 | 0 | 119.25 | 2022-03-02 15:34 | 2022-03-10 17:00 | 2022-03-04 12:30 | 2022-03-10 17:00 | 2022-03-09 11:45 |  |  | Repair hinges
MSA-DTWD | WA5151359 | 1 | Lane's Plumbing | BLD 833 Homestead - Kitchen *- Water leak | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 1 | 119 | 2022-02-17 12:35 | 2022-02-18 17:00 | 2022-02-17 14:00 | 2022-02-18 17:00 | 2022-02-22 13:00 |  |  | job completed - repaired leaking hot water ring main to homestead
MSA-DTAG | WA5660913 | 1 | Midolo Building Services | Courtroom 2 - entry door is slamming loudly and bouncing off the frame- See notes below | Building | Doors | 826.89 | Pass | Fail | 0 | 1 | 119 | 2022-07-19 13:31 | 2022-07-20 17:00 | 2022-07-20 10:00 | 2022-07-20 17:00 | 2022-07-25 09:00 |  | WCAPPR | new buffer & closer installed to door
MSA-DTWD | WA5977191 | 2 | COMMERCIAL PLUMBING AND GAS | ground, toilet-Leaking toilet in wooden boat works-see notes | Plumbing & Drainage | Toilets/Cisterns | 514.95 | Pass | Fail | 0 | 1 | 119 | 2022-09-27 14:19 | 2022-09-30 17:00 | 2022-09-30 16:00 | 2022-09-30 17:00 | 2022-10-05 15:00 |  |  | Replaced cistern
MSA-DFES | WA6131525 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 1-Bathroom-leaking hot water tap in vanity | Plumbing & Drainage | Water | 284.885 | Pass | Fail | 0 | 1 | 119 | 2022-10-31 08:15 | 2022-11-03 17:00 | 2022-11-03 11:30 | 2022-11-03 17:00 | 2022-11-08 10:30 |  | WCAPPR | Attended site for door one bathroom tap leaking on vanity on inspection I found both hot and cold mini stops leaking I have serviced both mini stops as well as servicing the hot and cold taps as theywere dripping afterwards after I’ve tested everything is working correctly cleaned up packed up
MSA-DFES | WA5679611 | 1 | Protek 24/7 Building & Maintenance | L2-Water leaking through the ceiling running down the window- see notes | Roofing | Metal Roofing | 555.59 | Pass | Fail | 0 | 1 | 118.75 | 2022-07-26 15:33 | 2022-07-27 17:00 | 2022-07-27 13:30 | 2022-07-27 17:00 | 2022-08-01 12:15 |  |  | inspect and clean and reseal
MSA-DTWD | WA5306131 | 1 | AHS Services WA Pty Ltd (Anchor) | A Block - Level 4 - Kitchen - leaking urn tap and a kitchen sink tap is leaking | Plumbing & Drainage | Materials | 814.245 | Pass | Fail | 0 | 1 | 118.5 | 2022-04-06 10:31 | 2022-04-07 17:00 | 2022-04-06 10:45 | 2022-04-07 17:00 | 2022-04-11 09:15 |  |  | Replaced rusty tap set to level 4 kitchen
MSA-DTWD | WA6517948 | 3 | Australian Airconditioning Services Pty Ltd | Walk in freezer - Isnt working | Refrigeration | Freezers | 301.28 | Pass | Pass | -1 | 0 | 118.5 | 2023-01-24 14:39 | 2023-02-01 17:00 | 2023-01-25 11:30 | 2023-02-01 17:00 | 2023-01-30 10:00
MSA-DTWD | WA6001070 | 2 | Water2water Pty Ltd | F block - Fabrication area - water cooler not cooling | Plumbing & Drainage | Water | 728.49 | Pass | Fail | 0 | 1 | 118.4333 | 2022-10-10 12:13 | 2022-10-13 17:00 | 2022-10-12 12:15 | 2022-10-13 17:00 | 2022-10-17 10:41 |  | WCAPPR | Plumber required to attend this job due to being hard wired, rescheduling when we can have a plumber attend.All works complete and tested. Arch’s supplied by clients.
MSA-DTAG | WA5692559 | 2 | Water2water Pty Ltd | Level 1 - Kitchen in Judicial Corridor - Instant hot water tap not working | Plumbing & Drainage | Water | 368.95 | Pass | Fail | -1 | 0 | 118.25 | 2022-08-03 14:37 | 2022-08-08 17:00 | 2022-08-04 13:30 | 2022-08-08 17:00 | 2022-08-09 11:45 |  | WCAPPR | Tap needs replacementUnable to isolate power will need an electrical person to attend
MSA-DCA | WA6014391 | 3 | FCT SURFACE CLEANING | Various locations graffiti - see locations below | Cleaning | Graffiti |  | Pass | Pass | -1 | 0 | 118.25 | 2022-10-12 08:50 | 2022-10-19 17:00 | 2022-10-12 11:30 | 2022-10-19 17:00 | 2022-10-17 09:45 |  |  | Removal of graffiti
MSA-DTWD | WA6143177 | 2 | AWB Co. | Rooms 3-10 and 3-11 (Same circuit) - No power to lectures desks | Electrical | General Electrical | 887.39 | Pass | Fail | 0 | 0 | 118.25 | 2022-11-01 11:05 | 2022-11-04 17:00 | 2022-11-02 09:15 | 2022-11-04 17:00 | 2022-11-07 07:30 |  | WCAPPR | Attended site and signed in. Completed JSA. De energised board. Replaced rcd. Tested. Working as intended. Took pic. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA6689172 | 2 | AWB Co. | x8 Faulty Lights - Spray booths | Electrical | Lighting, Internal |  | Pass | Fail | 0 | 0 | 118 | 2023-03-08 10:03 | 2023-03-13 17:00 | 2023-03-10 11:00 | 2023-03-13 17:00 | 2023-03-15 09:00 |  | WCAPPR
MSA-DTAG | WA5163596 | 1 | Sapio Pty Ltd | Security Keypad Rear entrance -Security system wont arm – fault msge – Network failure in courthouse | Security | Monitoring | 511.39 | Pass | Fail | 0 | 0 | 117.5 | 2022-02-18 10:22 | 2022-02-21 17:00 | 2022-02-18 11:00 | 2022-02-21 17:00 | 2022-02-23 08:30 |  | WACCES | Replaced Duress button and confirmed communications errors has been rectified
MSA-DCA | WA6190920 | 3 | Protek 24/7 Building & Maintenance | Ground & Level 1 - Foyer & rehearsal room 1 - Fire doors are sticking | Building | Fire Door | 259.39 | Pass | Pass | -1 | 0 | 117.5 | 2022-11-16 11:34 | 2022-11-23 17:00 | 2022-11-16 12:30 | 2022-11-23 17:00 | 2022-11-21 10:00 |  |  | Completed investigation on Jarrah doors as per breakdown report.Set of double doors have become dilapidated due to weathering and lack of maintenanceBraf Declined
MSA-DCA | WA6518692 | 2 | Protek 24/7 Building & Maintenance | Ladies Toilet in Foyer behind the reception-door is rubbing on floor- see notes | Building | Doors | 264.82 | Fail | Fail | 0 | 1 | 117.5 | 2023-01-25 10:28 | 2023-01-31 17:00 | 2023-02-01 09:30 | 2023-01-31 17:00 | 2023-02-06 07:00
MSA-DFES | WA4991189 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Dorm 5 - Sensor light in dorm 5 toilet is not working | Electrical | Lighting, Internal | 518.265 | Pass | Pass | -1 | 0 | 117.5 | 2022-01-04 16:28 | 2022-01-11 17:00 | 2022-01-06 11:30 | 2022-01-11 17:00 | 2022-01-11 09:00 |  | WACCES | complete
MSA-DTWD | WA6165809 | 2 | AWB Co. | Room G122 - Faulty Ceiling Fans | Electrical | General Electrical | 1066.26 | Pass | Fail | 0 | 1 | 117.5 | 2022-11-11 09:44 | 2022-11-16 17:00 | 2022-11-16 13:00 | 2022-11-16 17:00 | 2022-11-21 10:30 |  | WCAPPR | Attended site and signed in completed JSA. Liaised with site about works going ahead. Located room G122. Investigated fault on circuit. Pulled down fan and tested. Fan all good. Upon further investigation found to be faulty fan controller as its feeding all fans in classroom. Left site to pick up parts. Returned and replaced fan controller. Tested fan for correct operation. All working correctly. Notified relevant personnel. **job complete**
MSA-DCA | WA6401374 | 0 | Critical Fire Protection & Training | security room-fire panel-multiple fire alarms on fire panel | Fire Protection Services | Fire Protection - Monitor System | 944.08 | Pass | Fail | 0 | 1 | 117.5 | 2023-01-04 11:27 | 2023-01-04 13:27 | 2023-01-04 11:30 | 2023-01-04 15:27 | 2023-01-09 09:00
MSA-DFES | WA6461917 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - All bathrooms - Hand basins drain extremely slow | Plumbing & Drainage | Water | 297.4 | Pass | Fail | 0 | 0 | 117.2333 | 2023-01-17 08:27 | 2023-01-20 17:00 | 2023-01-18 12:00 | 2023-01-20 17:00 | 2023-01-23 09:14 |  | WCAPPR
MSA-DTWD | WA6149313 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire warning speakers not working | Fire Protection Services | Smoke and Heat Detection | 360.18 | Pass | Pass | -1 | 0 | 116.8333 | 2022-11-04 14:02 | 2022-11-09 17:00 | 2022-11-04 14:40 | 2022-11-09 17:00 | 2022-11-09 11:30 |  | WACCES | 1. SS-04/11/22-CALL OUT-P2 FEEREPORT-04/11/2022-NORMAL LABOUR CHARGES- 1 HOUR-Arrived on site @ 1440 Met with Brett (Facilities manager)____________________________________________________2. SS-09/11/22REPORT-09/11/22-NORMAL LABOUR CHARGES- 2 TECHNCICIANSCOMPLETED 09/11/2022
MSA-DTWD | WA6149316 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire warning speakers not working | Fire Protection Services | Smoke and Heat Detection | 360.18 | Pass | Pass | -1 | 0 | 116.8333 | 2022-11-04 14:05 | 2022-11-09 17:00 | 2022-11-04 14:40 | 2022-11-09 17:00 | 2022-11-09 11:30 |  | WACCES | 1. SS-04/11/22-CALL OUT-P2 FEEREPORT-04/11/2022-NORMAL LABOUR CHARGES- 1 HOUR-Arrived on site @ 1440 Met with Brett (Facilities manager)____________________________________________________2. SS-09/11/22REPORT-09/11/22-NORMAL LABOUR CHARGES- 2 TECHNICIANSCOMPLETED 09/11/2022
MSA-DTWD | WA6149318 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire warning speakers not working | Fire Protection Services | Smoke and Heat Detection | 360.18 | Pass | Pass | -1 | 0 | 116.8333 | 2022-11-04 14:06 | 2022-11-09 17:00 | 2022-11-04 14:40 | 2022-11-09 17:00 | 2022-11-09 11:30 |  | WACCES | 1. SS-04/11/22-CALL OUT-P2 FEEREPORT-04/11/2022-NORMAL LABOUR CHARGES- 1 HOUR-Arrived on site @ 1440 Met with Brett (Facilities manager)____________________________________________________2. SS-09/11/22REPORT-09/11/22-NORMAL LABOUR CHARGES- 2 TECHSCOMPLETED 09/11/2022
MSA-DFES | WA4983929 | 3 | Dom's Total Grounds Maintenance | Admin Lawn - Broken sprinkler, cnr of garden bed & lawn outside Administration Building | Landscaping & Gardening | Grounds Maintenance | 338 | Pass | Pass | -2 | -1 | 116.5 | 2021-12-23 14:49 | 2022-01-04 17:00 | 2021-12-24 17:15 | 2022-01-04 17:00 | 2021-12-29 13:45 |  |  | 2 x Call OutsPipe Fittings & Glue
MSA-DCA | WA5980123 | 0 | Critical Fire Protection & Training | Reception main fire- zone 14 alarm activating | Fire Protection Services | Fire Protection - Monitor System | 969.059 | Pass | Fail | 0 | 1 | 116.3333 | 2022-09-29 12:53 | 2022-09-29 14:53 | 2022-09-29 13:40 | 2022-09-29 16:53 | 2022-10-04 10:00 |  | WACCES | Attended site to investigate false alarm to fire panel. On arrival found previously activated detector in reset/normal and isolated condition. Checked history log to confirm isolated device was the activated device and found L1/S51 is device that caused false alarm.Physically investigated area zone 14 for access to detectors and to locate detector in alarm. After driving detector into alarm to identify which detector requires replacing found detector positioned directly above air handling ducting in loading bay. Due to location access articulating 12M boom required to access and replace detector with new. Detector L1/S51/Zn14 to remain isolated to eliminate any further false alarms until replacement can be conducted.
MSA-DTWD | WA6681984 | 2 | ECO PLUMBING AND GAS PTY LTD | Broken copper airline in U016 workshop. | Plumbing & Drainage | Water | 345.055 | Pass | Fail | 0 | 1 | 116.3333 | 2023-03-02 13:38 | 2023-03-08 17:00 | 2023-03-08 17:00 | 2023-03-08 17:00 | 2023-03-13 13:20 |  | WCAPPR
MSA-DTAG | WA5295588 | 3 | AWB Co. | Level 1 - Swipe reader unit removed – wall requires to be patched & painted | Painting | Internal | 552.4 | Pass | Pass | -1 | 0 | 116.25 | 2022-03-29 16:21 | 2022-04-05 17:00 | 2022-03-30 13:30 | 2022-04-05 17:00 | 2022-04-04 09:45 |  |  | Attended site patched hole in wall and paint to match
MSA-DTWD | WA5413858 | 2 | WESTERN IRRIGATION PTY LTD | Station 9 near fire pump station - Solenoid stuck - not closing | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 2629.19 | Pass | Pass | -1 | 0 | 116.2333 | 2022-05-12 14:15 | 2022-05-17 17:00 | 2022-05-12 14:16 | 2022-05-17 17:00 | 2022-05-17 10:30 |  |  | Investigate fault with station 9, return to site the following day with cable locator to assist in locating the faulty valve.Provide BRAF form to complete repairs.Carry out repairs and test for correct operation.
MSA-DTWD | WA6573508 | 3 | Equans Mechanical Services Australia | Aircon inoperative | Air Conditioning | Ducted Split System | 487.68 | Pass | Pass | -1 | 0 | 116 | 2023-02-14 13:56 | 2023-02-21 17:00 | 2023-02-15 14:00 | 2023-02-21 17:00 | 2023-02-20 10:00
MSA-DTWD | WA5201123 | 2 | Protek 24/7 Building & Maintenance | Roof leak above desk | Roofing | Metal Roofing | 848.7 | Pass | Pass | -1 | 0 | 116 | 2022-03-02 11:44 | 2022-03-08 17:00 | 2022-03-03 13:45 | 2022-03-08 17:00 | 2022-03-08 09:45 |  |  | Repair Roof leak
MSA-DTWD | WA6543852 | 2 | BAKE-QUIP PTY LTD | Oven door - Broken left hand side - third one up | Equipment | Catering Equipment | 800 | Pass | Pass | -1 | 0 | 115.75 | 2023-02-10 08:52 | 2023-02-15 17:00 | 2023-02-10 14:45 | 2023-02-15 17:00 | 2023-02-15 10:30
MSA-DTWD | WA5115911 | 1 | Damian Rak Electrical Pty Ltd | BLD 837A - Male Toilet - Exhaust fan faulty | Electrical | General Electrical |  | Pass | Fail | 0 | 0 | 115.5 | 2022-02-11 10:05 | 2022-02-14 17:00 | 2022-02-11 16:00 | 2022-02-14 17:00 | 2022-02-16 11:30 |  |  | job completed - replace echaust fan
MSA-DTAG | WA5323835 | 3 | FSA (WA) Pty Ltd | Perth Magistrates Court - Level 6 - Zone 37, Plant Room - activated - see details below | Fire Protection Services | Fire Protection - Monitor System | 485.65 | Pass | Pass | -1 | 0 | 115.5 | 2022-04-13 11:13 | 2022-04-22 17:00 | 2022-04-14 12:30 | 2022-04-22 17:00 | 2022-04-19 08:00 |  |  | Attended site to investigate/replace smoke detector in level 6 plant room. Unable to access DD Conditioner. Arranged to re-attend when Mech company are present.Re-attended site, replaced 2 x smoke detectors and bases in Level 6 SAF unit Z37
MSA-DCA | WA6519875 | 1 | Protek 24/7 Building & Maintenance | Beside Library Café - Paver loose, is a safety hazard | Paving & Roadworks | Paving | 278.96 | Pass | Fail | 0 | 0 | 115.5 | 2023-01-27 08:15 | 2023-01-30 17:00 | 2023-01-27 14:00 | 2023-01-30 17:00 | 2023-02-01 09:30 |  | WACCES
MSA-DTAG | WA6393824 | 3 | Midolo Building Services | Level 7 & 14 - Hole in ceiling, water damage to ceiling tile (see notes) | Building | Ceiling | 217.89 | Pass | Fail | 0 | 0 | 115 | 2022-12-29 10:40 | 2023-01-06 17:00 | 2023-01-04 14:00 | 2023-01-06 17:00 | 2023-01-09 09:00 |  | WACCES
MSA-DTWD | WA6127485 | 1 | AHS Services WA Pty Ltd (Anchor) | North Block Sewer leaking out of external drain near N108 Courtyard | Plumbing & Drainage | Sewer Drains & Septic Systems | 835.995 | Pass | Fail | 0 | 1 | 115 | 2022-10-26 08:07 | 2022-10-27 17:00 | 2022-10-26 14:30 | 2022-10-27 17:00 | 2022-10-31 09:30 |  |  | Cleared blocked drain full of roots
MSA-DTWD | WA5801396 | 2 | Protek 24/7 Building & Maintenance | Door closer not working properly - see notes below | Building | Doors | 681.065 | Pass | Fail | -1 | 0 | 114.5 | 2022-08-31 16:04 | 2022-09-05 17:00 | 2022-09-01 14:00 | 2022-09-05 17:00 | 2022-09-06 08:30 |  | WACCES | Installed new door closer
MSA-DTWD | WA6130446 | 1 | Jako Industries Pty Ltd | Hopper 3 & Hopper 4 faults - see notes below | Equipment | Electrical Equipment |  | Pass | Fail | 0 | 1 | 114.5 | 2022-10-28 12:17 | 2022-10-29 12:17 | 2022-10-28 12:30 | 2022-10-29 12:17 | 2022-11-02 07:00 |  |  | Travelled to site and gained access. Cleared out hopper 4. Tested systems and running as normal.
MSA-DTWD | WA5204327 | 1 | AHS Services WA Pty Ltd (Anchor) | Kendrew- E-Block - Deli external gas smell in the morning, please investigate at 6.30 am | Plumbing & Drainage | Gas | 4546.025 | Pass | Fail | -1 | 0 | 114.5 | 2022-03-04 09:41 | 2022-03-08 17:00 | 2022-03-04 13:30 | 2022-03-08 17:00 | 2022-03-09 08:00 |  |  | Completed
MSA-DCA | WA6109061 | 1 | ACTION GLASS & ALUMINIUM | North entry glass sliding door (outer) -Seals at bottom of the sliding door broken | Glazing | Door Glass | 268.12 | Pass | Fail | 0 | 1 | 114.4167 | 2022-10-20 13:19 | 2022-10-21 17:00 | 2022-10-20 15:15 | 2022-10-21 17:00 | 2022-10-25 09:40 |  |  | ATTENDED SITEREMOVED BROKEN PART OF DOOR STRIP AND MADE SAFE WITH SAFETY FILMRETURNED LATER DATESUPPLIED & FIT NEW PLASTIC STRIP AND MOHAIR TO DOORPLUS SILICONE
MSA-DCA | WA6520173 | 0 | Protek 24/7 Building & Maintenance | Garden Bed inbetween Pollys Cafe & Library - Massive slab of stone hanging out - Please make safe | Building | General Building | 438.65 | Pass | Fail | 0 | 1 | 114.25 | 2023-01-27 11:33 | 2023-01-27 13:33 | 2023-01-27 12:45 | 2023-01-27 15:33 | 2023-02-01 07:00 |  | WACCES
MSA-DTWD | WA6668690 | 1 | Protek 24/7 Building & Maintenance | Rear Fence - Repair cut mesh fence | Building | Steel Fencing & Gates | 644.115 | Pass | Fail | 0 | 1 | 114.25 | 2023-02-22 11:10 | 2023-02-23 17:00 | 2023-02-22 15:45 | 2023-02-23 17:00 | 2023-02-27 10:00 |  | WACCES
MSA-DCA | WA5383286 | 1 | Critical Fire Protection & Training | EWIS fault and charger fail indicator lamps both active. | Fire Protection Services | Fire Protection - Monitor System | 621.55 | Pass | Fail | 0 | 1 | 114 | 2022-04-27 13:45 | 2022-04-28 17:00 | 2022-04-27 14:00 | 2022-04-28 17:00 | 2022-05-02 08:00 |  |  | Attend site 27th April investigate reported issue with EWIS.Fault finding and discovered issue with battery temperaturesensing on charger (1st floor)Collected parts/ reattend 2nd May supplied and replacedtemperature sensing componentry on battery all ok following.Faults all clear.
MSA-DTWD | WA6081306 | 1 | AWB Co. | Dishwasher located on the Sth Western end of the kitchen keeps tripping | Equipment | Cleaning Equipment | 389.27 | Pass | Fail | 0 | 1 | 114 | 2022-10-18 14:35 | 2022-10-19 17:00 | 2022-10-19 15:00 | 2022-10-19 17:00 | 2022-10-24 09:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. De energised board. Replaced faulty rcd for dishwasher. Re energised. Tested to see if spdihswasher was working as intended. It was. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5215722 | 1 | High Tech Pest Control | D1 External - Large population of bees, risk to staff/students. | Pest Control | General Pest | 998 | Pass | Fail | 0 | 1 | 113.75 | 2022-03-10 15:48 | 2022-03-11 17:00 | 2022-03-11 13:30 | 2022-03-11 17:00 | 2022-03-16 07:15 |  |  | Bee Treatment to D Block back right and side has been completed.
MSA-DTAG | WA6683666 | 0 | Midolo Building Services | Detention cells 2&4-Privacy screen needs to be secured - see notes | Building | Internal Walls |  | Fail | Fail | 0 | 1 | 113.75 | 2023-03-03 10:54 | 2023-03-03 12:54 | 2023-03-03 14:30 | 2023-03-03 14:54 | 2023-03-08 08:15
MSA-DTAG | WA6127014 | 2 | EASTERN HILLS ELECTRICAL SERVICE | Various locations - flickering lights - see notes | Electrical | Lighting, Internal | 455.11 | Pass | Fail | 0 | 1 | 113 | 2022-10-25 16:12 | 2022-10-28 17:00 | 2022-10-28 16:30 | 2022-10-28 17:00 | 2022-11-02 09:30 |  | WCAPPR | Replaced 1x LED batten, 2x Standard tubes, 2x LED tubes
MSA-DTAG | WA5677272 | 2 | AHS Services WA Pty Ltd (Anchor) | L1-youth justice-Water penetrations above ceiling space | Roofing | Metal Roofing | 440 | Fail | Fail | 4 | 5 | 112.4 | 2022-07-25 13:38 | 2022-07-28 17:00 | 2022-08-25 02:30 | 2022-07-28 17:00 | 2022-08-29 18:54 |  |  | Job was handed over to roof plumber
MSA-DTWD | WA5680754 | 3 | Equans Mechanical Services Australia | Unable to change lead lag status between boiler 1 and 2 | Mechanical Services | Boilers | 927.395 | Pass | Pass | -1 | 0 | 105 | 2022-07-27 15:39 | 2022-08-03 17:00 | 2022-07-28 08:00 | 2022-08-03 17:00 | 2022-08-01 17:00 |  |  | SEE REPORT
MSA-DTWD | WA5462257 | 3 | AWB Co. | Expo - A Block - repair Roof Leak over stairs in Expo | Building | General Building | 7503.26 | Fail | Fail | 6 | 7 | 104 | 2022-05-19 12:56 | 2022-05-26 17:00 | 2022-07-07 06:30 | 2022-05-26 17:00 | 2022-07-11 14:30 |  |  | works completed as per signature slips
MSA-DCA | WA5142300 | 1 | EQUANS Mechanical Services (WA) Pty Limited | First floor - Boardroom - Air-conditioning has been reported as not cooling. | Air Conditioning | Room Air Conditioners | 293.025 | Pass | Fail | 0 | 1 | 103.7167 | 2022-02-16 14:12 | 2022-02-17 17:00 | 2022-02-17 08:20 | 2022-02-17 17:00 | 2022-02-21 16:03 |  |  | Attended site gained access and carried out inspection of AHU 10 serving board room. System found to be receiving start signal but not operating. Carried out hard reset of VSD and control and comms restored. Unit started up and ran. Possible cause of this could be that comms was interrupted between bms and AHU field PCB card or the age of VSD could be a factor indicating it is starting to fail. Unit is currently operating without fault. Note the system air flow static pressure sensor was noted to not be registering correct set point. Icon logic controls to provide quote for replacement. Work area has been left tidy.
MSA-DFES | WA6516822 | 2 | Australian HVAC Services Pty. Ltd. | Ground - Room 9 (Dorm 2) - Air Conditioning Unit Leaking water on to floor - see notes | Air Conditioning | Ducted Split System | 684.94 | Pass | Fail | 0 | 1 | 103.6667 | 2023-01-23 15:40 | 2023-01-27 17:00 | 2023-01-27 08:00 | 2023-01-27 17:00 | 2023-01-31 15:40
MSA-DTWD | WA5201184 | 2 | Techworks Electrical | E Block - Walkway light not working | Electrical | Lighting, Internal | 1471.26 | Pass | Pass | -1 | 0 | 103.6333 | 2022-03-02 12:23 | 2022-03-08 17:00 | 2022-03-04 06:52 | 2022-03-08 17:00 | 2022-03-08 14:30 |  |  | Replaced halogen security lights for new LEDs in E block
MSA-DCA | WA5509549 | 1 | EQUANS Mechanical Services (WA) Pty Limited | BMS Switching - Humidity alarm for FSU8 - Centenary gallery | Air Conditioning | Building HVAC Maintenance (Major Plant) | 345.35 | Pass | Fail | 0 | 1 | 102.6333 | 2022-06-13 01:23 | 2022-06-13 17:00 | 2022-06-13 02:00 | 2022-06-13 17:00 | 2022-06-17 08:38 |  |  | Completed
MSA-DTWD | WA6358240 | 3 | AWB Co. | Faulty ceiling lights | Electrical | Lighting, Internal | 1378.27 | Pass | Pass | -1 | 0 | 102 | 2022-12-06 08:33 | 2022-12-13 17:00 | 2022-12-09 09:00 | 2022-12-13 17:00 | 2022-12-13 15:00 |  | WCAPPR | Attended site signed in jsa completed. Removed and replaced remaining lights as per scope of works.Tested operational. Job completed
MSA-DTWD | WA6682126 | 2 | AWB Co. | O block - West Path - Damaged Pit Lids | Building | General Building | 1415.63 | Pass | Pass | -1 | 0 | 102 | 2023-03-02 16:09 | 2023-03-08 17:00 | 2023-03-03 09:00 | 2023-03-08 17:00 | 2023-03-07 15:00 |  | WCAPPR
MSA-DFES | WA6130550 | 3 | Protek 24/7 Building & Maintenance | Ablutions outside Reception-There is a hole in the wall behind the door in the male toilet | Building | Internal Walls | 317.23 | Pass | Pass | -1 | 0 | 101.5 | 2022-10-28 12:55 | 2022-11-04 17:00 | 2022-10-31 09:00 | 2022-11-04 17:00 | 2022-11-04 14:30 |  |  | Patch and paint hole in wall
MSA-DTWD | WA6680896 | 2 | AWB Co. | Faulty Dust extraction Ducting Direction Gates | Electrical | General Electrical | 323.96 | Pass | Pass | -1 | 0 | 101 | 2023-03-01 16:14 | 2023-03-07 17:00 | 2023-03-03 08:00 | 2023-03-07 17:00 | 2023-03-07 13:00 |  | WCAPPR
MSA-DTWD | WA5384329 | 3 | Equans Mechanical Services Australia | Spray booth extraction fan not working | Equipment | Electrical Equipment | 706.39 | Pass | Pass | -1 | 0 | 100.8333 | 2022-04-28 11:54 | 2022-05-05 17:00 | 2022-04-29 08:00 | 2022-05-05 17:00 | 2022-05-03 12:50 |  |  | 29th: Checked over the exhaust fan on the roof, Checked the wiring , need more wiring diagrams to help with chasing the problem. Couldn't get info as staff had gone home , will return.Job taken over by another tech V BELT REPLACED AND INVESTIAGTION INTO ELECTRICAL ISSUE - FIXED FAULT
MSA-DTWD | WA5689941 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet Ground Floor West Block not working | Plumbing & Drainage | Toilets/Cisterns | 532.57 | Pass | Fail | 0 | 0 | 100.5167 | 2022-08-02 15:28 | 2022-08-05 17:00 | 2022-08-04 11:30 | 2022-08-05 17:00 | 2022-08-08 16:01 |  |  | Job completed
MSA-DTWD | WA5081495 | 2 | M Construction (WA) | North side of entry car park - see notes below | Paving & Roadworks | Asphalt | 630.97 | Fail | Fail | 0 | 1 | 100.25 | 2022-01-20 14:41 | 2022-01-25 17:00 | 2022-01-28 10:15 | 2022-01-25 17:00 | 2022-02-01 14:30 |  |  | Located hole near car park. Mentioned to Dave that it needs further investigation for a potential leak underneath, but Dave advised to repair. Infilled with sand and stone
MSA-DCA | WA5257665 | 2 | Techworks Electrical | Bollards - lights are dim - contractor onsite | Electrical | General Electrical | 1347.5 | Pass | Fail | 0 | 0 | 100 | 2022-03-17 13:13 | 2022-03-22 17:00 | 2022-03-21 08:00 | 2022-03-22 17:00 | 2022-03-25 12:00 |  | WACCES | Repaired led lights and installed buzzers onto system to alert people when the bollards lower and raise up
MSA-DTWD | WA5381781 | 1 | Lane's Plumbing | BLD 833 - Kitchen - Ring main faulty | Plumbing & Drainage | Materials |  | Pass | Fail | 0 | 0 | 100 | 2022-04-26 11:35 | 2022-04-27 17:00 | 2022-04-26 12:00 | 2022-04-27 17:00 | 2022-04-30 16:00 |  |  | job completed - ring main replaced
MSA-DTWD | WA5987736 | 3 | COMMERCIAL PLUMBING AND GAS | Toilet leaking | Plumbing & Drainage | Toilets/Cisterns | 1987.65 | Pass | Fail | 0 | 1 | 100 | 2022-10-03 13:50 | 2022-10-10 17:00 | 2022-10-10 12:00 | 2022-10-10 17:00 | 2022-10-14 16:00 |  |  | replaced wall mounted pan inc required modifications
MSA-DTWD | WA5399171 | 3 | Falcetta Plumbing and Gas | Level 1 - Chiller Plantroom - Water leak from pipework connection to filter | Plumbing & Drainage | Water | 166.98 | Pass | Fail | 0 | 1 | 99.5 | 2022-05-09 16:36 | 2022-05-16 17:00 | 2022-05-16 16:00 | 2022-05-16 17:00 | 2022-05-20 19:30 |  |  | repaired connection fitting
MSA-DFES | WA5795603 | 3 | AWB Co. | L1-room 7-Duty room fire door to engine room is splitting along doors front edge-see notes | Building | Doors | 669.81 | Pass | Fail | 0 | 1 | 99.5 | 2022-08-25 13:43 | 2022-09-01 17:00 | 2022-09-01 15:00 | 2022-09-01 17:00 | 2022-09-05 18:30 |  |  | adjusted strike platereinforced cracked part of the door
MSA-DTAG | WA6020286 | 3 | Midolo Building Services | Main Entrance - Waste bin has detached from wall | Building | General Building | 524.66 | Pass | Pass | -1 | 0 | 99.5 | 2022-10-13 11:57 | 2022-10-20 17:00 | 2022-10-14 07:00 | 2022-10-20 17:00 | 2022-10-18 10:30 |  | WACCES | BIN HAS BEEN REMOVED PATCH & PAINT DONE
MSA-DTWD | WA6544291 | 1 | Protek 24/7 Building & Maintenance | Ground - B/C Block - Fire Exit door harden to open and close | Building | Fire Door | 1246.05 | Pass | Fail | 0 | 1 | 99.25 | 2023-02-10 11:28 | 2023-02-13 17:00 | 2023-02-13 08:00 | 2023-02-13 17:00 | 2023-02-17 11:15 |  | WACCES
MSA-DFES | WA4991047 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Female Firefighters Toilet - Exhaust Fan is noisy | Electrical | General Electrical | 419.81 | Pass | Fail | 0 | 0 | 99 | 2022-01-04 14:22 | 2022-01-07 17:00 | 2022-01-06 12:00 | 2022-01-07 17:00 | 2022-01-10 15:00 |  |  | Arrived on site at 13:15 to investigate exhaust fan not working located female toilets. Found exhaust fan was not working correctly and collected parts from nearest wholesaler and installed and tested. Left site at 15:00
MSA-DTWD | WA5790644 | 2 | Lane's Plumbing | Stand Pipe to the side of furniture shed - Faulty Valve | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 0 | 99 | 2022-08-22 11:45 | 2022-08-25 17:00 | 2022-08-22 14:00 | 2022-08-25 17:00 | 2022-08-26 17:00 |  |  | RETURN MODIFY PIPEWORK AND REPLACE VALVES
MSA-DCA | WA6298308 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Rear of transformer room-Water ingress from pipe into transformer room-see notes | Air Conditioning | Room Air Conditioners | 954.67 | Pass | Fail | 0 | 0 | 99 | 2022-12-01 08:56 | 2022-12-02 17:00 | 2022-12-01 13:00 | 2022-12-02 17:00 | 2022-12-05 16:00 |  |  | DAIKIN DUCTED SPLITS LEAKING WATER INTO FREO PORTS TRANSFORMER ROOM. ACCESSED DRAIN OUTSIDE TRANSFORMER ROOM AND WITH ASSISTANCE, EXTENDED DRAIN FROM INSIDE CAVITY TO OUTSIDE EXTERNAL WALL. WITH HOLE SAW DRILLED HOLE TO RUN DRAIN OUT AND DOWN CORRUGATED WALL. USED 40MM PVC TO CONNECT ELBOWS AND UNIONS, GLUED ALL SECTIONS TOGETHER AFTER MEASURING. MOUNTED DRAIN AND SADDLED TO CORRUGATION SO IT WON'T MOVE OR OBSTRUCT ANYTHING. TOOK PHOTO ON COMPLETION OF WORKS AND ADVISED PEY-SUE OF WORKS CARRIED OUT.
MSA-DTWD | WA6578333 | 2 | Australian Airconditioning Services Pty Ltd | Roof Plant Deck - CBs tripping and blown fuse- See notes | Air Conditioning | Room Air Conditioners | 1623.02 | Pass | Fail | 0 | 0 | 99 | 2023-02-15 09:11 | 2023-02-20 17:00 | 2023-02-17 07:30 | 2023-02-20 17:00 | 2023-02-21 10:30
MSA-DTWD | WA5141743 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 2 - B208 - Zip Boiler leaking into cupboard | Plumbing & Drainage | HWS/Units Electric & Gas | 1546.49 | Pass | Fail | 0 | 1 | 98.5 | 2022-02-16 12:11 | 2022-02-21 17:00 | 2022-02-21 08:00 | 2022-02-21 17:00 | 2022-02-25 10:30 |  |  | New unit required , awaiting approval to replaceCollected new unit accessed site removes faulty unit installed new, waited for calibration all good
MSA-DTWD | WA6129116 | 2 | Techworks Electrical | faulty light flickering | Electrical | Lighting, Internal | 336.735 | Pass | Pass | -1 | 0 | 98.5 | 2022-10-27 11:14 | 2022-11-01 17:00 | 2022-10-27 12:00 | 2022-11-01 17:00 | 2022-10-31 14:30 |  |  | Replaced tubes in c120 Replaced light fitting on ground floor kitchen Investigated lights not working on ground floor and first floor in C Block Found lights were plugged into 413 in roof space that had no power re plugged lights into other 413s that were part of the existing lighting circuit in hallwayMaterial used 2x 36w 840 tubes 2x s10 starters1x led panel 1200x300
MSA-DTWD | WA6257301 | 3 | COMMERCIAL PLUMBING AND GAS | ground-6F47 workshop-Sump from sinks to drain blocked | Plumbing & Drainage | Drainage | 1669.285 | Pass | Pass | -1 | 0 | 98.5 | 2022-11-24 13:56 | 2022-12-01 17:00 | 2022-11-25 09:00 | 2022-12-01 17:00 | 2022-11-29 11:30 |  |  | unblocked with drainsflush to scour
MSA-DTWD | WA5090557 | 3 | AWB Co. | S Block - Level 1 - S105 & S107 - desk edges have come off 10 desks | Building | General Building | 691.625 | Pass | Pass | -1 | 0 | 98.25 | 2022-01-25 13:44 | 2022-02-02 17:00 | 2022-01-27 13:15 | 2022-02-02 17:00 | 2022-01-31 15:30 |  |  | Attended site filled out JSA, cut measured all trims, glued with contact adhesive and trimmed around edges with router. Job completed
MSA-DTAG | WA5974468 | 1 | AHS Services WA Pty Ltd (Anchor) | Basement - Gas Kitchen (Plumbing Duct) - Water pipe valves above floor slab have seized - See notes | Plumbing & Drainage | Water | 292.795 | Pass | Pass | -1 | 0 | 98.25 | 2022-09-23 12:08 | 2022-09-27 17:00 | 2022-09-23 12:15 | 2022-09-27 17:00 | 2022-09-27 14:30 |  |  | Sprayed valves in duct in basement g4s kitchen
MSA-DFES | WA6257509 | 2 | Seme Solutions Pty Ltd | Engine Room - Alarm system keeps on activating for no reason. | Security | Monitoring | 507.74 | Pass | Fail | 0 | 0 | 98.25 | 2022-11-24 16:20 | 2022-11-29 17:00 | 2022-11-28 12:00 | 2022-11-29 17:00 | 2022-12-02 14:15 |  | WACCES | Replaced Zone 5 PIR (truck Shed Entry) Recomissioned and tested operational ok
MSA-DFES | WA6362881 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Room 33,13,9,5 - Multiple lights not serviceable | Electrical | Lighting, Internal | 1397.51 | Pass | Pass | -1 | 0 | 98.25 | 2022-12-09 14:30 | 2022-12-16 17:00 | 2022-12-12 09:45 | 2022-12-16 17:00 | 2022-12-16 12:00 |  |  | Matthew Kenney (12/12/2022) - Work NoteArrived onsite at 9:45 to repair/replace various faulty fittings throughout station, replaced faulty WP baton in Rm33 (tunic rm) with new led fitting, replaced faulty baton in rm 20 with new led fitting, replaced 1x 18w cfl lamp and 1x whole fitting at 2x faulty bunker lights rm 5 (veranda), replaced 1x 26w cfl lamp in rm 9, replaced 1x 26w cfl lamp in rm 10 and replace 1x 26w cfl lamp and 1x 10w es lamp in rm 13, have found multiple security lights out but have run out of time, spoke to staff and advised them that I will return and complete tomorrow, left site at 15:30.Matthew Kenney (16/12/2022) - Work NoteArrived onsite at 9.30 to repair 8x faulty security lights around station, replaced lamps at 2x security lights near carport, they are now working, replaced lamp at security light on exterior wall of engine bay fitting now works, 5x security light fittings have faulty ballasts, due to condition of existing lights i would recommend replacin
MSA-DTAG | WA6683507 | 2 | GPS Plumbing & Gas Services PtyLtd | cell 2-toilet plate is damaged - needs to be fitted with standard screws | Plumbing & Drainage | Toilets/Cisterns | 263.9025 | Pass | Pass | -1 | 0 | 98.25 | 2023-03-03 09:26 | 2023-03-09 17:00 | 2023-03-03 13:30 | 2023-03-09 17:00 | 2023-03-07 15:45
MSA-DCA | WA5081175 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 2- Plant Room - Black Swan - investigate control issue with fcu2.18 - please details | Air Conditioning | Building HVAC Maintenance (Major Plant) | 633.725 | Pass | Fail | 0 | 0 | 98 | 2022-01-20 11:36 | 2022-01-21 17:00 | 2022-01-20 14:00 | 2022-01-21 17:00 | 2022-01-24 16:00 |  |  | Investigated fcu 2.18 not getting an enable. Identified as a control issue, reset still not receiving an enable call. Honeywell attended site, investigated issue and rectified, all ok. Completed paperwork.
MSA-DTWD | WA5799766 | 1 | Schneider Electric Australia Pty Ltd | Control room - Access control cards not activating at East Perth Campus | Electrical | General Electrical |  | Fail | Fail | 0 | 1 | 98 | 2022-08-30 14:07 | 2022-08-31 17:00 | 2022-09-01 08:00 | 2022-08-31 17:00 | 2022-09-05 10:00 |  |  | Repairs
MSA-DTWD | WA6156376 | 2 | COMMERCIAL PLUMBING AND GAS | Double bowl sink between A256 & A257 very slow to drain away | Plumbing & Drainage | Water | 279.015 | Pass | Fail | 0 | 0 | 98 | 2022-11-09 07:37 | 2022-11-11 17:00 | 2022-11-10 17:00 | 2022-11-11 17:00 | 2022-11-14 19:00 |  |  | located and unblocked sink
MSA-DTWD | WA5490877 | 1 | AHS Services WA Pty Ltd (Anchor) | T-Block - Whole ground & 1st Floor - has no hot water | Plumbing & Drainage | HWS/Units Electric & Gas | 366.295 | Pass | Pass | -1 | 0 | 98 | 2022-06-03 10:01 | 2022-06-07 17:00 | 2022-06-03 13:00 | 2022-06-07 17:00 | 2022-06-07 15:00 |  |  | Investagated no hot water, had to get rheem.out on a service call due to faulty controllers. Hot water working correctly now
MSA-DFES | WA6020758 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | HWS is unserviceable, leaking, isolated at mains needs replacing. | Plumbing & Drainage | HWS/Units Electric & Gas | 1012.04 | Pass | Fail | 0 | 0 | 97.6 | 2022-10-13 19:05 | 2022-10-18 17:00 | 2022-10-17 07:34 | 2022-10-18 17:00 | 2022-10-21 09:10 |  |  | Arrived on site and singed in went to Hotwater unit located behind the BA room. Need to replaces a 50lt Dux por need a electrician to disconnect and reconnect and to shut of water and replace duro valve. Arrived on site and singed in went around the back of BA room and replaced a 50lt Termann hot water system put on new barcode on a Thermmann 50lt ( A40048612) old barcode A40437988W a old pro dux hot watersystem, could not work out how to put it on pro maps. Electrician will connect
MSA-DTWD | WA6154245 | 3 | Protek 24/7 Building & Maintenance | West End near garden - Hole cut in fence and section pulled up | Building | Steel Fencing & Gates | 500.985 | Pass | Pass | -1 | 0 | 97.5 | 2022-11-07 11:27 | 2022-11-14 17:00 | 2022-11-07 13:45 | 2022-11-14 17:00 | 2022-11-11 15:15 |  | WACCES | Install bottom rails, clamps and lace together. Drill holes and install barb wire
MSA-DCA | WA6544680 | 0 | EQUANS Mechanical Services (WA) Pty Limited | DO NOT Attend - First floor - Chiller No. 2 | Refrigeration | Chiller | 1714.01 | Pass | Fail | 0 | 1 | 97.5 | 2023-02-10 15:55 | 2023-02-10 17:55 | 2023-02-10 16:00 | 2023-02-10 19:55 | 2023-02-14 17:30
MSA-DTWD | WA5974327 | 1 | BJ SYSTEMS | Entrance - E-Block alarm panel not disarming the building | Security | Security Management System | 540 | Pass | Fail | -1 | 0 | 97.25 | 2022-09-23 10:24 | 2022-09-27 17:00 | 2022-09-23 16:15 | 2022-09-27 17:00 | 2022-09-27 17:30 |  |  | Drew Boyer (23/09/2022) - Attend site, called relevant personnel for access to system. Arranged for security to provide access to system, however, as this system is Gallagher (software based) system cannot be investigated as PC credentials are not known. Tracyupdated and will provide details/arrange for return next TuesdayDrew Boyer (27/09/2022) - Returned to site, investigated fault. Reset every controller on site and power cycled the dialler. System is functioning as intended
MSA-DTWD | WA5296267 | 2 | AHS Services WA Pty Ltd (Anchor) | Foyer area - Workshops the drinking fountain has a broken fawcet | Plumbing & Drainage | Water | 818.56 | Pass | Pass | -1 | 0 | 97.25 | 2022-03-30 10:51 | 2022-04-04 17:00 | 2022-03-31 12:45 | 2022-04-04 17:00 | 2022-04-04 14:00 |  |  | Completed
MSA-DCA | WA5053319 | 3 | GPS Plumbing & Gas Services PtyLtd | Studio underground - B1 - SU Female Bathrooms - Third tap from the entrance has a faulty sensor | Plumbing & Drainage | Materials | 513.7725 | Pass | Pass | -1 | 0 | 97.1667 | 2022-01-18 15:41 | 2022-01-25 17:00 | 2022-01-20 09:20 | 2022-01-25 17:00 | 2022-01-24 10:30 |  |  | Replaced mixer tap adjusted hole to suit new mixer
MSA-DCA | WA5069221 | 2 | Earth & Water Pty Ltd | Museum Plaza - Lawn - Underground Leak | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | -1 | 0 | 97.0333 | 2022-01-19 16:53 | 2022-01-24 17:00 | 2022-01-20 09:23 | 2022-01-24 17:00 | 2022-01-24 10:25 |  |  | job complete -
MSA-DTWD | WA5522426 | 1 | AWB Co. | AT102 - Dyno room tilt door has no power to isolator - door will not open | Electrical | General Electrical | 624 | Pass | Fail | 0 | 1 | 97 | 2022-06-15 15:29 | 2022-06-16 17:00 | 2022-06-16 14:00 | 2022-06-16 17:00 | 2022-06-20 15:00 |  | WCAPPR | Attended site signed in jsa completed. Installed new contactor in board. Contactor was stuck open and closing. Found fuse blown replaced. Wrong wiring on em lights fixed also as not getting power to correct terminals. Replaced e stop with new. ** job is not completed ***
MSA-DTWD | WA5752929 | 3 | Protek 24/7 Building & Maintenance | Carpark - Bollard in staff carpark area damaged | Building | Steel Work | 553.51 | Pass | Pass | -1 | 0 | 97 | 2022-08-17 12:52 | 2022-08-24 17:00 | 2022-08-18 12:00 | 2022-08-24 17:00 | 2022-08-22 13:00 |  |  | Bollard removed and returned to site
MSA-DTWD | WA5749293 | 2 | High Tech Pest Control | L1 kitchen roach issue | Pest Control | General Pest | 268.42 | Pass | Fail | 0 | 0 | 97 | 2022-08-17 08:46 | 2022-08-22 17:00 | 2022-08-19 07:45 | 2022-08-22 17:00 | 2022-08-23 08:45 |  |  | German cockroach infestation. Used Doxem delivery- no retreatment requried. See attached product information
MSA-DTWD | WA6509378 | 1 | AHS Services WA Pty Ltd (Anchor) | East Wing Ladies Toilets - Toilet pan wall seal leaking | Plumbing & Drainage | Toilets/Cisterns | 469.495 | Pass | Fail | 0 | 0 | 97 | 2023-01-20 09:59 | 2023-01-23 17:00 | 2023-01-20 13:00 | 2023-01-23 17:00 | 2023-01-24 14:00
MSA-DTAG | WA5791408 | 3 | GPS Plumbing & Gas Services PtyLtd | L1-Secure female staff toilets (next to Court 3 public gallery) no HW | Plumbing & Drainage | Water | 1058.34 | Pass | Pass | -1 | 0 | 96.8833 | 2022-08-23 07:02 | 2022-08-29 17:00 | 2022-08-25 13:45 | 2022-08-29 17:00 | 2022-08-29 14:38 |  |  | Inspected the hot water unit a new 25l hottie is required
MSA-DFES | WA5195733 | 0 | Go Doors | Door 1A - Appliance Bays - stuck i n partially open position and wont open or close | Building | Automatic Doors | 2077.5 | Pass | Fail | 0 | 1 | 96.75 | 2022-02-28 15:03 | 2022-02-28 17:03 | 2022-02-28 16:00 | 2022-02-28 19:03 | 2022-03-04 16:45 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5256732 | 1 | Protek 24/7 Building & Maintenance | Paddock Area - Area close to Iris street entrance - bollards removed from ground needs replacement | Building | Steel Fencing & Gates | 741.99 | Pass | Fail | 0 | 1 | 96.75 | 2022-03-17 08:15 | 2022-03-18 17:00 | 2022-03-18 10:15 | 2022-03-18 17:00 | 2022-03-22 11:00 |  | WACCES | Repair Bollards removed from ground
MSA-DTWD | WA5417565 | 1 | Protek 24/7 Building & Maintenance | Sunken and damaged brick paving between Blk 7 cafeteria and carpark 2 around drain and sewage pit | Flooring | Concrete | 614.125 | Pass | Fail | 0 | 1 | 96.75 | 2022-05-13 13:53 | 2022-05-16 17:00 | 2022-05-16 10:00 | 2022-05-16 17:00 | 2022-05-20 10:45 |  |  | Repair sunken pavers - remove and replace broken pavers
MSA-DTWD | WA6130532 | 3 | AWB Co. | Half lights out in Mine shaft | Electrical | Lighting, Internal | 1156.95 | Pass | Pass | -1 | 0 | 96.75 | 2022-10-28 12:48 | 2022-11-04 17:00 | 2022-10-31 11:45 | 2022-11-04 17:00 | 2022-11-04 12:30 |  | WCAPPR | Attended site and signed in. Completed JSA. Spoke to fm about job. Went to storeroom where we had stored parts for job and collected. Went to work area with 12ft ladder and set up securely. Isolated lighting circuit. Tested for dead. Took down old floodlight and replaced with new. Wired in PE Cell. Re energised and tested. Working as intended. Made pe cell water tight. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5611739 | 2 | AWB Co. | leaking roof | Building | Ceiling | 796.41 | Pass | Pass | -1 | 0 | 96.5167 | 2022-07-14 09:22 | 2022-07-19 17:00 | 2022-07-14 14:29 | 2022-07-19 17:00 | 2022-07-18 15:00 |  | WACCES | Investigated roof leakMade attempts to repair but weather conditions worsenedWill return on a dry day.Re-attended, stripped sections to allow more flow and re-sealed flashing
MSA-DTWD | WA5385223 | 2 | M Construction (WA) | S Block - S 007 - S Block Broken stair paver | Flooring | Concrete | 470.57 | Pass | Pass | -1 | 0 | 96.5 | 2022-04-29 08:22 | 2022-05-04 17:00 | 2022-04-29 12:30 | 2022-05-04 17:00 | 2022-05-03 13:00 |  |  | Drill out block paver, find new paver, clean out and glue in to set.
MSA-DTWD | WA6509351 | 3 | Protek 24/7 Building & Maintenance | Paving bricks lifting at entry causing trip hazard | Building | General Building | 728.58 | Pass | Pass | -1 | -1 | 96.5 | 2023-01-20 09:59 | 2023-01-30 17:00 | 2023-01-20 14:00 | 2023-01-30 17:00 | 2023-01-24 14:30 |  | WACCES
MSA-DTWD | WA6683654 | 0 | Precise Air Group | Library - D and C blocks - Chillers in Cand D blocks not running. | Air Conditioning | Ducted Split System | 658.78 | Pass | Fail | 0 | 1 | 96.3167 | 2023-03-03 10:49 | 2023-03-03 12:49 | 2023-03-03 12:00 | 2023-03-03 14:49 | 2023-03-07 12:19
MSA-DTWD | WA5081537 | 2 | M Construction (WA) | Kitchen Area - U-Block has a broken table leg in Kitchen area | Carpentry | Timber (all types) | 444.33 | Fail | Fail | 0 | 1 | 96.25 | 2022-01-20 15:21 | 2022-01-25 17:00 | 2022-01-28 09:45 | 2022-01-25 17:00 | 2022-02-01 10:00 |  |  | Attended site to repair broken table.
MSA-DTWD | WA6191161 | 2 | AWB Co. | Aroma cafe kitchen - AG10B - Bug zapper not working | Equipment | Electrical Equipment | 371.58 | Pass | Pass | -1 | 0 | 96.25 | 2022-11-16 13:18 | 2022-11-21 17:00 | 2022-11-17 12:30 | 2022-11-21 17:00 | 2022-11-21 12:45 |  | WACCES | Attended site and signed in. Completed jsa. Relocated bug zapper. Took down and stripped apart. Went to pro lamps for suitable tubes. Returned to site and replaced tubes and put fitting back together. Working as intended. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5794314 | 1 | Midolo Building Services | Ground - Basement - Closer on the back door is broken - Door will only open half-way | Building | Doors | 757.44 | Pass | Fail | 0 | 1 | 96.25 | 2022-08-24 13:53 | 2022-08-25 17:00 | 2022-08-25 08:30 | 2022-08-25 17:00 | 2022-08-29 08:45 |  | WACCES | new door closer installed
MSA-DCA | WA5413395 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Hot water is not working. The hot water system is located in the ground floor plant room. | Mechanical Services | Boilers | 215.715 | Pass | Fail | 0 | 0 | 96.1167 | 2022-05-12 10:47 | 2022-05-13 17:00 | 2022-05-12 13:03 | 2022-05-13 17:00 | 2022-05-16 13:10 |  |  | Checked water pump. Pump found to be offline again. Further investigation found that pump timer was fault. Timer has been replaced and operation restored. Will recheck during site PM inspection. Work area left tidy.
MSA-DTWD | WA6292811 | 1 | BAKE-QUIP PTY LTD | E Block - E58 - East end of kitchen - Combi Oven leaking a lot of water | Electrical | General Electrical | 574.6 | Fail | Fail | 1 | 2 | 96.0167 | 2022-11-29 13:18 | 2022-11-30 17:00 | 2022-12-09 12:15 | 2022-11-30 17:00 | 2022-12-13 12:16 |  |  | Refer to service report
MSA-DFES | WA5111596 | 0 | Critical Fire Protection & Training | Near BAT building - inground hydrant - is not turning off | Fire Protection Services | Fire Protection - Monitor System | 4850.31 | Fail | Fail | 0 | 1 | 96 | 2022-02-10 09:27 | 2022-02-10 11:27 | 2022-02-10 12:00 | 2022-02-10 13:27 | 2022-02-14 12:00 |  |  | Attended site and met with Julian who showed me to the damaged in ground hydrant.Isolated the pumps and removed the up stand.Found the spindle packing gland to be broken in half within the valve.The valve can not be individually isolated and the staff had advised me that they arecurrently doing exams which will lead to an extensive amount of water loss.Hand drained the area out around valve to take photos for quoting purposesWe will be required to cut the area of concrete around the valve and excavate down toit.Quote for these works to follow.Attended site and met with Julian who showed me to the damaged in ground hydrant.Isolated the pumps and removed the up stand.Found the spindle packing gland to be broken in half within the valve.The valve can not be individually isolated and the staff had advised me that they arecurrently doing exams which will lead to an extensive amount of water loss.Hand drained the area out around valve to take photos for quoting purposesWe will
MSA-DCA | WA5191805 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - investigate the RO tank overflowing | Air Conditioning | Room Air Conditioners | 606.975 | Pass | Fail | 0 | 0 | 96 | 2022-02-25 09:37 | 2022-02-28 17:00 | 2022-02-25 10:00 | 2022-02-28 17:00 | 2022-03-01 10:00 |  |  | Accessed plantroom and checked RO system, found the bypass solenoid slightly open continusly filling the tank. Drove to supplier to collect s new solenoid, returned to site, isolated mains water and replaced the solenoid. Carried out further investigation, it is recommended changing out the float trap valve for the steam generators as excessive water is being wasted.
MSA-DTWD | WA5494478 | 3 | AWB Co. | E101 - Light out | Electrical | General Electrical | 194.26 | Pass | Pass | -1 | 0 | 96 | 2022-06-07 15:47 | 2022-06-14 17:00 | 2022-06-10 10:00 | 2022-06-14 17:00 | 2022-06-14 10:00 |  | WCAPPR | Attended site signed In. Completed jsa. Replaced tubes and starters in light fitting. Light now working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5572877 | 3 | AWB Co. | Lighting faults | Electrical | Lighting, Internal | 779.89 | Pass | Fail | 0 | 0 | 96 | 2022-06-30 11:56 | 2022-07-07 17:00 | 2022-07-04 13:00 | 2022-07-07 17:00 | 2022-07-08 13:00 |  | WCAPPR | Attended site signed in jsa completed. replaced 30 tubes 36w. Replaced x6 18w plc 2p lamps.job is now completed
MSA-DCA | WA6108955 | 1 | Protek 24/7 Building & Maintenance | L2-Foyer – expansion gap. - Screw plates are missing from under brass plate on carpet. - see notes | Flooring | Carpet | 408.92 | Pass | Fail | 0 | 1 | 96 | 2022-10-20 12:25 | 2022-10-21 17:00 | 2022-10-21 08:30 | 2022-10-21 17:00 | 2022-10-25 08:30 |  | WACCES | Install new backing plates and check all others
MSA-DTWD | WA6190972 | 2 | Jako Industries Pty Ltd | Carpentry and joinery door U022 - Repair Hopper 5 not emptying | Equipment | Electrical Equipment |  | Pass | Pass | -1 | 0 | 96 | 2022-11-16 10:38 | 2022-11-21 17:00 | 2022-11-17 07:00 | 2022-11-21 17:00 | 2022-11-21 07:00 |  |  | Cleaned out hopper 5
MSA-DTAG | WA6256999 | 1 | Australian HVAC Services Pty. Ltd. | Level 1 - All Court Rooms - None of the air cons are working - See Notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1121.31 | Pass | Fail | 0 | 0 | 96 | 2022-11-24 11:00 | 2022-11-25 17:00 | 2022-11-24 12:00 | 2022-11-25 17:00 | 2022-11-28 12:00 |  |  | Attend site with icon logic. Access BMS and check programming of court 1 AHU 2 chilled water valve programming. Check valve to reverse action in program. Test operation at 0% then 100%. Found valve to now be working correctly. Carry out check on all court and waiting area valves. Found to work as normal. Check through BMS for any issues. Found all plant to be operating as normal.
MSA-DCA | WA6521480 | 2 | Earth & Water Pty Ltd | West of SLWA – by Birdbath - Garden not receiving water for tap timer | Plumbing & Drainage | Water |  | Fail | Fail | 1 | 1 | 96 | 2023-01-30 11:07 | 2023-02-02 17:00 | 2023-02-06 07:00 | 2023-02-02 17:00 | 2023-02-10 07:00
MSA-DFES | WA5396132 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Sewer pit - behind applied training - ablution block - full | Plumbing & Drainage | Sewer Drains & Septic Systems | 1773.97 | Pass | Fail | 0 | 1 | 95.9333 | 2022-05-06 08:38 | 2022-05-06 10:38 | 2022-05-06 09:05 | 2022-05-06 12:38 | 2022-05-10 09:01 |  |  | Located to site due to high level pump is going off opened the lid and found the pumps aren’t working tried everything but they are not pumping will return with a pump truck to get the water sucked out to inspect the pumps and have had the Permian by Tania .Returned back to site with wasteco and pumped out the water found the float was stuck down freed it was working correctly
MSA-DFES | WA5301862 | 3 | AWB Co. | Radio Comms Corner Office - One Ceiling Tile has a water stain from previously fixed roof leak | Building | Ceiling | 246.3 | Pass | Pass | -1 | 0 | 95.5333 | 2022-04-01 13:30 | 2022-04-08 17:00 | 2022-04-04 08:28 | 2022-04-08 17:00 | 2022-04-08 08:00 |  |  | roof leak rectified as per request
MSA-DCA | WA5588410 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plantroom Level 5 - Cooling System Alarm - is faulty | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2031.165 | Pass | Fail | 0 | 0 | 95.5 | 2022-07-07 16:07 | 2022-07-08 17:00 | 2022-07-07 16:30 | 2022-07-08 17:00 | 2022-07-11 16:00 |  |  | Refer to work logs. Airvision and Honeywell to quote up further repairs and new job to be raised.
MSA-DTWD | WA6108747 | 3 | COMMERCIAL PLUMBING AND GAS | Kitchen - Bad smell from sink - See notes below | Plumbing & Drainage | Water | 349.015 | Pass | Pass | -1 | 0 | 95.5 | 2022-10-20 10:47 | 2022-10-27 17:00 | 2022-10-21 16:00 | 2022-10-27 17:00 | 2022-10-25 15:30 |  |  | Repaired smelly sink and installed correct parts
MSA-DTWD | WA5980175 | 1 | BJ SYSTEMS | E & D Block - system not arming up | Security | Security Management System | 360 | Pass | Fail | 0 | 0 | 95.25 | 2022-09-29 13:11 | 2022-09-30 17:00 | 2022-09-29 15:45 | 2022-09-30 17:00 | 2022-10-03 15:00 |  |  | Drew Boyer (29/09/2022) - Attend site but access is impossible as no contacts are answering the phone. System is fine and arming this end, however D & E are not communicating through to monitoring. Return required Michael Peake (03/10/2022) - Attend site, signed in and notified ED Sec. Signed on to Gallagher and cleared all alarms, can see that multiple dial attempts have been unsuccessful. Went to dialler, powered down controller, powered back up, reprogrammed dialler and tested. Found this to be successful. Tested and confirmed alarms. All working ok
MSA-DTAG | WA5017150 | 0 | Sapio Pty Ltd | Door 19 - Custody - not opening electronically and have keys to open manually | Building | Security Doors | 390.26 | Fail | Fail | 0 | 1 | 95 | 2022-01-13 10:47 | 2022-01-13 12:47 | 2022-01-13 14:00 | 2022-01-13 14:47 | 2022-01-17 13:00 |  |  | Replaced monitor power supply and restored all clients to normal operating configuration. Custody Indigo Logon is now Custody01 for user custody. Bought 12v power supply from Altronics and camera monitor is up and running for Custody Intercom Door.
MSA-DTWD | WA5307271 | 2 | SCAVENGER SUPPLIES PTY LTD | CF3 - Fire alarm push button faulty | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | -1 | 0 | 95 | 2022-04-07 11:48 | 2022-04-12 17:00 | 2022-04-07 15:00 | 2022-04-12 17:00 | 2022-04-11 14:00 |  |  | completed 11/04/2022
MSA-DTAG | WA5413808 | 1 | Sapio Pty Ltd | Registry - Family Violence - Swipe access to doors won’t activate (lock or unlock) - See notes below | Security | Access Control | 446.1 | Pass | Fail | 0 | 0 | 95 | 2022-05-12 13:46 | 2022-05-13 17:00 | 2022-05-12 14:30 | 2022-05-13 17:00 | 2022-05-16 13:30 |  |  | Replaced Court 3 In-Session buttons. Reconfigured programming to suit new buttons. Disconnected button power frompanel. Tested ok. Adjusted external connection angel to cover gate , as per request.
MSA-DTWD | WA5660676 | 3 | AWB Co. | C11 - 2 light fittings not working possibly corroded inside | Electrical | Lighting, Internal | 484.27 | Pass | Pass | -1 | 0 | 95 | 2022-07-19 11:43 | 2022-07-26 17:00 | 2022-07-22 10:30 | 2022-07-26 17:00 | 2022-07-26 09:30 |  | WACCES | Attended site signed in jsa completed. Disconnected two lights and installed new weather proof light fittings which were on order. All tested and workingJob completed
MSA-DCA | WA6256785 | 2 | FCT SURFACE CLEANING | Ground - PCC Exterior - Graffiti Various Locations – see below | Cleaning | Graffiti |  | Pass | Pass | -1 | 0 | 95 | 2022-11-24 08:27 | 2022-11-29 17:00 | 2022-11-25 12:00 | 2022-11-29 17:00 | 2022-11-29 11:00 |  |  | Removal of graffiti
MSA-DTAG | WA6376421 | 3 | Midolo Building Services | L5-Jury room Court 57-Cabinet missing handle | Furniture | Office Furniture | 257.37 | Fail | Fail | 3 | 3 | 95 | 2022-12-15 15:10 | 2022-12-22 17:00 | 2023-01-09 14:30 | 2022-12-22 17:00 | 2023-01-13 13:30 |  | WACCES | HANDLES REPLACED
MSA-DTWD | WA6425395 | 1 | Protek 24/7 Building & Maintenance | Corridor & AG01, AG05 - Clean up & dry to lino and carpets after flooding of building | Flooring | Vinyl | 825.42 | Pass | Fail | 0 | 0 | 95 | 2023-01-12 09:47 | 2023-01-13 17:00 | 2023-01-12 12:00 | 2023-01-13 17:00 | 2023-01-16 11:00
MSA-DTAG | WA5796987 | 2 | Midolo Building Services | Level 4 - Court 41 - Judicial corridor is slamming door closer may be broken. | Building | Doors | 733.23 | Fail | Fail | 0 | 1 | 94.75 | 2022-08-26 16:05 | 2022-08-31 17:00 | 2022-09-02 10:00 | 2022-08-31 17:00 | 2022-09-06 08:45 |  | WACCES | new door closer installed
MSA-DTWD | WA5567165 | 3 | AWB Co. | 3B6 - auto workshop - Multiple faulty high bay lights | Electrical | Lighting, Internal | 4398.48 | Fail | Fail | 5 | 6 | 94.5 | 2022-06-23 15:54 | 2022-06-30 17:00 | 2022-08-05 10:30 | 2022-06-30 17:00 | 2022-08-09 09:00 |  | WCAPPR | Attended site signed in jsa completed. removed remaining lights in workshop. Disposed in metals bin as requested.installed two hi bays on engine room side. Put 20mm silver capping on unistrut to hide exposed cabling as requested by site. Put remaining 10 lengths in johns office and one hi bay left over wanted by site. Ewp offhiredJob is complete
MSA-DTWD | WA6126330 | 3 | AHS Services WA Pty Ltd (Anchor) | Cold water running unusually warm on all taps in Café and drinking fountain, | Plumbing & Drainage | Water | 163.3175 | Pass | Fail | 0 | 0 | 94.5 | 2022-10-25 11:27 | 2022-11-01 17:00 | 2022-10-31 09:30 | 2022-11-01 17:00 | 2022-11-04 08:00 |  |  | Returned to site to find job completed by different contractor
MSA-DTWD | WA5696072 | 3 | Australian Airconditioning Services Pty Ltd | B2123 International Office- E7 Fault showing on Split System AC | Air Conditioning | Room Air Conditioners | 1144.18 | Pass | Pass | -1 | 0 | 94.2833 | 2022-08-08 09:31 | 2022-08-15 17:00 | 2022-08-08 10:00 | 2022-08-15 17:00 | 2022-08-12 08:17 |  | WACCES | complete
MSA-DTWD | WA6113867 | 2 | JEM Carpentry | 843B - Faulty fascia and gutter | Roofing | Guttering |  | Pass | Fail | 0 | 0 | 94.25 | 2022-10-24 16:08 | 2022-10-27 17:00 | 2022-10-24 16:15 | 2022-10-27 17:00 | 2022-10-28 14:30 |  |  | Gutter maintenance
MSA-DTWD | WA5384401 | 0 | Critical Fire Protection & Training | The Whole Building - Fire Alarm has been activated - issue with EWIS system | Fire Protection Services | Fire Protection - Monitor System | 4103.58 | Pass | Fail | 0 | 1 | 94 | 2022-04-28 12:27 | 2022-04-28 14:27 | 2022-04-28 14:00 | 2022-04-28 16:27 | 2022-05-02 12:00 |  |  | Investigate EWIS issue.Attend site 2nd of May investigate EWIS issue on campus, foundEWIS in A, C,D block not operating as intended.Carried out further faultfinding, inspected A block found PSU notoperating correctly/damaged electronic componentry.PSU requires replacement.
MSA-DFES | WA5385995 | 3 | Critical Fire Protection & Training | 54 (Tower) - Lvl 2 - Tower (54) -see details below | Fire Protection Services | Fire Protection - Monitor System | 528.37 | Pass | Fail | 0 | 1 | 94 | 2022-04-29 14:12 | 2022-05-06 17:00 | 2022-05-06 14:00 | 2022-05-06 17:00 | 2022-05-10 12:00 |  |  | After investigation we determined that the leak was caused by a jumperwasher missing the backing nut which was causing the washer to not sitcorrectly.Sought approval from Critical Fire to replace hydrant head.Replaced hydrant head and coupling.All okay in departure.
MSA-DCA | WA5017444 | 2 | Earth & Water Pty Ltd | broken retic | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | -1 | 0 | 93.7667 | 2022-01-13 14:33 | 2022-01-18 17:00 | 2022-01-13 15:44 | 2022-01-18 17:00 | 2022-01-17 13:30 |  |  | - NOTE 33 hunter pros- 9 rainbird sprinklers- exposed where leak was supposed to be- noticed the leak was coming from sprinkler pooling.- noticed newly laid lawn had not been cut for 4 x sprinkler to pop up.- cut lawn so sprinklers could pop up- tested system- pooling fixed so backfilled and cleaned up- counted number of rainbird and hunter sprinklers- adjusted sprinklers- replaced mp1000 to a mp2000
MSA-DTWD | WA6540616 | 2 | AWB Co. | Rooms 1 - 5 - x12 Lights out | Electrical | Lighting, Internal | 1174.23 | Pass | Pass | -1 | 0 | 93.5 | 2023-02-09 12:14 | 2023-02-14 17:00 | 2023-02-10 12:00 | 2023-02-14 17:00 | 2023-02-14 09:30
MSA-DTWD | WA6578546 | 2 | Precise Air Group | aircon not working | Air Conditioning | Room Air Conditioners |  | Pass | Pass | -1 | 0 | 93.25 | 2023-02-15 10:20 | 2023-02-20 17:00 | 2023-02-16 09:00 | 2023-02-20 17:00 | 2023-02-20 06:15
MSA-DTWD | WA5101132 | 1 | M Construction (WA) | E18 Door has a broken hinge, needs middle and top hinges replaced | Building | Doors | 432.38 | Pass | Fail | 0 | 1 | 93.1667 | 2022-02-03 09:52 | 2022-02-04 17:00 | 2022-02-04 12:30 | 2022-02-04 17:00 | 2022-02-08 09:40 |  |  | Investigated door hinge. Is broken but secure. Will return to replace. Returned to site to replace with temporary parts as the required parts were unavailable. Parts ordered. Returned to replace with proper hinges.
MSA-DTWD | WA5378425 | 3 | AWB Co. | 4 x Bunker lights out on West Facing Exterior wall | Electrical | Lighting, External | 810.36 | Pass | Pass | -1 | 0 | 93 | 2022-04-20 14:03 | 2022-04-28 17:00 | 2022-04-22 14:15 | 2022-04-28 17:00 | 2022-04-26 11:15 |  |  | Attended site and signed in, reviewed JSA, spoke with fm about job isolated lighting circuit, mounted all lights to wall and fit off, re energised lighting, tested lights and they are working as intended, packed up, put all rubbish in the bin, completed paperwork , signed out , job complete
MSA-DTWD | WA5472111 | 1 | Falcetta Plumbing and Gas | External - C Block - blocked crate drain | Plumbing & Drainage | Drainage | 1463.84 | Pass | Fail | 0 | 0 | 93 | 2022-05-23 14:12 | 2022-05-24 17:00 | 2022-05-23 15:00 | 2022-05-24 17:00 | 2022-05-27 12:00 |  |  | unblocked drain at C block
MSA-DCA | WA5674844 | 1 | Critical Fire Protection & Training | Ground Floor - HBRC - Fire Panel - Issues with fire panel, see notes | Fire Protection Services | Fire Protection - Monitor System | 661.28 | Pass | Fail | 0 | 0 | 93 | 2022-07-21 14:37 | 2022-07-22 17:00 | 2022-07-21 15:00 | 2022-07-22 17:00 | 2022-07-25 12:00 |  |  | Adjustment completed during first attendance which rectified the issue but the issue returned.
MSA-DTAG | WA6000771 | 1 | Sapio Pty Ltd | Ground External - Staff Secure Parking - Car Park electronic gate is not working - See notes below | Security | Access Control | 1205.12 | Pass | Fail | 0 | 0 | 93 | 2022-10-10 10:15 | 2022-10-11 17:00 | 2022-10-10 14:30 | 2022-10-11 17:00 | 2022-10-14 11:30 |  | WACCES | closed off as per BRAF request
MSA-DTWD | WA6090909 | 2 | High Tech Pest Control | East entry - Bees under gutter / in top of wall | Pest Control | Specialist Pest | 425.25 | Pass | Pass | -1 | 0 | 93 | 2022-10-19 15:16 | 2022-10-24 17:00 | 2022-10-20 10:00 | 2022-10-24 17:00 | 2022-10-24 07:00 |  | WCAPPR | Returning 6am-7am 24/10/22 Monday with 2 techs and long ladder to reach area & eliminate bees.
MSA-DFES | WA5570207 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Storeroom - LED Tube replacement required in storeroom. | Electrical | Lighting, Internal | 334.185 | Pass | Fail | 0 | 1 | 92.75 | 2022-06-28 08:09 | 2022-07-01 17:00 | 2022-07-01 15:30 | 2022-07-01 17:00 | 2022-07-05 12:15 |  |  | Collected parts from nearest wholesaler at 10:30 and arrived onsite at 10:45. Removed faulty LED light and installed and tested new LED batten located storeroom. Notified staff of works completed and left site at 12:15
MSA-DFES | WA5216859 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - first light tanker charger is faullty | Electrical | General Electrical | 1385.251 | Pass | Fail | 0 | 1 | 92.75 | 2022-03-11 13:34 | 2022-03-11 15:34 | 2022-03-11 15:00 | 2022-03-11 17:34 | 2022-03-15 11:45 |  |  | Attend site 1500, called out to asses 12V transformer that has been moved to the floor of the garage to charge the Small Tankers, which has been a walkway hazard. Unable to action the job today as we will need to acquire the correct materials and an EWP to complete. Informed officers and left site 1630. 15/03/22 -Collected EWP and gear from workshop at 08:00, continued to site. Arrived at 08:40, installed 6mm cable from charger through ceiling to ceiling rose. Installed new 6mm flex dropper cable, remounted charger on wall. Tested with light tanker plugged in all okay. Left site at 11:45. Materials - 20m 6mm twin active, 8m 6mm twin flex cable, scissor lift and delivery. No signature as crews left for job.
MSA-DCA | WA6001264 | 0 | Automatic Fire Protection (ARA) | Fire panel in alarm | Fire Protection Services | Fire Protection - Monitor System | 990.81 | Fail | Fail | 0 | 1 | 92.5 | 2022-10-10 14:22 | 2022-10-10 16:22 | 2022-10-10 17:00 | 2022-10-10 18:22 | 2022-10-14 13:30 |  |  | On arrival, the beam detector on I/O L1 D55.1 Z3 was in alarm (due to dust from works) as was the fip mcp Z7 which had a broken glass andboth were isolated.The beam detector alarm would not reset despite dust from works having cleared. Inspected beam detector and it is in non-latching mode.There was scaffolding buttressed right up next to the beam sensor and possibly blocking its line of sight.Pushed scaffolding out of way but still wouldn’t reset.Pulled its 24v supply from the panel to shut it off then powered it back up and the alarm cleared.Didn’t have replacement glass for mcp (requires the wide glass -50mm high) so replaced with an Ampac resettable mcp.However on completion, the mcp sticks out too much for the panel.Reset the panel and all alarms are cleared. Deisolated beam and mcp and system is normal with no faults/isolations.REVISITRecommend either a thinner resettable mcp replacement or put original back in with a new glass. Have left original mcp inside panel.14/1
MSA-DTWD | WA5838617 | 1 | AWB Co. | Bay 13 - faulty 3 phase power socket | Electrical | General Electrical | 570.82 | Pass | Fail | 0 | 1 | 92.25 | 2022-09-08 15:37 | 2022-09-09 17:00 | 2022-09-09 15:30 | 2022-09-09 17:00 | 2022-09-13 11:45 |  | WCAPPR | Attended site and signed in. Completed jsa. Re located bay 13. Isolated power to 3 phase outlet by opening black box door above bay. Replaced old 3 phase outlet with new one. Tested for all correct voltages. Working as intended. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA6253584 | 2 | AWB Co. | N23 - damaged stop button cables to Dust extraction | Equipment | Electrical Equipment | 306.005 | Pass | Fail | 0 | 0 | 92.0167 | 2022-11-22 10:43 | 2022-11-25 17:00 | 2022-11-24 11:00 | 2022-11-25 17:00 | 2022-11-28 07:01 |  |  | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Upon investigation found to be that dust extraction was not in use. Site requested we tidy cables up and isolate machine. Cut cables. Placed conductors into connectors and into a wall mounted junction box.placed out of service tag inside box. Coiled redundant cables up and hung on side of machine. Tagged out circuit breaker. All left in a safe manner. Notified relevant personnel of works completed. **job complete**
MSA-DTAG | WA5780452 | 3 | Midolo Building Services | L4 female public toilet-Door closer damaged beyond repair. | Building | Doors | 777.24 | Pass | Pass | -1 | 0 | 92 | 2022-08-19 10:38 | 2022-08-26 17:00 | 2022-08-19 14:00 | 2022-08-26 17:00 | 2022-08-23 10:00 |  | WACCES | new door closer installed
MSA-DCA | WA5395292 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Air Conditioner 2 - VSD - running hot | Air Conditioning | Building HVAC Maintenance (Major Plant) | 619.98 | Pass | Fail | 0 | 1 | 92 | 2022-05-05 11:59 | 2022-05-05 13:59 | 2022-05-05 13:00 | 2022-05-05 15:59 | 2022-05-09 09:00 |  |  | During regular maintenance checks it was noticed the Ahu 2 variable speed drive was very hot. Upon further Investigation the main cooling drive was found to be faulty. Collected commercial fan, rcd and extension cord from supplier, returned to site, opened the variable speed drives front cover and set the fan to blow directly onto the vsd as temporary cooling. Parts are no longer available for the vsd. A new vsd and installation has been quoted for.
MSA-DTWD | WA5417308 | 3 | Falcetta Plumbing and Gas | Level 1 - Female Showers 1 -51 - Shower mixer valves out of calibration | Plumbing & Drainage | Water | 751.15 | Pass | Fail | 0 | 1 | 92 | 2022-05-13 11:51 | 2022-05-20 17:00 | 2022-05-20 15:00 | 2022-05-20 17:00 | 2022-05-24 11:00 |  | WACCES | replaced and adjusted tmv, adjusted other tmv
MSA-DCA | WA5693814 | 0 | EQUANS Mechanical Services (WA) Pty Limited | leak from one of the AHU 4 CHWV | Air Conditioning | Room Air Conditioners | 822.06 | Pass | Fail | 0 | 1 | 92 | 2022-08-04 15:40 | 2022-08-04 17:40 | 2022-08-04 16:00 | 2022-08-04 19:40 | 2022-08-08 12:00 |  |  | Accessed Ahu 4 and checked chilled water pipe work. Found water leaking from the gate valve and chilled water pipe work. Removed cladding and insulation and found the steel pipe heavly corded and rusted. Organised quote from contractors to replace the 36meters of steel pipework and replace with copper. Quote being prepared by supervisor.
MSA-DTWD | WA5491085 | 1 | Equans Mechanical Services Australia | Small fans on display fridge in cafeteria have failed, need to be replaced ASAP. | Refrigeration | Refrigerators | 733.94 | Pass | Pass | -1 | 0 | 91.9167 | 2022-06-03 12:09 | 2022-06-07 17:00 | 2022-06-03 13:35 | 2022-06-07 17:00 | 2022-06-07 09:30 |  |  | CHECKED OPERATION AFTER REPAIR- SETPOINT LOWERED TO 2DEG CYCLED OFF - ALL OK
MSA-DTWD | WA5111536 | 1 | Dormakaba Australia Pty Ltd | Block 9 - Level 1 - Main entrance - Automatic door not closing | Building | General Building | 428.83 | Pass | Fail | 0 | 0 | 91.7833 | 2022-02-10 08:58 | 2022-02-11 17:00 | 2022-02-10 15:13 | 2022-02-11 17:00 | 2022-02-14 11:00 |  |  | 10/2/22 - On inspection found that push button to exterior was sticking and broken which was causing door to stay open, please quote to supply and install new push button blank as requested by John, see attached photo.14/2/22 - Revisited site and installed 1 x push button switch to exterior to replace faulty one
MSA-DTWD | WA5290410 | 2 | M Construction (WA) | E-Block replace 2 broken hand towel dispensers above basins and repair holes in walls | Building | General Building | 565.81 | Pass | Pass | -1 | 0 | 91.5 | 2022-03-25 08:53 | 2022-03-30 17:00 | 2022-03-25 13:30 | 2022-03-30 17:00 | 2022-03-29 09:00 |  |  | Attended and investigated job, left site to source materials, returned to fill all holes in kitchen area with bog, installed two hand towel dispensers.
MSA-DTWD | WA6132124 | 0 | ACTION GLASS & ALUMINIUM | H2-smashed window | Glazing | Window Glass | 498.84 | Fail | Fail | 0 | 1 | 91.5 | 2022-10-31 11:55 | 2022-10-31 13:55 | 2022-10-31 14:30 | 2022-10-31 15:55 | 2022-11-04 10:00 |  |  | ATTENDED SITETEMP GLAZED BROKEN SIDELITE5.38 CLEAR LAMINATED SAFETY GLASS1-1160 X 229RETURNED LATER DATE TO REGLAZE8.38 CLEAR LAMINATED SAFETY GLASS1-1160 X 229
MSA-DTAG | WA5216844 | 1 | Midolo Building Services | Court room 1 - Leak in the roof - see notes below | Roofing | Metal Roofing | 491.29 | Pass | Fail | 0 | 0 | 91.25 | 2022-03-11 13:21 | 2022-03-14 17:00 | 2022-03-11 14:45 | 2022-03-14 17:00 | 2022-03-15 10:00 |  | WACCES | Repairs to roof leak completed
MSA-DTWD | WA6516328 | 2 | Securex Security Systems & Services | Fire door between 107 and 108 - Intruder alarm door sensor fallen out | Security | Security Management System | 363.27 | Pass | Fail | 0 | 1 | 91.25 | 2023-01-23 10:54 | 2023-01-27 17:00 | 2023-01-27 15:45 | 2023-01-27 17:00 | 2023-01-31 11:00
MSA-DTWD | WA5407647 | 2 | Equans Mechanical Services Australia | Level 4 - Plantroom - Boiler in alarm/tripped | Mechanical Services | Boilers | 921.94 | Pass | Pass | -1 | 0 | 91 | 2022-05-11 12:58 | 2022-05-16 17:00 | 2022-05-12 14:00 | 2022-05-16 17:00 | 2022-05-16 09:00 |  |  | ATTENDED SITE, SIGNED IN AND ACCESSED BUILDING B6 BOILER PLANTROOM. CHECKED THEBOILER AND FOUUD SYSTEM IN FAULT. RECORDED FAULT, RESET AND TESTED. NOTICED THEBOILER RUNNING LOUDER THEN NORMAL. CONTACTED BOILERTRONICS TO INVESTIGATEFURTHER.RETURNED TO SITE WITH BOILERTRONICS AND WAS NOTIFIED THE BEARINGS FOR THE FAN AREFAULTY. QUOTE WILL BE SENT THROUGH IN THE COMING WEEKS TO CARRY OUT REPAIRS.THIS CALL OUT IS COMPLETE. FURTHER WORKS IF APPROVED WILL NEED TO BE ON A NEW WA
MSA-DTWD | WA6560551 | 3 | ACTION GLASS & ALUMINIUM | Broken Slat window | Glazing | Window Glass | 393.995 | Pass | Pass | -1 | 0 | 91 | 2023-02-13 11:08 | 2023-02-20 17:00 | 2023-02-13 16:15 | 2023-02-20 17:00 | 2023-02-17 11:15
MSA-DTWD | WA5088701 | 2 | AWB Co. | Several faulty fluro tubes on high ceiling - see notes below | Electrical | Lighting, Internal | 263.3 | Pass | Fail | 0 | 0 | 90.75 | 2022-01-24 18:51 | 2022-01-28 17:00 | 2022-01-27 13:00 | 2022-01-28 17:00 | 2022-01-31 07:45 |  |  | Replaced faulty fluro lights as instructed by campus.works completed
MSA-DTWD | WA5460212 | 3 | Falcetta Plumbing and Gas | Male Student Toilet - Toilet Seat broken | Plumbing & Drainage | Toilets/Cisterns | 527.78 | Pass | Pass | -1 | 0 | 90.5 | 2022-05-18 11:58 | 2022-05-25 17:00 | 2022-05-20 16:30 | 2022-05-25 17:00 | 2022-05-24 11:00 |  | WACCES & WCAPPR | installed new seat and replaced 2nd
MSA-DFES | WA5797371 | 1 | WA BOILER SPARES & SERVICE | applied training ground - air shut down system has a leak in one of the tanks | Mechanical Services | Boilers | 998 | Pass | Fail | 0 | 1 | 90.5 | 2022-08-29 07:53 | 2022-08-29 17:00 | 2022-08-29 15:00 | 2022-08-29 17:00 | 2022-09-02 09:30 |  |  | Replaced faulty air reservoir on gas fired training pad
MSA-DTWD | WA5188602 | 2 | Techworks Plumbing | G1 staff room - G1 Node - Retic pipe leaking at roof level | Plumbing & Drainage | Water | 994.72 | Pass | Pass | -1 | 0 | 90 | 2022-02-23 10:07 | 2022-02-28 17:00 | 2022-02-24 14:30 | 2022-02-28 17:00 | 2022-02-28 08:30 |  |  | Rectified leaking reticulation on roof
MSA-DFES | WA5974537 | 0 | Protek 24/7 Building & Maintenance | Eastern end entry doors - Security door not latching - see notes below | Building | Security Doors | 239.78 | Fail | Fail | 0 | 1 | 90 | 2022-09-23 13:00 | 2022-09-23 15:00 | 2022-09-23 18:00 | 2022-09-23 17:00 | 2022-09-27 12:00 |  |  | Adjusted door closer , lubricated lock assembly
MSA-DTWD | WA5478826 | 1 | Dormakaba Australia Pty Ltd | Canteen - Canteen Sliding door is faulty | Building | Doors | 484.16 | Pass | Fail | 0 | 0 | 89.35 | 2022-05-26 13:58 | 2022-05-27 17:00 | 2022-05-26 15:22 | 2022-05-27 17:00 | 2022-05-30 08:43 |  |  | 26/5/22 - Attended site and found door to be operating ok, found floor guide loose and scraping on bottom of door, removed doors, tightened guide, refitted and adjusted door, replaced battery as requested by Kim, cleaned call sensors, checked boards and found mode connection board corroded which could be causing intermittent fault. Please quote to supply and install 1 x mode connection board, see attached photo30/5/22 - Inspected door and found mode board was corroded and faulty, replaced faulty board, tested door operation a number of times, all working fine.
MSA-DCA | WA6521842 | 3 | Protek 24/7 Building & Maintenance | External Grounds - A block & U block - Barbed wire needs repair/replace | Building | Steel Fencing & Gates | 840.75 | Pass | Fail | 0 | 0 | 89.25 | 2023-01-30 13:38 | 2023-02-06 17:00 | 2023-02-03 13:45 | 2023-02-06 17:00 | 2023-02-07 07:00 |  | WACCES
MSA-DTWD | WA5190782 | 1 | AWB Co. | 9G15 - Library work room - Emergency light not illuminated East exit. | Building | General Building | 964.055 | Pass | Fail | 0 | 0 | 81.25 | 2022-02-24 14:30 | 2022-02-25 17:00 | 2022-02-25 07:00 | 2022-02-25 17:00 | 2022-02-28 16:15 |  |  | Attended site and signed in. Completed JSA. Located library staff room with faulty exit sign. Ran new cable from board to exit light and terminated into exit sign. Put old cable in junction box and Made cable safe. Fed new cable down board. Terminated cable into test kit. Tested for correct operation. Notified of works completed. **job complete**
MSA-DTWD | WA5295246 | 2 | M Construction (WA) | D-Block - Canteen Kitchen - repair hole in wall above freezer | Building | General Building | 989.2 | Pass | Fail | 0 | 0 | 80.5 | 2022-03-29 12:03 | 2022-04-01 17:00 | 2022-04-01 07:00 | 2022-04-01 17:00 | 2022-04-04 15:30 |  |  | Repair hole and paint
MSA-DTWD | WA5513611 | 2 | JEM Carpentry | Front Porch - Porch ceiling faulty | Building | Ceiling |  | Fail | Fail | 9 | 9 | 80 | 2022-06-14 11:52 | 2022-06-17 17:00 | 2022-08-16 07:30 | 2022-06-17 17:00 | 2022-08-19 15:30 |  |  | Repairs to ceiling
MSA-DCA | WA5982660 | 3 | GPS Plumbing & Gas Services PtyLtd | Basement - Assembly Area - toilet bowl in 2nd cubicle from left | Plumbing & Drainage | Toilets/Cisterns | 2414.9625 | Pass | Pass | 0 | 0 | 79.6667 | 2022-09-30 13:18 | 2022-10-07 17:00 | 2022-10-04 07:50 | 2022-10-07 17:00 | 2022-10-07 15:30 |  | WACCES | Job completed as per Braf
MSA-DTWD | WA6301087 | 1 | AWB Co. | A107 - Bae Marie has stopped working | Electrical | General Electrical | 781.89 | Pass | Fail | 0 | 0 | 79.25 | 2022-12-02 13:27 | 2022-12-05 17:00 | 2022-12-05 09:15 | 2022-12-05 17:00 | 2022-12-08 16:30 |  | WACCES | Attended site and signed in, completed jsa, got keys from security, located Bain Marie, removed old elements and installed new elements, tested new elements, all working as intended, returned keys, signed out, completed paperwork, ***Job Complete***
MSA-DTWD | WA6155114 | 3 | AWB Co. | Towel rails have come away and need to be re - secured to wall | Building | Internal Walls | 225.96 | Pass | Fail | 0 | 0 | 78.75 | 2022-11-08 08:03 | 2022-11-15 17:00 | 2022-11-14 07:00 | 2022-11-15 17:00 | 2022-11-17 13:45 |  |  | Works completed
MSA-DTWD | WA6526765 | 2 | AWB Co. | Museum St courtyard - East block - Garden Bed lights out | Electrical | Lighting, External | 810.68 | Pass | Pass | 0 | 0 | 78.5 | 2023-02-01 10:38 | 2023-02-06 17:00 | 2023-02-03 10:00 | 2023-02-06 17:00 | 2023-02-06 16:30
MSA-DTWD | WA5481410 | 1 | Water2water Pty Ltd | W 109 and W 119 - Hot/cold water units not working | Plumbing & Drainage | Water | 904.8475 | Pass | Fail | 0 | 0 | 77.75 | 2022-05-30 13:01 | 2022-05-31 17:00 | 2022-05-31 10:45 | 2022-05-31 17:00 | 2022-06-03 16:30 |  | WACCES | -repaired zip unit in room w109 by replacing main board.-waiting for parts to repair zip unit in room w119.-Returned on 2/6/22 to replace main board on zip in w119 and noticed fan was very noisy when reassembled. 2.45pm - 4.15pm-Returned on 3/6/22 to replace noisy fan 4.00 - 4.30pm
MSA-DTWD | WA5413619 | 3 | Protek 24/7 Building & Maintenance | Water leak over new benchwork on northern side | Roofing | Metal Roofing | 403.75 | Pass | Pass | -1 | 0 | 77.5 | 2022-05-12 12:28 | 2022-05-19 17:00 | 2022-05-13 09:30 | 2022-05-19 17:00 | 2022-05-16 15:00 |  |  | Made temporary repair to roof leak - inspected for repair Braf Declined
MSA-DTWD | WA6535179 | 2 | Equans Mechanical Services Australia | Ground - F Block - Room F47 - Evaporative air conditioner not operating | Air Conditioning | Evaporative Coolers | 1431.6725 | Fail | Fail | 0 | 1 | 77.25 | 2023-02-06 14:58 | 2023-02-09 17:00 | 2023-02-10 09:45 | 2023-02-09 17:00 | 2023-02-13 15:00 |  | WACCES
MSA-DFES | WA5417626 | 2 | Protek 24/7 Building & Maintenance | Dorm 14 - Builder to look at render and paint from water damage on wall in dorm | Building | General Building | 1424.7 | Pass | Fail | 0 | 0 | 76.75 | 2022-05-13 14:27 | 2022-05-18 17:00 | 2022-05-17 08:00 | 2022-05-18 17:00 | 2022-05-20 12:45 |  |  | Record & Report
MSA-DCA | WA5491339 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant room (closest to wet room) - Indicator panel showing all red lights - See notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 554.65 | Pass | Fail | 0 | 0 | 76.5 | 2022-06-03 14:32 | 2022-06-07 17:00 | 2022-06-07 11:30 | 2022-06-07 17:00 | 2022-06-10 16:00 |  |  | See work logs
MSA-DCA | WA5688165 | 2 | SCAVENGER SUPPLIES PTY LTD | Ground Level - CEO’s Admin Office - Faulty Smoke detector | Fire Protection Services | Smoke and Heat Detection | 644.03 | Fail | Fail | 0 | 1 | 76.3833 | 2022-08-02 10:15 | 2022-08-05 17:00 | 2022-08-08 09:07 | 2022-08-05 17:00 | 2022-08-11 13:30 |  | WACCES | COMPLETED 11/08/2022-NOW ATTACHEDWork is scheduled for completion on 11/08/2022 to coincide with scheduled monthly servicing.11/08/2022claim resubmitted 29/08/2022
MSA-DCA | WA5289750 | 2 | Techworks Electrical | Power box vandalised – no power - see notes below | Electrical | General Electrical | 1165.1 | Pass | Pass | -1 | 0 | 76 | 2022-03-24 12:34 | 2022-03-29 17:00 | 2022-03-25 09:00 | 2022-03-29 17:00 | 2022-03-28 13:00 |  | WACCES | Replaced 2 x enclosures and internal components
MSA-DTAG | WA5401090 | 3 | Australian HVAC Services Pty. Ltd. | Level 8 - Aircon unit not working in Court 84 - no airflow | Air Conditioning | Room Air Conditioners | 298.26 | Pass | Pass | -1 | 0 | 76 | 2022-05-10 15:36 | 2022-05-17 17:00 | 2022-05-12 12:30 | 2022-05-17 17:00 | 2022-05-15 16:30 |  |  | Attend site. Access level 8 court 84 AC no airflow. Check temp and found to be 22.5 degrees. Check box and found actuator at minium airflow. Access level 6 and check bms. Check vav box serving court 84 and test operation of damper. Increase temp setpoint and found box to open to max airflow. Decrease temp setpoint and found box to drive to minium. Speak with building facilities and find out who put the call through and weather it was only airflow not temperature. Temperature appears to be fine. Security put the call through and need to be educated on how the system works . Increase in temp rise in airflow, decrease in temp drop in airflow. Access bms in Increase minium airflow setpoint to give a bit more air at minium. Will monitor operation.
MSA-MRWA | WA5780288 | 1 | EQUANS Mechanical Services (WA) Pty Limited | UPS auto dialer not working | Air Conditioning | Room Air Conditioners | 919.01 | Pass | Pass | 0 | 0 | 76 | 2022-08-19 09:10 | 2022-08-22 17:00 | 2022-08-19 12:00 | 2022-08-22 17:00 | 2022-08-22 16:00 |  |  | Attended call, carried out tests. Power failure tests worked. Others failed. Arranged for auto dealer tech to attended.
MSA-DTWD | WA5069040 | 1 | Equans Mechanical Services Australia | A Block - north side aircon not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 204.07 | Fail | Fail | 0 | 1 | 75.75 | 2022-01-19 14:07 | 2022-01-20 17:00 | 2022-01-21 10:15 | 2022-01-20 17:00 | 2022-01-24 14:00 |  |  | Completed findings found one room was set on heating mode unit had shut down at set point even though other controllers set on cooling. Readjusted setting monitored all OK. Cleaned up and completed paperwork and signed out.
MSA-DTWD | WA5214023 | 2 | AWB Co. | L009 - 2 pendant GPO's are faulty | Electrical | General Electrical | 957.09 | Pass | Fail | 0 | 0 | 75.75 | 2022-03-10 08:16 | 2022-03-15 17:00 | 2022-03-15 11:45 | 2022-03-15 17:00 | 2022-03-18 15:30 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm about job. Went to room where pendant GPOs were needing to be installed. Brought out all tools and equipment and set up. Spoke to lecturer and confirmed where he wanted the pendant GPOs to hang. Measure out length of flex that was needed to be cut. Replicated. Fit off both GPOs onto flex. Put glands on one way j box and drilled hole in back of j box for cables to enter on beams. Ran cable from board to where pendant GPOs were going. Measured out 2 lengths of jack chain suitable for cable, screwed jack chain to beam. Drilled through beam for cable to come in from behind. Fit off both j boxes and put covers on. Cable ties cable all way back to the board follow the same route as previous installs to make it look neat. De energised switchboard. Made sure was dead. Snaked down switchboard duct and got cable into board. Fit off cabling into spare RCD ( r9 ) . Put switchboard cover back on and re energised. Tested gpos and labelled. Ever
MSA-DTWD | WA5052719 | 3 | Protek 24/7 Building & Maintenance | Level 1 - E209 - Repair carpet warn under desks | Flooring | Carpet | 1680.25 | Pass | Fail | 0 | 0 | 75.5 | 2022-01-18 09:57 | 2022-01-25 17:00 | 2022-01-24 13:00 | 2022-01-25 17:00 | 2022-01-27 16:30 |  | WACCES | Repair Worn Carpet
MSA-DTWD | WA5186739 | 2 | AHS Services WA Pty Ltd (Anchor) | B block - ground floor - Mens toilet - Urinal flushing fault - overflowing when flushing | Plumbing & Drainage | Toilets/Cisterns | 342.7475 | Pass | Fail | 0 | 0 | 75.4 | 2022-02-22 09:01 | 2022-02-25 17:00 | 2022-02-25 09:45 | 2022-02-25 17:00 | 2022-02-28 13:09 |  |  | Found rught hand side urinal overflowing due to both being blocked and to much water.Installed valve to slow down pressure then used hot water to clear blockage.Returned to site to check-all working well
MSA-DCA | WA6544358 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 3 - Unit 3 - Aircon - Cracked unit | Air Conditioning | Room Air Conditioners | 931.22 | Pass | Fail | 0 | 0 | 75.4 | 2023-02-10 12:13 | 2023-02-10 14:13 | 2023-02-10 12:30 | 2023-02-10 16:13 | 2023-02-13 15:54
MSA-DFES | WA6504414 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - 9 - Toilet Cistern leaking water on to floor | Plumbing & Drainage | Toilets/Cisterns | 614.44 | Pass | Fail | 0 | 0 | 75.3333 | 2023-01-19 15:50 | 2023-01-20 17:00 | 2023-01-20 07:40 | 2023-01-20 17:00 | 2023-01-23 11:00 |  | WACCES
MSA-DTWD | WA4991908 | 3 | AWB Co. | first floor - east passageway entry - faulty lights | Electrical | Lighting, Internal | 287.02 | Pass | Fail | 0 | 0 | 75.25 | 2022-01-05 13:55 | 2022-01-12 17:00 | 2022-01-10 13:15 | 2022-01-12 17:00 | 2022-01-13 16:30 |  | WCAPPR | Attended site and signed in. Completed JSA. Located faulty light panel. Set up work area with equipment and gear. Isolated lighting circuit. Took down old light. Mounted bracket for new panel. Fitted off plug base and pit in roof. Plugged in light and made tidy in roof space. Slid light into position. Resecured everything. Re energised lighting circuit. Light is working as intended. Took picture of light. Completed paperwork. Signed out. ***Job complete***
MSA-DTWD | WA5100187 | 2 | AWB Co. | Spot welder damaged power cord | Electrical | General Electrical | 264.78 | Pass | Pass | 0 | 0 | 75.25 | 2022-02-02 11:35 | 2022-02-07 17:00 | 2022-02-04 11:15 | 2022-02-07 17:00 | 2022-02-07 14:30 |  | WACCES | Attended site and signed in. Completed JSA. Spoke to fm about job. Located spot welder that needed reconnecting. Took off isolator cover. Terminated cables. Put cover back on. Put covers back onto welder. Turned on welder. Completed paperwork. Signed out. Job complete
MSA-DTAG | WA5379176 | 3 | Seme Solutions Pty Ltd | System is falsa alarming on multiple zones - see notes below | Security | Monitoring | 357.5 | Pass | Pass | -1 | -1 | 74.75 | 2022-04-21 09:00 | 2022-04-29 17:00 | 2022-04-21 13:15 | 2022-04-29 17:00 | 2022-04-24 16:00 |  |  | Attended site, contacted monitoring station to book site onto test. Gathered zones false alarming from monitoring station. Investigated zones: Z90 - Duress custody control - tested okay, looked to have been tested during the day. Z66 & 67 - Isolated zones, deisolated to test if they are at fault. Z69 - L1 Power room reed constant alarm - faulty resistor, replaced and tested, no longer false alarming.
MSA-DTWD | WA5674648 | 2 | AWB Co. | Roof Leak - Above panel sizing saw | Roofing | Metal Roofing | 299.345 | Pass | Pass | -1 | 0 | 74.75 | 2022-07-21 13:06 | 2022-07-26 17:00 | 2022-07-22 12:00 | 2022-07-26 17:00 | 2022-07-25 14:45 |  |  | Attended, required return visit. Vent leaking above sculpture room, sealed flashing and replaced some teks.
MSA-DTWD | WA5090038 | 0 | Critical Fire Protection & Training | Fire .Panel - Fault on fire panel | Fire Protection Services | Fire Protection - Monitor System | 2880.58 | Pass | Fail | 0 | 0 | 74.5 | 2022-01-25 09:04 | 2022-01-25 11:04 | 2022-01-25 09:30 | 2022-01-25 13:04 | 2022-01-28 12:00 |  |  | On arrival to site found zone 24 level 1 C valve room pressure switch in alarm.No reason for activation. Sprinkler system sitting at normal pressure and pump did not start.Suspect faulty pressure switch to be investigated further.Whilst onsite, also found a visual line fault on level 1 north. Checked all visual warning devices in this area and all appeared to be working.Will require further investigation.Whilst testing EWIS in all zone setting, the panel showed a charger fault and a battery fault.Will also require further investigation.EWIS PSU ISSUEVoltage from EV3000 regulator cards not within tolerance for charging/ operation.Require replacement x 2 cards include labour
MSA-DTWD | WA5193876 | 2 | Equans Mechanical Services Australia | Replace faulty thermostat | Air Conditioning | Room Air Conditioners | 638.16 | Pass | Fail | 0 | 0 | 74.5 | 2022-02-25 15:19 | 2022-03-02 17:00 | 2022-02-28 08:00 | 2022-03-02 17:00 | 2022-03-03 10:30 |  |  | This job is for building 6Attended site before normal class hours. Ran new sensor cable into room 251. Relocated sensor and wired new cable to suit. Blanked off old sensor point. Confirmed VAV 2-3 working and adjusting correctly to maintain temp set point. Work area left tidy VAV 4-6 sensor cable traced. Temps are currently stable in this area.
MSA-DTWD | WA6372930 | 2 | Lane's Plumbing | BLD 823,824,825 and 826-lounge-Remove faulty Gas Heaters and make pipework safe | Plumbing & Drainage | Gas |  | Fail | Fail | 5 | 5 | 74.5 | 2022-12-14 12:38 | 2022-12-19 17:00 | 2023-01-20 09:30 | 2022-12-19 17:00 | 2023-01-23 12:00 |  |  | Isolate and tag offRelieve gas pressure no naked flamesREMOVE OLD ROOM HEATERS ISOLATE PIPEWORK AND PATCH GYPROCK TO COTTAGES
MSA-DCA | WA6578587 | 2 | Earth & Water Pty Ltd | Francis st - retic zone 1 - mainline leak in retic system | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 74.4167 | 2023-02-15 10:39 | 2023-02-20 17:00 | 2023-02-17 08:35 | 2023-02-20 17:00 | 2023-02-20 11:00
MSA-DCA | WA5587802 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Building, Block or Unit Geology Building Level-Mezzanine Level Room/Office-Plant Room 04-BMS alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1758.365 | Pass | Pass | -1 | 0 | 74 | 2022-07-07 10:47 | 2022-07-12 17:00 | 2022-07-08 09:30 | 2022-07-12 17:00 | 2022-07-11 11:30 |  |  | Attended site and investigated humidifier alarms. Found humidifier 03-01 in cylinder fault. 03-02 current circuit fault. 03-05 in fill time-out fault on both tanks. Isolated power to humidifier 03-01 and checked tank and cleaned. Elements on tank are corroded and brittle, new tank required. Installed tank and restored power to unit. Fault cleared will quote replacement tank. Power cycled 03-02 and tested operation, all ok. Isolated 03-05 and checked both tanks drain points and solenoid operating correctly. Drains clear. Tanks filled and monitored. All faults cleared will confirm Monday.Returned to site. Checked over humidifiers in mezzanine plantroom. 03-01 faulted on current alarm, reset, all ok. 03-02 + 03-05 faulted on filling alarm. Checked supply water strainer and filter. Strainer clean, replaced filter. Bled air from system. Reset faults and tested operation, all ok. Alarms cleared from bms all units operating as required. Completed paperwork.
MSA-DTWD | WA4991900 | 3 | AWB Co. | Senior lecturers office - Faulty lights | Electrical | Lighting, Internal | 324.46 | Pass | Fail | 0 | 0 | 74 | 2022-01-05 13:47 | 2022-01-12 17:00 | 2022-01-10 13:00 | 2022-01-12 17:00 | 2022-01-13 15:00 |  | WACCES | Attended site, signed in,spoke to fm about job, went to lecturers office, isolated lights , removed old lights , replaced with new , disposed of old lights in skip bin, removed tubes and disposed in allocated box , re energised lights , tested lights and working as intended , cleaned up , packed up, completed paperwork .***job completed***
MSA-DTWD | WA5100057 | 2 | AWB Co. | GPO smashed on south wall taped up and made safe | Electrical | General Electrical | 438.59 | Pass | Pass | 0 | 0 | 74 | 2022-02-02 10:34 | 2022-02-07 17:00 | 2022-02-04 11:15 | 2022-02-07 17:00 | 2022-02-07 13:15 |  | WACCES | Attended site and signed in. Completed JSA. spoke to fm. Re Located smashed GPOs on wall. Went to wholesaler to pick up parts ( for 3 jobs ). Isolated power circuits. Made sure it was dead. Took off old isolators and mounted new ones. Connected up. Put covers on. Re energised circuits. Labelled isolators. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5203676 | 2 | AWB Co. | Room ET 13 - GPO faulty | Electrical | General Electrical | 1275.35 | Pass | Fail | 0 | 0 | 74 | 2022-03-03 15:09 | 2022-03-09 17:00 | 2022-03-08 12:00 | 2022-03-09 17:00 | 2022-03-11 14:00 |  |  | Attended site and signed in. Completed JSA. Installed new duct work and installed 2 additional gpos to avoid extension leads. Replaced 3 phase outlet in automotive air con room, replaced switch mech in eg07. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5548998 | 2 | Protek 24/7 Building & Maintenance | (1st Floor East End Stairwell) - Door through to air cages - unable to open door,handle needs repair | Building | Doors | 463.775 | Pass | Fail | 0 | 0 | 74 | 2022-06-17 11:53 | 2022-06-22 17:00 | 2022-06-20 07:30 | 2022-06-22 17:00 | 2022-06-23 09:30 |  |  | Replace door handle
MSA-DFES | WA5468634 | 0 | ACTION GLASS & ALUMINIUM | Engine Room Door - glass panel has smashed | Building | General Building | 960.25 | Pass | Fail | 0 | 0 | 73.9167 | 2022-05-20 11:21 | 2022-05-20 13:21 | 2022-05-20 12:15 | 2022-05-20 15:21 | 2022-05-23 14:10 |  | WACCES | ATTENDED SITEREGLAZED BROKEN PANEL TO ROLLER DOOR6.38 CLEAR LAMINATED SAFETY GLASS1-878 X 1645PLUS SILICONE AND ARRIS EDGESRETURNED LATER DATE SUPPLIED & FIT TINT FILM1-878 X 1645
MSA-DTWD | WA6158867 | 2 | Australian Airconditioning Services Pty Ltd | E67 - No power to wall Split AC unit - See Notes | Air Conditioning | Room Air Conditioners | 1059.11 | Pass | Pass | -1 | 0 | 73.75 | 2022-11-10 09:40 | 2022-11-15 17:00 | 2022-11-11 08:00 | 2022-11-15 17:00 | 2022-11-14 09:45 |  |  | complete
MSA-MRWA | WA6377102 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 - Starting relay is chattering | Refrigeration | Chiller | 469.67 | Pass | Pass | -1 | 0 | 73.7167 | 2022-12-16 11:06 | 2022-12-21 17:00 | 2022-12-16 12:50 | 2022-12-21 17:00 | 2022-12-19 14:33 |  |  | Attended call, had system shut down and tagged out. Engaged Airvision to investigate. System operating normally.
MSA-DCA | WA5112136 | 3 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Mezzanine - State Records Office kitchen - see details | Plumbing & Drainage | Materials | 297.4225 | Pass | Fail | 0 | 0 | 73.6667 | 2022-02-10 13:41 | 2022-02-17 17:00 | 2022-02-15 15:50 | 2022-02-17 17:00 | 2022-02-18 17:30 |  | WACCES & WCAPPR | Replaced ministop
MSA-DTWD | WA5106435 | 0 | Protek 24/7 Building & Maintenance | A9 - vandalized window | Building | Windows | 968.375 | Pass | Fail | 0 | 0 | 73.5 | 2022-02-07 08:16 | 2022-02-07 10:16 | 2022-02-07 10:15 | 2022-02-07 12:16 | 2022-02-10 11:45 |  | WACCES | vandalized window
MSA-DTWD | WA5288768 | 2 | JEM Carpentry | 837A - Faulty Pavers in front of pool fence and road | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 5 | 5 | 73.5 | 2022-03-23 13:15 | 2022-03-28 17:00 | 2022-04-29 06:30 | 2022-03-28 17:00 | 2022-05-02 08:00 |  |  | job completed - repair pavers
MSA-DTWD | WA5301553 | 1 | Protek 24/7 Building & Maintenance | fence line along Jarrah road - fence cut, please secure & repair | Building | Steel Fencing & Gates | 801.54 | Pass | Pass | 0 | 0 | 73.5 | 2022-04-01 10:18 | 2022-04-04 17:00 | 2022-04-01 14:15 | 2022-04-04 17:00 | 2022-04-04 15:45 |  |  | Repair vandalized fence
MSA-DTWD | WA6519846 | 1 | AWB Co. | Lights tripping out | Electrical | Lighting, Internal | 471.7425 | Pass | Fail | 0 | 0 | 73.5 | 2023-01-27 07:54 | 2023-01-27 17:00 | 2023-01-27 10:30 | 2023-01-27 17:00 | 2023-01-30 12:00 |  | WACCES
MSA-DTWD | WA5384578 | 3 | AWB Co. | Ceiling damaged due to water - See notes below | Building | Ceiling | 468.5 | Pass | Fail | 0 | 0 | 73 | 2022-04-28 13:57 | 2022-05-05 17:00 | 2022-05-03 08:00 | 2022-05-05 17:00 | 2022-05-06 09:00 |  |  | ceiling works completed
MSA-DTAG | WA5385391 | 1 | Sapio Pty Ltd | Level 4 -Room 46 Duress alarm faulty - not operational . | Security | Monitoring | 327.11 | Pass | Pass | 0 | 0 | 73 | 2022-04-29 09:43 | 2022-05-02 17:00 | 2022-04-29 14:00 | 2022-05-02 17:00 | 2022-05-02 15:00 |  |  | Replaced Duress Transmitter, programmed to system, tested OK.
MSA-DTWD | WA5413684 | 3 | Protek 24/7 Building & Maintenance | 5F11 - Water leak from light fitting at entry to classroom | Building | General Building | 272.5 | Pass | Pass | -1 | 0 | 73 | 2022-05-12 12:54 | 2022-05-19 17:00 | 2022-05-13 10:30 | 2022-05-19 17:00 | 2022-05-16 11:30 |  |  | Report Issue with leaking valley BRAF declined
MSA-DTWD | WA5548763 | 3 | Precise Air Group | N30A Toilet Exhaust Fan not running | Equipment | Electrical Equipment | 876.44 | Pass | Pass | -1 | 0 | 73 | 2022-06-17 09:27 | 2022-06-24 17:00 | 2022-06-20 09:00 | 2022-06-24 17:00 | 2022-06-23 10:00 |  |  | Return to site replaced 3 phase isolation switch that was water damaged with new one checked operation all running efficiently
MSA-DTAG | WA6253220 | 1 | Sapio Pty Ltd | Custody area - Basement control room - Gallagher Server in custody is not connecting - see notes | Security | Access Control | 462.68 | Pass | Fail | 0 | 0 | 73 | 2022-11-22 09:52 | 2022-11-23 17:00 | 2022-11-22 12:30 | 2022-11-23 17:00 | 2022-11-25 13:30 |  |  | Installed Gallagher patch and confirmed correct operation
MSA-DTWD | WA6504035 | 3 | Equans Mechanical Services Australia | T block - Level 3 - Chiller 1 & 2 flow switches are faulty | Refrigeration | Chiller | 1505.94 | Pass | Pass | -1 | -1 | 73 | 2023-01-19 13:00 | 2023-01-27 17:00 | 2023-01-20 11:00 | 2023-01-27 17:00 | 2023-01-23 12:00
MSA-DCA | WA6561033 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-AREA 2 E BLOCK ZN 29 PIR E BLOCK STORE 3-SEE NOTES | Security | Security Management System |  | Pass | Fail | 0 | 0 | 73 | 2023-02-12 12:41 | 2023-02-13 17:00 | 2023-02-13 16:30 | 2023-02-13 17:00 | 2023-02-16 17:30 | 1
MSA-DCA | WA5290660 | 2 | Protek 24/7 Building & Maintenance | Ropes that hold window open have snapped, window wont stay open. | Building | Windows | 909.45 | Pass | Fail | 0 | 0 | 73 | 2022-03-25 10:46 | 2022-03-30 17:00 | 2022-03-28 10:00 | 2022-03-30 17:00 | 2022-03-31 11:00 |  |  | Repair window opening ropes
MSA-DTWD | WA6602711 | 1 | AWB Co. | Room 108 & 113 - All lights not working (see notes) | Electrical | Lighting, Internal | 536.37 | Pass | Pass | 0 | 0 | 73 | 2023-02-17 11:40 | 2023-02-20 17:00 | 2023-02-17 13:45 | 2023-02-20 17:00 | 2023-02-20 14:45
MSA-DTWD | WA5289965 | 1 | AHS Services WA Pty Ltd (Anchor) | A block - Level 1 - Exterior - main retic pipe along Royal Street is leaking | Plumbing & Drainage | Water | 635.7825 | Pass | Fail | 0 | 0 | 72.5 | 2022-03-24 14:45 | 2022-03-25 17:00 | 2022-03-25 07:30 | 2022-03-25 17:00 | 2022-03-28 08:00 |  |  | Dug hole and found leak coming from retic solenoid.Met retic tech who replaced leaking parts.Returned to check and found hole back filled-cleaned up
MSA-DCA | WA5453294 | 0 | Protek 24/7 Building & Maintenance | Level 2 - Studio 3 - door not closing properly | Building | Doors | 383 | Pass | Fail | 0 | 0 | 72.5 | 2022-05-17 09:44 | 2022-05-17 11:44 | 2022-05-17 11:30 | 2022-05-17 13:44 | 2022-05-20 12:00 |  |  | Replace electric Lock on Studio door
MSA-DCA | WA5298141 | 2 | ADVANCED LOCK & KEY | Fiji Room - Ground – external- Alcove above Fiji Room - see details below | Security | Locksmith | 307.5 | Pass | Fail | 0 | 0 | 72.4167 | 2022-03-31 15:12 | 2022-04-05 17:00 | 2022-04-04 15:00 | 2022-04-05 17:00 | 2022-04-07 15:25 |  |  | Replace
MSA-DTWD | WA6000951 | 2 | BAKE-QUIP PTY LTD | kitchen-ROTEL oven "2" requires a technician to adjust the internal Drive shaft Mechanism-see notes | Electrical | General Electrical | 383.2 | Fail | Fail | 0 | 1 | 72.25 | 2022-10-10 11:24 | 2022-10-13 17:00 | 2022-10-14 10:30 | 2022-10-13 17:00 | 2022-10-17 10:45 |  |  | Refer to service report
MSA-DTWD | WA6673357 | 0 | Equans Mechanical Services Australia | outside room 229, water pouring from the ceiling | Air Conditioning | Room Air Conditioners | 174.555 | Pass | Fail | 0 | 0 | 72.25 | 2023-02-24 13:14 | 2023-02-24 15:14 | 2023-02-24 14:00 | 2023-02-24 17:14 | 2023-02-27 14:15
MSA-DTWD | WA5588358 | 2 | Protek 24/7 Building & Maintenance | Vinyl floor lifting at join to wet area | Flooring | Vinyl | 323.26 | Pass | Pass | -1 | 0 | 72.25 | 2022-07-07 15:10 | 2022-07-12 17:00 | 2022-07-08 12:15 | 2022-07-12 17:00 | 2022-07-11 12:30 |  |  | repaired vinyl Sealed gap between main floor and bathroom floor, site requested
MSA-DTAG | WA5312448 | 2 | Midolo Building Services | Waiting Area - Chair that is bolted to the floor has bolt missing - see notes below | Furniture | Office Furniture | 347.02 | Fail | Fail | 1 | 1 | 72 | 2022-04-11 14:02 | 2022-04-14 17:00 | 2022-04-19 10:45 | 2022-04-14 17:00 | 2022-04-22 10:45 |  | WACCES | repairs made to chair. New gas strut installed
MSA-DTWD | WA5674652 | 2 | AWB Co. | Roof Leak - From air conditioning duct | Roofing | Metal Roofing | 318.575 | Pass | Pass | -1 | 0 | 72 | 2022-07-21 13:10 | 2022-07-26 17:00 | 2022-07-22 13:30 | 2022-07-26 17:00 | 2022-07-25 13:30 |  |  | Attended, need to returned to seal flexible joint.
MSA-DTWD | WA6673328 | 2 | AWB Co. | Sensor light not working | Electrical | Lighting, Internal | 975.34 | Pass | Fail | 0 | 0 | 72 | 2023-02-24 12:42 | 2023-03-01 17:00 | 2023-02-27 13:00 | 2023-03-01 17:00 | 2023-03-02 13:00 |  | WCAPPR
MSA-DTWD | WA5765760 | 1 | Australian Airconditioning Services Pty Ltd | Kitchen extraction fan not working | Equipment | Electrical Equipment | 881.59 | Pass | Fail | 0 | 0 | 71.8333 | 2022-08-18 14:37 | 2022-08-19 17:00 | 2022-08-19 08:00 | 2022-08-19 17:00 | 2022-08-22 07:50 |  |  | complete
MSA-DTWD | WA5674596 | 2 | AWB Co. | U Block - Ground Floor - Furniture Trades Workshop - Water leak from air con duct on eastern side | Roofing | Metal Roofing | 294.065 | Pass | Pass | -1 | 0 | 71.75 | 2022-07-21 12:48 | 2022-07-26 17:00 | 2022-07-22 13:00 | 2022-07-26 17:00 | 2022-07-25 12:45 |  |  | Attended, required return. Sealed base flashing and flexible evap to duct joining bags.
MSA-DTWD | WA5105277 | 1 | Falcetta Plumbing and Gas | T Block - Ground - Café - Kitchen - Café kitchen sinks no hot water | Plumbing & Drainage | HWS/Units Electric & Gas | 1450 | Pass | Pass | 0 | 0 | 71.5 | 2022-02-04 09:13 | 2022-02-07 17:00 | 2022-02-04 15:30 | 2022-02-07 17:00 | 2022-02-07 15:00 |  |  | replaced 3x faulty pumps and check valves
MSA-DTWD | WA6693208 | 1 | AHS Services WA Pty Ltd (Anchor) | disabled male toilet-HWS has split and leaking-call Kim before attendance | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 71.5 | 2023-03-10 08:16 | 2023-03-13 17:00 | 2023-03-10 12:30 | 2023-03-13 17:00 | 2023-03-13 12:00
MSA-DCA | WA5567701 | 1 | Dormakaba Australia Pty Ltd | Batavia Gallery - Automated push door button has partly detached from the wall, difficult for use | Building | Automatic Doors | 588.54 | Pass | Pass | 0 | 0 | 71.3667 | 2022-06-24 11:35 | 2022-06-27 17:00 | 2022-06-24 13:01 | 2022-06-27 17:00 | 2022-06-27 12:23 |  |  | 24/6/22 - On inspection found push button mounting plate is damaged, temporarily fix the plate, revisit required to replace mounting plate, see attached photo.24/6/22 - Re attended site, replaced damaged mounting block, also found push button was sticking, replaced push button, tested door operation a number of times, left door in good working condition.27/6/22 - Inspected door and found there was no power to the doors, found that the circuit breaker is faulty, advised site to callout electrician.
MSA-DTWD | WA5094516 | 3 | AWB Co. | room A51 - Flashing Fluoro A Block 1st floor Tombstone broken | Electrical | General Electrical | 267.84 | Pass | Pass | 0 | 0 | 71.25 | 2022-01-31 11:48 | 2022-02-07 17:00 | 2022-02-04 10:30 | 2022-02-07 17:00 | 2022-02-07 09:45 |  | WACCES | Attended site and signed in, completed jsa, spoke to fm. Located faulty tombstone in light fitting. Isolated power to lights. Got tombstones from H block. Took off old tombstones and replaced with new. Replaced tubes and starters. Put light fitting back together. Re energised lighting circuit. Everything working as intended. Took pictures before and after. Completed paperwork. Signed out. *** job complete ***
MSA-DCA | WA5660586 | 2 | Protek 24/7 Building & Maintenance | Geologist Building - Level 1 - Cleaners Cupboard 6 - Damage to door frame , striker plate, & slot | Building | Doors | 345.115 | Pass | Pass | 0 | 0 | 71.25 | 2022-07-19 10:55 | 2022-07-22 17:00 | 2022-07-19 12:00 | 2022-07-22 17:00 | 2022-07-22 11:15 |  | WACCES | Repair damaged door frame
MSA-DTWD | WA6544292 | 2 | BAKE-QUIP PTY LTD | restaurant - kitchen Prover Oven the water tap does not work | Electrical | General Electrical | 540.65 | Pass | Fail | 0 | 0 | 71.25 | 2023-02-10 11:22 | 2023-02-15 17:00 | 2023-02-13 09:00 | 2023-02-15 17:00 | 2023-02-16 08:15
MSA-DTWD | WA5101350 | 2 | AWB Co. | Faulty light fitting in lecturers’ extraction hood | Electrical | Lighting, Internal | 714.275 | Pass | Fail | 0 | 0 | 71.0167 | 2022-02-03 11:29 | 2022-02-08 17:00 | 2022-02-07 07:00 | 2022-02-08 17:00 | 2022-02-10 06:01 |  | WACCES | Attended site and signed in. Completed JSA. Located store room with 2x faulty battens. Supplied and replaced with 2x new LED fittings. Tested to see if working correctly. Also inspected Bain Marie as lights were not working. Found to be 1x blown globe. Reported all to FM. FM will action further if need be. Packed up site **job complete**
MSA-DTAG | WA6520417 | 3 | Midolo Building Services | Court room 1 - Public Entry Door to Slams shut - see notes | Building | Doors | 297.48 | Fail | Fail | 1 | 2 | 71 | 2023-01-27 14:20 | 2023-02-03 17:00 | 2023-02-13 08:00 | 2023-02-03 17:00 | 2023-02-16 07:00
MSA-DTWD | WA5091621 | 2 | Falcetta Plumbing and Gas | Block 3 - Ground - Male toilets - urinal blocked | Plumbing & Drainage | Toilets/Cisterns | 703.84 | Pass | Pass | -1 | 0 | 71 | 2022-01-27 09:43 | 2022-02-01 17:00 | 2022-01-28 12:00 | 2022-02-01 17:00 | 2022-01-31 11:00 |  | WCAPPR | Drainsflush unblock urinals
MSA-DTWD | WA5715429 | 2 | AHS Services WA Pty Ltd (Anchor) | Metals welding area and cutting rooms. Drains are blocked | Plumbing & Drainage | Drainage | 1186.165 | Pass | Fail | 0 | 0 | 71 | 2022-08-12 15:17 | 2022-08-17 17:00 | 2022-08-16 13:00 | 2022-08-17 17:00 | 2022-08-19 12:00 |  |  | Drains are blocked due to metal cutting going down the drain. Unblocked drains for jetter
MSA-DTWD | WA6111927 | 2 | Techworks Electrical | hallway has a flickering light needs replacing | Electrical | Lighting, Internal | 743.07 | Pass | Fail | 0 | 0 | 71 | 2022-10-21 11:37 | 2022-10-26 17:00 | 2022-10-24 11:30 | 2022-10-26 17:00 | 2022-10-27 10:30 |  | WACCES | Replaced 2 light fittings in P Block
MSA-MRWA | WA6691006 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Meeting Room G04A/C showing error message - cant operate A/C due to error | Air Conditioning | Ducted Split System |  | Pass | Pass | -1 | 0 | 71 | 2023-03-09 15:17 | 2023-03-14 17:00 | 2023-03-10 10:30 | 2023-03-14 17:00 | 2023-03-13 09:30
MSA-MRWA | WA5570377 | 1 | Water2water Pty Ltd | Kitchen - hot water urn faulty | Plumbing & Drainage | Water | 434.395 | Pass | Fail | 0 | 0 | 70.9167 | 2022-06-28 10:28 | 2022-06-29 17:00 | 2022-06-28 13:10 | 2022-06-29 17:00 | 2022-07-01 12:05 |  |  | Replaced front facsia board and pcb
MSA-DTWD | WA5727909 | 3 | AWB Co. | Cable box in N102 pulled off the wall please repair/replace | Electrical | Distribution Board | 999.63 | Pass | Pass | 0 | 0 | 70.8667 | 2022-08-15 13:03 | 2022-08-22 17:00 | 2022-08-19 12:23 | 2022-08-22 17:00 | 2022-08-22 11:15 |  |  | Job complete
MSA-DTWD | WA6527986 | 2 | AHS Services WA Pty Ltd (Anchor) | Room A101 - Isolation valve not turning water supply off needs replacing | Plumbing & Drainage | Drainage | 591.7675 | Pass | Pass | -1 | 0 | 70.75 | 2023-02-02 08:06 | 2023-02-07 17:00 | 2023-02-03 11:00 | 2023-02-07 17:00 | 2023-02-06 09:45
MSA-DTWD | WA5094830 | 3 | AWB Co. | C Block - Ground - C47 - a flickering fluoro | Electrical | General Electrical | 332.96 | Pass | Pass | 0 | 0 | 70.75 | 2022-01-31 14:22 | 2022-02-07 17:00 | 2022-02-04 10:00 | 2022-02-07 17:00 | 2022-02-07 08:45 |  | WACCES | Attended site and signed in. Completed JSA. spoke to fm. Went over to C block, salon 2. Found there were a few tubes out and a few tubes a different colour. Went through and replaced all tubes to be all same colour. Took pictures before and after. Everything now working as intended. Completed paperwork. Signed out. *** Job complete ***
MSA-DTAG | WA5797767 | 1 | Midolo Building Services | Ground Floor - Exit Door to the building – Security check point - Faulty Door - See notes below | Building | Doors | 491.97 | Pass | Fail | 0 | 0 | 70.75 | 2022-08-29 10:17 | 2022-08-30 17:00 | 2022-08-29 12:15 | 2022-08-30 17:00 | 2022-09-01 11:00 |  | WACCES | door patched & painted. Door closer repaired
MSA-DTWD | WA5289711 | 2 | M Construction (WA) | Gate 1 - Signage - has been damaged and removed from ground | Signage | General Signage | 566.32 | Pass | Pass | -1 | 0 | 70.5333 | 2022-03-24 11:58 | 2022-03-29 17:00 | 2022-03-25 12:00 | 2022-03-29 17:00 | 2022-03-28 10:32 |  |  | Attend site and inspected damaged sign located gate one. Returned to site with materials and removed sign from old concrete, dig new holes, fix sign. Install sign with cement.
MSA-DTAG | WA5548933 | 0 | Sapio Pty Ltd | SAT hearing room doors (Public entrance and exit doors) Rooms: 3:01, 5:01 and 4:04 - see details | Security | Access Control | 444.88 | Pass | Fail | 0 | 0 | 70.5 | 2022-06-17 11:07 | 2022-06-17 13:07 | 2022-06-17 12:30 | 2022-06-17 15:07 | 2022-06-20 11:00 |  |  | Replaced egress switches in Rooms 3.01 & 5.01. All ok.
MSA-DTWD | WA6358278 | 2 | AWB Co. | Fan switch is faulty (see notes) | Electrical | General Electrical | 278.775 | Pass | Fail | 0 | 0 | 70.5 | 2022-12-06 08:42 | 2022-12-09 17:00 | 2022-12-09 14:30 | 2022-12-09 17:00 | 2022-12-12 13:00 |  | WCAPPR | Attended site signed in jsa completed. Removed old switch and installed new. Tested operational and showed staff how to use. Job completed
MSA-DTAG | WA5216659 | 1 | Seme Solutions Pty Ltd | Multi alarms being activated during work hours and after hours. | Security | Security Management System | 455 | Pass | Pass | 0 | 0 | 70.25 | 2022-03-11 11:57 | 2022-03-14 17:00 | 2022-03-11 14:30 | 2022-03-14 17:00 | 2022-03-14 12:45 |  |  | Located source on tamper 2123. Isolated camera, but will require further investigation with 2 techs and EWP.Camera wont cause further tampers as is isolated.
MSA-DTWD | WA5584770 | 3 | AWB Co. | Lighting faults | Electrical | Lighting, Internal | 1202.49 | Pass | Pass | -1 | 0 | 70 | 2022-07-05 10:19 | 2022-07-12 17:00 | 2022-07-08 12:30 | 2022-07-12 17:00 | 2022-07-11 10:30 |  | WCAPPR | Attended site signed in jsa completed. Replaced various tubes in B6 as per lighting list given to dave gaff.job completed
MSA-DFES | WA5697190 | 3 | Australian HVAC Services Pty. Ltd. | Lecture room 8 - Slow water drip from air conditioner in roof. see notes | Air Conditioning | Room Air Conditioners | 996.62 | Pass | Fail | 0 | 0 | 70 | 2022-08-09 07:28 | 2022-08-15 17:00 | 2022-08-15 12:30 | 2022-08-15 17:00 | 2022-08-18 10:30 |  |  | Leaks should be fixed error codes checked and cleared
MSA-DTWD | WA6518750 | 1 | COMMERCIAL PLUMBING AND GAS | High moisture content reported in concrete floor. Source to be investigated | Plumbing & Drainage | Drainage | 998.455 | Pass | Fail | 0 | 0 | 70 | 2023-01-25 10:49 | 2023-01-27 17:00 | 2023-01-25 14:00 | 2023-01-27 17:00 | 2023-01-28 12:00
MSA-DCA | WA6531581 | 2 | GPS Plumbing & Gas Services PtyLtd | Male Bathroom - Theatre Foyer - Urinal flush button faulty- needs to be held in to function properly | Plumbing & Drainage | Toilets/Cisterns | 1113.075 | Pass | Fail | 0 | 0 | 70 | 2023-02-03 13:06 | 2023-02-08 17:00 | 2023-02-07 11:15 | 2023-02-08 17:00 | 2023-02-10 09:15 |  | WCAPPR
MSA-DCA | WA6654649 | 2 | Critical Fire Protection & Training | Auto announcement module - Main Fire Panel - not working | Fire Protection Services | Fire Protection - Monitor System | 429 | Pass | Pass | 0 | 0 | 70 | 2023-02-21 10:01 | 2023-02-24 17:00 | 2023-02-21 14:00 | 2023-02-24 17:00 | 2023-02-24 12:00
MSA-DCA | WA6520006 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 371.62 | Pass | Pass | 0 | 0 | 70 | 2023-01-27 09:42 | 2023-01-30 17:00 | 2023-01-27 13:00 | 2023-01-30 17:00 | 2023-01-30 11:00
MSA-DTAG | WA5094501 | 0 | AHS Services WA Pty Ltd (Anchor) | Family violence room - ceiling leaking - from plumbing pipes - toilet above migrates - see notes | Plumbing & Drainage | Water | 1003.2785 | Pass | Fail | 0 | 0 | 69.55 | 2022-01-31 11:37 | 2022-01-31 13:37 | 2022-01-31 12:27 | 2022-01-31 15:37 | 2022-02-03 10:00 |  |  | Completed
MSA-DTWD | WA5674621 | 2 | AWB Co. | roof leak | Roofing | Metal Roofing | 547.27 | Pass | Pass | -1 | 0 | 69.5 | 2022-07-21 12:58 | 2022-07-26 17:00 | 2022-07-22 14:30 | 2022-07-26 17:00 | 2022-07-25 12:00 |  |  | Attended and made temp repair, return required. 3 x leaks evident sealed all areas as per signature slip.
MSA-DCA | WA6518622 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - Dutch Wrecks Gallery - above cannon - AHU leaking | Air Conditioning | Room Air Conditioners | 760.13 | Pass | Fail | 0 | 0 | 69.5 | 2023-01-25 10:00 | 2023-01-27 17:00 | 2023-01-27 12:00 | 2023-01-27 17:00 | 2023-01-30 09:30
MSA-DTWD | WA6403725 | 2 | Building Automation & Electrical Services Pty Ltd | Building 1 - W606 plus - L6 high temp issues | Building | General Building |  | Pass | Pass | -1 | 0 | 69.4342 | 2023-01-06 14:21 | 2023-01-11 17:00 | 2023-01-06 14:34 | 2023-01-11 17:00 | 2023-01-09 12:00
MSA-DCA | WA4992414 | 2 | Techworks Plumbing | Repair hot water supply Level 3 Hackett Hall Cleaners Store 5 (top of stair 2) & Store 12 (Wildlife | Plumbing & Drainage | Water | 603.56 | Pass | Fail | 0 | 0 | 69.3 | 2022-01-06 11:32 | 2022-01-11 17:00 | 2022-01-10 14:30 | 2022-01-11 17:00 | 2022-01-13 11:48 |  | WACCES | Inspected tap to find no hot water, explored floor to find hidden cleaners room and hot water unit tested for power, no power,Access switch board to find the breaker has not been tripped,Electrican required
MSA-DCA | WA6357390 | 3 | Protek 24/7 Building & Maintenance | Studio Underground Door A - Skirting board is missing | Carpentry | Materials | 398.03 | Pass | Pass | -1 | 0 | 69.25 | 2022-12-05 13:02 | 2022-12-12 17:00 | 2022-12-06 10:45 | 2022-12-12 17:00 | 2022-12-09 08:00 |  | WACCES | Measure up to construct new pieces and take photosInstall new wall trim
MSA-DCA | WA5399239 | 2 | EQUANS Mechanical Services (WA) Pty Limited | geology bid, mezz plantroom 4 Investigate & repair critical humidifier Alarm to AHU 03.05 & AHU 08.0 | Air Conditioning | Room Air Conditioners | 912.3 | Pass | Fail | 0 | 0 | 69 | 2022-05-09 20:27 | 2022-05-12 17:00 | 2022-05-10 12:00 | 2022-05-12 17:00 | 2022-05-13 09:00 |  |  | Attended site, signed in and accessed the affected ahu's / areas. Found both ahu's 03.05 and 08.01 have blocked pre airfilters and blocked water humidifier filters.Ordered new filters, returned to site, isolated ahus and humidifiers and replaced filters. Ran, tested and checked operation and is now operating correctly.
MSA-DTAG | WA5493762 | 0 | Sapio Pty Ltd | Level 4 - Room 404 -security door - push button not working - see details below | Security | Access Control | 272.32 | Pass | Fail | 0 | 0 | 69 | 2022-06-07 10:06 | 2022-06-07 12:06 | 2022-06-07 12:00 | 2022-06-07 14:06 | 2022-06-10 09:00 |  | WACCES | Replaced Egress button on Level 4, Room 404 and 2 others.
MSA-DFES | WA5010469 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Gantry - leaking water valve at the gantry | Plumbing & Drainage | Water | 612.42 | Pass | Pass | -1 | 0 | 68.75 | 2022-01-12 14:59 | 2022-01-19 17:00 | 2022-01-14 13:00 | 2022-01-19 17:00 | 2022-01-17 09:45 |  |  | Replaced ball valve as required
MSA-DTAG | WA5193712 | 3 | Midolo Building Services | Front security entrance - see details | Building | General Building | 663.83 | Pass | Pass | 0 | 0 | 68.75 | 2022-02-25 13:15 | 2022-03-04 17:00 | 2022-03-01 11:30 | 2022-03-04 17:00 | 2022-03-04 08:15 |  | WACCES | new thresholds installed
MSA-DTAG | WA6519924 | 2 | Midolo Building Services | L8-Fault description The staples on the inside of the gallery door in court 81 have come loose. | Building | Doors | 229.26 | Fail | Fail | 1 | 1 | 68.75 | 2023-01-27 08:40 | 2023-02-01 17:00 | 2023-02-06 11:15 | 2023-02-01 17:00 | 2023-02-09 08:00
MSA-DTWD | WA6403489 | 2 | Techworks Electrical | Stores - Auto roller door does not open | Building | Automatic Doors | 725.525 | Pass | Fail | 0 | 0 | 68.5 | 2023-01-06 10:50 | 2023-01-11 17:00 | 2023-01-10 13:00 | 2023-01-11 17:00 | 2023-01-13 09:30
MSA-DTAG | WA5706184 | 2 | Water2water Pty Ltd | Detention - Water to water filter in detention is leaking - See notes below | Plumbing & Drainage | Water | 458.31 | Pass | Pass | -1 | 0 | 68.1667 | 2022-08-11 09:25 | 2022-08-16 17:00 | 2022-08-12 12:25 | 2022-08-16 17:00 | 2022-08-15 08:35 |  | WCAPPR | MAXIFLOW FILTRATION SYSTEM REPLACED LEAKING AP11 SINGLE HOUSING. ALL OKAY ON DEPARTURE.
MSA-DTWD | WA5107073 | 2 | Lane's Plumbing | faulty cistern | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 68 | 2022-02-07 14:09 | 2022-02-10 17:00 | 2022-02-07 15:30 | 2022-02-10 17:00 | 2022-02-10 11:30 |  |  | job completed - REPLACE FAULTY TOILET CISTERN TO TO HOUSE 16
MSA-DTWD | WA6155888 | 2 | AWB Co. | Outside Yard - Shed - garden shed roller door has broken lock | Security | Locksmith | 538.985 | Fail | Fail | 1 | 1 | 68 | 2022-11-08 14:47 | 2022-11-11 17:00 | 2022-11-15 14:00 | 2022-11-11 17:00 | 2022-11-18 10:00 |  |  | works completed as per sign slip
MSA-DTWD | WA4993406 | 1 | AWB Co. | main plant room - Faulty 3 Phase power points | Electrical | General Electrical | 1804.79 | Pass | Fail | 0 | 0 | 68 | 2022-01-07 13:18 | 2022-01-10 17:00 | 2022-01-10 13:30 | 2022-01-10 17:00 | 2022-01-13 09:30 |  |  | Attended site, signed in, completed jsa,spoke with fm about job,located plant room, mounted new GPOs on wall as per fm request, went to wholesaler to pick up parts, returned to site, isolated dB and ran cables in conduit, made entries into board and terminated cables , tested cables then energised circuit, tested gpos and rcd functions , cleaned up , packed up completed paperwork , job complete
MSA-DTWD | WA5839134 | 3 | AWB Co. | Irrigation box in gazebo adjacent to M Shed is damaged. Door is coming off. | Building | Doors | 576.42 | Pass | Fail | 0 | 0 | 68 | 2022-09-09 09:38 | 2022-09-16 17:00 | 2022-09-16 14:15 | 2022-09-16 17:00 | 2022-09-19 10:15 |  |  | Fixed irrigation door
MSA-DTAG | WA6129010 | 3 | Midolo Building Services | Multiple levels - Public toilets - metal toilet roll holders have been vandalised – see notes below | Building | General Building | 1111.16 | Fail | Fail | 4 | 5 | 68 | 2022-10-27 09:59 | 2022-11-03 17:00 | 2022-12-02 12:45 | 2022-11-03 17:00 | 2022-12-05 08:45 |  | WACCES | New toilet roll holders installed to all areas listed below & requested by Iain Johnston
MSA-DTWD | WA6294394 | 1 | Australian Airconditioning Services Pty Ltd | AC units not cooling in this area | Air Conditioning | Package | 790.86 | Fail | Fail | 0 | 1 | 68 | 2022-11-30 15:32 | 2022-12-01 17:00 | 2022-12-02 13:30 | 2022-12-01 17:00 | 2022-12-05 09:30 |  |  | complete
MSA-DTAG | WA6381267 | 1 | SCAVENGER SUPPLIES PTY LTD | Level 1 - Fire Panel is showing battery failure | Fire Protection Services | Fire Protection - Monitor System | 714.51 | Pass | Fail | 0 | 0 | 68 | 2022-12-19 12:46 | 2022-12-20 17:00 | 2022-12-19 13:00 | 2022-12-20 17:00 | 2022-12-22 09:00 |  | WACCES | 19/12/22 - Arrived on site @ 1300 The panel was in fault. Battery Detected/Failed Network Point 1 supply fault. Tried a master reset but the Panel goes back to the fault. Disconnected the back up batteries to try and clear the fault. Contacted Brian Ryan for further information. Brian contacted Ampac and they said it's a generic issue/problem when the batteries need replacement. EOL is 05/05/2023. Brian said the batteries have been under heavy load and will need to be swapped out. Suggested to change batteries for new to clear the fault. Also suggested not to do a cold reset due to other issues that could arise. 2 x 12V 26AH/20HR required. 20/12/22 - New Batteries ordered and awaiting delivery.
MSA-DTWD | WA5100407 | 2 | Precise Air Group | E block - SK2 - AC for room isnt working correctly | Air Conditioning | Room Air Conditioners | 434.33 | Pass | Pass | 0 | 0 | 67.9667 | 2022-02-02 13:14 | 2022-02-07 17:00 | 2022-02-04 15:05 | 2022-02-07 17:00 | 2022-02-07 11:03 |  |  | Replaced water solenoid valve
MSA-DTWD | WA5473261 | 2 | Falcetta Plumbing and Gas | Ladies toilet, Two toilets are dysfunctional. see more further information | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Fail | 0 | 0 | 67.75 | 2022-05-24 13:21 | 2022-05-27 17:00 | 2022-05-27 16:15 | 2022-05-27 17:00 | 2022-05-30 12:00 |  | WCAPPR | unblocked drain, inspected water supply, campus to monitor
MSA-DFES | WA5584915 | 1 | Protek 24/7 Building & Maintenance | admin ground-In Service/FDP Office-Roof leaking onto electrical equipment near OH&S workstation | Electrical | General Electrical | 439.5 | Pass | Fail | 0 | 0 | 67.75 | 2022-07-05 11:28 | 2022-07-06 17:00 | 2022-07-05 13:15 | 2022-07-06 17:00 | 2022-07-08 09:00 |  |  | Repairs to box gutter
MSA-DTWD | WA5209028 | 2 | AWB Co. | T block - Plant room level 3 servicing Cafe - See details below | Electrical | General Electrical | 483.825 | Pass | Pass | 0 | 0 | 67.75 | 2022-03-09 12:47 | 2022-03-14 17:00 | 2022-03-11 14:30 | 2022-03-14 17:00 | 2022-03-14 10:15 |  |  | Attended site and signed in. Completed JSA. Located hot water unit that I worked on friday. Check and tested to be at good temp and been hot all weekend and no complaints from the kitchen staff. Drained and heated back up to temp again and all is working perfectly. Signed out. Job complete
MSA-DTWD | WA5385303 | 2 | Equans Mechanical Services Australia | Corridor outside A305 Staffroom - A//C fault light illuminated | Air Conditioning | Building HVAC Maintenance (Major Plant) | 120.35 | Pass | Pass | -1 | 0 | 67.5167 | 2022-04-29 09:07 | 2022-05-04 17:00 | 2022-04-29 15:00 | 2022-05-04 17:00 | 2022-05-02 10:31 |  |  | Found the fault light , reset and test ran all OK
MSA-DCA | WA6149426 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Boiler fault | Mechanical Services | Boilers | 1615.47 | Pass | Fail | 0 | 0 | 67.5 | 2022-11-04 15:43 | 2022-11-04 17:43 | 2022-11-04 16:30 | 2022-11-04 19:43 | 2022-11-07 12:00 |  |  | CHECKED OUT BOILER IN FAULT. CHECKED SAFETY SWITCHES ON BOILER AND BMS. RESET POWER BUT UNABLE TO START BOILER. CONTACTED SCHNEIDER CONTROLS AND CHECKED OVER THE SYSTEM. MANAGED TO GET THE BOILER BACK ONLINE. WILL NEED TO BE INVESTIGATED FURTHER DURING OFFICE HOURS. TRAVELLED TO SITE AND CHECKED PLANT ROOM BOILER 1 NOT IN FAULT AND RUNNING. CHECKED BMS BOILER PAGES AND FOUND BOILER 1 IN ALARM. RESET BMS AND NOW NO FURTHER ALARMS. ACCESSED BOILER ROOM AGAIN AND CHECKED TO ENSURE BOILER 1 IS RUNNING AND BOILER 2 IS STILL TAGGED OFF BY BOILERTRONICS FOR QUOTED WORKS TO TAKE PLACE. NO FURTHER FAULTS FOUND. ADVISED CLIENT OF WORKS CARRIED OUT. MONITORED OPERATION OF BMS AND BOILER RUNNING PRIOR TO LEAVING SITE.
MSA-DTAG | WA6431426 | 1 | GPS Plumbing & Gas Services PtyLtd | Stirling Gardens Complex - Water dripping from the ceiling | Plumbing & Drainage | Drainage | 375.1025 | Pass | Pass | 0 | 0 | 67.4167 | 2023-01-13 14:35 | 2023-01-16 17:00 | 2023-01-13 15:55 | 2023-01-16 17:00 | 2023-01-16 11:20
MSA-DCA | WA5682996 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Old New Museum Area - Drip onto table which appears to be coming from exhaust fan ducting | Air Conditioning | Building HVAC Maintenance (Major Plant) | 427.925 | Pass | Pass | -1 | 0 | 67.1 | 2022-07-29 14:22 | 2022-08-05 17:00 | 2022-08-01 14:00 | 2022-08-05 17:00 | 2022-08-04 09:06 |  |  | Returned to site gained access and rechecked reported area and leak from EF-6. Confirmed that no pooling water had formed. Confirmed fan operation. Confirmed that pooling liquid was an oil based substance possibly dropped on table by one of the staff on site. No further action is required on this job.
MSA-DTWD | WA5674651 | 2 | AWB Co. | Roof Leak - From west end air conditioning duct | Roofing | Metal Roofing | 493.62 | Pass | Pass | -1 | 0 | 67 | 2022-07-21 13:08 | 2022-07-26 17:00 | 2022-07-22 15:00 | 2022-07-26 17:00 | 2022-07-25 10:00 |  |  | Attended, needed dry day to return. Sealed roof support and flexible joint base flashing
MSA-DTWD | WA6365999 | 1 | Lane's Plumbing | Gas Hot water system faulty | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 0 | 67 | 2022-12-13 14:00 | 2022-12-14 17:00 | 2022-12-13 14:00 | 2022-12-14 17:00 | 2022-12-16 09:00 |  |  | Completed
MSA-DTWD | WA6178520 | 2 | AWB Co. | ground staffroom-Flashing light | Electrical | Lighting, Internal | 443.73 | Pass | Pass | 0 | 0 | 67 | 2022-11-14 11:57 | 2022-11-17 17:00 | 2022-11-14 13:00 | 2022-11-17 17:00 | 2022-11-17 08:00 |  | WACCES | Attended site signed in jsa completed. Removed old light fitting and put new led panel in. Tested operational. Job completed
MSA-DFES | WA6184180 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Various locations - multiple lights are out - see notes | Electrical | General Electrical | 871.885 | Pass | Pass | -1 | -1 | 66.75 | 2022-11-15 10:44 | 2022-11-22 17:00 | 2022-11-15 13:45 | 2022-11-22 17:00 | 2022-11-18 08:30 |  |  | Signed in and located faulty lights. Replaced faulty fluorescent tubes and starters with new. Left site to get more fluorescents tubes and light fittings. Retuned to site replaced faulty lights with new in the shower and the faulty light outside. Continued with replacing the faulty tubes and starter with new. One light in the staff toilets near lecture room 8 after Changing the tubes one tube is still not working and the light will need to be replaced. Arrived onsite at 7:30 to replace faulty fluro fitting in staff toilet near lecture room 8, replaced faulty light fitting with new LED wide body baton, staff toilet light now working. Advised staff of works and left site at 8:30.
MSA-DTWD | WA6673483 | 2 | AHS Services WA Pty Ltd (Anchor) | Leaking vanity tap | Plumbing & Drainage | Water | 653.4725 | Pass | Fail | 0 | 0 | 66.75 | 2023-02-24 14:58 | 2023-03-01 17:00 | 2023-02-27 14:30 | 2023-03-01 17:00 | 2023-03-02 09:15
MSA-DFES | WA5585308 | 3 | Protek 24/7 Building & Maintenance | Admin ground-smoking area-Gutter overflowing | Roofing | Guttering | 248.25 | Pass | Pass | -1 | -1 | 66.5 | 2022-07-05 14:26 | 2022-07-12 17:00 | 2022-07-05 15:30 | 2022-07-12 17:00 | 2022-07-08 10:00 |  |  | Fascia repairs
MSA-DTWD | WA5888299 | 2 | AWB Co. | Room E30 - Faulty LED Light | Electrical | Lighting, Internal | 259.6175 | Pass | Fail | 0 | 0 | 66.5 | 2022-09-16 15:13 | 2022-09-21 17:00 | 2022-09-20 15:00 | 2022-09-21 17:00 | 2022-09-23 09:30 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Located room E30. Isolated circuit. Removed panel. Replaced driver with new. Reinstalled panel and sealed off. Energised. Tested, all working correctly. notified relevant personnel of works completed. **job complete**
MSA-DCA | WA5534492 | 2 | Protek 24/7 Building & Maintenance | External to State Library – south side - Bike rack is unsafe as fixings are coming loose - See notes | Building | General Building | 387.25 | Pass | Fail | 0 | 0 | 66.25 | 2022-06-16 11:09 | 2022-06-21 17:00 | 2022-06-21 13:45 | 2022-06-21 17:00 | 2022-06-24 08:00 |  | WCAPPR | Remove unsafe bike rack refitted paver
MSA-DTAG | WA5839316 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 10 - Coroners Court - Disabled Toilet - Little water flow - See notes below | Plumbing & Drainage | Water | 264.615 | Pass | Fail | 0 | 0 | 66.25 | 2022-09-09 11:01 | 2022-09-14 17:00 | 2022-09-12 14:30 | 2022-09-14 17:00 | 2022-09-15 08:45 |  |  | .
MSA-DCA | WA5687291 | 1 | Critical Fire Protection & Training | Level 4 - Rear Book Room - VESDA system shows fault in rear book room - | Fire Protection Services | Fire Protection - Monitor System | 676.755 | Pass | Fail | 0 | 0 | 66 | 2022-08-01 15:11 | 2022-08-02 17:00 | 2022-08-01 16:00 | 2022-08-02 17:00 | 2022-08-04 10:00 |  |  | Attended site as a call-out to investigate fire alarm panel VESDA fault. On arrival found level 4 zone 41 VESDA unit in (urgent/zone/airflow) fault. VESDA filter replaced as per photos attached.
MSA-MRWA | WA5116470 | 1 | Automatic Fire Protection (ARA) | Level 6 - Female Toilet - investigate and reset sensor | Fire Protection Services | Fire Protection - Monitor System | 808.035 | Pass | Pass | 0 | 0 | 65.75 | 2022-02-11 15:32 | 2022-02-14 17:00 | 2022-02-11 16:30 | 2022-02-14 17:00 | 2022-02-14 10:15 |  |  | Attended site spoke with Brendan from programmed he advised that the detector in the disabled toilet on level 6 had activated 2 times today once attended by technician Eugene and he thought it was due to aerosol spray and would like it tested to confirmed it is working okay, checked fip found detector was disabled and code red was in isolate.Tested detector and it activated as normal but would not reset after multiple attempts and was showing as dirty fault aswell, left detector isolated and will need to be replaced will require mx 850p addressable smoke detector and mx programmer which I did not have in van.Left fip in normal operation with single detector in disabled toilet isolated.Brendan had left for the day whilst onsite so was unable to get signed, tryed ringing Brendan as requested but didn’t answer and left voicemail.BG GA 14/2/22Returned to site, replaced and programmed in new Tyco 850P smoke detector. Monitored alarm, did not return. Removed isolation. System norma
MSA-DFES | WA5793146 | 0 | Anvil Doors | Engine room - south east - cable snapped stuck quarter open | Building | Doors | 632.25 | Fail | Fail | 0 | 0 | 65.6333 | 2022-08-23 16:01 | 2022-08-23 18:01 | 2022-08-23 18:19 | 2022-08-23 20:01 | 2022-08-26 11:57 |  |  | Technician secured the door and removed damaged bracket and cable. second tech returned the next day fixed bracket and re-attached cable.
MSA-DFES | WA6025309 | 1 | COMMERCIAL PLUMBING AND GAS | No HWS to property | Plumbing & Drainage | Water | 2572.62 | Pass | Fail | 0 | 0 | 65.5 | 2022-10-15 20:16 | 2022-10-17 17:00 | 2022-10-15 21:30 | 2022-10-17 17:00 | 2022-10-18 15:00 |  |  | repaired hot water unit and repaired hot water inlet
MSA-DTWD | WA6425891 | 2 | Precise Air Group | Chiller compound - Tripping out on cool flow switch | Air Conditioning | Building HVAC Maintenance (Major Plant) | 253.38 | Pass | Pass | -1 | 0 | 65.4667 | 2023-01-12 12:34 | 2023-01-17 17:00 | 2023-01-13 13:30 | 2023-01-17 17:00 | 2023-01-16 06:58
MSA-DTAG | WA5108491 | 1 | GPS Plumbing & Gas Services PtyLtd | Supreme Court – Stirling Gardens Complex - Ground - Female toilets - | Plumbing & Drainage | Materials | 601.15 | Pass | Fail | 0 | 0 | 65.0667 | 2022-02-08 14:23 | 2022-02-09 17:00 | 2022-02-08 15:40 | 2022-02-09 17:00 | 2022-02-11 08:44 |  | WCAPPR | Replaced basin taps to female toilet LHS ground floor.Had to isolate water to the whole building.Job could not be completed on the day because we disintegrated have approval to shut the water off.
MSA-DTAG | WA5052558 | 1 | Sapio Pty Ltd | Ground - Security - Duress alarm did not reset after testing. Showing active in error | Security | Monitoring | 2332.78 | Pass | Fail | 0 | 0 | 65 | 2022-01-18 09:01 | 2022-01-19 17:00 | 2022-01-18 11:00 | 2022-01-19 17:00 | 2022-01-21 04:00 |  |  | replaced damaged cables and separated duress buttons, programmed to individual inputs
MSA-DTWD | WA5694798 | 1 | Falcetta Plumbing and Gas | Toilet slow to empty on flushing | Plumbing & Drainage | Toilets/Cisterns | 871.6725 | Pass | Pass | 0 | 0 | 65 | 2022-08-05 13:29 | 2022-08-08 17:00 | 2022-08-05 17:30 | 2022-08-08 17:00 | 2022-08-08 10:30 |  | WCAPPR | long run of drain, accumulated blockage cleared by drainsflush
MSA-DTWD | WA5675850 | 2 | AWB Co. | Flicking fluero - High ceiling | Electrical | Lighting, Internal | 296.495 | Pass | Fail | 0 | 0 | 64.75 | 2022-07-22 14:29 | 2022-07-27 17:00 | 2022-07-26 14:30 | 2022-07-27 17:00 | 2022-07-29 07:15 |  | WCAPPR | Attended site and signed in,reviewed JSA,got keys from cleaner , got ladder into kitchen area, removed old tubes and starters, replaced with new , put old tubes and starters in store room , tested light and working as intended, returned keys to office, completed paperwork, sent signature slip through to jo to be signed **job completed**
MSA-DTWD | WA5116502 | 0 | Dormakaba Australia Pty Ltd | Passage -Auto slding door E201- Is closed wont open | Building | Automatic Doors | 660 | Pass | Fail | 0 | 0 | 63.2 | 2022-02-11 18:04 | 2022-02-11 20:04 | 2022-02-11 19:15 | 2022-02-11 22:04 | 2022-02-14 10:27 |  |  | WO-03014195 - On arrival, unable to unlock unit.Powered unit off to gain access for staff member.Unit showing fault G3.Left power off until return visit to rectify issue as approved by Steve.Please return with 2x techs due to safety and pelmet size.WO-03014584 - Reset the power back.Cleared the obstruction error code. Checked the wiring of external key switch trigger input.Required the keyswitch terminals. Fixed the door closed end channel just came out of frame.Checked all modes, sensors, internal push button, external keyswitch.
MSA-DCA | WA5421384 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Ground floor- Air condition system has gone off -Monitoring chiller and are off | Air Conditioning | Room Air Conditioners | 450 | Fail | Fail | 0 | 0 | 60 | 2022-05-13 19:35 | 2022-05-13 20:05 | 2022-05-13 21:00 | 2022-05-13 21:35 | 2022-05-16 09:00 |  | WACCES | Attended site, signed in and accessed the building management system. Checked the chiller page for any abnormalities and found system running on ETS with supplied chilled water temperatures around 7 degrees.Found ahu studio theatre 1A-01 not running and off on time schedules. Manualled the ahu on for the weekend until the time schedules have been updated. Returned the following Monday morning to check check the ahu and supply chilled water temperatures, central plant running as per normal with no new faults to report.
MSA-DTWD | WA5382148 | 1 | AWB Co. | Block 3 - Heavy Auto Workshop – distribution board making a buzzing noise – to be investigated | Electrical | General Electrical | 758.78 | Pass | Fail | 0 | 0 | 57.5 | 2022-04-26 14:16 | 2022-04-27 17:00 | 2022-04-27 00:30 | 2022-04-27 17:00 | 2022-04-29 10:00 |  |  | Fault rectified with further inspections by AJJobs now completed
MSA-DTWD | WA6111640 | 2 | JEM Carpentry | Outside steps - faulty non slip tape on steps | Carpentry | Staircases, Balustrades and Handrails |  | Fail | Fail | 1 | 1 | 57.5 | 2022-10-21 09:33 | 2022-10-26 17:00 | 2022-11-02 08:00 | 2022-10-26 17:00 | 2022-11-04 17:30 |  |  | tape installed
MSA-DTWD | WA5689947 | 3 | AWB Co. | Damaged ceiling needs repairing-see notes | Building | Ceiling | 997.6525 | Pass | Fail | 0 | 0 | 57.5 | 2022-08-02 15:32 | 2022-08-09 17:00 | 2022-08-09 07:00 | 2022-08-09 17:00 | 2022-08-11 16:30 |  |  | (09/08/2022) - Work NoteAttended site, filled out JSA, measured up, picked up materials, protected floor with dust sheet, cut plasterboard square, framed out and flushed with base coat installed ceiling hatch, will need to reschedule to put top coat on sand and paint white ceiling paint.Attended site, applied top coat, went to another job, whilst drying, attended back sanded and painted with ceiling white paint.
MSA-DTWD | WA6449976 | 1 | AHS Services WA Pty Ltd (Anchor) | Tap running in D Block male toilet | Plumbing & Drainage | Water | 1033.315 | Pass | Fail | 0 | 0 | 57.25 | 2023-01-16 08:41 | 2023-01-17 17:00 | 2023-01-17 07:15 | 2023-01-17 17:00 | 2023-01-19 16:30 |  | WACCES
MSA-DTWD | WA6676570 | 3 | Australian HVAC Services Pty. Ltd. | Block A - Level 3 - plantroom - Aircon - Tech on site | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | -1 | -1 | 56.5 | 2023-02-28 15:09 | 2023-03-08 17:00 | 2023-03-01 06:30 | 2023-03-08 17:00 | 2023-03-03 15:00
MSA-DTWD | WA6148383 | 2 | Water2water Pty Ltd | Water fountain leaking in J block | Plumbing & Drainage | Water | 2217.26 | Pass | Fail | 0 | 0 | 55.6667 | 2022-11-03 16:38 | 2022-11-08 17:00 | 2022-11-08 08:40 | 2022-11-08 17:00 | 2022-11-10 16:20 |  | WACCES | Unable to repair fountain, tank is rusted/corroded and leaking. New fountain required. Job on ‘Waiting on Parts’ until fountain is delivered Fountain now in stock. Replaced old leaking fountain with new including maxiflow water filter system.
MSA-DTAG | WA5399078 | 2 | Sapio Pty Ltd | 3 x false alarms – Duress changed to open state while Chambers 5 was empty on Saturday 7 May 2022 | Security | Security Management System | 645.45 | Pass | Fail | 0 | 0 | 55.5 | 2022-05-09 14:45 | 2022-05-12 17:00 | 2022-05-11 07:00 | 2022-05-12 17:00 | 2022-05-13 14:30 |  |  | Replaced faulty duress button with approved stainless steel plated, key resettable button. Tested and commissioned.
MSA-DTAG | WA6407281 | 1 | AHS Services WA Pty Ltd (Anchor) | Locker room - female staff toilet - Water leaking through slab from ground floor | Plumbing & Drainage | Water | 2084.0925 | Fail | Fail | 0 | 0 | 54.5167 | 2023-01-10 07:45 | 2023-01-10 17:00 | 2023-01-11 06:29 | 2023-01-10 17:00 | 2023-01-13 13:00
MSA-DFES | WA6088795 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Yard - Soakwell at the rear of the station next to the car bays against the blue wall. | Plumbing & Drainage | Drainage | 1021.235 | Pass | Fail | 0 | 0 | 54.5 | 2022-10-19 10:56 | 2022-10-24 17:00 | 2022-10-24 08:30 | 2022-10-24 17:00 | 2022-10-26 15:00 |  | WACCES | Replaced broken Septic Lid.
MSA-DFES | WA5399236 | 2 | Protek 24/7 Building & Maintenance | Dorm 1 Loose towel rail needs to be fixed to wall | Building | Internal Walls | 369.72 | Pass | Fail | 0 | 0 | 54.25 | 2022-05-09 19:55 | 2022-05-12 17:00 | 2022-05-11 07:30 | 2022-05-12 17:00 | 2022-05-13 13:45 |  | WACCES | Fix Loose towel rail
MSA-DTAG | WA6044410 | 0 | Sapio Pty Ltd | Level 6-all duress alarms not working | Security | Security Management System | 1218.1 | Pass | Fail | 0 | 0 | 54 | 2022-10-17 10:34 | 2022-10-17 12:34 | 2022-10-17 11:30 | 2022-10-17 14:34 | 2022-10-19 17:30 |  |  | Work performed by Michael Tomlinson (19/10/2022)Replaced IOC 1065 board and tested duress buttons, all OK.Job completed.
MSA-DCA | WA6578240 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Boiler No 1 | Building | General Building | 1662.355 | Pass | Fail | 0 | 0 | 54 | 2023-02-15 08:27 | 2023-02-15 10:27 | 2023-02-15 09:30 | 2023-02-15 12:27 | 2023-02-17 15:30
MSA-DTAG | WA6356817 | 2 | Australian HVAC Services Pty. Ltd. | Level 4 - 1987 Plantroom - Cooling tower is leaking water | Air Conditioning | Cooling Tower | 942.29 | Pass | Pass | 0 | 0 | 53.9833 | 2022-12-05 09:31 | 2022-12-08 17:00 | 2022-12-05 09:31 | 2022-12-08 17:00 | 2022-12-07 15:30 |  |  | Carry out further leak repair to cooling tower. Drill extra holes in tower and install bolts to clamp down on seal better. Go over all bolts to ensure tight. Seal sections with silicone where seal has come out. Allow to dry. Leave overnight, no more leaks found in the morning.
MSA-DFES | WA6378800 | 2 | Australian HVAC Services Pty. Ltd. | Station Officers 1st dorm Aircond is not working. | Air Conditioning | Room Air Conditioners | 2352.63 | Pass | Pass | 0 | 0 | 53.5 | 2022-12-19 07:27 | 2022-12-21 17:00 | 2022-12-19 09:30 | 2022-12-21 17:00 | 2022-12-21 15:00 |  |  | New aircon ro be quoted for install.
MSA-DTWD | WA5780382 | 2 | JEM Carpentry | Porch ceiling faulty | Building | Ceiling |  | Pass | Pass | 0 | 0 | 53.5 | 2022-08-19 09:58 | 2022-08-24 17:00 | 2022-08-22 07:00 | 2022-08-24 17:00 | 2022-08-24 12:30 |  |  | Painted and repaired
MSA-DCA | WA4994954 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Dutchwreck Gallery - AHU above cannon is leaking | Air Conditioning | Room Air Conditioners | 397.675 | Pass | Pass | 0 | 0 | 53.05 | 2022-01-10 09:01 | 2022-01-13 17:00 | 2022-01-10 11:44 | 2022-01-13 17:00 | 2022-01-12 16:47 |  |  | Attened 10/1/22 and carried out inspection no water found to be leaking. Returned to site and checked equipment operation. Confirmed base of unit and drip tray were both dry no.watwr currently dripping. Please note equipment is waiting on repairs due to fault that was identified on another job. Work area left tidy. Work area left tidy.
MSA-DFES | WA5888514 | 1 | Australian HVAC Services Pty. Ltd. | Alarms Room- Air condition fault | Air Conditioning | Room Air Conditioners | 888.8 | Pass | Fail | 0 | 0 | 53.0167 | 2022-09-16 17:31 | 2022-09-19 17:00 | 2022-09-19 11:00 | 2022-09-19 17:00 | 2022-09-21 16:01 |  |  | Returned to site and carried out further investigation into fcu 13 operation. Spoke to electrical company who installed the system and they advised the fcu is switched off by the door switch on the external door in the lounge. Inspected door switch and found when opened or closed the relay does not change. Suspect door switches may be faulty. Reported this to pfm and advised they engage an electrician to inspect/replace door switches. The aircon system is operational via the remote controller.
MSA-DTWD | WA5868551 | 1 | Lane's Plumbing | Sewer Pump Faulty | Plumbing & Drainage | Water |  | Pass | Fail | 0 | 0 | 53 | 2022-09-14 11:07 | 2022-09-15 17:00 | 2022-09-14 11:30 | 2022-09-15 17:00 | 2022-09-16 16:30 |  |  | Repairs to pump
MSA-DFES | WA6687733 | 1 | Australian HVAC Services Pty. Ltd. | Boiler ignition failure | Air Conditioning | Building HVAC Maintenance (Major Plant) | 932.37 | Pass | Fail | 0 | 0 | 52.9006 | 2023-03-07 09:20 | 2023-03-08 17:00 | 2023-03-07 10:53 | 2023-03-08 17:00 | 2023-03-09 15:47
MSA-DTAG | WA5862315 | 1 | Dormakaba Australia Pty Ltd | Ground Floor - Front entrance - electric sliding door is getting stuck open, not closing all the way | Building | Automatic Doors | 4447.74 | Pass | Fail | 0 | 0 | 52.6167 | 2022-09-13 16:45 | 2022-09-14 17:00 | 2022-09-14 09:33 | 2022-09-14 17:00 | 2022-09-16 14:10 |  |  | 14/9/22 - Inspected door and found open obstructing fault in door history, controller and boards are showing signs of wear due to age, spoke to site manager Iain Johnston and can we quote to replace el301 controller, option board kit , mode connection board and pib kit with 2ixio sensors.Unit working on departure.16/9/22 - Replaced parts as per BRAF, adjusted and tested, all ok.
MSA-DCA | WA5053331 | 2 | Earth & Water Pty Ltd | Urban Orchard - Zone 8 Urban Orchard Grass, South side - broken sprinkler | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 52.5 | 2022-01-18 16:03 | 2022-01-21 17:00 | 2022-01-19 10:00 | 2022-01-21 17:00 | 2022-01-21 14:30 |  |  | - fixed sprinkler in zone 8- ran system- cleaned up- checked "leak" in zone 14- issue is that the soils is super muddy and as its the lowest point water runs there creating a we hole in the ground.To fix this we need to dig out mud and fill hole with white sand
MSA-DCA | WA5301557 | 1 | EQUANS Mechanical Services (WA) Pty Limited | First Floor Labs - temperature is a bit low in gage could be faulty | Air Conditioning | Room Air Conditioners | 1061.275 | Pass | Fail | 0 | 0 | 52.4667 | 2022-04-01 10:21 | 2022-04-04 17:00 | 2022-04-04 08:57 | 2022-04-04 17:00 | 2022-04-06 13:25 |  |  | Returned to site with Alerton Controls BMS tech. Carried out further fault finding and temp humidity sensor in lab was found to be the cause of equipment reading out of normal temp range. A control offset temperature has been programmed into the BMS for AHU 4 to prevent further disruption to cooling and heating in the labs. A quote will be submitted for temps sensor replacement. No further action required on this job.
MSA-DTWD | WA6131686 | 2 | COMMERCIAL PLUMBING AND GAS | First cubicle (adjacent to urinal) constantly flowing - see notes below | Plumbing & Drainage | Toilets/Cisterns | 1027.3 | Pass | Pass | 0 | 0 | 52.25 | 2022-10-31 09:11 | 2022-11-03 17:00 | 2022-10-31 10:00 | 2022-11-03 17:00 | 2022-11-02 14:15 |  | WACCES | Replaced cistern
MSA-DTAG | WA5495044 | 3 | OCS SERVICES PTY LTD | Level 14 - Rooms 14.4 and 14.5 - Shampoo water damaged carpet tiles, rug & 2 fabric chairs | Cleaning | Cleaning | 942 | Pass | Pass | -1 | -1 | 52 | 2022-06-08 09:10 | 2022-06-15 17:00 | 2022-06-08 17:00 | 2022-06-15 17:00 | 2022-06-10 21:00 |  |  | Completed flood works
MSA-DTWD | WA5562956 | 1 | JEM Carpentry | BLD 840 - Roof leak | Roofing | Tiled Roofing |  | Pass | Fail | 0 | 0 | 52 | 2022-06-20 11:03 | 2022-06-21 17:00 | 2022-06-20 12:00 | 2022-06-21 17:00 | 2022-06-22 16:00 |  |  | Replaced tiles and fix roof leak
MSA-DTWD | WA5880317 | 3 | ACTION GLASS & ALUMINIUM | Nth Window NTL St. - Window film damaged Nth windows street level | Building | Windows | 2299.88 | Fail | Fail | 2 | 2 | 52 | 2022-09-15 12:11 | 2022-09-22 17:00 | 2022-10-05 07:00 | 2022-09-22 17:00 | 2022-10-07 11:00 |  |  | Attended site and assessed works required to North windows;Quote to remove internal & external tint film to windows with badly faded film only No replacement film required at this stage as specified by client Jewellery6 x 560 x 8501 x 600 x 13501 x 600 x 24001 x 600 x 14002 x 560 x 800Printing section - D1173 x 600 x 2350 3 x 560 x 6003 x 600 x 12004 x 600 x 24002 x 600 x 20002 x 600 x 12008 x 560 x 11502 x 600 x 2400Platform ladder required All work benches to be moved away from windows by others Work to be carried out during normal hours COMPLETED AS PER APPROVED BRAF
MSA-DCA | WA5686546 | 0 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Gas hot water heater is leaking water | Plumbing & Drainage | Gas | 3090.635 | Pass | Fail | 0 | 0 | 51.3333 | 2022-08-01 09:13 | 2022-08-01 11:13 | 2022-08-01 09:40 | 2022-08-01 13:13 | 2022-08-03 13:00 |  | WACCES | Uninstalled hwu, installed new hwu and temp valve, adjusted pipework to suit new hwu and temp valve, job delayed due to the supplier, removed old hwu from site
MSA-DTWD | WA6132632 | 2 | Protek 24/7 Building & Maintenance | Faulty door closer – Door between corridor and FG11 - see notes below | Building | Doors | 624.065 | Pass | Pass | 0 | 0 | 51.25 | 2022-10-31 17:01 | 2022-11-03 17:00 | 2022-11-01 11:45 | 2022-11-03 17:00 | 2022-11-03 15:00 |  | WACCES | Replace broken door closer
MSA-DFES | WA6403704 | 2 | Water2water Pty Ltd | Kitchen, left hand side of kitchen bench - No hot or cold water coming from tap | Plumbing & Drainage | Water | 341.155 | Pass | Pass | 0 | 0 | 51.25 | 2023-01-06 14:10 | 2023-01-11 17:00 | 2023-01-09 12:30 | 2023-01-11 17:00 | 2023-01-11 15:45 |  | WACCES
MSA-DTWD | WA6430664 | 2 | AWB Co. | C707 - Data & Power socket damaged | Electrical | General Electrical | 938.145 | Pass | Fail | 0 | 0 | 51.25 | 2023-01-13 07:42 | 2023-01-17 17:00 | 2023-01-17 09:15 | 2023-01-17 17:00 | 2023-01-19 12:30
MSA-DTWD | WA5715387 | 2 | ACTION GLASS & ALUMINIUM | Main Corridor - Glazing rubber missing from glass doors | Glazing | Door Glass | 304.14 | Pass | Fail | 0 | 0 | 51.2333 | 2022-08-12 14:40 | 2022-08-17 17:00 | 2022-08-17 12:30 | 2022-08-17 17:00 | 2022-08-19 15:44 |  | WACCES | ATTENDED SITE MADE SAFE MISSING BEAD WITH 1 L/M OF ANGLE AND 4 SCREWSRETURNED LATER DATE SUPPLIED & FIT NEW DOESKIN BEAD1-732 mmPLUS 1.5 L/M OF RUBBER REPLACED
MSA-DTAG | WA5628016 | 2 | Water2water Pty Ltd | JSO kitchen - Hot/cold BILLI water system not working, panel states leak, no leak visible | Plumbing & Drainage | Water | 439.215 | Pass | Fail | 0 | 0 | 51.1667 | 2022-07-15 10:17 | 2022-07-20 17:00 | 2022-07-19 11:30 | 2022-07-20 17:00 | 2022-07-21 14:40 |  |  | REPLACED TUBE KITS ON 19.7 ATTENDANCE.RECALLED TO REATTEND - RECONNECTED AND FITTED A FITTING ON THE HEAD.
MSA-DTAG | WA5679534 | 3 | Sapio Pty Ltd | Custody - Basement - CCTV/ Duress & door to be checked - See notes below | Security | Access Control | 204.44 | Pass | Fail | 0 | 0 | 51.1667 | 2022-07-26 14:45 | 2022-08-02 17:00 | 2022-08-01 07:20 | 2022-08-02 17:00 | 2022-08-03 10:30 |  |  | RCD testing complete. Faults raised on different work order number.
MSA-DCA | WA6403542 | 2 | GPS Plumbing & Gas Services PtyLtd | Urinal - constantly running water | Plumbing & Drainage | Toilets/Cisterns | 1680.8825 | Pass | Fail | 0 | 0 | 51 | 2023-01-06 11:22 | 2023-01-11 17:00 | 2023-01-11 12:40 | 2023-01-11 17:00 | 2023-01-13 15:40 |  | WACCES
MSA-DCA | WA5175199 | 0 | EQUANS Mechanical Services (WA) Pty Limited | plant room - chiller 1 in fault - see notes | Refrigeration | Chiller | 1335.8 | Pass | Fail | 0 | 0 | 50.5333 | 2022-02-21 11:00 | 2022-02-21 13:00 | 2022-02-21 11:30 | 2022-02-21 15:00 | 2022-02-23 14:02 |  |  | Returned to site gained access and carried out recheck of chiller. No further fault has occured. AV chiller tech has indicated that fault maybe due to a sensor or PCB starting to fail. If fault is to reoccur further action will be taken. Currently chiller has no active faults. Work area left tidy.
MSA-DCA | WA5796731 | 3 | Techworks Electrical | Ground Exterior - Broken Lights requiring repair - see notes below | Electrical | Lighting, External | 518.07 | Pass | Pass | 0 | 0 | 50.5 | 2022-08-26 13:01 | 2022-09-02 17:00 | 2022-08-31 12:00 | 2022-09-02 17:00 | 2022-09-02 14:30 |  |  | 1. arrived and started looking into why lights Didn’t have any power.2. found correct DB 3. found the contactor that controls them and found there was no 240,4. Tested fuse and found it was blown, tested circuit and all good.5. Replaced fuse and all working well. fuse from slwa stock
MSA-DTWD | WA6537266 | 0 | Protek 24/7 Building & Maintenance | Between B & D gate is damaged | Building | Steel Fencing & Gates | 1193.9 | Pass | Fail | 0 | 0 | 50.5 | 2023-02-07 08:18 | 2023-02-07 10:18 | 2023-02-07 08:30 | 2023-02-07 12:18 | 2023-02-09 11:00 |  | WACCES
MSA-DCA | WA4991516 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main Museum - Entry Way - Copper piping out the front of the Museum has been forcibly damaged | Plumbing & Drainage | Drainage | 920.925 | Pass | Fail | 0 | 0 | 50.4 | 2022-01-05 09:11 | 2022-01-06 17:00 | 2022-01-05 14:15 | 2022-01-06 17:00 | 2022-01-07 16:39 |  |  | Return to site before opening hours with materials required for job. Carried out repairs to broken pipework. Welded new copper fittings into place and fit new pipe support saddle. Confirmed condensation run off occurring from unit. Work area left tidy. No further action required on job.
MSA-DCA | WA5001195 | 0 | Protek 24/7 Building & Maintenance | pond leaking into SU foyer - see notes below | Plumbing & Drainage | Water | 293.975 | Pass | Fail | 0 | 0 | 50.25 | 2022-01-11 09:59 | 2022-01-11 11:59 | 2022-01-11 11:00 | 2022-01-11 13:59 | 2022-01-13 13:15 |  |  | Repair WPM
MSA-DTWD | WA5416879 | 2 | Protek 24/7 Building & Maintenance | FT02 Office - Roof Leak - Water leaking onto bookshelf - see notes below | Roofing | Metal Roofing | 425.5 | Pass | Fail | 0 | 0 | 50.25 | 2022-05-13 09:06 | 2022-05-18 17:00 | 2022-05-18 13:30 | 2022-05-18 17:00 | 2022-05-20 15:45 |  | WACCES | FT02 Office - Roof Leak - Water leaking onto bookshelfAttended site, measure up for a 300 mm deck tite with a pvc shroud around condenser and power cables to prevent future leaks and degradation to pipes and cables Braf declined
MSA-DTWD | WA6113323 | 2 | JEM Carpentry | Faulty fence | Building | Steel Fencing & Gates |  | Pass | Pass | 0 | 0 | 50.25 | 2022-10-24 10:37 | 2022-10-27 17:00 | 2022-10-24 10:45 | 2022-10-27 17:00 | 2022-10-26 13:00 |  |  | Repairs to fence
MSA-DTWD | WA6675906 | 1 | Protek 24/7 Building & Maintenance | North Exit door - All 3 hinges are worn and the door has dropped (see notes) | Building | Doors | 663.66 | Pass | Fail | 0 | 0 | 50.25 | 2023-02-28 10:18 | 2023-03-01 17:00 | 2023-03-01 10:45 | 2023-03-01 17:00 | 2023-03-03 13:00 |  | WACCES
MSA-DTAG | WA6408028 | 3 | Gilmour & Jooste Electrical | Electrical Faults - Multiple Lights out in Building - See Notes Below | Electrical | Lighting, Internal | 2093.11 | Pass | Fail | 0 | 0 | 50.1167 | 2023-01-10 13:56 | 2023-01-17 17:00 | 2023-01-17 07:00 | 2023-01-17 17:00 | 2023-01-19 09:07
MSA-DTAG | WA5748946 | 1 | Sapio Pty Ltd | Registry - Witness Room - Door release alarm in witness room not turning off- See notes below | Security | Access Control | 289.61 | Pass | Fail | 0 | 0 | 50 | 2022-08-17 08:31 | 2022-08-18 17:00 | 2022-08-17 12:30 | 2022-08-18 17:00 | 2022-08-19 14:30 |  |  | itted cover to break glass unit, provided site with 2 x reset keys.
MSA-DTWD | WA6113609 | 2 | AWB Co. | 3 faulty lights in Creche | Electrical | Lighting, Internal | 429.98 | Pass | Fail | 0 | 0 | 50 | 2022-10-24 13:12 | 2022-10-27 17:00 | 2022-10-26 13:00 | 2022-10-27 17:00 | 2022-10-28 15:00 |  | WACCES | Attended site signed in jsa completed, installed new drivers in 3 lights. All tested.job completed
MSA-DCA | WA6254106 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Gauge glass on Heating water vessel leaking | Mechanical Services | Boilers | 472.98 | Pass | Pass | 0 | 0 | 50 | 2022-11-22 15:25 | 2022-11-25 17:00 | 2022-11-23 07:00 | 2022-11-25 17:00 | 2022-11-25 09:00 |  |  | INVESTIGATED LEAK COMING FROM STEAM GEN 2. FOUND SMALL LEAK COMING FROM FLARE NUT. TIGHTENED AND CHECKED OVER. SMALL AMOUNT OF STEAM COMING FROM THE BOTTOM OF THE REFLEX GLASS. TESTED OPERATION AND UNABLE TO RECREATE LEAK. WILL MONITOR AND HAVE BOILERTRONICS ATTEND TO RECTIFY. BOILERTRONICS ATTENDED SITE. INVESTIGATED AND FOUND A CRACK IN THE REFLEX GLASS. CLEANED GAUGE AND REPLACED GLASS. ATTENDED SITE. CHECKED OVER WORK AND COMPLETED PAPERWORK.
MSA-DTAG | WA5994779 | 0 | GPS Plumbing & Gas Services PtyLtd | Basement - Service Duct - Drainpipe connection leaking | Plumbing & Drainage | Water | 847.0575 | Pass | Fail | 0 | 0 | 49.8333 | 2022-10-06 08:17 | 2022-10-06 10:17 | 2022-10-06 09:10 | 2022-10-06 12:17 | 2022-10-08 11:00 |  |  | Replaced faulty valve
MSA-DCA | WA6290392 | 0 | TK Elevator Australia Pty Ltd | Level-lift 1-doors will not open | Lifts | Lifts | 1775 | Fail | Fail | 0 | 0 | 49.7667 | 2022-11-28 08:29 | 2022-11-28 10:29 | 2022-11-28 12:41 | 2022-11-28 12:29 | 2022-11-30 14:27 |  |  | CALL: Right panel damaged and on an angle, door header bracket and door header panel bent/damaged and in need of adjustment andrepair. Upthrusts have been taken off and left in lift. Lift has been switched off from the motor room, WARNING: lift motor has brake bolts installed, brake release needed.REPAIR: fixed landing door
MSA-MRWA | WA5301206 | 2 | AWB Co. | Level 2 - Cubicle 2.101 and 2.05 - Lights not working | Electrical | Lighting, Internal | 438.07 | Pass | Fail | 0 | 0 | 49.75 | 2022-04-01 07:02 | 2022-04-05 17:00 | 2022-04-05 06:00 | 2022-04-05 17:00 | 2022-04-07 07:45 |  | WCAPPR | Attended site and signed in. Completed JSA. Located faulty light on level 2. Unplugged light and took down. Found a working light in store room that we could replace this with. Took down working light and replaced with other faulty one. Put up working light where faulty one used to be. Lights in office area are all now working as intended. Took pictures. Notice lights that were working yesterday now weren’t working, spoke with fm about this and after investigation determined it was a programming issue .Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5680268 | 2 | Water2water Pty Ltd | Student lunchroom C/block zippy boil not working | Plumbing & Drainage | Water | 800.255 | Pass | Fail | 0 | 0 | 49.75 | 2022-07-27 10:55 | 2022-08-01 17:00 | 2022-08-01 11:20 | 2022-08-01 17:00 | 2022-08-03 13:05 |  | WACCES | Work shop repairs 2/8/22 1.30-2.30pm. Replaced solenoids and diverted valve which was causing addition leaks.
MSA-DFES | WA5831454 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Water leak in training room 1. Electrician required to make safe/ | Electrical | General Electrical | 725.68 | Pass | Fail | 0 | 0 | 49.75 | 2022-09-04 18:33 | 2022-09-04 20:33 | 2022-09-04 19:15 | 2022-09-04 22:33 | 2022-09-06 21:00 |  |  | Arrived onsite at 19:15 to investigate water leak affecting lights in hallway. Found plumbers had recently been clearing drains and had caused water leaks onto electrics. Drain waste affected 2 x lights, now disconnected. Water also tripped 3 x circuits at main DB located hallway of water damage (DB-G2). Circuits remain off to ensure safety. Ensured all wet items were de energised before leaving site and notified site rep. Left site at 21:00.
MSA-DTWD | WA6362645 | 2 | Protek 24/7 Building & Maintenance | front of campus-remove rust damaged curved frame-and dispose using skip | Building | Steel Work | 741.58 | Pass | Pass | 0 | 0 | 49.75 | 2022-12-09 11:40 | 2022-12-14 17:00 | 2022-12-12 10:30 | 2022-12-14 17:00 | 2022-12-14 12:15 |  | WACCES | Remove sign frame
MSA-DFES | WA6650628 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room hallway - fluro lights not working (see notes) | Electrical | Lighting, Internal | 386.78 | Pass | Pass | -1 | -1 | 49.75 | 2023-02-20 12:10 | 2023-02-27 17:00 | 2023-02-21 07:00 | 2023-02-27 17:00 | 2023-02-23 08:45 |  | WACCES
MSA-DTWD | WA5487859 | 3 | AWB Co. | N25 - 2 x lights out | Electrical | General Electrical | 254.1 | Pass | Pass | 0 | 0 | 49.5 | 2022-06-02 08:57 | 2022-06-10 17:00 | 2022-06-08 11:45 | 2022-06-10 17:00 | 2022-06-10 13:15 |  | WACCES | Attended site signed in jsa completed. Got keys from office to get into room. Isolated r3 and removed timer switch for two row of lights with new plate and 20a switch mech. *** job is now completed ***
MSA-DFES | WA5586268 | 0 | MALCOLM THOMPSON PUMPS PTY LTD | applied training ground, bottom dam pump is making loud screeching noise | Mechanical Services | Pumps |  | Pass | Fail | 0 | 0 | 49.5 | 2022-07-06 12:01 | 2022-07-06 14:01 | 2022-07-06 12:30 | 2022-07-06 16:01 | 2022-07-08 14:00 |  |  | Removed pump, order seal and fit in pump reinstalled on site
MSA-DTAG | WA5609634 | 3 | Midolo Building Services | Basement - Cells 1 -5 - Security screws not to standard in cells - See notes below | Building | General Building | 654.81 | Pass | Fail | 0 | 0 | 49.5 | 2022-07-13 15:30 | 2022-07-20 17:00 | 2022-07-19 07:00 | 2022-07-20 17:00 | 2022-07-21 08:30 |  | WACCES | new screws installed to all areas stated below
MSA-DCA | WA5838313 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Address faults on security CCTV cameras, affected cameras include - see notes below | Security | CCTV Surveillance | 373.69 | Fail | Fail | 3 | 3 | 49.5 | 2022-09-08 12:16 | 2022-09-13 17:00 | 2022-10-04 08:00 | 2022-09-13 17:00 | 2022-10-06 09:30 |  |  | Performed fault finding. Found following cameras out of focus or color display incorrect.1508, 2107, 2108, 2206, 2412, 2414, 2415, 2416, 2404, 2509, 2515, 3005, 4019, 4225, 6013.Performed camera initialization and focusing.All listed cameras now operating ok.Checked by Security.
MSA-DTAG | WA6204589 | 3 | Australian HVAC Services Pty. Ltd. | Air Conditioning (above Court 5 stairwell) - Air con fault – No 11 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1102.8 | Pass | Pass | -1 | -1 | 49.5 | 2022-11-17 09:08 | 2022-11-24 17:00 | 2022-11-17 10:30 | 2022-11-24 17:00 | 2022-11-19 12:00 |  |  | Works complete
MSA-DTWD | WA6539460 | 2 | COMMERCIAL PLUMBING AND GAS | Mens student toilet - Toilet pan cistern is leaking onto the floor | Plumbing & Drainage | Toilets/Cisterns | 560.535 | Pass | Pass | -1 | 0 | 49.5 | 2023-02-08 13:20 | 2023-02-13 17:00 | 2023-02-08 15:30 | 2023-02-13 17:00 | 2023-02-10 17:00
MSA-DTWD | WA6531201 | 2 | Water2water Pty Ltd | Drinking fountain near room A230 - Water is not sufficiently cold | Plumbing & Drainage | HWS/Units Electric & Gas | 904.76 | Pass | Fail | 0 | 0 | 49.2667 | 2023-02-03 10:07 | 2023-02-08 17:00 | 2023-02-08 14:15 | 2023-02-08 17:00 | 2023-02-10 15:31 |  | WACCES
MSA-DFES | WA5378290 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Board Room Kitchen - Level 2 - Commissioners oven - not operating or turning on | Electrical | General Electrical | 149.805 | Pass | Fail | 0 | 0 | 49.25 | 2022-04-20 13:01 | 2022-04-21 17:00 | 2022-04-20 16:00 | 2022-04-21 17:00 | 2022-04-22 17:15 |  |  | Arrived on site at 1600 to investigate faulty oven in level 2 board room kitchen. Found power at oven however oven was not producing heat. Discovered faulty heating element and blown halogen globe within oven. Will need to return to site when parts have been ordered. Left site at 1715.
MSA-DTWD | WA5563500 | 3 | AWB Co. | Hot well tank compound - Pump causing relay to overheat. | Electrical | General Electrical | 585.92 | Pass | Pass | -1 | -1 | 49.25 | 2022-06-20 15:19 | 2022-06-27 17:00 | 2022-06-21 14:15 | 2022-06-27 17:00 | 2022-06-23 15:30 |  |  | Attended site and signed in. Completed JSA. Located hot well pump and control system. Ran through system and found the contactor for a pump to be burning out and running hot. Will require new replacement. Order parts and return. Signed out. Job not completeAttended site and signed in. Completed JSA. Located pump room control. Isolated switchboard. Supply and replace faulty contactor with new contactor and overload. Tested function all okay. Signed out. Job complete
MSA-DTWD | WA6535157 | 2 | Precise Air Group | AC 7 - Boiler Room not activating Fan Coil Unit | Air Conditioning | Room Air Conditioners | 1236.18 | Pass | Pass | 0 | 0 | 49.25 | 2023-02-06 14:50 | 2023-02-09 17:00 | 2023-02-07 10:00 | 2023-02-09 17:00 | 2023-02-09 11:15 |  | WACCES
MSA-DCA | WA6560297 | 0 | Property Fire Maintenance | Ground floor - Assembly area - Lock on the door isnt working and unable to close door | Fire Protection Services | Fire Protection - Monitor System | 530 | Pass | Fail | 0 | 0 | 49.1 | 2023-02-13 09:10 | 2023-02-13 11:10 | 2023-02-13 10:13 | 2023-02-13 13:10 | 2023-02-15 11:19 |  | WACCES
MSA-DFES | WA6401036 | 1 | Australian HVAC Services Pty. Ltd. | Coms Room - BSD fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1717.86 | Pass | Fail | 0 | 0 | 49.0769 | 2023-01-04 08:39 | 2023-01-05 17:00 | 2023-01-04 12:47 | 2023-01-05 17:00 | 2023-01-06 13:52
MSA-DTWD | WA5294735 | 2 | M Construction (WA) | A-Block - Level 2 - A233 - has a broken door hinge | Building | General Building | 190.18 | Pass | Pass | 0 | 0 | 49 | 2022-03-29 08:57 | 2022-04-01 17:00 | 2022-03-29 13:30 | 2022-04-01 17:00 | 2022-03-31 14:30 |  |  | Fixed broken door hinges
MSA-DTWD | WA5306404 | 2 | SCAVENGER SUPPLIES PTY LTD | Block 1 - Faulty EWIS system | Fire Protection Services | Fire Protection - Monitor System | 122.905 | Pass | Pass | -1 | 0 | 49 | 2022-04-06 13:08 | 2022-04-11 17:00 | 2022-04-06 15:00 | 2022-04-11 17:00 | 2022-04-08 16:00 |  |  | Attended the site after Dom the campus Manager called me explaining that the evacuation button on the EWIS system was still lit after completing a fire drill earlier in the day. Dom took me down to the EWIS and explained to me how he used it step by step when conducting the drill. Everything he said he did was correct, pressing the alert tone and then pressing it again to turn it off, then pressing the evac button to sound it and then pressing it again to turn it off. Dom then turned on the PA to speak then pressing it again to turn it off. As Dom turned off the PA he noticed that the Red led was still lit on the All Evac button but wasn't emitting the tone through the system. When I got to site the system was in isolation and the led was still lit. I tried to use the reset button but that did not succeed. I then conducted a hard reset, disconnecting the batteries and then turning the system off at the mains power. I then turned the system back on a couple of minutes later and then rec
MSA-MRWA | WA5611317 | 3 | AWB Co. | Level 8 - Executive Kitchen - Oven not turning on - See notes below - | Electrical | General Electrical | 353.985 | Pass | Pass | 0 | 0 | 49 | 2022-07-14 08:52 | 2022-07-21 17:00 | 2022-07-19 06:00 | 2022-07-21 17:00 | 2022-07-21 07:00 |  | WACCES | Attended site and signed in, completed jsa,went up to level 8 and isolated oven circuit, removed oven and took cover off , removed old timer, replaced with new, put cover back on and re energised circuit, tested oven , all working as intended, mounded oven in in cupboard , completed paperwork, packed up, signed out**job completed**
MSA-DCA | WA5689265 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - Level 5 - Chiller Faults - 4 faults | Refrigeration | Chiller | 709.45 | Pass | Fail | 0 | 0 | 49 | 2022-08-02 11:48 | 2022-08-03 17:00 | 2022-08-02 12:00 | 2022-08-03 17:00 | 2022-08-04 13:00 |  |  | Investigated issues with ets. Chiller 3 had faulted again and chiller 2 was in recycle mode due to temps being too low to start. Waiting on sensors to be replaced by Honeywell. Adjusted offsets to get chiller 2 to run. Not enough load for chiller 2 and chiller 4 to run together. Checked over actuators as temps and flow is showing a valve is shut and the chilled water isn't going to the field. Continued investigation on WA5692633
MSA-DTWD | WA5698234 | 2 | Protek 24/7 Building & Maintenance | Roof leak between roof access hatch and wall (possibly box gutter) | Roofing | Metal Roofing | 420.84 | Fail | Fail | 1 | 1 | 49 | 2022-08-09 15:57 | 2022-08-12 17:00 | 2022-08-16 11:15 | 2022-08-12 17:00 | 2022-08-18 12:15 |  |  | Removed old silicone seal and re sealed with new silicone
MSA-DCA | WA5018484 | 2 | EQUANS Mechanical Services (WA) Pty Limited | FCU in basement 1 is leaking water across the width of the unit. Leaking on to kitchen dish bench | Air Conditioning | Room Air Conditioners | 583.455 | Pass | Fail | 0 | 0 | 49 | 2022-01-14 12:03 | 2022-01-19 17:00 | 2022-01-18 08:30 | 2022-01-19 17:00 | 2022-01-20 09:30 |  |  | Investigated ac leaking water onto bench top. Found condensate pump not working. Power being supplied but pump not starting. Isolated power and removed faulty condensate pump. Sourced new and replaced. Restored power and tested operation, all ok. Completed paperwork.
MSA-DTWD | WA5407947 | 3 | AWB Co. | Block 3 - Ground - Metal Fabrication 1 workshop - Faulty coolant pump on Radial Arm drill | Electrical | General Electrical | 447.42 | Pass | Fail | 0 | 0 | 49 | 2022-05-11 15:18 | 2022-05-18 17:00 | 2022-05-17 13:00 | 2022-05-18 17:00 | 2022-05-19 14:00 |  | WCAPPR | Attended site signed in jsa completed. Unplugged drill and removed motor for coolant spray. Left tail isolated in junction box and sealed for protection. Plugged drill back in and found now power to gpo. Tested fuses in board and two fuses blew up. Replaced with new fuses in board and now drill works . *** job completed ***
MSA-DTWD | WA5200902 | 1 | Protek 24/7 Building & Maintenance | Walk way north side - Paving collapsing | Paving & Roadworks | Paving | 310.75 | Pass | Fail | 0 | 0 | 48.75 | 2022-03-02 10:07 | 2022-03-03 17:00 | 2022-03-02 14:15 | 2022-03-03 17:00 | 2022-03-04 15:00 |  |  | Walk way north side - Paving collapsing
MSA-DTAG | WA5106939 | 1 | Midolo Building Services | Interview Room 3 - window frame unsecure since glass had been replaced | Building | General Building | 277.42 | Fail | Fail | 0 | 0 | 48.5 | 2022-02-07 12:59 | 2022-02-08 17:00 | 2022-02-09 07:00 | 2022-02-08 17:00 | 2022-02-11 07:30 |  |  | WINDOW FRAMED SECURED/REPAIRED
MSA-DTWD | WA6683942 | 1 | WESTERN IRRIGATION PTY LTD | Front Lawn Right Hand Side of Driveway Entrance | Plumbing & Drainage | Drainage |  | Pass | Fail | 0 | 0 | 48.5 | 2023-03-03 13:59 | 2023-03-07 17:00 | 2023-03-07 12:00 | 2023-03-07 17:00 | 2023-03-09 12:30
MSA-DTWD | WA5398633 | 0 | Precise Air Group | Compressors have stopped working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 510.48 | Pass | Fail | 0 | 0 | 48.4833 | 2022-05-09 11:43 | 2022-05-09 13:43 | 2022-05-09 12:30 | 2022-05-09 15:43 | 2022-05-11 12:59 |  |  | On site for maintenance nessco needed for investigation
MSA-DFES | WA5087992 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Outside - Ground - Rear pillar hydrant is is continually leaking even when closed | Plumbing & Drainage | Water | 677.91 | Pass | Pass | 0 | 0 | 48.4167 | 2022-01-24 16:39 | 2022-01-28 17:00 | 2022-01-25 08:30 | 2022-01-28 17:00 | 2022-01-27 08:55 |  | WACCES | Checked fire Hayden found its unserviceable have ordered a new one in and will return when it comes in.Returned back to site with new parts tested and all working correctly.
MSA-DTAG | WA5655694 | 1 | Sapio Pty Ltd | Car park - Custody control room - Bail room door not working correctly | Security | Access Control | 748.26 | Pass | Fail | 0 | 0 | 48.25 | 2022-07-18 09:56 | 2022-07-19 17:00 | 2022-07-19 09:00 | 2022-07-19 17:00 | 2022-07-21 09:15 |  | WACCES | Installed back up battery to Custody door PSU, tested, all OK.
MSA-DTWD | WA5511989 | 2 | M Construction (WA) | Workshops - emergency egress door between room 7 and 8 - Door is sticking to open | Building | Doors | 453.23 | Pass | Pass | 0 | 0 | 48.0667 | 2022-06-13 11:56 | 2022-06-16 17:00 | 2022-06-14 11:30 | 2022-06-16 17:00 | 2022-06-16 11:34 |  |  | Attended site to investigate emergency door not opening, shaved down door on both the sides and the top. Re-housed mortice lock and bogged up old nails holes and painted.
MSA-DTWD | WA5479543 | 2 | Precise Air Group | E-Block - stores area has a under bench fridge tripping power | Refrigeration | Refrigerators | 340.14 | Pass | Pass | -1 | 0 | 48.05 | 2022-05-27 10:04 | 2022-06-01 17:00 | 2022-05-28 09:25 | 2022-06-01 17:00 | 2022-05-30 09:28 |  |  | Attended site inspected fridge. Found comp down to earth. Decommissioned and disposed of fridge.
MSA-DTWD | WA5115881 | 2 | Equans Mechanical Services Australia | F30 - Water leaking from aircon unit onto computer – western end unit | Air Conditioning | Room Air Conditioners | 764.57 | Pass | Pass | 0 | 0 | 48 | 2022-02-11 09:56 | 2022-02-16 17:00 | 2022-02-14 12:00 | 2022-02-16 17:00 | 2022-02-16 12:00 |  |  | Diagnosis found drain pump failure, purchased new removed old and replaced with new. Completed paperwork.
MSA-DTAG | WA5204727 | 3 | Sapio Pty Ltd | Level 10 - fire door not working | Security | Access Control | 1740.83 | Pass | Pass | -1 | -1 | 48 | 2022-03-04 12:54 | 2022-03-14 17:00 | 2022-03-08 15:00 | 2022-03-14 17:00 | 2022-03-10 15:00 |  |  | Installed Gallagher HBUS cable from Level 11 controller to Level 10 fire door. Reinstalled card readers and confirmed correct operation.
MSA-DTWD | WA5226759 | 1 | Australian HVAC Services Pty. Ltd. | Whole site - BMS System off line | Air Conditioning | Room Air Conditioners | 577.44 | Pass | Fail | 0 | 0 | 48 | 2022-03-09 12:20 | 2022-03-10 17:00 | 2022-03-09 12:30 | 2022-03-10 17:00 | 2022-03-11 12:30 |  |  | Recieved service call due to BMS being offline. Reset bms and tested ups. Ups works but one plug was on surge side.Spoke with it and they advised there were no power outages.Monitored system after reset and found that level 1 didn't start. Reset time schedule for level 1 then it started and worked fine.Monitored further and found all ok.BMS technician to return on Thursday and invetigate further.Attended site to check BMS was online. Found it was online and plant was operating correctly.
MSA-DTWD | WA5276188 | 3 | Workzone Pty Ltd | Main entrance Oxford St -Graffiti on the Oxford St walls and Richmond St shed | Cleaning | Graffiti | 806.03 | Pass | Pass | 0 | 0 | 48 | 2022-03-18 12:32 | 2022-03-25 17:00 | 2022-03-22 08:30 | 2022-03-25 17:00 | 2022-03-24 08:30 |  |  | Remove graffiti as per scope
MSA-DTWD | WA5278466 | 3 | AWB Co. | B5 - Level 2 - A252 store room - Light fitting damaged, caused by impact | Electrical | General Electrical | 418.73 | Pass | Pass | -1 | 0 | 48 | 2022-03-18 15:24 | 2022-03-25 17:00 | 2022-03-21 14:30 | 2022-03-25 17:00 | 2022-03-23 14:30 |  | WCAPPR | Attended site and signed in. Completed jsa. Spoke to fm. Re located store room. Wired plug into light fitting. Set up ladder and mounted light fitting to wall. Put light fitting together. Plugged in. Test and tagged. Turned on switch. Light is working as intended. Took picture. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5294240 | 2 | M Construction (WA) | E block - ground - Male toilets - wall bench has come away from its wall fixings | Building | Internal Walls | 696.74 | Pass | Pass | 0 | 0 | 48 | 2022-03-28 14:45 | 2022-03-31 17:00 | 2022-03-29 13:30 | 2022-03-31 17:00 | 2022-03-31 13:30 |  |  | Remove brackets from bench seat and reinstall.
MSA-DTWD | WA5513148 | 2 | AWB Co. | Undercover lights sparking when turned on | Electrical | Lighting, Internal | 158.3 | Pass | Pass | 0 | 0 | 48 | 2022-06-14 08:10 | 2022-06-17 17:00 | 2022-06-15 14:30 | 2022-06-17 17:00 | 2022-06-17 14:30 |  | WCAPPR | Attended site and signed in. Completed JSA. Spoke with Liam regarding his visit to job and he advised to replace the lamps to the fittings and leave the existing lights there. Site has lamps. Used sites stock to replace the lamps in the fittings tested all okay. Lights working. Signed out. Job complete
MSA-DTWD | WA6430981 | 2 | AWB Co. | 1st Floor Hallway- Light outside 8F57A not working. RCD tripped ant wont re- set | Electrical | Lighting, Internal | 350.435 | Pass | Fail | 0 | 0 | 48 | 2023-01-13 10:58 | 2023-01-18 17:00 | 2023-01-18 14:30 | 2023-01-18 17:00 | 2023-01-20 14:30 |  | WACCES
MSA-DTAG | WA5693813 | 3 | AHS Services WA Pty Ltd (Anchor) | L8-Toilet button is not working in male toilets | Plumbing & Drainage | Toilets/Cisterns | 596.47 | Pass | Pass | 0 | 0 | 47.75 | 2022-08-04 15:35 | 2022-08-11 17:00 | 2022-08-08 14:00 | 2022-08-11 17:00 | 2022-08-10 13:45 |  |  | Pneumatic flush buttons not working, required replacement.
MSA-DTWD | WA6518323 | 1 | Critical Fire Protection & Training | Fire panel - Device fault and low battery | Fire Protection Services | Fire Protection - Monitor System | 364.66 | Pass | Fail | 0 | 0 | 47.6667 | 2023-01-25 07:27 | 2023-01-25 17:00 | 2023-01-25 08:50 | 2023-01-25 17:00 | 2023-01-27 08:30
MSA-DTAG | WA6190420 | 0 | Seme Solutions Pty Ltd | Camera Issues - See Notes below | Security | CCTV Surveillance | 909.22 | Fail | Fail | 0 | 0 | 47.65 | 2022-11-16 08:19 | 2022-11-16 10:19 | 2022-11-16 10:30 | 2022-11-16 12:19 | 2022-11-18 10:09 |  |  | Cctv 1 server back online
MSA-DTWD | WA5383109 | 2 | SENTINEL LOCK SERVICE PTY LTD | Room FG10 - The door lock seems jammed and can’t be locked | Security | Locksmith | 101.09 | Pass | Fail | 0 | 0 | 47.6328 | 2022-04-27 12:10 | 2022-05-02 17:00 | 2022-05-02 12:00 | 2022-05-02 17:00 | 2022-05-04 11:38
MSA-DTWD | WA4991446 | 0 | Australian HVAC Services Pty. Ltd. | The Whole Complex - air con has shut down | Air Conditioning | Building HVAC Maintenance (Major Plant) | 925.41 | Pass | Fail | 0 | 0 | 47.5 | 2022-01-05 08:38 | 2022-01-05 10:38 | 2022-01-05 09:00 | 2022-01-05 12:38 | 2022-01-07 08:30 |  |  | Douglas Posthuma (06/01/2022) - Work NoteAttended site and found jace controller down again.Plugged in power pack and power cycled jace and found it connected within 5 minutesHvac Plant started and ran up properlyMonitored plant. Sourced a small table and power pack and placed in server room and connected all.Returned to sute following day and checked the system had come on & the jace was working.found it had and the bms was operating correctlyDouglas Posthuma (05/01/2022) - Work NoteCalled out because no aircon working in building.Attended site. Found bms desktop pc with comms lossRan network diagnostic test on desktop pc, result was no communication to end devicePower cycled Jace controller and network switchesChecked various Controllers for power and found they were all ready to operate but no comms from head end stopped them from startingCame back in and found desktop pc was able to access bms. So all AC plant should have startedChecked ahu 10 and foun
MSA-DTWD | WA5200921 | 1 | Protek 24/7 Building & Maintenance | Various roof leaks. Roof, gutter clean and inspection. | Roofing | Metal Roofing | 425.5 | Pass | Fail | 0 | 0 | 47.5 | 2022-03-02 10:19 | 2022-03-03 17:00 | 2022-03-02 13:15 | 2022-03-03 17:00 | 2022-03-04 12:45 |  |  | Various roof leaks
MSA-DTWD | WA5238553 | 3 | Falcetta Plumbing and Gas | A253 - student Kitchen - HW system has spilt tank | Plumbing & Drainage | Water | 1493.92 | Pass | Pass | -1 | -1 | 47.5 | 2022-03-16 07:30 | 2022-03-22 17:00 | 2022-03-16 18:00 | 2022-03-22 17:00 | 2022-03-18 17:30 |  |  | replaced hot water system and installed tmv
MSA-DCA | WA6537217 | 1 | EQUANS Mechanical Services (WA) Pty Limited | First Floor - Plant Room - Chiller 2 in fault | Refrigeration | Chiller | 1342.79 | Pass | Fail | 0 | 0 | 47.5 | 2023-02-07 07:53 | 2023-02-07 17:00 | 2023-02-07 15:00 | 2023-02-07 17:00 | 2023-02-09 14:30
MSA-DFES | WA5834448 | 1 | Anvil Doors | Engine room -External door number 3 is not closing | Building | Doors | 528 | Pass | Fail | 0 | 0 | 47.45 | 2022-09-06 19:37 | 2022-09-07 17:00 | 2022-09-07 10:25 | 2022-09-07 17:00 | 2022-09-09 09:52 |  |  | Safety Beam out of alignment
MSA-DCA | WA5520716 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - Plant room - Chiller 1 in fault | Refrigeration | Chiller | 397.675 | Pass | Pass | -1 | 0 | 47.2167 | 2022-06-15 10:03 | 2022-06-20 17:00 | 2022-06-15 14:55 | 2022-06-20 17:00 | 2022-06-17 14:08 |  |  | Returned to site gained access and completed inspection of chiller. All OK. No further faults have occured. Work area left tidy.
MSA-DTWD | WA5142303 | 1 | Techworks Plumbing | Campus - Ground - Water leak on campus (unknown location of leak) | Plumbing & Drainage | Water | 926.23 | Pass | Fail | 0 | 0 | 47 | 2022-02-09 08:45 | 2022-02-10 17:00 | 2022-02-09 09:00 | 2022-02-10 17:00 | 2022-02-11 08:00 |  |  | Kyle Pace (09/02/2022) - Work NoteAttended sight to find leak in south metro Tafe Rockingham, meter is spinning the kiloliters needle around every 4 seconds, walked around the premises and around the building block, had a walk through bathrooms and visually could not find any water or damage caused by water or any trials left behind, the school is in operation so I cannot isolate buildings, have confirmed with maintenance guy Dennis for our arrival on Friday 11/02/22 @5:30/6am the school doesn’t opened until 8am Patrick Granholm (11/02/2022) - Work NoteTravel to site and inspected meter, before anyone arrives at Tafe, meter is spinning constantly,Looked at plan and attempted to track pipe work, to see if any obvious wet area, no wet area present,Looked for main isolations valves around campus, unwind to find any,Isolated small isolations for bathrooms in building ,meter still spinning, Unable to find leak, Leak detection specialists required
MSA-DTAG | WA5400279 | 1 | AHS Services WA Pty Ltd (Anchor) | Temporary roof repair to back roof - see notes below | Roofing | Metal Roofing | 650.34 | Pass | Fail | 0 | 0 | 47 | 2022-05-10 09:08 | 2022-05-11 17:00 | 2022-05-10 10:30 | 2022-05-11 17:00 | 2022-05-12 09:30 |  |  | Started job before job was logged. As per signature slip.
MSA-DFES | WA6681527 | 0 | Australian HVAC Services Pty. Ltd. | re-fuel the generator | Equipment | Compressors, Generators | 1290.435 | Pass | Fail | 0 | 0 | 47 | 2023-03-02 09:18 | 2023-03-02 11:18 | 2023-03-02 10:00 | 2023-03-02 13:18 | 2023-03-04 09:00
MSA-DTWD | WA5186728 | 3 | Water2water Pty Ltd | B1 - Level 2 - S216 - Warm water from cold outlet Billie unit | Plumbing & Drainage | HWS/Units Electric & Gas | 226.9625 | Pass | Fail | 0 | 0 | 46.9333 | 2022-02-22 08:52 | 2022-03-01 17:00 | 2022-02-28 12:50 | 2022-03-01 17:00 | 2022-03-02 11:46 |  | WACCES | Returned unit to site. Connected unit and ran to temp. Billi SAHARA unit working fine. No chilled water from this unit. Normal operation
MSA-DTAG | WA5216539 | 2 | Sapio Pty Ltd | Security Desk - Court 1,5,6 duress alarms work - see notes below | Security | Monitoring | 310 | Pass | Pass | 0 | 0 | 46.8167 | 2022-03-11 11:02 | 2022-03-16 17:00 | 2022-03-14 09:26 | 2022-03-16 17:00 | 2022-03-16 08:15 |  |  | Attended and reconfigured duress alarms for judicial and magistrates courts on Court Rooms 1, 5, and 6. Conducted testing with court security and confirmed all duress alarms reporting through to Gallagher Duress Map View as required. All good.
MSA-DFES | WA5563147 | 3 | Protek 24/7 Building & Maintenance | Main Building - Dormitory 11 - inner door has come off the runner and does not slide freely | Building | Doors | 234.25 | Pass | Pass | -1 | -1 | 46.75 | 2022-06-20 12:09 | 2022-06-27 17:00 | 2022-06-21 11:00 | 2022-06-27 17:00 | 2022-06-23 09:45 |  |  | Repair sliding door and refit
MSA-DTWD | WA6509487 | 1 | Equans Mechanical Services Australia | C Block - CG42 - Server room - Daiken split system unit is leaking water from vents | Air Conditioning | Room Air Conditioners | 219.6 | Pass | Fail | 0 | 0 | 46.75 | 2023-01-20 11:19 | 2023-01-23 17:00 | 2023-01-23 10:15 | 2023-01-23 17:00 | 2023-01-25 09:00
MSA-DTAG | WA5862244 | 1 | Midolo Building Services | Corridor next to Justice Mazza chambers (near lift 4) - Leak in ceiling | Building | Ceiling | 1247 | Pass | Fail | 0 | 0 | 46.75 | 2022-09-13 15:10 | 2022-09-14 17:00 | 2022-09-14 10:00 | 2022-09-14 17:00 | 2022-09-16 08:45 |  | WACCES | Using a boom lift. Unblocked/cleaned down pipes as they could be a potential roof leak cause
MSA-DTWD | WA5286227 | 2 | AWB Co. | B block - External lights on during the day - P.E cell may be faulty | Electrical | General Electrical | 521.02 | Pass | Pass | 0 | 0 | 46.5 | 2022-03-21 13:39 | 2022-03-24 17:00 | 2022-03-21 14:00 | 2022-03-24 17:00 | 2022-03-23 12:30 |  | WCAPPR | Attended site signed in completed jsa. replaced faulty pe cell in B block.Lights work fine now and tested with cover.Job completed
MSA-DTWD | WA5548707 | 3 | AWB Co. | Faulty Data points 48 & 156 IT suspect damaged cable | Electrical | General Electrical | 358.46 | Pass | Pass | 0 | 0 | 46.5 | 2022-06-17 08:52 | 2022-06-24 17:00 | 2022-06-22 13:30 | 2022-06-24 17:00 | 2022-06-24 12:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Located data rack and the outlets in the office. Tested port 48 found to be okay. Tested patch lead and found to be faulty. Used sites leads and replaced patch lead. Tested port 156 and found no connection. Located port under desk back to patch panel and found to be 157. Patched in and tested. Both ports working and ready for service. Advised site. Signed out. Job complete
MSA-DTWD | WA6165958 | 1 | COMMERCIAL PLUMBING AND GAS | Waste water pipe is leaking in ceiling space | Plumbing & Drainage | Water | 692.485 | Pass | Pass | 0 | 0 | 46.5 | 2022-11-11 11:02 | 2022-11-14 17:00 | 2022-11-11 15:00 | 2022-11-14 17:00 | 2022-11-13 13:30 |  |  | replaced damaged PE pipe with new pvc
MSA-DCA | WA6399916 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Level - Fridge/Freezer not working | Refrigeration | Freezers | 2172.16 | Pass | Fail | 0 | 0 | 46.5 | 2023-01-03 08:13 | 2023-01-04 17:00 | 2023-01-03 14:30 | 2023-01-04 17:00 | 2023-01-05 13:00
MSA-DCA | WA5187630 | 1 | EQUANS Mechanical Services (WA) Pty Limited | roof plant room - chiller 2 condenser water pump issue | Air Conditioning | Room Air Conditioners | 1550.775 | Pass | Fail | 0 | 0 | 46.4667 | 2022-02-22 14:02 | 2022-02-23 17:00 | 2022-02-22 14:02 | 2022-02-23 17:00 | 2022-02-24 12:30 |  |  | Carried out condenser water pump 2 alarms with Schneider. Found the differential pressure switch faulty giving an incorrect status reading to the bms which is causing the alarms and lockouts. Schneider has temporary removed the plant lockout controls Logic until the differential pressure switch is replaced. A quote is being organised to carry out replacement of faulty DP switch.
MSA-DTWD | WA5670793 | 1 | Precise Air Group | Library is very cold-This is a BMS and Air/Con issue, NRP will need to engaged by Precise Air | Air Conditioning | Building HVAC Maintenance (Major Plant) | 522.86 | Pass | Fail | 0 | 0 | 46.3667 | 2022-07-20 08:13 | 2022-07-21 17:00 | 2022-07-20 15:18 | 2022-07-21 17:00 | 2022-07-22 13:40 |  | WACCES | Travelled to site, gained access, spoke with site contact in library noticed area very cold, checked operation of ahu 6, found no faults check boilers all ok. Found on BMS VAV 6.7 is in 100% causing ahu to feed 10 degrees supply air, isolated VAV 6.7, checked sensor found sensor requires replacing. Parts to be ordered. Picked up parts returned to site, isolated equipment, removed sensor, installed new sensor calibrated, checked operation, cleared debris from site
MSA-DTWD | WA5105792 | 2 | JEM Carpentry | trip hazard pavers | Paving & Roadworks | Paving |  | Pass | Fail | 0 | 0 | 46 | 2022-02-04 14:10 | 2022-02-09 17:00 | 2022-02-09 11:00 | 2022-02-09 17:00 | 2022-02-11 09:00 |  |  | job completed - replaced Sand and Pavers
MSA-DCA | WA5722557 | 0 | Critical Fire Protection & Training | 2 faulty fire detector causing the fire alarm | Fire Protection Services | Fire Protection - Monitor System | 308.22 | Pass | Fail | 0 | 0 | 46 | 2022-08-13 12:58 | 2022-08-13 14:58 | 2022-08-13 14:00 | 2022-08-13 16:58 | 2022-08-15 12:00 |  |  | .
MSA-DTWD | WA5781347 | 2 | AWB Co. | Light fitting in canopy on left hand side not working-see notes | Electrical | Lighting, Internal | 374.81 | Pass | Fail | 0 | 0 | 46 | 2022-08-19 16:37 | 2022-08-24 17:00 | 2022-08-23 09:00 | 2022-08-24 17:00 | 2022-08-25 07:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Located cleaner to gain access to E bock. Set up work area in E75. Removed cover from range hood. Isolated circuit requiring works. Removed old faulty fitting. Supplied and replaced with new LED batten. Energised circuit and tested for correct operation. Placed cover back on. Packed up work area. Notified relevant personnel of works done. **job complete**
MSA-DTWD | WA6539459 | 2 | COMMERCIAL PLUMBING AND GAS | L2 East Disabled toilet | Plumbing & Drainage | Toilets/Cisterns | 353.2 | Pass | Pass | -1 | 0 | 46 | 2023-02-08 13:16 | 2023-02-13 17:00 | 2023-02-08 15:00 | 2023-02-13 17:00 | 2023-02-10 13:00
MSA-DTAG | WA5309931 | 0 | Automatic Fire Protection (ARA) | Fire panel is in alarm - Unable to isolate. | Fire Protection Services | Fire Protection - Monitor System | 758.35 | Fail | Fail | 0 | 0 | 46 | 2022-04-10 15:09 | 2022-04-10 17:09 | 2022-04-10 17:30 | 2022-04-10 19:09 | 2022-04-12 15:30 |  |  | Earth fault coming building 87 SIP. Discovered earth fault coming from south link fire door holders (link between main building and building 87on south side). Door holders require tiny Allen key to open up to see connections which I didn’t have so I disconnected door holders from SIPto keep it fault free for the time being. Doors are closed whilst door holder disconnected. Door holders are doubled up on relay 1 with anotherset of doors in N/C terminal. Unsure if it’s door holder or cabling issue as I couldn’t disconnect cabling from holders.12/04/22 CS/EIAttended site & investigated the the South link door holder earth fault.Disconnected the 2 x door holders on the water damaged south link & observed the earth fault reset.Re-instated the relay 1 door holder output termination in the SIP & made safe the 2 x disconnected door holders at the south link.1 x 300mm universal door magnet required from AMPAC.1 x wall mounted 150mm universal door magnet required from AMPAC.The SIP is
MSA-DTWD | WA6131959 | 2 | ECO PLUMBING AND GAS PTY LTD | 2 leaking Taps in glazing workshop | Plumbing & Drainage | Water | 275.007 | Pass | Fail | 0 | 0 | 45.8167 | 2022-10-31 10:48 | 2022-11-03 17:00 | 2022-11-02 19:32 | 2022-11-03 17:00 | 2022-11-04 17:21 |  | WCAPPR | Replaced 1 tap other two wouldn’t isolate have to return to turn water off to college and replace taps
MSA-DTWD | WA6650945 | 2 | SCAVENGER SUPPLIES PTY LTD | Caged compound in “Pit” area - Fire extinguisher faulty | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 125.87 | Fail | Fail | 1 | 1 | 45.6833 | 2023-02-20 14:53 | 2023-02-23 17:00 | 2023-02-27 13:38 | 2023-02-23 17:00 | 2023-03-01 11:19
MSA-DTWD | WA5390689 | 2 | AWB Co. | 2 faulty fluro fittings | Electrical | Lighting, Internal | 238.74 | Pass | Fail | 0 | 0 | 45.5333 | 2022-05-02 15:00 | 2022-05-05 17:00 | 2022-05-04 09:28 | 2022-05-05 17:00 | 2022-05-06 07:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Got keys off cleaner. Located faulty lights. Replaced tubes. Took pictures, completed paperwork . Job complete
MSA-DTWD | WA5226910 | 3 | AWB Co. | Gym - Level 1 - Light not working - Light fitting approx 4m above floor level | Electrical | General Electrical | 416.81 | Pass | Pass | -1 | 0 | 45.5 | 2022-03-14 15:08 | 2022-03-21 17:00 | 2022-03-16 10:30 | 2022-03-21 17:00 | 2022-03-18 08:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Spoke to fm about job. Went inside and located 12ft platform ladder on site. Took ladder over to faulty light fitting in gym area. Took out globe to see what it was. Rang up pro lamps to see if they had any stock of this globe. They did. Went to pro lamps to pick up part. Returned to site. Put globe in light fitting. Light I now working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5382081 | 3 | Equans Mechanical Services Australia | Level 5 - Cooling towers - 1 drive belts loose | Air Conditioning | Room Air Conditioners | 815.35 | Pass | Pass | -1 | -1 | 45.5 | 2022-04-26 13:41 | 2022-05-03 17:00 | 2022-04-27 14:30 | 2022-05-03 17:00 | 2022-04-29 12:00 |  |  | Replaced the belts on cooling tower one
MSA-DTWD | WA5604035 | 3 | Protek 24/7 Building & Maintenance | B328- Damaged Lino in 3 x spots | Flooring | Vinyl | 586.54 | Pass | Pass | -1 | -1 | 45.5 | 2022-07-12 15:15 | 2022-07-19 17:00 | 2022-07-13 13:00 | 2022-07-19 17:00 | 2022-07-15 10:30 |  | WACCES | repaired damaged lino
MSA-DTWD | WA6108752 | 3 | AWB Co. | Dry goods store and Dish washing room - Lights working intermittently - See notes | Electrical | Lighting, Internal | 1230.005 | Pass | Pass | 0 | 0 | 45.5 | 2022-10-20 10:52 | 2022-10-27 17:00 | 2022-10-25 13:30 | 2022-10-27 17:00 | 2022-10-27 11:00 |  | WACCES | Attended site signed in jsa completed. Removed x4 fittings in canteen and replaced with new LED lights. Tested operational.Job completed
MSA-DFES | WA5127336 | 3 | Anvil Doors | Roller Door alarm - alarm continues to sound and may need a switch to override | Building | Automatic Doors | 648 | Pass | Pass | -1 | -1 | 45.3333 | 2022-02-14 12:40 | 2022-02-21 17:00 | 2022-02-14 12:40 | 2022-02-21 17:00 | 2022-02-16 10:00 |  |  | Attended Perth Fire station and installed pedestrian alarm override switch
MSA-DTWD | WA5305170 | 2 | AWB Co. | A Block - Ground - A20 - Double GPO has been pulled off the wall | Electrical | General Electrical | 443.45 | Pass | Pass | 0 | 0 | 45.25 | 2022-04-05 12:47 | 2022-04-08 17:00 | 2022-04-06 10:00 | 2022-04-08 17:00 | 2022-04-08 07:15 |  | WCAPPR | Attended site signed in completed jsa. got cleaner to let us into A block to finish works. Isolated circuit and moved power point higher. Patched hole with a mdf sheet as instructed. Also identified what circuit it was and labelled correctly as per photos.*** job completed ***
MSA-DTWD | WA5090357 | 3 | AWB Co. | North Block - Level 1 - N106 - A lights need replacing | Electrical | Lighting, Internal | 406.09 | Pass | Fail | 0 | 0 | 45 | 2022-01-25 11:32 | 2022-02-02 17:00 | 2022-02-01 14:45 | 2022-02-02 17:00 | 2022-02-03 11:45 |  | WCAPPR | Attended site, signed in , reviewed JSA, spoke to security and got keys, went to cafe and isolated lighting circuit, removed old light fitting, disposed of in bin , fixed new light to cling , wired up light , re energised lighting circuit and colour matched light, cleaned up , packed up, completed paperwork , signed out**job completed **
MSA-DTAG | WA5655863 | 1 | Total Security Systems Pty Ltd | Court 3 duress alarm on the Magistrates desk in Court 3.-will not reset | Security | Security Management System | 1198.5 | Pass | Fail | 0 | 0 | 45 | 2022-07-18 10:50 | 2022-07-19 17:00 | 2022-07-18 13:00 | 2022-07-19 17:00 | 2022-07-20 10:00 |  |  | 18/7/2022 - Jose Pereiratravel to site 1pm to 2.30pmtime on site 2.30pm to 3pmtravel from site 3.30pm to 5pmDuress cover had been broken off replacement needed20/7/2022 - Jose Pereiratravel to site 6.30am to 8amtime on site 8am to 8.30amtravel from site 8.30am to 10amInstalled and commissioned replacement duress in court 2
MSA-DTWD | WA5686814 | 2 | Protek 24/7 Building & Maintenance | Roof leak SW side of classroom, near windows - See notes below | Roofing | Metal Roofing | 562.52 | Pass | Fail | 0 | 0 | 45 | 2022-08-01 10:59 | 2022-08-04 17:00 | 2022-08-03 14:00 | 2022-08-04 17:00 | 2022-08-05 11:00 |  | WCAPPR | Repair Roof leak
MSA-DTWD | WA6364799 | 1 | Critical Fire Protection & Training | Library - Approx 75mm fire sprinkler pipe leaking at height. | Fire Protection Services | Sprinkler Systems | 3273.16 | Pass | Fail | 0 | 0 | 45 | 2022-12-12 15:08 | 2022-12-13 17:00 | 2022-12-12 17:00 | 2022-12-13 17:00 | 2022-12-14 14:00 |  |  | Attended site to investigate leak on sprinkler system in building b2.Leak in library west end on a threaded joint. There is a coupling on the other end withtwo back to back 15mm paps for sprinklers.I have drained the system to prevent any damage.An EWP will be needed to access the sprinkler pipe.The main stop valve on the sprinkler system will not fully close so we had to isolate thepumps as the jacking pump was turning on and off every 2 seconds which would burnout the pump.
MSA-DTWD | WA6515971 | 1 | Equans Mechanical Services Australia | Water coming out of the roof due to the condensation - AC (see notes) | Air Conditioning | Cooling Tower | 534.915 | Pass | Fail | 0 | 0 | 45 | 2023-01-23 08:01 | 2023-01-24 17:00 | 2023-01-23 12:30 | 2023-01-24 17:00 | 2023-01-25 09:30
MSA-DCA | WA6650559 | 0 | GPS Plumbing & Gas Services PtyLtd | mezzanine level - near Elevator - Male staff toilets - Tap wont turn off | Plumbing & Drainage | Water | 737.775 | Pass | Fail | 0 | 0 | 44.9167 | 2023-02-20 11:51 | 2023-02-20 13:51 | 2023-02-20 12:20 | 2023-02-20 15:51 | 2023-02-22 09:15 |  | WACCES
MSA-DFES | WA6668290 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Duty Room Area - Lights faulty (see notes) | Electrical | Lighting, Internal | 463.5475 | Pass | Pass | -1 | -1 | 44.75 | 2023-02-22 08:13 | 2023-03-01 17:00 | 2023-02-22 13:30 | 2023-03-01 17:00 | 2023-02-24 10:15 |  | WCAPPR
MSA-DTWD | WA6675132 | 2 | Equans Mechanical Services Australia | Eastern & Western evaps not cooling | Air Conditioning | Ducted Split System | 855.1575 | Pass | Fail | 0 | 0 | 44.75 | 2023-02-27 15:51 | 2023-03-02 17:00 | 2023-03-01 13:45 | 2023-03-02 17:00 | 2023-03-03 10:30
MSA-DFES | WA6132352 | 1 | SONTEC WA PTY LTD | Back gate won't open with the intercom system but will open with fobs and swipe card | Security | Access Control | 973.3 | Pass | Fail | 0 | 0 | 44.5 | 2022-10-31 13:31 | 2022-11-01 17:00 | 2022-10-31 14:30 | 2022-11-01 17:00 | 2022-11-02 11:00 |  |  | 31/10/22 - Dylan ParslowFound all yard cameras and intercoms offline.Power switched off at breaker for mid yard enclosures, due to contractors working on the gate.Switched on and tested, all working.2/11/22 - Dylan ParslowRecalled due to issue returning.Found door controller in mid enclosure as cause for comms issue.Likely caused by the power shutdown on circuit for extended period.Replaced door controller and tested, all ok.
MSA-DFES | WA5399169 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Station exterior next to kitchen/courtyard - see notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 503.44 | Pass | Fail | 0 | 0 | 44.4667 | 2022-05-09 16:28 | 2022-05-16 17:00 | 2022-05-16 14:02 | 2022-05-16 17:00 | 2022-05-18 10:30 |  | WCAPPR | 16.05.2022Inspecting the kitchen mixer tap and temperature. Water is running at 68 degrees Celsius. Electric hot water unit outside does not have a tempering valve on it. Supplied new tempering valve and parts,will return on site next day, Station’s staff had to leave.18.05.2022Removing old pipes from hot water unit. Installing tempering valve, new pipes and fittings. Tested for leaks, tested temperature, all works good
MSA-DTWD | WA5190056 | 2 | AWB Co. | Several fluros on High Ceiling not working | Electrical | Lighting, Internal | 503.115 | Pass | Fail | 0 | 0 | 44.25 | 2022-02-24 10:23 | 2022-03-01 17:00 | 2022-02-28 12:30 | 2022-03-01 17:00 | 2022-03-02 08:45 |  | WCAPPR | Attended site signed in completed jsa. Located room d210 and cleaned out diffusers with vacuum. 12 fittings all up had bees inside and rubbish. Advised site of job completion***JOB COMPLETED***
MSA-DCA | WA5486654 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - High pitched noise coming from inside plant room | Air Conditioning | Building HVAC Maintenance (Major Plant) | 397.675 | Pass | Fail | 0 | 0 | 44.1167 | 2022-06-01 09:33 | 2022-06-02 17:00 | 2022-06-01 13:07 | 2022-06-02 17:00 | 2022-06-03 09:14 |  |  | Returned to site gained access and rechecked plant room areas and equipment for high pitched sound. Confirmed with staff that sound had not reoccured during the previous business day. No further action able to be taken. Staff will need to advise if sound reoccurs. Currently there are no active system faults. Work area left tidy.
MSA-DTWD | WA5477365 | 3 | Precise Air Group | Block A - Cafe -temperature probe in the cold display unit faulty | Refrigeration | Refrigerators | 703.235 | Pass | Pass | -1 | -1 | 44 | 2022-05-25 13:18 | 2022-06-01 17:00 | 2022-05-25 14:00 | 2022-06-01 17:00 | 2022-05-27 10:00 |  |  | Attended supplier and collected temp probe. Attended site and completed pre start paperwork and signed in. Isolated unit and replaced space temp probe on display fridge. Test ran operation and checked accuracy of probe. Found all ok. Packed up work equipment and completed paperwork. Left all ok
MSA-DCA | WA5799727 | 2 | Earth & Water Pty Ltd | Garden bed west of State Library next to car park stairs - Leaking retic | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 0 | 0 | 44 | 2022-08-30 13:48 | 2022-09-02 17:00 | 2022-09-03 12:30 | 2022-09-02 17:00 | 2022-09-05 08:30 |  |  | repairs to retic
MSA-DCA | WA5092749 | 2 | Critical Fire Protection & Training | Ground - Security Control Room -CD player wired into EWIS system with very poor sound quality from s | Fire Protection Services | Fire Protection - Monitor System | 431.75 | Pass | Pass | 0 | 0 | 44 | 2022-01-28 09:47 | 2022-02-02 17:00 | 2022-01-30 12:00 | 2022-02-02 17:00 | 2022-02-01 08:00 |  |  | Attend EWIS background music fix as requested- Poor quality.Attend site 30th January, carried out checks of terminations, wiring and set up- advised unable to test.return 1st February early- carried out checks with Ben, all operated as intended- monitor. quoteprovided for timer setup.
MSA-DCA | WA5992024 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 not operational | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1108.62 | Pass | Fail | 0 | 0 | 44 | 2022-10-04 15:32 | 2022-10-05 17:00 | 2022-10-04 16:00 | 2022-10-05 17:00 | 2022-10-06 12:00 |  | WACCES | Found Chiller 2 in fault and low refrigerant alarm on stage 1. Air vision has attended site and is quoting to repair refrigerant leak on chiller. Stage 1 isolated, stage 2 is working OK.
MSA-MRWA | WA5994211 | 2 | GPS Plumbing & Gas Services PtyLtd | Left Hand Toilet-Slow Leak on toilet | Plumbing & Drainage | Toilets/Cisterns | 499.9875 | Pass | Pass | -1 | 0 | 44 | 2022-10-05 13:37 | 2022-10-10 17:00 | 2022-10-06 12:00 | 2022-10-10 17:00 | 2022-10-08 08:00 |  | WCAPPR | Replaced perished rubbers on the lhs cubicle
MSA-DCA | WA6190845 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Meeting Room (level 3) CO2 levels high requires immediate adjustment | Air Conditioning | Room Air Conditioners | 768.595 | Pass | Fail | 0 | 0 | 44 | 2022-11-16 10:49 | 2022-11-17 17:00 | 2022-11-16 13:00 | 2022-11-17 17:00 | 2022-11-18 09:00 |  |  | Attended site. Investigated meeting room ac on north east side. Found floor plan doesn't match bms schematics. Investigated further found 2x vav service the same meeting room as well as the supplementary unit. Worked as a team to confirm operation of vav by operating from bms and confirming operation at the unit. Found no sensors in meeting room which causes an inaccurate reading when room is occupied. Unable to investigate supplementary unit due to interviews being run. Will return out of hours when office is empty. Looking at the floor plan Honeywell may need to be engaged to relocate sensors and update floor plan on bms.Attended site before staff arrived. Accessed roof space to investigate ac unit serving the meeting room. Found fresh air damper in a closed position. Opened damper to 25% and confirmed opening. Checked over meeting room portable device currently reading below 500ppm, ok. Will need to engage Honeywell if issues persist. Tested operation of meeting room ac, all ok. C
MSA-DTWD | WA4992384 | 2 | Equans Mechanical Services Australia | BMS aircon system - Scheduling of aircon operation is not working | Air Conditioning | Room Air Conditioners | 432.63 | Fail | Fail | 3 | 3 | 43.8 | 2022-01-06 11:02 | 2022-01-11 17:00 | 2022-02-01 14:13 | 2022-01-11 17:00 | 2022-02-03 10:01 |  |  | Carried out checks , This was a maintenance not a break down so failure codes are inappropriate no assets listed.
MSA-DCA | WA6680894 | 3 | Dormakaba Australia Pty Ltd | Roller door damaged | Building | Automatic Doors | 1729.25 | Pass | Pass | -1 | -1 | 43.8 | 2023-03-01 16:16 | 2023-03-09 17:00 | 2023-03-01 16:30 | 2023-03-09 17:00 | 2023-03-03 12:18
MSA-DTWD | WA6131906 | 2 | M Construction (WA) | Refix white board to wall in O.006 | Building | Internal Walls | 395.69 | Pass | Fail | 0 | 0 | 43.75 | 2022-10-31 10:27 | 2022-11-03 17:00 | 2022-11-02 12:15 | 2022-11-03 17:00 | 2022-11-04 08:00 |  |  | Re-fitted white board using timber and angles
MSA-DFES | WA5108411 | 2 | Australian HVAC Services Pty. Ltd. | Administration - Ground - Operational Delivery - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 748.75 | Pass | Pass | 0 | 0 | 43.5 | 2022-02-08 13:52 | 2022-02-11 17:00 | 2022-02-09 14:30 | 2022-02-11 17:00 | 2022-02-11 10:00 |  |  | Picked up parts, accessed site, isolated ac 5, replaced controls & sensor & rewired. Re programmed controls & tested ok
MSA-DTWD | WA6001316 | 0 | AWB Co. | Room FG17 - F Block - Smells like ecletrical fire in main switch room - Heavy Stench of burnt | Electrical | General Electrical | 1132.985 | Pass | Fail | 0 | 0 | 43.5 | 2022-10-10 15:24 | 2022-10-10 17:24 | 2022-10-10 16:00 | 2022-10-10 19:24 | 2022-10-12 11:30 |  | WACCES | Attended site and signed in. Completed jsa. Located switchboard with faulty transformers. Supply and replace transformers after rectifying issues within the switchboard. Ran through with techs on site and found faults on the BMS side of things. Left with site to fix up the programming. No more burning smells coming from switchboard. All okay. Signed out. Job complete
MSA-DTWD | WA5677756 | 3 | AHS Services WA Pty Ltd (Anchor) | basin Tap cannot be turned off fully | Plumbing & Drainage | Water | 813.1799 | Pass | Pass | -1 | -1 | 43.3333 | 2022-07-26 07:14 | 2022-08-01 17:00 | 2022-07-26 14:00 | 2022-08-01 17:00 | 2022-07-28 09:20 |  |  | Replaced with new basin set
MSA-DCA | WA6526831 | 1 | Protek 24/7 Building & Maintenance | Outside PICA - External - Paving is uneven and trip hazard | Paving & Roadworks | Paving | 864.23 | Pass | Fail | 0 | 0 | 43.2333 | 2023-02-01 11:08 | 2023-02-02 17:00 | 2023-02-01 14:30 | 2023-02-02 17:00 | 2023-02-03 09:44
MSA-DTWD | WA5692203 | 3 | Equans Mechanical Services Australia | Chalk N Cheese Cafe Fridge running hot ( 10 degrees ) | Refrigeration | Refrigerators | 554.12 | Pass | Pass | -1 | -1 | 43 | 2022-08-03 11:19 | 2022-08-10 17:00 | 2022-08-03 15:00 | 2022-08-10 17:00 | 2022-08-05 10:00 |  |  | Attended call found system on 8C with controller reducing ECO. An offset temp function. Sourced manual for similar controller with similar function. However this controller did not have an ECO off function. Contracted controller manufacturer tech support who queried use of this type of controller on a food fridge as it is normally used on bottle fridges and non- perishable products. Could not assist with this controller as non standard customized version for fridge manufacturer. Contacted manufacturer who advised controller had been modified for perishable food fridges so suitable for purpose. Investigated operation found evap coil iced up. Defrosted overnight.Returned test ran system found coil icing up indicating short of refrigerant. System has no access ports to attach gauges.System will need to be taken outside and ports welded in as fire sprinklers in cafe. System needs to pressure tested and leak repaired if accessible, evacuated and charged. Will provide quote.
MSA-DTAG | WA5735496 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground disable toilet in public area blocked | Plumbing & Drainage | Toilets/Cisterns | 101.35 | Pass | Fail | 0 | 0 | 42.9833 | 2022-08-16 13:22 | 2022-08-17 17:00 | 2022-08-16 13:30 | 2022-08-17 17:00 | 2022-08-18 08:29 |  |  | Job completed
MSA-DCA | WA5128233 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main Building - Ground Floor - Plant Room - Chiller 1 in fault | Air Conditioning | Room Air Conditioners | 188.375 | Pass | Fail | 0 | 0 | 42.7833 | 2022-02-14 16:37 | 2022-02-15 17:00 | 2022-02-15 13:32 | 2022-02-15 17:00 | 2022-02-17 08:19 |  |  | Attened site gained access and carried out inspection of chiller fault. Chiller found the have go into lock out alarm due to indication of water flow DP internal fault. Confirmed water flow present at chiller. Reset equipment and placed into lead operation. Chiller started and ran normally. Water brought down to set point. Fault has not reoccured while on site. Work area left tidy. Will recheck during site PM inspection.
MSA-DFES | WA5495698 | 1 | Seme Solutions Pty Ltd | Critical Care paramedics office - Swipe card access to door not working - Door 18 | Security | Access Control | 357.5 | Pass | Fail | 0 | 0 | 42.75 | 2022-06-08 14:10 | 2022-06-09 17:00 | 2022-06-08 15:00 | 2022-06-09 17:00 | 2022-06-10 09:45 |  | WCAPPR | Trace faults. Reestablish connection to Titan. Correctly assign i/o config to doors and tested all doors to confirm no reoccurence. Backup titan
MSA-DCA | WA5128160 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Shipwreck Gallery- Xantho Gallery - Leak in Xantho Gallery | Air Conditioning | Room Air Conditioners | 711.625 | Pass | Fail | 0 | 0 | 42.7 | 2022-02-14 16:01 | 2022-02-15 17:00 | 2022-02-15 13:30 | 2022-02-15 17:00 | 2022-02-17 08:12 |  |  | Returned to site gained access and carried out repair to duct work top hat. Recheck for water leakage and dripping in gallery and from store room space above. All OK. Area was dry. No further action required. Work area left tidy.
MSA-DTAG | WA5204719 | 3 | Sapio Pty Ltd | Level 9 fire door not working | Security | Security Management System | 421.45 | Pass | Pass | -1 | -1 | 42.5 | 2022-03-04 12:48 | 2022-03-14 17:00 | 2022-03-08 14:00 | 2022-03-14 17:00 | 2022-03-10 08:30 |  |  | Installed new reed switch on Level 9 North Fire Door.Job completed.
MSA-DTAG | WA5296227 | 1 | Midolo Building Services | Ground - Registry - Door into Registry keeps slaming. Door closer requires adjusting or repair | Building | Doors | 572.68 | Pass | Fail | 0 | 0 | 42.5 | 2022-03-30 10:20 | 2022-03-31 17:00 | 2022-03-30 15:00 | 2022-03-31 17:00 | 2022-04-01 09:30 |  | WACCES | replaced door closer
MSA-DCA | WA5469474 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Basement Level 2-Rehearsal Room 1-ground aircon is not turned ON | Air Conditioning | Room Air Conditioners | 345.35 | Fail | Fail | 0 | 0 | 42.05 | 2022-05-21 10:33 | 2022-05-21 11:03 | 2022-05-21 16:21 | 2022-05-21 12:33 | 2022-05-23 10:24 |  |  | Site tech returned to site this morning following AH call over weekend and has been able to get equipment running normal again no further action is required on this job. Work area left tidy. AHU working correctly.
MSA-DTAG | WA5068967 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Registry/front office - Aircon in Registry not working | Air Conditioning | Room Air Conditioners | 746.57 | Pass | Fail | 0 | 0 | 42 | 2022-01-19 13:02 | 2022-01-20 17:00 | 2022-01-19 15:00 | 2022-01-20 17:00 | 2022-01-21 09:00 |  |  | REWIRED CONDENSOR FAN TO REPAIR AS TEMPORARY MEASURE UNTIL REPLACED.
MSA-DTWD | WA5692529 | 2 | Protek 24/7 Building & Maintenance | North western corner roof sheet lifting | Roofing | Metal Roofing | 438.44 | Pass | Pass | -1 | 0 | 42 | 2022-08-03 14:12 | 2022-08-08 17:00 | 2022-08-03 15:00 | 2022-08-08 17:00 | 2022-08-05 09:00 |  |  | repaired roof sheet
MSA-DCA | WA6048091 | 1 | Quality Pest & Weed Solutions PTY LTD | Front of Building - Bees are nesting/hanging around front of building causing nuisance to public | Pest Control | General Pest |  | Pass | Fail | 0 | 0 | 41.5 | 2022-10-17 13:16 | 2022-10-18 17:00 | 2022-10-17 13:30 | 2022-10-18 17:00 | 2022-10-19 07:00 |  |  | Removal of bee's
MSA-DCA | WA5090771 | 0 | Critical Fire Protection & Training | Mezzanine lift lobby activated on fire panel at stage door | Fire Protection Services | Fire Protection - Monitor System | 1012.74 | Pass | Fail | 0 | 0 | 41.5 | 2022-01-25 20:00 | 2022-01-25 22:00 | 2022-01-25 20:30 | 2022-01-26 | 2022-01-27 14:00 |  |  | On arrived fip in alarm Zone 10 - L03 D097 - Mezzanine MCP. No indication on MCP of possible causesZone 10 previously completely disabled due to ongoing issues with false alarms- At time of attendance Checked the zone, Zone was only partially disabledBrigade couldn’t find the alarm or any false alarm triggers. Zone 10 - left fully isolated - further investigation will be required
MSA-DCA | WA5392929 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - boiler 2 not resetting | Air Conditioning | Room Air Conditioners | 1680.505 | Fail | Fail | 0 | 0 | 41 | 2022-05-03 13:30 | 2022-05-03 14:00 | 2022-05-03 15:30 | 2022-05-03 15:30 | 2022-05-05 08:30 |  |  | Attended site, signed in and accessed the mechanical plantroom. Found boiler 2 in fault, reset and tested but faulted straight away. Left the Boiler 2 isolated until contractor can investigate fault. Organised Tomlinson contractors to carry out investigation on Boiler 2. The Flame scan on boiler 2 was faulty and was replaced. System reset on the BMS and monitored boiler 2 running conditions - now working as per normal.
MSA-DCA | WA6533237 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - FCU1 alarm - humidity | Air Conditioning | Room Air Conditioners | 468.81 | Pass | Fail | 0 | 0 | 35.0167 | 2023-02-04 22:20 | 2023-02-05 00:20 | 2023-02-04 22:21 | 2023-02-05 02:20 | 2023-02-06 09:22
MSA-DTWD | WA5588970 | 2 | ADVANCED LOCK & KEY | J121 Passage - Sub board lock faulty - Key 42886 | Security | Locksmith | 255 | Pass | Fail | 0 | 0 | 33.5667 | 2022-07-08 08:49 | 2022-07-13 17:00 | 2022-07-12 14:21 | 2022-07-13 17:00 | 2022-07-13 23:55 |  | WACCES | Attend site to replace flush lock on sub board J121 1x flush cabinet lock keyed to 42886
MSA-DTWD | WA5749780 | 1 | Milners Tree Solutions Pty Ltd | Between A & C Block - tree has fallen down on footpath | Landscaping & Gardening | Tree Lopping | 5200 | Fail | Fail | 0 | 0 | 33.4167 | 2022-08-17 09:14 | 2022-08-18 17:00 | 2022-08-20 06:35 | 2022-08-18 17:00 | 2022-08-21 16:00 |  |  | tree removal stump grinding. prune damaged trees
MSA-DTAG | WA5386086 | 2 | GPS Plumbing & Gas Services PtyLtd | Basement - Cell 3 - Custody - Damage to s/steel toilet bowl and fixing into wall – May need replacin | Plumbing & Drainage | Toilets/Cisterns | 571.11 | Pass | Fail | 0 | 0 | 33 | 2022-04-29 15:46 | 2022-05-04 17:00 | 2022-05-04 07:30 | 2022-05-04 17:00 | 2022-05-05 16:30 |  | WACCES | Replaced damaged plate and toilet push button
MSA-DTWD | WA6166469 | 2 | JEM Carpentry | 843B - Machinery Shed - Repair faulty sliding doors | Building | Doors |  | Fail | Fail | 1 | 1 | 33 | 2022-11-11 16:10 | 2022-11-16 17:00 | 2022-11-23 08:00 | 2022-11-16 17:00 | 2022-11-24 17:00 |  |  | Completed
MSA-DFES | WA5462146 | 1 | Go Doors | Main Car Park Gate - automatic gate is faulty | Building | Steel Fencing & Gates | 481 | Fail | Fail | 0 | 1 | 32.5 | 2022-05-19 11:34 | 2022-05-20 17:00 | 2022-05-23 08:00 | 2022-05-20 17:00 | 2022-05-24 16:30 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5681151 | 2 | Damian Rak Electrical Pty Ltd | Foyer store room - Faulty Power Point | Electrical | General Electrical |  | Fail | Fail | 0 | 0 | 32.5 | 2022-07-28 09:32 | 2022-08-02 17:00 | 2022-08-03 08:00 | 2022-08-02 17:00 | 2022-08-04 16:30 |  |  | repair to faulty power point
MSA-DTWD | WA6008179 | 2 | Techworks Electrical | Hallway-4 lights replaced in the walk way ceiling that are not working | Electrical | Lighting, Internal | 1706.535 | Pass | Pass | 0 | 0 | 32.5 | 2022-10-11 13:13 | 2022-10-14 17:00 | 2022-10-12 08:30 | 2022-10-14 17:00 | 2022-10-13 17:00 |  |  | Replaced 24 existing lights in hallway to new LED battern lights in E block
MSA-DTWD | WA6650883 | 1 | AWB Co. | Ground - No power to edge bander | Electrical | General Electrical | 1895.8 | Pass | Fail | 0 | 0 | 32.25 | 2023-02-20 14:06 | 2023-02-21 17:00 | 2023-02-21 09:00 | 2023-02-21 17:00 | 2023-02-22 17:15
MSA-DTAG | WA5854254 | 3 | AWB Co. | Flag Pole needs repairing - unable to get the rope to come down the pole | Building | Steel Work | 3788.42 | Fail | Fail | 7 | 8 | 32 | 2022-09-12 15:04 | 2022-09-19 17:00 | 2022-11-10 08:00 | 2022-09-19 17:00 | 2022-11-11 16:00 |  |  | Works completed
MSA-DCA | WA6405271 | 2 | GPS Plumbing & Gas Services PtyLtd | Courtyard Male Toilets - Hot Water Unit in male toilets is leaking | Plumbing & Drainage | Toilets/Cisterns | 1154.96 | Pass | Pass | 0 | 0 | 32 | 2023-01-09 12:06 | 2023-01-12 17:00 | 2023-01-11 08:00 | 2023-01-12 17:00 | 2023-01-12 16:00 |  | WACCES
MSA-DCA | WA5473087 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Plant Room - Chiller 1 faulty - see notes below | Refrigeration | Chiller | 659.3 | Pass | Fail | 0 | 0 | 31.6333 | 2022-05-24 12:27 | 2022-05-25 17:00 | 2022-05-25 07:00 | 2022-05-25 17:00 | 2022-05-26 14:38 |  |  | Returned to site gained access and confirmed chiller still operating and no faults active. Carried out change over of chillers and moniotored for fault. All OK. No active fault occured. Rechecked boiler and there were no active faults. Boilers were both running to set point. Work area has been left tidy. Chiller 2 has been left in lead operation. Chiller 1 water flow safty fault is believed to have been caused by power fluctuation with pump leading to loss of flow fault. Pump operation has been confirmed. Chiller has run without fault.
MSA-DFES | WA5829336 | 2 | Critical Fire Protection & Training | 2 isolations on the fire panel that has been installed in the reception that need investigation | Fire Protection Services | Fire Protection - Monitor System | 549 | Pass | Fail | 0 | 0 | 31.5 | 2022-09-02 12:17 | 2022-09-07 17:00 | 2022-09-07 01:30 | 2022-09-07 17:00 | 2022-09-08 09:00 |  |  | Found tank valve discharge fault/disabled. Carried outinvestigation/fault finding discovered M/V faulty / water ingressfrom conduits.Disconnected from circuit/bypassed / tagged out.Additionally corrected tank valve wiring signals.
MSA-DTAG | WA5792489 | 2 | EASTERN HILLS ELECTRICAL SERVICE | Ground - Registry - Flickering lights - See notes below | Electrical | Lighting, Internal | 843.72 | Pass | Pass | 0 | 0 | 31 | 2022-08-23 14:50 | 2022-08-26 17:00 | 2022-08-24 08:00 | 2022-08-26 17:00 | 2022-08-25 15:00 |  |  | Replaced 9x lights
MSA-DTWD | WA6509800 | 1 | Equans Mechanical Services Australia | Canteen kitchen - Freezer is tripping out | Refrigeration | Freezers | 1772.37 | Pass | Fail | 0 | 0 | 31 | 2023-01-20 15:55 | 2023-01-23 17:00 | 2023-01-23 08:00 | 2023-01-23 17:00 | 2023-01-24 15:00
MSA-DFES | WA6671523 | 0 | Critical Fire Protection & Training | Fire indicator panel no power | Fire Protection Services | Fire Protection - Monitor System | 1573.18 | Pass | Fail | 0 | 0 | 31 | 2023-02-23 08:38 | 2023-02-23 10:38 | 2023-02-23 09:00 | 2023-02-23 12:38 | 2023-02-24 16:00
MSA-DCA | WA6074745 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Behind Security Office-Freezer Drain Heater Failure Causing Icing. | Refrigeration | Freezers | 1511.02 | Pass | Pass | 0 | 0 | 31 | 2022-10-18 09:50 | 2022-10-19 17:00 | 2022-10-18 10:00 | 2022-10-19 17:00 | 2022-10-19 17:00 |  |  | During rm found drain line had blocked due to drain heater failing causing drain pan to fill with water and overflow causing a large ice block to form on both the floor and pan. Isolated power to controls and condensing unit on both coolroom and freezer as I needed to leave the doors open to allow room to defrost. Disconnected drain line from pan and removed pan from unit . Aided defrost by pouring boiling water down the drain and on the ice block. Due to how thick the ice block was and the melting time, used a sledgehammer to break up it up. Removed ice and allowed room to defrost overnight to remove moisture. Returned to site with new electric drain heater. Removed faulty heater. Due to shaping of pipework had to cut into sections to feed new drain heater. Glued sections back together and insulated the pipework. Wired electric heater in. Screwed evaporator panels back into place. Restored power and tested operation. Confirmed operation of drain heater working and freezer. Completed
MSA-DTWD | WA6426126 | 3 | AWB Co. | Francis St entrance -Under eaves have 2 x broken areas | Building | General Building | 1671.15 | Pass | Fail | 0 | 0 | 31 | 2023-01-12 14:47 | 2023-01-19 17:00 | 2023-01-19 07:00 | 2023-01-19 17:00 | 2023-01-20 14:00
MSA-DTWD | WA6669203 | 2 | Workzone Pty Ltd | Ground level - around all footpaths - repair pavers/trip hazard | Paving & Roadworks | Paving | 1941.93 | Fail | Fail | 1 | 1 | 31 | 2023-02-22 15:18 | 2023-02-27 17:00 | 2023-03-07 07:00 | 2023-02-27 17:00 | 2023-03-08 14:00
MSA-DTWD | WA5470299 | 1 | Protek 24/7 Building & Maintenance | E Block - Cafeteria - Roof leak in center of foyer | Roofing | Metal Roofing | 536.525 | Pass | Pass | 0 | 0 | 30.75 | 2022-05-23 09:29 | 2022-05-24 17:00 | 2022-05-23 09:30 | 2022-05-24 17:00 | 2022-05-24 16:15 |  |  | Repair roof leak - E Block - Cafeteria
MSA-DTWD | WA6431433 | 3 | Protek 24/7 Building & Maintenance | Block 1 - Block 7 and Block 9 - Footpath - brick paving rising causing a trip hazard | Paving & Roadworks | Paving | 1156.03 | Pass | Pass | 0 | 0 | 30.75 | 2023-01-13 14:42 | 2023-01-20 17:00 | 2023-01-19 07:15 | 2023-01-20 17:00 | 2023-01-20 14:00 |  | WACCES
MSA-DTAG | WA5660783 | 1 | Sapio Pty Ltd | Stairwell - Level 9 - Readers not working - See notes below | Security | Access Control | 498.33 | Pass | Fail | 0 | 0 | 30.5 | 2022-07-19 12:39 | 2022-07-20 17:00 | 2022-07-20 08:00 | 2022-07-20 17:00 | 2022-07-21 14:30 |  |  | Replaced door strike, tested for correct operation, all OK.
MSA-DTWD | WA5832230 | 2 | Equans Mechanical Services Australia | Air conditioner faulty, not turning on when switched on at wall switch.-see notes | Air Conditioning | Room Air Conditioners | 792.59 | Pass | Pass | 0 | 0 | 30.5 | 2022-09-05 11:55 | 2022-09-08 17:00 | 2022-09-06 09:30 | 2022-09-08 17:00 | 2022-09-07 16:00 |  | WCAPPR | Arrived on site signed in, checked in with Dennis. Assisted by Dave working at heights, also panel removal in class room for controller access. Started on fault found outdoor unit on roof break in cable. Repaired using blue points all Sundries used from van stock including cable ties, tape. Tested operation in unit all ok. Reassembled unit and replaced Ceiling panels complete paperwork and signed out.
MSA-DTWD | WA5399133 | 1 | Falcetta Plumbing and Gas | male, female and disabled toilets all blocked | Plumbing & Drainage | Toilets/Cisterns | 637.44 | Pass | Fail | 0 | 0 | 30.5 | 2022-05-09 15:36 | 2022-05-10 17:00 | 2022-05-10 10:30 | 2022-05-10 17:00 | 2022-05-11 17:00 |  |  | pumped down pit, repaired and repositioned floats
MSA-MRWA | WA6372095 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 2 - Aircon is broken-Already attended | Air Conditioning | Room Air Conditioners | 427.925 | Pass | Pass | 0 | 0 | 30.5 | 2022-12-14 08:34 | 2022-12-15 17:00 | 2022-12-14 09:00 | 2022-12-15 17:00 | 2022-12-15 15:30 |  |  | Picked up keys from DAC and attended site. Found control room warm. Checked aux units found them with no water flow fault. Checked BMS it indicated a CCW pump fault and that air supply temps for the floor were high indicating issues with central plant. Brett call building maintenance to attend. Advised Darren - control room manager, Programmed, and office. Left site will return once issues are resolved to determine if aux plant has resumed operation or if it has to be manually reset.Returned found units had reset and were operating normally.
MSA-DTAG | WA6533579 | 0 | Sapio Pty Ltd | Aprox 50 Cameras out - Connecting to sever error | Security | CCTV Surveillance | 979.16 | Pass | Fail | 0 | 0 | 30.5 | 2023-02-06 07:17 | 2023-02-06 09:17 | 2023-02-06 08:30 | 2023-02-06 11:17 | 2023-02-07 15:00
MSA-DTWD | WA5578178 | 2 | AWB Co. | Sensor not working to brig lights on | Electrical | General Electrical | 195.04 | Pass | Fail | 0 | 0 | 30.25 | 2022-07-01 09:30 | 2022-07-06 17:00 | 2022-07-06 06:30 | 2022-07-06 17:00 | 2022-07-07 12:45 |  | WACCES | Attended site signed in jsa completed. returned to site to get specific code from sensor and found sensor on but lights not on which was not the case on the first visit. Replaced two tubes in the lights and now the sensor is working correctly and there is light in storeroom. waited 20 mins to see if sensor turns off and it turns off and works correctly.job is completed
MSA-DFES | WA5126522 | 3 | Protek 24/7 Building & Maintenance | Ground - Watch Room / Appliance Bay door, screw snapped off securing lock mechanism. | Building | Doors | 337.655 | Pass | Pass | -1 | -1 | 30 | 2022-02-14 08:31 | 2022-02-21 17:00 | 2022-02-15 08:00 | 2022-02-21 17:00 | 2022-02-16 14:00 |  | WACCES | Screw snapped on door Lock
MSA-MRWA | WA6108853 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 5 - Room 5.09 - TV antenna no reception possible connection fail | Equipment | Electrical Equipment | 485.225 | Pass | Pass | 0 | 0 | 29.75 | 2022-10-20 11:51 | 2022-10-27 17:00 | 2022-10-25 10:15 | 2022-10-27 17:00 | 2022-10-26 16:00 |  | WCAPPR | Arrived on site at 15:30 to continue investigation for TV with no signal on level 5 room 5.09. Tested cable from meeting room end and TV’s. All working. Notified staff of outcome and left site at 16:00
MSA-DTWD | WA5567981 | 3 | AWB Co. | E200 - Replace light tubes not working | Electrical | General Electrical | 162.92 | Pass | Pass | -1 | 0 | 29.5167 | 2022-06-24 14:12 | 2022-07-01 17:00 | 2022-06-27 09:14 | 2022-07-01 17:00 | 2022-06-28 14:45 |  |  | Attended site and signed in. Completed JSA. Located E200 and found faulty light. Supplied and replaced tube and starter to fluro fitting. Tested all okay. Signed out. Job complete
MSA-DCA | WA5001378 | 1 | Earth & Water Pty Ltd | Zone 15 - water pressure issues | Landscaping & Gardening | Grounds Maintenance |  | Pass | Fail | 0 | 0 | 29.5 | 2022-01-11 11:46 | 2022-01-12 17:00 | 2022-01-11 12:00 | 2022-01-12 17:00 | 2022-01-12 17:30 |  |  | 12/01/22 Logan and John-Tested system-cleaned disc filter-Replaced zone 15 40mm solenoid as it has failed.-Joined 25mm "north garden drip" solenoid to zone 15-Ran system-Fixed numerous leaks in drip line (zone 15)-Ran zone 8 and 10. Operating effectively.-Changed mp2000 360 to mp3000 360 (zone8) to better cover lawn-Changed mp2000 90-210 which was broken / vandalised-Pressure tested zone 8, 10 and 15-Tested zone 5-Fixed lx pop up which had been snapped at the base.-Replaced 2x Hunter extra tall pop up internals that had been snapped off.-cleared some foliage from around nozzles-Pressure is good-flow tested zone 8, 10 and 15.
MSA-DTWD | WA6256915 | 2 | AWB Co. | Ground Floor - External Walkway - Refit loose paving and re grout | Building | General Building | 1054.92 | Fail | Fail | 3 | 3 | 29.5 | 2022-11-24 10:12 | 2022-11-29 17:00 | 2022-12-21 08:30 | 2022-11-29 17:00 | 2022-12-22 14:00 |  |  | Works completed
MSA-DTWD | WA5312466 | 1 | SCAVENGER SUPPLIES PTY LTD | FIP - C Block - Foyer - see details below | Fire Protection Services | Fire Protection - Monitor System | 674.86 | Pass | Fail | 0 | 0 | 29.3167 | 2022-04-11 14:12 | 2022-04-12 17:00 | 2022-04-12 07:20 | 2022-04-12 17:00 | 2022-04-13 12:39 |  |  | COMPLETED 13/04/2022SIGNATURE SLIP TO BE AUTHORISED.
MSA-DFES | WA6374808 | 3 | CLEVELAND COMPRESSED AIR SERVICES | Bowen St Workshop-ground-Welding Bay (Main Workshop Area)-compressed air fixtures faulty-see notes | Equipment Hire | Compressors, Generators | 700 | Fail | Fail | 5 | 5 | 29.05 | 2022-12-15 07:01 | 2022-12-21 17:00 | 2023-01-24 08:00 | 2022-12-21 17:00 | 2023-01-25 13:03 |  | WACCES
MSA-DTWD | WA5438103 | 1 | Falcetta Plumbing and Gas | Room F51 - Sewer drain blocked | Plumbing & Drainage | Sewer Drains & Septic Systems | 595.58 | Pass | Fail | 0 | 0 | 29 | 2022-05-16 12:31 | 2022-05-17 17:00 | 2022-05-17 10:30 | 2022-05-17 17:00 | 2022-05-18 15:30 |  | WACCES | clear gully and ensure pump station functioning
MSA-MRWA | WA5087981 | 2 | Water2water Pty Ltd | failed Ice machine in the basement | Plumbing & Drainage | Materials | 439.4375 | Pass | Pass | 0 | 0 | 28.8333 | 2022-01-24 16:19 | 2022-01-28 17:00 | 2022-01-27 11:10 | 2022-01-28 17:00 | 2022-01-28 16:00 |  | WACCES & WCAPPR | Faulty toggle switch. Now in the on position, will source and replace part.replaced filters on Twin blocked
MSA-MRWA | WA6399891 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Server room-over temp alarm | Air Conditioning | Room Air Conditioners | 484.23 | Pass | Pass | 0 | 0 | 28.8167 | 2023-01-03 08:04 | 2023-01-04 17:00 | 2023-01-03 08:15 | 2023-01-04 17:00 | 2023-01-04 13:04
MSA-DTWD | WA5069190 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 301.06 | Pass | Fail | 0 | 0 | 28.75 | 2022-01-19 16:33 | 2022-01-27 17:00 | 2022-01-27 10:15 | 2022-01-27 17:00 | 2022-01-28 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Re located room B43 with faulty lights. Pulled down a light and took cover off and tested for voltage at fitting, there was 0 volts. Kept pulling lights down and taking apart to test until we found twin active coming from the switch. Tested at that light and there was 240v. Found there was cabling going into a control system connected to some sort of remote. Searched all classrooms near by for remote. Couldn’t find it. Isolated lighting circuit and took actives out of control box, put connector on both actives and connector on neutral. Re energised circuit. Flipped switch on. All lights came on. Put light fitting back together. Spoke to fm and let him know what we did and he was happy. Packed up. Completed paperwork. Signed out. *** Job complete ***
MSA-DFES | WA5839051 | 2 | AWB Co. | Entry door from engine room to duty room - faulty, not closing | Building | Doors | 391.7575 | Fail | Fail | 0 | 0 | 28.75 | 2022-09-09 08:48 | 2022-09-14 17:00 | 2022-09-15 07:00 | 2022-09-14 17:00 | 2022-09-16 11:45 |  |  | Attended site, upon arrival fire station was going out, will need to re attendAutomatic door closer not closing, door also hitting the framePurchased new countersunk screws cleaned the automatic closer and lubricated, made minor adjustments. All working fine
MSA-DCA | WA6534176 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Geology - Mezzanine Level - Plant room 4 - Investigate and repair humidifier alarms. see notes | Building | General Building | 653.145 | Pass | Pass | 0 | 0 | 28.5167 | 2023-02-06 10:05 | 2023-02-07 17:00 | 2023-02-06 11:00 | 2023-02-07 17:00 | 2023-02-07 15:31
MSA-DTAG | WA5206694 | 1 | Sapio Pty Ltd | Level 6 -Room 609 and 603 - Duress alarm getting activated by itself | Security | Monitoring | 327.18 | Pass | Pass | 0 | 0 | 28.5 | 2022-03-08 08:53 | 2022-03-09 17:00 | 2022-03-08 12:30 | 2022-03-09 17:00 | 2022-03-09 17:00 |  |  | Returned and replaced batteries in Room 603 and 609 Duress. All cleared and working okay.
MSA-DCA | WA5308628 | 2 | Protek 24/7 Building & Maintenance | Ground – external - Eastern side of library - see details below | Building | General Building | 265.985 | Pass | Fail | 0 | 0 | 28.5 | 2022-04-08 14:10 | 2022-04-13 17:00 | 2022-04-13 11:15 | 2022-04-13 17:00 | 2022-04-14 15:45 |  | WACCES | Replace missing bolts on bike racks
MSA-DTWD | WA5471602 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 516.75 | Fail | Fail | 0 | 0 | 28.5 | 2022-05-23 13:07 | 2022-05-24 17:00 | 2022-05-25 11:15 | 2022-05-24 17:00 | 2022-05-26 15:45 |  |  | Repair Roof leak
MSA-DFES | WA5833767 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Circuit board - internal lights tripping - see notes | Electrical | Lighting, Internal | 1475.99 | Pass | Fail | 0 | 0 | 28.5 | 2022-09-06 11:35 | 2022-09-07 17:00 | 2022-09-06 13:15 | 2022-09-07 17:00 | 2022-09-07 17:45 |  |  | complete
MSA-DCA | WA5470654 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Jubilee - Ground Floor - Plant Room 3 - Air con fault - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 188.375 | Pass | Pass | 0 | 0 | 28 | 2022-05-23 11:34 | 2022-05-24 17:00 | 2022-05-23 12:00 | 2022-05-24 17:00 | 2022-05-24 16:00 |  |  | Attended site, signed in and accessed the Jubilee area and surrounding plantrooms. Checked all units operation and found working but no control. Located and accessed plantrooms with honeywell and carried out resets on the bms controllers. Logged on to the BMS and reset the alarms and all fan coil unit faults.
MSA-DCA | WA5470668 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Old Gaol - Ground Floor - Air con fault - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 188.375 | Pass | Pass | 0 | 0 | 28 | 2022-05-23 11:42 | 2022-05-24 17:00 | 2022-05-23 12:00 | 2022-05-24 17:00 | 2022-05-24 16:00 |  |  | Attended site, signed in and accessed the Gaol. Checked all units operation and found working but no control. Located and accessed plantrooms with honeywell and carried out resets on the bms controllers. Logged on to the BMS and reset the alarms and all fan coil unit faults.
MSA-DTWD | WA6145670 | 2 | AHS Services WA Pty Ltd (Anchor) | A336A - Mens Staff Urinal - Cistern button sticks open and continuously drips into urinal bowl | Plumbing & Drainage | Toilets/Cisterns | 340.7 | Fail | Fail | 0 | 0 | 28 | 2022-11-02 13:39 | 2022-11-07 17:00 | 2022-11-09 09:00 | 2022-11-07 17:00 | 2022-11-10 13:00 |  |  | nil
MSA-DTWD | WA5204139 | 2 | Techworks Plumbing | D Block - Ground - Southern side of workshop - Low pressure to water tap | Plumbing & Drainage | Water | 748.31 | Pass | Pass | 0 | 0 | 28 | 2022-03-04 08:08 | 2022-03-10 17:00 | 2022-03-08 07:00 | 2022-03-10 17:00 | 2022-03-09 11:00 |  |  | Dennis answered the phone he showed us the location and apologized on the description it’s actually north side of d block work shop, attached photos of the chrome tap is the tap that had low pressure to it, later to find out the whole main line in the ground supplying all taps along d workshop are not working the first tap has very low water pressure the second one has barely any water coming out and the last tap has no water at all, I have explained to Dennis this is a bigger problem then just low pressure to one tap, we believe this has something to do with the big water leak and Dennis is okay with signing this job of until the water leak is sorted out, they have another plumber apparently looking at the leak on Friday.
MSA-DTWD | WA5293999 | 3 | AWB Co. | Bike and Access door at rear - Bike door to be patched and both doors oxidized and need repaint. | Painting | External | 598.43 | Pass | Pass | -1 | -1 | 28 | 2022-03-28 11:58 | 2022-04-04 17:00 | 2022-03-29 11:30 | 2022-04-04 17:00 | 2022-03-30 15:30 |  |  | Remove door to fill patch and paint and re hung doorInstalled stainless steel kick plate to bike door
MSA-DTWD | WA5303867 | 3 | AWB Co. | W107 - Lights not working | Electrical | General Electrical | 1241.67 | Pass | Pass | -1 | -1 | 28 | 2022-04-04 13:00 | 2022-04-11 17:00 | 2022-04-05 11:30 | 2022-04-11 17:00 | 2022-04-06 15:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Replaced all faulty lighting throughout campus. Replaced faulty ballast in kitchen area. Found there was 2x globes we needed. Went to wholesaler to pick them up. Returned to site and installed. All lights are now working as intended. Put all faulty tubes in allocated bin, Took pictures of everything. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5792567 | 3 | COMMERCIAL PLUMBING AND GAS | Cistern running ladies Toilet | Plumbing & Drainage | Toilets/Cisterns | 1247.875 | Pass | Pass | -1 | 0 | 28 | 2022-08-23 15:06 | 2022-08-30 17:00 | 2022-08-26 10:00 | 2022-08-30 17:00 | 2022-08-27 14:00 |  |  | replaced cistern with new style invisi
MSA-DFES | WA5887434 | 3 | AWB Co. | Ground - Paul Van Der Meys office - Internal wall near window has plaster missing. | Building | General Building | 804.12 | Fail | Fail | 1 | 1 | 28 | 2022-09-16 07:39 | 2022-09-22 17:00 | 2022-09-28 07:00 | 2022-09-22 17:00 | 2022-09-29 11:00 |  |  | painting works completed as per quote
MSA-DTAG | WA5480120 | 2 | Gilmour & Jooste Electrical | Custody male toilets - Exhaust fan in male staff toilets in custody area not working | Electrical | General Electrical | 453.845 | Fail | Fail | 0 | 0 | 27.9667 | 2022-05-27 16:03 | 2022-06-01 17:00 | 2022-06-02 08:15 | 2022-06-01 17:00 | 2022-06-03 12:13 |  |  | Investigated faulty exhaust fan system, searched the building for exhaust fan motors. Found and replaced two broken fan belts supplied by site. Tested fans and ducting system now in working order.
MSA-DTWD | WA5016959 | 0 | CONNECT SECURITY SYSTEMS | Block 1 - cleaners store room - Unresponsive alarm panel | Security | Monitoring | 583.01 | Pass | Fail | 0 | 0 | 27.95 | 2022-01-13 09:15 | 2022-01-13 11:15 | 2022-01-13 10:02 | 2022-01-13 13:15 | 2022-01-14 13:59 |  |  | Replaced Power Supply and indivividually fused all inputs from Block 1 to understand what was shorting out the power supply.
MSA-DCA | WA5487161 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Wet processing Lab - Pressure gage fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 345.35 | Pass | Fail | 0 | 0 | 27.7833 | 2022-06-01 12:55 | 2022-06-01 14:55 | 2022-06-01 13:00 | 2022-06-01 16:55 | 2022-06-02 16:47 |  |  | Returned to site after settings adjustment and equipment reset. Confirmed no active air flow faults on FUM hoods EF-1 and EF-2. Confirmed room pressures to be stable and not fluctuating. Confirmed operation of AHU 6 OA damper as positive pressure relief when lab door closed. Confirmed no active fault with A/C equipment in room. Work area has been left tidy. No further action required.
MSA-DCA | WA5677517 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Fault description BMS notification showing Chiller 2 in fault. Please investigate. | Air Conditioning | Room Air Conditioners | 1204.73 | Pass | Fail | 0 | 0 | 27.7833 | 2022-07-25 15:05 | 2022-07-26 17:00 | 2022-07-26 12:00 | 2022-07-26 17:00 | 2022-07-27 15:47 |  |  | Returned to site with AV chiller tech. On further investigation of equipment intermittent fault was identified with chiller auxiliary electrical contacts. Note chiller has been stopped and restarted a number of times and fault has not reoccured. Due to age of parts quote will be submitted to PFM for repairs. All equipment has been left in auto operation. Currently there are no active alarms. No further action is able to be taken on this job.
MSA-DTAG | WA6001185 | 2 | MARSHALL BEATTIE AUTOMATION | Basement - carpark - Irwin Street auto car park gate is not fully closing – gate sensor activating | Building | Steel Fencing & Gates | 260 | Pass | Pass | 0 | 0 | 27.5833 | 2022-10-10 13:14 | 2022-10-13 17:00 | 2022-10-11 07:59 | 2022-10-13 17:00 | 2022-10-12 11:34 |  |  | Paul Cullum (12/10/2022) - Work NoteReturn to site as no one in attendnace yesterday morningInspection, security magnet/sensor not aligned. Adjusted drive closed limit till magnet/sensor aligned. Tested operation ok.Mark Wilkinson (11/10/2022) - Work NoteTravel to site, No site access, contacts not answering, unable to access gate, will need to reattend and return to site
MSA-DCA | WA6533244 | 1 | EQUANS Mechanical Services (WA) Pty Limited | 2x alarms fault - steam plant / geneators | Mechanical Services | Boilers | 446.29 | Pass | Pass | 0 | 0 | 27.5667 | 2023-02-05 04:00 | 2023-02-06 17:00 | 2023-02-05 06:00 | 2023-02-06 17:00 | 2023-02-06 09:34
MSA-DFES | WA5477558 | 2 | Australian HVAC Services Pty. Ltd. | Administration Building - Ground - Server Room - Left hand Air Conditioner is not working - see belo | Air Conditioning | Room Air Conditioners | 2232.68 | Pass | Pass | -1 | 0 | 27.5 | 2022-05-25 14:38 | 2022-05-30 17:00 | 2022-05-26 14:00 | 2022-05-30 17:00 | 2022-05-27 17:30 |  |  | System checked Monday all working well
MSA-DTWD | WA6254119 | 1 | Australian Airconditioning Services Pty Ltd | AC unit in lecturers office not working, wont turn on | Air Conditioning | Room Air Conditioners | 776.2 | Pass | Fail | 0 | 0 | 27.5 | 2022-11-22 15:52 | 2022-11-23 17:00 | 2022-11-23 08:00 | 2022-11-23 17:00 | 2022-11-24 11:30 |  |  | Checked unit and found tripped on HP safety. Reset and unit running. Due to age of unit, HP control to be replaced.Replaced hp controller. Unit has been running for 2 weeks now without HP issues.
MSA-DTWD | WA4993484 | 2 | Precise Air Group | E-Block Deli, the refrigerated display unit is not cooling and has a loose side panel | Refrigeration | Refrigerators | 658.61 | Pass | Pass | 0 | 0 | 27.5 | 2022-01-07 15:01 | 2022-01-12 17:00 | 2022-01-10 11:30 | 2022-01-12 17:00 | 2022-01-11 15:00 |  |  | Returned the next day and found system to hold pressure. Evacuated and charged system. Test ran and watched system reach set point. Left all ok
MSA-DCA | WA5142573 | 1 | Techworks Plumbing | Jubilee Building - Ground - UAT - Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 816.63 | Pass | Fail | 0 | 0 | 27.5 | 2022-02-16 15:36 | 2022-02-17 17:00 | 2022-02-17 07:00 | 2022-02-17 17:00 | 2022-02-18 10:30 |  |  | 17/2 - Attended site signed in at security and went to the jubilee building, signed in there also and spoke to the girl at reception who showed me where the toilet is, she explained to me that this toilet is always getting blocked and wants to know why, so I started to plunge toilet it was blocked really bad and I noticed that the sink was blocking up also and even overflowing out of the floor waste, I managed to eventually unblock it with the plunger and sink and floor waste were good after that to, Completed paperwork 18/2 I found an IO in the plant room behind the toilets and did a camera inspection of the drain and ran it about 30 metres down the drain and was unable to find any debris or reason as to why this toilet keep blocking up, besides there is a rubber joiner about 2m down that connects the two pipes together which has a gap in between it, it is possible that over time it could be building up in that gap and blocking up, but as for this inspection I could not find anoth
MSA-DTWD | WA5686858 | 2 | AWB Co. | Water leak in computer room R019 | Roofing | Metal Roofing | 999.735 | Pass | Pass | 0 | 0 | 27.5 | 2022-08-01 11:22 | 2022-08-04 17:00 | 2022-08-03 10:45 | 2022-08-04 17:00 | 2022-08-04 14:15 |  |  | Repaired box gutter using zinc L flashing
MSA-DFES | WA6014275 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room - Strip light fallen from ceiling | Electrical | Lighting, Internal | 1237.68 | Pass | Fail | 0 | 0 | 27.5 | 2022-10-12 07:54 | 2022-10-12 17:00 | 2022-10-12 13:30 | 2022-10-12 17:00 | 2022-10-13 17:00 |  |  | Arrived onsite at 13:15 to install 6 x LED battens to remove hazards from ageing old fittings. Installed and tested all 6 lights, all good. Notified staff of works completed whilst onsite and left site at 17:00
MSA-DCA | WA6144927 | 1 | Techworks Electrical | Various Levels - Faulty Light Switches - See notes | Electrical | General Electrical | 1061.595 | Pass | Pass | 0 | 0 | 27.5 | 2022-11-02 10:00 | 2022-11-03 17:00 | 2022-11-02 11:30 | 2022-11-03 17:00 | 2022-11-03 15:00 |  |  | Replaced light switches throughout admin building and warehouse area
MSA-DTWD | WA6290625 | 1 | Australian Airconditioning Services Pty Ltd | Water leaking from A/C | Air Conditioning | Room Air Conditioners | 509.72 | Pass | Pass | 0 | 0 | 27.5 | 2022-11-28 10:03 | 2022-11-29 17:00 | 2022-11-28 12:00 | 2022-11-29 17:00 | 2022-11-29 15:30 |  |  | complete
MSA-DTWD | WA6526724 | 3 | AWB Co. | 7x lights out | Electrical | Lighting, Internal | 995.825 | Pass | Fail | 0 | 0 | 27.5 | 2023-02-01 10:17 | 2023-02-08 17:00 | 2023-02-08 07:00 | 2023-02-08 17:00 | 2023-02-09 10:30
MSA-DCA | WA6527250 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Roof Space - Plant Room - Water leak from FCU 1 Duct at Steam Inlet | Air Conditioning | Room Air Conditioners | 1179.89 | Pass | Fail | 0 | 0 | 27.5 | 2023-02-01 15:09 | 2023-02-02 17:00 | 2023-02-02 07:00 | 2023-02-02 17:00 | 2023-02-03 10:30
MSA-DTWD | WA5572648 | 3 | Precise Air Group | Room G120 - Excessive noise from AC or Ventilation Fan | Equipment | Electrical Equipment | 892.535 | Pass | Pass | 0 | 0 | 27.3667 | 2022-06-30 09:09 | 2022-07-07 17:00 | 2022-07-04 10:24 | 2022-07-07 17:00 | 2022-07-05 13:46 |  | WACCES | Faulty fresh air inline exhaust fan bearings noisy needs replacing Asset is FANTECH RIL-200SW Ref 02E73750 replaced with new fan alot quiter
MSA-DTAG | WA5108262 | 3 | AHS Services WA Pty Ltd (Anchor) | Ground - Male staff toilets - Basin in male staff toilets isn’t draining | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | -1 | -1 | 27.35 | 2022-02-08 12:55 | 2022-02-15 17:00 | 2022-02-08 13:00 | 2022-02-15 17:00 | 2022-02-09 16:21 |  |  | Used plunger to clear blocked basin in male toilet on hrs floor
MSA-DFES | WA5568884 | 2 | Water2water Pty Ltd | Level 1 - Kitchen - Faulty Kitchen Hot water tap u/S Billi brand or similar | Plumbing & Drainage | HWS/Units Electric & Gas | 848.2975 | Pass | Pass | 0 | 0 | 27.25 | 2022-06-27 09:47 | 2022-06-30 17:00 | 2022-06-28 13:00 | 2022-06-30 17:00 | 2022-06-29 16:15 |  | WACCES | TECH ATTENDED, REPLACED ELEMENT. UNIT STILL NOT HEATING - TOOK BACK TO WORKSHOP FOR FURTHER DIAGNOSIS. HOT PUMP REPLACED AND ON TEST, ALL OKAY. REINSTALLED UNIT - ALL OKAY ON DEPARTURE.
MSA-DTWD | WA5686575 | 2 | Protek 24/7 Building & Maintenance | Water leaking through roof near penetration for extraction unit in battery charging room | Roofing | Metal Roofing | 389.78 | Pass | Pass | 0 | 0 | 27.25 | 2022-08-01 09:30 | 2022-08-04 17:00 | 2022-08-01 10:45 | 2022-08-04 17:00 | 2022-08-02 14:00 |  |  | Repair Roof leak
MSA-DCA | WA5323731 | 0 | Techworks Electrical | No lights including emergency exit lighting is working | Electrical | General Electrical | 995.48 | Pass | Fail | 0 | 0 | 27 | 2022-04-13 10:37 | 2022-04-13 12:37 | 2022-04-13 11:30 | 2022-04-13 14:37 | 2022-04-14 14:30 |  |  | Inspected lights out, traced cabling to find no faults. Inspected switchboard, found wire loose from contact. Re-ran cabling where required and reconnected and lights to ensure for correct operation
MSA-DTAG | WA5513220 | 1 | Sapio Pty Ltd | Ground Floor - Security Desk - Duress Alarm continuing to go off | Security | Monitoring | 450.45 | Pass | Pass | 0 | 0 | 27 | 2022-06-14 08:46 | 2022-06-15 17:00 | 2022-06-14 10:00 | 2022-06-15 17:00 | 2022-06-15 13:00 |  |  | Replaced duress in Legal Aid Commission Office wall duress, tested OK.
MSA-DTWD | WA5564273 | 1 | Protek 24/7 Building & Maintenance | High Ground floor gutter - North side of building - F Block gutter full of water – SEE DETAILS BELOW | Roofing | Tiled Roofing | 237.125 | Pass | Pass | 0 | 0 | 27 | 2022-06-21 09:21 | 2022-06-22 17:00 | 2022-06-21 12:00 | 2022-06-22 17:00 | 2022-06-22 15:00 |  |  | Cleaned blocked gutter to repair overflow
MSA-DCA | WA6074297 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Behind security office - cool room reading 9 degrees c | Refrigeration | Coolroom | 2350.42 | Pass | Pass | 0 | 0 | 27 | 2022-10-18 09:37 | 2022-10-19 17:00 | 2022-10-18 10:00 | 2022-10-19 17:00 | 2022-10-19 13:00 |  |  | Investigated high Temp alarm in cool room carried out Investigation and found unit short of refrigerat source equipment to carry out repairs and investigation reclined refrigeration system found United lose half of its charge carried out pressure test found
MSA-DTAG | WA6113650 | 1 | Australian HVAC Services Pty. Ltd. | President's chamber - Judge’s chambers air-conditioning is not operating - see notes below | Air Conditioning | Room Air Conditioners | 1782.72 | Pass | Fail | 0 | 0 | 27 | 2022-10-24 13:39 | 2022-10-25 17:00 | 2022-10-25 08:00 | 2022-10-25 17:00 | 2022-10-26 11:00 |  |  | Pick up new transformer from supplier. Attend site. Access electrical control board. Disconnect wiring to failed transformer and remove. Install new transformer and connect wiring. Deisolate power supply and test operation. Found controls now online. Found unit to start and operate as normal.
MSA-MRWA | WA6291045 | 1 | AWB Co. | loud humming sound on mezzanine floor - see notes | Electrical | General Electrical | 461.62 | Pass | Pass | 0 | 0 | 27 | 2022-11-28 11:52 | 2022-11-29 17:00 | 2022-11-28 12:00 | 2022-11-29 17:00 | 2022-11-29 15:00 |  |  | Attended site and signed in. Reviewed JSA. Liaised with site contact about noise again and he showed me a video of humming sound. Pulled down more led lights and inspected to see if the dimmers were compatible with drivers. All seemed to be fine. Investigated roof space and found to be Control gear for multiple metal halide lights on exterior near downlight cut outs. Located board where they were fed from. Energised. Humming noise appeared. Also found to be timer was out and was coming on during the day not after hours. Rectified so they only come on after hours. No problem with the humming noise. Just the control gear. Notified relevant personnel of works completed **job complete**
MSA-DTAG | WA6361568 | 3 | Australian HVAC Services Pty. Ltd. | Air flow in managers office next to print room is very low | Air Conditioning | Building HVAC Maintenance (Major Plant) | 460.88 | Pass | Pass | 0 | 0 | 27 | 2022-12-08 10:51 | 2022-12-15 17:00 | 2022-12-14 07:00 | 2022-12-15 17:00 | 2022-12-15 10:00 |  |  | Attend site. Access ground registry area. Check VAV 2L.32 serving serving managers office. Found to have minimal airflow. Check box and found to be delivering 190l/s. Box has a very long duct run. Check all outlets off box. Found to have 4 outlets. Due to box being at the very end of the run this box looses airflow as the other boxes open. Further investigation found the ductwork from this box to be 150 diameter to managers office. Shut off outlet in print room and vacant room to push more air into managers office. Found air to increase slightly. Shut off outlet to front desk area and found airflow to increase considerably. Sensor is in vacant room and would work better in managers office. Found on warm day with all other boxes open, box airflow dropped from 190l/s to 53L/S. Unable to get the required airflow to this area. Duct run is too long.
MSA-DTWD | WA6689051 | 3 | AWB Co. | Lights not working (Explosion proof type) | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 27 | 2023-03-08 08:53 | 2023-03-15 17:00 | 2023-03-13 12:00 | 2023-03-15 17:00 | 2023-03-14 15:00 |  | WACCES
MSA-DTWD | WA6721539 | 1 | Equans Mechanical Services Australia | Upright double door freezer running warm - see notes | Refrigeration | Freezers |  | Pass | Pass | 0 | 0 | 26.95 | 2023-03-14 09:28 | 2023-03-15 17:00 | 2023-03-14 13:15 | 2023-03-15 17:00 | 2023-03-15 16:12
MSA-DCA | WA5477213 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Boardroom, temperatures, please investigates. Reports of it being very cold. | Air Conditioning | Room Air Conditioners | 136.05 | Pass | Pass | 0 | 0 | 26.8667 | 2022-05-25 11:59 | 2022-05-26 17:00 | 2022-05-25 12:43 | 2022-05-26 17:00 | 2022-05-26 15:35 |  |  | Returned to site rechecked unit and confirmed no further adjustment required on equipment. AHU keeping area to set point. Work area left tidy.
MSA-DTWD | WA6142931 | 1 | SCAVENGER SUPPLIES PTY LTD | Fault buffer alarm on main fire panel needs to be cleared. | Fire Protection Services | Fire Protection - Monitor System | 320.55 | Pass | Pass | 0 | 0 | 26.8333 | 2022-11-01 09:49 | 2022-11-02 17:00 | 2022-11-01 10:10 | 2022-11-02 17:00 | 2022-11-02 13:00 |  |  | Initial visit completed 1/11/2022- Further investigation required Arrived on site @ 1110. The EWIS was beeping, muted the buzzer on EWIS.Amplifier/Speaker fault showing on EWIS in Zone 3 block A.Tried a master reset on both the FIP and EWIS but kept re-occurring.Building construction work is happening next to Zone 3 block A. Security escorted me to the building and met with the builder.Majority of Block A is getting gutted and renovated, see photos attached.As you can see in the photos the detector is on the floor along with the fire cable cut in the roof.When signing in on site the builder informed me I - Fire isolated zones the previous week.See photo attached.Further investigation required.Finished on site @ 1210Site LocationBlock A Zone 3 Job Completed 2/11/2022- Removed zone 3 on EWIS due to construction work causing multiple faults. A 47K resistor was installed into to zone 3 terminals to close off the line/circuit. All faults on EWIS have cleared and system is work
MSA-DTWD | WA5323592 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire Pump Water Tank - Water pouring out of fire pump water tank | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 1090.21 | Pass | Fail | 0 | 0 | 26.8167 | 2022-04-13 09:29 | 2022-04-13 11:29 | 2022-04-13 10:00 | 2022-04-13 13:29 | 2022-04-14 12:49 |  | WCAPPR | 13/4/22 - Our technician has attended today @ 10.00AM .This is all related to the tank drain down work order/BRAF IN PLACE.. Regards.SIGNATURE SLIP TO BE AUTHORISED
MSA-DTWD | WA5797790 | 3 | AWB Co. | F 61 - Power switch LED light not working | Electrical | General Electrical | 999.425 | Pass | Pass | -1 | -1 | 26.75 | 2022-08-29 10:41 | 2022-09-05 17:00 | 2022-08-31 12:15 | 2022-09-05 17:00 | 2022-09-01 15:00 |  |  | Attended site and signed in. Reviewed JSA. Liaised with fm about works going ahead. Located room F58. Gained access to room. Isolated A/C circuit. Ran cable and installed green indicator light near A/C to notify class when A/C is running. Energised circuit. Tested for correct operation. Repeated process for other A/C in room. Cleaned and packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5588978 | 2 | ADVANCED LOCK & KEY | J127 - Sub board lock faulty - Key 42886 | Security | Locksmith | 217.5 | Pass | Pass | 0 | 0 | 26.6667 | 2022-07-08 08:53 | 2022-07-13 17:00 | 2022-07-12 09:15 | 2022-07-13 17:00 | 2022-07-13 11:55 |  | WACCES | ite to install carbine C4 cam lock to sub board J127 1x C4 cam lock carbine keyed to 42886
MSA-DFES | WA5105058 | 2 | AWB Co. | Double use bathroom between dorms - cover on metal hand towel dispenser is broken | Building | Steel Work | 412.87 | Pass | Pass | 0 | 0 | 26.5833 | 2022-02-04 07:15 | 2022-02-08 17:00 | 2022-02-07 12:45 | 2022-02-08 17:00 | 2022-02-08 15:20 |  |  | Removed old, and supplied and installed new paper towel dispenser
MSA-DTWD | WA5378077 | 3 | AWB Co. | Network port not working | Electrical | General Electrical | 568.4 | Pass | Pass | 0 | 0 | 26.5 | 2022-04-20 11:08 | 2022-04-28 17:00 | 2022-04-26 13:15 | 2022-04-28 17:00 | 2022-04-27 15:45 |  | WCAPPR | Attended site and signed in, completed jsa,spoke with fm about job, measured and mounted Aussie duct to wall , fixed mounting blocks to wall, ran cable and put covers on , vacuumed up and moved all furniture back to original positions, cleaned up, packed up, completed paperwork, signed outJob completed
MSA-DTWD | WA5378279 | 1 | BAKE-QUIP PTY LTD | D Block - Ground - D16 Baking Lab - Rotel oven thermostat issue – Middle deck | Equipment | Catering Equipment | 676.4 | Pass | Fail | 0 | 0 | 26.5 | 2022-04-20 12:58 | 2022-04-21 17:00 | 2022-04-21 11:00 | 2022-04-21 17:00 | 2022-04-22 13:30 |  | WCAPPR | REFER TO SERVICE REPORT.
MSA-DTWD | WA5562732 | 1 | Damian Rak Electrical Pty Ltd | 840 - Various ceiling lights faulty | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 26.5 | 2022-06-20 09:35 | 2022-06-21 17:00 | 2022-06-20 12:30 | 2022-06-21 17:00 | 2022-06-21 15:00 |  |  | Job completed
MSA-DTWD | WA6130686 | 1 | Australian Airconditioning Services Pty Ltd | AC4 not working - See notes below | Air Conditioning | Room Air Conditioners | 1042.4 | Pass | Fail | 0 | 0 | 26.5 | 2022-10-28 14:19 | 2022-10-31 17:00 | 2022-10-31 07:30 | 2022-10-31 17:00 | 2022-11-01 10:00 |  |  | Checked unit and found no start signal from BMS. Organised Alerton to re wire BMS control. Alerton re wired unit and fixed start signal.1/11/22 Ran and tested unit, unit is 30plus years old and on R22. Unit is running ok, electricals and gas charge ok.
MSA-DTAG | WA6230125 | 1 | Gilmour & Jooste Electrical | Front driveway - Driveway alert light hanging off wall | Electrical | Lighting, External | 270.27 | Pass | Fail | 0 | 0 | 26.5 | 2022-11-18 11:16 | 2022-11-21 17:00 | 2022-11-21 06:00 | 2022-11-21 17:00 | 2022-11-22 08:30 |  | WACCES | Welded broken light back together and re fixed it too the top of the pole. Tested all working
MSA-DTWD | WA6531612 | 2 | Precise Air Group | A316 - Science Labs - Fume hood Extraction not working | Electrical | General Electrical | 1641.18 | Pass | Pass | 0 | 0 | 26.5 | 2023-02-03 13:21 | 2023-02-08 17:00 | 2023-02-06 07:30 | 2023-02-08 17:00 | 2023-02-07 10:00
MSA-DTWD | WA5010453 | 1 | Australian HVAC Services Pty. Ltd. | Whole building - lost cooling from the a/c | Air Conditioning | Room Air Conditioners | 975.12 | Pass | Fail | 0 | 0 | 26.5 | 2022-01-12 14:40 | 2022-01-13 17:00 | 2022-01-13 07:00 | 2022-01-13 17:00 | 2022-01-14 09:30 |  |  | Douglas Posthuma (14/01/2022) - Work NoteArrrived to site, found chiller 1 running.Found chiller 2 not running and found condenser water pump not running but chilled water pump was runningNoticed chiller 2 compressors were starting and stopping immediatelyUnable to access computer to check controls so performed a power cycle on both Controllers inside the chiller 2 plantroom.Found condenser water pump started almost immediately and then chiller 2 compressor 1 started soon thereafterReturned site with cables to try connect hvac laptop directly to the Vykon controller but unsuccessfulReturned following day and power cycled vykon controllerReturned in afternoon after ahu 14 controller not calling for chilled water valve. Power cycled controller but no change. Require further interrogation of ahu 14 controller. Will do so on another job
MSA-DTWD | WA6649967 | 1 | High Tech Pest Control | Ant problem under building | Pest Control | General Pest | 885.81 | Pass | Pass | 0 | 0 | 26.5 | 2023-02-20 08:32 | 2023-02-21 17:00 | 2023-02-20 13:00 | 2023-02-21 17:00 | 2023-02-21 15:30
MSA-DCA | WA5459881 | 1 | Critical Fire Protection & Training | CRC History/Anthropology Area - History Office Area - Thermal Detector in fault | Fire Protection Services | Smoke and Heat Detection | 1585.42 | Pass | Pass | 0 | 0 | 26.3333 | 2022-05-18 09:37 | 2022-05-19 17:00 | 2022-05-18 09:40 | 2022-05-19 17:00 | 2022-05-19 12:00 |  |  | 18/5 - 122 faults on loop 1 on arrival. Investigated cable pits from panel to sub panel. Investigated all input/output modules on VESDA units and found all operating as intended. The next step is to check output voltage on loop card to confirm loop card has potentially been damaged through hazardous weather/lightning strikes in area. 18/5 - Specialist Fire Electrician attended and investigated the reported loop issue with fire system and confirmed replacement card was required.19/5 - Returned at the verbal approval of Reese Withey to complete the loop card replacement.
MSA-DTAG | WA5271936 | 3 | Midolo Building Services | Courtside - Ground - Custody Shower door - please see detaild below | Building | Doors | 399.99 | Fail | Fail | 2 | 2 | 26.25 | 2022-03-18 09:52 | 2022-03-25 17:00 | 2022-04-06 07:30 | 2022-03-25 17:00 | 2022-04-07 09:45 |  | WACCES | Door patched & painted
MSA-DFES | WA5534686 | 0 | SONTEC WA PTY LTD | Stairwell 2 - external door not locking | Security | Access Control | 470 | Pass | Fail | 0 | 0 | 26.25 | 2022-06-16 13:15 | 2022-06-16 15:15 | 2022-06-16 14:35 | 2022-06-16 17:15 | 2022-06-17 16:50 |  |  | 16/6/22 - Dean Simpson, Zach HarrowerTested door and door locks everytime when handle has not been used within time limit.Appears egress is holding door open from lock.Took lock apart and will either need to replace part or lock.Return required.17/6/22 - Dylan Parslow, Joshua Park,Replaced part and adjusted lock for egress signal and tested.All working ok.
MSA-DCA | WA5792146 | 2 | GPS Plumbing & Gas Services PtyLtd | Toilet is out of order and possibly leaking, please investigate | Plumbing & Drainage | Toilets/Cisterns | 312.29 | Pass | Pass | 0 | 0 | 26.25 | 2022-08-23 11:50 | 2022-08-26 17:00 | 2022-08-24 13:45 | 2022-08-26 17:00 | 2022-08-25 16:00 |  | WACCES | Ordered new side entry inlet from Reece. Will be at store tomorrow morning.
MSA-DTWD | WA6366131 | 1 | Protek 24/7 Building & Maintenance | Rear Compound - damaged fence panel | Building | Steel Fencing & Gates | 742.905 | Pass | Fail | 0 | 0 | 26.25 | 2022-12-13 15:53 | 2022-12-14 17:00 | 2022-12-14 12:45 | 2022-12-14 17:00 | 2022-12-15 15:00 |  | WACCES | Removed and replaced damaged mesh fencing
MSA-DTWD | WA6520319 | 2 | CONNECT SECURITY SYSTEMS | Ground - Alarm panel - Alarm panel showing low battery | Security | Monitoring | 1168.37 | Pass | Pass | 0 | 0 | 26.25 | 2023-01-27 12:52 | 2023-02-01 17:00 | 2023-01-30 09:15 | 2023-02-01 17:00 | 2023-01-31 11:30
MSA-DFES | WA5188906 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Outside and engine room - low water pressure - see notes below | Plumbing & Drainage | Water | 1137.05 | Fail | Fail | 0 | 0 | 26.1667 | 2022-02-23 12:23 | 2022-02-28 17:00 | 2022-03-02 13:20 | 2022-02-28 17:00 | 2022-03-03 15:30 |  |  | Attended site for low water pressure on the cold side have not been able to find a cause for the low water pressure we believe there is a possible blockage in the cold line I have run a new line to increase the water pressure to A suitable pre
MSA-DCA | WA6183728 | 1 | EQUANS Mechanical Services (WA) Pty Limited | plant room No4-Mezz level-multiple alarms resulting from gen test | Air Conditioning | Building HVAC Maintenance (Major Plant) | 976.86 | Pass | Pass | 0 | 0 | 26.1667 | 2022-11-15 08:11 | 2022-11-16 17:00 | 2022-11-15 13:00 | 2022-11-16 17:00 | 2022-11-16 15:10 |  |  | DIALLED INTO SITE AND CHECKED THROUGH ALARM TRIPS. FOUND MULTIPLE UNITS ACROSS SITE HAD LOSS SIGNAL DUE TO GENERATOR TEST. UNABLE TO RESTART ALL REMOTELY. ATTENDED SITE AND SIGNED IN. CHECKED OPERATION OF UNITS THAT DIDN'T REGAIN COMMS. POWER CYCLED HONEYWELL CONTROLS AND POWER TO AFFECTED UNITS AND TESTED OPERATION. 5 UNITS BACK ONLINE, CONFIRMED OPERATION. 4 UNITS ARE STILL HAVING ISSUES. ENGAED HONEYWELL TO INVESTIGATE FURTHER. CHECKED AND FOUND ALL WAS RESTORED TO NORMAL. FOUND THE PROBLEM WAS CAUSED BY GENERATOR TEST. RESET CONTROLLER AND CHECKED OPERATIONS, ALL OK.
MSA-DCA | WA5141348 | 1 | Precise Air Group | Ground - Planet Books - AC in tenancy Planet Books is spitting water over stock | Air Conditioning | Room Air Conditioners | 540.26 | Pass | Pass | 0 | 0 | 26.0833 | 2022-02-16 09:36 | 2022-02-17 17:00 | 2022-02-16 12:05 | 2022-02-17 17:00 | 2022-02-17 14:10 |  |  | Returned to site with additional ladder and apprentice, befor store opens, insulated drain pipe to eliminate condensation on external of drain, explained to tenant that doors should be closed to eliminate any outside air issue etc. cleared debris from site
MSA-MRWA | WA6394253 | 2 | EQUANS Mechanical Services (WA) Pty Limited | lift motor room - LMR A/C 1 tripping circuit | Air Conditioning | Building HVAC Maintenance (Major Plant) | 500 | Pass | Pass | 0 | 0 | 26.0667 | 2022-12-30 10:13 | 2023-01-05 17:00 | 2023-01-03 11:05 | 2023-01-05 17:00 | 2023-01-04 13:09
MSA-DCA | WA5417616 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - Investigate the water leak at the back of boiler 3 | Mechanical Services | Boilers | 790.7 | Pass | Fail | 0 | 0 | 26 | 2022-05-13 14:16 | 2022-05-16 17:00 | 2022-05-16 08:00 | 2022-05-16 17:00 | 2022-05-17 10:00 |  |  | Attended site, signed in and accessed boiler plantroom with RCR Tomlinson. Boiler 3 running as per normal with no new faults. Discovered the boiler flue entering the ceiling / roof space was leaking water and needs to be resealed correctly by a roof plumber. The boiler Flue also has water seaping out through the lagging onto the floor. A quote will be sent in the coming weeks as a process of elimination to rectify this.
MSA-DTWD | WA6521964 | 1 | Equans Mechanical Services Australia | West End - Evaporative air conditioner not working on cooling cycle - operating on fan mode only | Air Conditioning | Evaporative Coolers | 399.78 | Fail | Fail | 0 | 0 | 26 | 2023-01-30 15:09 | 2023-01-31 17:00 | 2023-02-01 08:00 | 2023-01-31 17:00 | 2023-02-02 10:00
MSA-DTWD | WA5101742 | 3 | Precise Air Group | Aircon in S106 Client Services swing vent not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 235.48 | Pass | Pass | 0 | 0 | 26 | 2022-02-03 14:19 | 2022-02-10 17:00 | 2022-02-07 10:00 | 2022-02-10 17:00 | 2022-02-08 12:00 |  |  | Inspected unit. Reset and left operating all ok . See invoice notes
MSA-DFES | WA5175520 | 2 | MALCOLM THOMPSON PUMPS PTY LTD | Bottom Dam - Broken cooling fan on bottom dam panel | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 26 | 2022-02-21 12:10 | 2022-02-24 17:00 | 2022-02-22 07:00 | 2022-02-24 17:00 | 2022-02-23 09:00 |  |  | job completed - replaced faulty fan
MSA-DTWD | WA5407272 | 1 | Equans Mechanical Services Australia | S Block air con / chiller not working – no alarm showing | Air Conditioning | Building HVAC Maintenance (Major Plant) | 838.71 | Pass | Fail | 0 | 0 | 26 | 2022-05-11 10:47 | 2022-05-12 17:00 | 2022-05-12 10:00 | 2022-05-12 17:00 | 2022-05-13 12:00 |  |  | On arrival found chiller alarming on Flow Interlock.Manualled both chiller and CHW pump. Had to drive open the CHW Bypass as this was closed and the field wasclosed, so no flow was going through the vessel.Ran chiller on test, found flow switch operating as normal and chiller started up with no issues. All pressures andtemperatures where within range.Found CHW Flow Interlock relay to be working but looked scorched from overheating. Recommend replacing.Also found condenser fan motor overload had tripped. Reset and ran on test
MSA-DTWD | WA5460180 | 3 | AWB Co. | Lights not working and have broken fittings | Electrical | General Electrical | 559.0925 | Pass | Pass | 0 | 0 | 26 | 2022-05-18 11:46 | 2022-05-25 17:00 | 2022-05-23 10:30 | 2022-05-25 17:00 | 2022-05-24 12:30 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Located toilet with faulty lights. Isolated. Supplied and replaced old lights with new LED battens. Reenergised circuit. Tested for correct operation. All working correctly. Notified fm. **job complete**
MSA-DTAG | WA5628279 | 1 | Automatic Fire Protection (ARA) | Main Fire Panel error light | Fire Protection Services | Fire Protection - Monitor System | 461.48 | Pass | Pass | 0 | 0 | 26 | 2022-07-15 12:55 | 2022-07-18 17:00 | 2022-07-18 07:00 | 2022-07-20 18:00 | 2022-07-19 09:00 |  | WCAPPR | 18/07/2022Attended site spoke to Kay she advised the had a mock fire drill on Friday and no tones could be heard top floor of sheriffs office building, checked eiws panel and found speaker fault on that level will require 2 x techs to test area and rectify fault, you will need to speak to site to organise appropriate time to test evac tones.19/07/2022Reattended site performed tone test of area and found no speakers working in zone, checked amplifier feeding zone and found fuse had blown replaced fuse and fault cleared and tones now audible in area.
MSA-DTWD | WA6020649 | 3 | COMMERCIAL PLUMBING AND GAS | Vehicle Body Building hardstand - Blocked Drain | Plumbing & Drainage | Drainage | 769.195 | Pass | Pass | -1 | -1 | 26 | 2022-10-13 15:12 | 2022-10-20 17:00 | 2022-10-13 16:00 | 2022-10-20 17:00 | 2022-10-14 18:00 |  |  | investigate stormwater, open seized gatic lid
MSA-DTWD | WA6292847 | 3 | Techworks Plumbing | A and B Block - Exterior - x4 down pipes - Brackets loose and need replacing | Plumbing & Drainage | Drainage | 759.91 | Pass | Pass | -1 | -1 | 26 | 2022-11-29 13:48 | 2022-12-06 17:00 | 2022-12-01 11:30 | 2022-12-06 17:00 | 2022-12-02 13:30 |  |  | 4/6 can be repaired on ground/extension ladder2/6 must be repaired on an ewpthere is restricted access, so we may need measure how far the EWP can extend its platform (pictures attached)600mm of 100x100mm downpipe needs replacinginstalled 2x pvc saddle clips on vent risercoated clips and screws with anti-rusting spray due to vicinity of oceanrepaired 500mm of downpipe and installed clipinstalled sump box and grate to help with discharge
MSA-DTWD | WA6666512 | 1 | Equans Mechanical Services Australia | Aircon - Faulty - No cold air supplied | Air Conditioning | Room Air Conditioners | 835.14 | Pass | Fail | 0 | 0 | 26 | 2023-02-21 13:40 | 2023-02-22 17:00 | 2023-02-22 12:00 | 2023-02-22 17:00 | 2023-02-23 14:00
MSA-DTWD | WA6674614 | 2 | Australian Airconditioning Services Pty Ltd | AC not cooling - control panel randomly in fault - see notes | Air Conditioning | Room Air Conditioners | 1025.37 | Pass | Pass | 0 | 0 | 26 | 2023-02-27 11:10 | 2023-03-02 17:00 | 2023-02-28 07:30 | 2023-03-02 17:00 | 2023-03-01 09:30 |  | WACCES
MSA-DTWD | WA6680341 | 2 | AWB Co. | east side along Pathway - Pitt lids x3 West side P Block are damaged and require fixing | Building | General Building | 1367.32 | Pass | Pass | -1 | -1 | 26 | 2023-03-01 10:15 | 2023-03-07 17:00 | 2023-03-01 13:00 | 2023-03-07 17:00 | 2023-03-02 15:00 |  | WACCES
MSA-DFES | WA5696081 | 3 | Dom's Total Grounds Maintenance | Applied training car park - Broken Retic Pipe | Plumbing & Drainage | Water | 398.5 | Pass | Pass | -1 | -1 | 25.8333 | 2022-08-08 09:35 | 2022-08-15 17:00 | 2022-08-09 16:00 | 2022-08-15 17:00 | 2022-08-10 17:50 |  |  | 2 x Call Outs, Labour & Parts
MSA-DCA | WA5239517 | 1 | TK Elevator Australia Pty Ltd | Basement 2 - Lift 7 - doors opening and closing erratically | Lifts | Lifts |  | Pass | Fail | 0 | 0 | 25.8167 | 2022-03-16 12:38 | 2022-03-17 17:00 | 2022-03-17 07:54 | 2022-03-17 17:00 | 2022-03-18 09:43 |  |  | Lift7 Greem Rm-Hydraulic :bottom landing door switch not making adjusted switch and order new part,left lift running
MSA-DCA | WA5090818 | 0 | Critical Fire Protection & Training | HBR Buidling - Fire Panel - electrical fault - | Electrical | Distribution Board | 3684.5652 | Pass | Fail | 0 | 0 | 25.75 | 2022-01-26 09:17 | 2022-01-26 11:17 | 2022-01-26 10:15 | 2022-01-26 13:17 | 2022-01-27 12:00 |  |  | Investigate fault .Paul on site defective psu. Paul to organise new part and install. Collections ewis.
MSA-DTWD | WA5795298 | 3 | AWB Co. | Room B405E - 3 lights out plus exit light | Electrical | Lighting, Internal | 999.385 | Pass | Pass | 0 | 0 | 25.75 | 2022-08-25 10:55 | 2022-09-01 17:00 | 2022-08-29 14:15 | 2022-09-01 17:00 | 2022-08-30 16:00 |  |  | Lots of light fittings need replaced due to all lamp holders being brittle
MSA-DTWD | WA5001491 | 2 | Equans Mechanical Services Australia | F59 - air con is not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 245.93 | Pass | Pass | 0 | 0 | 25.5 | 2022-01-11 12:37 | 2022-01-14 17:00 | 2022-01-12 09:00 | 2022-01-14 17:00 | 2022-01-13 10:30 |  |  | Found the thermostat which is in the ceiling space set on 24 and low fan , dropped the temp to 22 and increased the fan speed.
MSA-DTWD | WA5206972 | 0 | Equans Mechanical Services Australia | Cafeteria - Cool room not cold - | Refrigeration | Coolroom | 722.17 | Pass | Fail | 0 | 0 | 25.5 | 2022-03-08 10:21 | 2022-03-08 12:21 | 2022-03-08 12:00 | 2022-03-08 14:21 | 2022-03-09 13:30 |  | WCAPPR | Arrived on site signed in, checked in with Dennis. Gathered tools and equipment, removed old condenser fan motor and replaced with new tested all ok. Cleaned up and completed paperwork and signed out.
MSA-DTWD | WA5438134 | 1 | FSA (WA) Pty Ltd | A146a Male shower - Fire alarm activated while using the shower | Fire Protection Services | Fire Protection - Monitor System | 367.08 | Pass | Pass | 0 | 0 | 25.5 | 2022-05-16 12:42 | 2022-05-17 17:00 | 2022-05-16 13:00 | 2022-05-17 17:00 | 2022-05-17 14:30 |  |  | Arrived to find smoke detector in shower on alarm. Wireless detector so need to order and return tomorrow to replace and reprogram. Left isolated and notified John on site. Returned the next day and replaced with a heat detector to stop any false alarms. Re programmed at fire panel and de isolated system. All ok.
MSA-DTAG | WA5499831 | 1 | Sapio Pty Ltd | Ground - Registry - Alarm system fault - Main office HBUS O/I not responding | Security | Monitoring | 719.95 | Pass | Pass | 0 | 0 | 25.5 | 2022-06-10 14:29 | 2022-06-13 17:00 | 2022-06-10 15:30 | 2022-06-13 17:00 | 2022-06-11 17:00 |  |  | Reattended site as issue had returned, replaced HBUS IO Board, tested, all OK.
MSA-DTWD | WA5568824 | 2 | AWB Co. | 2 Lights faulty | Electrical | Lighting, Internal | 567.805 | Pass | Pass | 0 | 0 | 25.5 | 2022-06-27 09:17 | 2022-06-30 17:00 | 2022-06-27 14:00 | 2022-06-30 17:00 | 2022-06-28 15:30 |  | WACCES | Attended site signed in jsa completed. Picked up lights from wholesaler and installed in class. All works fine now and tested.job completed
MSA-DFES | WA5839375 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | GPO's not working | Electrical | General Electrical | 671.095 | Pass | Pass | -1 | -1 | 25.5 | 2022-09-09 11:40 | 2022-09-14 17:00 | 2022-09-09 12:00 | 2022-09-14 17:00 | 2022-09-10 13:30 |  |  | Restored power to site, switch board upgrade or main switch and back bone cabling upgrade recommend
MSA-DTWD | WA6127059 | 2 | LIGHTHOUSE LOCKSMITHS | Repair/replace digital lock. | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 25.5 | 2022-10-25 16:46 | 2022-10-28 17:00 | 2022-10-26 11:30 | 2022-10-28 17:00 | 2022-10-27 13:00 |  |  | 26/10 removed digital locks on first floor d block 27/10 made and fitted scar plates to cover holes
MSA-DTAG | WA6364508 | 3 | Midolo Building Services | Level 3 - Public corridor - ceiling access to fix fire sprinkler - see notes | Building | Ceiling | 635.24 | Pass | Pass | -1 | -1 | 25.5 | 2022-12-12 12:09 | 2022-12-19 17:00 | 2022-12-13 07:00 | 2022-12-19 17:00 | 2022-12-14 08:30 |  |  | MANHOLE INSTALLED & SEATS SECURED
MSA-DTAG | WA6131978 | 3 | Australian HVAC Services Pty. Ltd. | Roof - A/C unit to be disconnected to allow for roof repairs | Air Conditioning | Building HVAC Maintenance (Major Plant) | 877.56 | Pass | Pass | -1 | -1 | 25.3167 | 2022-10-31 10:51 | 2022-11-07 17:00 | 2022-11-01 09:41 | 2022-11-07 17:00 | 2022-11-02 11:00 |  |  | Attended site, accessed roof & disconnected ac to ups room to allow roof repairsReturned to site and reistated pipework & cables to ac in ups room , evacuated system and opened system .tested operation, ok
MSA-DTWD | WA5116344 | 2 | Protek 24/7 Building & Maintenance | D Block - Ground - D1 main door to ladies toilet - Unable to close door looks like damaged hinges | Building | Doors | 151.825 | Pass | Pass | 0 | 0 | 25.25 | 2022-02-11 14:04 | 2022-02-16 17:00 | 2022-02-14 07:15 | 2022-02-16 17:00 | 2022-02-15 08:30 |  |  | Damaged Hinges to ladies toilet door
MSA-DTAG | WA6190562 | 2 | Midolo Building Services | Level 4 - Court 42 - Prisoners seats in Court 42 dock are loose | Furniture | Indoor Furniture | 733.04 | Pass | Pass | -1 | 0 | 25.25 | 2022-11-16 09:13 | 2022-11-21 17:00 | 2022-11-17 07:15 | 2022-11-21 17:00 | 2022-11-18 08:30 |  |  | SEAT REMOVED & REPAIRED IN WORKSHOP, THEN RE-INSTALLED
MSA-DFES | WA5393908 | 2 | AWB Co. | Ground - Engine Room - please see below details | Building | General Building | 392.56 | Pass | Pass | -1 | 0 | 25.25 | 2022-05-04 11:06 | 2022-05-09 17:00 | 2022-05-05 12:00 | 2022-05-09 17:00 | 2022-05-06 13:15 |  |  | Install magnetic catch to door and refix magnet control biz back to wall. Problem with magnetic control box not energisinginstall electric magnet for door
MSA-DFES | WA5998349 | 2 | SONTEC WA PTY LTD | Level 1 - Camera 3 not showing on main monitor in reception - see notes below | Security | CCTV Surveillance | 619.18 | Pass | Pass | 0 | 0 | 25.25 | 2022-10-07 14:31 | 2022-10-12 17:00 | 2022-10-10 12:45 | 2022-10-12 17:00 | 2022-10-11 14:00 |  |  | 10/10/22 - Dylan ParslowFound camera 3 not powering up.Recomend replacement.11/10/22 - Dylan ParslowReplaced camera 3.All tested ok.
MSA-DTWD | WA6148692 | 2 | AWB Co. | replace lights in bathroom and passage A115 | Electrical | Lighting, Internal | 949.08 | Pass | Pass | 0 | 0 | 25.25 | 2022-11-04 08:12 | 2022-11-09 17:00 | 2022-11-07 14:30 | 2022-11-09 17:00 | 2022-11-08 15:45 |  |  | Attended site and signed in, reviewed JSA, replaced remaining tubes in A115(quiet study area), all lights now working as intended, completed paperwork,signed out , job completed
MSA-DTWD | WA5069183 | 3 | AWB Co. | 2 x lights out | Electrical | Lighting, Internal | 184.82 | Pass | Fail | 0 | 0 | 25 | 2022-01-19 16:24 | 2022-01-27 17:00 | 2022-01-27 15:00 | 2022-01-27 17:00 | 2022-01-28 16:00 |  | WCAPPR | Attended site and signed in. Completed JSA. Set up work area. Located which lights were faulty. Replaced tubes and starters in required fittings. Took pictures. Everything working as intended. Completed paperwork. Signed out. *** Job complete ***
MSA-DCA | WA5108671 | 2 | Techworks Electrical | Library - Disintegrated tombstones in lights in Library replacements on site | Electrical | Lighting, Internal | 1446.9 | Fail | Fail | 1 | 1 | 25 | 2022-02-08 16:07 | 2022-02-11 17:00 | 2022-02-16 09:30 | 2022-02-11 17:00 | 2022-02-17 10:30 |  |  | Replaced with LEDs
MSA-DTAG | WA5201271 | 3 | Midolo Building Services | Level 3 - Court 38 - Behind - soap dispenser in rest room is damaged | Building | Internal Walls | 225.17 | Pass | Pass | -1 | -1 | 25 | 2022-03-02 13:04 | 2022-03-10 17:00 | 2022-03-03 12:45 | 2022-03-10 17:00 | 2022-03-04 13:45 |  | WACCES | supply 3 & install 1 soap dispensers
MSA-DTWD | WA5400898 | 1 | Lane's Plumbing | Paddock 1 - Faulty valves on two sheep water troughs | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 25 | 2022-05-10 14:00 | 2022-05-11 17:00 | 2022-05-10 15:00 | 2022-05-11 17:00 | 2022-05-11 16:00 |  |  | Replaced faulty valve
MSA-DTWD | WA5407841 | 1 | Precise Air Group | A Block - A51 - VAV duct has come away from VAV creating a noise hazard | Air Conditioning | Evaporative Coolers | 455.26 | Pass | Fail | 0 | 0 | 25 | 2022-05-11 14:12 | 2022-05-12 17:00 | 2022-05-12 09:30 | 2022-05-12 17:00 | 2022-05-13 10:30 |  |  | Attended supplier and collected duct . Returned to site and completed pre start paperwork and signed in. Accessed ceiling space and replaced section of disintegrated duct. Test ran equipment. Left in good working order.
MSA-DTWD | WA5416912 | 3 | AWB Co. | G Block West - 6 x eternal lights faulty | Electrical | Lighting, External | 1818.625 | Fail | Fail | 4 | 4 | 25 | 2022-05-13 09:20 | 2022-05-20 17:00 | 2022-06-14 10:30 | 2022-05-20 17:00 | 2022-06-15 11:30 |  |  | Attended site and signed in, reviewed jsa , spoke with fm about job, isolated lighting circuits and removed remaining old fittings, replaced with new, re energised circuit and tested lighting,all lights working as intended, completed paperwork ,packed up, signed out ***job completed***
MSA-DTAG | WA5675261 | 3 | MALCO FLOORING PTY LTD | Court Room 5 - Carpet tile is raised up and the floor is squeaky near JSO entry door- See notes | Flooring | Carpet | 405 | Pass | Pass | -1 | 0 | 25 | 2022-07-22 09:11 | 2022-07-29 17:00 | 2022-07-25 07:30 | 2022-07-29 17:00 | 2022-07-26 08:30 |  |  | REPLACED RAMP AND INSTALLED CARPET TILES SUPPLIED FROM STORE TO COURT ROOM 5 WHERE CARPET TILE RAISED AND THE FLOOR IS SQUEAKY
MSA-DTWD | WA5696800 | 1 | Precise Air Group | Display fridge not cooling cafe | Refrigeration | Refrigerators | 467.35 | Pass | Fail | 0 | 0 | 25 | 2022-08-08 14:40 | 2022-08-09 17:00 | 2022-08-09 08:00 | 2022-08-09 17:00 | 2022-08-10 09:00 |  |  | attended site signed in and gained access to the Cafe. Carried out checks on display fridge. Unit was down at set point but pressures seemed a little off. suspect unit may be low on gas. Will monitor on maintenance and submit quote if nessesary.re attended and spoke with tenants and informed me that the fridge was working. will close off for now and monitor moving forward
MSA-DTAG | WA5853808 | 1 | Water2water Pty Ltd | Level 3 - Admin kitchen - Billi unit displaying leak fault – bar code A402021132 | Plumbing & Drainage | Water | 1398.3 | Pass | Pass | 0 | 0 | 25 | 2022-09-12 11:23 | 2022-09-13 17:00 | 2022-09-12 12:55 | 2022-09-13 17:00 | 2022-09-13 13:55 |  |  | System in fault on arrival, leak and pcb failure. Replaced main pcb board and tube kit. No water through unit. Replaced inlet solenoids, still not working. Removed unit from site, to the workshop. Replaced plv. Returned unit to site, ran to temp, normal operation
MSA-DTWD | WA5080643 | 3 | Penske Power Systems | Level 1 - N122 - Emergency Generator failed to start - Failed batteries | Equipment Hire | Compressors, Generators |  | Fail | Fail | 1 | 1 | 25 | 2022-01-20 08:07 | 2022-01-28 17:00 | 2022-02-02 10:00 | 2022-01-28 17:00 | 2022-02-03 11:00 |  |  | job completed -Tested main batteries and also failed test. Organised and collected new batteries to install. Removed and installed new batteries. Carried out test and showing full voltage 25v. Remove battery charger as original worked with new batteries. Ran genset and started up as per normal. Packed up and returned to workshop.
MSA-DTWD | WA5128028 | 2 | Falcetta Plumbing and Gas | Level 1 - D113 - Jewellery Workshop - Gas isolation valve not aligned (forced) | Plumbing & Drainage | Gas | 1397.6 | Pass | Fail | 0 | 0 | 25 | 2022-02-14 15:25 | 2022-02-17 17:00 | 2022-02-17 14:30 | 2022-02-17 17:00 | 2022-02-18 15:30 |  | WACCES | completed repairs inside and reported on storage area
MSA-DTWD | WA6113327 | 2 | JEM Carpentry | Faulty fence | Building | Steel Fencing & Gates |  | Pass | Fail | 0 | 0 | 25 | 2022-10-24 10:40 | 2022-10-27 17:00 | 2022-10-27 14:30 | 2022-10-27 17:00 | 2022-10-28 15:30 |  |  | installed fencing
MSA-DTWD | WA5101605 | 1 | Falcetta Plumbing and Gas | 2 x damaged cisterns | Plumbing & Drainage | Toilets/Cisterns | 845.06 | Pass | Pass | 0 | 0 | 24.75 | 2022-02-03 13:11 | 2022-02-04 17:00 | 2022-02-03 14:15 | 2022-02-04 17:00 | 2022-02-04 15:00 |  |  | replaced 2 cisterns
MSA-DFES | WA5108476 | 1 | Australian HVAC Services Pty. Ltd. | Dorm 6 (Room 26) - Aircon is not working with error code: CH67 | Air Conditioning | Room Air Conditioners | 130.05 | Pass | Fail | 0 | 0 | 24.75 | 2022-02-08 14:26 | 2022-02-09 17:00 | 2022-02-09 08:15 | 2022-02-09 17:00 | 2022-02-10 09:00 |  |  | Attempted to access site at 8:15am & 10:30am (09/02/21), no fire-fighters onsite, returned to site 8am (10/02/21). Arrived onsite, signed in & spoke to onsite representative who directed me to dorms with faulty A/C units, began investigation & found that we already have a repair job open for this unit. We had been waiting on parts, although parts have now arrived as of late last week. Repairs will be carried out today.Ref work order - WA4958783
MSA-DTWD | WA5660604 | 2 | AHS Services WA Pty Ltd (Anchor) | taps behind electro technology and plumbing sections are loose and leaking | Plumbing & Drainage | Water | 1132.85 | Pass | Pass | 0 | 0 | 24.7167 | 2022-07-19 11:03 | 2022-07-22 17:00 | 2022-07-20 06:30 | 2022-07-22 17:00 | 2022-07-21 07:13 |  |  | Job completed
MSA-DTWD | WA6127007 | 2 | LIGHTHOUSE LOCKSMITHS | Repair/replace Digital lock in D008. | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 24.6667 | 2022-10-25 16:09 | 2022-10-28 17:00 | 2022-10-26 11:50 | 2022-10-28 17:00 | 2022-10-27 12:30 |  |  | 26/10 removed digital lock on ground floor d block 27/10- made scar plates to cover holes
MSA-DCA | WA5679525 | 2 | GPS Plumbing & Gas Services PtyLtd | Both tap sets to be faulty in dressing room M1 | Plumbing & Drainage | Water | 703.205 | Fail | Fail | 1 | 1 | 24.6333 | 2022-07-26 14:39 | 2022-07-29 17:00 | 2022-08-02 14:22 | 2022-07-29 17:00 | 2022-08-03 15:00 |  | WCAPPR | Rh basin taps done. Was asked to leave as change room.was needed for performers.
MSA-DFES | WA5382239 | 3 | Australian HVAC Services Pty. Ltd. | Station Dinning Room - air conditioner fan is making a grating noise when operating | Air Conditioning | Room Air Conditioners | 334.88 | Pass | Fail | 0 | 0 | 24.5 | 2022-04-26 16:11 | 2022-05-03 17:00 | 2022-05-03 08:00 | 2022-05-03 17:00 | 2022-05-04 08:30 |  |  | Noise coming from Louvre motor assy. Part has been replaced and tested
MSA-DTWD | WA5563262 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire Panel alarm - is unable to reset after alarm | Fire Protection Services | Fire Protection - Monitor System | 425.58 | Pass | Fail | 0 | 0 | 24.5 | 2022-06-20 13:20 | 2022-06-20 15:20 | 2022-06-20 14:00 | 2022-06-20 17:20 | 2022-06-21 14:30 |  | WACCES | ATTENDED 20/6/22 - TO INVESTIGATE ISSUE - RETURNED 21/6/22 WITH NEW SENSOR TO BE INSTALLED AS NONE ON VEHICLE AT TIME OF CALL OUT. PLEASE SEE SIG SLIP AND REPORT.
MSA-DTWD | WA6156512 | 1 | Protek 24/7 Building & Maintenance | N Block decking - broken slat | Carpentry | Timber (all types) | 221.74 | Pass | Fail | 0 | 0 | 24.5 | 2022-11-09 08:29 | 2022-11-10 17:00 | 2022-11-10 14:00 | 2022-11-10 17:00 | 2022-11-11 14:30 |  |  | Replaced damaged deck board
MSA-DTWD | WA5189030 | 1 | Techworks Plumbing | S block - chiller - to dig bitumen and expose leaking pipe for aircon vendor | Plumbing & Drainage | Water | 912.33 | Pass | Fail | 0 | 0 | 24.5 | 2022-02-23 13:22 | 2022-02-24 17:00 | 2022-02-24 13:30 | 2022-02-24 17:00 | 2022-02-25 14:00 |  |  | Investigated leak near chiller, found cause of problem and exposed 20mm pressure T. The fitting has failed and needs repair work done.Originally the TAFE asked us to only expose the pipe and NOT fix the pipe itself. Once we were onsite and exposed the pipework, they asked to actually fix the pipe and to return 25/2
MSA-DFES | WA5392984 | 2 | AWB Co. | Hallway Door - Door between engine room & Duty Office needs hinge and screws replaced | Building | Doors | 188.5 | Pass | Pass | 0 | 0 | 24.5 | 2022-05-03 13:53 | 2022-05-06 17:00 | 2022-05-05 14:30 | 2022-05-06 17:00 | 2022-05-06 15:00 |  |  | Attended site to inspect works required and take sizes.Installed new hinge to fire door
MSA-DCA | WA6001246 | 1 | Protek 24/7 Building & Maintenance | Accessible Toilet Door Not Closing Properly-see notes | Building | Doors | 278.96 | Pass | Fail | 0 | 0 | 24.5 | 2022-10-10 14:06 | 2022-10-11 17:00 | 2022-10-11 08:15 | 2022-10-11 17:00 | 2022-10-12 08:45 |  |  | Adjusted toilet door
MSA-DCA | WA6653812 | 1 | Techworks Electrical | Level 2 (FOH 1) - Special Exhibitions Gallery - Cubicle toilets at the back of Seg - No lights | Electrical | Lighting, Internal | 135.15 | Pass | Fail | 0 | 0 | 24.5 | 2023-02-21 07:12 | 2023-02-21 17:00 | 2023-02-21 09:00 | 2023-02-21 17:00 | 2023-02-22 09:30
MSA-DTWD | WA6184753 | 3 | COMMERCIAL PLUMBING AND GAS | level 4 - plant room - Rinnai HD 200i Domestic Gas water heater Keeps cutting out | Plumbing & Drainage | Gas | 1090.8 | Pass | Pass | 0 | 0 | 24.4833 | 2022-11-15 12:16 | 2022-11-22 17:00 | 2022-11-21 16:30 | 2022-11-22 17:00 | 2022-11-22 16:59 |  |  | replaced fan assembly and flue connector
MSA-DFES | WA5656654 | 3 | SONTEC WA PTY LTD | Suspended all access for card number 12681 | Security | Access Control | 230 | Pass | Pass | -1 | -1 | 24.4706 | 2022-07-18 16:14 | 2022-07-25 17:00 | 2022-07-19 12:20 | 2022-07-25 17:00 | 2022-07-20 12:48
MSA-DTWD | WA5800859 | 3 | AWB Co. | Pin board fallen off concrete wall | Building | Internal Walls | 92.805 | Pass | Fail | 0 | 0 | 24.4167 | 2022-08-31 12:53 | 2022-09-07 17:00 | 2022-09-07 13:50 | 2022-09-07 17:00 | 2022-09-08 14:15 |  |  | screwed pin board back to wall
MSA-DTWD | WA5380181 | 3 | AWB Co. | Room G116 - 5 x lights out in classroom | Electrical | Lighting, Internal | 336.22 | Pass | Fail | 0 | 0 | 24.3667 | 2022-04-22 09:13 | 2022-05-02 17:00 | 2022-05-02 11:08 | 2022-05-02 17:00 | 2022-05-03 11:30 |  | WCAPPR | Attended site and signed in, completed jsa,spoke with fm about job, isolated lighting circuits and removed old tubes and starters , replaced multiple tombstones , replaced tubes and starters , re energised lighting circuit, tested lights and working as intended,cleaned up,packed up,completed paperwork,signed out,Job completed
MSA-DTWD | WA5565790 | 2 | LIGHTHOUSE LOCKSMITHS | Key Tag 81 & Key tag 21 & Key tag 27 & 93 - new keys cut required x 6 each - See site contact | Security | Locksmith | 692.8 | Pass | Pass | -1 | 0 | 24.3333 | 2022-06-22 11:20 | 2022-06-27 17:00 | 2022-06-23 08:25 | 2022-06-27 17:00 | 2022-06-24 08:45 |  |  | attended site and replaced keys, need to reattend with parts. reattended and replaced 6 x keys
MSA-DTWD | WA5727211 | 0 | Boilertronics | Level 5 - boiler room - boiler will not start up | Mechanical Services | Boilers | 590.25 | Pass | Fail | 0 | 0 | 24.3167 | 2022-08-15 07:51 | 2022-08-15 09:51 | 2022-08-15 08:12 | 2022-08-15 11:51 | 2022-08-16 08:31 |  |  | Traveled to siteFound HWH in fault.Appliance has failed on fault 1 on the LFL reset appliance found appliance failing on fault P on LFL removed diffuser and changed position of the ignition rod. Stripped out air pressure switch pick up and inspected for debris . Found buildup of leaves on the air inlet cleaned and fired appliance.Checked start gas 16.3% 02Low fire 4.5%02 high fire 5.4%
MSA-DTWD | WA5109972 | 1 | Equans Mechanical Services Australia | Block 7 - Kitchen -Faulty Air conditioner in kitchen. see notes | Air Conditioning | Room Air Conditioners | 669.76 | Pass | Fail | 0 | 0 | 24.25 | 2022-02-09 14:43 | 2022-02-10 17:00 | 2022-02-10 11:15 | 2022-02-10 17:00 | 2022-02-11 11:30 |  |  | CHECKED AND FOUND ISSUE WITH WIRING.ALTER THE WIRING AND TESTED ON LOW AND HIGH SPEEDALL WORKING FINE.
MSA-DTWD | WA5177200 | 1 | ECO PLUMBING AND GAS PTY LTD | Sink drain blocked | Plumbing & Drainage | Drainage | 439.83 | Pass | Fail | 0 | 0 | 24.25 | 2022-02-21 16:02 | 2022-02-22 17:00 | 2022-02-22 13:30 | 2022-02-22 17:00 | 2022-02-23 13:45 |  | WACCES | cleared blockage
MSA-DFES | WA5294221 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Training Room down lights - Training Room downlights not working. Controlled by switch and dimmer | Electrical | General Electrical | 311.01 | Pass | Fail | 0 | 0 | 24.25 | 2022-03-28 14:20 | 2022-04-04 17:00 | 2022-04-04 14:45 | 2022-04-04 17:00 | 2022-04-05 15:00 |  |  | Attend site 1445. Investigate downlights not working on TV room. Found dimmer to be faulty and in need of replacement. Have temporarily bypassed the dimmer so lights do work, however one globe is currently faulty and in need of replacing. Informed staff of outcomes of investigation and intent to return with gear at a later date. Signed out at 1530. Returned next day at 1415. Replaced 3x globes and 1x dimmer. Lights now working and dimmable. Informed staff of outcomes and left site at 1500.
MSA-DTWD | WA5513178 | 1 | SCAVENGER SUPPLIES PTY LTD | L Block - FIP Offline | Fire Protection Services | Fire Protection - Monitor System | 1582.14 | Pass | Pass | 0 | 0 | 24.25 | 2022-06-14 08:24 | 2022-06-15 17:00 | 2022-06-14 09:45 | 2022-06-15 17:00 | 2022-06-15 10:00 |  |  | AUTHORISED TO GO AHEAD WITH WORK TO COMPLETION WITHOUT BY JANINE GOLSWORTHY 14/06/202214/06/2022- ATTENDED BY WB-BW-PARTS AQUIRED15/06/2022 -ATTENDED BY WB-BR- WORK COMPLETED**BRAF SUBMITTED 15/06/2022***
MSA-DTWD | WA6129464 | 2 | JEM Carpentry | Faulty fence cactus | Building | Steel Fencing & Gates |  | Pass | Pass | -1 | -1 | 24.25 | 2022-10-27 16:02 | 2022-11-01 17:00 | 2022-10-27 16:15 | 2022-11-01 17:00 | 2022-10-28 16:30 |  |  | Removal of cactus
MSA-DTAG | WA5839617 | 3 | Midolo Building Services | multiple chairs not bolted down - see notes below | Furniture | Indoor Furniture | 357.38 | Pass | Pass | 0 | 0 | 24.25 | 2022-09-09 14:00 | 2022-09-16 17:00 | 2022-09-14 09:15 | 2022-09-16 17:00 | 2022-09-15 09:30 |  |  | all chairs secured with new fixings
MSA-DCA | WA6466770 | 1 | Property Fire Maintenance | Street Level - Sub Stage - Door trimming near bottom of door to sub stage near green room | Fire Protection Services | Fire Protection - Monitor System | 540 | Pass | Fail | 0 | 0 | 24.2167 | 2023-01-17 13:38 | 2023-01-18 17:00 | 2023-01-18 12:32 | 2023-01-18 17:00 | 2023-01-19 12:45 |  | WACCES
MSA-DTWD | WA5493625 | 1 | AHS Services WA Pty Ltd (Anchor) | Tower Building -Fourth Floor - Gas smell near lifts | Plumbing & Drainage | Gas | 989.03 | Pass | Pass | 0 | 0 | 24.1333 | 2022-06-07 09:25 | 2022-06-08 17:00 | 2022-06-07 09:26 | 2022-06-08 17:00 | 2022-06-08 09:34 |  |  | Investigate gas leak in tower building, Locate gas services and boiler rooms. Testing completed the following morning and passed.
MSA-DCA | WA6178075 | 3 | Property Fire Maintenance | Ground / L2 - Collections Store 1 and L2 plantroom doors -Selector not operating correctly | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 181 | Pass | Pass | -1 | -1 | 24.0833 | 2022-11-14 09:22 | 2022-11-21 17:00 | 2022-11-15 13:33 | 2022-11-21 17:00 | 2022-11-16 13:38 |  |  | Fire Door Technician attended site and inspected the defect raised by another contractor. Both Doors Sequence Selectors were not required to be replaced. We adjusted one to function as required and the other was in full working order. We installed BCA Signage to door.
MSA-DFES | WA6008499 | 1 | Anvil Doors | Engine room door 3- door is faulting as per defects team | Building | Doors | 4510 | Fail | Fail | 4 | 4 | 24.0667 | 2022-10-11 15:48 | 2022-10-12 17:00 | 2022-11-08 11:38 | 2022-10-12 17:00 | 2022-11-09 11:42 |  |  | REPLACED CONTROLLERS TO DOOR 3INSTALL CLUTCH TO DOOR 4
MSA-DTWD | WA6154689 | 2 | Precise Air Group | Block D - Staff area - level 3 - Airconditioning not cool enough | Air Conditioning | Room Air Conditioners | 523.66 | Pass | Pass | 0 | 0 | 24.0333 | 2022-11-07 15:34 | 2022-11-10 17:00 | 2022-11-08 10:01 | 2022-11-10 17:00 | 2022-11-09 10:03 |  |  | arrived on site and signed in, located bms controls and carried out investigations, found some units with errors, checked units with alarms and checked chiller and ahu's, no faults found, checked vrv boxes and boxes not getting signal from bms, reset bms to gain better access, reset alarms and ran system, units running as they shouldPLease not Promap was not operating yesterday so unable to sign into while on site
MSA-DCA | WA6516250 | 1 | Precise Air Group | Basement store - Freezer not getting down to temperature - notes | Refrigeration | Freezers | 354.73 | Pass | Pass | 0 | 0 | 24.0167 | 2023-01-23 10:15 | 2023-01-24 17:00 | 2023-01-23 10:37 | 2023-01-24 17:00 | 2023-01-24 10:38
MSA-DTWD | WA5608844 | 2 | Precise Air Group | Exhaust Fan faulty | Air Conditioning | Room Air Conditioners | 287.17 | Fail | Fail | 10 | 10 | 24.0167 | 2022-07-13 12:03 | 2022-07-18 17:00 | 2022-09-28 07:44 | 2022-07-18 17:00 | 2022-09-29 07:45 |  |  | travelled to site checked exhaust fans in g Block toilets ha ve escalated to get them replace by Silvio Facility manager he is oking braff and work order .
MSA-DTWD | WA6258509 | 2 | Precise Air Group | Noisy air con | Air Conditioning | Room Air Conditioners | 381.6 | Pass | Pass | 0 | 0 | 24.0167 | 2022-11-25 12:41 | 2022-11-30 17:00 | 2022-11-28 10:29 | 2022-11-30 17:00 | 2022-11-29 10:30 |  |  | Attended site and signed out key/swipe card, gained access to D block room 203. Ran aircon system and found that the heat exchanger was squealing through the ductwork due to the silicone cracking from age. Re sealed ductwork and found noise had stopped.
MSA-DTWD | WA5976528 | 1 | Precise Air Group | Level 1 Roof Space - Restaurant kitchen evap on roof leaking through light fitting | Air Conditioning | Evaporative Coolers | 741.15 | Pass | Fail | 0 | 0 | 24.0167 | 2022-09-27 09:55 | 2022-09-28 17:00 | 2022-09-27 18:27 | 2022-09-28 17:00 | 2022-09-28 18:28 |  |  | attended site and locatedcreported leak. Removed light fitti ng and could not find any active leak related to the evap un it. Replaced bleed valve pointed out by facilities. do not b elieve this is the source of the leak as occupants believe i t only happens when it rains.
MSA-DTWD | WA6402043 | 2 | CLEVELAND COMPRESSED AIR SERVICES | 8mm overhead copper airline has been bent/damaged needs to be repaired/straightened-notes | Equipment Hire | Compressors, Generators | 412.5 | Fail | Fail | 1 | 2 | 24.0167 | 2023-01-05 07:57 | 2023-01-09 17:00 | 2023-01-19 11:12 | 2023-01-09 17:00 | 2023-01-20 11:13
MSA-DCA | WA5295549 | 0 | Techworks Electrical | Sections Building - losing power (popping in and out) | Electrical | General Electrical | 1397.19 | Pass | Fail | 0 | 0 | 24 | 2022-03-29 15:24 | 2022-03-29 17:24 | 2022-03-29 16:00 | 2022-03-29 19:24 | 2022-03-30 16:00 |  | WCAPPR | Phase failure relay is starting to fail - Set parameter thresholds to be slightly more tolerant whilst a newer upgraded model was being ordered - all OK.
MSA-DTWD | WA5675724 | 1 | AWB Co. | exhaust rang hood and lights not working | Electrical | Lighting, Internal | 640.5275 | Fail | Fail | 0 | 0 | 24 | 2022-07-22 13:10 | 2022-07-25 17:00 | 2022-07-26 08:00 | 2022-07-25 17:00 | 2022-07-27 08:00 |  |  | Attended site and signed in. Completed JSA. Liaised with cleaner about access to room. Isolated power. Moved ovens out of way. Supplied and replaced 3x old fittings with new LED battens. Energised and tested for correct operation. All working correctly. Moved ovens back to original state. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5679407 | 0 | Nessco Pressure Systems | RETROSPECTIVE WORK ORDER INV 123482-Oil and Glass plant - Compressor has seized up | Equipment Hire | Compressors, Generators |  | Fail | Fail | 0 | 0 | 24 | 2022-07-26 07:49 | 2022-07-26 09:49 | 2022-07-27 07:00 | 2022-07-26 11:49 | 2022-07-28 07:00 | 1 |  | Completed
MSA-DTAG | WA5798611 | 1 | Sapio Pty Ltd | Ground - Custody - Cameras have dropped out again – 35 in total | Security | CCTV Surveillance | 398.12 | Pass | Fail | 0 | 0 | 24 | 2022-08-29 16:20 | 2022-08-30 17:00 | 2022-08-30 09:00 | 2022-08-30 17:00 | 2022-08-31 09:00 |  |  | Attended site. Traced fault to PoE network switch located in room close to vending machines. Power cycled switch and tested. All missing cameras get back online and started recording. No fault present.
MSA-DFES | WA6111561 | 2 | MALCOLM THOMPSON PUMPS PTY LTD | Ground - Top dam - Parade Ground - top dam pump, it has a leaking relief valve | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 24 | 2022-10-21 08:43 | 2022-10-26 17:00 | 2022-10-21 09:00 | 2022-10-26 17:00 | 2022-10-22 09:00 |  |  | Replaced vacuum relief valve
MSA-DTWD | WA6132087 | 2 | ECO PLUMBING AND GAS PTY LTD | B 17 Block disable toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 98.54 | Pass | Fail | 0 | 0 | 24 | 2022-10-31 11:42 | 2022-11-03 17:00 | 2022-11-02 19:23 | 2022-11-03 17:00 | 2022-11-03 19:23 |  |  | Used plunger to unblock toilet
MSA-DFES | WA6144494 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Fire Fighters shower-shower rose flexible rose faulty | Plumbing & Drainage | Water | 212.76 | Pass | Pass | 0 | 0 | 24 | 2022-11-02 07:15 | 2022-11-04 17:00 | 2022-11-03 15:00 | 2022-11-04 17:00 | 2022-11-04 15:00 |  | WCAPPR | Attended site once access was available to inspect the faulty shower Rose in the first shower on the left in the first bathroom put inspection I found the flexible hoses damaged I’ve replaced it with a new one the new head after I’ve tested everything is working correctly cleaned up packed up
MSA-DFES | WA6359841 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - comcen female change room - No hot water in ladies shower - see notes | Plumbing & Drainage | HWS/Units Electric & Gas | 877.085 | Pass | Pass | 0 | 0 | 24 | 2022-12-07 07:10 | 2022-12-09 17:00 | 2022-12-07 15:30 | 2022-12-09 17:00 | 2022-12-08 15:30 |  |  | Attend site to change AVG temperature valve, located temperature valve in cupboard of women’s change room in comsen centre, removed old temperature valve, modified pipe work for newtemperature valve, installed new temperature valve, checked for leaks, temperature valve not leaking, tested taps and showers for hot water, cleaned up packed up.
MSA-DTAG | WA6579161 | 0 | Sapio Pty Ltd | Room L10-13 - ICT Door will not open at all | Security | Access Control | 1919.17 | Pass | Fail | 0 | 0 | 24 | 2023-02-15 15:17 | 2023-02-15 17:17 | 2023-02-15 16:30 | 2023-02-15 19:17 | 2023-02-16 16:30
MSA-DTWD | WA6132459 | 2 | ECO PLUMBING AND GAS PTY LTD | Drainage pipe to brick saws has collapsed needs to be reinstalled and cleaned | Plumbing & Drainage | Drainage | 330.61 | Pass | Fail | 0 | 0 | 23.9833 | 2022-10-31 14:00 | 2022-11-03 17:00 | 2022-11-02 19:25 | 2022-11-03 17:00 | 2022-11-03 19:24 |  |  | Unblocked 150mm drain and reclipped to wall
MSA-DCA | WA5477255 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant room, BMS notification of boiler fault, 24 May 2022 at 1:36pm. Please investigate | Air Conditioning | Building HVAC Maintenance (Major Plant) | 188.375 | Pass | Pass | 0 | 0 | 23.8667 | 2022-05-25 12:24 | 2022-05-26 17:00 | 2022-05-25 15:44 | 2022-05-26 17:00 | 2022-05-26 15:36 |  |  | Returned to site and rechecked boiler. No active faults and equipment running as required to keep building at set point. On speaking with site BMS tech pricing provided for replacement of heating water DP transducer as they are starting to intermittently fault. Confirmed plant operation. No further action can be taken on this job. Quote will be submitted for repairs. Work area left tidy.
MSA-DTWD | WA5833240 | 1 | Protek 24/7 Building & Maintenance | Roof leak around aircon unit | Roofing | Metal Roofing | 551.995 | Pass | Pass | 0 | 0 | 23.75 | 2022-09-06 08:44 | 2022-09-07 17:00 | 2022-09-06 09:15 | 2022-09-07 17:00 | 2022-09-07 09:00 |  |  | Invistigate roof leak Water test roofFound leak entry point Sealed dektight Re water tested to confirm
MSA-DTWD | WA6379244 | 1 | Total Security Systems Pty Ltd | Security alarm - Alarm batteries require checking - Gallagher system showing issues | Security | Security Management System | 475 | Pass | Pass | 0 | 0 | 23.75 | 2022-12-19 10:16 | 2022-12-20 17:00 | 2022-12-19 11:15 | 2022-12-20 17:00 | 2022-12-20 11:00 |  |  | 19/12/2022 - Evan Thompson - 11.15am to 12pmAttended site for Gallagher battery faults to T block ground floor East. I tested the batteries and under load with no AC the batteries drop to 11.6v.Please order 4x new alarm batteries to be replaced tomorrow. 20/12/2022 - Evan Thompson - 10.30am to 11amAttended site to replace 4x controller batteries.
MSA-DFES | WA6561041 | 2 | Protek 24/7 Building & Maintenance | Rear door on the Academy Store is not closing properly-see notes | Building | Doors | 551.3 | Pass | Pass | 0 | 0 | 23.75 | 2023-02-13 16:43 | 2023-02-16 17:00 | 2023-02-14 13:45 | 2023-02-16 17:00 | 2023-02-15 13:30
MSA-DCA | WA5482219 | 0 | EQUANS Mechanical Services (WA) Pty Limited | temperature is rising and the BMS alarm has gone off | Refrigeration | Freezers | 711.625 | Pass | Fail | 0 | 0 | 23.7333 | 2022-05-31 10:08 | 2022-05-31 12:08 | 2022-05-31 11:00 | 2022-05-31 14:08 | 2022-06-01 10:44 |  |  | Returned to site gained access and rechecked walk in freezer at HBC. Confirmed temp at set point of -19 and cycling correctly. Checked coil and confirmed free of moisture and frost build up. Confirmed all fan were operating once door close switch was made. Confirmed defrost heater operation. Fault is believed to have been caused by power surge. No further action is currently able to be taken on this job. Work area has been left tidy. Equipment is operating to requirements.
MSA-DTWD | WA6521388 | 2 | Australian Airconditioning Services Pty Ltd | FG11 - FG12 - Faulty isolator on chiller | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1053.1 | Pass | Pass | 0 | 0 | 23.5833 | 2023-01-30 10:24 | 2023-02-02 17:00 | 2023-01-30 10:25 | 2023-02-02 17:00 | 2023-01-31 10:00
MSA-DTWD | WA5609098 | 3 | AHS Services WA Pty Ltd (Anchor) | Basin Tap running A Block Male West End Ground Floor | Plumbing & Drainage | Water | 518.58 | Fail | Fail | 0 | 0 | 23.55 | 2022-07-13 13:52 | 2022-07-20 17:00 | 2022-07-21 07:30 | 2022-07-20 17:00 | 2022-07-22 07:03 |  |  | Job completed
MSA-DTWD | WA5066925 | 2 | Falcetta Plumbing and Gas | Level 2 - Creche - Sink is leaking into the wall | Plumbing & Drainage | Water | 438.14 | Pass | Pass | -1 | 0 | 23.5 | 2022-01-19 09:49 | 2022-01-24 17:00 | 2022-01-20 17:00 | 2022-01-24 17:00 | 2022-01-21 16:30 |  |  | cut cupboard to access and repair 50mm pipe
MSA-DTWD | WA5381546 | 3 | AWB Co. | Room 3G1 - Light switch stuck in off position | Electrical | General Electrical | 402.94 | Pass | Pass | -1 | -1 | 23.5 | 2022-04-26 09:47 | 2022-05-03 17:00 | 2022-04-27 10:30 | 2022-05-03 17:00 | 2022-04-28 10:00 |  |  | Attended site signed in completed jsa. Replaced switch in class. Works fine now. *** job completed ***
MSA-DTWD | WA5794466 | 2 | AWB Co. | faulty exhaust fan - making a horrible noise | Electrical | General Electrical | 673.535 | Pass | Fail | 0 | 0 | 23.5 | 2022-08-24 15:49 | 2022-08-29 17:00 | 2022-08-29 14:00 | 2022-08-29 17:00 | 2022-08-30 13:30 |  |  | Attended site and signed in, reviewed jsa,spoke with fm about job, set up work area, isolated fan, replaced fan belts on motors, re energised and tested , all working as intended, packed up, cleaned up, job completed
MSA-DTWD | WA5839438 | 2 | AWB Co. | Air con plant room - 2 x plant room doors catching and not opening properly - | Building | Doors | 839.83 | Pass | Fail | 0 | 0 | 23.5 | 2022-09-09 12:17 | 2022-09-14 17:00 | 2022-09-14 11:00 | 2022-09-14 17:00 | 2022-09-15 10:30 |  |  | Attend site carried out works as requested .
MSA-DTWD | WA6148893 | 2 | COMMERCIAL PLUMBING AND GAS | D18 hand wash area-Water supply leak-see notes | Plumbing & Drainage | Water | 566.15 | Pass | Pass | 0 | 0 | 23.5 | 2022-11-04 10:02 | 2022-11-09 17:00 | 2022-11-08 16:30 | 2022-11-09 17:00 | 2022-11-09 16:00 |  |  | repaired trough and wall
MSA-DTWD | WA6523201 | 1 | AWB Co. | Q Block - Exhaust fans are faulty | Electrical | General Electrical | 916.445 | Pass | Pass | 0 | 0 | 23.5 | 2023-01-31 13:13 | 2023-02-01 17:00 | 2023-01-31 14:00 | 2023-02-01 17:00 | 2023-02-01 13:30
MSA-DTWD | WA6674744 | 2 | Australian Airconditioning Services Pty Ltd | CG10 workshop - Evap No13 is noisy, making a squealing noise (see notes) | Air Conditioning | Ducted Split System | 495.82 | Pass | Pass | 0 | 0 | 23.5 | 2023-02-27 11:54 | 2023-03-02 17:00 | 2023-02-28 11:00 | 2023-03-02 17:00 | 2023-03-01 10:30 |  | WACCES
MSA-DTWD | WA6680463 | 1 | Techworks Electrical | Power board circuit tripping | Electrical | Distribution Board |  | Pass | Pass | 0 | 0 | 23.5 | 2023-03-01 11:29 | 2023-03-02 17:00 | 2023-03-01 12:30 | 2023-03-02 17:00 | 2023-03-02 12:00
MSA-DTWD | WA4990911 | 2 | Equans Mechanical Services Australia | Outside Cafe Counter - water on floor outside (possible from the aircon drip tray above) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 455.23 | Pass | Pass | 0 | 0 | 23.5 | 2022-01-04 13:05 | 2022-01-07 17:00 | 2022-01-04 14:30 | 2022-01-07 17:00 | 2022-01-05 14:00 |  |  | Checked the area in front of the canteen , no water on the floor, requires two people to access the FCU5th returned with a second person, couldn't find the leak staff will call up when happening.11th January Adjusted the drip tray so the water goes towards the pump
MSA-DTWD | WA5193769 | 2 | AWB Co. | BG25 workshop - Broken 15Amp 56 series Switched GPO (will need to be replaced) | Electrical | General Electrical | 527.97 | Pass | Pass | 0 | 0 | 23.5 | 2022-02-25 14:01 | 2022-03-02 17:00 | 2022-02-28 14:30 | 2022-03-02 17:00 | 2022-03-01 14:00 |  | WACCES | Attended site signed in completed jsa. Spoke with frank about swaping gpo. Isolated B8 and Replaced gpo and tested for operation. All tested ok ***JOB COMPLETED***
MSA-DTWD | WA5511859 | 1 | SCAVENGER SUPPLIES PTY LTD | Ground Floor - B8 - Fault showing on fire panel | Fire Protection Services | Fire Protection - Monitor System | 899.11 | Pass | Pass | 0 | 0 | 23.5 | 2022-06-13 10:11 | 2022-06-14 17:00 | 2022-06-13 13:00 | 2022-06-14 17:00 | 2022-06-14 12:30 |  | WACCES | OUR TECHNICIANS HAVE ATTENDED 13/6 - SEE SIG SLIP AND JOB REPORT. ADDITIONAL VISIT REQUIRED WITH CHERRY PICKER. TECHNICIANS RETURNED TO SITE 14/6 - SEE DOCUMENTATION.
MSA-DFES | WA5790837 | 0 | ADVANCED LOCK & KEY | Back door to the radio comms building - faulty lock - building unsecure | Building | Doors | 1455.84 | Pass | Fail | 0 | 0 | 23.5 | 2022-08-22 13:12 | 2022-08-22 15:12 | 2022-08-22 14:30 | 2022-08-22 17:12 | 2022-08-23 14:00 |  |  | Replace Mortice lock
MSA-DCA | WA5215392 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Revolving door - still opening halfling way the and issue of the middle panel doors shuttering | Building | Automatic Doors | 678 | Pass | Pass | 0 | 0 | 23.25 | 2022-03-10 11:41 | 2022-03-11 17:00 | 2022-03-10 14:45 | 2022-03-11 17:00 | 2022-03-11 14:00 |  |  | 10/03 - Attended site and inspected revolving door. Noted door operations and found bumping along. Inspected and found a brake wheel cracking andperishing. Also noted the beginning of the same to the corresponding drive assembly. Requires new drive assemblies and brake assemblies fitted.Quote to follow.Re-attend 11/03 - Attended site and inspected revolving door. Required to explain to management ( Jill and Christian ) and staff on site issues with wheels to door andreset procedures if required during the interim repair period.Quoted job done on Work order - WA5289980
MSA-DFES | WA5398820 | 2 | Protek 24/7 Building & Maintenance | L1 Men’s toilet – toilet roll holder has partially come off the wall | Building | Internal Walls | 680.85 | Pass | Pass | 0 | 0 | 23.25 | 2022-05-09 12:43 | 2022-05-12 17:00 | 2022-05-10 11:45 | 2022-05-12 17:00 | 2022-05-11 11:00 |  |  | Refixed toilet roll holder
MSA-DTAG | WA6425754 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 4 - Plantroom - Floor drain is blocked | Plumbing & Drainage | Water | 654.7275 | Pass | Pass | 0 | 0 | 23.2167 | 2023-01-12 11:33 | 2023-01-13 17:00 | 2023-01-12 11:50 | 2023-01-13 17:00 | 2023-01-13 11:03
MSA-MRWA | WA6400276 | 2 | EQUANS Mechanical Services (WA) Pty Limited | CRAC 2 - Replace leaking water filter holder to CRAC 2 - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 493.25 | Pass | Pass | 0 | 0 | 23.05 | 2023-01-03 10:50 | 2023-01-06 17:00 | 2023-01-03 13:52 | 2023-01-06 17:00 | 2023-01-04 12:55
MSA-DTWD | WA5693205 | 3 | AWB Co. | Level 2 - AMEP back office - one of the lights have stopped working | Electrical | Lighting, Internal | 937.135 | Pass | Fail | 0 | 0 | 23 | 2022-08-04 10:21 | 2022-08-11 17:00 | 2022-08-11 11:45 | 2022-08-11 17:00 | 2022-08-12 10:45 |  |  | Attended site and signed in completed jsa, spoke with fm about job,replaced remaining tubes on list, replaced light in crèche kitchen area with led batten, replace globes on exterior wall lighting, completed paperwork,signed out, job complete
MSA-DTWD | WA5086797 | 3 | CONNECT SECURITY SYSTEMS | B Block - Ground - BG15 -Security Camera needs to be moved & reset | Security | Monitoring | 992.71 | Fail | Fail | 0 | 0 | 23 | 2022-01-21 13:19 | 2022-01-31 17:00 | 2022-02-01 13:00 | 2022-01-31 17:00 | 2022-02-02 12:00 |  |  | Relocated CCTV Camera/PIR
MSA-DTWD | WA5163659 | 1 | Falcetta Plumbing and Gas | Ground floor - A15 Disabled Toilet - The toilet is blocked despite multiple attempts to unblock. | Plumbing & Drainage | Water | 328.49 | Pass | Pass | 0 | 0 | 23 | 2022-02-18 10:54 | 2022-02-21 17:00 | 2022-02-18 13:00 | 2022-02-21 17:00 | 2022-02-19 12:00 |  | WCAPPR | monitor and prepare submersibles
MSA-DTWD | WA5226941 | 1 | Lane's Plumbing | Outside BLD 839 - Burst Water Pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 23 | 2022-03-14 15:44 | 2022-03-15 17:00 | 2022-03-14 16:30 | 2022-03-15 17:00 | 2022-03-15 15:30 |  |  | job completed - REPAIR LEAKING PIPE AT BUILDING 839
MSA-DCA | WA5399202 | 2 | Dormakaba Australia Pty Ltd | Connections L3 auto door is faulty, east side, one side/leaf not closing on command, | Building | Automatic Doors | 780 | Pass | Pass | 0 | 0 | 23 | 2022-05-09 17:58 | 2022-05-12 17:00 | 2022-05-10 10:50 | 2022-05-12 17:00 | 2022-05-11 09:50 |  |  | 10/5/22 - 1045774 Can not work on there door during business require a A/H recall before site open and a 10foot ladder requested by Neil. Standing in front of XIXO no LED could be a power issue and battery could be low.11/5/22 - Attended site with additional tech and 10 ft platform step ladder, inspected door and found cables had came out of pib board, remade connections, checked over door, reset and tested operation.
MSA-DTWD | WA5568104 | 1 | AWB Co. | Faulty lights | Electrical | Lighting, Internal | 338.22 | Pass | Fail | 0 | 0 | 23 | 2022-06-24 15:58 | 2022-06-27 17:00 | 2022-06-27 15:00 | 2022-06-27 17:00 | 2022-06-28 14:00 |  |  | Attended site and signed in. Signed onto jsa. Re located work area. Made sure circuit was isolated. Put up new 4ft led batten. Tested. Working as intended. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5674313 | 1 | Midolo Building Services | Level 1 - Youth Justice - 2 x leaking from ceiling over light fixtures- See notes below | Building | Ceiling | 801.55 | Fail | Fail | 3 | 3 | 23 | 2022-07-21 10:36 | 2022-07-22 17:00 | 2022-08-09 12:00 | 2022-07-22 17:00 | 2022-08-10 11:00 |  | WACCES | Assess and rectify leaks
MSA-DTWD | WA5799853 | 3 | AWB Co. | Cluster of lights out front of library counters | Electrical | Lighting, Internal | 998.13 | Pass | Pass | -1 | -1 | 23 | 2022-08-30 15:07 | 2022-09-06 17:00 | 2022-08-31 11:30 | 2022-09-06 17:00 | 2022-09-01 10:30 |  |  | Job complete
MSA-DTWD | WA6361554 | 1 | Critical Fire Protection & Training | C111 - Diesel Hydrant pump coolant tank empty - see notes | Mechanical Services | Pumps | 477.73 | Pass | Pass | 0 | 0 | 23 | 2022-12-08 10:50 | 2022-12-09 17:00 | 2022-12-08 13:00 | 2022-12-09 17:00 | 2022-12-09 12:00 |  |  | Attended site to repair float valve on diesel pump coolant system .Float valve replaced however this did not fix the coolant issue as the water pump on thediesel motor still does not push water through the cooling line.We recommend either repair or replacement of the coolant pump (if we cannot sourcereplacement parts).Quote to follow.
MSA-MRWA | WA4991936 | 3 | GPS Plumbing & Gas Services PtyLtd | Workshop sink drain pipe leaking | Plumbing & Drainage | Water | 467.78 | Pass | Pass | 0 | 0 | 22.8667 | 2022-01-05 14:13 | 2022-01-12 17:00 | 2022-01-10 15:20 | 2022-01-12 17:00 | 2022-01-11 14:12 |  |  | Replaced leaking chrome waste and replaced rubber washers, ran the tap for 10mins no leaks found
MSA-DTWD | WA5296003 | 1 | Precise Air Group | E-Block E-Vap Restaurant Kitchen continuously dumping water | Air Conditioning | Room Air Conditioners | 552.59 | Pass | Pass | 0 | 0 | 22.7667 | 2022-03-30 08:31 | 2022-03-31 17:00 | 2022-03-30 14:00 | 2022-03-31 17:00 | 2022-03-31 12:46 |  |  | Collected solenoid from supplier. Returned to site and acessed evap on roof. Isolated system and removed old solenoid and installed new. Found to run and operate all ok. Checked over evap drains to confirm no more leaks are present left all ok.
MSA-DTWD | WA5826993 | 1 | Equans Mechanical Services Australia | Our commercial fridge in the TAFE kitchen is not functioning at all’ | Refrigeration | Refrigerators | 422.3025 | Pass | Fail | 0 | 0 | 22.75 | 2022-09-01 07:11 | 2022-09-01 17:00 | 2022-09-01 12:45 | 2022-09-01 17:00 | 2022-09-02 11:30 |  | WACCES | Drove to site , found the two door glass door fridge in the training kitchen was tripping the circuit breaker. Metered out the electrical system and found the problem was with the light and heater circuit , isolated and tested the operation all OK. Need to pick up a terminal strip for the wiring and fit tomorrow. 2/9/22: Repaired terminal strip , test ran all OK. Lights and heaters working fridge down to 4deg c
MSA-DTWD | WA5974552 | 3 | Protek 24/7 Building & Maintenance | Storage Area - Gate cant be locked from outside | Building | Steel Fencing & Gates | 278.91 | Pass | Pass | -1 | -1 | 22.75 | 2022-09-23 13:22 | 2022-10-03 17:00 | 2022-09-27 11:45 | 2022-10-03 17:00 | 2022-09-28 10:30 |  |  | Replace gate lock
MSA-DTWD | WA6159134 | 2 | AWB Co. | 2 Balustrade stainless steel cables missing and 1 has securing nut missing - See notes | Electrical | General Electrical | 577.01 | Pass | Fail | 0 | 0 | 22.75 | 2022-11-10 12:05 | 2022-11-15 17:00 | 2022-11-15 13:30 | 2022-11-15 17:00 | 2022-11-16 12:15 |  | WACCES | Attended site and signed in. Completed jsa. Went to wholesaler to pick up parts. Returned to down galvanised wire to size and fit off onto stairs. Tightened up nuts on either side. Took pics. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6253924 | 1 | Protek 24/7 Building & Maintenance | Ground Floor - Male Public Toilet - Closers need adjusting - See Notes | Building | General Building | 361.72 | Pass | Fail | 0 | 0 | 22.75 | 2022-11-22 13:12 | 2022-11-23 17:00 | 2022-11-23 09:00 | 2022-11-23 17:00 | 2022-11-24 07:45 |  |  | Adjust closer Tested door, door is now closing and locking smoothly
MSA-DCA | WA5572735 | 0 | GPS Plumbing & Gas Services PtyLtd | All Toilets - are blocked and not flushing | Plumbing & Drainage | Toilets/Cisterns | 1387.535 | Pass | Fail | 0 | 0 | 22.6667 | 2022-06-30 10:06 | 2022-06-30 12:06 | 2022-06-30 11:06 | 2022-06-30 14:06 | 2022-07-01 09:46 |  |  | Cleared blocked main drain to building caused by tree roots.Tree roots damaged sewer pipes.New sewer drain to building required asap.
MSA-MRWA | WA6128771 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Bank of lights have tripped the office RCD | Electrical | Lighting, Internal | 455.53 | Pass | Pass | 0 | 0 | 22.6333 | 2022-10-27 08:08 | 2022-10-28 17:00 | 2022-10-27 08:52 | 2022-10-28 17:00 | 2022-10-28 07:30 |  |  | Sebastian Davis (27/10/2022) - Work NoteArrived onsite and signed in.Located faulty circuit and counted lights on circuit for an upgrade. Reset circuit breaker and ensured it stayed on.Informed staff of works and signed out.Will need 600x600 panels lights.All lights already on 413Cameron Vasey (28/10/2022) - Work NoteOnsite 630 replaced and tested rcbo on R2 did not trip while onsite. Replaced light in far kitchenette. There's about 60 ballasts on the circuit which would be causing the fault.
MSA-DTAG | WA6516211 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Judicial Wing - Airconditioning too warm, not cooling properly | Air Conditioning | Ducted Split System | 460.88 | Pass | Pass | 0 | 0 | 22.6167 | 2023-01-23 09:52 | 2023-01-24 17:00 | 2023-01-23 09:53 | 2023-01-24 17:00 | 2023-01-24 08:30
MSA-DTWD | WA6578298 | 2 | Precise Air Group | Repair water leaking from Daikin Air Conditioner | Air Conditioning | Ducted Split System | 810.805 | Pass | Pass | -1 | 0 | 22.5833 | 2023-02-15 08:58 | 2023-02-20 17:00 | 2023-02-16 09:43 | 2023-02-20 17:00 | 2023-02-17 08:18
MSA-DTWD | WA5609095 | 3 | AHS Services WA Pty Ltd (Anchor) | Urinal Button not working A126 | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Fail | Fail | 0 | 0 | 22.5333 | 2022-07-13 13:54 | 2022-07-20 17:00 | 2022-07-21 08:33 | 2022-07-20 17:00 | 2022-07-22 07:05 |  |  | Job completed
MSA-DFES | WA5128300 | 2 | Australian HVAC Services Pty. Ltd. | Ground - External - Refrigeration unit – Evaporator iced up and condenser unit running continually | Refrigeration | Refrigerators | 737.12 | Pass | Pass | 0 | 0 | 22.5 | 2022-02-14 17:00 | 2022-02-17 17:00 | 2022-02-15 14:00 | 2022-02-17 17:00 | 2022-02-16 12:30 |  |  | Works Completed as per service report.Recharged system with refrigerant, all appears to be functioning satisfactory. Phoned client, advised of works carried out, left site, all ok.
MSA-DTWD | WA5175454 | 1 | Equans Mechanical Services Australia | G23.1 Clinic - Water incrementally leaking from split AC, possible condensation pump issue | Air Conditioning | Room Air Conditioners | 604.71 | Pass | Pass | 0 | 0 | 22.5 | 2022-02-21 11:51 | 2022-02-22 17:00 | 2022-02-21 15:00 | 2022-02-22 17:00 | 2022-02-22 13:30 |  |  | Failed condensate pump. Replaced pump
MSA-DTWD | WA5301658 | 3 | AWB Co. | E-Block Restaurant Kitchen the range hood has split from its housing joint | Equipment | Catering Equipment | 419.61 | Pass | Pass | -1 | 0 | 22.5 | 2022-04-01 11:14 | 2022-04-08 17:00 | 2022-04-04 12:30 | 2022-04-08 17:00 | 2022-04-05 11:00 |  | WCAPPR | Attended site and signed in, reviewed JSA, spoke with fm about job, went to range hood and removed timber and clamps , cleaned up stainless steel, re beaded edges , packed up , cleaned up, completed paperwork, signed out , Job completed
MSA-DTAG | WA5687294 | 2 | Midolo Building Services | Court 6 - Ground Level - Door is slamming closed - See notes below | Building | Doors | 887.04 | Pass | Fail | 0 | 0 | 22.5 | 2022-08-01 15:16 | 2022-08-04 17:00 | 2022-08-04 14:00 | 2022-08-04 17:00 | 2022-08-05 12:30 |  | WACCES | new door closer installed. Door repaired
MSA-DFES | WA6293318 | 2 | AWB Co. | ground - Entry door from carpark- Hydraulic door closer is broken | Building | Doors | 355.4925 | Pass | Pass | 0 | 0 | 22.5 | 2022-11-30 07:51 | 2022-12-02 17:00 | 2022-11-30 13:30 | 2022-12-02 17:00 | 2022-12-01 12:00 |  |  | Repair door closerSecured closer box to door
MSA-DTAG | WA6517481 | 1 | Australian HVAC Services Pty. Ltd. | Building extremely warm can we please alter the start time to ensure that the building is cool. | Air Conditioning | Evaporative Coolers | 1179.28 | Pass | Pass | 0 | 0 | 22.5 | 2023-01-24 10:18 | 2023-01-25 17:00 | 2023-01-24 14:00 | 2023-01-25 17:00 | 2023-01-25 12:30
MSA-DTWD | WA6523263 | 3 | GRAFFITI FORCE PTY LTD | Roof - East - Graffiti at height | Cleaning | Graffiti | 843 | Pass | Pass | -1 | -1 | 22.5 | 2023-01-31 13:48 | 2023-02-07 17:00 | 2023-02-02 10:30 | 2023-02-07 17:00 | 2023-02-03 09:00
MSA-DCA | WA5133740 | 1 | Precise Air Group | Plant room - Chiller 1 reoccurring fault, low evac temps | Air Conditioning | Room Air Conditioners | 829.135 | Fail | Fail | 0 | 0 | 22.4167 | 2022-02-15 13:32 | 2022-02-16 17:00 | 2022-02-18 12:51 | 2022-02-16 17:00 | 2022-02-19 11:16 |  |  | Subcontractor attended and rectified
MSA-DCA | WA5151640 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Ground floor - Main Kitchen - Cool room not working | Refrigeration | Coolroom | 2124.4 | Pass | Pass | -1 | -1 | 22.3333 | 2022-02-17 15:10 | 2022-02-24 17:00 | 2022-02-17 15:10 | 2022-02-24 17:00 | 2022-02-18 13:30 |  |  | Attended site. Investigated coolroom in high temp alarm. Found unit tripped on hp. Reset and tested operation. Found condenser fan motor to be faulty causing unit to trip on hp. Replaced with new and tested, unit coming down to temp was at 8°c. Will return tomorrow to check over. Returned to site unit had tripped out on hp. Isolated power and reclaimed refrigerant from system as unable to attach high side gauge as service valve was leaking. Replaced faulty shrader valve and tighten gland on service valve. Flushed system with nitrogen to remove any contaminants. Evacuated system and charged with the reclaimed R507. Restored power and tested operation of unit. Confirmed operation of safety controllers and watched unit cycle off, all ok. Completed paperwork
MSA-DTWD | WA5461863 | 1 | Precise Air Group | Ground Floor & First Floor - All of building - Q-Block chiller in fault and pump in fault | Refrigeration | Chiller | 510.48 | Pass | Pass | 0 | 0 | 22.1667 | 2022-05-19 09:24 | 2022-05-20 17:00 | 2022-05-19 09:30 | 2022-05-20 17:00 | 2022-05-20 07:40 |  |  | Attended site and found that there is an active mismatch fault for Chiller 2 Circulation PumpFound a graphics fault not allowing the user to reset the pump fault, rest the fault via the engineering software andrectified the graphics fault.All appears to now be operating correctly
MSA-DTAG | WA5204751 | 3 | Sapio Pty Ltd | Ground service hallway auto door fault. | Security | Access Control | 790 | Pass | Pass | -1 | -1 | 22.0833 | 2022-03-04 13:03 | 2022-03-14 17:00 | 2022-03-08 17:00 | 2022-03-14 17:00 | 2022-03-09 15:05 |  |  | Ran new cable to auto door and reprogrammed output
MSA-DFES | WA5397272 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - Dorm 8 Bathroom - Toilet seat broken | Plumbing & Drainage | Toilets/Cisterns | 727.91 | Pass | Fail | 0 | 0 | 22.0667 | 2022-05-06 14:26 | 2022-05-11 17:00 | 2022-05-11 12:26 | 2022-05-11 17:00 | 2022-05-12 10:30 |  |  | Had to install a new toilet seat located Drom 8 had get one from Reece
MSA-DTAG | WA6560959 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Custody - Toilets & HWS leaking (see notes) | Plumbing & Drainage | Toilets/Cisterns | 535.125 | Pass | Fail | 0 | 0 | 22.05 | 2023-02-13 15:01 | 2023-02-14 17:00 | 2023-02-14 10:30 | 2023-02-14 17:00 | 2023-02-15 08:33
MSA-DTAG | WA5794229 | 1 | Australian HVAC Services Pty. Ltd. | 1987 Wing-Temperature in Vaughan JA chambers is too warm-see notes | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Pass | 0 | 0 | 22 | 2022-08-24 13:20 | 2022-08-25 17:00 | 2022-08-24 13:30 | 2022-08-25 17:00 | 2022-08-25 11:30 |  |  | 43416Attend site and access lev 4 plantroom. Locate bms computer and reconnect and install in steel cupboard to prevent more damage from dust and to be able to look at the building AC operation.
MSA-DTAG | WA5867236 | 0 | Sapio Pty Ltd | All levels - Comms room - Card read not working | Security | Keys & Access | 324.44 | Pass | Fail | 0 | 0 | 22 | 2022-09-14 09:39 | 2022-09-14 11:39 | 2022-09-14 11:00 | 2022-09-14 13:39 | 2022-09-15 09:00 |  |  | Replaced mortice lock L6 Patch Room, tested for correct operation, all OK.
MSA-DCA | WA5987806 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Loading Bay 7 - Franks Pianos Office - BMS is not functioning properly - See notes | Building | General Building | 896.89 | Fail | Fail | 0 | 0 | 22 | 2022-10-03 10:11 | 2022-10-03 12:11 | 2022-10-03 14:00 | 2022-10-03 14:11 | 2022-10-04 12:00 |  |  | Diagnosed faulty power supply to Schneider i/o controls. Replaced power supply supplied by Schneider inside collections MSSB.
MSA-DTWD | WA5195740 | 2 | Falcetta Plumbing and Gas | Male toilet - Cistern leaking | Plumbing & Drainage | Toilets/Cisterns | 923.39 | Pass | Pass | 0 | 0 | 22 | 2022-02-28 15:12 | 2022-03-03 17:00 | 2022-03-02 14:30 | 2022-03-03 17:00 | 2022-03-03 12:30 |  |  | replaced in duct cistern with invisi dual flush
MSA-DTAG | WA5699704 | 0 | Seme Solutions Pty Ltd | Swipe Card Access and Gate Entry not working due to water damage (Rain) - see notes | Security | Security Management System | 489.58 | Pass | Fail | 0 | 0 | 21.7833 | 2022-08-10 11:25 | 2022-08-10 13:25 | 2022-08-10 12:30 | 2022-08-10 15:25 | 2022-08-11 10:17 |  |  | Tested card reader changing output state correctly, found output triggering dry contact feed to gate motor correctly. Found gate motor relay stuck in latched position. Removed and replaced seized relay. Tested gate fully operational .
MSA-DFES | WA5133869 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Engine Room - Leaking sink tap in engine room | Plumbing & Drainage | Materials | 470.96 | Pass | Fail | 0 | 0 | 21.75 | 2022-02-15 15:50 | 2022-02-22 17:00 | 2022-02-22 14:30 | 2022-02-22 17:00 | 2022-02-23 12:15 |  |  | Re-attended site to follow up on low water pressure after replacing wall tops in engine room I have found three fixtures all located around the engine room to have low water pressure every other featurein the station is working correctly I have turned off and isolated both hot water units one located outside the kitchen and one located near the gym after I have checked to see the water pressure andfound water pressure is returned as normal there are no signs of leaks anywhere on the Lines after turning the hot water units back on The water pressure has remained cleaned up packed up
MSA-DTWD | WA6108806 | 0 | AWB Co. | near Reception - Electrical box - distribution fault, burning smell coming from area | Electrical | Distribution Board | 1009.18 | Pass | Fail | 0 | 0 | 21.75 | 2022-10-20 11:30 | 2022-10-20 13:30 | 2022-10-20 12:15 | 2022-10-20 15:30 | 2022-10-21 10:00 |  | WCAPPR | As per report attached
MSA-DTWD | WA6407625 | 1 | Equans Mechanical Services Australia | No water running through evap cooler on the south west corner. | Air Conditioning | Evaporative Coolers | 589.4075 | Pass | Pass | 0 | 0 | 21.75 | 2023-01-10 10:15 | 2023-01-11 17:00 | 2023-01-10 12:15 | 2023-01-11 17:00 | 2023-01-11 10:00 |  | WACCES
MSA-DCA | WA5714983 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 1 - 1st Floor Female Toilets - Sink taps faulty - See notes below | Plumbing & Drainage | Water | 648.8425 | Pass | Pass | 0 | 0 | 21.6833 | 2022-08-12 09:57 | 2022-08-19 17:00 | 2022-08-16 11:50 | 2022-08-19 17:00 | 2022-08-17 09:31 |  |  | Inspected the job and got all materials required but l have to return tomorrow early morning as the site would not allow the water to be turned off for repairs to occur
MSA-DCA | WA5298169 | 1 | ADVANCED LOCK & KEY | Lower Basement Level - Fire Pump room - Broken door lock carpark entry to Fire Pump Room | Security | Locksmith | 252.5 | Pass | Pass | 0 | 0 | 21.6667 | 2022-03-31 15:33 | 2022-04-01 17:00 | 2022-03-31 16:10 | 2022-04-01 17:00 | 2022-04-01 13:50 |  |  | Replace L003 Fire Cylinder to basement fire pump
MSA-MRWA | WA5010319 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Dry cooler in fault | Equipment | Compressors, Generators | 502.325 | Pass | Pass | 0 | 0 | 21.5 | 2022-01-12 12:25 | 2022-01-13 17:00 | 2022-01-12 12:30 | 2022-01-13 17:00 | 2022-01-13 10:00 |  |  | Travelled to site and signed in. Located air dry and sir compressor compound. Found air dry switched off. Turned on and alarm was sounding. Checked the air lines and found excessive water throughout the system. Bled water from lines and filters. Checked over condenser and found condenser fan to be faulty and jammed up causing it to trip on high pressure. Got verbal gonahead to carry out repairs. Parts will be sourced tomorrow and fitted. Braf will be submitted. Travelled to supplier to pick up parts. Travelled to site and signed in. Located Air dryer compound and isolated unit and removed old faulty seized condenser fan and installed new fan. Bled water from system and test ran unit all ok.
MSA-DTWD | WA5201208 | 2 | Falcetta Plumbing and Gas | Urinal blocked will not drain away | Plumbing & Drainage | Drainage | 779.06 | Pass | Pass | -1 | -1 | 21.5 | 2022-03-02 12:39 | 2022-03-08 17:00 | 2022-03-03 17:00 | 2022-03-08 17:00 | 2022-03-04 14:30 |  |  | unblocked 1 urinal, replaced service kits and caps to 2 urinals
MSA-DTAG | WA5392206 | 3 | Midolo Building Services | Loose paver out on the top step at the front of the courthouse. | Paving & Roadworks | Paving | 405.71 | Pass | Pass | -1 | -1 | 21.5 | 2022-05-03 08:32 | 2022-05-10 17:00 | 2022-05-05 09:00 | 2022-05-10 17:00 | 2022-05-06 06:30 |  |  | Pavers re secured & some replaced
MSA-DCA | WA5393979 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Centenrary Galleries - humidifuer alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 293.025 | Pass | Fail | 0 | 0 | 21.5 | 2022-05-04 11:45 | 2022-05-04 13:45 | 2022-05-04 13:30 | 2022-05-04 15:45 | 2022-05-05 11:00 |  |  | Attended site, signed in and accessed Centenary building roof space. Located FCU 8 and checked humidifier operation, found various faults present. Isolated the humidifier, draindowned and carried out a full clean and reset maintenance hours.Reinstated power, checked, tested and recorded amp draws and general operation - unit running as per normal.
MSA-DCA | WA6301051 | 1 | Protek 24/7 Building & Maintenance | PICA Bar - Ramp outside front of building - Water is leaking between wall and paving | Building | External Walls | 652.96 | Pass | Fail | 0 | 0 | 21.5 | 2022-12-02 13:02 | 2022-12-05 17:00 | 2022-12-05 11:30 | 2022-12-05 17:00 | 2022-12-06 09:00 |  | WACCES | Repaired Leaking Pipe Below Pavers
MSA-DTWD | WA6522350 | 2 | AWB Co. | Lights in operative in classroom | Electrical | Lighting, Internal | 1243.4 | Pass | Pass | 0 | 0 | 21.5 | 2023-01-31 07:19 | 2023-02-02 17:00 | 2023-01-31 13:30 | 2023-02-02 17:00 | 2023-02-01 11:00 |  | WACCES
MSA-DTWD | WA5879930 | 2 | AHS Services WA Pty Ltd (Anchor) | Urinal running constantly | Plumbing & Drainage | Toilets/Cisterns | 898.6125 | Pass | Pass | 0 | 0 | 21.4167 | 2022-09-15 10:15 | 2022-09-20 17:00 | 2022-09-19 12:35 | 2022-09-20 17:00 | 2022-09-20 10:00 |  |  | Replaced urinal system because Old system was leaking Andy unavailable
MSA-DTWD | WA5994837 | 1 | Precise Air Group | Exhaust fan is not working | Air Conditioning | Room Air Conditioners | 602.49 | Pass | Pass | 0 | 0 | 21.4 | 2022-10-06 09:04 | 2022-10-07 17:00 | 2022-10-06 12:30 | 2022-10-07 17:00 | 2022-10-07 09:54 |  | WACCES | Attended Joondalup Campus with Alex to investigate why 2 exhaust fan systems are not operational. I have arrived on site and signed in and they checked out the 2 exhaust fans (kitchen 1 and 2). I have switched both fans on and they have come on with no problems. I have spoke to one of the staff from the facilitys office and he has notified me that this wasn't working but is intermittent. I have checked out the Switchboard and had a Look that the timers are working, checked the terminals are all tight, I have checked the controllers are working In all 3 modes, checked contactors are operational and just checked all the mechanical side of the fans, I have also taken off switched to ensure there is no loose connections. All seems to be fine and there is no faults. Had the units running for the duration of being on site and switched on and off a few times. There are no issues .Programmed has notified us that this is working back to normal after I had adjusted the timer. Work had been co
MSA-DCA | WA5312077 | 1 | Earth & Water Pty Ltd | James Street Amphitheatre - Zone 13, broken sprinklers. Reset sprinkler times to 5am-6am | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 21.35 | 2022-04-11 10:56 | 2022-04-12 17:00 | 2022-04-11 15:03 | 2022-04-12 17:00 | 2022-04-12 12:24 |  |  | Suspend watering from Zone 13Have the broken sprinkler repairedReset the watering time to around 5.00am - 6.00am - In this way it may avoid further vandalising.Replaced damaged sprinkler on zone 13.Condition Of Asset After:Sprinklers on zone 13 now fully operation again.
MSA-DTWD | WA5673371 | 1 | SCAVENGER SUPPLIES PTY LTD | Main Entrance - Fire Hydrant Leaking | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 99.37 | Pass | Pass | 0 | 0 | 21.35 | 2022-07-20 14:30 | 2022-07-21 17:00 | 2022-07-20 16:00 | 2022-07-21 17:00 | 2022-07-21 13:21 |  |  | RCT- P1 WA5673371 DTWD SMT Thornlie Campus Thornlie Campus-Block 1Main Entrance - Fire Hydrant LeakingAttended site 1600 20/7Found hydrant leaking with a build up of water after taking the bic cap off. Found that the handle was a little loose so I have tightened it and the leak has seemed to have stopped. Dom will monitor tomorrow morning and advise if it's still leaking or not. Left site at 1630 20/71300 21/7 received a call from Dom to advise that the hydrant is no longer leaking and that tightening the hydrant has stopped the leak. This job can now be closed.
MSA-DFES | WA6650994 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Reception - Sewage pump - Gone in alarm | Plumbing & Drainage | Sewage Treatment Plant | 1237.12 | Pass | Fail | 0 | 0 | 21.2833 | 2023-02-20 15:50 | 2023-02-21 17:00 | 2023-02-21 10:27 | 2023-02-21 17:00 | 2023-02-22 07:44 |  | WACCES
MSA-DCA | WA5686835 | 0 | Protek 24/7 Building & Maintenance | First Floor - Roof Level - Beaufort Street - Roof Leak | Roofing | Metal Roofing | 562.125 | Pass | Fail | 0 | 0 | 21.25 | 2022-08-01 11:11 | 2022-08-01 13:11 | 2022-08-01 11:45 | 2022-08-01 15:11 | 2022-08-02 09:00 |  |  | Works to be completed as a LVM
MSA-DFES | WA6560117 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Hot water system failed | Plumbing & Drainage | HWS/Units Electric & Gas | 375.0625 | Pass | Fail | 0 | 0 | 21.25 | 2023-02-13 07:58 | 2023-02-13 17:00 | 2023-02-13 13:30 | 2023-02-13 17:00 | 2023-02-14 10:45 |  | WACCES
MSA-DTWD | WA6688970 | 2 | AWB Co. | Repair or replace data point | Electrical | General Electrical | 930.58 | Pass | Pass | -1 | -1 | 21.25 | 2023-03-08 08:14 | 2023-03-13 17:00 | 2023-03-08 14:00 | 2023-03-13 17:00 | 2023-03-09 11:15
MSA-DTWD | WA5452957 | 1 | Equans Mechanical Services Australia | EG19 Kitchen - Polar freezer is running at 1 to 0 Deg and not cooling | Refrigeration | Freezers | 245.93 | Pass | Fail | 0 | 0 | 21.25 | 2022-05-17 09:28 | 2022-05-18 17:00 | 2022-05-18 12:15 | 2022-05-18 17:00 | 2022-05-19 09:30 |  |  | Arrived on site signed in, checked in with Sharyn. Gathered tools and equipment started checks on controls and operation all ok. No fault found unit at temperature. Possible door open overnight. Reported findings cleaned up and completed paperwork.
MSA-DCA | WA5001194 | 3 | GPS Plumbing & Gas Services PtyLtd | 2nd Floor - HBRC Plant Room/Boiler Room - Pipe line for non potable water faulty | Air Conditioning | Room Air Conditioners | 640.555 | Pass | Pass | -1 | -1 | 21.1667 | 2022-01-11 09:57 | 2022-01-18 17:00 | 2022-01-12 13:50 | 2022-01-18 17:00 | 2022-01-13 11:00 |  |  | Repaired leaking 25mm pipe to hot water unit in plant room
MSA-DCA | WA5692633 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main Building-Chilled water plant temperature alarm | Air Conditioning | Cooling Tower | 1437.89 | Pass | Fail | 0 | 0 | 21.15 | 2022-08-03 18:51 | 2022-08-03 20:51 | 2022-08-03 18:51 | 2022-08-03 22:51 | 2022-08-04 16:00 |  |  | Attended site (03/08) as bms was showing high temps and sending alarms. Job raised. Investigated chilled water plant. Found agwa running ets but no flow coming to the building. Checked valves around the gallery, all showing open. Switched plant to local and confirmed operation. Will need to return tomorrow and investigate valves at the library and confirm operation. (04/08) Returned to site. Checked over plant and drawings. Located plantroom in lower floor carpark. Sourced keys from security and accessed plantroom. Found actuator sticking on main iso valve. Released and switched plant back to ets. Agwa operating off ets. Honeywell to quote replacement actuator.
MSA-DTWD | WA5392161 | 1 | AHS Services WA Pty Ltd (Anchor) | 3.21 - Shower - no hotwater and replacement shower head is required | Plumbing & Drainage | HWS/Units Electric & Gas | 1501.8475 | Pass | Pass | 0 | 0 | 21.05 | 2022-05-03 08:11 | 2022-05-04 17:00 | 2022-05-03 12:30 | 2022-05-04 17:00 | 2022-05-04 09:33 |  |  | Carried out repairs to shower including supply and install new shower head and service taps. Hot water system failed, 50L electric Rhee unit replaced as required. Electrician Disconnect and reconnect also part of the scope.
MSA-DTWD | WA5105312 | 2 | Falcetta Plumbing and Gas | Level 2 - Student Male toilets - Urinal blocked | Plumbing & Drainage | Water | 640.7 | Pass | Pass | 0 | 0 | 21 | 2022-02-04 09:18 | 2022-02-09 17:00 | 2022-02-07 17:00 | 2022-02-09 17:00 | 2022-02-08 14:00 |  | WCAPPR | Unblocked urinal, scoured hard buildup
MSA-DTWD | WA5175483 | 1 | BJ SYSTEMS | Admin/ Workshops entrances -Workshops alarm code not responding with Ed Sec | Security | Monitoring | 278.75 | Pass | Pass | 0 | 0 | 21 | 2022-02-21 12:03 | 2022-02-22 17:00 | 2022-02-21 13:45 | 2022-02-22 17:00 | 2022-02-22 10:45 |  |  | 21/02/2022 - Code issues, David has asked me to leave as did not go to Kendrick22/02/2022 - Added 2x missing pins for Facilities and Cleaners, for Clarkson. Security pin appears ok. Clarkson offline, pins not downloaded to site yet. Attend Clarkson, network outage being addressed by Telstra and Tafe. Cannot make further checks, pins will be auto added once comms restored anyway
MSA-DTWD | WA5677334 | 2 | AHS Services WA Pty Ltd (Anchor) | All Levels - A Block - Computer Area - Repair water leak from toilet blocks on all levels | Plumbing & Drainage | Toilets/Cisterns | 1861.88 | Pass | Pass | 0 | 0 | 21 | 2022-07-25 14:02 | 2022-07-28 17:00 | 2022-07-27 11:00 | 2022-07-28 17:00 | 2022-07-28 08:00 |  |  | Replaced multiple leaking fixtures
MSA-DTWD | WA5831869 | 2 | AHS Services WA Pty Ltd (Anchor) | A25A Male toilet - Both hand basins have low water flow - 2nd hand basin also spins around | Plumbing & Drainage | Water | 775.3825 | Pass | Pass | 0 | 0 | 21 | 2022-09-05 09:10 | 2022-09-08 17:00 | 2022-09-06 15:00 | 2022-09-08 17:00 | 2022-09-07 12:00 |  |  | .
MSA-DTWD | WA6255770 | 1 | COMMERCIAL PLUMBING AND GAS | U Block - male accessible toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 269.015 | Pass | Pass | 0 | 0 | 21 | 2022-11-23 13:31 | 2022-11-24 17:00 | 2022-11-23 18:00 | 2022-11-24 17:00 | 2022-11-24 15:00 |  |  | Unblocked toilet
MSA-DCA | WA6405519 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Harry Butler Centre - Chillers and lab temperatures very high - Please check | Air Conditioning | Building HVAC Maintenance (Major Plant) | 281.53 | Pass | Fail | 0 | 0 | 21 | 2023-01-09 14:59 | 2023-01-09 16:59 | 2023-01-09 15:00 | 2023-01-09 18:59 | 2023-01-10 12:00
MSA-DTWD | WA6539047 | 1 | AWB Co. | Disabled toilet - No Lights | Electrical | Lighting, Internal | 1001.12 | Pass | Pass | 0 | 0 | 21 | 2023-02-08 10:03 | 2023-02-09 17:00 | 2023-02-08 12:00 | 2023-02-09 17:00 | 2023-02-09 09:00
MSA-DFES | WA6690374 | 1 | Australian HVAC Services Pty. Ltd. | aircon in BA compressor room house has failed | Air Conditioning | Ducted Split System | 541.45 | Pass | Pass | 0 | 0 | 21 | 2023-03-09 09:14 | 2023-03-10 17:00 | 2023-03-09 12:00 | 2023-03-10 17:00 | 2023-03-10 09:00
MSA-DTAG | WA5454480 | 1 | Sapio Pty Ltd | Level 1 - President Buss Chambers - Issues with duress alarms - See notes below | Security | Keys & Access | 232.77 | Pass | Pass | 0 | 0 | 20.9167 | 2022-05-17 11:43 | 2022-05-18 17:00 | 2022-05-17 11:45 | 2022-05-18 17:00 | 2022-05-18 08:40 |  |  | Replaced judges duress
MSA-DTWD | WA6526793 | 3 | AWB Co. | C700 - All the edge lights are mismatched or not working around elevators and hallway | Electrical | Lighting, External | 813.86 | Pass | Pass | -1 | -1 | 20.75 | 2023-02-01 10:50 | 2023-02-08 17:00 | 2023-02-02 13:15 | 2023-02-08 17:00 | 2023-02-03 10:00
MSA-DTAG | WA6383855 | 2 | Midolo Building Services | Outdoor Ground - Outdoor flag pole - Flag unable to be put up as link on the string is broken | Recreation | General | 409.76 | Fail | Fail | 3 | 3 | 20.75 | 2022-12-20 14:18 | 2022-12-23 17:00 | 2023-01-10 13:30 | 2022-12-23 17:00 | 2023-01-11 10:15 |  | WACCES | replace cable and clamps
MSA-DTAG | WA5101857 | 2 | Sapio Pty Ltd | Duress button did not lock tenancy doors to L23 – Staff were still able to enter the floor | Security | Monitoring | 490 | Pass | Pass | -1 | -1 | 20.5 | 2022-02-03 15:48 | 2022-02-08 17:00 | 2022-02-03 17:00 | 2022-02-08 17:00 | 2022-02-04 13:30 |  | WACCES | Work performed by Michael Tomlinson 03/02/2022 & 04/02/2022:Reconfigured duress and checked over new door lock modes when duress is activated. Doors now won't allow readers during alarm activation as requested. All working okay and tested with Tammy at reception.Tested and checked current operation. Returned and set up new lobby lockdown as per Corbin's request. All working & tested OK.
MSA-DTWD | WA5305336 | 2 | BAKE-QUIP PTY LTD | E Block - Ground - E58 LSK Kitchen - Combi Oven not working on steam function | Equipment | Catering Equipment | 375 | Pass | Pass | 0 | 0 | 20.5 | 2022-04-05 14:21 | 2022-04-08 17:00 | 2022-04-06 11:15 | 2022-04-08 17:00 | 2022-04-07 07:45 |  |  | No fault found.
MSA-DCA | WA5762064 | 0 | EQUANS Mechanical Services (WA) Pty Limited | level 4 plant room - gas smell in plant room | Air Conditioning | Room Air Conditioners | 371.62 | Pass | Fail | 0 | 0 | 20.5 | 2022-08-18 12:25 | 2022-08-18 14:25 | 2022-08-18 12:30 | 2022-08-18 16:25 | 2022-08-19 09:00 |  |  | Attended site, signed in and accessed the boiler plantroom. Found a strong gas smell comming from around the hot water Boilers. Was unable to find the exact location of the leak. Manualled the hot water system to ETS. Isolated both Boilers and tagged out. Engaged Boilertronics to investigate the leak. Boilertronics have confirmed the leaks are coming from the rear door tape seals.
MSA-DCA | WA6154647 | 3 | Protek 24/7 Building & Maintenance | Ground Floor External - Courtyard to west of SLWA - Decking in some areas loose and missing | Building | General Building | 687.04 | Pass | Pass | -1 | -1 | 20.5 | 2022-11-07 14:49 | 2022-11-14 17:00 | 2022-11-08 11:30 | 2022-11-14 17:00 | 2022-11-09 08:00 |  |  | Replaced damaged board Replaced loose screws
MSA-DTWD | WA5655755 | 1 | Precise Air Group | Fumehood 7 A314 has stopped working | Electrical | General Electrical | 423.86 | Pass | Pass | 0 | 0 | 20.4167 | 2022-07-18 10:18 | 2022-07-19 17:00 | 2022-07-18 14:05 | 2022-07-19 17:00 | 2022-07-19 10:30 |  |  | Travelled to site, found fume cupboard being held out by BMS, reset cupboard, spoke with site contact regarding issue. Job to be raised to BMS contractor
MSA-DCA | WA5324348 | 0 | Dormakaba Australia Pty Ltd | Roller door stuck midway open | Building | Automatic Doors | 640 | Pass | Fail | 0 | 0 | 20.3833 | 2022-04-13 14:14 | 2022-04-13 16:14 | 2022-04-13 15:05 | 2022-04-13 18:14 | 2022-04-14 11:28 |  |  | 13/4/22 - Assessed door and found slats have been caught on top of guides causing door to come out of guides, haul chain assembly has been broken and requires replacement, 2 Dormakaba technicians to revisit with large scissor lift with outriggers to fix and further assess door due to slope of ground and height of door14/4/22 - Got door back into guides but there is too much damage to the curtain as well as the motor. Please quote to replace. Height 4700 width. 5040 daylight. Right handed 3 phase inboard kit. Ps the buttons on the 21D2 switch are all worn out. Please quote to replace as well. Safety beams. Seam ok to leave on. Color is faded but looks like monument Matt.
MSA-MRWA | WA6721680 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Failed air con unit in workshop or mmatroligy | Air Conditioning | Ducted Split System |  | Pass | Pass | 0 | 0 | 20.35 | 2023-03-14 10:50 | 2023-03-15 17:00 | 2023-03-14 13:39 | 2023-03-15 17:00 | 2023-03-15 10:00
MSA-DFES | WA5566885 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room west side front - Engine room light next to new vent not working | Electrical | Lighting, Internal | 124.95 | Pass | Pass | 0 | 0 | 20.25 | 2022-06-23 12:23 | 2022-06-24 17:00 | 2022-06-23 13:30 | 2022-06-24 17:00 | 2022-06-24 09:45 |  | WCAPPR | Arrived on site at 0915 to investigate Engine room west side front - Engine room light next to new vent not working. Discovered led panel unplugged. Reconnected light, informed staff and left site at 0945
MSA-DTAG | WA6157390 | 0 | Sapio Pty Ltd | Graffix sytstem is showing a fire trip in level 1 - and cant clear | Fire Protection Services | Fire Protection - Fire Brigade | 710.16 | Pass | Fail | 0 | 0 | 20.25 | 2022-11-09 16:59 | 2022-11-09 18:59 | 2022-11-09 18:15 | 2022-11-09 20:59 | 2022-11-10 14:30 |  |  | attended site and found alarm has restored, simulated fire trip on security side and confirmed correct operation
MSA-DFES | WA6393966 | 1 | Critical Fire Protection & Training | ground floor fire panel-battery fault in fire panel | Fire Protection Services | Fire Protection - Monitor System | 595.405 | Pass | Pass | 0 | 0 | 20.25 | 2022-12-29 13:41 | 2022-12-30 17:00 | 2022-12-29 15:45 | 2022-12-30 17:00 | 2022-12-30 12:00 |  | WACCES | Battery fail on FIPChecked PSU diagnostics / mains checks/ clearedBatts appear not dated could not see stickerFault cleared , monitor for now as new batteries mayberequired.Advised security.
MSA-DTWD | WA6523427 | 3 | Protek 24/7 Building & Maintenance | Uneven brick paving at side entrance to building | Paving & Roadworks | Paving | 355.6 | Pass | Pass | -1 | -1 | 20.25 | 2023-01-31 15:52 | 2023-02-07 17:00 | 2023-02-02 12:15 | 2023-02-07 17:00 | 2023-02-03 08:30
MSA-DFES | WA5304079 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | 1st floor - SOC Kitchen - kitchen sink leaking | Plumbing & Drainage | Drainage | 476.13 | Pass | Fail | 0 | 0 | 20.2167 | 2022-04-04 14:28 | 2022-04-07 17:00 | 2022-04-07 15:51 | 2022-04-07 17:00 | 2022-04-08 12:04 |  | WACCES | Replaced sink mixer tap
MSA-DFES | WA6504365 | 2 | Dom's Total Grounds Maintenance | retic controller is faulty | Landscaping & Gardening | Grounds Maintenance | 620 | Fail | Fail | 1 | 1 | 20.1667 | 2023-01-19 15:11 | 2023-01-24 17:00 | 2023-01-31 13:45 | 2023-01-24 17:00 | 2023-02-01 09:55
MSA-DTAG | WA5481560 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - Plant room - Fault description Both water pumps have earth faults in cables | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1705.99 | Pass | Pass | -1 | -1 | 20.0667 | 2022-05-30 14:26 | 2022-06-07 17:00 | 2022-05-30 14:26 | 2022-06-07 17:00 | 2022-05-31 10:30 |  |  | Attend site with electrician and isolate heating water pumps. Isolate main board. Disconnect mains wiring to fuses and remove fuses from board. Install din rail in board and fit circuit breakers. Drill holes through board to run new wire up and out to ceiling. Pick up existing cable tray and run wiring accross beams. Secure new wiring. Connect new wiring to existing pump isolators. Remove old wiring conduit and junction bow floor wiring penatration. Connect new wiring to circuit breakers and deisolate power supply. Test operation of pumps and found both to run with no earth faults. Pumps now working as normal. Will monitor over a few days.
MSA-DTWD | WA6528193 | 1 | Precise Air Group | aircon not working | Air Conditioning | Room Air Conditioners | 253.38 | Pass | Pass | 0 | 0 | 20.0167 | 2023-02-02 09:26 | 2023-02-03 17:00 | 2023-02-02 12:22 | 2023-02-03 17:00 | 2023-02-03 08:23 |  | WACCES
MSA-DCA | WA5565102 | 0 | Critical Fire Protection & Training | M Block - Fire hydrant leaking | Fire Protection Services | Fire Protection - Monitor System | 723.3 | Pass | Fail | 0 | 0 | 20 | 2022-06-21 13:41 | 2022-06-21 15:41 | 2022-06-21 14:00 | 2022-06-21 17:41 | 2022-06-22 10:00 |  |  | Attended site to investigate/repair leaking pipework in M block.After locating the pipe we could not fix on the evening of 21/6/22 as wedid not have a large enough ladder to get to the access hatch.Isolated and drained Fire system to stop the leak informed securitymonitoring and Critical Fire that the pumps where shut off for the night.Returned to site 22/6/22 with 12 foot ladder and repaired pipework.Restored fire service and informed security monitoring.All okay on departure. No one on site to sign paperwork at time ofdeparture.
MSA-DTWD | WA5869378 | 1 | Techworks Plumbing | A011/A/012 Male/Female toilets are blocked | Plumbing & Drainage | Toilets/Cisterns | 1991.54 | Pass | Pass | 0 | 0 | 20 | 2022-09-14 13:28 | 2022-09-15 17:00 | 2022-09-14 14:00 | 2022-09-15 17:00 | 2022-09-15 10:00 |  |  | Found I.O and sent the drain machine down until blockage cleared. Used the camera to check any faults in drain, which we found the section near the septics may be back falling as we spotted water in the line but no obstruction.
MSA-DFES | WA5093723 | 0 | Australian HVAC Services Pty. Ltd. | Metro operations first floor - air con isnt working. | Air Conditioning | Cooling Tower | 645.5 | Pass | Fail | 0 | 0 | 20 | 2022-01-30 13:01 | 2022-01-30 15:01 | 2022-01-30 13:30 | 2022-01-30 17:01 | 2022-01-31 09:30 |  |  | Received callout and travelled to site. Signed in and accessed MOC. Spoke to staff who reported aircon not running. Checked and found pac units running but main system off. Found after hours button not working. Accessed bms and found 4 controllers were offline. Accessed controllers and reset. Once controllers communication was restored I set the time schedule to run through to Monday. Found all plant activated and began cooling. Monitored operation and found building temps slowly dropping. Will follow up on Monday.
MSA-DFES | WA6517979 | 0 | Critical Fire Protection & Training | Hydrant is completely failed from joinery - Massive leak - Water has been turned - 100ml pipe | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 936.28 | Pass | Fail | 0 | 0 | 20 | 2023-01-24 15:05 | 2023-01-24 17:05 | 2023-01-24 16:00 | 2023-01-24 19:05 | 2023-01-25 12:00
MSA-DTWD | WA5116182 | 2 | AWB Co. | Block 3 - Ground - Metal Fabrication 1 workshop - 3 phase power point in welding bay 6 has no power | Electrical | General Electrical | 392.26 | Pass | Fail | 0 | 0 | 19.75 | 2022-02-11 11:29 | 2022-02-16 17:00 | 2022-02-16 15:30 | 2022-02-16 17:00 | 2022-02-17 11:15 |  | WACCES | Attended site and signed in. Completed JSA. Located booth 6 in block 3. Isolated power to outlet. Supply and replace faulty RCD in outlet. Reinstated power. Tested all okay. Signed out. Job complete
MSA-DCA | WA6178905 | 1 | Protek 24/7 Building & Maintenance | Roe Street (Lower Ground) level - external-damaged fence-see notes | Building | Steel Fencing & Gates | 249.86 | Pass | Fail | 0 | 0 | 19.75 | 2022-11-14 14:40 | 2022-11-15 17:00 | 2022-11-15 12:00 | 2022-11-15 17:00 | 2022-11-16 07:45 |  | WACCES | * Temporary re strap of joining wire *Installation of HD Cable ties to refit mesh to frame as a temporary make good solution Re laced a chainmesh gate to storage area near six pack car park
MSA-DTWD | WA6688982 | 2 | AWB Co. | 13G1 Demountable- Lights not working - T5 type tubes | Electrical | Lighting, Internal | 655.2975 | Pass | Pass | -1 | 0 | 19.75 | 2023-03-08 08:23 | 2023-03-13 17:00 | 2023-03-09 13:15 | 2023-03-13 17:00 | 2023-03-10 09:00
MSA-DTWD | WA5226866 | 1 | BAKE-QUIP PTY LTD | Kendrew- E-Block SK3 Mini prover on left of kitchen( tagged out ) also tripping power circuit | Equipment | Catering Equipment | 519.8 | Pass | Fail | 0 | 0 | 19.75 | 2022-03-14 14:06 | 2022-03-15 17:00 | 2022-03-15 13:00 | 2022-03-15 17:00 | 2022-03-16 08:45 |  | WACCES | Refer to service report
MSA-DTWD | WA5305888 | 2 | AWB Co. | Project store - u022.6 - emergency stop button broken | Electrical | General Electrical | 828.76 | Pass | Pass | -1 | 0 | 19.75 | 2022-04-06 08:30 | 2022-04-11 17:00 | 2022-04-07 12:15 | 2022-04-11 17:00 | 2022-04-08 08:00 |  |  | Attended site and signed in. Signed onto jsa. Re located stop start DOL that we installed yesterday. Saddled conduit to framework. Tested saw to see if it was working as intended. Everything working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA6693704 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet leaking at base | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 19.7333 | 2023-03-10 13:29 | 2023-03-15 17:00 | 2023-03-13 14:45 | 2023-03-15 17:00 | 2023-03-14 10:29
MSA-DTAG | WA5735001 | 1 | Seme Solutions Pty Ltd | Rockingham Justice Complex Security Gate swipe card not working | Security | Access Control | 317.49 | Fail | Fail | 0 | 0 | 19.6 | 2022-08-16 10:54 | 2022-08-17 17:00 | 2022-08-19 13:15 | 2022-08-17 17:00 | 2022-08-20 08:51 |  | WACCES | 16/08/2022 Travel 1120 to 1200 Onsite from 1200 to 1430 had a lunch break from 1300 to 1330 After investigating the issue and checking the card reader and programming I found a faulty relay in the cabinet near the gate motor
MSA-DFES | WA5092231 | 0 | Australian HVAC Services Pty. Ltd. | Lounge - burst water pipe from AC unit internal of roof. | Air Conditioning | Ducted Split System | 666.81 | Pass | Fail | 0 | 0 | 19.5 | 2022-01-27 20:00 | 2022-01-27 22:00 | 2022-01-27 21:00 | 2022-01-28 | 2022-01-28 16:30 |  |  | Attended Service call. Discovered that AC condensate drain is blocked. Unable to access the Condensate drain. Returned the next day to install manhole to grant access to drain. Unblock drain and found that it seems to be operating correctly.
MSA-DFES | WA5099001 | 1 | Dom's Total Grounds Maintenance | External - side fence - tree has fallen and needs to be removed | Landscaping & Gardening | General Tree Works | 622.5 | Pass | Pass | 0 | 0 | 19.5 | 2022-02-01 12:38 | 2022-02-02 17:00 | 2022-02-01 16:35 | 2022-02-02 17:00 | 2022-02-02 12:05 |  |  | Tree Loppers to remove fallen branches
MSA-DTAG | WA5399207 | 3 | Midolo Building Services | L3, 4 Waiting chairs are loose – need to be tightened | Furniture | Commercial Furniture | 277.42 | Pass | Pass | -1 | -1 | 19.5 | 2022-05-09 18:17 | 2022-05-16 17:00 | 2022-05-11 14:00 | 2022-05-16 17:00 | 2022-05-12 09:30 |  | WACCES | BROKEN CHAIRS REPLACED ALL SCREWS AND BOLTS TIGHTENED
MSA-DCA | WA5462470 | 1 | Building Automation & Electrical Services Pty Ltd | Issues with BMS controls, auditorium too hot | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 19.5 | 2022-05-19 15:19 | 2022-05-20 17:00 | 2022-05-19 15:30 | 2022-05-20 17:00 | 2022-05-20 11:00 |  |  | Repairs to BMS
MSA-DTWD | WA5511818 | 1 | Equans Mechanical Services Australia | Upright Freezer running warm. | Refrigeration | Freezers | 553.63 | Pass | Pass | 0 | 0 | 19.5 | 2022-06-13 09:31 | 2022-06-14 17:00 | 2022-06-13 13:30 | 2022-06-14 17:00 | 2022-06-14 09:00 |  |  | .
MSA-DFES | WA5693240 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Kitchen - water leaking from the rangehood | Electrical | General Electrical | 287.415 | Pass | Pass | 0 | 0 | 19.5 | 2022-08-04 10:39 | 2022-08-05 17:00 | 2022-08-04 13:30 | 2022-08-05 17:00 | 2022-08-05 09:00 |  |  | Arrived on site at 0700 to investigate Kitchen - water leaking from the rangehood. Dismantled rangehood casing containingterminations which were not exposed to water. Discovered very minimal amount of water which has passed throughventilation duct from extractor on roof. Could no locate signs of water damage in ceiling space. Informed staff and left site at0900.
MSA-DTWD | WA5696594 | 3 | Equans Mechanical Services Australia | Toilet Exhaust Fan N14 fault | Equipment | Electrical Equipment | 382.135 | Pass | Pass | -1 | -1 | 19.5 | 2022-08-08 12:49 | 2022-08-15 17:00 | 2022-08-10 15:00 | 2022-08-15 17:00 | 2022-08-11 10:30 |  |  | Attended call, investigated status and functionality of fan on BMS. Not a BMS fault.Investigated unit found it had tripped over load. Reset and Tested. Operating normally.Checked belts and bearing for grease - all good.
MSA-DFES | WA6390223 | 1 | Anvil Doors | Engine Room Door -First Light Tanker - Front Door - keeps going into fault | Building | Doors | 4019.25 | Pass | Fail | 0 | 0 | 19.5 | 2022-12-22 07:18 | 2022-12-22 17:00 | 2022-12-22 16:40 | 2022-12-22 17:00 | 2022-12-23 12:10 |  |  | COMPLETE MOTOR REPLACEMENT REQUIRED
MSA-DTWD | WA6666053 | 1 | Equans Mechanical Services Australia | Room A356 - FCU - air con not working - Tripping circuit breaker | Air Conditioning | Ducted Split System | 264.645 | Pass | Fail | 0 | 0 | 19.5 | 2023-02-21 13:30 | 2023-02-22 17:00 | 2023-02-22 14:00 | 2023-02-22 17:00 | 2023-02-23 09:30
MSA-DTWD | WA5677992 | 3 | AHS Services WA Pty Ltd (Anchor) | Double sink to A311 is leaking | Plumbing & Drainage | Water | 242.12 | Pass | Pass | -1 | -1 | 19.3667 | 2022-07-26 08:57 | 2022-08-02 17:00 | 2022-07-26 14:00 | 2022-08-02 17:00 | 2022-07-27 09:22 |  |  | Tightened trap under sink
MSA-DTWD | WA6158995 | 0 | Precise Air Group | K Block Cafeteria - Freezer is not working | Refrigeration | Freezers | 981.7 | Pass | Fail | 0 | 0 | 19.2833 | 2022-11-10 10:45 | 2022-11-10 12:45 | 2022-11-10 12:03 | 2022-11-10 14:45 | 2022-11-11 07:20 |  |  | Attended site and signed in. Made way over to canteen and spoke to staff about issue with freezer room. Found system evap completely iced over. Isolated system, took evaporator apart and de-iced. Ran system up and took readings, indicated system was running slightly short of refrigerant. Picked refrigerant and returned to site. Proceeded to add refrigerant to system and monitor. Found system readings improve and freezer room reaching desired temperature. Suspect issue was due to age of system, short of refrigerant and the door being left open when stocking. Freezer system is very aged, in poor condition and past life expectancy, recommend budgeting for replacement ASAP.
MSA-DTWD | WA5382042 | 1 | AWB Co. | Blue 8 circuit breaker faulty it want reset | Electrical | General Electrical | 247.26 | Pass | Pass | 0 | 0 | 19.25 | 2022-04-26 13:22 | 2022-04-27 17:00 | 2022-04-26 14:45 | 2022-04-27 17:00 | 2022-04-27 10:00 |  | WACCES | Attended site completed jsa signed in. Replaced rcd in B block electrical engineering switchboard. Circuit is now working fine and no tripping. *** job completed ***
MSA-DTWD | WA5780240 | 3 | GRAFFITI FORCE PTY LTD | Graffiti Tagging walls and stalls – G129 | Cleaning | Graffiti | 800.5 | Fail | Fail | 0 | 1 | 19.25 | 2022-08-19 08:43 | 2022-08-26 17:00 | 2022-08-29 12:45 | 2022-08-26 17:00 | 2022-08-30 08:00 |  |  | REMOVAL OF GRAFFITI FROM WALLS AND STALLS OF E BLOCK TOILETS
MSA-DFES | WA6177747 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Tunic Room -GPO for drier not working | Electrical | General Electrical | 54.225 | Pass | Pass | 0 | 0 | 19.05 | 2022-11-14 07:22 | 2022-11-18 17:00 | 2022-11-15 14:15 | 2022-11-18 17:00 | 2022-11-16 09:18 |  |  | Carson Marshall (15/11/2022) - Work NoteLocated GPO not working in tunic room for the dryer. Found B15 RCD had tripped, checked circuit over and everything was good. Turned breaker back on and everything working in good order. Alerted station of fault and completion.
MSA-DTWD | WA5833109 | 2 | AHS Services WA Pty Ltd (Anchor) | Urinal button requires replacing B Block Ground Floor East end | Plumbing & Drainage | Toilets/Cisterns | 94.19 | Pass | Pass | 0 | 0 | 19.0333 | 2022-09-06 08:01 | 2022-09-09 17:00 | 2022-09-06 13:30 | 2022-09-09 17:00 | 2022-09-07 08:32 |  |  | Job completed
MSA-DFES | WA5680440 | 0 | Critical Fire Protection & Training | half of the building cannot dis activate smoke alarms | Fire Protection Services | Smoke and Heat Detection | 545.82 | Pass | Fail | 0 | 0 | 19 | 2022-07-27 12:24 | 2022-07-27 14:24 | 2022-07-27 14:00 | 2022-07-27 16:24 | 2022-07-28 09:00 |  |  | REPLACEMENT COMPLETED
MSA-DCA | WA6378019 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room -Chiller 3 is at fault number - Alarm has come up on the screen | Air Conditioning | Cooling Tower | 1773.05 | Fail | Fail | 0 | 0 | 19 | 2022-12-17 14:20 | 2022-12-17 16:20 | 2022-12-18 15:00 | 2022-12-17 18:20 | 2022-12-19 10:00 |  |  | Chillers 2 and 3 faulted in state Library plantroom.Chiller 2 faulted on start fault and transition contact fault.Chiller 3 faulted on start fault.18/12/22To get water temps lowered chillers 2 and 3 were put out of service, forced enable on for chillers 1 and 4. This was done to maintain the chilled water temperature setpoint. To lower the CHW load, State theatre and Art Gallery were put onto local mode to help.Contacted Air vision to attend site first thing in the morning 19/12/22 Air vision attended site and checked units. Chillers 2 & 3 were reset and tested. Testing found them all okay and are running again. Fault has been put down to issue with power supply to the building / chillers. Will monitor for similar faults occurring in the future.With chillers 2 and 3 now running correctly we put the chiller control back into automatic and Theatre and Gallery off local mode.
MSA-DTWD | WA6674285 | 2 | AHS Services WA Pty Ltd (Anchor) | Ladies toilets - the left hand basin tap doesnt work | Plumbing & Drainage | Drainage | 453.205 | Pass | Pass | 0 | 0 | 19 | 2023-02-27 09:17 | 2023-03-02 17:00 | 2023-02-28 13:30 | 2023-03-02 17:00 | 2023-03-01 08:30
MSA-DTWD | WA6000936 | 1 | High Tech Pest Control | Top of Loading dock - Bee hive/swarm has attached itself to a garden bench - see notes | Pest Control | General Pest | 720.3 | Pass | Pass | 0 | 0 | 19 | 2022-10-10 11:20 | 2022-10-11 17:00 | 2022-10-10 13:00 | 2022-10-11 17:00 | 2022-10-11 08:00 |  | WACCES | collected beehive storage box with Queen reservior and installed 10/10/22.Bentley TAFE Bee relocation box 11.10.22 - progress being made with queen staying in the box.To collect and remove in next days/ next week.
MSA-MRWA | WA5697506 | 2 | EQUANS Mechanical Services (WA) Pty Limited | failed air conditioners | Air Conditioning | Room Air Conditioners | 202.705 | Fail | Fail | 1 | 1 | 18.9667 | 2022-08-09 10:03 | 2022-08-12 17:00 | 2022-08-16 14:32 | 2022-08-12 17:00 | 2022-08-17 09:30 |  |  | Attended call, found no power supply to unit. Trace power failure to local CB. Electrician on site replaced. Tested and left running.
MSA-DTAG | WA6020639 | 2 | Australian HVAC Services Pty. Ltd. | Level 4 - Custody Corridor - Air con not working in custody corridor leading from court 42 | Air Conditioning | Room Air Conditioners | 246.92 | Pass | Pass | -1 | -1 | 18.9333 | 2022-10-13 15:03 | 2022-10-18 17:00 | 2022-10-13 15:04 | 2022-10-18 17:00 | 2022-10-14 10:00 |  |  | Attend site. Access level 4 and check temps. Found to be as normal. Access BMS and check operation of AC serving court 43. Found to be working as normal. All controls online and working. Confirm control reset the previous day has returned all plant to normal operation.
MSA-DTWD | WA5395024 | 2 | AWB Co. | F Block - Ground floor - F1 - One orange power point not working one has broken safety flap | Electrical | General Electrical | 562.8425 | Pass | Pass | -1 | -1 | 18.75 | 2022-05-05 10:19 | 2022-05-10 17:00 | 2022-05-05 12:30 | 2022-05-10 17:00 | 2022-05-06 07:15 |  | WACCES | Attended site signed in jsa completed. Met susan on site to gain access at 6am. Isolated b15 and r15 to replace two gpo’s. replaced and tested fine.*** job completed **
MSA-DCA | WA4990558 | 2 | Precise Air Group | Performance Space Store Room - Leak for Air Con plant | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 18.6667 | 2022-01-04 09:18 | 2022-01-07 17:00 | 2022-01-04 11:00 | 2022-01-07 17:00 | 2022-01-05 05:40 |  |  | Found drain fitting on unit has minor leak due to west and tear. Removed piece reseated and reinstated. Tested all running to specs
MSA-DTWD | WA6521846 | 0 | SENTINEL LOCK SERVICE PTY LTD | Room 14 - Students locked in room | Security | Locksmith | 417.51 | Pass | Pass | 0 | 0 | 18.6667 | 2023-01-30 13:42 | 2023-01-31 17:00 | 2023-01-30 14:50 | 2023-01-31 17:00 | 2023-01-31 09:30
MSA-DTWD | WA5689826 | 3 | AHS Services WA Pty Ltd (Anchor) | Sink Leaking | Plumbing & Drainage | Water | 153.32 | Pass | Pass | -1 | -1 | 18.55 | 2022-08-02 14:06 | 2022-08-09 17:00 | 2022-08-04 12:20 | 2022-08-09 17:00 | 2022-08-05 06:53 |  |  | Job completed
MSA-DTAG | WA5294019 | 1 | Sapio Pty Ltd | ground - Registry office door - Registry door fails to release after registering swipe card | Security | Access Control | 370 | Pass | Pass | 0 | 0 | 18.5 | 2022-03-28 12:15 | 2022-03-29 17:00 | 2022-03-28 13:30 | 2022-03-29 17:00 | 2022-03-29 08:00 |  |  | Replaced 8H Module. Tested all associated doors. Tested OK.Job completed.
MSA-DTWD | WA6255549 | 2 | Equans Mechanical Services Australia | Room D215 - Air con is freezing - No heating - See Notes Below | Air Conditioning | Room Air Conditioners | 354.735 | Pass | Pass | -1 | -1 | 18.5 | 2022-11-23 11:36 | 2022-11-28 17:00 | 2022-11-23 14:30 | 2022-11-28 17:00 | 2022-11-24 09:00 |  |  | Attended site, investigated vav 2.2 heater bank not heating. After testing all the solid relay, contractors, circuit breaker. All are electrically operating. But because the Bms is not in operation, I can't see it control is sending a signal to the relay to fire up the heater bank. Unfortunately I need the BMS to be operating.
MSA-DCA | WA6381732 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Admin - AC1 temp alarm | Air Conditioning | Room Air Conditioners | 414.14 | Pass | Fail | 0 | 0 | 18.5 | 2022-12-19 14:07 | 2022-12-19 16:07 | 2022-12-19 14:30 | 2022-12-19 18:07 | 2022-12-20 09:00 |  |  | Attended site and looked at admin ahu 1 zone 4. Found damper to be in incorrect position. Adjusted to correct alignment, lubricated and tested. Re attended site this morning and found no fault
MSA-DTWD | WA6676171 | 1 | AWB Co. | Room F42 - Breaker White 8 in electrical distribution board constantly tripping | Electrical | Distribution Board | 617.56 | Pass | Pass | 0 | 0 | 18.5 | 2023-02-28 12:12 | 2023-03-01 17:00 | 2023-02-28 13:30 | 2023-03-01 17:00 | 2023-03-01 08:00 |  | WCAPPR
MSA-DTAG | WA6113419 | 1 | Gilmour & Jooste Electrical | Level 1 - 1987 Wing - Light flickering – new light bulb required | Electrical | Lighting, Internal | 104.655 | Pass | Pass | 0 | 0 | 18.3333 | 2022-10-24 11:28 | 2022-10-25 17:00 | 2022-10-24 12:00 | 2022-10-25 17:00 | 2022-10-25 06:20 |  |  | Repair lights. Tested and working.
MSA-DCA | WA5679643 | 0 | TK Elevator Australia Pty Ltd | Main Gallery- Lift is not working Stuck on Level G - Door wide open and wont close | Lifts | Lifts | 4782 | Pass | Fail | 0 | 0 | 18.25 | 2022-07-26 17:01 | 2022-07-26 19:01 | 2022-07-26 19:01 | 2022-07-26 21:01 | 2022-07-27 13:16 |  |  | AU779418 - Lift 1 Art (large)-Geared :On arrival found lift stopped with landing door lock error, checkrd and found level1 RHS slow speed landing door panel hanger bracket bent and doorpanel wedged, door panel hanger bracket needs replacement/ repair, put the lift on shut down for landing door panel hanger bracket replacement/ repair , brought to thenotice of Bronwyn.AU780013 - Removed and straightened landing door hanger brackets on level 1 caused by obstruction in landing sill
MSA-DFES | WA4992711 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Applied training ground - Emergency shower - see details below | Plumbing & Drainage | Drainage | 213.86 | Pass | Pass | 0 | 0 | 18.1667 | 2022-01-06 16:38 | 2022-01-13 17:00 | 2022-01-11 14:54 | 2022-01-13 17:00 | 2022-01-12 09:04 |  | WACCES | Tested the safety shower flow
MSA-DTWD | WA6294410 | 1 | Western Resource Recovery Pty Ltd | Pit 6 blocked | Plumbing & Drainage | Drainage | 9395.6 | Pass | Fail | 0 | 0 | 18.1 | 2022-11-30 15:40 | 2022-12-01 17:00 | 2022-12-01 14:57 | 2022-12-01 17:00 | 2022-12-02 09:03 |  |  | WRR OPERATOR ATTENDED SITE ON 01/12/22 AND PUMPED OUT BLOCKED PIT 6 AS REQUESTED.EXTRACTED 11,320 LT OF WASTE LIQUID & TOOK TO WRR FACILITY FOR DISPOSAL.
MSA-MRWA | WA5378524 | 1 | TK Elevator Australia Pty Ltd | Lift 3 - level 5 - lift faulty | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 18.05 | 2022-04-20 15:12 | 2022-04-21 17:00 | 2022-04-20 17:06 | 2022-04-21 17:00 | 2022-04-21 11:09 |  |  | Lift out of service is lift 4, not lift 3. Checked RBC board for the rope brake. Yellow led flashing 10 times indicating a general error. Reset the RBC board. Checked the power supply voltage. Checked the board terminal connections. Tested lift operation without fault. Cleared all logs on lifts 3 and 4.to be closed out at $0 cost
MSA-DTWD | WA4991650 | 2 | Falcetta Plumbing and Gas | A block - Male toilet - urinal continuously running water | Plumbing & Drainage | Toilets/Cisterns | 414.28 | Fail | Fail | 0 | 1 | 18 | 2022-01-05 10:38 | 2022-01-10 17:00 | 2022-01-13 15:30 | 2022-01-10 17:00 | 2022-01-14 09:30 |  |  | sourced and replaced urinal solenoid
MSA-DTWD | WA5565075 | 0 | Techworks Plumbing | D002 - Female student toilet - blocked drains | Plumbing & Drainage | Toilets/Cisterns | 1914.49 | Pass | Fail | 0 | 0 | 18 | 2022-06-21 13:36 | 2022-06-21 15:36 | 2022-06-21 15:00 | 2022-06-21 17:36 | 2022-06-22 09:00 |  |  | Attend site for drain blockage. Inspection of site and location of drainage before being able to commence with clearing. Used both the jetter and could drain machine filling up with the camera to show a clear drain
MSA-DTWD | WA5833011 | 2 | AHS Services WA Pty Ltd (Anchor) | A Block- West Level 2 - Male Toilets - Blocked toilet & Broken button | Plumbing & Drainage | Toilets/Cisterns | 242.12 | Pass | Pass | 0 | 0 | 18 | 2022-09-06 07:08 | 2022-09-08 17:00 | 2022-09-06 14:30 | 2022-09-08 17:00 | 2022-09-07 08:30 |  |  | Job completed
MSA-DTWD | WA6359381 | 1 | High Tech Pest Control | Beehive from upper court yard | Pest Control | General Pest | 325.25 | Pass | Fail | 0 | 0 | 18 | 2022-12-06 15:15 | 2022-12-07 17:00 | 2022-12-07 13:30 | 2022-12-07 17:00 | 2022-12-08 07:30 |  | WCAPPR | Bee hive dusted inside tree hollow with Permethrin dust Starr Dust Pro(R)
MSA-DCA | WA6383919 | 0 | Automatic Fire Protection (ARA) | Ground Floor - Security - 2 Faulty smoke detectors | Fire Protection Services | Smoke and Heat Detection | 1080.495 | Fail | Fail | 0 | 0 | 18 | 2022-12-20 15:19 | 2022-12-20 17:19 | 2022-12-20 17:30 | 2022-12-20 19:19 | 2022-12-21 11:30 |  |  | 20/12/22 CS Attended site and replaced 1x smoke detector, will require revisit in the morning with another smoke detector and scissor(onsite).21/12/22 CSReturned to site and replaced other smoke detector, panel sitting normal.
MSA-DTWD | WA6585772 | 1 | COMMERCIAL PLUMBING AND GAS | North side of block 3 - damaged pipe in ground | Plumbing & Drainage | Drainage | 489.15 | Pass | Pass | 0 | 0 | 18 | 2023-02-16 10:45 | 2023-02-17 17:00 | 2023-02-16 15:00 | 2023-02-17 17:00 | 2023-02-17 09:00
MSA-DTWD | WA6672860 | 2 | ECO PLUMBING AND GAS PTY LTD | Hot water tap leaking | Plumbing & Drainage | Water | 200.53 | Pass | Pass | 0 | 0 | 17.8 | 2023-02-24 09:04 | 2023-03-01 17:00 | 2023-02-27 17:22 | 2023-03-01 17:00 | 2023-02-28 11:10
MSA-DFES | WA5869148 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | multiple locations - faulty plumbing issues - see notes below | Plumbing & Drainage | Water | 358.75 | Pass | Pass | 0 | 0 | 17.75 | 2022-09-14 11:55 | 2022-09-21 17:00 | 2022-09-19 15:00 | 2022-09-21 17:00 | 2022-09-20 08:45 |  | WACCES | Arrived on site and singed in went to Change room 4 location engine bay need to pick up part's and come back and install a new shower head, went to practical training ground toilets and looked for shower head that is leaking found it in shower 4 something need to get parts from Reece and come back and install a new one. Had to pick up part's from Reece this morning 20/9/22 and installed 2 new shower heads in charge room 4 and one in shower 4 training ground
MSA-DFES | WA5987379 | 3 | Protek 24/7 Building & Maintenance | Perimeter fence requires fixing | Building | Steel Fencing & Gates | 323.78 | Pass | Pass | -1 | 0 | 17.75 | 2022-10-03 11:06 | 2022-10-10 17:00 | 2022-10-06 14:30 | 2022-10-10 17:00 | 2022-10-07 08:15 |  |  | Removed damaged fence brackets x8Painted and installed new fence brackets X 8Re adjusted bracket that was mis aligned
MSA-DFES | WA6687948 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Laundry room- ladies bathroom - back room - Light broken | Electrical | Lighting, Internal |  | Pass | Fail | 0 | 0 | 17.75 | 2023-03-07 10:40 | 2023-03-14 17:00 | 2023-03-14 15:15 | 2023-03-14 17:00 | 2023-03-15 09:00
MSA-DTAG | WA5482483 | 1 | AAA Ability Locksmiths | Court Room 1- Door - not closing properly - push button door | Security | Locksmith | 495 | Pass | Pass | 0 | 0 | 17.6667 | 2022-05-31 12:30 | 2022-06-01 17:00 | 2022-05-31 14:05 | 2022-06-01 17:00 | 2022-06-01 07:45 |  |  | 31/05/2022- Attend site, door closer arm in the wrong location. Door needs removing and relocate door closer 2 technicians required. 01/06/2022- Remove door and position correctly.
MSA-DTWD | WA5413871 | 2 | Damian Rak Electrical Pty Ltd | BLD 821 - Gym - Light switch faulty and 4 fluros faulty | Electrical | General Electrical |  | Pass | Pass | -1 | -1 | 17.5 | 2022-05-12 14:27 | 2022-05-17 17:00 | 2022-05-12 15:00 | 2022-05-17 17:00 | 2022-05-13 08:30 |  |  | job completed - lights repaired
MSA-DCA | WA6231260 | 0 | Precise Air Group | Main Air con is not working and they have a show tonight | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1238.02 | Pass | Fail | 0 | 0 | 17.5 | 2022-11-18 16:34 | 2022-11-18 18:34 | 2022-11-18 17:00 | 2022-11-18 20:34 | 2022-11-19 10:30 |  |  | Call-out for AC 2 in main theatre area at 5pm to 9pm ,kept blowing control fuses when switching from cooling to heating cycle had to go get control fuses at 8pm from another tech to go back Saturday morning 6.30am to 10.30am to check unit ,upon further investigation found control wires for hp/Lp ,reversing valve, hot gas bypass and condenser coil sensor had all burnt out and fuse together from wires rubbing on steel cabinet from vibration,required all 4 control circuits on stage 1 to be rewired ,checked full operation of system on cooling and heating cycles all running well for Saturdays show .
MSA-DCA | WA5534839 | 0 | Techworks Electrical | Gound Floor - Front Entrance - Gantry light - has been vandalized and hanging down | Electrical | General Electrical | 983.07 | Pass | Fail | 0 | 0 | 17.2333 | 2022-06-16 14:50 | 2022-06-16 16:50 | 2022-06-16 15:16 | 2022-06-16 18:50 | 2022-06-17 08:30 |  |  | Replaced water damaged lights. Siliconed all lights and fixed covers to base’s to prevent further damage
MSA-DTWD | WA6540188 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 2 - Female toilet - Toilet has running water on the floor | Plumbing & Drainage | Toilets/Cisterns | 231.3325 | Pass | Pass | -1 | -1 | 17 | 2023-02-09 09:01 | 2023-02-14 17:00 | 2023-02-09 15:30 | 2023-02-14 17:00 | 2023-02-10 08:30
MSA-DCA | WA6688278 | 0 | Techworks Electrical | transformer room-plant room 5-main circuit breaker has tripped | Electrical | General Electrical |  | Pass | Fail | 0 | 0 | 17 | 2023-03-07 13:14 | 2023-03-07 15:14 | 2023-03-07 14:00 | 2023-03-07 17:14 | 2023-03-08 07:00
MSA-DTWD | WA5564636 | 1 | M Construction (WA) | damaged internal metal ceiling to spray booth including rusted seal panel | Building | Ceiling | 794.39 | Pass | Fail | 0 | 0 | 17 | 2022-06-21 11:39 | 2022-06-22 17:00 | 2022-06-22 13:30 | 2022-06-22 17:00 | 2022-06-23 06:30 |  |  | Attended site to replace corroded ceiling panel.
MSA-DCA | WA5838520 | 0 | EQUANS Mechanical Services (WA) Pty Limited | External plant room - really loud noise chiller 3 | Refrigeration | Chiller | 709.45 | Fail | Fail | 0 | 0 | 17 | 2022-09-08 14:13 | 2022-09-08 16:13 | 2022-09-08 17:30 | 2022-09-08 18:13 | 2022-09-09 10:30 |  |  | Trent Jackson attended call out but unable to access as site was unattended.Attended site. Investigated noise coming from plantroom. Found noise coming from the estop safety valve which is connected to the air compressor. Accessed bms and gave the air compressor enable to run. Safety valve remained open and bleeding air from the system. Checked over workshop and found emergency stop button sticking which has broken the circuit. Recommend replacing, will submit das to replace. Released button and tested operation of plant. Safety valve has closed and the workshop is maintaining 100 psi of pressure. Checked driers for water and bled, all ok. Removed manual override on bms and switched plant back to auto. Completed paperwork.
MSA-DTWD | WA5390670 | 1 | ECO PLUMBING AND GAS PTY LTD | D1 - Pastry lab - Faulty filtered water tap | Plumbing & Drainage | Drainage | 247.845 | Fail | Fail | 0 | 0 | 16.75 | 2022-05-02 14:49 | 2022-05-03 17:00 | 2022-05-04 14:45 | 2022-05-03 17:00 | 2022-05-05 07:30 |  |  | Replaced ministop and spout. Serviced hot tap
MSA-DCA | WA6293022 | 0 | Critical Fire Protection & Training | Fire panel fault in reception area | Fire Protection Services | Fire Protection - Monitor System | 1222.1625 | Pass | Fail | 0 | 0 | 16.75 | 2022-11-29 16:37 | 2022-11-29 18:37 | 2022-11-29 18:00 | 2022-11-29 20:37 | 2022-11-30 10:45 |  |  | Start time: 6pmFinish time: 6:15pmPanel was Normal on arrival although the code red was in system 1 fault.Suspected faulty detector in basement area requires further investigation.
MSA-DCA | WA5207733 | 1 | EQUANS Mechanical Services (WA) Pty Limited | BMS offline - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 293.025 | Pass | Pass | 0 | 0 | 16.6667 | 2022-03-08 16:39 | 2022-03-09 17:00 | 2022-03-08 16:50 | 2022-03-09 17:00 | 2022-03-09 09:30 |  |  | Dialled into site and investigated issue with rehearsal room 1 ac. Found temp setpoint set to 16c Increased setpoint to 23c Attended site Reset computer and tested bms, all ok Changed setpoint to 20c as requested and checked over ahu, all ok Completed paperwork
MSA-DTWD | WA5661025 | 1 | AWB Co. | various locations- fluros need changing-B building L3 tower needs to be change first | Electrical | Lighting, Internal | 228.425 | Pass | Pass | 0 | 0 | 16.5333 | 2022-07-19 14:28 | 2022-07-20 17:00 | 2022-07-19 16:43 | 2022-07-20 17:00 | 2022-07-20 09:15 |  |  | Attended site and signed in. Completed JSA. Located lights not working on level 3. Supply and replaced tube and starters as required. Checked out other levels. Supply and replace other lamps on level 2 and 4. Tested all okay. Signed out. Job complete
MSA-DCA | WA5231927 | 0 | Precise Air Group | Level 2 - Store room- Water leaking through light fitting - possible AC leaking. | Air Conditioning | Room Air Conditioners | 596.51 | Fail | Fail | 0 | 0 | 16.5 | 2022-03-15 18:18 | 2022-03-15 20:18 | 2022-03-15 20:30 | 2022-03-15 22:18 | 2022-03-16 13:00 |  |  | Gained access to unit, unblocked drain tested ok
MSA-DCA | WA6157391 | 0 | Automatic Fire Protection (ARA) | Ground Floor - Security - Fire panel fault - L3 Concourse | Fire Protection Services | Fire Protection - Monitor System | 844.14 | Pass | Fail | 0 | 0 | 16.5 | 2022-11-09 17:03 | 2022-11-09 19:03 | 2022-11-09 18:00 | 2022-11-09 21:03 | 2022-11-10 10:30 |  |  | 9/11/22 CS Attended after hours call out for a fault on level 3 concourse. A smoke detector has gone into maintenance fault with an a value of10 (L3 D74 Z30).As no stock available, this will need to be replaced asap in the morning.Required is an ampac addressable smoke detector with extension pole/detector head attachment.10/11 KS Attended site and fitted new detector and de isolated left normal
MSA-DFES | WA5478978 | 0 | Anvil Doors | Engine Room - Door 1 - please check the engine room | Building | Automatic Doors | 500 | Fail | Fail | 1 | 1 | 16.3833 | 2022-05-26 16:08 | 2022-05-26 18:08 | 2022-05-30 15:38 | 2022-05-26 20:08 | 2022-05-31 08:01 |  |  | Technician attended the P0 Call out within 1 hour on 26/05/22.It was advised by station staff that the door had taken impact damage 2 days prior to the P0 reactive call out.The glass had been smashed and repaired by a glazier. The door had not been taken care of and began to become inoperable.Technician was able to get the door operational.It is advised in further that if a door is impacted that we are notified for reactive call out. So that the door can be assessed bya qualified technician. This will allow you to take the correct course of action for repairs, as advised by the technician.
MSA-DTWD | WA6023086 | 2 | High Tech Pest Control | Large population of bees entering external brickwork and making their way into the office | Pest Control | General Pest | 270.25 | Pass | Pass | 0 | 0 | 15.55 | 2022-10-14 16:54 | 2022-10-19 17:00 | 2022-10-18 15:27 | 2022-10-19 17:00 | 2022-10-19 07:00 |  |  | Attended 18/10 and asked to return 6am next morning, 19.10.22 for treatment.18.10.22 12.45-13.2519.10.22 6.10 AM-7AM
MSA-DFES | WA5204629 | 1 | Anvil Doors | Engine Room - Automatic Door - motor is running but door is not opening and burning smell from motor | Building | Automatic Doors | 2272 | Pass | Pass | -1 | 0 | 15.5 | 2022-03-04 12:01 | 2022-03-08 17:00 | 2022-03-04 19:30 | 2022-03-08 17:00 | 2022-03-05 11:00 |  |  | Update--Hi programmed,Update.Our technician attended Osborne Park Fire station tonight. Unfortunately the bifold door can still no be shut as there is a fault with the motor only spinning in one direction.I have arranged for an electrician to attend tomorrow morning.The station crew are aware of the situation.If the motor is faulty it may need to be replaced.Update.The CB6 Controller was found to be faulty and replaced onsite-- No BRAF was submitted as urgent repairs were required to secure the fire station over the week end
MSA-DCA | WA6667893 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Foyer - Front desk lighting pad - Unable to turn all lights off | Electrical | Lighting, Internal | 345.095 | Pass | Pass | 0 | 0 | 15.25 | 2023-02-21 16:32 | 2023-02-22 17:00 | 2023-02-21 16:45 | 2023-02-22 17:00 | 2023-02-22 08:00
MSA-DTWD | WA6377461 | 1 | Equans Mechanical Services Australia | Aircon is cooling some zones and not others | Air Conditioning | Ducted Split System | 1210.195 | Fail | Fail | 0 | 0 | 15 | 2022-12-16 15:38 | 2022-12-19 17:00 | 2022-12-19 22:30 | 2022-12-19 17:00 | 2022-12-20 13:30 |  |  | 19/12/22: Checked the aircons out found a/c one not running , problem with power . Return tomorrow with second person need a hand 20/12/22 Checked the in coming power , need a second tech to be the sub board while checking on the roof . Found a intermittent fault with tng isolator which was holding out the compressor. Picked up parts from the suppliers, returned to site replaced the isolator, restarted and test ran all OK.
MSA-DCA | WA6407252 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 - Plant Room in State Library - Cooling tower fault on net board | Air Conditioning | Cooling Tower | 371.62 | Fail | Fail | 0 | 0 | 15 | 2023-01-10 07:25 | 2023-01-10 17:00 | 2023-01-10 19:00 | 2023-01-10 17:00 | 2023-01-11 10:00
MSA-DTWD | WA5548804 | 2 | AWB Co. | Exhaust Fan faulty | Equipment | Electrical Equipment | 581.78 | Pass | Pass | 0 | 0 | 14.75 | 2022-06-17 09:55 | 2022-06-22 17:00 | 2022-06-22 00:15 | 2022-06-22 17:00 | 2022-06-22 15:00 |  |  | Attended site and signed in. Completed jsa. Spole to Jeffrey. Located faulty exhaust fan. After further investigation we found that the timer was faulty, spoke to Jeffrey and he said to replace timer. Went to wholesaler to pick up parts. Returned to site. Replaced timer. Everything working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6253679 | 2 | Dormakaba Australia Pty Ltd | WO created for invoicing purposes - WA6109194 - See Notes | Building | Doors |  | Pass | Pass | 0 | 0 | 14.2667 | 2022-11-22 11:20 | 2022-11-25 17:00 | 2022-11-22 18:14 | 2022-11-25 17:00 | 2022-11-23 08:30 |  |  | Work was completed 21/10 as per original work order WA6109194
MSA-DTWD | WA5853866 | 3 | Equans Mechanical Services Australia | Fridge faulty | Refrigeration | Refrigerators | 219.6 | Pass | Pass | -1 | -1 | 14 | 2022-09-12 11:42 | 2022-09-19 17:00 | 2022-09-13 01:30 | 2022-09-19 17:00 | 2022-09-13 15:30 |  |  | RECLAIMED THE GAS FROM OLD FRIDGES.
MSA-DTAG | WA6362654 | 2 | Dom's Total Grounds Maintenance | Outside childrens court garden - Damaged and broken reticulation - See Notes Below | Landscaping & Gardening | Grounds Maintenance | 333 | Fail | Fail | 0 | 0 | 14 | 2022-12-09 11:49 | 2022-12-14 17:00 | 2022-12-17 08:30 | 2022-12-14 17:00 | 2022-12-17 22:30 |  |  | Call Out, Labour & Supply Retic Parts
MSA-DTWD | WA5201277 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 310.75 | Pass | Fail | 0 | 0 | 13.75 | 2022-03-02 13:12 | 2022-03-03 17:00 | 2022-03-03 07:00 | 2022-03-03 17:00 | 2022-03-03 20:45 |  |  | Roof leak
MSA-DTWD | WA5781281 | 2 | GRAFFITI FORCE PTY LTD | Remove Graffiti male toilet A Block Level 2 | Cleaning | Graffiti | 290.5 | Fail | Fail | 1 | 1 | 13.25 | 2022-08-19 14:49 | 2022-08-24 17:00 | 2022-09-02 00:30 | 2022-08-24 17:00 | 2022-09-02 13:45 |  |  | removal of graffiti from block A level 2 male toilets
MSA-DCA | WA6523365 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Mech office-air con is blowing warm air in wrong direction | Air Conditioning | Room Air Conditioners | 506.75 | Pass | Fail | 0 | 0 | 13.0667 | 2023-01-31 15:11 | 2023-01-31 17:11 | 2023-01-31 15:56 | 2023-01-31 19:11 | 2023-02-01 05:00
MSA-DFES | WA5001678 | 2 | AWB Co. | Kitchen - chipped brand new caesar stone | Equipment | Catering Equipment | 1000 | Fail | Fail | 1 | 1 | 13.0167 | 2022-01-11 14:52 | 2022-01-14 17:00 | 2022-01-21 02:10 | 2022-01-14 17:00 | 2022-01-21 15:11 |  |  | Attended site and repaired stone chip in benchtop. Job complete
MSA-DFES | WA6190605 | 2 | Protek 24/7 Building & Maintenance | Main Entry Door at rear of premise - faulty closer - see notes below | Building | Doors | 179.47 | Pass | Pass | -1 | -1 | 13 | 2022-11-16 09:20 | 2022-11-21 17:00 | 2022-11-16 14:30 | 2022-11-21 17:00 | 2022-11-17 03:30 |  | WCAPPR | Adjusted the door closer , removed the internal lock set repaired the door , install additional fixing to backin plate , re fit door lock assembly
MSA-DCA | WA6652758 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Collection store 2 - Humidity alarm | Air Conditioning | Room Air Conditioners | 1492.115 | Pass | Fail | 0 | 0 | 12.7833 | 2023-02-20 23:31 | 2023-02-21 01:31 | 2023-02-20 23:43 | 2023-02-21 03:31 | 2023-02-21 12:30
MSA-DTWD | WA5696528 | 2 | AWB Co. | B Block - Male Staff Toilet - Replace blown light globe in the male staff toilet | Electrical | Lighting, Internal | 159.9775 | Pass | Pass | 0 | 0 | 12.75 | 2022-08-08 12:30 | 2022-08-11 17:00 | 2022-08-10 02:45 | 2022-08-11 17:00 | 2022-08-10 15:30 |  |  | NA
MSA-DTWD | WA6126953 | 3 | Equans Mechanical Services Australia | L Shed - Floristry cool room - noisy, faulty belt | Refrigeration | Coolroom | 213.675 | Pass | Pass | -1 | -1 | 12.75 | 2022-10-25 15:23 | 2022-11-01 17:00 | 2022-10-27 01:15 | 2022-11-01 17:00 | 2022-10-27 14:00 |  |  | REPORT
MSA-MRWA | WA6364913 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Cooling tower leaking Level 10 (9 in system) | Air Conditioning | Cooling Tower | 1321.4 | Pass | Fail | 0 | 0 | 12.75 | 2022-12-12 19:15 | 2022-12-12 21:15 | 2022-12-12 20:00 | 2022-12-12 23:15 | 2022-12-13 08:45 |  |  | Followed up on Chauns call out the night before were water supply to cooling towers was isolated to prevent further leaking and BMS schedule adjust to prevent chillers coming on in case they demanded more water for towers.Attended site, found that tighting fittings only increase leaking. Called in Hallgroves pipe fitters to assess and rectify issues with fitting. Check BMS and ambient temperature brought building systems back on line as ambient 15 C and ambient temp locked out to 20c. Advised Brendan and Danika of reasoning and that pipefitter arrival immenient. Checked buildings operation and left running.
MSA-DCA | WA6208285 | 1 | Techworks Electrical | Christmas light trail fittings are exposed to elements, please make safe. | Electrical | Lighting, Internal | 3069.94 | Pass | Fail | 0 | 0 | 12 | 2022-11-17 15:57 | 2022-11-18 17:00 | 2022-11-18 06:00 | 2022-11-18 17:00 | 2022-11-18 18:00 |  |  | Made all electrical connections water sealed by installing adaptable boxs and extension lead IP rated boxs
MSA-DTWD | WA5586123 | 2 | JEM Carpentry | House 13 - Faulty fence back yard | Building | Steel Fencing & Gates |  | Pass | Pass | 0 | 0 | 11 | 2022-07-06 10:43 | 2022-07-11 17:00 | 2022-07-09 07:00 | 2022-07-11 17:00 | 2022-07-09 18:00 |  |  | New fence installed
MSA-DTWD | WA5258185 | 1 | Precise Air Group | Fault with AC in Music Dept, G Block, Leederville. Need to assess condition of system | Air Conditioning | Building HVAC Maintenance (Major Plant) | 423.86 | Pass | Fail | 0 | 0 | 10.95 | 2022-03-17 16:44 | 2022-03-18 17:00 | 2022-03-18 07:00 | 2022-03-18 17:00 | 2022-03-18 17:57 |  |  | Attended site, shown location of AC units in question. Found return air filters blocked and require replacement. With further investigation filters have been ordered on another work order. Inspected air flows and found damper closed in certain areas - restricting airflow causing temp issues. Open dampers monitored operation. Space temp improved. Liaised with site FM.
MSA-DTWD | WA6687829 | 1 | Precise Air Group | Chiller compound - Chiller 1 i fault | Refrigeration | Chiller | 366 | Pass | Fail | 0 | 0 | 10.7833 | 2023-03-07 09:58 | 2023-03-08 17:00 | 2023-03-08 07:00 | 2023-03-08 17:00 | 2023-03-08 17:47
MSA-DTWD | WA6255792 | 2 | JEM Carpentry | Between House 814 and house 813- Faulty ringlock fence | Building | Steel Fencing & Gates |  | Fail | Fail | 1 | 1 | 10.75 | 2022-11-23 13:56 | 2022-11-28 17:00 | 2022-12-02 06:45 | 2022-11-28 17:00 | 2022-12-02 17:30 |  |  | Repairs to fence
MSA-DTWD | WA5586064 | 1 | JEM Carpentry | House 13-Repair faulty pavers back of house | Paving & Roadworks | Paving |  | Fail | Fail | 0 | 0 | 10.5 | 2022-07-06 10:21 | 2022-07-07 17:00 | 2022-07-08 09:00 | 2022-07-07 17:00 | 2022-07-08 19:30 |  |  | Completed
MSA-DTWD | WA5294957 | 1 | WESTERN IRRIGATION PTY LTD | Bushland - Bushland Reserve southwest corner of carpark facing Education Drive | Landscaping & Gardening | Grounds Maintenance | 2817.75 | Pass | Pass | 0 | 0 | 10 | 2022-03-29 10:05 | 2022-03-30 17:00 | 2022-03-30 06:30 | 2022-03-30 17:00 | 2022-03-30 16:30 |  |  | Excavated and redirected mainline as required.
MSA-DTWD | WA5751986 | 2 | JEM Carpentry | Bedroom 2 - Wall plaster bubbling investigate | Building | Internal Walls |  | Pass | Pass | 0 | 0 | 10 | 2022-08-17 11:25 | 2022-08-22 17:00 | 2022-08-22 07:00 | 2022-08-22 17:00 | 2022-08-22 17:00 |  |  | Replaced and painted
MSA-DTWD | WA5656061 | 2 | AHS Services WA Pty Ltd (Anchor) | ground-ladies toilet-the shower drain is blocked | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 9.5 | 2022-07-18 11:31 | 2022-07-21 17:00 | 2022-07-19 06:30 | 2022-07-21 17:00 | 2022-07-19 16:00 |  |  | Job completed
MSA-DTWD | WA6111591 | 2 | JEM Carpentry | Faulty non slip tape on steps | Building | General Building |  | Fail | Fail | 1 | 1 | 9.5 | 2022-10-21 08:59 | 2022-10-26 17:00 | 2022-11-04 08:00 | 2022-10-26 17:00 | 2022-11-04 17:30 |  |  | installed new tape
MSA-DTWD | WA6111644 | 2 | JEM Carpentry | BLD 820-outside steps-Faulty non slip tape on steps | Carpentry | Staircases, Balustrades and Handrails |  | Fail | Fail | 1 | 1 | 9.5 | 2022-10-21 09:34 | 2022-10-26 17:00 | 2022-11-02 08:00 | 2022-10-26 17:00 | 2022-11-02 17:30 |  |  | Tape layed
MSA-DTWD | WA5586718 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, Internal | 2039.61 | Pass | Pass | -1 | -1 | 9.5 | 2022-07-06 13:54 | 2022-07-11 17:00 | 2022-07-07 06:00 | 2022-07-11 17:00 | 2022-07-07 15:30 |  |  | Replaced multiple faulty lights through the room
MSA-DTWD | WA6680576 | 2 | COMMERCIAL PLUMBING AND GAS | Bad smell coming from sink | Plumbing & Drainage | Drainage | 1044.275 | Pass | Pass | -1 | -1 | 9.5 | 2023-03-01 12:39 | 2023-03-07 17:00 | 2023-03-02 09:00 | 2023-03-07 17:00 | 2023-03-02 18:30
MSA-DTAG | WA5693050 | 1 | OCS SERVICES PTY LTD | Level 4 - Court41 - Covid Clean of entire court | Cleaning | Emergency Cleans |  | Pass | Fail | 0 | 0 | 9.2833 | 2022-08-04 09:04 | 2022-08-05 17:00 | 2022-08-05 08:43 | 2022-08-05 17:00 | 2022-08-05 18:00 |  |  | Completed t 1700 covid clean
MSA-DTWD | WA5067000 | 3 | AWB Co. | Level 1 - Male staff toilet - Repaint ceiling damaged by water leak | Building | General Building | 880 | Fail | Fail | 1 | 1 | 9 | 2022-01-19 09:56 | 2022-01-27 17:00 | 2022-01-31 07:00 | 2022-01-27 17:00 | 2022-01-31 16:00 |  |  | Repainted ceiling in male toilet, job complete
MSA-DTWD | WA5067062 | 3 | AWB Co. | Level 4 - N428B - Repaint damaged wall in old office | Building | General Building | 925 | Fail | Fail | 1 | 1 | 9 | 2022-01-19 10:06 | 2022-01-27 17:00 | 2022-01-31 07:00 | 2022-01-27 17:00 | 2022-01-31 16:00 |  |  | Wall has been repainted. Job Complete
MSA-DTWD | WA5216888 | 3 | AWB Co. | Jobs and Skills centre 219 - Patch and paint main wall | Building | General Building | 1680.39 | Pass | Pass | 0 | 0 | 9 | 2022-03-11 13:32 | 2022-03-18 17:00 | 2022-03-15 07:00 | 2022-03-18 17:00 | 2022-03-15 16:00 |  |  | Prep and paint office walls, doors, frames and skirtings
MSA-DTWD | WA5367729 | 2 | AWB Co. | Damaged wall and tiles | Building | Internal Walls | 870 | Fail | Fail | 1 | 1 | 9 | 2022-04-19 10:00 | 2022-04-22 17:00 | 2022-04-27 07:00 | 2022-04-22 17:00 | 2022-04-27 16:00 |  |  | Replace damaged tiles
MSA-DTWD | WA5454527 | 1 | SCAVENGER SUPPLIES PTY LTD | FIP needs isolating - See notes below | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 9 | 2022-05-17 12:07 | 2022-05-18 17:00 | 2022-05-18 07:00 | 2022-05-18 17:00 | 2022-05-18 16:00 |  |  | Completed 18/05/2022
MSA-DTWD | WA5706797 | 2 | JEM Carpentry | BLD 816 - Faulty Fence | Building | Steel Fencing & Gates |  | Pass | Pass | 0 | 0 | 9 | 2022-08-11 14:06 | 2022-08-16 17:00 | 2022-08-15 08:30 | 2022-08-16 17:00 | 2022-08-15 17:30 |  |  | Repairs to fence
MSA-DTWD | WA5838603 | 3 | AWB Co. | Patch and Paint damaged walls | Painting | Internal | 1763.32 | Fail | Fail | 1 | 1 | 9 | 2022-09-08 15:21 | 2022-09-15 17:00 | 2022-09-23 07:00 | 2022-09-15 17:00 | 2022-09-23 16:00 |  |  | painting works completed
MSA-DTWD | WA5980240 | 3 | AWB Co. | Storeroom door paint has been scuffed and removed | Building | Doors | 677.62 | Pass | Pass | 0 | 0 | 9 | 2022-09-29 13:36 | 2022-10-06 17:00 | 2022-10-03 07:00 | 2022-10-06 17:00 | 2022-10-03 16:00 |  |  | Storeroom door paint has been scuffed and removed
MSA-DTWD | WA6356776 | 1 | COMMERCIAL PLUMBING AND GAS | Gas oven won’t ignite - See notes | Plumbing & Drainage | Gas | 374.06 | Pass | Fail | 0 | 0 | 9 | 2022-12-05 09:01 | 2022-12-06 17:00 | 2022-12-06 11:00 | 2022-12-06 17:00 | 2022-12-06 20:00 |  |  | repaired pilot assembly
MSA-DTWD | WA6361798 | 3 | AWB Co. | Hairdressing sink cabinet paint scuffed and damaged needs to be re painted | Painting | Internal | 906.42 | Pass | Pass | 0 | 0 | 9 | 2022-12-08 13:19 | 2022-12-15 17:00 | 2022-12-13 07:00 | 2022-12-15 17:00 | 2022-12-13 16:00 |  |  | painting works completed
MSA-DCA | WA5828935 | 2 | Techworks Electrical | Faulty kitchen light | Electrical | Lighting, Internal | 532.54 | Pass | Pass | 0 | 0 | 8.5333 | 2022-09-02 09:09 | 2022-09-07 17:00 | 2022-09-06 08:58 | 2022-09-07 17:00 | 2022-09-06 17:30 |  |  | Repaired - further info to come
MSA-DTWD | WA5835541 | 3 | AWB Co. | Holes in wall near passage A317 | Building | Internal Walls | 975.465 | Pass | Pass | 0 | 0 | 8.5 | 2022-09-07 09:22 | 2022-09-14 17:00 | 2022-09-13 06:30 | 2022-09-14 17:00 | 2022-09-13 15:00 |  |  | Make good to damaged wall including paint all affected area.
MSA-DTWD | WA5887793 | 3 | AWB Co. | Main Entrance - Up lights for Artwork faulty Executive Pool main entrance | Electrical | Lighting, Internal | 1106.1 | Pass | Pass | 0 | 0 | 8.5 | 2022-09-16 10:02 | 2022-09-23 17:00 | 2022-09-23 08:00 | 2022-09-23 17:00 | 2022-09-23 16:30 |  |  | Actual start 12.30pm
MSA-DFES | WA6125902 | 0 | SONTEC WA PTY LTD | building alarm cannot be disarmed battery needs to be disconnected-see notes | Security | Security Management System | 456 | Pass | Fail | 0 | 0 | 8.5 | 2022-10-25 09:14 | 2022-10-25 11:14 | 2022-10-25 10:15 | 2022-10-25 13:14 | 2022-10-25 18:45 |  |  | 25/10/22 - Joshua ParkAttended in the morning to disconnect AC power and back up batteries.Returned after power restored to reconnect.
MSA-DTAG | WA6129408 | 3 | PPM Project Painting & Maintenance | Lvel 3 - Public toilet - Graffiti on male toilet wall – Hay Street end | Cleaning | Graffiti |  | Fail | Fail | 4 | 4 | 8.5 | 2022-10-27 14:41 | 2022-11-03 17:00 | 2022-12-01 07:30 | 2022-11-03 17:00 | 2022-12-01 16:00 |  |  | Removal of graffiti
MSA-DCA | WA6157258 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Revolving door - Door sleeves to remain open function is not working. | Building | Automatic Doors | 2393.5 | Fail | Fail | 2 | 2 | 8.5 | 2022-11-09 14:19 | 2022-11-10 17:00 | 2022-11-22 07:30 | 2022-11-10 17:00 | 2022-11-22 16:00 |  |  | Completed quoted works:" Safe removal of ceiling panels to further investigate fault, Check level 3 programming on the revolver and logic settings. Check all door components."Test and check door operation."The above work is to be carried out during normal business hours
MSA-DTWD | WA5379350 | 2 | AWB Co. | K Block - Damaged fridge door in the Cafeteria | Equipment | Catering Equipment | 1046.96 | Fail | Fail | 1 | 1 | 8.5 | 2022-04-21 10:19 | 2022-04-27 17:00 | 2022-05-04 07:00 | 2022-04-27 17:00 | 2022-05-04 15:30 |  |  | works completed BRAF attachedno-one on site to sign
MSA-DCA | WA5472069 | 1 | Techworks Electrical | James Street entrance - Ground – external - Bollards have not been fully going down -see notes | Equipment | Electrical Equipment | 2122.64 | Pass | Pass | 0 | 0 | 8.5 | 2022-05-23 13:48 | 2022-05-24 17:00 | 2022-05-24 07:00 | 2022-05-24 17:00 | 2022-05-24 15:30 |  | WACCES | Completed investigations with James from Marshall beatie. Found that all limit switches need replacing and a service of the cylinder is neededOpen up control panel. Safety loops/plug is out, plug in. Bridge activation, 1st bollard lowered almost instantly, 2nd(closest to garden) took 10/15 sec after. Traffic lights went from off to red, never changed to green to pass. Testedphone in activation, same as above. Tested loop exit activation, again as above.Removed lid of bollard, checked joints, all ok. Made adjustments to valves/solenoids, bollards now raise more or lesstogether, but lowering 2nd still 5sec behind. Checked limits for traffic light control. Limits are in series tops and bottomsof bollards. Proved bottom of each faulty, hence no green light. Tested safety loops (3 in series) each Pur-80/Bl-83/R-80micro Henry's, 198 total. Safety intermittently faults. Attempts to get No2 bollard out failed, 1 bolts too rusted and deepinside. 2 need 1/2 sq drive 900mm long with 22mm
MSA-DTWD | WA6020140 | 2 | Techworks Electrical | Replace damaged Contactor 24S in the MSS-5 Switchboard | Electrical | Distribution Board | 607.34 | Pass | Pass | 0 | 0 | 8.5 | 2022-10-13 11:09 | 2022-10-18 17:00 | 2022-10-18 07:00 | 2022-10-18 17:00 | 2022-10-18 15:30 |  |  | Rectified hot spot on cable
MSA-DTWD | WA6253814 | 2 | AHS Services WA Pty Ltd (Anchor) | damaged tap on sink opposite Bain Marie - see notes | Plumbing & Drainage | Water | 564.375 | Fail | Fail | 1 | 1 | 8.5 | 2022-11-22 12:20 | 2022-11-25 17:00 | 2022-12-05 07:00 | 2022-11-25 17:00 | 2022-12-05 15:30 |  |  | Installed a new drain for Bain Marie, had to be removable for cleaning purposes
MSA-DTAG | WA6373469 | 2 | Gilmour & Jooste Electrical | custody-ground-Check Roller Door panel for short and UPS GPO for power issue-see notes-see notes | Electrical | General Electrical | 279.08 | Pass | Fail | 0 | 0 | 8.3 | 2022-12-14 14:14 | 2022-12-19 17:00 | 2022-12-19 09:00 | 2022-12-19 17:00 | 2022-12-19 17:18 |  |  | Completed court maintenance. Investigated fault to roller door not operating down from computer system. Traced cable back from roller door. Tested controls at roller door. Found no 12v dc voltage when switching from pc. Will close job off and return with Sapio to continue.
MSA-DTWD | WA5392328 | 1 | Lane's Plumbing | In front of transformer BLD behind Homestead BLD 833 Grass area - Burst water pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 8.25 | 2022-05-03 09:23 | 2022-05-04 17:00 | 2022-05-03 09:30 | 2022-05-04 17:00 | 2022-05-03 17:45 |  |  | job completed - repaired burst water main
MSA-DTWD | WA6020135 | 2 | Techworks Electrical | Replace main lighting switch in Distribution Board DB-2 - See notes below | Electrical | Distribution Board | 546.31 | Pass | Pass | 0 | 0 | 8.2 | 2022-10-13 11:07 | 2022-10-18 17:00 | 2022-10-18 07:00 | 2022-10-18 17:00 | 2022-10-18 15:12 |  |  | Rectified hot spot on cable
MSA-DCA | WA5204441 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Jubelia - First Floor - Reflections entry door - magnetic catch been cut | Building | Fire Door | 550 | Fail | Fail | 1 | 1 | 8 | 2022-03-04 10:47 | 2022-03-04 12:47 | 2022-03-11 08:00 | 2022-03-04 14:47 | 2022-03-11 16:00 |  | WACCES | Works completed by Honeywell
MSA-DTWD | WA5231191 | 3 | Equans Mechanical Services Australia | Oil Pressure Transducer Fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 796.85 | Fail | Fail | 1 | 1 | 8 | 2022-03-15 09:42 | 2022-03-22 17:00 | 2022-03-29 08:00 | 2022-03-22 17:00 | 2022-03-29 16:00 |  |  | ..
MSA-DFES | WA5302737 | 1 | Critical Fire Protection & Training | Pillar fire hydrant at the rear of the yard has been pulled over from ground level | Plumbing & Drainage | Materials | 3319.3 | Fail | Fail | 4 | 4 | 8 | 2022-04-03 06:01 | 2022-04-04 06:01 | 2022-05-04 08:00 | 2022-04-04 06:01 | 2022-05-04 16:00
MSA-DTWD | WA5379813 | 1 | Equans Mechanical Services Australia | Rooms AT228 & AT229 - Aircon not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 7341.48 | Fail | Fail | 6 | 6 | 8 | 2022-04-21 15:15 | 2022-04-22 17:00 | 2022-05-31 08:00 | 2022-04-22 17:00 | 2022-05-31 16:00 |  |  | Attended site to complete works as per the quote supplied. Replaced the compressor and inv board on slave 1.Reclaimed all e refrigerant from the system, 44.8kg. Spoke to the contact for the job about the gas charge as it isnot noted on the units and highlighted in the quote. We advised to put back in what we take out. Replace thecompressor and inv board, pressure tested the system. Vac and recharged the system with the same charge aspulled out. Re coded back in the slave module and tested the operation of the unit. Fully operational at the time ofreport.
MSA-DTWD | WA5393997 | 2 | AWB Co. | Entrance door has damaged paint | Building | Doors | 925 | Pass | Pass | 0 | 0 | 8 | 2022-05-04 11:56 | 2022-05-09 17:00 | 2022-05-06 08:00 | 2022-05-09 17:00 | 2022-05-06 16:00 |  |  | Contractor attended and repainted door.no-one on site to sign
MSA-DTWD | WA5399229 | 2 | Equans Mechanical Services Australia | roof plant area : Chiller fault - will not reset | Refrigeration | Chiller | 4887.63 | Fail | Fail | 3 | 3 | 8 | 2022-05-09 19:41 | 2022-05-12 17:00 | 2022-05-31 08:00 | 2022-05-12 17:00 | 2022-05-31 16:00 |  |  | CONDENSER FAN MOTOR REPLACED ON CHILLER
MSA-DTWD | WA5477068 | 2 | Water2water Pty Ltd | Drinking fountain not working properly seems to run all the time | Plumbing & Drainage | Water | 377.525 | Pass | Pass | 0 | 0 | 8 | 2022-05-25 11:48 | 2022-05-30 17:00 | 2022-05-27 08:00 | 2022-05-30 17:00 | 2022-05-27 16:00 |  |  | REPLACED BUBBLER, TAP ADAPTER & NIPPLE. ALL OKAY ON DEPARTURE.
MSA-DTWD | WA5487416 | 2 | Precise Air Group | C 108 Kitchen - Ac not working in the kitchen area - "clean filter" is showing on controller | Air Conditioning | Room Air Conditioners | 3681.34 | Fail | Fail | 13 | 13 | 8 | 2022-06-01 14:59 | 2022-06-07 17:00 | 2022-09-08 08:00 | 2022-06-07 17:00 | 2022-09-08 16:00 |  |  | Faulty parts swapped out as per quote, unit operating ok
MSA-DCA | WA5656395 | 1 | Precise Air Group | Kitchen AC Unit is not producing cold air | Air Conditioning | Room Air Conditioners | 1869.32 | Fail | Fail | 11 | 11 | 8 | 2022-07-18 13:39 | 2022-07-19 17:00 | 2022-10-03 08:00 | 2022-07-19 17:00 | 2022-10-03 16:00 |  |  | Gas leak completed as per quote
MSA-MRWA | WA5764729 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Failed Telescopic exhaust duct | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 8 | 2022-08-18 14:30 | 2022-08-25 17:00 | 2022-08-22 08:00 | 2022-08-25 17:00 | 2022-08-22 16:00 |  | WCAPPR | Attended call, found fan had tripped overload. Reset. Non operational. Went to inspect was unable to find safe access. Informed office and inspected area with Craig.
MSA-DTWD | WA5827151 | 1 | Equans Mechanical Services Australia | Level 1 - main corridor next T118 - Air conditioning water leak overnight in ceiling void | Air Conditioning | Room Air Conditioners | 2936.21 | Fail | Fail | 7 | 7 | 8 | 2022-09-01 08:27 | 2022-09-02 17:00 | 2022-10-23 08:00 | 2022-09-02 17:00 | 2022-10-23 16:00 |  |  | Carry out take 5 and sign onto swms.Carry out repair of leaking HW piping on level one as per BRAF.Refilled and bleed of air, check for leaks-ok.Completed Paperwork
MSA-DFES | WA6534224 | 1 | Critical Fire Protection & Training | By back Gate - Above ground Hydrant leaking by back gate.AMS1296006 | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 1571.13 | Fail | Fail | 1 | 1 | 8 | 2023-02-06 10:26 | 2023-02-07 17:00 | 2023-02-17 08:00 | 2023-02-07 17:00 | 2023-02-17 16:00 |  | WACCES
MSA-DTWD | WA6674444 | 2 | Australian HVAC Services Pty. Ltd. | Evaporative air is not working | Air Conditioning | Room Air Conditioners | 1533.24 | Pass | Pass | 0 | 0 | 8 | 2023-02-27 10:04 | 2023-03-02 17:00 | 2023-02-27 11:00 | 2023-03-02 17:00 | 2023-02-27 19:00
MSA-DTAG | WA5176962 | 3 | AWB Co. | G Floor - Toilet - Lights in male public toilet have failed – opposite caffisimo | Electrical | Lighting, Internal | 1117.74 | Pass | Pass | 0 | 0 | 8 | 2022-02-21 14:49 | 2022-02-28 17:00 | 2022-02-26 07:00 | 2022-02-28 17:00 | 2022-02-26 15:00 |  |  | Need to get a copy of electrical drawings for site as no one knows where they are
MSA-DTAG | WA5495026 | 3 | Midolo Building Services | Level 14 - Room 14.5 - Replace water damaged ceiling tiles | Building | General Building | 1265.49 | Pass | Pass | -1 | -1 | 8 | 2022-06-08 09:03 | 2022-06-15 17:00 | 2022-06-10 07:00 | 2022-06-15 17:00 | 2022-06-10 15:00 |  |  | DAMAGED CEILING TILES REPLACED
MSA-DTAG | WA5578754 | 1 | Sapio Pty Ltd | Car park - Custody Control room -Electronic doors not working correctly - See notes below | Security | Access Control | 269 | Pass | Pass | 0 | 0 | 8 | 2022-07-01 16:04 | 2022-07-04 17:00 | 2022-07-04 08:30 | 2022-07-04 17:00 | 2022-07-04 16:30 |  |  | Returned to site afterwards and re-tested all reported doors. Found all doors are having Mortice type of electronic locksand will not unlock if door's handle has been pressed.
MSA-DTWD | WA5677549 | 3 | AWB Co. | Men’s toilet - Repair, Patch and paint water damaged ceiling above balcony | Building | Ceiling | 954.955 | Pass | Pass | 0 | 0 | 8 | 2022-07-25 15:41 | 2022-08-01 17:00 | 2022-07-29 07:30 | 2022-08-01 17:00 | 2022-07-29 15:30 |  |  | Painting works completed as per Work Order 28469.
MSA-DTAG | WA5839566 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 10 - Registry of Births, Deaths and Marriages - Main Hot water system faulty - See notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 1068.527 | Pass | Pass | 0 | 0 | 8 | 2022-07-26 14:51 | 2022-07-27 17:00 | 2022-07-27 07:00 | 2022-07-27 17:00 | 2022-07-27 15:00 |  |  | Works completed under original work order WA5679544
MSA-DTWD | WA5993452 | 3 | AWB Co. | Courtyard behind RM114 Beauty - Paint on handrails peeling off | Painting | External | 845.8 | Pass | Pass | 0 | 0 | 8 | 2022-10-05 10:27 | 2022-10-12 17:00 | 2022-10-12 07:00 | 2022-10-12 17:00 | 2022-10-12 15:00 |  |  | painting works completed
MSA-DTWD | WA6154326 | 2 | AWB Co. | (Perth 27 Museum) - Verandah - Iron balustrade and handrails need attention - See notes below | Painting | External | 9905.52 | Fail | Fail | 3 | 3 | 8 | 2022-11-07 11:54 | 2022-11-10 17:00 | 2022-11-28 07:00 | 2022-11-10 17:00 | 2022-11-28 15:00 |  |  | Works completed
MSA-DTWD | WA6178831 | 1 | Australian Airconditioning Services Pty Ltd | 6D27 - Dust extraction system low vacuum. Possible blockage | Air Conditioning | Room Air Conditioners | 1998.84 | Fail | Fail | 0 | 0 | 8 | 2022-11-14 13:54 | 2022-11-15 17:00 | 2022-11-17 07:30 | 2022-11-15 17:00 | 2022-11-17 15:30 |  |  | Arrived and found EWP is required to inspect.Returned with EWP. Found small restrictions and cleared near work benches. No major restrictions in duct work suction is now working.
MSA-DTWD | WA6229204 | 3 | AWB Co. | Brick wall is stained and unable to be cleaned and requires repainting | Painting | Internal | 1368.42 | Fail | Fail | 1 | 1 | 8 | 2022-11-18 09:28 | 2022-11-25 17:00 | 2022-12-02 07:00 | 2022-11-25 17:00 | 2022-12-02 15:00 |  |  | painting works completed
MSA-DTWD | WA6360719 | 3 | AWB Co. | Storeroom - 500mm x 500 mm hole in ceiling needs painting | Painting | Internal | 1698.42 | Fail | Fail | 8 | 8 | 8 | 2022-12-07 13:24 | 2022-12-14 17:00 | 2023-02-10 07:00 | 2022-12-14 17:00 | 2023-02-10 15:00 |  |  | Works completed
MSA-DTWD | WA6426127 | 3 | AWB Co. | Garage west entrance - Bollards and rails pint damaged and peeling | Painting | External | 3678.42 | Fail | Fail | 0 | 0 | 8 | 2023-01-12 14:48 | 2023-01-19 17:00 | 2023-01-20 07:00 | 2023-01-19 17:00 | 2023-01-20 15:00
MSA-DFES | WA6519172 | 3 | MALCOLM THOMPSON PUMPS PTY LTD | Ground level - Top Dam - relief valve needs replacing | Plumbing & Drainage | Water |  | Fail | Fail | 3 | 3 | 8 | 2023-01-25 13:30 | 2023-02-02 17:00 | 2023-02-21 06:00 | 2023-02-02 17:00 | 2023-02-21 14:00
MSA-DFES | WA5491504 | 1 | Anvil Doors | Daglish FS- engine room panel lift door not on operation | Carpentry | Materials | 3044.56 | Pass | Pass | 0 | 0 | 7.9667 | 2022-06-04 12:35 | 2022-06-07 17:00 | 2022-06-04 14:47 | 2022-06-07 17:00 | 2022-06-04 22:45 |  |  | Impact Damage. Since last service. There has been damage done to door. Evidence suggests that door closed onto an unknown object.Motor and power has been isolated and door is operational on manual only.Controllers will need replacement with power supplyDamage will need to be quoted for repairs.Please see attached BRAF, Quote and service reportsQuoted works are now complete. This will be Quoted in accordance with Quote and Braf submitted.
MSA-DCA | WA5190089 | 1 | Critical Fire Protection & Training | Leaking sprinkler pipe in mechanical plantroom 2, above return air 1A 01. | Fire Protection Services | Sprinkler Systems | 1222.3 | Fail | Fail | 2 | 2 | 7.8667 | 2022-02-24 10:40 | 2022-02-25 17:00 | 2022-03-10 08:00 | 2022-02-25 17:00 | 2022-03-10 15:52 |  |  | Attended site and replaced section of corroded sprinkler pipe as per approved BRAF.
MSA-DTWD | WA6020132 | 2 | Techworks Electrical | Level 1 - Plant Room 2 damaged dust collector - See notes below | Electrical | Distribution Board | 518.27 | Pass | Pass | 0 | 0 | 7.7667 | 2022-10-13 11:00 | 2022-10-18 17:00 | 2022-10-18 07:44 | 2022-10-18 17:00 | 2022-10-18 15:30 |  |  | Rectified hot spots on cable
MSA-DTWD | WA5520431 | 1 | M Construction (WA) | West end Fire escape exit area - fire escape door has raised/ uneven pavers exiting the building | Flooring | Concrete | 331.46 | Pass | Pass | 0 | 0 | 7.75 | 2022-06-15 09:49 | 2022-06-16 17:00 | 2022-06-16 07:00 | 2022-06-16 17:00 | 2022-06-16 14:45 |  |  | Lifted raised pavers laid a new dust bed to tbe level. Relaid pavers and filled gaps with sand filler.
MSA-DTWD | WA5098564 | 1 | JEM Carpentry | Please replace faulty eave lining at front of house and remove debris | Carpentry | Timber (all types) |  | Fail | Fail | 0 | 0 | 7.5 | 2022-02-01 10:15 | 2022-02-02 17:00 | 2022-02-04 09:30 | 2022-02-02 17:00 | 2022-02-04 17:00 |  |  | Job completed - fixed of eaves sheet - replaced and painted
MSA-DTAG | WA5288702 | 3 | FSA (WA) Pty Ltd | See details below: | Fire Protection Services | Fire Protection - Monitor System | 345.18 | Pass | Pass | -1 | -1 | 7.5 | 2022-03-23 12:37 | 2022-03-30 17:00 | 2022-03-26 06:30 | 2022-03-30 17:00 | 2022-03-26 14:00 |  |  | Attend site to isolate fire panel for works by HVAC Australia. Isolated multiple zones and notified security monitoring.6:30am to 7:30amRe attended site to de-isolate fire panel and clear system. Reset and cleared system and all is ok. Notified security monitoring and all is back online.1pm to 2pm
MSA-DCA | WA5380563 | 2 | FCT SURFACE CLEANING | Ground Level - Various Locations – Graffiti - See Additional Comments | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 7.5 | 2022-04-22 13:37 | 2022-04-28 17:00 | 2022-04-27 06:00 | 2022-04-28 17:00 | 2022-04-27 13:30 |  |  | removal graffiti
MSA-DFES | WA5534841 | 3 | Protek 24/7 Building & Maintenance | Administration - Operational Delivery - Door is stuck | Building | Doors | 349 | Pass | Pass | 0 | 0 | 7.5 | 2022-06-16 14:53 | 2022-06-23 17:00 | 2022-06-22 07:30 | 2022-06-23 17:00 | 2022-06-22 15:00 |  |  | Planed sticking doors in office
MSA-DTWD | WA5588930 | 3 | AWB Co. | Level 1 - Exterior - pavers ruptured at front of A Block West End | Flooring | Concrete | 1170.42 | Fail | Fail | 4 | 4 | 7.5 | 2022-07-08 08:24 | 2022-07-15 17:00 | 2022-08-11 07:00 | 2022-07-15 17:00 | 2022-08-11 14:30 |  |  | Scope of Works:Strip back numerous areas of paving ,Remove roots ,Replace sand screed,Relay paving to remove trip hazards,Supply 50 pavers to replace broken onesJob completed
MSA-DTWD | WA5973159 | 3 | AWB Co. | Door to 129 damaged - missing a chunk –Patch or replace & Paint | Building | Doors | 831.275 | Pass | Pass | 0 | 0 | 7.5 | 2022-09-21 11:10 | 2022-09-29 17:00 | 2022-09-29 07:00 | 2022-09-29 17:00 | 2022-09-29 14:30 |  |  | Removed door from the door frame, removed and replaced damaged strip, sealed with an undercoat, 2 coats gloss
MSA-DFES | WA5977083 | 3 | Australian HVAC Services Pty. Ltd. | Air con vent in Lecture room 6 has fallen from the ceiling - see notes below | Air Conditioning | Room Air Conditioners | 353.9 | Pass | Pass | -1 | -1 | 7.5 | 2022-09-27 13:37 | 2022-10-04 17:00 | 2022-09-29 07:00 | 2022-10-04 17:00 | 2022-09-29 14:30 |  |  | Rhys Hall (29/09/2022) - Work Notearrived on site and got told was supposed to call before arrival, the room is currently occupied so will re attend after 12.Arrived back on site and signed in etc.After investigating the air vent it seems one of the four the brackets had come of, I re attached and drilled then riveted all 4 brackets.I then re installed the air vent.Cleaned up packed up tools and then signed out and left site.
MSA-DCA | WA5995685 | 3 | Techworks Electrical | Ground - Exhibition and Design Building - Faulty Lights - See notes below | Electrical | Lighting, External | 230.88 | Pass | Pass | 0 | 0 | 7.5 | 2022-10-06 14:49 | 2022-10-13 17:00 | 2022-10-10 08:30 | 2022-10-13 17:00 | 2022-10-10 16:00 |  |  | Replaced various lights within admin building for new led panels
MSA-DTWD | WA6008482 | 3 | AWB Co. | Damaged brick paving at the eastern entrance - see notes below | Flooring | Concrete | 3898.42 | Fail | Fail | 3 | 3 | 7.5 | 2022-10-11 15:22 | 2022-10-18 17:00 | 2022-11-09 07:00 | 2022-10-18 17:00 | 2022-11-09 14:30 |  |  | paving works completed
MSA-DCA | WA6391655 | 1 | SCAVENGER SUPPLIES PTY LTD | Hackett Hall - Ground Floor - Studio 1 - leaking fire sprinkler | Fire Protection Services | Sprinkler Systems | 2103.78 | Pass | Pass | 0 | 0 | 7.5 | 2022-12-22 14:44 | 2022-12-23 17:00 | 2022-12-23 08:00 | 2022-12-23 17:00 | 2022-12-23 15:30 |  | WACCES | WORKS COMPLETED 23/12/22 - BRAF SENT TO WASC - 3/1/23
MSA-DTWD | WA6426136 | 3 | AWB Co. | Francis St Entrance - Old sign damaged and falling over | Building | General Building | 956.58 | Fail | Fail | 1 | 1 | 7.5 | 2023-01-12 14:56 | 2023-01-19 17:00 | 2023-01-24 02:30 | 2023-01-19 17:00 | 2023-01-24 10:00
MSA-DTWD | WA6489543 | 3 | AWB Co. | All science labs- replace ceiling tiles in A Block Level 3 Laboratory operations | Building | Ceiling | 1983.32 | Pass | Pass | 0 | 0 | 7.5 | 2023-01-18 14:28 | 2023-01-25 17:00 | 2023-01-24 07:00 | 2023-01-25 17:00 | 2023-01-24 14:30
MSA-DCA | WA6516130 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 in fault | Refrigeration | Chiller | 596.84 | Pass | Pass | 0 | 0 | 7.5 | 2023-01-23 09:16 | 2023-01-24 17:00 | 2023-01-23 09:30 | 2023-01-24 17:00 | 2023-01-23 17:00
MSA-DTWD | WA6572770 | 1 | WESTERN IRRIGATION PTY LTD | Near Simpson Ave - Reticulation stations 10 & 11 are not opening (see notes) | Plumbing & Drainage | Drainage | 1865.3 | Pass | Pass | 0 | 0 | 7.5 | 2023-02-14 08:40 | 2023-02-15 17:00 | 2023-02-15 07:00 | 2023-02-15 17:00 | 2023-02-15 14:30
MSA-DTWD | WA6538102 | 0 | Techworks Plumbing | All of L Block Toilets overflowing | Plumbing & Drainage | Toilets/Cisterns | 15523.8 | Fail | Fail | 3 | 3 | 7.4833 | 2023-02-07 14:37 | 2023-02-07 16:37 | 2023-03-02 07:00 | 2023-02-07 18:37 | 2023-03-02 14:29
MSA-DTWD | WA6130081 | 2 | JEM Carpentry | BLD 843B - 5 Faulty roof sheets | Roofing | Metal Roofing |  | Pass | Pass | -1 | -1 | 7.25 | 2022-10-28 09:42 | 2022-11-02 17:00 | 2022-10-28 09:45 | 2022-11-02 17:00 | 2022-10-28 17:00 |  |  | fixed roof due to hail damage
MSA-DTWD | WA6256926 | 2 | Techworks Plumbing | N Block ladies toilet - Damaged toilet may need replacing - see notes | Plumbing & Drainage | Toilets/Cisterns | 1296.9 | Pass | Pass | -1 | -1 | 7.2167 | 2022-11-23 15:24 | 2022-11-28 17:00 | 2022-11-24 10:30 | 2022-11-28 17:00 | 2022-11-24 17:43 |  |  | Arrived on sight signed in at front desk found N block female toilets and broken pans, cisterns were both faulty so replaced both toilets and new cisterns new isolation valves & flexis, installed 2 new pan adapters as old ones were perished, cleaned up sight and signed out signature slip signed by mike facility’s manager
MSA-DTWD | WA5395171 | 1 | SCAVENGER SUPPLIES PTY LTD | All Blocks - EWIS System - Evacuation warning system not heard in various blocks- see notes below | Fire Protection Services | Fire Protection - Monitor System | 758.35 | Pass | Pass | 0 | 0 | 7.1833 | 2022-05-05 11:02 | 2022-05-06 17:00 | 2022-05-06 08:00 | 2022-05-06 17:00 | 2022-05-06 15:11 |  |  | ATTENDED 6/5/22 - Note our technicians have spoken with our School contact Dennis Jardine - re: requesting another Work order be issued as our technicians need to re-attend for further investigation - see job report attached. Please can you issue another work order for them to attend next week.All blocks work except for H and G block, investigation still ongoing
MSA-DTWD | WA6255378 | 3 | AWB Co. | Walls to be patched due to impact and drill holes in walls and repainted | Building | Internal Walls | 1489.42 | Fail | Fail | 0 | 0 | 7.15 | 2022-11-23 10:03 | 2022-11-30 17:00 | 2022-12-02 07:00 | 2022-11-30 17:00 | 2022-12-02 14:09 |  |  | painting works completed
MSA-DTWD | WA5693774 | 3 | Equans Mechanical Services Australia | L3-boiler room-Repair Solar Hot Water system to D Block Green Skills | Plumbing & Drainage | Water | 309.69 | Pass | Pass | 0 | 0 | 7.0333 | 2022-08-04 15:14 | 2022-08-11 17:00 | 2022-08-09 08:00 | 2022-08-11 17:00 | 2022-08-09 15:02 |  |  | SEE EMAIL
MSA-DTWD | WA5286777 | 2 | JEM Carpentry | Muresk sign at corner of Muresk Road - Muresk direction sign faulty | Carpentry | Materials |  | Fail | Fail | 0 | 0 | 7 | 2022-03-22 08:10 | 2022-03-25 17:00 | 2022-03-28 07:30 | 2022-03-25 17:00 | 2022-03-28 14:30 |  |  | Sign damaged by vehicle and frame damaged beyond repair.
MSA-DTWD | WA5305246 | 2 | WESTERN IRRIGATION PTY LTD | F Block - Ground - Station 5 reticulation loss of power - Retic station 5 has lost power | Landscaping & Gardening | Grounds Maintenance | 973.23 | Fail | Fail | 1 | 1 | 7 | 2022-04-05 13:25 | 2022-04-08 17:00 | 2022-04-12 06:30 | 2022-04-08 17:00 | 2022-04-12 13:30 |  |  | Technician found tree roots had damaged the solenoid wires, ran new wires in conduit. Test for correct operation.
MSA-DCA | WA5487146 | 2 | Techworks Plumbing | Level 2 - UAT - Faulty Toilet seat - minor repairs to toilet seat | Plumbing & Drainage | Toilets/Cisterns | 311.67 | Pass | Pass | -1 | -1 | 7 | 2022-06-01 12:48 | 2022-06-07 17:00 | 2022-06-02 06:30 | 2022-06-07 17:00 | 2022-06-02 13:30 |  |  | Re tightened toilet
MSA-DTWD | WA5589321 | 2 | Milners Tree Solutions Pty Ltd | Block 10 - Grounds - Various trees have dead branches hanging off | Landscaping & Gardening | Tree Lopping | 5200 | Fail | Fail | 6 | 6 | 7 | 2022-07-08 12:01 | 2022-07-13 17:00 | 2022-08-25 06:30 | 2022-07-13 17:00 | 2022-08-25 13:30 |  |  | tree removals, stump grinding, pruning
MSA-DCA | WA5722529 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 Plant room - Alarm is going off for the aircon Chiller | Air Conditioning | Materials | 1798.765 | Fail | Fail | 1 | 1 | 7 | 2022-08-13 10:28 | 2022-08-13 12:28 | 2022-08-23 03:30 | 2022-08-13 14:28 | 2022-08-23 10:30 |  |  | Assisted the on call technician, remotely logged into the ETS this morning 13/8/22 and found all chillers off. Supply water temperature to AGWA was at 14.0 degrees and did not change over to local automatically. I have manualled AGWA into local for now and the on call technician has confirmed the central plant is operating as per normal at AGWA. The alarms this morning seems to be generated by a chiller staging issue at the ETS. I have put chiller 1 back to auto but not sure if Honeywell have replaced and calibrated the sensors for this chiller. Chiller 4 is handling the load easily at the moment, but chiller 2 and 3 try to start up randomly even when chiller 4 is managing the load. I will monitor supply water temperatures to the Museum and engage Honeywell.18/8/22Honeywell have confirmed there is still an on going issue with one of the main isolation chw actuators. Quote to be sent in the coming days.AGWA chw system left in local until new actuator is replaced.
MSA-DCA | WA5791289 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Humidity alarm alerted - AC 2 Gallery 2578 - value is 43.4375 | Building | Materials | 830.525 | Pass | Pass | 0 | 0 | 7 | 2022-08-23 02:17 | 2022-08-23 17:00 | 2022-08-23 03:30 | 2022-08-23 17:00 | 2022-08-23 10:30 |  |  | After hours callout 23/8/22 - ChuanAttended site after a call out. Signed in and gain to access AC 2 humidifier not working. Check FCU 2 fan it was operating, yes ok. check the supply heated water it was working, checked chilled water. Confirmed everything is working. Informed site service Technician of my finding. Requires monitoring and or further investigation. 23/8/22 - Jason Reattended call and carried out further checks. Checked and tested operation of all the heating and chilled water actuators - all driving correctly. No central plant equipment was in fault at the time of call out. Was notified that the centenary link doors were open and possibly bringing in outside air to the gallery. Will monitor this and further investigate and test.
MSA-DFES | WA5961479 | 1 | Go Doors | Main Entry - Front right hand roller door - Drive shaft has come off - Door has come off tracks | Building | Roller Shutters | 2388.72 | Pass | Pass | 0 | 0 | 7 | 2022-09-19 08:11 | 2022-09-20 17:00 | 2022-09-19 11:00 | 2022-09-20 17:00 | 2022-09-19 18:00 |  |  | Completed works. Please see attachments.
MSA-DTAG | WA6155504 | 3 | Midolo Building Services | External -Governors Lane - Several potholes in driveway need to be sealed & filled in - OSH Issue | Paving & Roadworks | Paving | 1885.9 | Fail | Fail | 3 | 3 | 7 | 2022-11-08 11:06 | 2022-11-15 17:00 | 2022-12-08 08:00 | 2022-11-15 17:00 | 2022-12-08 15:00 |  | WACCES | POTHOLES FILLED
MSA-MRWA | WA6402206 | 0 | EQUANS Mechanical Services (WA) Pty Limited | x2 Server CRAC units - Hardwire fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1436.03 | Pass | Fail | 0 | 0 | 7 | 2023-01-05 08:52 | 2023-01-05 10:52 | 2023-01-05 09:00 | 2023-01-05 12:52 | 2023-01-05 16:00
MSA-DTWD | WA6526809 | 3 | AWB Co. | C300 - hallway - x15 lights need replacing | Electrical | Lighting, Internal | 1341.97 | Pass | Pass | 0 | 0 | 7 | 2023-02-01 10:52 | 2023-02-08 17:00 | 2023-02-07 08:00 | 2023-02-08 17:00 | 2023-02-07 15:00
MSA-DCA | WA5105827 | 3 | Techworks Electrical | 4 x Fluro baton lights in Fiji room have failed. Replace with LED | Electrical | Lighting, Internal | 1424.77 | Pass | Pass | 0 | 0 | 7 | 2022-02-04 14:48 | 2022-02-11 17:00 | 2022-02-09 08:30 | 2022-02-11 17:00 | 2022-02-09 15:30 |  |  | Replaced lights for new led panel lights and frames. re-wired where suitable
MSA-DTAG | WA5469001 | 1 | FSA (WA) Pty Ltd | Retrospective Work Order - Pump Room - DO NOT ATTEND - see notes below | Fire Protection Services | Fire Protection - Monitor System | 1386.46 | Pass | Pass | 0 | 0 | 7 | 2022-05-20 06:45 | 2022-05-20 17:00 | 2022-05-20 07:00 | 2022-05-20 17:00 | 2022-05-20 14:00 | 1 |  | Attend site investigate low pressureFound jacking pump check valve passingReplaced jacking pump check valve
MSA-DTWD | WA5477077 | 3 | AWB Co. | Paint over graffiti - colour to match existing | Building | Internal Walls | 870 | Pass | Pass | -1 | -1 | 7 | 2022-05-25 11:53 | 2022-06-01 17:00 | 2022-05-26 07:00 | 2022-06-01 17:00 | 2022-05-26 14:00 |  |  | Paint over graffiti - colour to match existingsign slip and jsa on same attachment
MSA-DTWD | WA5862268 | 3 | AWB Co. | 30Ab: Undercover carpark lights not working | Electrical | Lighting, External | 1490.14 | Pass | Pass | -1 | -1 | 7 | 2022-09-13 15:26 | 2022-09-20 17:00 | 2022-09-15 08:30 | 2022-09-20 17:00 | 2022-09-15 15:30 |  |  | Cbus technician required to check timers on exterior lights
MSA-MRWA | WA5970619 | 0 | Automatic Fire Protection (ARA) | level 1 - Fire water pipe - Leaking from level 1 to ground floor | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 1904.23 | Pass | Fail | 0 | 0 | 7 | 2022-09-20 08:29 | 2022-09-20 10:29 | 2022-09-20 08:30 | 2022-09-20 12:29 | 2022-09-20 15:30 |  |  | Attended site for leaking sprinkler pipelocated a 80mm sprinkler main that was leaking from a coupling that was quite rustedisolated and drained sprinkler installationback on site ,drained excess water from pipe workcut out and replaced 400mm of 80mm mainsrefilled sprinkler installation and cleared fip
MSA-DTWD | WA6148999 | 1 | Lane's Plumbing | In front of house 801 near large tree-Burst waterpipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 7 | 2022-11-04 11:07 | 2022-11-07 17:00 | 2022-11-04 11:30 | 2022-11-07 17:00 | 2022-11-04 18:30 |  |  | Repairs to burst water pipe
MSA-DTWD | WA6208159 | 2 | AWB Co. | Multiple lights not working in main area of the library | Electrical | Lighting, Internal | 1498.645 | Pass | Pass | -1 | -1 | 7 | 2022-11-17 13:46 | 2022-11-22 17:00 | 2022-11-18 08:30 | 2022-11-22 17:00 | 2022-11-18 15:30 |  |  | Attended site and signed in. Liaised with FM about works going ahead. Collected site keys. Went through and counted up how many tubes were required to complete job. Got parts. Went through and replaced all lights as per lighting list. Replaced 2x ballast in gym office. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6426060 | 1 | Equans Mechanical Services Australia | Chiller Plant room - Chiller 1 in lockout | Air Conditioning | Building HVAC Maintenance (Major Plant) | 399.78 | Pass | Pass | 0 | 0 | 7 | 2023-01-12 14:09 | 2023-01-13 17:00 | 2023-01-13 07:00 | 2023-01-13 17:00 | 2023-01-13 14:00
MSA-DCA | WA6503727 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Martime Plant Room - BMS in alarm (see notes) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1630.11 | Pass | Pass | 0 | 0 | 7 | 2023-01-19 10:59 | 2023-01-20 17:00 | 2023-01-20 07:00 | 2023-01-20 17:00 | 2023-01-20 14:00
MSA-DCA | WA6527957 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Wearhouse - Molecular Lab 2 - Temperature high, panel says 23 but it’s warming up | Air Conditioning | Evaporative Coolers | 1034.72 | Pass | Pass | 0 | 0 | 7 | 2023-02-02 07:52 | 2023-02-02 17:00 | 2023-02-02 08:30 | 2023-02-02 17:00 | 2023-02-02 15:30
MSA-DCA | WA6151645 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 & 2 in fault | Refrigeration | Chiller | 281.53 | Pass | Fail | 0 | 0 | 6.95 | 2022-11-07 08:02 | 2022-11-07 10:02 | 2022-11-07 08:02 | 2022-11-07 12:02 | 2022-11-07 14:59 |  |  | Reset both chillers and recorded faults. Took photos of chiller alarm interface screen. Monitored operation of both chillers for some time no further faults at this time.
MSA-DTAG | WA5479203 | 1 | Sapio Pty Ltd | Ground - Registry - Staff back door – Gallagher system beeping - see notes below | Security | Access Control | 482.22 | Pass | Pass | 0 | 0 | 6.9167 | 2022-05-27 08:04 | 2022-05-30 17:00 | 2022-05-27 08:05 | 2022-05-30 17:00 | 2022-05-27 15:00 |  |  | Installed new lock and tested
MSA-DTAG | WA5656605 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Ladies toilet - Toilet seat in first toilet is broken. Seat lifts away from toilet | Plumbing & Drainage | Toilets/Cisterns | 196.165 | Pass | Pass | 0 | 0 | 6.8333 | 2022-07-18 15:14 | 2022-07-21 17:00 | 2022-07-20 06:40 | 2022-07-21 17:00 | 2022-07-20 13:30 |  |  | Tightened lhs toilet seat
MSA-DTWD | WA5088780 | 2 | Precise Air Group | Plantroom No 1 - AHU 2 :Zone two sensor is not working - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 789.27 | Fail | Fail | 1 | 1 | 6.7667 | 2022-01-24 18:55 | 2022-01-28 17:00 | 2022-02-07 07:53 | 2022-01-28 17:00 | 2022-02-07 14:39 |  |  | Arrived on site and signed in as necessary. Due to multiple zone sensors causing issue impossible shorting between sensors and the device or possible faulty device would recommend in gauging control subcontractor to attend and further diagnose controls issues. Also looked into issue of outside air damper open on ahu reported by facilities. Damp it closed as per BMS command. All ok.
MSA-DCA | WA5215731 | 1 | Automatic Fire Protection (ARA) | Isolation needs to be carried out on all detectors | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 6.75 | 2022-03-10 16:27 | 2022-03-11 17:00 | 2022-03-11 06:30 | 2022-03-11 17:00 | 2022-03-11 13:15 |  |  | Isolated zones 1-20 for worksJN 11/3/22Deisolated above zones. No one from Programmed on site to sign got signature from arts tenancy.
MSA-DTWD | WA5976988 | 3 | AWB Co. | HVAC Plant rooms-light tubes need replacing | Electrical | Lighting, Internal | 1245.1275 | Pass | Pass | 0 | 0 | 6.75 | 2022-09-27 12:56 | 2022-10-04 17:00 | 2022-10-03 07:00 | 2022-10-04 17:00 | 2022-10-03 13:45 |  |  | Lots of emergency light fixtures need replacing in stairwells and plant rooms
MSA-DCA | WA5413389 | 1 | EQUANS Mechanical Services (WA) Pty Limited | BMS nonresponsive, unable to program events. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 188.375 | Fail | Fail | 0 | 0 | 6.5833 | 2022-05-12 10:44 | 2022-05-13 17:00 | 2022-05-16 09:20 | 2022-05-13 17:00 | 2022-05-16 15:55 |  |  | Carried out inspection of BMS and time schedules program for special events. On investigation it was identified that event dates had been entered into the wrong part of program causing the time clock enterys to lock out. On confirmation with Icon Logic site BMS contractor confirmed findings. Time incorrect data cleared from time clock boxes and normal system function has now resumed. Confirmed events are able to be programmed. Work area left tidy.
MSA-DTWD | WA5459826 | 1 | SCAVENGER SUPPLIES PTY LTD | Check Fire lines for for leak in ceiling | Fire Protection Services | Sprinkler Systems | 740.58 | Pass | Pass | 0 | 0 | 6.5167 | 2022-05-18 09:10 | 2022-05-19 17:00 | 2022-05-18 09:21 | 2022-05-19 17:00 | 2022-05-18 15:52 |  |  | COMPLETED 18/05/2022OTHER CONTRACTOR CAUSED THIS PROBLEM.oTHER WORK COMPLETED WHILE ON SITE RELATED TO THIS WORK. SEE JANINE GOLDSWORTHY
MSA-DCA | WA5038616 | 3 | FCT SURFACE CLEANING | Ground - PICA and around Fiji room and car park doors - graffiti | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 6.5 | 2022-01-17 15:28 | 2022-01-24 17:00 | 2022-01-18 06:30 | 2022-01-24 17:00 | 2022-01-18 13:00 |  |  | job completed - Attended site and removed various pieces of graffiti from the Perth Cultural Centre Precinct.
MSA-DTAG | WA5091256 | 1 | Total Security Systems Pty Ltd | Door control monitor in CCR has failed (possible warranty) | Security | Security Management System | 1088.88 | Pass | Pass | 0 | 0 | 6.5 | 2022-01-27 07:30 | 2022-01-27 17:00 | 2022-01-27 09:30 | 2022-01-27 17:00 | 2022-01-27 16:00 |  |  | 27/1/2022 - Michael Higginbotham - 9.30am to 4pmAttended site and checked monitor to faults, checked cabling. Confirmed issue was user error. The F11 button on the keyboard had been pressed which changed the layout, showed site they needed to press escape to get back to main layout. Did a quick run-through with staff on how to interact with indigovision menus, mounted TV on adjustable bracket as they keep knocking the connection. Job complete.
MSA-DTAG | WA5549096 | 3 | Australian HVAC Services Pty. Ltd. | Plantroom 3 - Abnormal noise emitting from A/C plantroom 3 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 472.79 | Pass | Pass | -1 | -1 | 6.5 | 2022-06-17 12:49 | 2022-06-24 17:00 | 2022-06-20 08:00 | 2022-06-24 17:00 | 2022-06-20 14:30 |  |  | Attend site. Access plantroom 3 and check noise coming from AC unit. Dismantle unit and found Vbelt to have developed a crack causing a thumping noise. Remove belt from unit and install spare belt. Tighten and allign new belt and check operation. Found unit condenser water to hotter than normal. Access cooling tower and check operation. Found no power to cooling tower. Found there to be a new circulation pump installed. Access switchboard in ground level plantroom 6, found circuit breaker serving cooling tower to be tripped. Reset breaker and found to now have poer to cooling tower. Check plant and found AC 2 serving court 10 and 11 not running. Access plantroom and swith to manual operation, found to start. Access bms and check time schedule, found to be normal and there is an enable to start. Click on the enable and set to auto, found unit to now start. This would have been caused by the morning power loss. Check over the rest of the plant and found operating like normal.
MSA-DTWD | WA6256973 | 2 | JEM Carpentry | Ground - Lounge - Leaking wall | Building | Internal Walls |  | Fail | Fail | 2 | 2 | 6.5 | 2022-11-24 10:47 | 2022-11-29 17:00 | 2022-12-13 11:00 | 2022-11-29 17:00 | 2022-12-13 17:30 |  |  | Completed
MSA-DTWD | WA6509309 | 2 | M Construction (WA) | Broken side bed curtains | Building | Curtains & Blinds | 677.88 | Pass | Pass | 0 | 0 | 6.5 | 2023-01-20 09:31 | 2023-01-25 17:00 | 2023-01-23 06:30 | 2023-01-25 17:00 | 2023-01-23 13:00
MSA-DTWD | WA6516829 | 2 | Australian Airconditioning Services Pty Ltd | Faulty thermostat on free standing fridge | Refrigeration | Refrigerators | 819.34 | Pass | Pass | 0 | 0 | 6.5 | 2023-01-23 15:46 | 2023-01-27 17:00 | 2023-01-24 08:00 | 2023-01-27 17:00 | 2023-01-24 14:30
MSA-DCA | WA5174716 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Nosie coming from the boilers | Mechanical Services | Boilers | 829.375 | Pass | Pass | 0 | 0 | 6.5 | 2022-02-21 08:27 | 2022-02-22 17:00 | 2022-02-21 13:00 | 2022-02-22 17:00 | 2022-02-21 19:30 |  |  | Plant now operating as required.
MSA-DTWD | WA5215609 | 2 | ECO PLUMBING AND GAS PTY LTD | drain is blocked | Plumbing & Drainage | Water | 993.235 | Pass | Pass | 0 | 0 | 6.5 | 2022-03-10 14:16 | 2022-03-15 17:00 | 2022-03-14 08:30 | 2022-03-15 17:00 | 2022-03-14 15:00 |  |  | Cleared blockage using jetter
MSA-DTWD | WA5393885 | 1 | Equans Mechanical Services Australia | Block 7 - Cafeteria - Faulty exhaust fan in dish – possible bearings faulty | Air Conditioning | Room Air Conditioners | 1200.12 | Pass | Pass | 0 | 0 | 6.5 | 2022-05-04 10:52 | 2022-05-05 17:00 | 2022-05-05 08:30 | 2022-05-05 17:00 | 2022-05-05 15:00 |  |  | ACCESS ROOF AND INSPECT EXHAUST FAN, FOUND FAN MOTOR BEARINGS VERY NOISY. ISOLATE POWER AND REMOVE FAULTY MOTOR, INSTALL NEW FAN MOTOR. ATTEMPTED TO START UP, CIRCUIT BREAKER TRIPPED. SWITCHBOARD LABELLED INCORRECTLY, ELECTRICIAN REQUIRED TO TURN BACK ON
MSA-MRWA | WA5499136 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 Cafe - radio system and antenna are both faulty | Electrical | General Electrical | 497.775 | Pass | Pass | 0 | 0 | 6.5 | 2022-06-10 10:21 | 2022-06-17 17:00 | 2022-06-14 07:00 | 2022-06-17 17:00 | 2022-06-14 13:30 |  |  | Collected tester and gear from workshop at 07:00 and continued to site. Arrived on site 08:00. To investigate tv areal and points with bad signal, checked with tester all splitters and cabling. Will need to return to invesigate level 1 cafe radio with no signal. Left site at 13:30
MSA-DTWD | WA5567160 | 3 | AWB Co. | 3B6 - 10 faulty lights | Electrical | Lighting, Internal | 1590.59 | Fail | Fail | 3 | 3 | 6.5 | 2022-06-23 15:52 | 2022-06-30 17:00 | 2022-07-20 08:30 | 2022-06-30 17:00 | 2022-07-20 15:00 |  |  | Attended site signed in jsa completed. Removed x11 old fluro fittings. Replaced with new 40w led batterns. Updated switchboard schedule as it was incorrectly labelled by insight electrical.job completed
MSA-DTWD | WA5586733 | 2 | Lane's Plumbing | BLD 875-Burst water pipe (eaten by pigs) | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 6.5 | 2022-07-06 14:09 | 2022-07-11 17:00 | 2022-07-08 10:30 | 2022-07-11 17:00 | 2022-07-08 17:00 |  |  | job completed - repair burst water pipes at piggery
MSA-DTWD | WA5780386 | 2 | JEM Carpentry | side gate faulty | Building | Steel Fencing & Gates |  | Pass | Pass | -1 | -1 | 6.5 | 2022-08-19 10:03 | 2022-08-24 17:00 | 2022-08-19 10:30 | 2022-08-24 17:00 | 2022-08-19 17:00 |  |  | Repairs to gate
MSA-DTWD | WA6358749 | 3 | AWB Co. | Damaged ceiling and cubicle walls (see notes) | Painting | Internal | 1390.42 | Pass | Pass | -1 | -1 | 6.5 | 2022-12-06 09:48 | 2022-12-13 17:00 | 2022-12-09 07:00 | 2022-12-13 17:00 | 2022-12-09 13:30 |  |  | painting works completed
MSA-DTWD | WA6358965 | 3 | AWB Co. | Undercover courtyard - D Block Exterior - Faulty timber paneling | Building | External Walls | 756.87 | Pass | Pass | -1 | -1 | 6.5 | 2022-12-06 11:27 | 2022-12-13 17:00 | 2022-12-07 10:00 | 2022-12-13 17:00 | 2022-12-07 16:30 |  |  | Took measurements, frame built, attached to the side structures and horizontal beams were attached to the vertical beams to avoid excess damage as this is a temporary structure/Cut plywood to fit, and screwed into the frame to ensure sturdiness of the structureJSA completedJob completed
MSA-DCA | WA5018123 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Molecular lab - aircon is faulty high temperature | Air Conditioning | Room Air Conditioners | 931.39 | Pass | Fail | 0 | 0 | 6.4333 | 2022-01-14 09:07 | 2022-01-14 11:07 | 2022-01-14 10:43 | 2022-01-14 13:07 | 2022-01-14 17:09 |  |  | Atteneded site and carried out investigations of A/C package unit fault. LP trio found to be active. Carried out reset and monitored operation. LP trip occured after 10min of system operation. On fault identification gas leak found on pipe work near compressor. Isolated unit set up gas recovery equipment and carried out repairs to welded fitting. Pressure tested and once confirmed holding placed into vacuum and then restored gas charge. Normal system operation has resumed. No further action required. Work area left tidy.
MSA-DTWD | WA5164099 | 1 | Precise Air Group | P Block - p002.4- Air con is not coming on | Air Conditioning | Room Air Conditioners | 323.48 | Pass | Pass | 0 | 0 | 6.3167 | 2022-02-18 15:46 | 2022-02-21 17:00 | 2022-02-21 07:30 | 2022-02-21 17:00 | 2022-02-21 13:49 |  |  | Attended site and completed pre start paperwork andsigned in. Acessed unit in room p 02.4. Inspected system and found power pcb/power relay has failed. Failing tosend power to indoor control pcb. Due to age andcondition of system replacement of unit is recommended. System also on r22. Submitted details for quotation.
MSA-DTWD | WA6072536 | 3 | AWB Co. | Exterior courtyard - Umbrella has broken wire and pole | Furniture | Outdoor Furniture | 279.42 | Fail | Fail | 3 | 3 | 6.2667 | 2022-10-18 08:35 | 2022-10-25 17:00 | 2022-11-15 07:00 | 2022-10-25 17:00 | 2022-11-15 13:16 |  |  | Works completed
MSA-DFES | WA5499926 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Applied Training Ground - Compressor Shed - green safety light faulty - see notes below | Electrical | General Electrical | 245.27 | Pass | Pass | 0 | 0 | 6.25 | 2022-06-10 15:48 | 2022-06-13 17:00 | 2022-06-13 07:30 | 2022-06-13 17:00 | 2022-06-13 13:45 |  | WACCES | Returned to site at 13:15 to install and test 1 x light globe to spinning safety light located compressor shed. Gained access to area and installed and tested globe. Satisfied with operation, left site at 13:45
MSA-DTWD | WA6520381 | 1 | Australian Airconditioning Services Pty Ltd | Arcus free standing fridge has faulty digital display – Affecting compressor | Refrigeration | Refrigerators | 236.72 | Pass | Pass | 0 | 0 | 6.1833 | 2023-01-27 13:42 | 2023-01-30 17:00 | 2023-01-30 08:00 | 2023-01-30 17:00 | 2023-01-30 14:11
MSA-DFES | WA4993507 | 1 | Australian HVAC Services Pty. Ltd. | Sensor - AHU8 Supply temperature has failed | Air Conditioning | Building HVAC Maintenance (Major Plant) | 597.57 | Fail | Fail | 3 | 3 | 6.1667 | 2022-01-07 16:10 | 2022-01-10 17:00 | 2022-02-03 08:17 | 2022-01-10 17:00 | 2022-02-03 14:27 |  | WACCES | Picked up new sensor and attended site. Replaced failed temp sensor on ahu 8. Calibrated new sensor. Confirmed correct operation.
MSA-DFES | WA6528998 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Station Officer's Ensuite - Toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 350.9625 | Pass | Pass | 0 | 0 | 6.1333 | 2023-02-02 13:26 | 2023-02-03 17:00 | 2023-02-03 08:00 | 2023-02-03 17:00 | 2023-02-03 14:08 |  | WACCES
MSA-DTAG | WA5287375 | 1 | OCS SERVICES PTY LTD | Ground floor - Registry - Covid Clean - see notes | Cleaning | Cleaning |  | Pass | Fail | 0 | 0 | 6.0333 | 2022-03-22 12:13 | 2022-03-23 17:00 | 2022-03-23 11:58 | 2022-03-23 17:00 | 2022-03-23 18:00 |  |  | Covid clean
MSA-DTWD | WA5090696 | 2 | Techworks Electrical | has a faulty data port | Electrical | General Electrical | 1200 | Pass | Pass | 0 | 0 | 6 | 2022-01-25 15:08 | 2022-01-31 17:00 | 2022-01-31 06:00 | 2022-01-31 17:00 | 2022-01-31 12:00 |  |  | Completed data point install due to failed cabling
MSA-DTWD | WA5163641 | 3 | Equans Mechanical Services Australia | Room F59 - Air Con is not working | Air Conditioning | Room Air Conditioners | 538.95 | Pass | Pass | -1 | -1 | 6 | 2022-02-18 10:44 | 2022-02-25 17:00 | 2022-02-21 10:00 | 2022-02-25 17:00 | 2022-02-21 16:00 |  |  | Arrived on site signed in, fault find on unit repaired fault a fuse blown. Replaced from van stock. Completed increased time settings from two hours to 7 hours operations. Cleaned up and completed paperwork.
MSA-DTWD | WA5201189 | 1 | BAKE-QUIP PTY LTD | E-Block SK1 oven door hinge broken needed for use on Friday | Equipment | Catering Equipment | 780.4 | Pass | Pass | 0 | 0 | 6 | 2022-03-02 12:28 | 2022-03-03 17:00 | 2022-03-03 10:30 | 2022-03-03 17:00 | 2022-03-03 16:30 |  |  | Refer to service report
MSA-DTWD | WA5201481 | 3 | AWB Co. | 3 lights not working | Electrical | Lighting, Internal | 1188.29 | Pass | Pass | -1 | -1 | 6 | 2022-03-02 15:31 | 2022-03-10 17:00 | 2022-03-04 07:00 | 2022-03-10 17:00 | 2022-03-04 13:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Went around and did count up of faulty lights. Went to pro lamps to pick up parts. Returned to site. Replaced tubes and starters as per lists. Cleaned up all work areas. Completed paperwork. Signed out. *** Job complete ***
MSA-DCA | WA5204683 | 2 | Techworks Electrical | Studio Underground - Door B corridor - see notes below | Electrical | Emergency & Exit Lighting | 653.25 | Pass | Pass | 0 | 0 | 6 | 2022-03-04 12:15 | 2022-03-10 17:00 | 2022-03-10 08:00 | 2022-03-10 17:00 | 2022-03-10 14:00 |  | WACCES | Replaced with new exit sign.
MSA-DCA | WA5207730 | 0 | EQUANS Mechanical Services (WA) Pty Limited | aircon not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 366.28 | Fail | Fail | 0 | 0 | 6 | 2022-03-08 16:19 | 2022-03-08 18:19 | 2022-03-09 10:00 | 2022-03-08 20:19 | 2022-03-09 16:00 |  |  | Travelled to site and signed in. Located clean room lab 1 and found Temperzone unit had a LP fault. Leak checked unit and found a leak present on the weld entering the TX valve. With assistance of Paul as the fire watch rewelded pipe and then pressure tested. Pressure test held. Evacuated system and charged with 12kg of R410a. Tested operation room is now cooling as it should without fault.
MSA-DTWD | WA5296255 | 2 | Techworks Electrical | C-Block - rooms C214 and C222 - have flickering lights need replacing | Electrical | General Electrical | 1249.23 | Pass | Pass | 0 | 0 | 6 | 2022-03-30 10:35 | 2022-04-04 17:00 | 2022-04-04 08:00 | 2022-04-04 17:00 | 2022-04-04 14:00 |  |  | Replaced fluro tubes in level 2 D block
MSA-DTWD | WA5301604 | 1 | WESTERN IRRIGATION PTY LTD | Break on Retic Mainline, SW Cnr of campus Education Drive (Adjacent to previous leak) | Plumbing & Drainage | Water | 1554.42 | Pass | Pass | 0 | 0 | 6 | 2022-04-01 10:45 | 2022-04-04 17:00 | 2022-04-04 06:00 | 2022-04-04 17:00 | 2022-04-04 12:00 |  |  | Locate break in mainline, excavate repair break, back fill and test for leaks.
MSA-DTWD | WA5308067 | 2 | Techworks Electrical | E block - External walkway has a blown light | Electrical | Lighting, External | 1232.48 | Pass | Pass | 0 | 0 | 6 | 2022-04-08 08:35 | 2022-04-13 17:00 | 2022-04-13 10:30 | 2022-04-13 17:00 | 2022-04-13 16:30 |  |  | Replaced faulty lights with new led up/down lights
MSA-DTWD | WA5367431 | 0 | Equans Mechanical Services Australia | Cool room - not working at all | Refrigeration | Coolroom | 673.7 | Pass | Fail | 0 | 0 | 6 | 2022-04-19 07:54 | 2022-04-19 09:54 | 2022-04-19 09:00 | 2022-04-19 11:54 | 2022-04-19 15:00 |  |  | Arrived on site signed in, checked in with Phil. Gathered tools and equipment started fault checks. Found thermostat not cutting unit in..isolated and replaced with new. Monitored operation all ok. Cleaned up work area. Completed paperwork and signed out.
MSA-DCA | WA5397221 | 2 | Techworks Electrical | BOH - OP Spiral stairs & Audio Patch Room - see notes below | Electrical | General Electrical | 1264.44 | Pass | Pass | 0 | 0 | 6 | 2022-05-06 14:14 | 2022-05-11 17:00 | 2022-05-11 07:00 | 2022-05-11 17:00 | 2022-05-11 13:00 |  |  | Replaced various blown globes in spiral staircase and batton light in audio patch room
MSA-DTWD | WA5399195 | 2 | Techworks Electrical | ground all blown lights in Kitchens, Staff rooms, stores areas, hallways and Restaurant | Electrical | Lighting, Internal | 2291.97 | Pass | Pass | 0 | 0 | 6 | 2022-05-09 17:44 | 2022-05-12 17:00 | 2022-05-12 06:00 | 2022-05-12 17:00 | 2022-05-12 12:00 |  |  | Replaced lights throughout e block
MSA-DTAG | WA5413889 | 2 | Sapio Pty Ltd | Registry - Front Counter - Duress Button stuck | Security | Monitoring | 331.39 | Pass | Pass | -1 | -1 | 6 | 2022-05-12 14:50 | 2022-05-17 17:00 | 2022-05-13 09:00 | 2022-05-17 17:00 | 2022-05-13 15:00 |  | WACCES | Replaced duress on Zone 53, tested, all OK.
MSA-DTWD | WA5473015 | 3 | AWB Co. | roof leak | Roofing | Metal Roofing | 1296.86 | Pass | Pass | -1 | -1 | 6 | 2022-05-24 12:19 | 2022-05-31 17:00 | 2022-05-27 09:00 | 2022-05-31 17:00 | 2022-05-27 15:00 |  |  | Cut away apron flashing to expose rusted sections, treated with crommelins. Installed new sheeting over rusted section.Installed new apron flashing, sealed dekitit, flu pipe and renewed A/c seals. Installed new ceiling tiles underneath.
MSA-DCA | WA5479383 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main Building - Lower Ground Floor - Faulty Fridge freezer needs repair | Refrigeration | Freezers | 450 | Pass | Pass | 0 | 0 | 6 | 2022-05-27 09:18 | 2022-05-30 17:00 | 2022-05-27 10:00 | 2022-05-30 17:00 | 2022-05-27 16:00 |  |  | Attended site, signed in and accessed basement Freezer room a/c unit.Checked the condensing unit and found the unit short of gas. Isolated unit and charged with nitrogen. Leak checked the unit and found the refrigerant leak coming from the bottom the suction line accumulator. Checked the electrical wiring and Compressor components and found the Compressor run capacitor and start capacitor also out of range. Collected all details and parts numbers for pricing and forwarded on to my supervisor to quote.
MSA-DCA | WA5522454 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Near Technical office - Water pooling on floor from ceiling (level 2). - see notes below | Air Conditioning | Room Air Conditioners | 746.88 | Pass | Pass | -1 | -1 | 6 | 2022-06-15 16:23 | 2022-06-22 17:00 | 2022-06-16 09:30 | 2022-06-22 17:00 | 2022-06-16 15:30 |  |  | Referencing Protek report sent by Reese. Checked over winch room split units on both east and west side leaking water. No leaks from units but during bad weather water can be sucked in by the supply fan. Was in the process of raising a DAS to carry out coil cleans on all 6 splits and to flush common drain. Carried out cleans to west side units and flushed drain line, all ok. Carried coil clean on east side units and flushed drain and vacuumed. Will quote to remove main drain and install a condensate pump as drain doesn't have any fall and water sits in the pipe. Checked office on level 2 no leaks coming from air-conditioning, all ok. Completed paperwork.
MSA-DTWD | WA5680430 | 3 | AWB Co. | Guest Services ladies toilets-sink cabinet coming away from wall | Carpentry | Joinery | 628.34 | Pass | Pass | 0 | 0 | 6 | 2022-07-27 12:11 | 2022-08-03 17:00 | 2022-08-01 09:30 | 2022-08-03 17:00 | 2022-08-01 15:30 |  |  | Installed 2 x adjustable legs on front of sink vanity unit in women’s toilet
MSA-DTWD | WA5794322 | 2 | AWB Co. | No lights working | Electrical | Lighting, Internal | 1076.06 | Pass | Pass | 0 | 0 | 6 | 2022-08-24 13:57 | 2022-08-29 17:00 | 2022-08-29 08:15 | 2022-08-29 17:00 | 2022-08-29 14:15 |  |  | More lights out in main foyerBRAF approval attached
MSA-DFES | WA5794679 | 3 | AWB Co. | main admin ground Command, Leadership and Development-crack in wall | Building | Internal Walls | 840.42 | Fail | Fail | 1 | 1 | 6 | 2022-08-25 07:03 | 2022-08-31 17:00 | 2022-09-06 07:30 | 2022-08-31 17:00 | 2022-09-06 13:30
MSA-DFES | WA5861110 | 1 | Australian HVAC Services Pty. Ltd. | Ground server room-Air Conditioner is blowing hot air and before it was blinking in error (Left one) | Air Conditioning | Room Air Conditioners | 1429.65 | Pass | Pass | 0 | 0 | 6 | 2022-09-13 06:39 | 2022-09-13 17:00 | 2022-09-13 11:00 | 2022-09-13 17:00 | 2022-09-13 17:00 |  |  | System fixed and operating correctly.
MSA-DCA | WA5869133 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Basement - CCR Room - Critical error on monitoring system | Security | Monitoring | 944.42 | Pass | Fail | 0 | 0 | 6 | 2022-09-14 11:47 | 2022-09-14 13:47 | 2022-09-14 13:30 | 2022-09-14 15:47 | 2022-09-14 19:30 |  | WACCES | Honeywell attended and resolved issue with server alarm
MSA-DTWD | WA5887834 | 3 | AWB Co. | Lift lobby - L2 Plant room doors not latching | Building | Doors | 709.38 | Pass | Pass | 0 | 0 | 6 | 2022-09-16 10:16 | 2022-09-23 17:00 | 2022-09-23 08:30 | 2022-09-23 17:00 | 2022-09-23 14:30 |  |  | Door is water damaged as per photos, weather seal damaged,outside push down lock damaged and replaced bothReassembled the internal weather strip, door still having trouble closing due to the metal plate not being able to be screwed into the concrete pad, fabricated metal plate to hold the push down lock in place
MSA-DTWD | WA5988673 | 3 | JEM Carpentry | Exterior fence around building needs repair - see notes below | Building | Steel Fencing & Gates |  | Pass | Pass | -1 | -1 | 6 | 2022-10-04 10:31 | 2022-10-11 17:00 | 2022-10-07 12:00 | 2022-10-11 17:00 | 2022-10-07 18:00 |  |  | install and supply sitefencing and appropriatesignage
MSA-DCA | WA5998715 | 0 | Techworks Electrical | Perth Cultural Centre Precinct-James Street Amphitheatre -Ground Floor - bollards not lowring | Electrical | General Electrical | 270.265 | Pass | Fail | 0 | 0 | 6 | 2022-10-08 15:06 | 2022-10-08 17:06 | 2022-10-08 15:30 | 2022-10-08 19:06 | 2022-10-08 21:30 |  |  | Attended Perth cultural centre.problem raising bollards.checked over electrical cabinets containing control to bollards. switched isolator off and back on. the reset got the bollards working correctly again.
MSA-DTWD | WA6000787 | 3 | AWB Co. | West Laneway - Floodlight out in West laneway | Electrical | Emergency & Exit Lighting | 1471.91 | Pass | Pass | -1 | -1 | 6 | 2022-10-10 10:33 | 2022-10-17 17:00 | 2022-10-13 10:45 | 2022-10-17 17:00 | 2022-10-13 16:45 |  |  | Job complete
MSA-DTWD | WA6008417 | 3 | Equans Mechanical Services Australia | Rebalance zones - as to much air coming out of one zone and not enough out of another-see notes | Air Conditioning | Room Air Conditioners | 1547.96 | Fail | Fail | 0 | 0 | 6 | 2022-10-11 14:24 | 2022-10-18 17:00 | 2022-10-21 10:00 | 2022-10-18 17:00 | 2022-10-21 16:00 |  | WCAPPR | Arrived on site signed in with Dennis. Gathered tools and controls using a hood for diffusers balanced GBlock open and office areas. Changed operation proceedure on interview area to only work when used. Cleaned up and completed paperwork. Icon logic on site to assist control changes and zone balancing on bms.
MSA-DTWD | WA6014370 | 1 | Techworks Plumbing | C45 - hairdressing laundry - blocked drain | Plumbing & Drainage | Drainage | 1270.28 | Pass | Pass | 0 | 0 | 6 | 2022-10-12 08:45 | 2022-10-13 17:00 | 2022-10-12 11:30 | 2022-10-13 17:00 | 2022-10-12 17:30 |  |  | Attended site at midland tafe and signed in at front office.spoke to facilities manager about the blockage and he took us to the area where it was and explained to us what was going on, they had a laundry sink that keeps getting blocked up and every time they use the washing machines at the same time the sink will overflow, also some of the hair cleaning basins we’re getting blocked up also.so we started by trying to plunge the sink to see if we could get any movement but that didn’t do much, we took trap a party to see if there were any hard blockages in there and found some hair to be bundled up in it but not enough to block it up, we cleared it out and then we put a drain spring down the waste to get rid of any debris, we didn’t get much out of it.we also tried feeding a hose down the waste to clear anything out then we put the trap back together and tested and the hose did make a difference and the sink started draining slowly but still not 100%, we found an IO outside and turne
MSA-DTWD | WA6020163 | 2 | WESTERN IRRIGATION PTY LTD | Near C Block - Child Care - Reticulation solenoid stuck -not opening allowing water to C & G Blocks | Landscaping & Gardening | Grounds Maintenance | 1324.13 | Pass | Pass | 0 | 0 | 6 | 2022-10-13 11:15 | 2022-10-18 17:00 | 2022-10-18 10:45 | 2022-10-18 17:00 | 2022-10-18 16:45 |  |  | Located and replaced solenoid valve and fittings.
MSA-DTWD | WA6253988 | 1 | Equans Mechanical Services Australia | Air con leaking through electrical conduit at Number 12 - See Notes | Air Conditioning | Room Air Conditioners | 1038.165 | Pass | Pass | 0 | 0 | 6 | 2022-11-22 13:47 | 2022-11-23 17:00 | 2022-11-23 07:30 | 2022-11-23 17:00 | 2022-11-23 13:30 |  |  | Attended site, investigated water leak from Evap. A260. Found solenoid valve was leaking water. Left site, travelled to suppliers pick up new solenoid valve, return back to site, fitted new valve. Tested new valve, all OK. Filled out paperwork. 2nd man to foot ladder Sign out
MSA-DTWD | WA6292960 | 2 | AWB Co. | Courtyard - Rectify uneven paving (see notes) | Paving & Roadworks | Paving | 1918.42 | Fail | Fail | 0 | 0 | 6 | 2022-11-29 15:10 | 2022-12-02 17:00 | 2022-12-05 07:00 | 2022-12-02 17:00 | 2022-12-05 13:00 |  |  | paving works completed
MSA-DTWD | WA6370878 | 3 | AWB Co. | Section of wall needs to be repainted due to excessive marks and Scuffs | Building | Internal Walls | 818.42 | Pass | Pass | 0 | 0 | 6 | 2022-12-14 10:21 | 2022-12-21 17:00 | 2022-12-20 09:30 | 2022-12-21 17:00 | 2022-12-20 15:30 |  |  | painting works completed
MSA-DTAG | WA6373536 | 3 | Midolo Building Services | Level 7 & 8 - Stairwell - Balcony door exterior has laminated | Building | Doors | 878.67 | Pass | Pass | -1 | -1 | 6 | 2022-12-14 15:03 | 2022-12-21 17:00 | 2022-12-15 07:00 | 2022-12-21 17:00 | 2022-12-15 13:00 |  |  | BALCONY DOOR REPAIRED
MSA-DTWD | WA6375573 | 1 | WESTERN IRRIGATION PTY LTD | Reticulation not working - No flow. | Plumbing & Drainage | Water | 1080 | Pass | Pass | 0 | 0 | 6 | 2022-12-15 08:56 | 2022-12-16 17:00 | 2022-12-16 05:30 | 2022-12-16 17:00 | 2022-12-16 11:30 |  |  | Install and commission flow switch
MSA-DFES | WA6466771 | 3 | Australian HVAC Services Pty. Ltd. | Main Administration- Ground- Lecture room 5 & 6 - Air-conditioning not working | Air Conditioning | Room Air Conditioners | 807.94 | Pass | Pass | 0 | 0 | 6 | 2023-01-17 13:44 | 2023-01-24 17:00 | 2023-01-23 07:30 | 2023-01-24 17:00 | 2023-01-23 13:30
MSA-DTWD | WA6539483 | 2 | Protek 24/7 Building & Maintenance | Both Lecture Theatres - near emergency exit- replace metal edging on carpet | Flooring | Carpet | 736.71 | Fail | Fail | 0 | 0 | 6 | 2023-02-08 13:26 | 2023-02-13 17:00 | 2023-02-14 09:00 | 2023-02-13 17:00 | 2023-02-14 15:00
MSA-DCA | WA6669237 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Alexander - BMS - shows 2 alarms for AC9 high RH | Building | General Building | 478.19 | Pass | Pass | -1 | -1 | 6 | 2023-02-22 16:05 | 2023-02-27 17:00 | 2023-02-23 12:00 | 2023-02-27 17:00 | 2023-02-23 18:00
MSA-DTAG | WA5495205 | 1 | OCS SERVICES PTY LTD | 2A – desk in main office (COVID SIGN) - Covid Clean Required | Cleaning | Emergency Cleans |  | Pass | Pass | 0 | 0 | 5.8833 | 2022-06-08 10:12 | 2022-06-09 17:00 | 2022-06-09 11:07 | 2022-06-09 17:00 | 2022-06-09 17:00 |  |  | Covid completed
MSA-DTWD | WA5111879 | 3 | AWB Co. | Level 3 - South Block - Roof - Circuit faulty to roof lighting | Electrical | Lighting, Internal | 970.865 | Pass | Pass | 0 | 0 | 5.75 | 2022-02-10 11:46 | 2022-02-17 17:00 | 2022-02-16 07:15 | 2022-02-17 17:00 | 2022-02-16 13:00 |  |  | Attended site signed in. completed jsa. Spoke with FM about location of job and fault.located board with fault, inspected board. Found to be 3 poles on east side were not illuminating. Removed floor tiles to investigate cable entry to lights. Found to be all siliconed up. Removed red side panels and found terminal blocks. disconnected load side of light pole to eliminate light fitting faults tested okDisconnected light 2 cabling to see which way the fault was going. cables 1 to 2 tested fine. Rewired load back up and reset breaker and lights 1 & 2 started working. Isolated. continued on to light 3. Tested cable from L2 to L3 cable fine. Bypassed terminal block on L3 to load and reset breaker, lights illuminated. found to be fault to earth on L3 is now rectified. made sure all connections were safe and correct.Left lights on for 20min. All lights stayed on. Secured panels back onto light poles. Packed up site. Notified site of completion. IR TEST FROM BOARD OUT TO FIELDA-E 550 M
MSA-DTWD | WA5681603 | 1 | Securex Security Systems & Services | B Block -Alarm, section 2 & 6 is not communicating with Education security - Gallagher system | Security | Security Management System | 1000 | Pass | Fail | 0 | 0 | 5.75 | 2022-07-28 13:27 | 2022-07-29 17:00 | 2022-07-29 11:45 | 2022-07-29 17:00 | 2022-07-29 17:30 |  |  | (29/07/2022) - Work NoteInvestigate reported issue.System is reporting as intended.B Block input expander, URI and 2x remote arming terminals found to be offline.F Block also has devices offline.No plans where this hardware is located so a physical search of the building is required. Hardwareeventually located.Investigation has lead to the discovery of a short circuit on the cable feeding a remote armingterminal. Cable has been disconnected which has restored offline devices
MSA-DFES | WA6000884 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Training Tower - Electrical junction box located on West side of training tower is cracked | Electrical | General Electrical | 535.035 | Pass | Pass | 0 | 0 | 5.75 | 2022-10-10 11:07 | 2022-10-17 17:00 | 2022-10-17 10:15 | 2022-10-17 17:00 | 2022-10-17 16:00 |  |  | Arrived on site at 10:30 to investigate cracked junction box in training tower, found work orders addresses to be wrong and no one on site can find fault and are saying job is actually for Kiara FS. Left site at 11:15.Second arrival: Replaced broken junction box at west of training tower. Notified staff of works and left sitePicked up parts from whole saler from 16:45-15:15.
MSA-DTWD | WA6375251 | 3 | AWB Co. | faulty light | Electrical | Lighting, Internal | 1266.98 | Pass | Pass | 0 | 0 | 5.75 | 2022-12-15 08:26 | 2022-12-22 17:00 | 2022-12-21 08:00 | 2022-12-22 17:00 | 2022-12-21 13:45 |  |  | Attended site! Signed in, completed jsa, spoke to fm, located faulty lights and replace with new ones, tested to see if everything was working, all good, packed up and cleaned up, sign out, completed paperwork. ***Job completed***
MSA-DTWD | WA5672947 | 1 | Lane's Plumbing | Sheep Paddock behind shearing shed - Faulty Float | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 5.75 | 2022-07-20 10:55 | 2022-07-21 17:00 | 2022-07-20 11:15 | 2022-07-21 17:00 | 2022-07-20 17:00 |  |  | REPLACE FAULTY VALVE TO STOCK TROUGH NEAR SHEARING SHED
MSA-DTWD | WA5869623 | 1 | AWB Co. | A101 Rear Emergency door damaged needs replacement | Building | Doors | 270.345 | Pass | Pass | 0 | 0 | 5.75 | 2022-09-14 15:15 | 2022-09-15 17:00 | 2022-09-15 08:30 | 2022-09-15 17:00 | 2022-09-15 14:15 |  |  | attended sitequote to make replacementBRAF declined - invoice costs to date
MSA-DTWD | WA6301028 | 1 | JEM Carpentry | Farm grain shed - Front doors faulty | Building | Doors |  | Pass | Pass | 0 | 0 | 5.75 | 2022-12-02 12:37 | 2022-12-05 17:00 | 2022-12-02 12:45 | 2022-12-05 17:00 | 2022-12-02 18:30 |  |  | Repairs
MSA-DTWD | WA6482373 | 2 | AWB Co. | Rectify issues with 3 phase drill press plugs | Equipment | Power Tools | 1315.6475 | Pass | Pass | 0 | 0 | 5.75 | 2023-01-18 09:38 | 2023-01-23 17:00 | 2023-01-20 07:00 | 2023-01-23 17:00 | 2023-01-20 12:45
MSA-DTWD | WA6674455 | 2 | AWB Co. | Ladies toilets - 3 lights not working in ladies toilets | Electrical | Lighting, Internal | 1206.1275 | Pass | Pass | 0 | 0 | 5.75 | 2023-02-27 10:06 | 2023-03-02 17:00 | 2023-02-28 09:45 | 2023-03-02 17:00 | 2023-02-28 15:30
MSA-DTWD | WA5473009 | 3 | AWB Co. | P03 - Front foyer – 1 x round light not working | Electrical | Lighting, Internal | 751.38 | Pass | Pass | 0 | 0 | 5.65 | 2022-05-24 12:17 | 2022-05-31 17:00 | 2022-05-31 10:21 | 2022-05-31 17:00 | 2022-05-31 16:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located lighting in p block, 3x lights weren’t working, measured old lighting and went to wholesaler to find suitable replacement, returned to site and isolated lighting, removed cover of old lights and mounted base of oyster To framework, wired in lighting and re energised circuit, lights working as intended , cleaned up, packed up, completed paperwork, signed out ***job completed***
MSA-DTWD | WA5090698 | 2 | Techworks Electrical | has a faulty data port | Electrical | General Electrical | 999.11 | Pass | Pass | 0 | 0 | 5.5833 | 2022-01-25 15:23 | 2022-01-31 17:00 | 2022-01-31 07:00 | 2022-01-31 17:00 | 2022-01-31 12:35 |  |  | installed new data point as cabling failed
MSA-DFES | WA5288877 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Safety shower 6 - Eyewash hasn't got pressure | Plumbing & Drainage | Water | 591.97 | Pass | Pass | 0 | 0 | 5.5833 | 2022-03-23 15:04 | 2022-03-28 17:00 | 2022-03-28 10:00 | 2022-03-28 17:00 | 2022-03-28 15:35 |  |  | Repaired emergency eye wash
MSA-DTWD | WA5152898 | 2 | SCAVENGER SUPPLIES PTY LTD | Block S - Fire hydrant has burst and unable to isolate. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) |  | Fail | Fail | 0 | 0 | 5.5167 | 2022-02-17 18:11 | 2022-02-22 17:00 | 2022-02-25 10:00 | 2022-02-22 17:00 | 2022-02-25 15:31 |  |  | Plumbers on site had stopped the leak. Valves and seals have perished and need replacing. BRAF to be sent for 5 Yearly service to be conducted to all Hydrants and Boosters on site.no charge for this WA#
MSA-DTWD | WA5105119 | 3 | AWB Co. | 429B - Cabinets not secure - see notes below | Building | Internal Walls | 586.75 | Pass | Pass | 0 | 0 | 5.5 | 2022-02-04 07:55 | 2022-02-10 17:00 | 2022-02-10 10:30 | 2022-02-10 17:00 | 2022-02-10 16:00 |  |  | Refix cabinets as required
MSA-DTAG | WA5141551 | 3 | PPM Project Painting & Maintenance | Level 4 - Irwin Street - Remove torn wallpaper from public corridor wall & paint the affected area | Building | Internal Walls |  | Fail | Fail | 0 | 0 | 5.5 | 2022-02-16 11:00 | 2022-02-23 17:00 | 2022-02-26 08:00 | 2022-02-23 17:00 | 2022-02-26 13:30 |  |  | job completed - repaired and painted
MSA-DTAG | WA5141579 | 3 | PPM Project Painting & Maintenance | Level 13 - Conference room - Small area of paint peeling from ceiling near windows | Building | Internal Walls |  | Fail | Fail | 0 | 0 | 5.5 | 2022-02-16 11:13 | 2022-02-23 17:00 | 2022-02-26 08:00 | 2022-02-23 17:00 | 2022-02-26 13:30 |  |  | job completed - repaired and painted
MSA-DTAG | WA5190766 | 3 | PPM Project Painting & Maintenance | Level 4 - Public corridor - Hole has been puched in gyprock wall | Building | General Building |  | Pass | Pass | -1 | -1 | 5.5 | 2022-02-24 14:24 | 2022-03-03 17:00 | 2022-02-26 08:00 | 2022-03-03 17:00 | 2022-02-26 13:30 |  |  | job completed - repaired and painted walls
MSA-DTWD | WA5216937 | 2 | Building Automation & Electrical Services Pty Ltd | East Block - Level 3 - E324 - VAV fault - E3-06 showing no airflow - actuator not driving | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 5.5 | 2022-03-11 14:11 | 2022-03-16 17:00 | 2022-03-16 10:30 | 2022-03-16 17:00 | 2022-03-16 16:00 |  |  | East Block - Level 3 - E324 - VAV fault - E3-06 showing no airflow - actuator not driving
MSA-DTWD | WA5287641 | 2 | High Tech Pest Control | Campus entry - Hayman road -Large population of bees present in retic pit on LHS of the Campus Entry | Pest Control | General Pest | 519 | Fail | Fail | 1 | 1 | 5.5 | 2022-03-22 14:14 | 2022-03-25 17:00 | 2022-03-29 06:00 | 2022-03-25 17:00 | 2022-03-29 11:30 |  |  | Removal of bees to another site
MSA-DTWD | WA5470663 | 0 | AWB Co. | R Block - Water damage - getting into the building via door ways | Cleaning | Cleaning |  | Pass | Fail | 0 | 0 | 5.5 | 2022-05-23 11:36 | 2022-05-23 13:36 | 2022-05-23 12:00 | 2022-05-23 15:36 | 2022-05-23 17:30 |  |  | Attended site R Block - Water damage - getting into the building via door waysAdditional Notes: Water damage on carpets and foyer
MSA-DTWD | WA5481325 | 2 | Techworks Electrical | -Block Restaurant down lights not working | Electrical | Lighting, Internal | 1618.57 | Pass | Pass | 0 | 0 | 5.5 | 2022-05-30 12:18 | 2022-06-02 17:00 | 2022-05-31 06:00 | 2022-06-02 17:00 | 2022-05-31 11:30 |  |  | Replaced dimmers in restaurant area to new led dimmers to suit led fitting. Halogens still cutting out before led so the replacement of the rest of the downlights was done. Lights now all dim at the same level.
MSA-DTWD | WA5682275 | 1 | AHS Services WA Pty Ltd (Anchor) | toilets flooding. | Plumbing & Drainage | Water | 941.9 | Pass | Pass | 0 | 0 | 5.5 | 2022-07-29 07:53 | 2022-07-29 17:00 | 2022-07-29 08:00 | 2022-07-29 17:00 | 2022-07-29 13:30 |  |  | Found disabled toilet inlet valve jammed open, and drainage to that block, blocked. Located man hole near by infested with roots. Managed to clear roots but will need further investigation with camera and jetter
MSA-DTWD | WA5699302 | 2 | AWB Co. | staff corridor-Two light fitting are broken beyond repair-see notes | Electrical | Lighting, Internal | 998.295 | Pass | Pass | 0 | 0 | 5.5 | 2022-08-10 08:38 | 2022-08-15 17:00 | 2022-08-15 11:15 | 2022-08-15 17:00 | 2022-08-15 16:45 |  |  | Couldn’t fit led troffers to ceiling space as requested as original lights are longer than led troffers so there would have been a gap in the ceiling
MSA-DTWD | WA5790383 | 2 | AWB Co. | Door needs to be repaired/replaced | Building | Doors | 2050.42 | Fail | Fail | 6 | 6 | 5.5 | 2022-08-22 10:20 | 2022-08-25 17:00 | 2022-10-03 12:30 | 2022-08-25 17:00 | 2022-10-03 18:00 |  |  | door works completed BRAF approved and attached
MSA-DFES | WA6080032 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Power issues – RCD keep tripping and ICT going down | Electrical | General Electrical | 493.23 | Pass | Pass | 0 | 0 | 5.5 | 2022-10-18 13:24 | 2022-10-21 17:00 | 2022-10-20 09:45 | 2022-10-21 17:00 | 2022-10-20 15:15 |  |  | Arrived on site at 09:45. Spoke with staff about problem, station got called out and had to leave site. Left site 10:00. Will need to return to site to investigate problem. Arrived on site at 12:45. Spoke with staff and they explained issues with power tripping in the old fire station around office area. Tested circuit all okay. Located ethanet switch with short circuit. Opened up switch and found it has burnt out due to dust and low ventilation in cupboard. Removed switch from circuit and swapped with spare in coms rack. Left site at 15:15
MSA-DTWD | WA6360823 | 3 | Australian Airconditioning Services Pty Ltd | **Retrospective work order** Staff room 2G1/2 - A/C Not working | Air Conditioning | Room Air Conditioners | 1579.76 | Fail | Fail | 4 | 4 | 5.5 | 2022-12-07 15:09 | 2022-12-14 17:00 | 2023-01-11 07:30 | 2022-12-14 17:00 | 2023-01-11 13:00 | 1 | WACCES | Replaced additional PCBs and tested operation. All ok
MSA-DTWD | WA6425685 | 2 | Protek 24/7 Building & Maintenance | Damaged decking slats have metal covering them | Flooring | Timber | 661.14 | Pass | Pass | 0 | 0 | 5.5 | 2023-01-12 10:58 | 2023-01-17 17:00 | 2023-01-16 06:30 | 2023-01-17 17:00 | 2023-01-16 12:00
MSA-DTWD | WA6450270 | 2 | AHS Services WA Pty Ltd (Anchor) | hot water storage unit is leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 1692.255 | Fail | Fail | 1 | 1 | 5.5 | 2023-01-16 10:30 | 2023-01-19 17:00 | 2023-01-23 07:30 | 2023-01-19 17:00 | 2023-01-23 13:00
MSA-DTWD | WA6531615 | 3 | AWB Co. | Repair Screens dislodged in B205 | Building | Internal Screens | 630.405 | Pass | Pass | 0 | 0 | 5.5 | 2023-02-03 13:21 | 2023-02-10 17:00 | 2023-02-07 09:30 | 2023-02-10 17:00 | 2023-02-07 15:00
MSA-DTWD | WA5101756 | 2 | AWB Co. | faulty RCD | Electrical | Distribution Board | 907.27 | Pass | Pass | 0 | 0 | 5.5 | 2022-02-03 14:27 | 2022-02-08 17:00 | 2022-02-07 08:30 | 2022-02-08 17:00 | 2022-02-07 14:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located appliance that needed testing and tagging. Tested and tagged out appliance. All working correctly. Also found R9 tripping and won’t reset. Located 1x double gpo labelled R9 which was powering 2x ovens. Removed ovens from gpo n tried to reset. Still wouldn’t reset. Removed gpo from wall n cables. Megger the circuit. Came up with Dead short. Traced cable and found blank plate with junction. Opened up. Split cables and megger the cable going back to oven. All good. Megger the circuit which goes into ground suspecting it goes straight to S/B. Came up with Dead short. Removed cable, ducting and mounting block which was feeding the oven. Left cable which was coming from the ground in conduit, mounting block, placed cables in connectors and placed blank plate back on. Installed 2x new 56 series gpos with 1x switch in conduit on existing circuit W8. Also replaced 1x 56 series 3phase plug and switch.
MSA-DTWD | WA5106731 | 2 | Techworks Electrical | D-Block - G/Floor - Canteen and hallway to canteen has flickering lights | Electrical | General Electrical | 2107.56 | Pass | Pass | 0 | 0 | 5.5 | 2022-02-07 11:02 | 2022-02-10 17:00 | 2022-02-10 07:00 | 2022-02-10 17:00 | 2022-02-10 12:30 |  |  | Replaced all faulty lights in d block ground floor for new led fittings
MSA-DCA | WA5190933 | 1 | Protek 24/7 Building & Maintenance | Heath Ledger theatre - Audotorium - large celing panel loose about to fall | Building | Materials | 856.1 | Pass | Pass | 0 | 0 | 5.5 | 2022-02-24 22:11 | 2022-02-25 22:11 | 2022-02-25 07:00 | 2022-02-25 22:11 | 2022-02-25 12:30 |  |  | Repair large ceiling Panel
MSA-DTAG | WA5407636 | 3 | PPM Project Painting & Maintenance | Level 16 - Balcony - Graffiti on the outside of level 6 west balcony | Cleaning | Graffiti |  | Fail | Fail | 1 | 1 | 5.5 | 2022-05-11 12:53 | 2022-05-18 17:00 | 2022-05-23 10:00 | 2022-05-18 17:00 | 2022-05-23 15:30 |  |  | Removal of graffiti
MSA-DCA | WA6007540 | 1 | TK Elevator Australia Pty Ltd | Level 2-Lift 7-stuck on Level 2 – Out of order displaying the morning after last MWR completed. | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 5.5 | 2022-10-11 08:32 | 2022-10-12 17:00 | 2022-10-11 09:15 | 2022-10-12 17:00 | 2022-10-11 14:45 |  |  | to be closed out at $0 cost
MSA-DFES | WA6113022 | 3 | Dom's Total Grounds Maintenance | Level 1 - Front Lawn - 2 Reticulation have been damaged - See notes | Landscaping & Gardening | Grounds Maintenance | 777 | Fail | Fail | 1 | 1 | 5.5 | 2022-10-24 08:40 | 2022-10-31 17:00 | 2022-11-09 07:00 | 2022-10-31 17:00 | 2022-11-09 12:30 |  |  | Fix all breakages as required
MSA-DTWD | WA6129470 | 1 | WESTERN IRRIGATION PTY LTD | Repair reticulation leak in the lawn area between O Block and B Block.-see notes | Landscaping & Gardening | Grounds Maintenance | 1562.22 | Pass | Pass | 0 | 0 | 5.5 | 2022-10-27 16:20 | 2022-10-28 17:00 | 2022-10-28 05:30 | 2022-10-28 17:00 | 2022-10-28 11:00 |  |  | Excavate and repair mainline leak. Tested - operating correctly.
MSA-DTWD | WA6290490 | 1 | AWB Co. | Main switchboard - Faulty RCD for server unit | Electrical | Distribution Board | 930.56 | Pass | Pass | 0 | 0 | 5.5 | 2022-11-28 09:16 | 2022-11-29 17:00 | 2022-11-29 07:00 | 2022-11-29 17:00 | 2022-11-29 12:30 |  |  | Attended site signed in jsa completed. Found breaker tripped and wont reset. Makes big bang when doing so. Disconnected all loads and blew white discrimination fuse of 65A.followed cabling around building to find rat had bitten through and shorted active and earth together. Replaced cable and tested fine now. Turned breaker on and finishedJob completed
MSA-DTWD | WA6503901 | 2 | BAKE-QUIP PTY LTD | Demo Kitchen - Comvo therm steamer showing error code E01.0 Low water | Catering | Catering Services | 1042.8 | Pass | Pass | -1 | -1 | 5.5 | 2023-01-19 12:05 | 2023-01-24 17:00 | 2023-01-20 09:15 | 2023-01-24 17:00 | 2023-01-20 14:45
MSA-DTAG | WA6681412 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 15-Toilets & Kitchen - Both toilets arent flushing properly, constant gurling noise in Kitchen | Plumbing & Drainage | Drainage | 892.72 | Pass | Pass | 0 | 0 | 5.5 | 2023-03-02 08:30 | 2023-03-03 17:00 | 2023-03-03 10:00 | 2023-03-03 17:00 | 2023-03-03 15:30
MSA-DTWD | WA5111901 | 3 | SCAVENGER SUPPLIES PTY LTD | F Block - SIP Z5 ST:CONV FLT Zone faults 1 of 1 - see further notes below | Fire Protection Services | Fire Protection - Monitor System | 1639.74 | Pass | Pass | 0 | 0 | 5.4833 | 2022-02-10 11:59 | 2022-02-17 17:00 | 2022-02-17 09:31 | 2022-02-17 17:00 | 2022-02-17 15:00 |  | WACCES | completed 17/02/2022
MSA-DTWD | WA5105443 | 1 | Techworks Electrical | Kendrew- E block. E40 lights out and outside of office light out, and cool room 3 | Electrical | General Electrical | 815 | Pass | Pass | 0 | 0 | 5.4 | 2022-02-04 10:51 | 2022-02-07 17:00 | 2022-02-07 07:00 | 2022-02-07 17:00 | 2022-02-07 12:24 |  |  | Attended site, inspected lights out and and sourced materials to rectify. Replaced lights in coolroom and in office
MSA-DFES | WA5564139 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Dorm 2 and Dorm 4 (vanity flick mixer) - Fluoro needs replacing | Electrical | General Electrical | 81.585 | Pass | Pass | 0 | 0 | 5.4 | 2022-06-21 08:31 | 2022-06-24 17:00 | 2022-06-22 08:51 | 2022-06-24 17:00 | 2022-06-22 14:15 |  |  | Arrived onsite at 14:00 to investigate lights not working located dorm 2 and 4. Found lights were not working due to faulty parts. Replaced all necessary parts and tested. Left site at 14:15
MSA-DCA | WA6667933 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Lower GRND Collection store 2 - Humidity alarm Value 61.37 | Air Conditioning | Room Air Conditioners | 872.76 | Pass | Fail | 0 | 0 | 5.3333 | 2023-02-21 23:56 | 2023-02-22 01:56 | 2023-02-22 00:10 | 2023-02-22 03:56 | 2023-02-22 05:30
MSA-DFES | WA5052633 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - drop down lead from the roof isn't working | Electrical | General Electrical | 985.69 | Pass | Fail | 0 | 0 | 5.3333 | 2022-01-18 09:27 | 2022-01-18 11:27 | 2022-01-18 09:40 | 2022-01-18 13:27 | 2022-01-18 15:00 |  |  | Attended site to investigate faulty pendant gpo. Checked ceiling rose and plug top terminations. Found active wire in the ceiling rose had been pulled out of the terminal and was loose. Found active probe on the male plugtop had also come loose. Repaired both faults and tested. Notified staff and signed out.
MSA-DTWD | WA5101680 | 3 | Techworks Electrical | P Block - Ground - P008 - flickering light above Elaine Lamonds desk | Electrical | Lighting, Internal | 136.87 | Pass | Pass | 0 | 0 | 5.3167 | 2022-02-03 13:48 | 2022-02-10 17:00 | 2022-02-07 07:00 | 2022-02-10 17:00 | 2022-02-07 12:19 |  |  | Replaced faulty parts to fluorescent light
MSA-DTWD | WA5613682 | 3 | AWB Co. | Small leak just inside entry door | Roofing | Metal Roofing | 484.265 | Pass | Pass | -1 | -1 | 5.2833 | 2022-07-14 15:06 | 2022-07-21 17:00 | 2022-07-15 06:58 | 2022-07-21 17:00 | 2022-07-15 12:15 |  |  | Investigated area above leak.found silicone issues around vent.made repairs
MSA-DTWD | WA5001325 | 1 | AWB Co. | Comms Room - power keeps tripping causing UPs to kick in | Electrical | General Electrical | 997.68 | Pass | Pass | 0 | 0 | 5.25 | 2022-01-11 11:18 | 2022-01-12 17:00 | 2022-01-12 07:30 | 2022-01-12 17:00 | 2022-01-12 12:45 |  |  | Attended site and signed in. Completed JSA. Spoke with ICT guy on site regarding server issues that had been happening , went to server room with him and inspected GPOs /server rack , went to find circuit in switchboard located in foyer area, opened up switchboard and burning smell was present, took top cover off of board , looked down and saw arcing coming from fuse , removed fuses immediately as it was a fire risk , facilities manager was present and explained to him why site needed to be shut down , called AJ to attend as I need a 2nd tradesman on site to isolate whole Distribution board, found that wires in line side of blue phase were loose causing a great amount of heat to damage cable and fuse base/cartridge, called wholesaler to find replacement parts, went to pick up parts, removed all damaged cable and fuses and replaced with circuit breaker , made metal cover plate as circuit breaker didn’t fit original cut out , tested cables and were all good , turned off all circuits and
MSA-DTWD | WA5111530 | 2 | AWB Co. | Science Block S Block - Ground - Compound outside S6 -see details below | Building | General Building | 900.355 | Pass | Pass | 0 | 0 | 5.25 | 2022-02-10 08:53 | 2022-02-15 17:00 | 2022-02-14 07:00 | 2022-02-15 17:00 | 2022-02-14 12:15 |  |  | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Located cut fence out the back of science. Replaced and repaired fencing with new chain mesh. Notified of works completed. **job complete**
MSA-DTWD | WA5115913 | 3 | AWB Co. | Door not closing and when forced closed emits high whistling noise due to extraction fan | Building | Doors | 852.215 | Pass | Pass | 0 | 0 | 5.25 | 2022-02-11 10:06 | 2022-02-18 17:00 | 2022-02-16 08:00 | 2022-02-18 17:00 | 2022-02-16 13:15 |  |  | The room had 4 exhaust fans inside of it when normally a room of its size would only have 1. Thiscreated a loud whistling noise and made the door hard to close.Because the room is now used by staff to store their bicycles I put the first vent on the top of the door toprevent any wheels damaging it. When that proved not to be enough air access for the exhaust fansadded a smaller vent at the bottom. This was enough to stop the whistling, when the Maintenanceofficer inspected the job he was happy.I noticed that there are several holes in the ceiling of the room that are feeding air to the fans. If theseare filled in it is likely another small vent will be needed in the door.
MSA-DTWD | WA5378512 | 2 | AWB Co. | U022.6 - Faulty start button for radial arm saw | Electrical | General Electrical | 686.25 | Pass | Pass | -1 | -1 | 5.25 | 2022-04-20 15:01 | 2022-04-26 17:00 | 2022-04-21 10:15 | 2022-04-26 17:00 | 2022-04-21 15:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Found lecturer and discussed what he wanted and what was possible to do, checked regulations , pulled off stop/start button and rewired configuration, found lecturer again and showed him machine operation , lecturer was happy , re mounted all switches, and conduits , cleaned up, packed up, completed paperwork, signed outJob completed
MSA-DTWD | WA5696865 | 2 | Milners Tree Solutions Pty Ltd | Driveway entrance - Tree faulty - See notes below | Landscaping & Gardening | Tree Lopping | 4400 | Fail | Fail | 1 | 1 | 5.25 | 2022-08-08 15:57 | 2022-08-11 17:00 | 2022-08-15 06:40 | 2022-08-11 17:00 | 2022-08-15 11:55 |  |  | tree removal and stump grinding.
MSA-DTWD | WA6111462 | 2 | AWB Co. | Replace light tubes as required A313 | Electrical | Lighting, Internal | 1265.7625 | Pass | Pass | 0 | 0 | 5.25 | 2022-10-21 07:42 | 2022-10-25 17:00 | 2022-10-25 11:30 | 2022-10-25 17:00 | 2022-10-25 16:45 |  |  | Job complete
MSA-DTWD | WA6293458 | 1 | Equans Mechanical Services Australia | Ground/First Level - B Block Staffrooms - Air Con not cooling, reading 28 degrees | Air Conditioning | Evaporative Coolers | 600.3925 | Fail | Fail | 1 | 1 | 5.25 | 2022-11-30 08:56 | 2022-12-01 17:00 | 2022-12-05 09:45 | 2022-12-01 17:00 | 2022-12-05 15:00 |  |  | Checked out AHU'S B1 & B2 , The belts all OK , B2 filters block , went off site and picked up new ones. Tried to access the bms but there is a problem with it, the girls on site logged a job to get it fixed .Need the bms to check temperatures and the positioning of the outside air and water valve on B2.Need to return and check once bms up and running. 12/12/22:BMS up and running temperatures all OK
MSA-DTWD | WA5128082 | 1 | Techworks Electrical | F Block - Ground - West side interior - faulty light switch west side interior | Electrical | General Electrical | 139.2 | Pass | Pass | 0 | 0 | 5.2167 | 2022-02-14 15:50 | 2022-02-15 17:00 | 2022-02-15 08:30 | 2022-02-15 17:00 | 2022-02-15 13:43 |  |  | Inspected lights not turning off. Found light switch to be faulty. Replaced switching mechanism
MSA-DTWD | WA5287684 | 2 | Precise Air Group | B block - B 106 - BMS calling for heating | Air Conditioning | Room Air Conditioners | 722.135 | Fail | Fail | 1 | 1 | 5.2167 | 2022-03-22 14:21 | 2022-03-25 17:00 | 2022-04-01 07:00 | 2022-03-25 17:00 | 2022-04-01 12:13 |  |  | Attended site and completed pre start paperwork andsigned in. Met with boilertronics. Adjusted bms and setup a heating call to start boiler. Kept in contact with boiler tech and increased load as required. Once boilertech had finished I put set points back as found.Completed paperwork.
MSA-DCA | WA6393884 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Open Storage Area - Freezer is running too high - Leaking water | Refrigeration | Freezers | 1475.94 | Pass | Fail | 0 | 0 | 5.2 | 2022-12-29 11:29 | 2022-12-29 13:29 | 2022-12-29 11:29 | 2022-12-29 15:29 | 2022-12-29 16:41 |  |  | Whilst undertaking maintenance found freezer stuck on defrost with large puddles of water on floor around outside of room. Investigated and advised Sue. Raised job. Found:1. Room temperature of 9.8C. 2. Controller had not terminated defrost needs replacement.3. On manually terminating defrost evaporate fans cam on immediately - no delay.4. Compressor did not come on.5. Found pressure control faulty, bellows engaged but internal switch not making connection. - needs replacement.6. Bypassed and tested system found unit short of refrigerant. 7. Noted oil / signs of leak on suction valve and pressure controller lines.- leaks needs fixing.8. Puddles on floor external to room indicate damaged sealed and potential moisture penetration into panels thus causing ice and damage. Damaged floor plate below door indicated ice damage. Room may need to be disassembled and dried before being reassembled to prevent further damage. Tagged out and isolated. Door left open.To be quoted.
MSA-DTAG | WA5325529 | 1 | OCS SERVICES PTY LTD | Level 14 - Magistrates Chambers - COVID clean of chambers 14.06 on level 14 - see details | Cleaning | Emergency Cleans |  | Pass | Pass | 0 | 0 | 5.2 | 2022-04-14 09:53 | 2022-04-19 17:00 | 2022-04-19 11:48 | 2022-04-19 17:00 | 2022-04-19 17:00 |  |  | Covid clean
MSA-DTAG | WA5676914 | 3 | SCAVENGER SUPPLIES PTY LTD | Ground - FIP - See notes below | Fire Protection Services | Fire Protection - Monitor System | 428.86 | Pass | Pass | 0 | 0 | 5.1833 | 2022-07-25 11:25 | 2022-08-01 17:00 | 2022-07-30 07:00 | 2022-08-01 17:00 | 2022-07-30 12:11 |  |  | Mechanical shutdown complete. Report to follow
MSA-DFES | WA5490937 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - Laundry - Packaged Sullage Chamber Alarm light on | Plumbing & Drainage | Water | 741.55 | Pass | Pass | 0 | 0 | 5.1333 | 2022-06-03 10:26 | 2022-06-09 17:00 | 2022-06-07 07:52 | 2022-06-09 17:00 | 2022-06-07 13:00 |  |  | Attended site for ground level laundry packaged sullage pump alarm light on upon inspection I found that the pump itself is working but there is a possible fault with the sensor causing it to sound thealarm will have to replace this will have to organise A subcontractor come out and replace the sensor
MSA-DTWD | WA6393995 | 2 | Precise Air Group | Chiller is dropping in and out continuously, BMS also showing pattern of the issue (see notes) | Refrigeration | Chiller | 287.17 | Pass | Pass | 0 | 0 | 5.0833 | 2022-12-29 14:44 | 2023-01-04 17:00 | 2023-01-04 07:33 | 2023-01-04 17:00 | 2023-01-04 12:38
MSA-DTWD | WA6414971 | 2 | CLEVELAND COMPRESSED AIR SERVICES | Motor vehicle service area -Faulty connections to portable reels | Equipment | Compressors, Generators | 1068.9 | Fail | Fail | 0 | 0 | 5.0833 | 2023-01-11 11:25 | 2023-01-16 17:00 | 2023-01-17 08:00 | 2023-01-16 17:00 | 2023-01-17 13:05
MSA-DTWD | WA6292028 | 3 | AWB Co. | Remove Damaged Bollard and pave over , at entry to rear carpark off Fielder Street | Paving & Roadworks | Paving | 1698.42 | Pass | Pass | 0 | 0 | 5.05 | 2022-11-29 07:20 | 2022-12-05 17:00 | 2022-12-05 07:00 | 2022-12-05 17:00 | 2022-12-05 12:03 |  |  | Works completed
MSA-DFES | WA6129418 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground-Female and Male Toilets in the amenities Room keep losing water in them | Plumbing & Drainage | Toilets/Cisterns | 549.04 | Pass | Pass | 0 | 0 | 5.0092 | 2022-10-27 14:48 | 2022-11-01 17:00 | 2022-11-01 08:45 | 2022-11-01 17:00 | 2022-11-01 13:46 |  |  | Attended site for ground female male toilets in the amenities room keep losing water in them I’ve talked to site they’ve told me that every 3 to 4 days when the toilets are not in use that they lose the water in the bowl upon inspection I have inspected the movies rooms and toilets are flushing through to the IRS which they are I have also inspected the engine room toilets which is working after doing several toilet paper test and I found that awful of the toilets are clearing correctly and the drainage systems running as intended I ran the drain machine down from the gully as far As I can reach with the drain machine which is 8 rods I have not come across any blockages I’ve gone down as there was a potential of having a partial blockage in the line after I’ve tested again everything is working correctly cleaned up packed up
MSA-DCA | WA5098338 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Humidity levels are faulty | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2072.825 | Fail | Fail | 4 | 4 | 5 | 2022-02-01 08:45 | 2022-02-02 17:00 | 2022-03-01 08:00 | 2022-02-02 17:00 | 2022-03-01 13:00 |  |  | Attended site, signed and accessed the BMS, Found faults with RO storage tanks demineralised water levels high and low alarms. Checked the RO system, pumps and water feeds. A high level sensor intermittently faults sending the ro water tank levels to fluctuate. RO controls Logic has been temporarily adjusted to prevent low water levels until a new sensor is installed.
MSA-DTAG | WA5127754 | 3 | PPM Project Painting & Maintenance | Wall next to footpath, McIver side - Graffiti on the side wall (RHS) of courthouse above see notes | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 5 | 2022-02-14 14:06 | 2022-02-21 17:00 | 2022-02-15 08:00 | 2022-02-21 17:00 | 2022-02-15 13:00 |  |  | Job completed - Prepare by cleaning surface. Apply one coat of oil based sealer to prevent from bleeding through. Apply two coats of low Sheen Acrylic to match existing
MSA-DTWD | WA5312151 | 3 | AWB Co. | Water leak - Outside of A45 and 1 x next to void near A38 stairs | Roofing | Metal Roofing | 989 | Pass | Pass | -1 | -1 | 5 | 2022-04-11 11:22 | 2022-04-20 17:00 | 2022-04-14 06:30 | 2022-04-20 17:00 | 2022-04-14 11:30 |  |  | Attend, investigated multiple areas of possible water ingress, sealed multiple areas and re-fixed loose wall claddingsections.Please note surface rust is present to many areas.
MSA-DTWD | WA5488678 | 1 | CLEVELAND COMPRESSED AIR SERVICES | J126 - Reconnect Air Hose at height - EWP required | Equipment | Compressors, Generators | 1250 | Pass | Pass | 0 | 0 | 5 | 2022-06-02 14:50 | 2022-06-03 17:00 | 2022-06-03 08:00 | 2022-06-03 17:00 | 2022-06-03 13:00 |  |  | Supplied EWP hireRe-secured flexible dropper from high levelAdjusted support cable to flexible hoseTested all ok
MSA-DTWD | WA5565460 | 2 | Protek 24/7 Building & Maintenance | Roof - External above stairwells - build-up of leaves in the box gutters | Building | General Building | 560.52 | Fail | Fail | 0 | 0 | 5 | 2022-06-22 08:02 | 2022-06-27 17:00 | 2022-06-30 11:00 | 2022-06-27 17:00 | 2022-06-30 16:00 |  |  | Cleaned out gutters and Installed mesh
MSA-DTWD | WA5567159 | 3 | AWB Co. | 3B7 - 7 faulty lights | Electrical | Lighting, Internal | 1047.56 | Fail | Fail | 5 | 5 | 5 | 2022-06-23 15:50 | 2022-06-30 17:00 | 2022-08-04 09:30 | 2022-06-30 17:00 | 2022-08-04 14:30 |  |  | Attended site signed in jsa completed. Removed and disposed of x7 fittings in 3B5. Replaced with new 40w led batterns. All tested and okJob completed
MSA-DTWD | WA5584163 | 2 | Schneider Electric Australia Pty Ltd | Entry foyer-Access Control System fault | Security | Access Control |  | Pass | Pass | 0 | 0 | 5 | 2022-07-05 07:51 | 2022-07-07 17:00 | 2022-07-06 11:00 | 2022-07-07 17:00 | 2022-07-06 16:00 |  |  | Restarted controller with event schedules and confirmed all points were active.
MSA-DTWD | WA5660199 | 2 | AWB Co. | Level G.L covered corridor-Lights not coming on the covered walkway outside staff room | Electrical | Lighting, Internal | 997.05 | Pass | Pass | 0 | 0 | 5 | 2022-07-19 07:30 | 2022-07-21 17:00 | 2022-07-19 08:00 | 2022-07-21 17:00 | 2022-07-19 13:00 |  |  | Attended site signed in jsa completed. Spoke with kevin about security lighting. Found x3 rcd’s tripped in two boards, reset as some water/moisture must have got in14 globes faulty and x 2 ballasts. Replaced all and tested. Stil not on as pe cell faulty so replaced x2 pe cell as requested by site. All working now correctly.Job completed
MSA-DTWD | WA5673285 | 2 | Damian Rak Electrical Pty Ltd | Various security lights around campus faulty x 15 | Electrical | Lighting, External |  | Fail | Fail | 9 | 9 | 5 | 2022-07-20 13:37 | 2022-07-25 17:00 | 2022-09-27 11:00 | 2022-07-25 17:00 | 2022-09-27 16:00 |  |  | changed lights LED
MSA-DCA | WA6019619 | 0 | EQUANS Mechanical Services (WA) Pty Limited | level 4 plant room - pump failiar spraying out water | Building | Materials | 694.67 | Pass | Fail | 0 | 0 | 5 | 2022-10-13 06:50 | 2022-10-13 08:50 | 2022-10-13 08:00 | 2022-10-13 10:50 | 2022-10-13 13:00 |  |  | Attended site. Investigated pump spraying water in level 4 plantroom. Found water spraying from heating water booster pump. Isolated power to motor. Isolated supply and return and opened bypass valve. Drained water from lines and disconnected the pump. Roped pump down to the ground. Accessed bms and isolated booster pump. Dropped pump off at repairers. Returned to site and vacuum water and mopped. Quoted for repairs and installation of pump and carried out paperwork.
MSA-DFES | WA6113013 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | New Building - Front Garden - Light which illuminates flagpole does not work - Circuit keeps trippin | Electrical | Lighting, External | 632.76 | Pass | Pass | -1 | -1 | 5 | 2022-10-24 08:37 | 2022-10-31 17:00 | 2022-10-25 12:30 | 2022-10-31 17:00 | 2022-10-25 17:30 |  |  | arrived on site to fix faulty light fitting illuminating flag. Found there to be an inline join in the conduit which was a dead short to E-A and E-N. Ran new cabling and fixed lighting circuit. Tested light circuit was working correctly and left site
MSA-DTWD | WA6128923 | 2 | JEM Carpentry | 843B-Faulty Sliding Doors | Building | Doors |  | Pass | Pass | -1 | -1 | 5 | 2022-10-27 09:17 | 2022-11-01 17:00 | 2022-10-27 09:30 | 2022-11-01 17:00 | 2022-10-27 14:30 |  |  | Repairs to doors
MSA-DTWD | WA6357291 | 3 | Equans Mechanical Services Australia | Level 8 plant room - Return Air Fan for AHU 2 noisy | Equipment | Electrical Equipment | 709.62 | Pass | Pass | -1 | -1 | 5 | 2022-12-05 12:11 | 2022-12-12 17:00 | 2022-12-07 11:00 | 2022-12-12 17:00 | 2022-12-07 16:00 |  |  | apprentice to assist as confined space
MSA-DTWD | WA6404975 | 3 | AWB Co. | electrical breaker on the freezer circuit constantly tripping. | Electrical | General Electrical | 953.16 | Pass | Pass | 0 | 0 | 5 | 2023-01-09 10:43 | 2023-01-16 17:00 | 2023-01-13 08:00 | 2023-01-16 17:00 | 2023-01-13 13:00
MSA-DTWD | WA6463426 | 1 | Precise Air Group | H003 - West Evap A/C not cooling only blowing warm air | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1246.18 | Pass | Pass | 0 | 0 | 5 | 2023-01-17 10:01 | 2023-01-18 17:00 | 2023-01-18 11:00 | 2023-01-18 17:00 | 2023-01-18 16:00
MSA-DTWD | WA6516646 | 1 | Lane's Plumbing | Lot 301 - Report of significant water leak near piggery - possible busted pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 5 | 2023-01-23 13:38 | 2023-01-24 17:00 | 2023-01-23 14:00 | 2023-01-24 17:00 | 2023-01-23 19:00
MSA-DTWD | WA6540199 | 2 | AWB Co. | Lighting incorrectly wired (see notes) | Electrical | Lighting, Internal | 566.53 | Pass | Pass | -1 | -1 | 5 | 2023-02-09 09:00 | 2023-02-14 17:00 | 2023-02-10 06:30 | 2023-02-14 17:00 | 2023-02-10 11:30
MSA-DCA | WA6653993 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Boiler 1 in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 786.945 | Pass | Pass | 0 | 0 | 5 | 2023-02-21 08:51 | 2023-02-22 17:00 | 2023-02-21 11:00 | 2023-02-22 17:00 | 2023-02-21 16:00
MSA-DTWD | WA5086695 | 2 | Equans Mechanical Services Australia | Building 2 - Level 3 - plantroom - AHU L1-8 SA fan in fault - not running | Air Conditioning | Room Air Conditioners | 757.64 | Fail | Fail | 3 | 3 | 5 | 2022-01-21 11:38 | 2022-01-27 17:00 | 2022-02-18 07:00 | 2022-01-27 17:00 | 2022-02-18 12:00 |  |  | Attended site and carried out investigations of reported temp issue. On investigation it was noted that there was very low air flow in office. On inspection split found to have occured in duct work. Parts source for repair. Second tech completed. Confirmed no air leakage. Confirmed all bms setting back to normal. Work area left tidy.
MSA-DCA | WA5087536 | 2 | Earth & Water Pty Ltd | leak on 40mm pipe | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 5 | 2022-01-24 10:34 | 2022-01-28 17:00 | 2022-01-24 12:00 | 2022-01-28 17:00 | 2022-01-24 17:00 |  |  | job completed - Arrived on site, assessed the damage to the 40mm line and the location of the new sprinkler between the steel statue and therock garden bed.Dug a trench from the sprinkler to the location of the new sprinkler, ran ez tube and fitted a threaded tee.Repaired the 40mm line and replaced the tee that feeds the 25mm.****found another 40mm line that was badly damaged and full of mud and dirt, however after running all the zones there wasno sign of the line being in use. Most likely a spare line or old line.***EURRaised the sprinklers that were too low and cleaned out around the heads that weren't popping up properly.Pruned overgrown shrubs and plants in the 4 garden beds near cleaners shed
MSA-DTAG | WA5141570 | 3 | PPM Project Painting & Maintenance | Level 4 - Male public toilet - Graffiti on toilet ceiling | Building | Internal Walls |  | Pass | Pass | 0 | 0 | 5 | 2022-02-16 11:06 | 2022-02-23 17:00 | 2022-02-23 08:30 | 2022-02-23 17:00 | 2022-02-23 13:30 |  |  | Job completed - Prepare by cleaning surface. Apply one coat of acrylic sealer Apply two coats of ceiling flat Acrylic to match existing through ceiling
MSA-DTWD | WA5301873 | 2 | M Construction (WA) | D block - Canteen - Kitchen - replace 3 broken wall tiles | Building | Internal Walls | 515.63 | Pass | Pass | 0 | 0 | 5 | 2022-04-01 13:32 | 2022-04-06 17:00 | 2022-04-04 07:00 | 2022-04-06 17:00 | 2022-04-04 12:00 |  |  | Replace 3 broken tiles
MSA-DTWD | WA5308071 | 2 | AWB Co. | F17 Storeroom - Light Switch no longer functional | Electrical | General Electrical | 999.67 | Pass | Pass | 0 | 0 | 5 | 2022-04-08 08:46 | 2022-04-13 17:00 | 2022-04-12 07:30 | 2022-04-13 17:00 | 2022-04-12 12:30 |  |  | Attended site signed in completed jsa. Found switch no longer working. Site asked for a sensor in middle of room. Found sensor and mounted in room. Did junction in mounting block. Ran cables from light to light and blanked of switch. All works fine tested ok.*** job completed ***
MSA-DTWD | WA5406865 | 3 | AWB Co. | faulty ilghting | Electrical | Lighting, Internal | 2168.88 | Pass | Pass | -1 | -1 | 5 | 2022-05-11 06:56 | 2022-05-17 17:00 | 2022-05-12 07:00 | 2022-05-17 17:00 | 2022-05-12 12:00 |  |  | Attended site signed in jsa completed. Spoke to Dave gaff about jobs and got keys and list of lights out in B2 building. Replaced various tubes in building. All tested fine and working.*** job completed ****
MSA-DTWD | WA5407404 | 2 | AWB Co. | Staff Car Park - Ground -please see details below | Electrical | General Electrical | 1636.9 | Fail | Fail | 1 | 1 | 5 | 2022-05-11 11:34 | 2022-05-16 17:00 | 2022-05-26 07:00 | 2022-05-16 17:00 | 2022-05-26 12:00 |  |  | Replace 3x Faulty street lighting in staff carpark. 2x lights are working, 1x didn’t work and had to further investigate fault using the EWP. Found no power to cable. Informed site. Cost have gone over BRAF
MSA-DTWD | WA5413227 | 1 | Protek 24/7 Building & Maintenance | B67 & B68 (rooms joined) - Roof leak | Building | General Building | 1000 | Pass | Pass | 0 | 0 | 5 | 2022-05-12 09:46 | 2022-05-13 17:00 | 2022-05-13 07:00 | 2022-05-13 17:00 | 2022-05-13 12:00 |  | WCAPPR | Repaired Roof leak - B67 & B68
MSA-DTWD | WA5469088 | 2 | AWB Co. | Customer Service - 1F21 - Blind assy behind air conditioner has fallen down | Building | Curtains & Blinds | 395 | Fail | Fail | 0 | 0 | 5 | 2022-05-20 15:46 | 2022-05-25 17:00 | 2022-05-26 07:00 | 2022-05-25 17:00 | 2022-05-26 12:00 |  |  | Customer Service - 1F21 - Blind assy behind air conditioner has fallen down
MSA-DTWD | WA5486326 | 2 | AWB Co. | E202 - Replace lights not working | Electrical | General Electrical | 998.3 | Pass | Pass | -1 | -1 | 5 | 2022-06-01 08:06 | 2022-06-07 17:00 | 2022-06-02 09:15 | 2022-06-07 17:00 | 2022-06-02 14:15 |  |  | Job complete
MSA-DTWD | WA5682294 | 2 | Techworks Electrical | SK2-lights are flickering, please replace | Electrical | Lighting, Internal | 1542.72 | Pass | Pass | 0 | 0 | 5 | 2022-07-29 08:04 | 2022-08-03 17:00 | 2022-08-03 06:00 | 2022-08-03 17:00 | 2022-08-03 11:00 |  |  | Replaced failed 230mm downlights in E block with new 230mm led downlight .1x outside restaurant kitchen.1x inside restaurant customer toilet.Replaced failed 250mm square downlight outside directors office with new 250mm led square downlight.Replaced 28w tubes and electronic ballast in E block SK2 and restaurant kitchen.
MSA-DTWD | WA5686829 | 3 | AWB Co. | 9 x Flickering lights – C601 | Electrical | Lighting, Internal | 998.66 | Pass | Pass | -1 | -1 | 5 | 2022-08-01 11:07 | 2022-08-08 17:00 | 2022-08-03 07:00 | 2022-08-08 17:00 | 2022-08-03 12:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job and got list. Went around site and counted up faulty lighting to see what we needed. Replaced some lighting in B1 with site supplied tubes. Went to wholesaler to pick up parts. Returned to site and replaced remaining of faulty lighting. Took after pictures. Lighting list is complete. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5715267 | 2 | Techworks Electrical | S Block - First Floor - 2 long flouros out near electrical cupboards | Electrical | Lighting, Internal | 1204.365 | Pass | Pass | 0 | 0 | 5 | 2022-08-12 12:46 | 2022-08-17 17:00 | 2022-08-16 10:00 | 2022-08-17 17:00 | 2022-08-16 15:00 |  |  | Replaced drivers in lights and re connected the led strip's back together
MSA-DTWD | WA5753026 | 2 | Workzone Pty Ltd | L Block - Horticulture Area -Tunnel green house - Cover has been smashed to pieces | Building | General Building | 870 | Pass | Pass | 0 | 0 | 5 | 2022-08-17 13:20 | 2022-08-22 17:00 | 2022-08-22 09:00 | 2022-08-22 17:00 | 2022-08-22 14:00 |  |  | Cut up and remove metal tunnel greenhouse
MSA-DFES | WA5794387 | 3 | AWB Co. | external perimeter of all buildings increasing mold at base of external walls facing into Wellington | Building | External Walls | 818.42 | Pass | Pass | 0 | 0 | 5 | 2022-08-24 14:37 | 2022-08-31 17:00 | 2022-08-28 07:00 | 2022-08-31 17:00 | 2022-08-28 12:00 |  |  | clean the mould etc from the exterior of the Fire Station on Wellington Street. Work completed on Sunday 28 August2022.
MSA-DTWD | WA5796056 | 2 | Techworks Electrical | South side walkway lights not working | Electrical | Lighting, External | 135.15 | Pass | Pass | 0 | 0 | 5 | 2022-08-26 08:40 | 2022-08-31 17:00 | 2022-08-31 07:00 | 2022-08-31 17:00 | 2022-08-31 12:00 |  |  | Trent Broom (31/08/2022) - Work NoteSouth side Path way lights require replacement Light pole numbers 32 to 38 See photo for old pole
MSA-DTWD | WA5976873 | 2 | AWB Co. | Swicthboard fuses blowing when swictehd to Emergency lights | Electrical | Distribution Board | 609.33 | Pass | Pass | 0 | 0 | 5 | 2022-09-27 11:57 | 2022-09-30 17:00 | 2022-09-30 09:00 | 2022-09-30 17:00 | 2022-09-30 14:00 |  |  | Job complete
MSA-DTWD | WA5987802 | 3 | AWB Co. | Level 1 - Central Lift foyer and corridor - Lights out | Electrical | Lighting, Internal | 1179.08 | Pass | Pass | 0 | 0 | 5 | 2022-10-03 14:50 | 2022-10-10 17:00 | 2022-10-07 11:15 | 2022-10-10 17:00 | 2022-10-07 16:15 |  |  | Job complete
MSA-DTWD | WA6000824 | 3 | AWB Co. | B200 - Lights out and buzzing x 3 | Electrical | Lighting, Internal | 1516.03 | Pass | Pass | 0 | 0 | 5 | 2022-10-10 10:44 | 2022-10-17 17:00 | 2022-10-14 07:00 | 2022-10-17 17:00 | 2022-10-14 12:00 |  |  | Job complete
MSA-DTWD | WA6000827 | 3 | AWB Co. | Staff toilets 304 - 2 x lights out | Electrical | Lighting, Internal | 1981.33 | Pass | Pass | 0 | 0 | 5 | 2022-10-10 10:48 | 2022-10-17 17:00 | 2022-10-14 12:00 | 2022-10-17 17:00 | 2022-10-14 17:00 |  |  | Job complete
MSA-DTWD | WA6014427 | 3 | AWB Co. | Hand rails to bike store paint has peeled off | Painting | External | 873.42 | Fail | Fail | 1 | 1 | 5 | 2022-10-12 09:08 | 2022-10-19 17:00 | 2022-10-28 07:00 | 2022-10-19 17:00 | 2022-10-28 12:00 |  |  | painting works completed
MSA-DCA | WA6021384 | 0 | TK Elevator Australia Pty Ltd | Basement Lift 6-lift is in fault | Lifts | Lifts |  | Pass | Fail | 0 | 0 | 5 | 2022-10-14 07:31 | 2022-10-14 09:31 | 2022-10-14 08:15 | 2022-10-14 11:31 | 2022-10-14 13:15 |  |  | Lift6 Loading Dock-Elevator > MR > Hydraulic :Lift ooo on top floor, doors opening and closing, door shoe broken and wedged under door tracks. Lift back in service.to be closed at $0 cost
MSA-DCA | WA6082538 | 1 | EQUANS Mechanical Services (WA) Pty Limited | HBRC - VSD IN ALARM | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 5 | 2022-10-18 15:37 | 2022-10-19 17:00 | 2022-10-19 10:00 | 2022-10-19 17:00 | 2022-10-19 15:00 |  |  | Power reset to vsd and vsd alarm reset on bms. No other fault found.
MSA-DCA | WA6126592 | 2 | Precise Air Group | Aircon not working – Large meeting room | Air Conditioning | Room Air Conditioners | 655.33 | Pass | Pass | 0 | 0 | 5 | 2022-10-25 12:29 | 2022-10-28 17:00 | 2022-10-26 07:30 | 2022-10-28 17:00 | 2022-10-26 12:30 |  |  | Attended site and gained access to meeting room. Ran system up and tested operation on heating and cooling, found system operational and reaching set points. Spoke to programmed contact to let them know and was asked to drop set point slightly. While checking the system, found that the evaporator motor contactor was very loud and making poor connection, suspect it would fail soon. Picked up new contactor and overload from supplier, returned to site to swap out. Tested new contactor, operating correctly on inspection. AC18 is very old and past life expectancy, recommend budgeting to upgrade system.
MSA-DCA | WA6293677 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - HBC Chiller 1 & 2 in fault again | Air Conditioning | Materials | 596.84 | Pass | Pass | 0 | 0 | 5 | 2022-11-30 10:16 | 2022-12-01 17:00 | 2022-11-30 10:20 | 2022-12-01 17:00 | 2022-11-30 15:20 |  |  | Reset power to chiller after activation of alarm. Tested operation of chiller after reset, now chiller back online and working again.
MSA-DTWD | WA6407989 | 2 | Equans Mechanical Services Australia | Cafeteria L2 - Refrigerated Display case getting warm | Refrigeration | Refrigerators | 582.27 | Pass | Pass | 0 | 0 | 5 | 2023-01-10 13:31 | 2023-01-13 17:00 | 2023-01-12 10:00 | 2023-01-13 17:00 | 2023-01-12 15:00
MSA-DFES | WA6426121 | 2 | AWB Co. | Engine Bay - Repair and paint roof where cable was repaired | Painting | Internal | 873.42 | Fail | Fail | 2 | 2 | 5 | 2023-01-12 14:43 | 2023-01-17 17:00 | 2023-02-01 07:00 | 2023-01-17 17:00 | 2023-02-01 12:00
MSA-DTWD | WA6482341 | 2 | Precise Air Group | Mclarty -Q Block - chiller pump failure- not cooling | Refrigeration | Chiller | 697.74 | Pass | Pass | -1 | -1 | 5 | 2023-01-18 09:21 | 2023-01-23 17:00 | 2023-01-19 07:30 | 2023-01-23 17:00 | 2023-01-19 12:30
MSA-DTAG | WA6509574 | 2 | AWB Co. | Bike Shed- Light cable damaged see notes | Electrical | General Electrical | 621.83 | Pass | Pass | -1 | -1 | 5 | 2023-01-20 12:21 | 2023-01-25 17:00 | 2023-01-20 12:22 | 2023-01-25 17:00 | 2023-01-20 17:22
MSA-DTWD | WA6528600 | 1 | Equans Mechanical Services Australia | aircon not working | Air Conditioning | Room Air Conditioners | 489.87 | Fail | Fail | 0 | 0 | 5 | 2023-02-02 11:08 | 2023-02-03 17:00 | 2023-02-06 07:30 | 2023-02-03 17:00 | 2023-02-06 12:30
MSA-DTWD | WA6540480 | 0 | WESTERN IRRIGATION PTY LTD | Green house - Water leak under ground | Plumbing & Drainage | Water | 736.84 | Pass | Fail | 0 | 0 | 5 | 2023-02-09 11:20 | 2023-02-09 13:20 | 2023-02-09 11:30 | 2023-02-09 15:20 | 2023-02-09 16:30
MSA-DTWD | WA6540655 | 3 | AWB Co. | 5 Fluorescents and 2 x High Bay lights need replacing. EWP access only | Electrical | General Electrical | 1816.72 | Pass | Pass | 0 | 0 | 5 | 2023-02-09 12:36 | 2023-02-16 17:00 | 2023-02-14 07:00 | 2023-02-16 17:00 | 2023-02-14 12:00
MSA-DTWD | WA6560578 | 3 | Equans Mechanical Services Australia | Room - N-122 - Broken fridge | Refrigeration | Refrigerators | 489.87 | Pass | Pass | -1 | -1 | 5 | 2023-02-13 11:15 | 2023-02-20 17:00 | 2023-02-16 10:30 | 2023-02-20 17:00 | 2023-02-16 15:30
MSA-DTWD | WA6585716 | 3 | AWB Co. | Ceiling Lights - Need replacing | Electrical | Lighting, Internal | 1302.73 | Pass | Pass | 0 | 0 | 5 | 2023-02-16 10:22 | 2023-02-23 17:00 | 2023-02-20 09:00 | 2023-02-23 17:00 | 2023-02-20 14:00
MSA-DCA | WA6681422 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Level 5 - Chiller 2 in fault | Refrigeration | Chiller |  | Pass | Fail | 0 | 0 | 5 | 2023-03-02 08:42 | 2023-03-02 10:42 | 2023-03-02 09:00 | 2023-03-02 12:42 | 2023-03-02 14:00
MSA-DFES | WA5469550 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Rheem hot water tank has burst - leaking cold water from behind | Plumbing & Drainage | HWS/Units Electric & Gas | 4351.7 | Fail | Fail | 4 | 4 | 4.9833 | 2022-05-21 20:01 | 2022-05-21 22:01 | 2022-06-16 06:50 | 2022-05-22 00:01 | 2022-06-16 11:49 |  | WACCES | New hot water tank installed. All working correctly.
MSA-DCA | WA6113471 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 in fault | Refrigeration | Chiller | 930.29 | Pass | Pass | 0 | 0 | 4.9167 | 2022-10-24 11:52 | 2022-10-25 17:00 | 2022-10-25 07:45 | 2022-10-25 17:00 | 2022-10-25 12:40 |  |  | SEE REPORT
MSA-DTWD | WA4995048 | 2 | Precise Air Group | Block A - Level 1 - A52 - BMS is not showing any readings | Air Conditioning | Building HVAC Maintenance (Major Plant) | 141.29 | Pass | Pass | 0 | 0 | 4.8667 | 2022-01-10 09:46 | 2022-01-13 17:00 | 2022-01-10 10:30 | 2022-01-13 17:00 | 2022-01-10 15:22 |  |  | While on site found bms unable to communicate with equipment. Attempted reset of bms as well as modem butwas unsuccessful. Po sent to elecmec.
MSA-DTWD | WA5239671 | 2 | SENTINEL LOCK SERVICE PTY LTD | Block 3 - Ground - 3G1 - Switchboard lock faulty | Security | Locksmith | 219.93 | Fail | Fail | 1 | 1 | 4.8333 | 2022-03-16 14:12 | 2022-03-21 17:00 | 2022-03-30 08:45 | 2022-03-21 17:00 | 2022-03-30 13:35 |  | WACCES | Block 3 -3Go switchboard lock faulty.Lock replaced
MSA-DFES | WA5569334 | 3 | SONTEC WA PTY LTD | Security Cameras - Sontec to attend site and check cameras | Security | CCTV Surveillance | 1202.5 | Pass | Pass | -1 | -1 | 4.8333 | 2022-06-27 13:40 | 2022-07-04 17:00 | 2022-06-28 13:00 | 2022-07-04 17:00 | 2022-06-28 17:50 |  |  | 28/6/22 - Dylan Parslow, Joshua ParkInvestigated issues with CCTV cameras disconecting from software.Reterminated entry door camera.Cameras reconnecting to server but not refreshing image at workstation.
MSA-DFES | WA5200835 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Few lights blow through station - please check all lights - see notes | Electrical | Lighting, Internal | 708.94 | Pass | Fail | 0 | 0 | 4.75 | 2022-03-02 09:30 | 2022-03-02 11:30 | 2022-03-02 11:00 | 2022-03-02 13:30 | 2022-03-02 15:45 |  |  | Attended site and replaced blown lights in old fire station. Replaced the following; 1 x Pe cell, 2 x spot lamp, 1 x 12v lamp, 1 x 36W T8 fluro, 4 x 18W T8 fluro, 1 x S10 starter, 4 x S2 starter. Tested and notified staff.
MSA-DCA | WA5298152 | 2 | FCT SURFACE CLEANING | Urban Orchard - Ground – external - Graffiti on garden bed yellow bench top. Cleaners cannot remove | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 4.75 | 2022-03-31 15:19 | 2022-04-05 17:00 | 2022-04-04 06:30 | 2022-04-05 17:00 | 2022-04-04 11:15 |  |  | Removed graffiti from urban orchard ground around garden bed with yellow benchtop.
MSA-DTWD | WA6258059 | 2 | AHS Services WA Pty Ltd (Anchor) | Pond pump is not running | Plumbing & Drainage | Water | 339.626 | Fail | Fail | 0 | 0 | 4.75 | 2022-11-25 10:19 | 2022-11-30 17:00 | 2022-12-02 08:00 | 2022-11-30 17:00 | 2022-12-02 12:45 |  |  | Replaced pump other pump burnt out
MSA-DFES | WA6393265 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | FF Rear Dorm - Area 18 - Broken Bed Light Fitting (see notes) | Electrical | Lighting, Internal | 396.745 | Pass | Pass | 0 | 0 | 4.75 | 2022-12-28 11:56 | 2023-01-05 17:00 | 2023-01-03 10:30 | 2023-01-05 17:00 | 2023-01-03 15:15
MSA-DFES | WA6408024 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Bay - charging cable has come away from the ceiling | Electrical | General Electrical | 1348.165 | Pass | Pass | 0 | 0 | 4.75 | 2023-01-10 13:55 | 2023-01-11 17:00 | 2023-01-11 06:30 | 2023-01-11 17:00 | 2023-01-11 11:15
MSA-DCA | WA5216743 | 2 | FCT SURFACE CLEANING | Various locations - Graffiti | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 4.75 | 2022-03-11 12:28 | 2022-03-16 17:00 | 2022-03-14 06:15 | 2022-03-16 17:00 | 2022-03-14 11:00 |  |  | job complete - Outside the entrance of the SLWA carpark next to the red booster cabinet• Around the back of the Blue Room• Wall next to Pretzels under the SLWA walkway entrance• Paving out the front of PICA Bar
MSA-DTWD | WA5231117 | 2 | SPECIALISED TREE SERVICE | Muresk Road after main entrance - Tree branches overhanging road dangerous to school bus. | Landscaping & Gardening | Tree Lopping |  | Fail | Fail | 6 | 6 | 4.75 | 2022-03-15 09:30 | 2022-03-18 17:00 | 2022-04-28 07:00 | 2022-03-18 17:00 | 2022-04-28 11:45 |  |  | Removal of tree branches
MSA-DFES | WA5460357 | 2 | Protek 24/7 Building & Maintenance | Stores door hinge is breaking away from door frame | Building | Doors | 494.695 | Pass | Pass | -1 | -1 | 4.75 | 2022-05-18 13:19 | 2022-05-23 17:00 | 2022-05-19 09:15 | 2022-05-23 17:00 | 2022-05-19 14:00 |  |  | Repair Door hinge
MSA-DTWD | WA5480945 | 3 | AWB Co. | A Block - Rear Courtyard - Lights not working | Electrical | Lighting, External | 604.66 | Pass | Pass | 0 | 0 | 4.75 | 2022-05-30 09:31 | 2022-06-07 17:00 | 2022-06-07 10:45 | 2022-06-07 17:00 | 2022-06-07 15:30 |  |  | Job complete
MSA-DTWD | WA5796162 | 2 | AWB Co. | D, N & E Blocks - Driveway lights breaker at main switchboard tripping and requires resetting daily | Electrical | Distribution Board | 523.8475 | Pass | Pass | 0 | 0 | 4.75 | 2022-08-26 09:09 | 2022-08-31 17:00 | 2022-08-29 07:00 | 2022-08-31 17:00 | 2022-08-29 11:45 |  |  | Attended site and signed in. Completed JSA. Located all carpark lights controlled by B7 in suspect of tripping. Found 9 x poles on the circuit. 1 pole is isolated last year due to a underground fault in the cabling. Inspected and tested the cabling from switchboard and found short on both active and neutral. Inspected and tested at each pole 1 by 1. Could not access pole 2 as the decking is wrapped around it. Come to pole 5 and when splitting the cables found fault to disappear. Reconnected and found fault was back. Removed cabling and put in join outside of the pole and found cabling all good. Resulted in the terminal block inside the pole is faulty and broken down to earth. Removed and insulated from the base to pole. Reconnected Cabling feeds and pole tops to all poles. Retested before energising and found no fault present. Turned on B7 carpark lighting again and walked to check all the fittings working besides the isolated pole. No fault found now. All is working. Closed up all pol
MSA-DTWD | WA5799734 | 3 | AWB Co. | Intercom Faulty | Electrical | General Electrical | 737.3975 | Pass | Pass | 0 | 0 | 4.75 | 2022-08-30 13:53 | 2022-09-06 17:00 | 2022-09-06 11:30 | 2022-09-06 17:00 | 2022-09-06 16:15 |  |  | Job complete
MSA-DTWD | WA6674495 | 2 | CONNECT SECURITY SYSTEMS | Alarm fault 079 has occured on several occasions | Security | Security Management System | 879.08 | Pass | Pass | 0 | 0 | 4.6667 | 2023-02-27 10:24 | 2023-03-02 17:00 | 2023-03-02 08:40 | 2023-03-02 17:00 | 2023-03-02 13:20
MSA-DFES | WA5294313 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Building - FIRE STATION - Ground - Front Yard - see notes below | Plumbing & Drainage | Water | 981.06 | Pass | Pass | 0 | 0 | 4.6667 | 2022-03-28 16:24 | 2022-03-31 17:00 | 2022-03-30 07:20 | 2022-03-31 17:00 | 2022-03-30 12:00 |  |  | Had to replaces a PRV VALVE OUT THE FRONT OF THE FIRE STATION and copper pipe
MSA-DCA | WA5200135 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Fittings have blown off RO Pump and flooded plant room | Air Conditioning | Building HVAC Maintenance (Major Plant) | 417.605 | Fail | Fail | 2 | 2 | 4.65 | 2022-03-01 14:40 | 2022-03-01 16:40 | 2022-03-16 12:21 | 2022-03-01 18:40 | 2022-03-16 17:00 |  |  | Accessed the pland room and found the RO pump discharge line had blown off. Isolated the RO plant and drove to suppliers to collect new lines and fittings. Returned to site, fitted new lines and fittings, reinstated the pump and checked and tested. RO plant up and running. New pressure gauge is required.
MSA-DCA | WA5296315 | 0 | EQUANS Mechanical Services (WA) Pty Limited | plant room - isolate temporally and reinstate all mechanical services | Air Conditioning | Room Air Conditioners | 261.63 | Pass | Fail | 0 | 0 | 4.6333 | 2022-03-30 11:17 | 2022-03-30 13:17 | 2022-03-30 12:19 | 2022-03-30 15:17 | 2022-03-30 16:57 |  |  | Returned to site gained access to plant area and restarted isolated critical cooling equipment. Confirmed operation restored to chillers, boiler and water pump sets. Confirmed no active equipment faults. Confirmed plant working as per BMS and buildings requirements. Work area has been left tidy. Plant operating in auto function.
MSA-DCA | WA5087098 | 1 | EQUANS Mechanical Services (WA) Pty Limited | please attend and check the A/C for the museum after the water leak | Air Conditioning | Materials | 345.35 | Pass | Pass | 0 | 0 | 4.6 | 2022-01-23 18:55 | 2022-01-24 17:00 | 2022-01-24 07:00 | 2022-01-24 17:00 | 2022-01-24 11:36 |  |  | Received notification of job and atteneded site. Gained access and carried out assessment. Located buckets in gallery and checked ducted work and pipe work in celling for signs of corrosion. Note there is no mech plant located directly above or around area. Only ductwork. On the floor above there a wet area for the lab witch had a fun hood with deionised water plumbed to it and a sink. Confirmed no water pooling. Thei will be rechecked for further signs of leaking during the PM inspection. Site FM Pey-Sue has been updated. Was area left tidy.
MSA-DFES | WA4985422 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | SimCentre - Ground - Female Toilet - cold water tap is very stiff and likely to left in open | Plumbing & Drainage | Water | 216.85 | Pass | Pass | -1 | -1 | 4.5667 | 2021-12-29 13:14 | 2022-01-06 17:00 | 2021-12-30 08:15 | 2022-01-06 17:00 | 2021-12-30 12:49 |  | WCAPPR | Serviced taps
MSA-DCA | WA5207658 | 2 | Precise Air Group | Water dripping from ceiling, where Air conditioner runs - see notes below | Air Conditioning | Room Air Conditioners | 518.05 | Pass | Pass | 0 | 0 | 4.55 | 2022-03-08 15:18 | 2022-03-11 17:00 | 2022-03-10 12:03 | 2022-03-11 17:00 | 2022-03-10 16:36 |  | WACCES | Insulated pipe
MSA-DCA | WA6526643 | 0 | GPS Plumbing & Gas Services PtyLtd | Ground floor - Hot water system leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 1757.0875 | Pass | Fail | 0 | 0 | 4.55 | 2023-02-01 09:38 | 2023-02-01 11:38 | 2023-02-01 10:42 | 2023-02-01 13:38 | 2023-02-01 15:15
MSA-DTWD | WA6149040 | 3 | AWB Co. | near ramp to train station-Brick paving damage -see notes | Paving & Roadworks | Paving | 928.42 | Pass | Pass | 0 | 0 | 4.5167 | 2022-11-04 11:38 | 2022-11-11 17:00 | 2022-11-10 11:00 | 2022-11-11 17:00 | 2022-11-10 15:31 |  |  | Works completed
MSA-DFES | WA4991193 | 2 | AWB Co. | Ground - Engine Bay - see notes below | Building | Internal Walls | 416.25 | Pass | Pass | 0 | 0 | 4.5 | 2022-01-04 16:38 | 2022-01-07 17:00 | 2022-01-07 07:00 | 2022-01-07 17:00 | 2022-01-07 11:30 |  |  | Patch, touch up and paint panel and surrounds above door
MSA-DTWD | WA5091353 | 1 | Milners Tree Solutions Pty Ltd | Block A - Staff carpark - tree has fallen and needs to be removed | Landscaping & Gardening | General Tree Works | 2800 | Pass | Pass | 0 | 0 | 4.5 | 2022-01-27 08:26 | 2022-01-28 17:00 | 2022-01-28 06:30 | 2022-01-28 17:00 | 2022-01-28 11:00 |  |  | fallen tree removed
MSA-DTWD | WA5098773 | 2 | High Tech Pest Control | Level 1 - plaster area - remove pigeons from plaster area | Pest Control | Specialist Pest | 999.9 | Fail | Fail | 5 | 5 | 4.5 | 2022-02-01 11:20 | 2022-02-04 17:00 | 2022-03-12 07:00 | 2022-02-04 17:00 | 2022-03-12 11:30 |  | WCAPPR | Visit 1 conducted for scope of job 3.2.22, Visit 2 arranged - no show from TAFE 5.2.22 (Saturday morning), Visit 3 booked 12.3.22 and a number of birds baited, collected and removed
MSA-DTWD | WA5098893 | 1 | AWB Co. | F Block - Ground - F100 -3 phase outlet casing damaged and tagged out | Electrical | General Electrical | 1374.44 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-01 12:08 | 2022-02-02 17:00 | 2022-02-02 08:00 | 2022-02-02 17:00 | 2022-02-02 12:30 |  |  | Attended site and signed in. Complete JSA. spoke to fm about the job, located all GPOs with technician in f block, went to wholesaler to pick up parts, returned to site, isolated all GPOs , removed old and damaged GPOs and replaced on original bases, removed old broken GPOs w/isolators that were located on steel ibeams , drilled new holes and tapped them so bolts could be used to fix GPOs to pole, fixed GPOs to pole and wired them up, re energised GPOs and tested , all GPOs working as intended , removed plug tops off of linisher , welder and 10pt press and put heat shrink on knocked parts of cable, tested and tagged them , cleaned up , packed up , completed paperwork, **job completed**
MSA-DTAG | WA5100152 | 2 | EASTERN HILLS ELECTRICAL SERVICE | Ground - Custody - 4 x fluorescents lights faulty | Electrical | Lighting, Internal | 264.78 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-02 11:19 | 2022-02-07 17:00 | 2022-02-07 09:30 | 2022-02-07 17:00 | 2022-02-07 14:00 |  |  | Replaced tubes and starters
MSA-DTWD | WA5101872 | 1 | Critical Fire Protection & Training | Centre Block - Level 1 - Fire Pump & valve room - Fire Alarm - zone 24 - see details | Fire Protection Services | Fire Protection - Monitor System | 589.19 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-03 16:27 | 2022-02-04 17:00 | 2022-02-04 07:30 | 2022-02-04 17:00 | 2022-02-04 12:00 |  |  | Technician investigated alarm on FIP - signs of a slow leak found under valve in pump room - wet fire technician required to investigate and rectifyWhilst on site technician has found EWIS panel in fault - Fire Electrician required to fault find and repair issue with EWISBRAF submitted 4/2/2022 and not approved.
MSA-DTWD | WA5105424 | 0 | Equans Mechanical Services Australia | Canteen kitchen - freezer running warm | Refrigeration | Freezers | 1000 | Pass | Fail | 0 | 0 | 4.5 | 2022-02-04 10:40 | 2022-02-04 12:40 | 2022-02-04 11:00 | 2022-02-04 14:40 | 2022-02-04 15:30 |  |  | Found the two door freezer in the canteen short of gas, picked up pro seal , repaired a gas leak , charged up and put pro seal in the system. Room F5 , found the system short of gas , condenser on the roof. Tighten up the flare nuts couldn't find any other leaks , put seal pro in the system.
MSA-DTWD | WA5163203 | 3 | AWB Co. | North Block - Level 2 - Repair sliding glass doors tracks to North Block Display Boards Level 2 | Building | Internal Walls | 416.25 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-18 07:07 | 2022-02-24 17:00 | 2022-02-21 07:00 | 2022-02-24 17:00 | 2022-02-21 11:30 |  |  | Attended site, filled out JSA, spoke to Steve for locations of pin boards. They wanted all glass doors removed from display pin board cabinets around the TAFE, they didn’t have keys for the locks so had to drill all the locks to gain access to remove glass doors and stored all doors over in C block.Photos attached with map positioning of cabinets.
MSA-DTWD | WA5174958 | 1 | Precise Air Group | Q-Block chiller in fault again | Air Conditioning | Room Air Conditioners | 497.12 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-21 09:23 | 2022-02-22 17:00 | 2022-02-22 07:30 | 2022-02-22 17:00 | 2022-02-22 12:00 |  |  | Attended site and completed pre start paperwork andsigned in. Collected keys from kendrew and attendedmaclarty. Found chiller 2 to be running. Accessed bms.Found pump 1 to be out on flow switch alarm and pump runfault. Attempted to reset on bms but was unsuccessful.Looked to acess pump vsd. Found mssb locked. Spoke withfm and tracked down keys. Accessed vsd in mssb. Ran pumpon manual and inspected/tested flow switch. Found to havecontinuity. Test ran pump. Found to start and run.Checked status relay , found ok. Attempted to reset faulton innotech but was unable to. Went back up to bms andreset computer. Logged on to system and attempted toreset fault on bms. Found fault to clear this time.Chiller 2 shutdown and chiller 1/pump 1 started and ran.Monitored system and left unit operating. Fm monitor.
MSA-DTWD | WA5186839 | 1 | Equans Mechanical Services Australia | Air-con filters are noisy | Air Conditioning | Room Air Conditioners | 413.37 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-22 09:34 | 2022-02-23 17:00 | 2022-02-23 08:00 | 2022-02-23 17:00 | 2022-02-23 12:30 |  |  | FOUND SOUND COMING FROM RETURN AIR FILTERS - WASHED OUT WAITED F TO DRY AND PUT BACK IN -TESTED ALL OK
MSA-DTWD | WA5191927 | 1 | Equans Mechanical Services Australia | Welding bay extraction fan not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 505.84 | Pass | Pass | 0 | 0 | 4.5 | 2022-02-25 10:30 | 2022-02-28 17:00 | 2022-02-28 08:00 | 2022-02-28 17:00 | 2022-02-28 12:30 |  |  | Arrived on site signed in. Checked in with Dennis, gathered tools and equipment started investigation on system found belts stretched and worn, phoned suppliers, went picked up and returned. Re.oved old and fitted new. Tested system all ok. Cleaned up and completed paperwork. Signed out.
MSA-DTWD | WA5192019 | 0 | Precise Air Group | Aircon leaking water on roof unable to turn water off | Air Conditioning | Building HVAC Maintenance (Major Plant) | 706.44 | Pass | Fail | 0 | 0 | 4.5 | 2022-02-25 11:03 | 2022-02-25 13:03 | 2022-02-25 11:30 | 2022-02-25 15:03 | 2022-02-25 16:00 |  |  | Access to evaporative unit to H block canteen shows constant leaking of water.Unit electrically isolated and mains water line incoming isolated. Taps to individual units not present.Found cracked copper piping to waterline flare, threaded nut and thread gone to solenoid. Rectified threads and cut copper crack out and moving of olive. Adjusted waterline tension in incoming waterline as tight/tensioned line has caused overenthusiastic of float and solenoid and brass flare nut. Tested all ok, no leaks now.
MSA-DCA | WA5203651 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis st building - level 3 - plant room 9 - investigate and repair BMS notification | Air Conditioning | Room Air Conditioners | 606.975 | Pass | Pass | 0 | 0 | 4.5 | 2022-03-03 14:49 | 2022-03-04 17:00 | 2022-03-04 12:00 | 2022-03-04 17:00 | 2022-03-04 16:30 |  |  | Attended site, signed in and accessed plant rooms and humidifiers in fault. Ahu 03-01, 03-03 and 07-01. Found various parts require replacement - heater elements, solenoids, strainers, hoses ets. A quote will be sent to repair the humidifiers. Affected humidifiers have been isolated and tagged out.
MSA-DTWD | WA5204890 | 3 | Protek 24/7 Building & Maintenance | Walkway - Loose brick paving | Building | General Building | 804.54 | Pass | Pass | -1 | -1 | 4.5 | 2022-03-04 14:44 | 2022-03-14 17:00 | 2022-03-08 09:45 | 2022-03-14 17:00 | 2022-03-08 14:15 |  |  | Loose Brick Paving
MSA-DTWD | WA5231377 | 2 | AWB Co. | D block - D07 -3 x lights out (Location provided below) | Electrical | General Electrical | 888.36 | Pass | Pass | 0 | 0 | 4.5 | 2022-03-15 09:01 | 2022-03-18 17:00 | 2022-03-17 07:00 | 2022-03-18 17:00 | 2022-03-17 11:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Went to library and located all lights that needed tubes and starters replacing. A lot of light fittings has broken tombstones, used all tombstones that were on site, still required more. Went to wholesaler to pick up 8x tombstones to complete lighting in library. Returned to site and changed over all faulty tombstones. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5304167 | 1 | BAKE-QUIP PTY LTD | E-Block - SK3 front lecturers oven not heating up | Equipment | Catering Equipment | 685 | Pass | Pass | 0 | 0 | 4.5 | 2022-04-04 15:23 | 2022-04-05 17:00 | 2022-04-05 07:30 | 2022-04-05 17:00 | 2022-04-05 12:00 |  |  | Refer to service report
MSA-DTWD | WA5306128 | 2 | WESTERN IRRIGATION PTY LTD | External - Prospect Place side of the building - reticulation is broken | Landscaping & Gardening | Grounds Maintenance | 788.63 | Pass | Pass | 0 | 0 | 4.5 | 2022-04-06 10:28 | 2022-04-11 17:00 | 2022-04-11 07:00 | 2022-04-11 17:00 | 2022-04-11 11:30 |  |  | Locate and replace faulty solenoid valves, replace broken sprinklers and tested irrigation system.
MSA-DTWD | WA5384541 | 3 | AWB Co. | Water Leaks into classrooms from Window seals - See notes | Building | Windows | 3785 | Fail | Fail | 19 | 19 | 4.5 | 2022-04-28 13:41 | 2022-05-05 17:00 | 2022-09-16 07:30 | 2022-05-05 17:00 | 2022-09-16 12:00 |  | WCAPPR | Works completed as per braf
MSA-DTWD | WA5413851 | 3 | AWB Co. | Room C401 - Flickering Fluoro's | Electrical | Lighting, Internal | 638.35 | Pass | Pass | 0 | 0 | 4.5 | 2022-05-12 14:10 | 2022-05-19 17:00 | 2022-05-18 07:00 | 2022-05-19 17:00 | 2022-05-18 11:30 |  |  | Attended site signed in jsa completed, spoke with dave gaff to get keys. Also recieved a lighting list for B1 Block for various lights not working. Replaced all lights on list in B1. *** job is completed ***
MSA-DTWD | WA5479397 | 2 | Techworks Electrical | D-Block - Level 1 - Library - light not working above counter | Electrical | General Electrical | 295.24 | Pass | Pass | 0 | 0 | 4.5 | 2022-05-27 09:23 | 2022-06-01 17:00 | 2022-05-31 07:00 | 2022-06-01 17:00 | 2022-05-31 11:30 |  |  | Replaced various fluros and starters to lights in library
MSA-DCA | WA5482346 | 2 | Techworks Plumbing | Level 2 - Various toilet accessories needing repair/replacement - see notes below | Plumbing & Drainage | Toilets/Cisterns | 1233.12 | Pass | Pass | 0 | 0 | 4.5 | 2022-05-31 11:23 | 2022-06-03 17:00 | 2022-06-02 06:30 | 2022-06-03 17:00 | 2022-06-02 11:00 |  |  | Rectified various issues with toilets by replacing and re tightening toilet seats and re tightening flush buttons
MSA-DCA | WA5488070 | 3 | Techworks Electrical | Walkway between G, N and L, K Blocks and boundary with Birdwood Parade - lights faulty | Electrical | General Electrical | 1216.95 | Pass | Pass | 0 | 0 | 4.5 | 2022-06-02 10:09 | 2022-06-10 17:00 | 2022-06-07 10:00 | 2022-06-10 17:00 | 2022-06-07 14:30 |  |  | Completed fault finding of lights not working and a site wide audit of outside lighting.
MSA-DTAG | WA5512072 | 3 | PPM Project Painting & Maintenance | External - Magistrates emergency exit door & wall in garden bed - Graffiti | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 4.5 | 2022-06-13 13:05 | 2022-06-20 17:00 | 2022-06-14 11:30 | 2022-06-20 17:00 | 2022-06-14 16:00 |  |  | Removal of graffiti
MSA-DCA | WA5512292 | 0 | Techworks Plumbing | toilet blocked unusable on the jubilee building ground floor | Plumbing & Drainage | Drainage | 609.9 | Pass | Fail | 0 | 0 | 4.5 | 2022-06-13 17:32 | 2022-06-13 19:32 | 2022-06-13 18:00 | 2022-06-13 21:32 | 2022-06-13 22:30 |  |  | Arrived on site Signed in a security deskFound blocked toilet blocksStarted by plunging both toilets That didn't clear so I tried plunging from the showerThat didn't clear it either.I then found a plant room backed onto the toilet block that had two clean outs. I then tried my drain rods. It took a lot of plunging with the rods from both clean outs to get the drain flowing.Turned on both basins and both showers ran for 30 minutes.Flushed both toilets multiple timesPut 20 buckets of water down the clean outs.Tidy up signed out
MSA-DCA | WA5548941 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Basement Level - Communications 01 (Server Room) - BMS Alarm has fault - See notes below | Security | Monitoring | 1000 | Pass | Pass | 0 | 0 | 4.5 | 2022-06-17 11:17 | 2022-06-20 17:00 | 2022-06-17 12:00 | 2022-06-20 17:00 | 2022-06-17 16:30 |  |  | Honeywell attended site/remote logged in and carried out reset on controller 044 offline. Further works required by electricians
MSA-DTWD | WA5656632 | 1 | ECO PLUMBING AND GAS PTY LTD | The sink in E Block by E210 is blocked and water - see notes below | Plumbing & Drainage | Drainage | 592.44 | Pass | Fail | 0 | 0 | 4.5 | 2022-07-18 15:38 | 2022-07-19 17:00 | 2022-07-19 13:30 | 2022-07-19 17:00 | 2022-07-19 18:00 |  |  | Cleared blockage using large drain machine
MSA-DTWD | WA5696321 | 1 | Techworks Plumbing | External service compound front elevation - Water escaping from top of electric Rheem storage heater | Plumbing & Drainage | Water | 5764.64 | Fail | Fail | 1 | 1 | 4.5 | 2022-08-08 11:02 | 2022-08-09 17:00 | 2022-08-18 06:30 | 2022-08-09 17:00 | 2022-08-18 11:00 |  |  | Replaced broken hot water unit
MSA-DTWD | WA5698057 | 2 | M Construction (WA) | B block, Yellagonga. Repair holes in walls and ceilings | Building | Internal Walls | 501.67 | Pass | Pass | 0 | 0 | 4.5 | 2022-08-09 14:04 | 2022-08-12 17:00 | 2022-08-12 08:00 | 2022-08-12 17:00 | 2022-08-12 12:30 |  |  | Patched holes in walls and ceiling with rapid base then topped and painted patches.
MSA-DFES | WA5698101 | 1 | Workzone Pty Ltd | Yard-shed blown over and need to be removed | Building | External Walls | 995 | Pass | Pass | 0 | 0 | 4.5 | 2022-08-09 14:31 | 2022-08-10 17:00 | 2022-08-10 12:30 | 2022-08-10 17:00 | 2022-08-10 17:00 |  |  | Shed dismantled , removed from site and taken to tip.
MSA-DCA | WA5735457 | 2 | Techworks Electrical | Lighting Control Room (follow spot side) Light switch on main entry side - See notes | Electrical | Lighting, Internal | 522.675 | Pass | Pass | 0 | 0 | 4.5 | 2022-08-16 13:01 | 2022-08-19 17:00 | 2022-08-18 09:30 | 2022-08-19 17:00 | 2022-08-18 14:00 |  |  | Replace faulty intermediate switch in spot room. Test lights are functioning correctly after switch replacement. Also check over other lighting switches in the area for damage.Materials; 1x intermediate switch mech.
MSA-DTAG | WA5750170 | 2 | Australian HVAC Services Pty. Ltd. | Level 11 - Meeting Room 1 - Air conditioner fan omitting loud noise, cannot be adjusted | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Pass | -1 | -1 | 4.5 | 2022-08-17 09:36 | 2022-08-22 17:00 | 2022-08-17 10:00 | 2022-08-22 17:00 | 2022-08-17 14:30 |  |  | Attend site. Access level 11 and check loud noise in hearing room 1. Found air noise to be louder than normal. Access ceiling space and found VAV box cap to have fallen off spigot. Re tape cap to spigot and found noise to lessen. Still found air noise to be slightly high. Access level 6 and check BMS. Found level 11 to 14 offline. Obtain keys from key box Basement and access level 12. Locate BMS outstation and carry out power cycle. Return to level 6 and monitor. Found floors to slowly come back online. Level 11 now back online. Check air noise in hearing room 1 and found to return to normal. AC working ok.
MSA-DCA | WA5796965 | 0 | Techworks Plumbing | UAT Toilet behind the welcome desk - Blocked Sink | Plumbing & Drainage | Drainage | 301.08 | Pass | Fail | 0 | 0 | 4.5 | 2022-08-26 15:33 | 2022-08-26 17:33 | 2022-08-26 16:00 | 2022-08-26 19:33 | 2022-08-26 20:30 |  |  | Took off trap and emptied out gunk. Seals were worn out so used the seals from the unisex toilet in jubilee.Tested and cleaned up
MSA-DFES | WA5839246 | 2 | MALCO FLOORING PTY LTD | Office - carpet is lifting 300 x 300mm center of room | Flooring | Carpet | 1825 | Fail | Fail | 12 | 12 | 4.5 | 2022-09-09 10:44 | 2022-09-14 17:00 | 2022-12-09 07:00 | 2022-09-14 17:00 | 2022-12-09 11:30 |  |  | The carpet has delaminated from the backing and room requires replacementReplaced room with selected carpet tiles
MSA-DTWD | WA5973083 | 3 | AWB Co. | Level 2 Foyer - 11 x compound tubes out in down lights | Electrical | Lighting, Internal | 1977.465 | Pass | Pass | -1 | -1 | 4.5 | 2022-09-21 10:18 | 2022-09-29 17:00 | 2022-09-23 08:00 | 2022-09-29 17:00 | 2022-09-23 12:30 |  |  | Job complete
MSA-DTWD | WA5994801 | 2 | M Construction (WA) | Grounds - Walkway pavers become uneven causing potential trip hazards - See notes | Flooring | Concrete | 547.33 | Pass | Pass | 0 | 0 | 4.5 | 2022-10-06 08:41 | 2022-10-11 17:00 | 2022-10-11 06:30 | 2022-10-11 17:00 | 2022-10-11 11:00 |  |  | Removed all paves in area. Removed tree root, Reload paving flat using Cracked Dust and hunched all edges.
MSA-DTWD | WA6000394 | 0 | ACTION GLASS & ALUMINIUM | 4x smashed windows-windows repaired and glass cleaned up | Glazing | Window Glass | 2316.1 | Pass | Fail | 0 | 0 | 4.5 | 2022-10-10 07:36 | 2022-10-10 09:36 | 2022-10-10 09:00 | 2022-10-10 11:36 | 2022-10-10 13:30 |  |  | TWO MEN ATTENDED SITEREGLAZED 4 BROKEN WINDOWS6.38 CLEAR LAMINATED SAFETY GLASS1-1568 X 9083-1561 X 91415 L/M OF RUBBER REPLACED PLUS SILICONE AND 2 SCREWSAS PER APPROVED BRAF
MSA-DTWD | WA6001249 | 2 | AWB Co. | lights flickering | Electrical | Lighting, Internal | 1737.265 | Pass | Pass | 0 | 0 | 4.5 | 2022-10-10 14:08 | 2022-10-13 17:00 | 2022-10-12 12:15 | 2022-10-13 17:00 | 2022-10-12 16:45 |  |  | Job complete
MSA-DFES | WA6113395 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Hot water system - Element and thermostat in fault, to be checked - see notes below | Electrical | General Electrical | 1157.345 | Fail | Fail | 1 | 1 | 4.5 | 2022-10-24 11:21 | 2022-10-25 17:00 | 2022-10-31 10:00 | 2022-10-25 17:00 | 2022-10-31 14:30 |  |  | Tasz Cumming (31/10/2022) - Work NoteArrived onsite and was unable to find a local isolation cock for the HWU and had to isolate water to the entire office then drained the tanks ready for changeover . Installed new element and re filled tanks until water came out of the open pressure relief valve closed off taps and valves and checked it was water tight then energised the CCT and tested for correct operation .
MSA-DTWD | WA6206443 | 3 | AWB Co. | West corridor - 4 x Edge Fluros out in corridor. | Electrical | Lighting, Internal | 766.96 | Pass | Pass | -1 | -1 | 4.5 | 2022-11-17 10:40 | 2022-11-24 17:00 | 2022-11-18 06:30 | 2022-11-24 17:00 | 2022-11-18 11:00 |  |  | Attended site and signed in. Liaised with FM about works going ahead. Collected site keys. Went through and counted up how many tubes were required to complete job. Got parts. Went through and replaced all lights as per lighting list. Replaced 2x ballast in gym office. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DCA | WA6206486 | 1 | Techworks Electrical | External Ground - Grass Area next to STC - Christmas lights in tree unsafe, require electrician. | Electrical | Lighting, External | 1214.835 | Pass | Pass | 0 | 0 | 4.5 | 2022-11-17 10:47 | 2022-11-18 17:00 | 2022-11-18 11:00 | 2022-11-18 17:00 | 2022-11-18 15:30 |  |  | New test tags on all 50 items required, installed big adaptable boxes to house all of the lighting equipment needed for all lights. Tested and working
MSA-DTWD | WA6249766 | 3 | AWB Co. | Central fire stair - landing lights out - L6,4,3,2&1, total of 5 lights | Electrical | Lighting, Internal | 286.03 | Pass | Pass | 0 | 0 | 4.5 | 2022-11-21 14:29 | 2022-11-28 17:00 | 2022-11-28 07:00 | 2022-11-28 17:00 | 2022-11-28 11:30 |  |  | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Located central stairwell with lights out. Went through and replaced various globes (supplied by site) as directed. Switched to emergency to see if all were working, replaced tubes which were out. Energised. Notified relevant personnel of works completed. **job complete**
MSA-DTAG | WA6359326 | 1 | SCAVENGER SUPPLIES PTY LTD | sprinkler pump - faulty valve | Fire Protection Services | Fire Protection - Monitor System | 1001.355 | Pass | Pass | 0 | 0 | 4.5 | 2022-12-06 14:34 | 2022-12-07 17:00 | 2022-12-07 10:30 | 2022-12-07 17:00 | 2022-12-07 15:00 |  |  | BRAF to be SUBMITTEDP1-ATTENDED-06/12/22 JAKE ADAM 3.10PM-4.30PMRE-ATTENDANCE-07/12/22 BEAU WYLLIE 10.30AM-2.30PM PLUMBER TO COMPLETE WORK 1.45PM TO 2.30PM-MATERIALS USEDCOMPLETED 07/12/22
MSA-DCA | WA6400393 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Honeywell BMS alarm – TEF23_SeqLockoutAlm - see notes | Security | Security Management System | 788.595 | Pass | Pass | 0 | 0 | 4.5 | 2023-01-03 12:04 | 2023-01-06 17:00 | 2023-01-04 07:00 | 2023-01-06 17:00 | 2023-01-04 11:30
MSA-DTWD | WA6450293 | 2 | Equans Mechanical Services Australia | Chiller 1 compressor 3 requires new discharge temp sensor | Equipment | Compressors, Generators | 1597.02 | Fail | Fail | 3 | 3 | 4.5 | 2023-01-16 10:40 | 2023-01-19 17:00 | 2023-02-10 07:30 | 2023-01-19 17:00 | 2023-02-10 12:00
MSA-DTWD | WA6572652 | 1 | Precise Air Group | SK1 aircon not working again (Call Back) | Air Conditioning | Ducted Split System | 1118.845 | Pass | Pass | 0 | 0 | 4.5 | 2023-02-14 07:29 | 2023-02-14 17:00 | 2023-02-14 07:30 | 2023-02-14 17:00 | 2023-02-14 12:00
MSA-DTWD | WA6603023 | 1 | AWB Co. | Mats require replacement - see notes | Flooring | Rubber | 456.415 | Pass | Pass | 0 | 0 | 4.5 | 2023-02-17 11:59 | 2023-02-20 17:00 | 2023-02-20 07:00 | 2023-02-20 17:00 | 2023-02-20 11:30
MSA-DCA | WA6681230 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Harry bulter centre chiller is fault | Building | Materials | 506.75 | Pass | Fail | 0 | 0 | 4.5 | 2023-03-02 06:05 | 2023-03-02 08:05 | 2023-03-02 08:00 | 2023-03-02 10:05 | 2023-03-02 12:30
MSA-DTWD | WA6688517 | 2 | Protek 24/7 Building & Maintenance | Collapsed large metal shelving unit – OSH issue | Carpentry | Joinery | 396.29 | Pass | Pass | 0 | 0 | 4.5 | 2023-03-07 16:03 | 2023-03-10 17:00 | 2023-03-08 10:45 | 2023-03-10 17:00 | 2023-03-08 15:15
MSA-DTAG | WA5094196 | 0 | Australian HVAC Services Pty. Ltd. | entire building - no aircon | Air Conditioning | Room Air Conditioners | 737.04 | Pass | Fail | 0 | 0 | 4.4833 | 2022-01-31 09:23 | 2022-01-31 11:23 | 2022-01-31 11:01 | 2022-01-31 13:23 | 2022-01-31 15:30 |  |  | Travelled to site. Signed in. Got keys. Went to BMS room. Logged into BMS. Investigated AC system. Found all aircons working fine apart from AHU 1 that serves Admin. Ran tests. Found fault light on on MSSB. Reset power to VSD. AC started up. Faulted within 5mins, Automatically restarted, faulted after another 5mins, automatically restarted, then ran fine for the next couple hours.On advice from Mark K, let the staff know to monitor the aircon over the next couple days.Packed up and left site.
MSA-DTWD | WA5699395 | 3 | Equans Mechanical Services Australia | BMS Delta System stopped working | Air Conditioning | Room Air Conditioners | 769.6 | Pass | Pass | 0 | 0 | 4.4167 | 2022-08-10 09:23 | 2022-08-17 17:00 | 2022-08-15 09:00 | 2022-08-17 17:00 | 2022-08-15 13:25 |  |  | SEE REPORT - QUOTE TO FOLLOW BMS UPGRADE
MSA-DTWD | WA5490968 | 3 | ADVANCED LOCK & KEY | Centre Block - C208 - Door not latching shut | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 4.4 | 2022-06-03 10:45 | 2022-06-13 17:00 | 2022-06-08 08:55 | 2022-06-13 17:00 | 2022-06-08 13:19 |  |  | Cut strike in on aluminium partition on c208 as door wasn’t latching8:55-9:35
MSA-DTWD | WA5325826 | 2 | Equans Mechanical Services Australia | C4 - faulty pump on AC unit | Air Conditioning | Room Air Conditioners | 342.79 | Fail | Fail | 0 | 0 | 4.3833 | 2022-04-14 12:51 | 2022-04-21 17:00 | 2022-04-22 08:00 | 2022-04-21 17:00 | 2022-04-22 12:23 |  |  | Pump replaced
MSA-DCA | WA6257482 | 0 | TK Elevator Australia Pty Ltd | Lift has stopped | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 4.35 | 2022-11-24 15:53 | 2022-11-24 17:53 | 2022-11-25 08:58 | 2022-11-24 19:53 | 2022-11-25 13:19 |  |  | Lift was through the bottom limit. Tested operation. Returned to the office, and sourced a replacement limit switch for the down slowdown limit.Also sourced a platform ladder. Replaced the bottom slowdown limit, and extended the activation arm for more positive activation. Also monitored the M relay circuit voltages.Tested lift operation without further fault. Returned the lift to service
MSA-DTWD | WA6653886 | 1 | Precise Air Group | Deli and Skills kitchen 1 -E Vap not working (see notes) | Air Conditioning | Evaporative Coolers | 4972.165 | Pass | Pass | 0 | 0 | 4.3167 | 2023-02-21 07:47 | 2023-02-21 17:00 | 2023-02-21 08:00 | 2023-02-21 17:00 | 2023-02-21 12:19
MSA-DCA | WA5174677 | 0 | Critical Fire Protection & Training | Fire panel alarm activating | Fire Protection Services | Fire Protection - Monitor System | 466.655 | Pass | Fail | 0 | 0 | 4.2833 | 2022-02-21 08:23 | 2022-02-21 10:23 | 2022-02-21 10:00 | 2022-02-21 12:23 | 2022-02-21 14:17 |  |  | Faulty brigade card. Brigade crd to be replaced.
MSA-DTAG | WA6535146 | 3 | Dormakaba Australia Pty Ltd | Registry ground-entry door -Electronic lock not engaging at Registry Door | Building | Automatic Doors | 533.62 | Fail | Fail | 1 | 1 | 4.2667 | 2023-02-06 14:49 | 2023-02-13 17:00 | 2023-02-17 08:22 | 2023-02-13 17:00 | 2023-02-17 12:38
MSA-DFES | WA5099792 | 1 | Australian HVAC Services Pty. Ltd. | Front side of the bay - Aircondition system is not working - Error E4 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 737.225 | Pass | Pass | 0 | 0 | 4.2667 | 2022-02-02 08:49 | 2022-02-03 08:49 | 2022-02-02 12:00 | 2022-02-03 08:49 | 2022-02-02 16:16 |  |  | New main pcb installed
MSA-DTWD | WA5010045 | 1 | UNIVERSAL DOORS | Heavy Truck Roller Door - Ground - AT106 roller door - Broken Roller- bearing is faulty | Building | Doors |  | Fail | Fail | 2 | 2 | 4.25 | 2022-01-12 09:48 | 2022-01-13 17:00 | 2022-01-28 08:45 | 2022-01-13 17:00 | 2022-01-28 13:00 |  |  | replaced track
MSA-DTWD | WA5092563 | 1 | AHS Services WA Pty Ltd (Anchor) | Waste Compound - Exterior - Tap in Skip Compound has split copper pipe | Plumbing & Drainage | Water | 519.5575 | Pass | Pass | 0 | 0 | 4.25 | 2022-01-28 08:01 | 2022-01-31 17:00 | 2022-01-28 11:45 | 2022-01-31 17:00 | 2022-01-28 16:00 |  |  | Cut uo concrete to expose cracked piece of copper. Replaced section of pipework. Concreted area.
MSA-MRWA | WA5799596 | 2 | Automatic Fire Protection (ARA) | Fire Panel - Reset / Investigate fault on L7 bathroom | Fire Protection Services | Fire Protection - Monitor System | 338.7 | Pass | Pass | 0 | 0 | 4.25 | 2022-08-30 12:55 | 2022-09-02 17:00 | 2022-09-02 08:45 | 2022-09-02 17:00 | 2022-09-02 13:00 |  |  | Located and removed tape from detector in toilets. Found detector to be labelled incorrectly. Performed program change to updatedescription. De-isolated
MSA-DTWD | WA5888330 | 3 | AWB Co. | Timber battens above vending machines require re fixing and replacing | Electrical | General Electrical | 525.6925 | Pass | Pass | 0 | 0 | 4.25 | 2022-09-16 15:48 | 2022-09-23 17:00 | 2022-09-23 06:30 | 2022-09-23 17:00 | 2022-09-23 10:45 |  |  | re-fit timber battens
MSA-DTWD | WA5888334 | 3 | AWB Co. | Staff Kitchen - Reception Area - Re fit first aid cabinet | Building | General Building | 107.805 | Pass | Pass | 0 | 0 | 4.25 | 2022-09-16 15:50 | 2022-09-23 17:00 | 2022-09-23 06:30 | 2022-09-23 17:00 | 2022-09-23 10:45 |  |  | Works completed
MSA-DTAG | WA6402699 | 3 | AWB Co. | Level 10-Lights need changing-see notes | Electrical | Lighting, Internal | 271.06 | Pass | Pass | 0 | 0 | 4.25 | 2023-01-05 15:15 | 2023-01-12 17:00 | 2023-01-09 10:15 | 2023-01-12 17:00 | 2023-01-09 14:30
MSA-DTWD | WA5108509 | 3 | AWB Co. | Lights flickering and some blown | Electrical | Lighting, Internal | 786.065 | Pass | Pass | 0 | 0 | 4.25 | 2022-02-08 14:52 | 2022-02-15 17:00 | 2022-02-15 10:30 | 2022-02-15 17:00 | 2022-02-15 14:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located various locations and replaced faulty tubes and starters. Notified site of works completed. **job complete**
MSA-DTWD | WA5203681 | 2 | Protek 24/7 Building & Maintenance | D Block - Room D23 - Roof Leak | Roofing | Metal Roofing | 720.75 | Pass | Pass | 0 | 0 | 4.25 | 2022-03-03 15:14 | 2022-03-09 17:00 | 2022-03-08 07:30 | 2022-03-09 17:00 | 2022-03-08 11:45 |  |  | D Block - Room D23 - Roof Leak
MSA-DTWD | WA5204899 | 3 | AWB Co. | J126 - J Block - Offensive graffitti scratched into doors leading into J126, door needs paint | Building | General Building | 388.055 | Pass | Pass | 0 | 0 | 4.25 | 2022-03-04 14:51 | 2022-03-14 17:00 | 2022-03-11 11:15 | 2022-03-14 17:00 | 2022-03-11 15:30 |  |  | Attended site and sanded vandalised door, purchased paint and applied two coats
MSA-DTWD | WA5216747 | 2 | AWB Co. | L3 & L4 - B Block West Stairwell - Multiple Emg Light Fittings Faulty | Electrical | Lighting, Internal | 830.8 | Pass | Pass | 0 | 0 | 4.25 | 2022-03-11 12:32 | 2022-03-16 17:00 | 2022-03-14 07:00 | 2022-03-16 17:00 | 2022-03-14 11:15 |  |  | Attended site and signed in, completed jsa,spoke to fm about job, fm wanted all lights in stair well changed to led as tubes and tombstones were all in poor condition, went to wholesaler to pick up parts, returned to site, isolated lighting circuits, removed old lights, replaced with new, re energised circuit, tested all lights and working as intended, cleaned up , packed up, completed paperwork, signed out, Job completed
MSA-DTWD | WA5294785 | 2 | ECO PLUMBING AND GAS PTY LTD | Blocked drains possible jetta required | Plumbing & Drainage | Drainage | 629.395 | Pass | Fail | 0 | 0 | 4.25 | 2022-03-29 09:15 | 2022-04-01 17:00 | 2022-04-01 13:00 | 2022-04-01 17:00 | 2022-04-01 17:15 |  | WACCES | cleared blockage
MSA-DCA | WA5511730 | 0 | Schneider Electric Australia Pty Ltd | Ground Floor - Control to doors and lighting not responding - issue with iinet BMS | Building | General Building |  | Pass | Fail | 0 | 0 | 4.25 | 2022-06-13 08:12 | 2022-06-13 10:12 | 2022-06-13 09:45 | 2022-06-13 12:12 | 2022-06-13 14:00 |  |  | Restarted the server PC and confirmed client OC's were now communicating with the server.Confirmed that INet was now working on all site PC's
MSA-DCA | WA5511839 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Lift 7 - not leaving level 1 - displaying out of order - See notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 4.25 | 2022-06-13 09:46 | 2022-06-14 17:00 | 2022-06-13 10:00 | 2022-06-14 17:00 | 2022-06-13 14:15 |  |  | Lift7 Green Rm-Hydraulic :Ongoing issue with lift tripping out on run time protection. Lift on street level and keyed to park mode and below floor level. Switched back to normal and reset processor. Tested operation and could not reproduce fault. Left in service further investigation into ongoing fault needed.
MSA-MRWA | WA5587750 | 2 | AWB Co. | Level 2 - 5 light sections on eastern side of RTTO, plus 2 lights in common area - See notes below | Electrical | Lighting, Internal | 946.46 | Pass | Pass | -1 | -1 | 4.25 | 2022-07-07 10:21 | 2022-07-12 17:00 | 2022-07-08 07:00 | 2022-07-12 17:00 | 2022-07-08 11:15 |  |  | Picked up keys from DAC. Attended site and signed in. Completed JSA. Located lights on level 2 not working. Investigated to find faulty control gear and lamps. Supply and replaced as required. Lights all working besides one next to the window. Notified PFM. Signed out. Job complete. Return keys to DAC
MSA-DFES | WA5681670 | 2 | Australian HVAC Services Pty. Ltd. | Ground Level - Multiple air cons not working - See notes below | Air Conditioning | Room Air Conditioners | 581.95 | Pass | Pass | -1 | -1 | 4.25 | 2022-07-28 13:55 | 2022-08-02 17:00 | 2022-07-29 10:45 | 2022-08-02 17:00 | 2022-07-29 15:00 |  |  | No further r her issues found
MSA-DTWD | WA5693667 | 3 | AWB Co. | RCD in RM A104B trips when switch activated | Electrical | General Electrical | 507.5925 | Pass | Pass | 0 | 0 | 4.25 | 2022-08-04 14:11 | 2022-08-11 17:00 | 2022-08-11 07:00 | 2022-08-11 17:00 | 2022-08-11 11:15 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,investigated fault in light , found that there was a fault in the active on the load side of the switch going to the light, removed old light and found water , removed old faulty light and replaced with new, silicone up all screws and cable entry to prevent water from entering, fault still on active, spoke to fm and came to the decision to put in a new switch next to booth, went to wholesaler and picked up materials, returned to site and installed switch , light now working, packed up, cleaned up, completed paperwork,signed out**job completed*
MSA-DFES | WA5832685 | 1 | Australian HVAC Services Pty. Ltd. | Server room - aircon not working | Air Conditioning | Room Air Conditioners | 806.07 | Pass | Pass | 0 | 0 | 4.25 | 2022-09-05 15:02 | 2022-09-06 17:00 | 2022-09-06 07:30 | 2022-09-06 17:00 | 2022-09-06 11:45 |  |  | Fault on ac fixed.
MSA-DTWD | WA5971142 | 3 | AWB Co. | Main entrance - 9 x anti skateboard nubs broken off | Paving & Roadworks | Paving | 695.1225 | Pass | Pass | 0 | 0 | 4.25 | 2022-09-20 11:49 | 2022-09-28 17:00 | 2022-09-27 07:00 | 2022-09-28 17:00 | 2022-09-27 11:15 |  |  | Called to site, actual 12 skateboard deterrents were requiredDetergents have been glued and concrete around the drill holes have been smoothed out using builders bog
MSA-DCA | WA6020008 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground - Car park - Cooling tower leaking | Air Conditioning | Cooling Tower | 484.23 | Pass | Pass | 0 | 0 | 4.2167 | 2022-10-13 09:47 | 2022-10-14 17:00 | 2022-10-13 09:47 | 2022-10-14 17:00 | 2022-10-13 14:00 |  |  | Repairs to cooling tower float valve. Adjustment to both tower water levels.
MSA-DTWD | WA5291175 | 2 | SCAVENGER SUPPLIES PTY LTD | UPS that is powering the EWIS in T Block needs replacing(it has died) | Fire Protection Services | Fire Protection - Monitor System | 2192.86 | Fail | Fail | 4 | 4 | 4.1667 | 2022-03-25 16:15 | 2022-03-30 17:00 | 2022-04-26 10:00 | 2022-03-30 17:00 | 2022-04-26 14:10 |  | WACCES | COMPLETED AS PER APPROVED BRAF 26/04/2022
MSA-DTAG | WA5706338 | 2 | AHS Services WA Pty Ltd (Anchor) | Potential Water Leak - Notified by Water Corp Meter Reader | Plumbing & Drainage | Water | 548.61 | Pass | Pass | 0 | 0 | 4.1667 | 2022-08-11 10:46 | 2022-08-16 17:00 | 2022-08-16 09:00 | 2022-08-16 17:00 | 2022-08-16 13:10 |  |  | Repaired hole in water main to courthouse,no more leaks on site
MSA-DTWD | WA5980100 | 3 | Water2water Pty Ltd | C102-water fountain not working | Plumbing & Drainage | Water | 838.975 | Pass | Pass | -1 | -1 | 4.1667 | 2022-09-29 12:43 | 2022-10-06 17:00 | 2022-09-30 12:00 | 2022-10-06 17:00 | 2022-09-30 16:10 |  |  | Repaired multiple issues with Billi unit. Unit running to specs
MSA-DCA | WA5887844 | 1 | EQUANS Mechanical Services (WA) Pty Limited | External plant room - Chiller 2 in fault | Refrigeration | Chiller | 315.315 | Pass | Pass | 0 | 0 | 4.1667 | 2022-09-16 10:38 | 2022-09-19 17:00 | 2022-09-16 12:40 | 2022-09-19 17:00 | 2022-09-16 16:50 |  |  | Attended site gained access and carried out investigations of fault on CH-2. Water flow safty interlock was active. Carried out equipment reset and placed unit into lead operation. Monitored equipment functions and no further fault confirmed pump operation all ok. No further fault occured.
MSA-DTAG | WA6255465 | 2 | Australian HVAC Services Pty. Ltd. | Level 1-Transformer room-Noise is emitting from exhaust fan unit | Air Conditioning | Room Air Conditioners | 267.45 | Pass | Pass | -1 | -1 | 4.1 | 2022-11-23 10:53 | 2022-11-28 17:00 | 2022-11-23 10:54 | 2022-11-28 17:00 | 2022-11-23 15:00 |  |  | Access transformer room. Check for noise coming from exhaust system. Remove panels and inspect motor. Check bearings and found to be slightly noisy but not causing noise. Further inspection found a mount nut had come loose and making a squeaking noise on the frame. Tighten nut and found noise to stop. Check all other nuts and found to be ok.
MSA-DTWD | WA5133409 | 1 | Precise Air Group | E-Block - Ground - E63 - stores cool room E63 fans on cooling unit not working | Air Conditioning | Room Air Conditioners | 745.795 | Pass | Pass | 0 | 0 | 4.0833 | 2022-02-15 10:35 | 2022-02-16 17:00 | 2022-02-15 11:25 | 2022-02-16 17:00 | 2022-02-15 15:30 |  |  | Attended site and completed pre start paperwork and signed in. Accessed freezer in kitchen stores and inspected. Found evap to have one fan motor not operating , section of evap iced up and drain to have come away from drain exit of evap causing moisture to drain into freezer room. This is causing excessive frost in room. Re attached drain to drain exit and tested drain heater. Found ok. Put system on a defrost and defrosted coil as well as checking function of all heater elements ( coil/drain pan) once coil defrosted inspected fan motor. Checked for voltage and found 240v present at fan motor. Fan motor has failed. Collected details and located new fan motor. Collected fan motor from suppliers. Returned to site and isolated / locked out equipment. Removed old fan motor and installed new. Test ran and found all 3 fans to start and run. Watched system cycle on and off a couple of times. Completed paperwork. No further works required.
MSA-DTWD | WA5151011 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, Internal | 220.43 | Pass | Pass | -1 | -1 | 4.0833 | 2022-02-17 10:11 | 2022-02-22 17:00 | 2022-02-18 08:00 | 2022-02-22 17:00 | 2022-02-18 12:05 |  |  | Inspected lights out, sourced LED light fitting replacement to fit into ceiling grid. Returned to site, removed surface mount fluro light fittings and installed new LED panels into ceiling grid.
MSA-DCA | WA6684294 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main Gallery - AC Humidity Alarm for Gallery 1 & 6 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 546.18 | Pass | Fail | 0 | 0 | 4.0333 | 2023-03-05 17:14 | 2023-03-05 19:14 | 2023-03-05 17:47 | 2023-03-05 21:14 | 2023-03-05 21:49
MSA-DTAG | WA4993505 | 1 | Australian HVAC Services Pty. Ltd. | Roof - AC Plant - No Flow on Units 1, 3, 4; Alarms on 1, 4 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 658.55 | Pass | Pass | 0 | 0 | 4 | 2022-01-07 16:01 | 2022-01-10 17:00 | 2022-01-10 08:00 | 2022-01-10 17:00 | 2022-01-10 12:00 |  |  | Attend site. Check BMS and found HPWU 4 and 5 to be in alarm. HPWU 3 is currently out of service with a refrigerant leak and waiting for condenser fan motor to be rewound. Found unit 5 tripped on freeze protection. Found unit 4 low evap leaving water temp. Reset unit 5 and monitor operation. Reset unit 4 and found to trip again. Check water leaving temp and found to be reading 0.5 and return 13. Found sensor temp to jump back up to 13. Carry out reset and found unit to run for haft an hour and then fault again sensor back to 0 degrees. Sensor has intermittent fault causing sensor to to run out of required parameters. Will monitor and if fails again will replace.
MSA-DTWD | WA4994860 | 3 | Schneider Electric Australia Pty Ltd | Main Entry door - Proximity reader damaged | Building | Doors |  | Pass | Pass | -1 | -1 | 4 | 2022-01-10 08:15 | 2022-01-17 17:00 | 2022-01-11 08:00 | 2022-01-17 17:00 | 2022-01-11 12:00 |  |  | Attended site and inspected reader at 12 Aberdeen st.Reader mounting has been damaged. I was able to resecure reader to wall mounting but readerwill need to be replaced.Replacement reader has been back ordered from supplier
MSA-DTWD | WA5001192 | 1 | WESTERN IRRIGATION PTY LTD | Exit sign - Verge/grass area - broken retic main line | Plumbing & Drainage | Water | 2139.55 | Pass | Pass | 0 | 0 | 4 | 2022-01-11 09:58 | 2022-01-12 17:00 | 2022-01-12 07:30 | 2022-01-12 17:00 | 2022-01-12 11:30 |  |  | Locate, excavate and repair broken mainline.
MSA-DCA | WA5018052 | 2 | Techworks Electrical | Interior wall - lights out in block | Electrical | General Electrical | 440.53 | Pass | Pass | 0 | 0 | 4 | 2022-01-14 08:08 | 2022-01-19 17:00 | 2022-01-18 06:00 | 2022-01-19 17:00 | 2022-01-18 10:00 |  |  | found issues to be cables not joined correctly in ceiling space from when walls were demolished to create bigger spaces, feeds were coming out to locations but then not joined onto the loops to the lights from where the switches would have been. Once circuits were sorted out went through and swapped blown tubes that were also contributing to lights being out.
MSA-DCA | WA5052520 | 1 | EQUANS Mechanical Services (WA) Pty Limited | AHU 4 is faulty | Air Conditioning | Building HVAC Maintenance (Major Plant) | 450 | Pass | Pass | 0 | 0 | 4 | 2022-01-18 08:48 | 2022-01-19 17:00 | 2022-01-18 09:00 | 2022-01-19 17:00 | 2022-01-18 13:00 |  |  | Assisted the Architect, engineer and Facilities Management with Art Gallery walk through.
MSA-DTWD | WA5052673 | 2 | Critical Fire Protection & Training | Level 4 - Centre Block Staff Room - Sprinkler is leaking | Fire Protection Services | Fire Protection - Monitor System | 993.07 | Pass | Pass | 0 | 0 | 4 | 2022-01-18 09:37 | 2022-01-21 17:00 | 2022-01-21 08:00 | 2022-01-21 17:00 | 2022-01-21 12:00 |  |  | Signed in isolated FIP.Drained all 4 systems to be safe.Removed sprinkler that was leaking from bulb and replaced with a new sprinkler.Refilled system and tested for leaks all ok.Cleared alarms on FIP.Reset back to normal operation
MSA-MRWA | WA5081158 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Failed air conditioning unit | Air Conditioning | Room Air Conditioners | 1000 | Fail | Fail | 0 | 0 | 4 | 2022-01-20 11:31 | 2022-01-28 17:00 | 2022-01-31 12:00 | 2022-01-28 17:00 | 2022-01-31 16:00 |  |  | Works carried out by subcontractor NRP.
MSA-DTWD | WA5081413 | 3 | Schneider Electric Australia Pty Ltd | Koorlak - Main door scanning issues | Building | Automatic Doors |  | Pass | Pass | -1 | -1 | 4 | 2022-01-20 13:40 | 2022-01-28 17:00 | 2022-01-21 08:00 | 2022-01-28 17:00 | 2022-01-21 12:00 |  |  | job completed - Attended site and investigated door faults on Doors W206 and W207Found that a power supply in level 2 east cabinet failed after power failedCollected new power supply and batteries from supplierReturned to site and replace partsChecked and confirmed power supply voltages of all three power suppliesConfirmed battery charge voltage and also tested power fail battery back up
MSA-DTAG | WA5086175 | 1 | Australian HVAC Services Pty. Ltd. | 1987 Building - Level 1 - Air-conditioning in 1987 stopped working | Air Conditioning | Room Air Conditioners | 428.31 | Pass | Pass | 0 | 0 | 4 | 2022-01-21 10:19 | 2022-01-24 17:00 | 2022-01-21 10:30 | 2022-01-24 17:00 | 2022-01-21 14:30 |  |  | JOB NUMBER #40420Attend site. Access BMS and check operation of AC unit. Found AC 3 serving magistrates area not cooling. Access plantroom and check operation. Found unit to be locked out. Check all safety controls and found compressor 1 contactor overload tripped. Reset overload and reset lockout relay. Check operation of unit. Found fan to start, compressor one started but eas drawing no amps on the blue phase. Turn unit off and diagnose cause. Trace wiring back to the compressor and found a bad connection to the compressor terminal. Cut wire and strip back fit new spade female connection and fit to terminal. Turn unit on and check operation. Found compressor to start and draw 10amps each phase. Unit is now working ok.
MSA-DTWD | WA5087954 | 1 | Precise Air Group | Display Fridge in cafe Mt Lawley not working | Refrigeration | Refrigerators | 623.86 | Pass | Pass | 0 | 0 | 4 | 2022-01-24 15:30 | 2022-01-25 17:00 | 2022-01-25 12:00 | 2022-01-25 17:00 | 2022-01-25 16:00 |  |  | Attended site and completed pre start paperwork and signed in. Acessed display fridge in canteen and inspected. Found all components operating. Found system short of gas. Started gas leak procedure. Pressure tested with nitrogen and went over system with leak detector. Found leaks on both schrader cores. Replaced schrader cores and pressure tested system to confirm no more leaks are present. Once satisfied let nitrogen go and evacuated system under 500microns. Charged with 690 grams of 134a. Test ran system and watched system cycle on and off. Left unit operating in good working order.
MSA-DTAG | WA5090604 | 1 | Midolo Building Services | Ground - Court room 2 - Hinge on bottom of public entrance door is bent and does not close properly | Building | Doors | 484.66 | Pass | Pass | 0 | 0 | 4 | 2022-01-25 14:15 | 2022-01-27 17:00 | 2022-01-27 09:30 | 2022-01-27 17:00 | 2022-01-27 13:30 |  | WCAPPR | HINGES X 3 REPLACED- DOOR ADJUSTED. REPAIRS MADE.
MSA-DCA | WA5092022 | 1 | EQUANS Mechanical Services (WA) Pty Limited | expansion coupling about to fail. | Air Conditioning | Room Air Conditioners | 954.855 | Fail | Fail | 0 | 0 | 4 | 2022-01-27 13:16 | 2022-01-28 17:00 | 2022-01-31 12:00 | 2022-01-28 17:00 | 2022-01-31 16:00 |  |  | Collected parts and materials, drove to site, signed in and accessed the chiller plantroom. Isolated the pump, drained down system and carried out vibration coupling changes. Filled system and reinstated power, checked and tested for any leaks. All OK.
MSA-DTWD | WA5094295 | 1 | Schneider Electric Australia Pty Ltd | Block B - Level 1 - B105 Facilities Office -Fault with Schneider iNet access database - see details | Security | Access Control |  | Pass | Pass | 0 | 0 | 4 | 2022-01-31 09:54 | 2022-02-01 17:00 | 2022-02-01 08:00 | 2022-02-01 17:00 | 2022-02-01 12:00 |  |  | Job completed - Attended site and investigated software issue
MSA-DTAG | WA5094358 | 1 | Australian HVAC Services Pty. Ltd. | 1903 - Basement - Court 7 - Air con not switching | Air Conditioning | Room Air Conditioners | 428.31 | Pass | Pass | 0 | 0 | 4 | 2022-01-31 10:24 | 2022-02-01 17:00 | 2022-01-31 10:30 | 2022-02-01 17:00 | 2022-01-31 14:30 |  |  | 40502
MSA-DTWD | WA5098731 | 2 | Schneider Electric Australia Pty Ltd | Level 2 - Ground - W206, W207 - Classroom Doors will not secure - power supply failure | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 4 | 2022-02-01 10:48 | 2022-02-04 17:00 | 2022-02-01 12:00 | 2022-02-04 17:00 | 2022-02-01 16:00 |  |  | job completed - Attended site and investigated door faults on Doors W206 and W207Found that a power supply in level 2 east cabinet failed after power failedCollected new power supply and batteries from supplierReturned to site and replace partsChecked and confirmed power supply voltages of all three power suppliesConfirmed battery charge voltage and also tested power fail battery back up
MSA-DTWD | WA5099008 | 2 | Building Automation & Electrical Services Pty Ltd | Level 2 - room B251 - Classroom very hot | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Fail | Fail | 7 | 7 | 4 | 2022-02-01 12:26 | 2022-02-04 17:00 | 2022-03-22 07:30 | 2022-02-04 17:00 | 2022-03-22 11:30 |  |  | Repairs
MSA-DCA | WA5099046 | 2 | Protek 24/7 Building & Maintenance | M Block - M block windows & screens and hole in the wall - see notes below | Building | Windows | 440.66 | Pass | Pass | 0 | 0 | 4 | 2022-02-01 13:42 | 2022-02-04 17:00 | 2022-02-02 10:15 | 2022-02-04 17:00 | 2022-02-02 14:15 |  |  | Secure windows and repair minor hole in wall
MSA-DTWD | WA5099117 | 1 | Equans Mechanical Services Australia | G10 Clinic Prep Room - AC is not running | Air Conditioning | Room Air Conditioners | 579.41 | Pass | Pass | 0 | 0 | 4 | 2022-02-01 14:17 | 2022-02-02 17:00 | 2022-02-02 08:00 | 2022-02-02 17:00 | 2022-02-02 12:00 |  |  | Travelled to site and signed in. Located G10 clinic prep room and found the Mitsubishi vrv split not running. Checked upstairs controller and found to have no power. Checked evaporator and found to have no power also. Circuit breaker was on. Travel cable back to a electrical box with a condensate pump in it. Checked pump and found to be faulty and not sucking. Travelled to supplier to pick up parts. Installed new condensate pump and tested all ok.
MSA-DTWD | WA5099727 | 2 | Precise Air Group | faulty evap air con constantly dumping water | Air Conditioning | Evaporative Coolers | 898.28 | Pass | Pass | 0 | 0 | 4 | 2022-02-02 08:14 | 2022-02-07 17:00 | 2022-02-04 08:00 | 2022-02-07 17:00 | 2022-02-04 12:00 |  |  | Replace drain seal and solenoid on evap 5, replace cap on evap 6, replaced sump dump on evap 11 and transformer. Fixed water dumping
MSA-DCA | WA5100980 | 3 | Protek 24/7 Building & Maintenance | Movement and discolouration in floorboards | Flooring | Timber | 686.6 | Pass | Pass | 0 | 0 | 4 | 2022-02-03 08:45 | 2022-02-10 17:00 | 2022-02-09 11:15 | 2022-02-10 17:00 | 2022-02-09 15:15 |  |  | Refixed loose boards, removed discolouration
MSA-DCA | WA5105843 | 0 | EQUANS Mechanical Services (WA) Pty Limited | D Mineralized pump - failing and effect humidity | Air Conditioning | Room Air Conditioners | 816.275 | Pass | Fail | 0 | 0 | 4 | 2022-02-04 15:08 | 2022-02-04 17:08 | 2022-02-04 15:30 | 2022-02-04 19:08 | 2022-02-04 19:30 |  |  | Accessed the chiller plant room and investigated the D mineralised pump. Found the pump had faulted, reset failure fault and still alarmed. Isolated the pump and removed the electrical cover and found a burnt relay. Found a spare relay on site and replaced. Checked and tested the operation and is now working correctly. It is recommended replacing the pump completely to avoid further compilations and alarms. Due to pump failure all the humidifiers in the centenary wing faulted due to insufficient water pressure. Accessed the centenary building and roof space and reset humidifiers.
MSA-DFES | WA5105847 | 3 | Critical Fire Protection & Training | Ground Floor -Please attend site for FIP error BGA/FIP 2nd floor & Plant Room | Fire Protection Services | Fire Protection - Monitor System | 2734.59 | Pass | Pass | 0 | 0 | 4 | 2022-02-04 15:16 | 2022-02-11 17:00 | 2022-02-10 08:00 | 2022-02-11 17:00 | 2022-02-10 12:00 |  |  | Fault latched on 2nd floor / plant EWIS zone• Checked all plant room connections (speakers)-all ok• Checked audibility of 2nd floor/ewis speakers- all ok• Reset zone all clear- as latched faults on this system the issue only need to appear for 5 seconds to stay faulted.• Swapped zone wiring internal to EWIS 1st floor/ 2nd floor for trial to confirm if field or amp( internal EWIS) • Info tagged EWIS• Security to call if fault reoccurs• Spoke with site contact programmed he was understandingChecked speaker connections, found few poor connections, re terminated.°Investigate speaker status/cabling on Level 2 and Plantroom. Redo several terminations as inadequate.°Cabling to amps have been corrected, (1 South and 1 North mixed up).°Fault cleared.°If fault re-occurs, re-attend early morning, (Critical to organize).°Inspected minimum 100% Plant speakers. Inspected minimum 75% L 2 speakers, (unable to access others).°Fault potentially other Zone due to wiring mix up?
MSA-DTAG | WA5106610 | 3 | PPM Project Painting & Maintenance | Graffiti on door in laneway - between 1903 & 1987 buildings | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 4 | 2022-02-07 09:34 | 2022-02-14 17:00 | 2022-02-16 08:00 | 2022-02-14 17:00 | 2022-02-16 12:00 |  |  | job completed - Prepare by cleaning surface. Apply one coat of oil based primer and one coat of Gloss Enamel to match existing
MSA-DTWD | WA5126666 | 3 | Equans Mechanical Services Australia | Level 3 - Room 305 - No air flow - see details | Air Conditioning | Room Air Conditioners | 580.81 | Pass | Pass | 0 | 0 | 4 | 2022-02-14 09:14 | 2022-02-21 17:00 | 2022-02-18 12:00 | 2022-02-21 17:00 | 2022-02-18 16:00 |  |  | Attended site gained access and carried out inspection of VAV and BMS control. VAV found to be set to inactive operations mode on BMS set back to auto and confirmed damper operation. VAV resumed normal function and now supply. Accessed vav confirmed operation and stroke. Monitored function.
MSA-DTWD | WA5151593 | 3 | Schneider Electric Australia Pty Ltd | Chalk and cheese cafe - Main door not self locking | Building | Automatic Doors |  | Fail | Fail | 1 | 1 | 4 | 2022-02-17 14:22 | 2022-02-24 17:00 | 2022-03-03 07:30 | 2022-02-24 17:00 | 2022-03-03 11:30 |  |  | JOB COMPLETED - Attended site and investigated door fault with Chalk and Cheese. Found that the BGU was activated. Reset BGU and tested door operation. Whilst on site investigated door 251 and found that the Door seal is pushing the door against the Lock there fore making the lock appear to be sticking. Also removed redundant card swipe reader from 25 Aberdeen St fire stairwell
MSA-MRWA | WA5175240 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Auto dialer - reprogram auto dialer contact | Air Conditioning | Room Air Conditioners | 1110 | Fail | Fail | 1 | 1 | 4 | 2022-02-21 11:15 | 2022-02-22 17:00 | 2022-03-04 08:00 | 2022-02-22 17:00 | 2022-03-04 12:00 |  |  | works completed, waiting on BRAF approval.
MSA-DCA | WA5190134 | 2 | Techworks Electrical | Stuart Leach’s office - Fluorescent light fitting needs replacement. Fittings on site. | Electrical | Lighting, Internal | 748.31 | Pass | Pass | 0 | 0 | 4 | 2022-02-24 11:07 | 2022-03-01 17:00 | 2022-02-28 09:00 | 2022-03-01 17:00 | 2022-02-28 13:00 |  |  | Replaced fluro lights for led panels in stuarts office and in library
MSA-DTWD | WA5199796 | 2 | WESTERN IRRIGATION PTY LTD | Grounds Retic not running to program, sprinklers not working | Plumbing & Drainage | Water | 712.55 | Pass | Pass | 0 | 0 | 4 | 2022-03-01 11:58 | 2022-03-04 17:00 | 2022-03-04 09:30 | 2022-03-04 17:00 | 2022-03-04 13:30 |  |  | Tested all irrigation stations and replace broken sprinklers.
MSA-DTWD | WA5201155 | 2 | Techworks Electrical | Ladies toilets lights not working | Electrical | Lighting, Internal | 996.67 | Pass | Pass | 0 | 0 | 4 | 2022-03-02 11:58 | 2022-03-08 17:00 | 2022-03-08 06:00 | 2022-03-08 17:00 | 2022-03-08 10:00 |  |  | Replaced fluro lights to LEDs in a block female toilets and replaced fluro tubes in library
MSA-DTWD | WA5203070 | 1 | Protek 24/7 Building & Maintenance | B67 - Roof leak over welding bays | Building | General Building | 685.8 | Pass | Pass | 0 | 0 | 4 | 2022-03-03 10:30 | 2022-03-04 17:00 | 2022-03-04 07:30 | 2022-03-04 17:00 | 2022-03-04 11:30 |  |  | Repair Roof leak
MSA-DTAG | WA5204294 | 1 | Australian HVAC Services Pty. Ltd. | Supreme Court Gardens - Court 3 - Air con is not working | Air Conditioning | Room Air Conditioners | 428.31 | Pass | Pass | -1 | -1 | 4 | 2022-03-04 09:33 | 2022-03-08 17:00 | 2022-03-04 12:00 | 2022-03-08 17:00 | 2022-03-04 16:00 |  |  | Attend site. Organise access through Sally Port to access court 3 plantroom. Check operation of Unit and found not running. Check all safety switches and found to be normal. Carry out electrical fault finding. Found bad neutral connection on evap fan contactor coil. Remove wire from contactor and srip back for cleaner connection. Replace wire in contactor and found neutral to now return to all coils. Found unit to start and operate as normal. Will monitor operation over a week.
MSA-DTWD | WA5215619 | 3 | Building Automation & Electrical Services Pty Ltd | D Block - BMS Control Room - BMS to Green skills has stopped working | Building | General Building |  | Fail | Fail | 1 | 1 | 4 | 2022-03-10 14:25 | 2022-03-17 17:00 | 2022-03-25 12:00 | 2022-03-17 17:00 | 2022-03-25 16:00 |  |  | Reset to all controllers
MSA-DCA | WA5216722 | 1 | Barclay Engineering | Level 2 - HLT Loading Dock -Fire Doors inoperable, hydraulic pump runs continuously. see notes | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) |  | Fail | Fail | 1 | 1 | 4 | 2022-03-11 12:11 | 2022-03-14 17:00 | 2022-03-18 08:00 | 2022-03-14 17:00 | 2022-03-18 12:00 |  |  | job completed - Fix sliding door rollers on Meter Shed at Water Corp Kalgoorlie
MSA-DTWD | WA5216894 | 2 | JEM Carpentry | Outside BLD 822 and BLD 820 - Various pieces of outdoor furniture faulty | Furniture | Outdoor Furniture |  | Fail | Fail | 14 | 14 | 4 | 2022-03-11 13:50 | 2022-03-16 17:00 | 2022-06-21 12:00 | 2022-03-16 17:00 | 2022-06-21 16:00 |  |  | Repairs to furniture
MSA-DTWD | WA5271966 | 2 | Protek 24/7 Building & Maintenance | Eaves outside of E30 - Water leaking through Mini Orb corrugated sheets/trims around columns | Roofing | Metal Roofing | 872.9 | Pass | Pass | 0 | 0 | 4 | 2022-03-18 09:55 | 2022-03-23 17:00 | 2022-03-22 07:30 | 2022-03-23 17:00 | 2022-03-22 11:30 |  |  | Repair water leaking through Corrugated sheets
MSA-DCA | WA5288850 | 3 | Techworks Electrical | round light boxes - Two lights on the external poster boxes not working - see notes | Electrical | Lighting, External | 578.36 | Pass | Pass | 0 | 0 | 4 | 2022-03-23 14:11 | 2022-03-30 17:00 | 2022-03-28 10:30 | 2022-03-30 17:00 | 2022-03-28 14:30 |  |  | Attended site and looked into issues with two signs. Found both required new drivers as they weren't putting out the correct voltage for the LEDs. Replaced 2x drivers and all working well.
MSA-DTWD | WA5288938 | 3 | Schneider Electric Australia Pty Ltd | B block - Level 1 - There is a fault with the iNet Seven October 2021 database report | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Fail | Fail | 0 | 0 | 4 | 2022-03-23 16:42 | 2022-03-30 17:00 | 2022-04-01 08:00 | 2022-03-30 17:00 | 2022-04-01 12:00 |  |  | Received copy of database not available previously. Discovered that for the individual numbersthat transaction history was requested, multiple individual numbers were assigned to the persons. Provided all individualassignment detail and transaction data directly to Gareth via email.
MSA-DTWD | WA5295396 | 2 | Schneider Electric Australia Pty Ltd | B2 - Level 1 - All Building - No Communication in all building | Security | Access Control |  | Pass | Pass | 0 | 0 | 4 | 2022-03-29 13:22 | 2022-04-01 17:00 | 2022-03-30 08:00 | 2022-04-01 17:00 | 2022-03-30 12:00 |  |  | Job completed
MSA-DTAG | WA5301508 | 3 | Australian HVAC Services Pty. Ltd. | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 595.79 | Pass | Pass | -1 | -1 | 4 | 2022-03-26 06:00 | 2022-04-01 17:00 | 2022-03-26 08:00 | 2022-04-01 17:00 | 2022-03-26 12:00 | 1 |  | Retrospective work order required for a technician to isolate chilled water plant & cooling tower - Saturday 26 March from 08.00am until 12 noon
MSA-DFES | WA5303139 | 1 | MALCOLM THOMPSON PUMPS PTY LTD | Applied training ground - top and bottom dam - pump is alarming top dam and bottom pump wont turn on | Hydraulics | Hydraulic Pump Pipework |  | Pass | Pass | 0 | 0 | 4 | 2022-04-04 08:34 | 2022-04-05 17:00 | 2022-04-04 09:00 | 2022-04-05 17:00 | 2022-04-04 13:00 |  |  | job completed -ACADEMY HAD BEEN TESTING THE BACKUP GENERATOR POWER SUPPLY AND PUT THE TOP AND BOTTOM DAMPUMPS INTO MANUAL RESET MODE.RESET THE CONTROL PANELS AND RUN UP PUMPS FOR TESTING.LEFT BOTTOM DAM ON FOR CIRCULATION AS DAM WATER IS VERY DIRTY.NO FURTHER ACTION REQUIRED. SERVICE REQUEST IS NOW COMPLETE.
MSA-DTWD | WA5305383 | 1 | Equans Mechanical Services Australia | Cool room not cooling | Refrigeration | Coolroom | 629.87 | Pass | Pass | 0 | 0 | 4 | 2022-04-05 15:06 | 2022-04-06 17:00 | 2022-04-06 09:30 | 2022-04-06 17:00 | 2022-04-06 13:30 |  |  | Arrived on site signed in, gathered tools and equipment started checks on operation. Assisted by Dave checking in ceiling unit, access dificult. Found burnt wiring, replaced wiring from van stock. Sundries used small. Completed and tested system all ok monitored operation and and cooling all ok. Cleaned up and completed paperwork.
MSA-DTWD | WA5307242 | 2 | AWB Co. | STH wall near C44 - Hairdressing under croft Lighting out | Electrical | General Electrical | 901.14 | Pass | Pass | -1 | -1 | 4 | 2022-04-07 11:30 | 2022-04-12 17:00 | 2022-04-08 08:15 | 2022-04-12 17:00 | 2022-04-08 12:15 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty lighting. Figured out what we needed in order to completed job. Went to wholesaler to pick up all parts for job. Returned to site. Took down old light and replaced with new LED batten. Cut conduit and corrie to suited length. Saddled everything to roof. Put up other light in front of door. Siliconed all holes and any other entry points to eliminate risk of water damage. Repeated this procedure onto other side and made symmetrical. Packed and cleaned up both work areas. Took pictures of lights working. Completed paperwork. Signed out. *** job complete ***
MSA-MRWA | WA5319167 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Bitumen spray shed - Ground - External exhaust duct split | Air Conditioning | Ducted Split System | 450 | Pass | Pass | -1 | -1 | 4 | 2022-04-12 12:43 | 2022-04-19 17:00 | 2022-04-13 08:00 | 2022-04-19 17:00 | 2022-04-13 12:00 |  |  | Travelled to site and signed in. Located exhaust fan and isolated unit and removed torn canvas connection and wire brushed surrounds and sprayed with contact adhesive. Cut new canvas to size and sprayed with adhesive and wrapped around exhaust cowling. Reinstalled hose clamps and tightened. Waited for adhesive to dry and test ran unit all ok.
MSA-DTWD | WA5380588 | 2 | Schneider Electric Australia Pty Ltd | Access System not connecting between Lvlle & 30 Aberdeen | Security | Access Control |  | Fail | Fail | 0 | 0 | 4 | 2022-04-22 13:54 | 2022-04-28 17:00 | 2022-04-29 08:00 | 2022-04-28 17:00 | 2022-04-29 12:00 |  |  | Attended site at Leederville and inspected access control systemFound that all appeared to be working correctlyAttended site at 30 Aberdeen St to see if I could reprogram one of the cards that was having issuesLocated card and re programed the accessand found that there was a duplicate cardJohn Re programed the card number with the individual and found that the card is now workingJohn was going to check the remaining cards
MSA-DTAG | WA5381823 | 3 | Australian HVAC Services Pty. Ltd. | Level 8 - Court 84 - Air con is not turning on automatically | Air Conditioning | Room Air Conditioners | 428.31 | Pass | Pass | 0 | 0 | 4 | 2022-04-26 11:54 | 2022-05-03 17:00 | 2022-05-03 08:00 | 2022-05-03 17:00 | 2022-05-03 12:00 |  |  | Attend site. Access BMS and check operation of VAV box serving court 84. Found temps to be at setpoint. Drive box to min and max airflow, working ok. Access court 84 and check calibration of sensor, ok. Monitor operation of AC and found to be working as normal. VAV box is designed to go to minimum airflow when room temp is at setpoint. Check other courts on level 8 and found all to be working as normal.
MSA-DFES | WA5389983 | 3 | MR POTHOLE | Zendobia Tce - Parking area behind DO Applied Training Office - Tree Roots have damaged the Asphalt | Paving & Roadworks | Asphalt |  | Fail | Fail | 9 | 9 | 4 | 2022-05-02 09:20 | 2022-05-09 17:00 | 2022-07-12 12:00 | 2022-05-09 17:00 | 2022-07-12 16:00 |  |  | cut and lift entire area being 30mm thick! remove visible puff balls / cut and remove tree root along kerb line /apply mixture of copper sulphate and water 50mm: 500mm ratio to entire area / reset road base / lay asphalt 30mm
MSA-DCA | WA5396160 | 1 | Schneider Electric Australia Pty Ltd | Ground - Control Room - Issue with the lighting and door access system software | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 4 | 2022-05-06 08:51 | 2022-05-09 17:00 | 2022-05-06 10:30 | 2022-05-09 17:00 | 2022-05-06 14:30 |  |  | Installed controller
MSA-DTWD | WA5407848 | 3 | Schneider Electric Australia Pty Ltd | South block - W127 - Access Control System does not secure door | Security | Access Control |  | Fail | Fail | 2 | 2 | 4 | 2022-05-11 14:04 | 2022-05-18 17:00 | 2022-05-31 08:00 | 2022-05-18 17:00 | 2022-05-31 12:00 |  |  | Completed
MSA-DTWD | WA5416682 | 3 | Schneider Electric Australia Pty Ltd | West Block - Communications Riser Cabinet - Replace faulty & Out of Date batteries to Access System | Security | Access Control |  | Fail | Fail | 2 | 2 | 4 | 2022-05-13 07:43 | 2022-05-19 17:00 | 2022-05-31 12:00 | 2022-05-19 17:00 | 2022-05-31 16:00 |  |  | Job completed - Attended site and inspected access control cabinets in Li West Block for out of dated batteriesCollected replacement batteries from supplierReturned to site and installed batteriesChecked and tested battery backup function of cabinets in LlWeat Block
MSA-DTWD | WA5438131 | 2 | Techworks Electrical | Ladies toilets lights not working | Electrical | Lighting, Internal | 1584.54 | Pass | Pass | 0 | 0 | 4 | 2022-05-16 12:42 | 2022-05-19 17:00 | 2022-05-18 12:00 | 2022-05-19 17:00 | 2022-05-18 16:00 |  |  | Replaced all lights in girls and boys toilet with new led
MSA-DTWD | WA5472142 | 3 | Precise Air Group | Cool Room motors drain leaking into cool room | Refrigeration | Coolroom | 443.86 | Pass | Pass | -1 | -1 | 4 | 2022-05-23 14:41 | 2022-05-30 17:00 | 2022-05-25 07:30 | 2022-05-30 17:00 | 2022-05-25 11:30 |  |  | Attended site and completed pre start paperwork and singed In. Acessed cool room in cafe and found drain to be overflowing. Inspected and attempted to clear drain from entry. Drain is connected to wall split in kitchen drain. Pressure came out of that drain instead of pushing blockage out of exit. Cut drain above exit. Found drain full of water and dirt . Cleared drain with pressurised nitrogen. Found drain to clear. Travlled to supplier and collected beverage tube and hose clamps. Returned to site and fitted. This tube can be taken off in the event the drain blocks up again. Tested drain and found water to run off all ok. Mopped up water and tidied up work area. Monitored and completed paperwork. No further works required.
MSA-DCA | WA5482657 | 2 | Techworks Electrical | Main Building - Various Levels -Light switches and dimmers need replacing - See notes below | Electrical | General Electrical | 793.19 | Pass | Pass | 0 | 0 | 4 | 2022-05-31 13:53 | 2022-06-03 17:00 | 2022-06-02 09:00 | 2022-06-03 17:00 | 2022-06-02 13:00 |  |  | Replaced 9x dimmersReplaced 4x switch Mech blanks
MSA-DTWD | WA5482721 | 1 | Precise Air Group | A51 - VAV duct has come away from VAV - creating a noise hazard | Air Conditioning | Room Air Conditioners | 528.52 | Pass | Pass | 0 | 0 | 4 | 2022-05-31 14:32 | 2022-06-01 17:00 | 2022-06-01 08:00 | 2022-06-01 17:00 | 2022-06-01 12:00 |  |  | Attended site signed in and spoke to client. Located and inspected area with noise complaint. Found ductwork had come loose and torn. Due to design of the ceiling slats a second person was needed to safely removed and reinstall slats. Ductwork was cut and reinstalled and slats put back.
MSA-DTWD | WA5486360 | 2 | AWB Co. | Replace lights in staff kitchen not working | Electrical | Lighting, Internal | 988.14 | Pass | Pass | -1 | -1 | 4 | 2022-06-01 08:15 | 2022-06-07 17:00 | 2022-06-03 11:00 | 2022-06-07 17:00 | 2022-06-03 15:00 |  |  | More lights out in corridors that need light fittings replaced
MSA-DTWD | WA5487459 | 2 | Equans Mechanical Services Australia | AG10B Café Kitchen - Display Fridge not working due to blocked/dirty coils | Refrigeration | Refrigerators | 446.78 | Pass | Pass | -1 | -1 | 4 | 2022-06-01 15:35 | 2022-06-07 17:00 | 2022-06-03 09:30 | 2022-06-07 17:00 | 2022-06-03 13:30 |  |  | Collected coil cleaner and materials required for works. Travelled to site signed in and carried out inspection of equipment. Isolated unit removed panels and carried out coil clean in evap and condenser coils with food proccing area approved product. Noted heavy sediment build up within evap condensation tray. Cleared and removed sediments. Once coil free of partials and condensation drain confirmed to be working normal. Restored power to unit and carried out operation test. Noted evap fans had failed. Site have indicated they will raise another job for further investigation. Work area had been left tidy.
MSA-DTWD | WA5499244 | 2 | Schneider Electric Australia Pty Ltd | North Block - N129 - Access control systems have lost comms to 30, 19,12 Aberdeen & 133 Newcastle | Security | Access Control |  | Pass | Pass | 0 | 0 | 4 | 2022-06-10 11:51 | 2022-06-15 17:00 | 2022-06-15 12:00 | 2022-06-15 17:00 | 2022-06-15 16:00 |  |  | job completed - Checked and confirmed that the Xenta controllers were responding to Ping commandsRestarted Xenta in 30 19. 12 Aberdeen st and also 133 New Castle StChecked and confirmed access transactions and controller status was now correct
MSA-DTWD | WA5547962 | 1 | Lane's Plumbing | BLD 821 - Boiler room - Hot water pipe faulty | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 4 | 2022-06-17 08:13 | 2022-06-20 17:00 | 2022-06-17 09:30 | 2022-06-20 17:00 | 2022-06-17 13:30 |  |  | REPLACE CORRODED LEAKING PIPEWORK IN BOILER ROOM BLD 821
MSA-DTAG | WA5566676 | 2 | Total Security Systems Pty Ltd | Door in garage entering building - Swipe access not locking automatically | Security | Access Control | 735 | Pass | Pass | 0 | 0 | 4 | 2022-06-23 10:45 | 2022-06-28 17:00 | 2022-06-28 11:45 | 2022-06-28 17:00 | 2022-06-28 15:45 |  |  | 28/6/2022 - Jose Pereira Travel to site 11.45am to 1.15pmTime on site 1.15pm to 1.45pmTravel from site 2.15pm to 3.45pmInvestigate issue - Adjusted the door closer door now closes completely as this was stopping it from closing. No issue, just needed adjustment. Not a warranty issue.
MSA-DTWD | WA5572172 | 2 | Lane's Plumbing | BLD 816- Kitchen -Faulty leaking p trap | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 4 | 2022-06-29 14:28 | 2022-07-04 17:00 | 2022-07-01 10:30 | 2022-07-04 17:00 | 2022-07-01 14:30 |  |  | repairs to tap
MSA-MRWA | WA5583839 | 1 | Schindler Lifts Australia | Lift 1 - stuck on level 7 - see notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 4 | 2022-07-04 15:29 | 2022-07-05 17:00 | 2022-07-05 09:30 | 2022-07-05 17:00 | 2022-07-05 13:30 |  |  | Works completed
MSA-DTWD | WA5609501 | 3 | Building Automation & Electrical Services Pty Ltd | Room sensor reading 38.7 actual 21 degrees | Building | General Building |  | Fail | Fail | 0 | 0 | 4 | 2022-07-13 14:58 | 2022-07-20 17:00 | 2022-07-21 07:30 | 2022-07-20 17:00 | 2022-07-21 11:30 |  |  | Repairs
MSA-DTWD | WA5628179 | 2 | Techworks Plumbing | Wall hung basin ripped off wall | Plumbing & Drainage | Water | 451.15 | Pass | Pass | 0 | 0 | 4 | 2022-07-15 11:46 | 2022-07-20 17:00 | 2022-07-19 09:00 | 2022-07-20 17:00 | 2022-07-19 13:00 |  |  | Attended site for a detached wall hung basin. Removed broken basin andinspected; found the plugs had been pulled out as the holes were drilledwith a larger sized drillbit than required.went to Reece to grab new fixings and a 12mm drill it and returned to site,drilled the new holes and installed basin.siliconed the perimeter and a little on the back of the basin to Give thenew fixings some extra support.re wrapped basin in danger tape, cleaned up and left site.
MSA-DTWD | WA5655435 | 3 | AWB Co. | Blown fluros | Electrical | Lighting, Internal | 530.59 | Pass | Pass | 0 | 0 | 4 | 2022-07-18 08:24 | 2022-07-25 17:00 | 2022-07-25 09:00 | 2022-07-25 17:00 | 2022-07-25 13:00 |  |  | Attended site signed in jsa completed. Replaced various tubes and globes in B1 building.All tested and working. Job completed
MSA-DTWD | WA5655920 | 3 | AWB Co. | Patch paint water damaged ceiling ( leak repaired ) | Building | Ceiling | 873.42 | Fail | Fail | 1 | 1 | 4 | 2022-07-18 11:05 | 2022-07-25 17:00 | 2022-07-29 08:00 | 2022-07-25 17:00 | 2022-07-29 12:00 |  |  | Patch paint water damaged ceiling ( leak repaired )
MSA-DTWD | WA5677303 | 2 | Building Automation & Electrical Services Pty Ltd | Fume Cupboard 7 wont start up BMS | Building | General Building |  | Pass | Pass | 0 | 0 | 4 | 2022-07-25 13:49 | 2022-07-28 17:00 | 2022-07-28 12:00 | 2022-07-28 17:00 | 2022-07-28 16:00 |  |  | Completed
MSA-DTAG | WA5680217 | 2 | EASTERN HILLS ELECTRICAL SERVICE | ground-Registry/Custody/Court 2- various fluro's flickering - see notes | Electrical | Lighting, Internal | 973.13 | Pass | Pass | -1 | -1 | 4 | 2022-07-27 10:41 | 2022-08-01 17:00 | 2022-07-28 09:00 | 2022-08-01 17:00 | 2022-07-28 13:00 |  |  | Replaced various lights
MSA-DTWD | WA5693765 | 2 | AWB Co. | install Airway Canisters N117 falling off wall-see notes | Building | Internal Walls | 433.42 | Pass | Pass | 0 | 0 | 4 | 2022-08-04 15:03 | 2022-08-09 17:00 | 2022-08-09 10:30 | 2022-08-09 17:00 | 2022-08-09 14:30 |  |  | Works completed
MSA-DTWD | WA5697813 | 3 | Techworks Electrical | Various lights out - Replace lighting that is not functioning correctly | Electrical | Lighting, Internal | 1394.9 | Pass | Pass | -1 | -1 | 4 | 2022-08-09 12:05 | 2022-08-16 17:00 | 2022-08-10 11:00 | 2022-08-16 17:00 | 2022-08-10 15:00 |  |  | Replaced tubes and downlights in kendrew D block, McLarty Q block and Clarkson campus
MSA-DTWD | WA5698168 | 2 | Schneider Electric Australia Pty Ltd | N129 - Access system lost connection to all campus | Security | Access Control |  | Fail | Fail | 0 | 0 | 4 | 2022-08-09 15:13 | 2022-08-12 17:00 | 2022-08-15 08:00 | 2022-08-12 17:00 | 2022-08-15 12:00 |  |  | Job is completed - Access control is operating correctly
MSA-DFES | WA5699648 | 2 | Workzone Pty Ltd | Volunteers side - water leak in training room - see notes | Building | Ceiling | 720 | Fail | Fail | 0 | 0 | 4 | 2022-08-10 11:09 | 2022-08-15 17:00 | 2022-08-18 06:00 | 2022-08-15 17:00 | 2022-08-18 10:00 |  |  | Repair roof leak, treat ceiling with mould killer
MSA-DTWD | WA5700049 | 3 | Equans Mechanical Services Australia | Roomm/Office F58 - 2 x Faulty Aircon wall switches, please repair. | Air Conditioning | Room Air Conditioners | 417.55 | Pass | Pass | 0 | 0 | 4 | 2022-08-10 14:23 | 2022-08-17 17:00 | 2022-08-17 12:00 | 2022-08-17 17:00 | 2022-08-17 16:00 |  |  | Checked system and switches all operating correctly tried swapping switches for neon type unable due to swithch settings not correct only signal type. Lecturers confused when turning unit on weather it started and they continually pressing causing issues with unit operations.
MSA-DTWD | WA5706276 | 1 | COMMERCIAL PLUMBING AND GAS | Outside near access ramp East end of building - Underground water supply leak - See notes below | Plumbing & Drainage | Water | 469.15 | Pass | Fail | 0 | 0 | 4 | 2022-08-11 10:10 | 2022-08-12 17:00 | 2022-08-12 15:00 | 2022-08-12 17:00 | 2022-08-12 19:00 |  |  | dug and repaired 20mm pipe near demountable
MSA-DTWD | WA5714711 | 3 | Building Automation & Electrical Services Pty Ltd | Plant Room Boiler - Replace faulty 24 VDC Transformer A Block Boiler | Mechanical Services | Boilers |  | Pass | Pass | 0 | 0 | 4 | 2022-08-12 08:04 | 2022-08-19 17:00 | 2022-08-18 07:30 | 2022-08-19 17:00 | 2022-08-18 11:30 |  |  | Repairs to boiler
MSA-DTWD | WA5715221 | 2 | Damian Rak Electrical Pty Ltd | Building 844 - faulty security lights | Electrical | Lighting, External |  | Fail | Fail | 2 | 2 | 4 | 2022-08-12 12:15 | 2022-08-17 17:00 | 2022-09-02 08:00 | 2022-08-17 17:00 | 2022-09-02 12:00 |  |  | Repairs to lights
MSA-DTWD | WA5752061 | 2 | Techworks Electrical | Level g - Metals Section - the metal Cropper has a broken power plug and cord | Electrical | General Electrical | 953.35 | Pass | Pass | 0 | 0 | 4 | 2022-08-17 11:18 | 2022-08-22 17:00 | 2022-08-22 09:00 | 2022-08-22 17:00 | 2022-08-22 13:00 |  |  | Work NoteAttended site installed supply cable for metal cropper machine Direction Tested machine all working Lecturer tested machine all working
MSA-DTWD | WA5762040 | 2 | Lane's Plumbing | Faulty PVC join | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 4 | 2022-08-18 12:23 | 2022-08-23 17:00 | 2022-08-19 10:30 | 2022-08-23 17:00 | 2022-08-19 14:30 |  |  | Job is complete - Faulty PVC join repaired
MSA-DFES | WA5780635 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Heritage Shed Ground Left Front drain is overflowing - see notes | Plumbing & Drainage | Water | 624.68 | Pass | Pass | -1 | -1 | 4 | 2022-08-19 12:05 | 2022-08-26 17:00 | 2022-08-22 08:00 | 2022-08-26 17:00 | 2022-08-22 12:00 |  |  | Attend site to check out storm drain not draining away in driveway. Removed lid found tank is full to top and not draining down. Hire pump to suck down tank to check if tank outlet is blocked or if there is a problem with leach drain system. Ground around leach drain is very wet, likely the ground can’t absorb any more water causing carpark drain not to drain down. We would recommend inter connecting other car park drain together that way water will be pumped out in to over flow area. Or upgrade leach drain area for more ground soakage. Tank size is 1500wide x 1500 deep with 150 outlet
MSA-DTWD | WA5790972 | 3 | Building Automation & Electrical Services Pty Ltd | broken actuator on heating mechanism | Building | General Building |  | Fail | Fail | 3 | 3 | 4 | 2022-08-22 13:47 | 2022-08-29 17:00 | 2022-09-21 07:30 | 2022-08-29 17:00 | 2022-09-21 11:30 |  |  | Completed
MSA-DCA | WA5798534 | 3 | Techworks Plumbing | Jubilee Building - Ground Floor - Admin UAT - Toilet Cistern is out of service | Plumbing & Drainage | Toilets/Cisterns | 917.77 | Pass | Pass | -1 | -1 | 4 | 2022-08-29 15:03 | 2022-09-05 17:00 | 2022-08-30 14:00 | 2022-09-05 17:00 | 2022-08-30 18:00 |  |  | Arrived at the museum for leaking toilet.i went around the back to the exposed flush pipe and removed it. The pipe had dwv sockets glued on, which would not have been sealing the pipework due to the approved fitting being a slightly different size to the outlet of the cistern. The kee seal was also crooked due to the pipe not being long enough.I removed that and the outlet valve because the pan was also leaking.we headed to Reece and came back to site with a new flush pipe and outlet valve.I made the hole in the wall big enough for me to fit a longer-cut flush valve in and pushed it on. We installed the new outlet valve and turned the water back on, checking for leaks.everythinng was sealed, so I re installed the wall panel and cleaned up the working area.left site and dropped trailer off.
MSA-DTWD | WA5832743 | 1 | Australian Airconditioning Services Pty Ltd | Cool room fan not working - Please see notes | Refrigeration | Coolroom | 879.64 | Pass | Pass | 0 | 0 | 4 | 2022-09-05 16:01 | 2022-09-06 17:00 | 2022-09-06 08:00 | 2022-09-06 17:00 | 2022-09-06 12:00 |  |  | complete
MSA-DTWD | WA5853752 | 2 | Equans Mechanical Services Australia | Chiller compound - Rear of block B - Fault on chiller 1, circuit A | Refrigeration | Chiller | 776.42 | Fail | Fail | 1 | 1 | 4 | 2022-09-12 10:39 | 2022-09-15 17:00 | 2022-09-23 08:00 | 2022-09-15 17:00 | 2022-09-23 12:00 |  |  | SEE REPORT
MSA-DCA | WA5853878 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - Cooling Tower 1 - Cooling Tower belts fallen off pulley | Air Conditioning | Cooling Tower | 666.22 | Pass | Pass | 0 | 0 | 4 | 2022-09-12 11:51 | 2022-09-13 17:00 | 2022-09-12 12:00 | 2022-09-13 17:00 | 2022-09-12 16:00 |  |  | Found 5x belts had fallen off cooling tower pulleys. Isolated power to cooling tower and disabled enable call. Removed side panel to access belts and pulleys. Found belts worn and cracked. Sourced replacement. Returned to site and fitted belts, found belts to be loose. Realigned motor to get correct tension on belts. Secured side panel back to cooling tower. Restored power and enabled call. Tested operation of ct, all ok. Completed paperwork.
MSA-DTWD | WA5878347 | 3 | Equans Mechanical Services Australia | N129 faulty fridge | Air Conditioning | Room Air Conditioners | 760.14 | Pass | Pass | -1 | -1 | 4 | 2022-09-15 07:34 | 2022-09-21 17:00 | 2022-09-15 11:00 | 2022-09-21 17:00 | 2022-09-15 15:00 |  |  | INVESTIGATED FRIDGE FAULTY FOUND LOOSEN WIRING, FIXED THE ISSUE ANDTEST FRIDGE.
MSA-DCA | WA5972969 | 2 | FCT SURFACE CLEANING | Ground Floor Exterior - Gantry hoarding (Murray St side) - External Graffiti on hoarding | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 4 | 2022-09-21 09:40 | 2022-09-27 17:00 | 2022-09-23 06:30 | 2022-09-27 17:00 | 2022-09-23 10:30 |  |  | Removal of graffiti
MSA-DCA | WA5974426 | 2 | EQUANS Mechanical Services (WA) Pty Limited | SLWA - Level 5 - Plant room - Plant equipment faults due to generator load testing | Equipment | Electrical Equipment | 534.91 | Pass | Pass | 0 | 0 | 4 | 2022-09-23 11:32 | 2022-09-29 17:00 | 2022-09-27 05:00 | 2022-09-29 17:00 | 2022-09-27 09:00 |  |  | Attended site. Accessed bms and shutdown plant. Carried out isolation of plant (pumps, chillers, boilers and vsds) and tagged out. Switched AGWA into local. Contractors carried out generator testing. Monitored plant and temps across the PCC. Generator test was unsuccessful and will need to rescheduled to a later date. Contractor advised works complete. Restored power to plant and switched system back to auto. Reset alarms from bms and confirmed plant started. Plant operational. Completed paperwork.
MSA-DTWD | WA5977917 | 3 | Schneider Electric Australia Pty Ltd | 240 IT department-Magnet Lock Mech on Door to IT not working | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 4 | 2022-09-28 07:22 | 2022-10-04 17:00 | 2022-10-03 08:00 | 2022-10-04 17:00 | 2022-10-03 12:00 |  |  | Repairs to door
MSA-DTWD | WA5995212 | 2 | AWB Co. | Fluoro tubes not working | Electrical | Lighting, Internal | 1209.85 | Pass | Pass | 0 | 0 | 4 | 2022-10-06 11:11 | 2022-10-11 17:00 | 2022-10-11 12:45 | 2022-10-11 17:00 | 2022-10-11 16:45 |  |  | Job complete
MSA-DTWD | WA5997699 | 1 | Equans Mechanical Services Australia | Anodes deteriorated and require replacement | Air Conditioning | Building HVAC Maintenance (Major Plant) | 644.42 | Pass | Pass | 0 | 0 | 4 | 2022-10-07 09:01 | 2022-10-10 17:00 | 2022-10-10 08:00 | 2022-10-10 17:00 | 2022-10-10 12:00 |  |  | SEE REPORT
MSA-DTWD | WA6072474 | 1 | Precise Air Group | The air conditioner in skills kitchen 3 is not working. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 625.01 | Pass | Pass | 0 | 0 | 4 | 2022-10-18 08:45 | 2022-10-19 17:00 | 2022-10-19 12:00 | 2022-10-19 17:00 | 2022-10-19 16:00 |  |  | attended site signed in and filled out nessesary paperwork. Located evap units not in operation. After carrying out functional checks ofcthe mechanical equipment and electrical testing of the units a problem was found in the controls section. after repairing we tested evaps 5.1 and 5.2 both units returned to normal operation.
MSA-DCA | WA6075716 | 1 | Critical Fire Protection & Training | Sprinkler head in ceiling space corroded and leaking. | Fire Protection Services | Sprinkler Systems | 1314.68 | Pass | Pass | 0 | 0 | 4 | 2022-10-18 10:23 | 2022-10-19 17:00 | 2022-10-19 08:00 | 2022-10-19 17:00 | 2022-10-19 12:00 |  |  | .
MSA-DFES | WA6108696 | 3 | Critical Fire Protection & Training | Replace/repair faulty water tank valve found at WA5829336 attendance - See notes below | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 1633.5 | Fail | Fail | 2 | 2 | 4 | 2022-10-20 10:13 | 2022-10-27 17:00 | 2022-11-07 08:00 | 2022-10-27 17:00 | 2022-11-07 12:00 |  | WACCES | Please allow:• Isolate system, drain down• Remove Potter valve tamper device and replace with new• Remove faulty butterfly valve and replace with new• Mechanical and electrical labour to complete the above• Reinstate system and test
MSA-DFES | WA6111778 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | ground bat building-arious lights out ground floor of BAT Building, 2 x lights out in Control Room | Electrical | Lighting, Internal | 854.38 | Pass | Pass | 0 | 0 | 4 | 2022-10-21 10:16 | 2022-10-24 17:00 | 2022-10-21 11:00 | 2022-10-24 17:00 | 2022-10-21 15:00 |  |  | Completed
MSA-DTWD | WA6111825 | 2 | Precise Air Group | S block S200-air con not working | Air Conditioning | Room Air Conditioners | 681.32 | Pass | Pass | 0 | 0 | 4 | 2022-10-21 10:40 | 2022-10-26 17:00 | 2022-10-24 12:00 | 2022-10-26 17:00 | 2022-10-24 16:00 |  |  | Attended site a d assessed area. Replaced fuse and re programmed controls. Unit left in normal operation
MSA-DTWD | WA6129034 | 2 | Protek 24/7 Building & Maintenance | A354 Carpet Tiles Under OSH Safety staff member & entry to A333 are lifting | Flooring | Carpet | 764.19 | Pass | Pass | -1 | -1 | 4 | 2022-10-27 10:18 | 2022-11-01 17:00 | 2022-10-28 10:30 | 2022-11-01 17:00 | 2022-10-28 14:30 |  |  | Replaced 4 carpet tiles and fitted door threshold strip
MSA-DFES | WA6149425 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Outside and inside station - Security Light not working - See notes below | Electrical | Lighting, Internal | 989.1 | Pass | Pass | 0 | 0 | 4 | 2022-11-04 15:44 | 2022-11-07 17:00 | 2022-11-07 12:30 | 2022-11-07 17:00 | 2022-11-07 16:30 |  |  | On site already from previous job at 12:00. Proceeded to collect materials to replace 2 x Faulty Security Lights and 1 x faulty Hallway Light with LED Varieties. Replaced fittings and tested, all working okay. Informed site rep of works complete and left site at 15:45.
MSA-DTWD | WA6156794 | 2 | AWB Co. | Sliding door hard to slide | Building | Doors | 432.85 | Pass | Pass | 0 | 0 | 4 | 2022-11-09 10:26 | 2022-11-14 17:00 | 2022-11-14 10:30 | 2022-11-14 17:00 | 2022-11-14 14:30 |  |  | Works completed
MSA-DTWD | WA6190380 | 0 | COMMERCIAL PLUMBING AND GAS | Block T , U , V - No water in blocks | Plumbing & Drainage | Water | 404.15 | Pass | Fail | 0 | 0 | 4 | 2022-11-16 07:46 | 2022-11-16 09:46 | 2022-11-16 09:30 | 2022-11-16 11:46 | 2022-11-16 13:30 |  |  | reset pumps, checked tanks, restored water, removed valve handles
MSA-DTWD | WA6191197 | 2 | Critical Fire Protection & Training | EWIS in alarm Nth level 1 visual line fault - see notes | Fire Protection Services | Smoke and Heat Detection | 431.3 | Pass | Pass | -1 | -1 | 4 | 2022-11-16 13:30 | 2022-11-21 17:00 | 2022-11-17 08:00 | 2022-11-21 17:00 | 2022-11-17 12:00 |  |  | The monitoring of the line was moved. This was monitored for 7 days and as the fault has not returned we believe this has fixed the issue.
MSA-DTWD | WA6230201 | 3 | Building Automation & Electrical Services Pty Ltd | N122 - BMS - AHU 1 North OA Vents not responding to BMS | Building | General Building |  | Pass | Pass | 0 | 0 | 4 | 2022-11-18 11:29 | 2022-11-25 17:00 | 2022-11-25 12:00 | 2022-11-25 17:00 | 2022-11-25 16:00 |  |  | Attended site on reports of no control over the O/A dampers on AHU 1 North.• Attended site to reports of no dampers operating on AHU 1 north.• Local checks at the controller found the output controller in good workingorder.• Actuators were found and tests on locking bolts to the damper shafts werechecked. No faults were found.• Manual override control of Outside Air Damper, Exhaust Damper & RecircDamper was carried out. All 3 dampers had full range of operation. From fullyclosed at 0V to 100% open at 10V. (voltages taken and were correct)• The AHU was then given a range of different temp set points to proveprogram control. The programming strategy was monitored to watch dampercontrol. No faults were found.• The AHU 1 North control air dampers operated together via one signal outputto make sure the balance of supply & return air is always maintained. The controlsignal to override these dampers is done on the BMS via the recirc damperoutput ONLY. The BMS shows only value p
MSA-DTAG | WA6231068 | 2 | Australian HVAC Services Pty. Ltd. | Level 8 - Court 84 - court room is too hot – possible issue with airconditioner | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Pass | 0 | 0 | 4 | 2022-11-18 13:18 | 2022-11-23 17:00 | 2022-11-21 08:00 | 2022-11-23 17:00 | 2022-11-21 12:00 |  |  | Attend site. Access level 6 BMS. Check operation of VAV 8.05 serving court 84. Found court room temp to be 22.8 degrees. Drive box to min and max airflows and found to reach design flow. Access level 8 court 84 and check calibration of sensor, ok. Return to BMS level 6 and monitor operation. Minimum airflow setpoint is 50l/s and at minimum one would think there was no airflow. Once the box reaches setpoint it reduces the airflow. Box setpoint is 22.8, lower setpoint to 22.5. Box is working as normal.
MSA-DTAG | WA6293615 | 1 | Australian HVAC Services Pty. Ltd. | Court 6 - Extremely hot, valve may need replacing | Air Conditioning | Package | 407.39 | Pass | Pass | 0 | 0 | 4 | 2022-11-30 10:01 | 2022-12-01 17:00 | 2022-11-30 11:00 | 2022-12-01 17:00 | 2022-11-30 15:00 |  |  | Attend site. Access BMS and check operation of AC serving court 6. Found court served by FCU 8. Check valves on bms and found heating valves shut. Found cooling valves, modulating 100% and shut off open. Access roof and check valves. Found heating valves shut. Found modulating valve 100% open and shut off valve shut. Check voltages to valve and found to be normal. Attemp to drive valve manually but found very tight. Disconnect actuator from valve and manually open valve with a shifter. Valve is seizing up. Leave valve in the open position. Access BMS and override cooling shut off valve to open. Monitor operation and found supply air temp to drop. Das has been submitted for replace off these valves. Waiting on approval
MSA-DTWD | WA6298162 | 1 | Techworks Plumbing | south side garden bed water coming up from ground - see notes | Plumbing & Drainage | Water | 917.88 | Pass | Pass | 0 | 0 | 4 | 2022-12-01 07:43 | 2022-12-01 17:00 | 2022-12-01 08:00 | 2022-12-01 17:00 | 2022-12-01 12:00 |  |  | Attended site at Munster college spoke to Rick he showed us where the garden bed was that had the leak we dug to find leaking pipe found retic pipe in the ground had burst we cut out a section of pipe to be repaired grabbed a 2 50 mm pressure couplings, 1x 50 mm repair coupling and some glue from reece repaired pipe and tested backfilled and cleaned upLeft site and completed paperwork
MSA-DTWD | WA6357665 | 1 | COMMERCIAL PLUMBING AND GAS | L2 Ladies Staff Toilet - Leaking cistern | Plumbing & Drainage | Toilets/Cisterns | 1236.8825 | Pass | Pass | 0 | 0 | 4 | 2022-12-05 15:32 | 2022-12-06 17:00 | 2022-12-06 12:00 | 2022-12-06 17:00 | 2022-12-06 16:00 |  |  | replaced old single flush cistern with invisi dual flush
MSA-DTWD | WA6362478 | 2 | Precise Air Group | Aircon to D Block Level 3 not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 456.08 | Pass | Pass | 0 | 0 | 4 | 2022-12-09 11:03 | 2022-12-14 17:00 | 2022-12-12 08:00 | 2022-12-14 17:00 | 2022-12-12 12:00 |  |  | Arrived on site and located equipment, no access to bms, investigated why system isn't running, after investigation found vsd not sending out power to run, checked vsd settings and turned unit on, monitored system and checked all operations and amps for fan motor, all seems to be fine and working as it should
MSA-DFES | WA6363900 | 2 | AWB Co. | Ground office - Fly screens damaged from weather mesh is ruined. | Building | Windows | 469.98 | Fail | Fail | 0 | 0 | 4 | 2022-12-12 08:03 | 2022-12-15 17:00 | 2022-12-16 12:30 | 2022-12-15 17:00 | 2022-12-16 16:30 |  |  | Removed 2 security screensRemoved damaged fly wire and spline,Replaced fly screen mesh and spline and replaced security screensJob completed
MSA-DCA | WA6389752 | 3 | Protek 24/7 Building & Maintenance | Basement - EF Plenum (Basement Tunnels) - leaves vacuumed from Exhaust Fan intake plenum - See Notes | Building | General Building | 122.4 | Pass | Pass | 0 | 0 | 4 | 2022-12-21 15:33 | 2022-12-30 17:00 | 2022-12-28 06:30 | 2022-12-30 17:00 | 2022-12-28 10:30 |  |  | Vacuumed leaves from plenum room
MSA-DCA | WA6407508 | 0 | TK Elevator Australia Pty Ltd | Back of House Lift - stuck on ground floor and door wont open | Lifts | Lifts | 1180 | Pass | Fail | 0 | 0 | 4 | 2023-01-10 09:22 | 2023-01-10 11:22 | 2023-01-10 09:52 | 2023-01-10 13:22 | 2023-01-10 13:52
MSA-DTWD | WA6415295 | 2 | Milners Tree Solutions Pty Ltd | east of J005 & South N001 - dead tree to be removed | Landscaping & Gardening | Tree Lopping | 2000 | Fail | Fail | 2 | 2 | 4 | 2023-01-11 15:42 | 2023-01-16 17:00 | 2023-01-30 06:45 | 2023-01-16 17:00 | 2023-01-30 10:45
MSA-DTAG | WA6426044 | 3 | Sapio Pty Ltd | Registry - Base of stairs - Security screen not working | Security | Monitoring | 722.17 | Fail | Fail | 0 | 0 | 4 | 2023-01-12 13:55 | 2023-01-19 17:00 | 2023-01-20 12:30 | 2023-01-19 17:00 | 2023-01-20 16:30
MSA-DTWD | WA6430770 | 2 | Techworks Electrical | 1st Floor Ladies toilets East - Lights not working | Electrical | Lighting, Internal | 596.89 | Pass | Pass | 0 | 0 | 4 | 2023-01-13 08:56 | 2023-01-18 17:00 | 2023-01-16 07:30 | 2023-01-18 17:00 | 2023-01-16 11:30
MSA-DCA | WA6438880 | 0 | EQUANS Mechanical Services (WA) Pty Limited | both chillers in the harry butler centre has failed | Equipment | Electrical Equipment | 709.47 | Pass | Fail | 0 | 0 | 4 | 2023-01-14 10:32 | 2023-01-14 12:32 | 2023-01-14 11:00 | 2023-01-14 14:32 | 2023-01-14 15:00
MSA-DFES | WA6487657 | 3 | Critical Fire Protection & Training | Practical training ground- Twin head pillar hydrant near dam- will not open | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 660 | Pass | Pass | 0 | 0 | 4 | 2023-01-18 13:56 | 2023-01-25 17:00 | 2023-01-23 12:00 | 2023-01-25 17:00 | 2023-01-23 16:00
MSA-DCA | WA6503936 | 2 | SCAVENGER SUPPLIES PTY LTD | HH/ Francis St- Hall 1- Restore fire sprinkler - see notes | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 1033.68 | Pass | Pass | -1 | -1 | 4 | 2023-01-19 12:15 | 2023-01-24 17:00 | 2023-01-20 13:30 | 2023-01-24 17:00 | 2023-01-20 17:30 |  | WACCES
MSA-DTAG | WA6516275 | 2 | Australian HVAC Services Pty. Ltd. | Air-conditioning on Level 6 not working | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Pass | -1 | -1 | 4 | 2023-01-23 10:28 | 2023-01-27 17:00 | 2023-01-23 12:00 | 2023-01-27 17:00 | 2023-01-23 16:00
MSA-DCA | WA6520776 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room on level 4 - Audible alarm from steam generator 2. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 546.18 | Pass | Fail | 0 | 0 | 4 | 2023-01-29 14:27 | 2023-01-29 16:27 | 2023-01-29 14:45 | 2023-01-29 18:27 | 2023-01-29 18:45
MSA-DCA | WA6527051 | 3 | Techworks Electrical | Basement - Men’s Toilets - RCD is tripping now new lights have been installed | Electrical | Lighting, Internal | 834.56 | Pass | Pass | 0 | 0 | 4 | 2023-02-01 13:14 | 2023-02-08 17:00 | 2023-02-06 12:00 | 2023-02-08 17:00 | 2023-02-06 16:00
MSA-DTWD | WA6528211 | 2 | Schneider Electric Australia Pty Ltd | room - N129 - COMM's Error on Access System | Security | Access Control |  | Fail | Fail | 0 | 0 | 4 | 2023-02-02 09:43 | 2023-02-07 17:00 | 2023-02-10 08:00 | 2023-02-07 17:00 | 2023-02-10 12:00
MSA-DTWD | WA6534564 | 2 | AWB Co. | Block B - Room infront of reception - Air vent hanging from ceiling | Building | Ceiling | 453.5 | Pass | Pass | 0 | 0 | 4 | 2023-02-06 13:29 | 2023-02-09 17:00 | 2023-02-07 09:00 | 2023-02-09 17:00 | 2023-02-07 13:00
MSA-DTWD | WA6537729 | 2 | AWB Co. | Ceiling lights faulty | Electrical | Lighting, Internal | 675.32 | Pass | Pass | 0 | 0 | 4 | 2023-02-07 11:18 | 2023-02-10 17:00 | 2023-02-10 12:30 | 2023-02-10 17:00 | 2023-02-10 16:30
MSA-DTWD | WA6539455 | 1 | Precise Air Group | SK1 - Evap blowing warm air, no cooling | Air Conditioning | Ducted Split System | 861.48 | Pass | Pass | 0 | 0 | 4 | 2023-02-08 13:20 | 2023-02-09 17:00 | 2023-02-09 09:00 | 2023-02-09 17:00 | 2023-02-09 13:00
MSA-DTWD | WA6572742 | 2 | Equans Mechanical Services Australia | After hours button goes red when pushed but air is not coming on and area is very warm | Air Conditioning | Ducted Split System | 1355.75 | Fail | Fail | 1 | 1 | 4 | 2023-02-14 08:28 | 2023-02-17 17:00 | 2023-02-21 09:00 | 2023-02-17 17:00 | 2023-02-21 13:00
MSA-DTAG | WA6650872 | 2 | Australian HVAC Services Pty. Ltd. | Aircon not working in custody control area | Air Conditioning | Ducted Split System | 460.88 | Pass | Pass | 0 | 0 | 4 | 2023-02-20 13:53 | 2023-02-23 17:00 | 2023-02-21 08:00 | 2023-02-23 17:00 | 2023-02-21 12:00
MSA-DTWD | WA6676541 | 2 | Critical Fire Protection & Training | Slow leak from fire sprinkler head Eastern wall - could be from head unit? | Fire Protection Services | Sprinkler Systems | 533.5 | Pass | Pass | 0 | 0 | 4 | 2023-02-28 14:37 | 2023-03-03 17:00 | 2023-03-01 12:00 | 2023-03-03 17:00 | 2023-03-01 16:00
MSA-DTWD | WA6680816 | 2 | WESTERN IRRIGATION PTY LTD | Water recycling shed - water recyling plant is not working | Plumbing & Drainage | Water |  | Fail | Fail | 1 | 1 | 4 | 2023-03-01 14:48 | 2023-03-07 17:00 | 2023-03-13 08:00 | 2023-03-07 17:00 | 2023-03-13 12:00
MSA-DTWD | WA6688992 | 2 | AWB Co. | closer is not working the door is closing with a big bang-see notes | Building | Doors | 453.5 | Pass | Pass | -1 | -1 | 4 | 2023-03-08 08:27 | 2023-03-13 17:00 | 2023-03-09 09:00 | 2023-03-13 17:00 | 2023-03-09 13:00
MSA-DTWD | WA6722038 | 3 | AWB Co. | Light not working and has no diffuser | Electrical | Lighting, Internal |  | Pass | Pass | -1 | -1 | 4 | 2023-03-14 14:25 | 2023-03-21 17:00 | 2023-03-15 09:00 | 2023-03-21 17:00 | 2023-03-15 13:00
MSA-DTAG | WA5390368 | 1 | Schindler Lifts Australia | Lift 2 - Carriage ceiling light in lift 2 is flashing | Lifts | Lifts |  | Pass | Fail | 0 | 0 | 4 | 2022-05-02 12:22 | 2022-05-03 17:00 | 2022-05-03 13:31 | 2022-05-03 17:00 | 2022-05-03 17:31 |  |  | When responding to the callback dated 03.05.2022, the Schindler Technician found a problem with your equipment. The car lighting/ interior was faulty. Following our attendance, the equipment was left in service.
MSA-DTWD | WA4986239 | 1 | Equans Mechanical Services Australia | Server Room - Air conditioner has a recurring fault and not cooling - see details below | Air Conditioning | Room Air Conditioners | 371.51 | Pass | Pass | 0 | 0 | 4 | 2021-12-31 12:48 | 2022-01-04 17:00 | 2022-01-04 10:00 | 2022-01-04 17:00 | 2022-01-04 14:00 |  |  | Found the controllers in the stores area flashing L5, caused by sudden high amps on inverter compressors. Called Daikin assist and went through a diagnostic testing procedure, isolated the slaves and checked put back on line. Checked all the inverter compressors, reset the FCU'S put panels back on and restarted all OK.
MSA-DFES | WA5001049 | 3 | AWB Co. | Internal door to hallway - door handle faulty, not operational | Building | Doors | 408 | Pass | Pass | -1 | -1 | 4 | 2022-01-11 08:21 | 2022-01-18 17:00 | 2022-01-12 07:00 | 2022-01-18 17:00 | 2022-01-12 11:00 |  |  | Supply + Install new door handle , remove door and secure door frame , alter door as required and reinstate.
MSA-DTAG | WA5037928 | 3 | Schindler Lifts Australia | Level 10 - Lift 3 - door is opening and is constantly beeping and stuck on level 2A | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 4 | 2022-01-17 09:00 | 2022-01-24 17:00 | 2022-01-17 09:15 | 2022-01-24 17:00 | 2022-01-17 13:15 |  |  | To be closed of at $0 cost
MSA-DTWD | WA5087607 | 1 | Precise Air Group | Air con is faulty - not turning on | Air Conditioning | Room Air Conditioners | 830.08 | Fail | Fail | 0 | 0 | 4 | 2022-01-24 11:10 | 2022-01-25 17:00 | 2022-01-27 10:00 | 2022-01-25 17:00 | 2022-01-27 14:00 |  |  | Attended site and located reported area. After carrying out fault finding we found the time delay relay had failed. Travelled to supplier and purchased new relay. Yearned back to site and fitted to unit. Unit left operational and in working order
MSA-DTWD | WA5094904 | 2 | AWB Co. | E Block - Ground - Lathe Faulty not turning on | Electrical | General Electrical | 633.21 | Pass | Pass | 0 | 0 | 4 | 2022-01-31 15:24 | 2022-02-03 17:00 | 2022-02-02 13:00 | 2022-02-03 17:00 | 2022-02-02 17:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located lathes that needed disconnecting. Got keys for locks from storeman so we could access inside box. De energised all feeds to lathes from switchboard and tagged out at board. Went through and took incoming feed out of box and putting j box on with connectors. Put out of service tags on all J boxes and coiled up cable neatly. Took pictures of everything after we had done. Completed paperwork. Signed out. *** Job completed ***
MSA-DTWD | WA5115874 | 2 | AWB Co. | Security lighting along walkway is not working | Electrical | Lighting, External | 962.06 | Pass | Pass | 0 | 0 | 4 | 2022-02-11 09:50 | 2022-02-16 17:00 | 2022-02-16 07:00 | 2022-02-16 17:00 | 2022-02-16 11:00 |  |  | Attended site and signed in. Completed JSA. Located faulty light fittings along side of b block. Supply and replaced fittings, lamps and starters where required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5141618 | 3 | AWB Co. | Metal Framed Door is Coming away from Door Frame due to screws stripped from frame | Building | Doors | 431.66 | Pass | Pass | -1 | -1 | 4 | 2022-02-16 11:30 | 2022-02-23 17:00 | 2022-02-17 10:45 | 2022-02-23 17:00 | 2022-02-17 14:45 |  |  | Replace door hinges to canteen external doors
MSA-DCA | WA5207709 | 2 | Techworks Electrical | Corner of G block - Corner security light is flashing which needs replacement | Electrical | Lighting, External | 499.98 | Pass | Pass | 0 | 0 | 4 | 2022-03-08 15:50 | 2022-03-11 17:00 | 2022-03-10 10:00 | 2022-03-11 17:00 | 2022-03-10 14:00 |  |  | identified and Found corroded connection inside fittings. Re-terminated and all working well. sealed unit
MSA-DTWD | WA5226642 | 1 | AHS Services WA Pty Ltd (Anchor) | A block - Level 2 - A220 - Male toilet - 3 Phase hot water unit is leaking | Plumbing & Drainage | Materials | 1048.36 | Pass | Pass | 0 | 0 | 4 | 2022-03-14 10:34 | 2022-03-15 17:00 | 2022-03-14 11:30 | 2022-03-15 17:00 | 2022-03-14 15:30 |  |  | Completed
MSA-DTWD | WA5290028 | 1 | AWB Co. | D Block - Ground - D30 - D30 breaker tripped then was reset and went “bang” and tripped again | Electrical | General Electrical | 763.48 | Pass | Pass | 0 | 0 | 4 | 2022-03-24 15:36 | 2022-03-25 17:00 | 2022-03-25 08:30 | 2022-03-25 17:00 | 2022-03-25 12:30 |  |  | Attended site signed in completed jsa. Spoke with site fm about tripping breaker. Breaker was tripping the board main switch in different panel Disconnected load side cables and done IR testing on circuit. Results passed, turned breaker off and turned on and it tripped again but only the rcd in the board not further downstream. Isolated board and removed breaker. Found a short inside the rcd. Replaced with new rcd and now works perfect and no tripping.*** job completed ***
MSA-DTWD | WA5294027 | 3 | AWB Co. | Bike door - Door kick plate damaged and requires replacement | Building | Doors | 721.5 | Pass | Pass | -1 | -1 | 4 | 2022-03-28 12:13 | 2022-04-04 17:00 | 2022-03-29 07:00 | 2022-04-04 17:00 | 2022-03-29 11:00 |  |  | Removed door filled and painted and re hung door
MSA-DTWD | WA5297397 | 1 | Mizco Pty Ltd | BLD 832 - Faulty heating settings - see notes | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Fail | Fail | 6 | 6 | 4 | 2022-03-31 09:59 | 2022-04-01 17:00 | 2022-05-10 10:00 | 2022-04-01 17:00 | 2022-05-10 14:00 |  |  | Replaced pressure switch
MSA-DTWD | WA5306145 | 1 | Protek 24/7 Building & Maintenance | Block 10 - Ground - Footpath between block 8 and 10 - Paving raised caused trip hazard | Building | General Building | 655 | Pass | Pass | -1 | -1 | 4 | 2022-04-06 10:35 | 2022-04-11 17:00 | 2022-04-06 11:30 | 2022-04-11 17:00 | 2022-04-06 15:30 |  |  | Repair paving
MSA-DTAG | WA5308699 | 1 | OCS SERVICES PTY LTD | Additonal cleaning required, faeces and other hygienic products to be cleaned - see notes below | Cleaning | Cleaning |  | Pass | Pass | 0 | 0 | 4 | 2022-04-08 14:51 | 2022-04-11 17:00 | 2022-04-09 10:00 | 2022-04-11 17:00 | 2022-04-09 14:00 |  |  | Clean external rear Magrites exit
MSA-DTAG | WA5325613 | 0 | Sapio Pty Ltd | Main wall - Cameras for SAT in control room - (DMJC Level 10) - not working | Security | CCTV Surveillance | 190 | Pass | Fail | 0 | 0 | 4 | 2022-04-14 10:40 | 2022-04-14 12:40 | 2022-04-14 12:15 | 2022-04-14 14:40 | 2022-04-14 16:15 |  |  | Rejoined WS to domain and restarted PC. All back up and running OK. Checked all cameras andconfirmed all OK.
MSA-DTAG | WA5400940 | 3 | Australian HVAC Services Pty. Ltd. | L13 Loud noise coming from air vent adjacent to Magistrates lift | Air Conditioning | Room Air Conditioners | 428.31 | Pass | Pass | -1 | -1 | 4 | 2022-05-10 14:13 | 2022-05-17 17:00 | 2022-05-10 14:30 | 2022-05-17 17:00 | 2022-05-10 18:30 |  |  | Attend site. Access level 13 and investigate air noise. Access ceiling and found vav boxes in the closed position. Access level 6 plantroom and check bms. Found level 7 to 14 all boxes offline. Obtain keys from key box and access controller on level 8 and 12. Carry out power cycle and wait for controllers to reset. Found controllers to slowly reset. Floors now coming back online. Monitor operation and make sure floors come up to temp. Have contacted icon logic about this issue and what options we have to stop this issue from occurring. Icon logic will get back to me.
MSA-DFES | WA5495754 | 2 | Protek 24/7 Building & Maintenance | Level 1 - Banging noise above female and male toilet in main building | Building | General Building | 707.04 | Pass | Pass | -1 | -1 | 4 | 2022-06-08 15:00 | 2022-06-13 17:00 | 2022-06-09 08:30 | 2022-06-13 17:00 | 2022-06-09 12:30 |  |  | Replace dektite, secure roof vent cover
MSA-DTWD | WA5499871 | 0 | Protek 24/7 Building & Maintenance | Room F50 - Roof Leak- Will need water soaker & Blower | Roofing | Metal Roofing | 655 | Pass | Fail | 0 | 0 | 4 | 2022-06-10 14:55 | 2022-06-10 16:55 | 2022-06-10 16:00 | 2022-06-10 18:55 | 2022-06-10 20:00 |  |  | Roof Leak - Room F50
MSA-DTWD | WA5511987 | 2 | Techworks Electrical | G/1 Workshops lights not working, walkways and workshops | Electrical | Lighting, Internal | 890.43 | Pass | Pass | 0 | 0 | 4 | 2022-06-13 11:48 | 2022-06-16 17:00 | 2022-06-15 10:00 | 2022-06-16 17:00 | 2022-06-15 14:00 |  |  | Replaced lights in workshops, walkways, passages and rooms
MSA-DTWD | WA5566072 | 2 | Equans Mechanical Services Australia | Block 10 - Ground - Toilets - Toilet exhaust fan not working | Air Conditioning | Materials | 513.73 | Fail | Fail | 0 | 0 | 4 | 2022-06-22 14:16 | 2022-06-27 17:00 | 2022-06-28 11:30 | 2022-06-27 17:00 | 2022-06-28 15:30 |  |  | Found fan to be operating Found contactor to be partially seized and not pulling in correctly. Picked up parts from suppliers and returned to site. Isolated power. Replaced fan contacter and fitted new overload to suit. Wired accordingly. Removed isolation and started unit. Adjusted time clock and checked operation. All ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5584026 | 3 | AWB Co. | C block exterior-Repair bricks coming out of wall | Building | External Walls | 550.42 | Pass | Pass | 0 | 0 | 4 | 2022-07-05 06:45 | 2022-07-11 17:00 | 2022-07-11 11:30 | 2022-07-11 17:00 | 2022-07-11 15:30 |  |  | replace bricks and repointing
MSA-DTWD | WA5603690 | 3 | AWB Co. | B Block - Level 1 - Lights are tripping out | Electrical | Lighting, Internal | 559.01 | Pass | Pass | -1 | -1 | 4 | 2022-07-12 12:07 | 2022-07-19 17:00 | 2022-07-12 13:00 | 2022-07-19 17:00 | 2022-07-12 17:00 |  |  | Work NoteAttended site and signed in. Completed JSA. Spoke with facilities regarding the lights. Rick was not on site on Monday’s attendance. We were now advised that the circuit in fault in W1. I had not worked on W1, previously we found B1 was 5 hours behind and circuit was intermittently tripping on power shut off. W1 on Monday had tested good and in working order. Turned on lights and found W1 to now trip after about 30 seconds. Began investigating this fault. Found 2 x faults within carpark circuit. Isolated furtherest pole on the northern side, as it is showing a fault underground between the pole on N to E. Reinstated other poles to be working. Disconnected and removed junction box within the pit servicing W1. Created a new junction with solder and heat shrink with resin and placed rubber boot over the joins with it facing up to force water to run down and over the junction not in it. Tested circuit before energising and no fault found. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5628560 | 2 | AWB Co. | Rain Leak | Building | Ceiling | 758.58 | Fail | Fail | 1 | 1 | 4 | 2022-07-15 14:35 | 2022-07-20 17:00 | 2022-07-28 11:30 | 2022-07-20 17:00 | 2022-07-28 15:30 |  |  | Signed out key with security then inspected the water damaged ceiling in classroom S203. There are computers and desks in the way that will need covering up and I will also need a large platform ladder. I measured the ceiling height which is 3.6 meters then spoke with student services and the room is free today. I will attend my other jobs first then phone office. Returned with Craig and large platform ladder. We both carried the ladder up the stairs to avoid hitting the walls. I scraped back the loose paint and filled with plaster. I then sanded down the plaster and used stain block on the walls to cover over the water stains. We painted the ceiling and walls then vacuumed the work area to complete the job.
MSA-DTWD | WA5672943 | 3 | AWB Co. | 5 x lights out | Electrical | Lighting, Internal | 990.93 | Pass | Pass | -1 | -1 | 4 | 2022-07-20 10:50 | 2022-07-27 17:00 | 2022-07-22 10:00 | 2022-07-27 17:00 | 2022-07-22 14:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,went to b2 and wrote down list of all lighting requiring attention, went to wholesaler to pick up parts , returned to site and replaced tubes and light fittings, job limit reached (called fm and he said he will put another job through) , completed paperwork, signed out **job completed**
MSA-DTWD | WA5693826 | 2 | M Construction (WA) | ground-Entry door south side-Sliding door requires new rollers, is very hard to open. | Building | Doors | 1529.22 | Fail | Fail | 3 | 3 | 4 | 2022-08-04 15:53 | 2022-08-09 17:00 | 2022-08-31 13:00 | 2022-08-09 17:00 | 2022-08-31 17:00 |  | WACCES | Complete as per quote
MSA-DFES | WA5831448 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Water leak in training room | Plumbing & Drainage | Water | 658.02 | Pass | Fail | 0 | 0 | 4 | 2022-09-04 16:28 | 2022-09-04 18:28 | 2022-09-04 17:30 | 2022-09-04 20:28 | 2022-09-04 21:30 |  |  | Attended after hours and found sewage dripping down in ground floor corridor. This is coming from various point in the drain unknown as drain is lagged. Have isolated water to male taps and unpluggedurinal sensors. Have called for electrician and cleaners .. 2nd floor seems ok still to use.AHS has done some jetting and something has gone wrong or failed. I have isolated the hot and cold to the basins ,disconnected the urinal flushing and locked the toilet doors in the males 1st floor,done the same in females but not able to fully isolate the water I think the valve is faulty 32/40mm ball valve under the basin, may need replacing will need a shut down of water to the buildingthou. Taped the taps up. DFES on site said they will tape up all the doors to the toilets on ground and first floors.. removed ceiling panels but cleaners and wet vacuum will be needed to clean up. Madesafe and AHS needs to return to fix up their job, . Left 3 buckets to try and catch drips. The first floor mal
MSA-DTWD | WA5862050 | 3 | Critical Fire Protection & Training | Pre action pump room air leak - 211 | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 1173.7 | Pass | Pass | -1 | -1 | 4 | 2022-09-13 13:28 | 2022-09-20 17:00 | 2022-09-14 07:00 | 2022-09-20 17:00 | 2022-09-14 11:00 |  |  | Attended ste to Perth campus b1 to rectify a leak on the pre action system on level 2.Upon arrival the pipework was leaking in the pre action valve room on a short horizontalpiece of 65mm pipework.Isolated and drained the pre action system and replaced elbows, couplings andpipework.Once installed the system was filled with air and reinstated to normal operation.
MSA-DTWD | WA5980432 | 1 | Lane's Plumbing | Blocked toilet in the ensuite | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 4 | 2022-09-29 14:52 | 2022-09-30 17:00 | 2022-09-30 08:30 | 2022-09-30 17:00 | 2022-09-30 12:30 |  |  | Unblocked toilet
MSA-DCA | WA5982846 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Old Gaol - Ground Level - AC system heating control fault - See notes below | Air Conditioning | Room Air Conditioners | 484.23 | Pass | Pass | 0 | 0 | 4 | 2022-09-30 15:13 | 2022-10-05 17:00 | 2022-10-04 10:00 | 2022-10-05 17:00 | 2022-10-04 14:00 |  |  | Will quote for Mitsubishi electric to attend
MSA-DTAG | WA5987381 | 1 | Total Security Systems Pty Ltd | Sally Port intercom will not reset after call | Security | Security Management System |  | Pass | Pass | 0 | 0 | 4 | 2022-10-03 11:18 | 2022-10-04 17:00 | 2022-10-04 07:00 | 2022-10-04 17:00 | 2022-10-04 11:00 |  |  | 4/10/2022 - Michael Higginbotham travel to site 7am to 8.30amtime on site 8.30am to 9.30amtravel from site 9.30am to 11amConfirmed cancel not working om main unit in security hut.Cycled cell guard unit inside rack and re established systems functionality.Job complete.
MSA-DFES | WA6042077 | 1 | Critical Fire Protection & Training | tower 3 - next to gantry - broken hydrant | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 685.48 | Pass | Pass | 0 | 0 | 4 | 2022-10-17 08:20 | 2022-10-18 17:00 | 2022-10-17 10:00 | 2022-10-18 17:00 | 2022-10-17 14:00 |  |  | attended site to 547 Dundas Road to repair an inground fire hydrant.Upon inspection we determined that the spindle bolt was snapped.stripped apart the inground fire hydrant to get too the spindle bolt.removed snapped bolt and sourced new bolt from local supplierthe new bolt is high tensile so this should not happen again.rebuilt the inground fire hydrant back up and reinstated the water too check for leaks.hydrant is now repaired.
MSA-DTWD | WA6088619 | 3 | AWB Co. | A213 Staff room - Roof leak above A213 | Roofing | Tiled Roofing | 802.97 | Pass | Pass | -1 | -1 | 4 | 2022-10-19 09:37 | 2022-10-26 17:00 | 2022-10-20 07:00 | 2022-10-26 17:00 | 2022-10-20 11:00 |  |  | work completed as per signature slip
MSA-DTWD | WA6111841 | 2 | AWB Co. | ground metal fab - Faulty 3 Phase power point next to Plasma Cutter | Electrical | General Electrical | 1621.49 | Fail | Fail | 7 | 7 | 4 | 2022-10-21 10:52 | 2022-10-26 17:00 | 2022-12-14 08:30 | 2022-10-26 17:00 | 2022-12-14 12:30 |  |  | Attended site signed in jsa completed. Installed cable from board to outlet as per scope. Tested operational and comissioned.Job completed
MSA-DTWD | WA6128059 | 3 | AWB Co. | Patch and paint small wall area currently not painted - see notes below | Building | Internal Walls | 906.42 | Fail | Fail | 1 | 1 | 4 | 2022-10-26 11:59 | 2022-11-02 17:00 | 2022-11-07 07:00 | 2022-11-02 17:00 | 2022-11-07 11:00 |  |  | painting works completed
MSA-DCA | WA6149368 | 1 | Building Automation & Electrical Services Pty Ltd | Level 1 - Stage Door/ General - Unable to access BMS system - Technical Fault | Security | Access Control |  | Pass | Pass | 0 | 0 | 4 | 2022-11-04 14:32 | 2022-11-07 17:00 | 2022-11-07 10:00 | 2022-11-07 17:00 | 2022-11-07 14:00 |  |  | There really isn't anything manually or via BMS in this area to reduce the air temp.Mainly due to the rooms location. Which is underground/basement level. This area isdependent on the main AHU to be in full operational use.
MSA-DTWD | WA6155942 | 2 | AWB Co. | Skirting warped and twisted and pulling away from wall - See notes | Building | Internal Walls | 502.5 | Pass | Pass | 0 | 0 | 4 | 2022-11-08 15:28 | 2022-11-11 17:00 | 2022-11-10 10:00 | 2022-11-11 17:00 | 2022-11-10 14:00 |  |  | Works completed
MSA-DFES | WA6178944 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Large drains on apron, and rear gate full of debris and need cleaning. | Plumbing & Drainage | Drainage | 670.3 | Pass | Pass | -1 | -1 | 4 | 2022-11-14 15:04 | 2022-11-21 17:00 | 2022-11-17 10:00 | 2022-11-21 17:00 | 2022-11-17 14:00 |  |  | Attend site to investigate blocked spoon drains. Was directed by station staff to problem drains. Found spoon drains at rear gate and at front entrance completely full of leaves, sand and rubbish. Approx40m of spoon drain. Cleared debris from spoon drains and all okay.
MSA-DTWD | WA6521274 | 1 | Equans Mechanical Services Australia | Jewellery Workshops - multiple rooms - faulty airconditioning | Air Conditioning | Ducted Split System | 570.28 | Pass | Pass | 0 | 0 | 4 | 2023-01-30 09:40 | 2023-01-31 17:00 | 2023-01-31 07:00 | 2023-01-31 17:00 | 2023-01-31 11:00
MSA-DFES | WA6573250 | 2 | AWB Co. | Unit - SO dorm - Sliding window frame damaged. (see notes) | Building | Windows | 478.5 | Fail | Fail | 1 | 1 | 4 | 2023-02-14 11:56 | 2023-02-17 17:00 | 2023-02-22 11:30 | 2023-02-17 17:00 | 2023-02-22 15:30
MSA-DCA | WA6579147 | 3 | Techworks Electrical | Level 2 - Ladies toilets - Light continuously flickering | Electrical | Lighting, Internal | 332.005 | Pass | Pass | -1 | -1 | 4 | 2023-02-15 15:06 | 2023-02-22 17:00 | 2023-02-17 07:00 | 2023-02-22 17:00 | 2023-02-17 11:00
MSA-DCA | WA6390597 | 1 | Techworks Electrical | LX Bridges- Forestage Wall – HLT Lighting Bridges - GPO on wall is faulty - See Notes | Electrical | General Electrical | 573.84 | Pass | Pass | 0 | 0 | 3.9833 | 2022-12-22 10:52 | 2022-12-23 17:00 | 2022-12-23 08:45 | 2022-12-23 17:00 | 2022-12-23 12:44 |  |  | Arrived On site signed in and got keys then meet ken as Dylan is not on sight,found GPO that was faulty and where it was feed from, did some testing and found beetween active and neutral had 160v then we went down to level 1 theatre audio db and tested love from the rcd it was fed from, suspected junction somewhere that has loose neutral join, new circuit will need to be installed approx. 5 levels up, this circuit can not be re-energised as the cable is unsafe. quote to be provided.
MSA-DCA | WA4994790 | 0 | TK Elevator Australia Pty Ltd | Kitchen lift - out of order | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 3.9833 | 2022-01-10 07:31 | 2022-01-10 09:31 | 2022-01-11 12:09 | 2022-01-10 11:31 | 2022-01-11 16:08 |  |  | Replaced car slipper guide gibs on car top. Ran and checked operation, placed lift back into service.
MSA-DTWD | WA5861450 | 2 | COMMERCIAL PLUMBING AND GAS | Water supply leak at wash trough - see notes below | Plumbing & Drainage | Water | 459.15 | Pass | Pass | 0 | 0 | 3.9833 | 2022-09-13 09:35 | 2022-09-16 17:00 | 2022-09-16 13:00 | 2022-09-16 17:00 | 2022-09-16 16:59 |  |  | removed trough, chipped wall, repaired pipe, reinstalled trough
MSA-DTWD | WA5069177 | 2 | AHS Services WA Pty Ltd (Anchor) | Library Female Toilet 2nd cubicle toilet leaking water | Plumbing & Drainage | Toilets/Cisterns | 466.75 | Pass | Pass | 0 | 0 | 3.9667 | 2022-01-19 16:03 | 2022-01-24 17:00 | 2022-01-21 09:00 | 2022-01-24 17:00 | 2022-01-21 12:58 |  |  | Completed
MSA-DCA | WA6425298 | 1 | Precise Air Group | Controller 7 Comms Error. Controller off line. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 612.78 | Pass | Pass | 0 | 0 | 3.9667 | 2023-01-12 08:46 | 2023-01-13 17:00 | 2023-01-13 09:00 | 2023-01-13 17:00 | 2023-01-13 12:58
MSA-DCA | WA6250407 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Harry Butler Centre - Plant Room - Both Chillers are down | Refrigeration | Chiller | 371.62 | Pass | Pass | 0 | 0 | 3.9667 | 2022-11-22 08:02 | 2022-11-22 10:02 | 2022-11-22 08:03 | 2022-11-22 12:02 | 2022-11-22 12:01 |  |  | Reset both chillers 1 & 2. Monitored operation after reset. Checked bms for any further faults. Advised Sue of works carried out prior to leaving site.
MSA-DTWD | WA5090303 | 0 | ECO PLUMBING AND GAS PTY LTD | Block I & block J - no water to blocks | Plumbing & Drainage | Water | 528.28 | Pass | Fail | 0 | 0 | 3.95 | 2022-01-25 11:04 | 2022-01-25 13:04 | 2022-01-25 12:30 | 2022-01-25 15:04 | 2022-01-25 16:27 |  |  | Repaired burst pipe, clean out and flushed lines.
MSA-DFES | WA6400045 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Hydrant at rear of building above ground-major water leak | Plumbing & Drainage | Water | 643.06 | Pass | Fail | 0 | 0 | 3.95 | 2023-01-03 09:12 | 2023-01-03 11:12 | 2023-01-03 09:30 | 2023-01-03 13:12 | 2023-01-03 13:27
MSA-DTAG | WA5683036 | 2 | OCS SERVICES PTY LTD | Outside wall near emergency magistrates exit-Faecal matter on the outside wall near the magistrate | Cleaning | Sanitary Services |  | Pass | Pass | 0 | 0 | 3.95 | 2022-07-29 15:04 | 2022-08-03 17:00 | 2022-08-01 07:00 | 2022-08-03 17:00 | 2022-08-01 10:57 |  |  | Completed
MSA-DCA | WA6159121 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire Alarm fault in back up battery room - relating to fire suppression | Fire Protection Services | Fire Protection - Monitor System | 1425.32 | Pass | Fail | 0 | 0 | 3.9167 | 2022-11-10 11:51 | 2022-11-10 13:51 | 2022-11-10 12:50 | 2022-11-10 15:51 | 2022-11-10 16:45 |  |  | Attended site at 12.40pm to a Priority 0 call-out. Signed in at security where Howard told me what was going on. Howard explained to me that all 4 suppression systems were in common fault and were isolated at the SIP and that the SIP was also isolated on the MFIP. I proceeded to have a look at the SIP where all 4 systems were in common fault and the the Vesda's in all 4 utilities rooms were in fault. All systems were inoperable and the VWD's were lit and were alarming. After opened one of the vesda's it was noticed that the filter was dated in November 2020. Therefore the filter was needing to be replaced. I tried to plug my computer into the vesda to ascertain that this was the fault. Unfortunately I didn't have the right patch lead for this and it was later dropped of by another technician an hour later. All 4 vesda's were opened and it was made obvious to me that all faults were in relation to the filters needing replacement. All 4 filters were replaced and all 4 vesda's were re-pro
MSA-DTWD | WA5187076 | 1 | Precise Air Group | C003 - Air con is not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 3.85 | 2022-02-22 11:11 | 2022-02-23 17:00 | 2022-02-23 07:30 | 2022-02-23 17:00 | 2022-02-23 11:21 |  |  | Attended site and completed pre start paperwork and signed in. Acessed package system serving room c003. Found system running. Removed filter and washed. Isolated unit and checked supply air fan belts. All ok . Reinstated power and test ran and monitored. Put temp up as people in the room were getting cold. Watched unit cycle on and off a few times. Left all ok.
MSA-DTAG | WA5294618 | 0 | Sapio Pty Ltd | All Floors -All cameras are failing to connect to the server | Security | Monitoring | 490 | Pass | Pass | 0 | 0 | 3.85 | 2022-03-29 08:09 | 2022-03-29 10:09 | 2022-03-29 08:09 | 2022-03-29 12:09 | 2022-03-29 12:00 |  |  | Restored connection to all cameras on Milestone
MSA-DCA | WA5460201 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 Faulty | Refrigeration | Chiller | 240.7 | Pass | Pass | 0 | 0 | 3.8167 | 2022-05-18 11:54 | 2022-05-19 17:00 | 2022-05-19 12:02 | 2022-05-19 17:00 | 2022-05-19 15:51 |  |  | Carried out investigations of chiller 1 fault. HP safty trip noted to have occured on all compressor stages. Carried out reset of fault and placed chiller into lead operation. Monitored operation and confirm no further fault occured. Spoke with site BMS techs and extra data monitoring will be set up for chiller. No further action is able to be carried out on this job. If further fault is indicated site will be advised. Work area left tidy.
MSA-DTWD | WA6680456 | 2 | Dormakaba Australia Pty Ltd | N67 - Signage roller door - Repair roller door mechanism | Building | Automatic Doors | 206.95 | Pass | Pass | -1 | -1 | 3.8167 | 2023-03-01 11:30 | 2023-03-07 17:00 | 2023-03-02 09:26 | 2023-03-07 17:00 | 2023-03-02 13:15
MSA-DTAG | WA5697581 | 2 | AHS Services WA Pty Ltd (Anchor) | Magistrate Shower - No pressure, water at a trickle | Plumbing & Drainage | Water | 140.77 | Fail | Fail | 1 | 1 | 3.7833 | 2022-08-09 10:31 | 2022-08-12 17:00 | 2022-08-16 09:20 | 2022-08-12 17:00 | 2022-08-16 13:07 |  |  | Job completed
MSA-DTWD | WA5887583 | 2 | Precise Air Group | Air con very stuffy | Air Conditioning | Room Air Conditioners | 253.38 | Pass | Pass | 0 | 0 | 3.7833 | 2022-09-16 08:43 | 2022-09-21 17:00 | 2022-09-21 07:54 | 2022-09-21 17:00 | 2022-09-21 11:41 |  |  | arrived at site ,spoke to Steve facilities manger about room B207 ,checked room found room had big heat load when occupi ed with about 20 students and full of computers running, che cked BMS Controls with Paul from BAE SERVICES who look after all BMS Services here unit is Running at full capacity ,he advised it needs to have a new thermostat control with an oc cupied switch installed to increase airflow when classes are being carried out .Person to contact is Steve Kingslow at B AE SERVICES to get a quote .
MSA-DTWD | WA5127221 | 1 | AHS Services WA Pty Ltd (Anchor) | A block - Level 4 - female toilets - toilet flush not working | Plumbing & Drainage | Toilets/Cisterns | 1279.7325 | Pass | Pass | 0 | 0 | 3.7667 | 2022-02-14 11:52 | 2022-02-15 17:00 | 2022-02-15 07:15 | 2022-02-15 17:00 | 2022-02-15 11:01 |  |  | Picked up and replaced broken cistern Left hand side female level 4.Drilled out walls and fitted new buttons
MSA-DCA | WA6685307 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidity Alarm going off in Ground Level. | Air Conditioning | Ducted Split System | 546.18 | Pass | Fail | 0 | 0 | 3.7667 | 2023-03-06 15:01 | 2023-03-06 17:01 | 2023-03-06 16:00 | 2023-03-06 19:01 | 2023-03-06 19:46
MSA-DTWD | WA5106479 | 1 | Building Automation & Electrical Services Pty Ltd | Repair to BMS to acivate chiller one form defect pump replacement | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 3.75 | 2022-02-07 08:40 | 2022-02-08 17:00 | 2022-02-07 08:45 | 2022-02-08 17:00 | 2022-02-07 12:30 |  |  | Repair to BMS to acivate chiller one form defect pump replacement
MSA-DCA | WA5109658 | 2 | FCT SURFACE CLEANING | Fiji room – external door - Graffiti tag on the external Fiji room steel door. | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 3.75 | 2022-02-09 12:11 | 2022-02-14 17:00 | 2022-02-11 09:00 | 2022-02-14 17:00 | 2022-02-11 12:45 |  |  | graffitti
MSA-DTWD | WA5163946 | 2 | AWB Co. | A Block - A318 - Fume Hood No 11 has no power | Electrical | General Electrical | 687.35 | Pass | Pass | 0 | 0 | 3.75 | 2022-02-18 13:42 | 2022-02-23 17:00 | 2022-02-21 09:45 | 2022-02-23 17:00 | 2022-02-21 13:30 |  |  | Attended site and signed in. Completed jsa. Located room with faulty fume hood / no power fume hood. Looked for circuit that fume hood may be powered from and went to board to turn on. Everything was already turned on in board. Came back to fume booth and had a look at how everything was wired , found contactor box at top of fume booth , spoke with lecturers in area and they said it stopped working whilst they were using it, it was also said that 2x induction hot plates were being used at the time, opened contactor box and found that fuse had blown , tested cables and no fault detected, grabbed a fuse from booth next to it to test if it would work, booth worked , tested light and light wasn’t working, went to wholesaler and grabbed fuses and an led batten , returned to site, took off covers and removed light from booth, removed old light and replaced with new led, replace fuse , tested booth and load tested powerpoints on booth , everything working as intended, packed up , cleaned up,
MSA-DTAG | WA5207025 | 3 | AWB Co. | Basement - Kitchen - GPO in custody kitchen cabinet is not working | Electrical | General Electrical | 430.2 | Pass | Pass | -1 | -1 | 3.75 | 2022-03-08 10:33 | 2022-03-15 17:00 | 2022-03-09 10:00 | 2022-03-15 17:00 | 2022-03-09 13:45 |  |  | Job complete
MSA-DTWD | WA5287029 | 1 | Protek 24/7 Building & Maintenance | B Block Electrical Section - Gutters are blocked need cleaning out | Roofing | Guttering | 649.75 | Pass | Pass | 0 | 0 | 3.75 | 2022-03-22 09:33 | 2022-03-23 17:00 | 2022-03-23 11:00 | 2022-03-23 17:00 | 2022-03-23 14:45 |  |  | Clean Blocked Gutters
MSA-DTWD | WA5390260 | 1 | Protek 24/7 Building & Maintenance | Ground - J Block - External Footpath - Several trip hazards on the paved footpath | Building | General Building | 329.875 | Pass | Pass | 0 | 0 | 3.75 | 2022-05-02 11:26 | 2022-05-03 17:00 | 2022-05-03 11:15 | 2022-05-03 17:00 | 2022-05-03 15:00 |  |  | Pavers lifting on Pathway - Braf declined
MSA-DFES | WA5397393 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Whole of level 1 - Light globes out - See notes below | Electrical | Lighting, Internal | 985.63 | Pass | Pass | 0 | 0 | 3.75 | 2022-05-06 15:56 | 2022-05-13 17:00 | 2022-05-13 09:45 | 2022-05-13 17:00 | 2022-05-13 13:30 |  |  | Arrived on site at 0945 to identify and replace fluros out on 1st floor. Located 28 fluro’s requiring replacing, while on site 22 x 18W/840 4pin fluros (11lts) and 11x 14W/840 2ft tubes (11lts) were also found blown on lvl1 which surrounding wholesalers did not have in stock. Left site at 1050 to pick up parts from wholesaler. Returned back on site at 1145 and replaced/reenergised all fluros around 1st floor. Left site at 1330.
MSA-DTWD | WA5416828 | 2 | AWB Co. | roof leak | Roofing | Metal Roofing | 875.79 | Pass | Pass | 0 | 0 | 3.75 | 2022-05-13 08:42 | 2022-05-18 17:00 | 2022-05-16 06:45 | 2022-05-18 17:00 | 2022-05-16 10:30 |  |  | C026 replaced dektites, sealed flashing, sealed parapit capping, butane taped exposed box gutter lip, C210 sealed window flashing back into place. Site to monitor.
MSA-DTWD | WA5454350 | 3 | Equans Mechanical Services Australia | Level 4 - Plantroom - Hot Water System not working | Plumbing & Drainage | HWS/Units Electric & Gas | 2155.02 | Fail | Fail | 11 | 11 | 3.75 | 2022-05-17 10:37 | 2022-05-24 17:00 | 2022-08-09 13:30 | 2022-05-24 17:00 | 2022-08-09 17:15 |  |  | SEE REPORT
MSA-DTWD | WA5472901 | 2 | Precise Air Group | restaurant kitchen under bench fridge, under the microwave, still not working | Refrigeration | Refrigerators | 193.62 | Pass | Pass | 0 | 0 | 3.75 | 2022-05-24 11:30 | 2022-05-27 17:00 | 2022-05-27 10:00 | 2022-05-27 17:00 | 2022-05-27 13:45 |  |  | Attended site and completed pre start paperwork and signed in. Acessed restraunt kitchen and located under bench fridge. This fridge currently has parts on order. Will follow up. This work order can be closed.
MSA-DCA | WA5497211 | 0 | TK Elevator Australia Pty Ltd | Ground Floor - Lift 7 is stuck | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 3.75 | 2022-06-09 15:44 | 2022-06-09 17:44 | 2022-06-10 08:30 | 2022-06-09 19:44 | 2022-06-10 12:15 |  |  | Lift7 Greem Rm-Hydraulic :Lift out of order. Found run timet tripped, reset and checked relevant circuits, unable to reproduce fault, left in service.to be closed out at $0 cost
MSA-DTWD | WA5562775 | 2 | ECO PLUMBING AND GAS PTY LTD | E58 Large Scale Kitchen - P Trap not draining properly | Plumbing & Drainage | Drainage | 559.565 | Fail | Fail | 3 | 3 | 3.75 | 2022-06-20 09:43 | 2022-06-23 17:00 | 2022-07-12 11:15 | 2022-06-23 17:00 | 2022-07-12 15:00 |  |  | Replaced tundish for steam ovens
MSA-DTWD | WA5570332 | 2 | M Construction (WA) | Verandah Outside of Office - Wooden verandah steps require attention | Building | General Building | 453.06 | Pass | Pass | 0 | 0 | 3.75 | 2022-06-28 09:41 | 2022-07-01 17:00 | 2022-07-01 09:30 | 2022-07-01 17:00 | 2022-07-01 13:15 |  |  | Leveled of stairs with pavers. Concreted in stair threads, installed wider steps wing weatherproof fixings.
MSA-DTWD | WA5682745 | 3 | AWB Co. | 4 x lights out | Electrical | Lighting, Internal | 639.7975 | Pass | Pass | 0 | 0 | 3.75 | 2022-07-29 11:29 | 2022-08-05 17:00 | 2022-08-02 07:00 | 2022-08-05 17:00 | 2022-08-02 10:45 |  |  | Attended site and signed in. Completed JSA. Located lights not working as per lighting list. Supply and replace tubes and starters to light fittings. Supply and replaced ballasts to lights required. Tested all okay. Checked out laneway security lighting and found that all the lights except the flood light at the gate work on the override. Got site to check out the BMS to see if it has been switched off . All lights are okay. Signed out. Job complete
MSA-DCA | WA5861508 | 3 | FCT SURFACE CLEANING | Beaufort St side of buildings - Graffitti / Tagging on walls - See notes below | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 3.75 | 2022-09-13 09:43 | 2022-09-20 17:00 | 2022-09-15 10:00 | 2022-09-20 17:00 | 2022-09-15 13:45 |  |  | Removal of graffiti
MSA-DTWD | WA5887574 | 2 | Precise Air Group | Air con very stuffy | Air Conditioning | Room Air Conditioners | 354.73 | Pass | Pass | 0 | 0 | 3.75 | 2022-09-16 08:41 | 2022-09-21 17:00 | 2022-09-21 07:54 | 2022-09-21 17:00 | 2022-09-21 11:39 |  |  | was advised by Steve the facilities Manager that room A230 w as not working, found location and pulled out ceiling tile a nd checked VAV Aiflow had no air checked other rooms next to it none as well then went to locate plantroom on roof that AHU5 was and found that fan was not running ,checked switch board, then found VSD had gone out on high amp fault ,had to turn breaker off to reset VSD then had to go through all me nus to reprogram and get Running in Auto checked BMS and che cked operation all running efficiently again .
MSA-DCA | WA6001171 | 3 | Protek 24/7 Building & Maintenance | Above cleaners room-roof leak | Roofing | Metal Roofing | 651.67 | Pass | Pass | -1 | -1 | 3.75 | 2022-10-10 13:11 | 2022-10-17 17:00 | 2022-10-12 08:45 | 2022-10-17 17:00 | 2022-10-12 12:30 |  |  | Replace dektight
MSA-DTWD | WA6229735 | 1 | Lane's Plumbing | Gas Hot water system faulty | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 3.75 | 2022-11-18 10:29 | 2022-11-21 17:00 | 2022-11-18 14:45 | 2022-11-21 17:00 | 2022-11-18 18:30 |  |  | Completed
MSA-DTWD | WA6356925 | 3 | Protek 24/7 Building & Maintenance | AF1 door - Door getting stuck on raised concrete | Building | Doors | 933.57 | Pass | Pass | -1 | -1 | 3.75 | 2022-12-05 10:06 | 2022-12-12 17:00 | 2022-12-07 10:15 | 2022-12-12 17:00 | 2022-12-07 14:00 |  |  | Grind concrete to allow sufficient gap between concrete and bottom of door.
MSA-DTWD | WA6357316 | 2 | JEM Carpentry | Replace faulty tape on steps that has lifted through rain | Building | General Building |  | Fail | Fail | 0 | 0 | 3.75 | 2022-12-05 12:22 | 2022-12-08 17:00 | 2022-12-09 08:30 | 2022-12-08 17:00 | 2022-12-09 12:15 |  |  | Replaced tapes on steps
MSA-DCA | WA6364542 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Defence Gallery - Emergency Spitfire lights faulty | Electrical | General Electrical | 428.655 | Pass | Pass | 0 | 0 | 3.75 | 2022-12-12 12:35 | 2022-12-13 17:00 | 2022-12-13 13:15 | 2022-12-13 17:00 | 2022-12-13 17:00 |  |  | Arrived onsite at 13:15 to investigate emergency lights not working correctly located first floor near dome cinema. Found emergency lifhts had no power to fittings which was noticed visually by site staff when emergency lights started running off battery due to loss of power supply. Found where lights were controlled from and conducted thorough investigation and found 2 x contractors had slight issues which may have been causing emergency lighting issue. Upon returning from king on a switchboard found lights had came back on without action from myself. Lights now work and may suddenly stop working due to mysterious nature of fault. Lights working as of today and documented appropriately. Will monitor situation and take further action if required. Left site at 17:00
MSA-DCA | WA6376098 | 0 | Earth & Water Pty Ltd | zone 13-big screen and pretzel garden beds-retic is on app saying turned off | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 1 | 1 | 3.75 | 2022-12-15 12:46 | 2022-12-15 14:46 | 2022-12-21 06:45 | 2022-12-15 16:46 | 2022-12-21 10:30 |  |  | Completed
MSA-DTWD | WA6521294 | 3 | AWB Co. | GPO faulty ( tripping RCD ) | Electrical | General Electrical | 636.28 | Pass | Pass | -1 | -1 | 3.75 | 2023-01-30 09:46 | 2023-02-06 17:00 | 2023-01-31 10:00 | 2023-02-06 17:00 | 2023-01-31 13:45
MSA-DTWD | WA6538199 | 2 | AWB Co. | 3 lights out ladies toilet | Electrical | Lighting, Internal | 743.6675 | Pass | Pass | 0 | 0 | 3.75 | 2023-02-07 15:58 | 2023-02-10 17:00 | 2023-02-09 10:30 | 2023-02-10 17:00 | 2023-02-09 14:15
MSA-DTAG | WA6668639 | 3 | AWB Co. | Level 3 - Lift 9 - Emergancy light has failed | Electrical | General Electrical | 409.6675 | Pass | Pass | -1 | -1 | 3.75 | 2023-02-22 10:45 | 2023-03-01 17:00 | 2023-02-22 11:15 | 2023-03-01 17:00 | 2023-02-22 15:00
MSA-DTWD | WA6690331 | 1 | AHS Services WA Pty Ltd (Anchor) | Basin taps are not turning on | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 3.75 | 2023-03-09 08:56 | 2023-03-10 17:00 | 2023-03-10 06:59 | 2023-03-10 17:00 | 2023-03-10 10:44
MSA-DTWD | WA5584679 | 2 | AHS Services WA Pty Ltd (Anchor) | Ground-room B003 hot water is set too hot, ( burning hands when turned on to use ) | Plumbing & Drainage | Water | 662.7525 | Pass | Pass | 0 | 0 | 3.7333 | 2022-07-05 09:41 | 2022-07-08 17:00 | 2022-07-07 08:25 | 2022-07-08 17:00 | 2022-07-07 12:09 |  |  | Completed
MSA-DTWD | WA5188743 | 0 | Equans Mechanical Services Australia | External - Chiller - inground water leak from the chiller | Air Conditioning | Building HVAC Maintenance (Major Plant) | 245.93 | Pass | Fail | 0 | 0 | 3.6833 | 2022-02-23 11:12 | 2022-02-23 13:12 | 2022-02-23 12:35 | 2022-02-23 15:12 | 2022-02-23 16:16 |  |  | INVESTIGATED AND FOUND WATER LEAK NOT FROM CHILLER. ANOTHER COMPANY ATTENDEDAND CARRIED OUT REPAIRS.
MSA-DTWD | WA5715264 | 2 | BAKE-QUIP PTY LTD | SK 2 combi oven leaking constantly | Equipment | Catering Equipment | 909.9 | Pass | Pass | 0 | 0 | 3.6667 | 2022-08-12 12:41 | 2022-08-17 17:00 | 2022-08-15 07:30 | 2022-08-17 17:00 | 2022-08-15 11:10 |  |  | Refer to service report
MSA-DTWD | WA5481465 | 3 | AWB Co. | Level 1 - B127 - Workshop - Door closer has damaged external door | Building | Doors | 435.125 | Pass | Pass | -1 | -1 | 3.6667 | 2022-05-30 13:28 | 2022-06-07 17:00 | 2022-06-02 08:40 | 2022-06-07 17:00 | 2022-06-02 12:20 |  |  | Attended site 02/06Repairs to door with metal plates and bolts.Reinstall door closerCleaned area Job Complete
MSA-DTWD | WA6586252 | 3 | Precise Air Group | Replace aircon vent | Air Conditioning | Ducted Split System | 412.405 | Pass | Pass | 0 | 0 | 3.6667 | 2023-02-16 15:02 | 2023-02-23 17:00 | 2023-02-21 09:04 | 2023-02-23 17:00 | 2023-02-21 12:44
MSA-MRWA | WA5488168 | 3 | SONTEC WA PTY LTD | Front Gate - Front pedestrian gate not responding to exit button or reader - see notes below | Security | Access Control | 1042.68 | Pass | Pass | 0 | 0 | 3.65 | 2022-06-02 11:00 | 2022-06-10 17:00 | 2022-06-07 09:21 | 2022-06-10 17:00 | 2022-06-07 13:00 |  |  | 7/6/22 - Dean Simpson, Zach HarrowerReplaced faulty lock on pedestrian gate, and tested all ok.Gate 3 won't open with keypad.Relay and PCB only getting 4v. Could be faulty, also cable to gate from keypad not run in underground cable, which could cause an issue.
MSA-DCA | WA5675926 | 0 | Techworks Electrical | PICA Bar - Check Electrical Supply due to event | Electrical | General Electrical | 336.745 | Pass | Pass | 0 | 0 | 3.65 | 2022-07-22 16:21 | 2022-07-22 18:21 | 2022-07-22 16:30 | 2022-07-22 20:21 | 2022-07-22 20:09 |  |  | Attended site and checked over installation to fill out COP Form 5.
MSA-DFES | WA5832015 | 2 | Australian HVAC Services Pty. Ltd. | Level 2 - Payroll - Air conditoner in the payroll area is very hot | Air Conditioning | Room Air Conditioners | 407.39 | Pass | Pass | 0 | 0 | 3.6194 | 2022-09-05 10:19 | 2022-09-08 17:00 | 2022-09-06 07:22 | 2022-09-08 17:00 | 2022-09-06 10:59 |  |  | Attended site and signed in. Inspected payroll office and found vav 7.2.3 serving area operating correctly. Checked trendlogs and found previous Max room temp was 23.1. Checked operation of box in cooling and heating modes and found all ok. Monitored operation and found air volume increases as room temp increases correctly. No faults identified on system.
MSA-DFES | WA5770084 | 1 | Anvil Doors | Security Gate - Security auto gate not shutting correctly-Please attend Friday am | Security | Access Control | 516 | Pass | Pass | 0 | 0 | 3.6167 | 2022-08-18 16:19 | 2022-08-19 17:00 | 2022-08-19 11:17 | 2022-08-19 17:00 | 2022-08-19 14:54 |  |  | Checked Gate and found Limit Switch was loose. Limit Magnet has been secured and gate operational
MSA-DCA | WA6298288 | 0 | Precise Air Group | Follow Spot Room - aircon isnt working (not cooling) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 572.22 | Pass | Fail | 0 | 0 | 3.6167 | 2022-12-01 08:53 | 2022-12-01 10:53 | 2022-12-01 10:23 | 2022-12-01 12:53 | 2022-12-01 14:00 |  |  | Attended site and signed in. Accessed light control room and ran system, found no cooling present. Went up on the roof to check condenser unit and noticed compressor failing to start, de-energised the system and check compressor, found that the capacitor had failed and needed replacing. Left site to pick up new capacitor from supplier and returned to site. Proceeded to fit new capacitor, energise and run unit again. Found compressor working and system cooling. Unit is very aged, past life expectancy and runs on R22 refrigerant, recommend budgeting for replacement asap.
MSA-DCA | WA5614020 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire Panel Front Foyer - Zone 32 in pre alarm | Fire Protection Services | Fire Protection - Monitor System | 658.98 | Pass | Fail | 0 | 0 | 3.6 | 2022-07-14 21:34 | 2022-07-14 23:34 | 2022-07-14 22:24 | 2022-07-15 01:34 | 2022-07-15 02:00 |  |  | COMPLETED 15/07/2022SC-5668 PRIORITY 0 CALL OUT - 14/7/2022 AFTER HOURS LABOUR-14/7/2022 + 15/07/2022- 10:30PM - 2:00AM.-HOWARD SECURITY ONSITE BUT WOULD NOT SIGN SIGN SLIP TO CONFIRM ATTENDANCESENSOR REPAIR TO BE CONDUCTED ON A DIFFERENT WORK ORDER.
MSA-DCA | WA5491507 | 2 | TK Elevator Australia Pty Ltd | elevatior not working Level 1 green room lift 7 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 3.5833 | 2022-06-04 10:01 | 2022-06-09 17:00 | 2022-06-09 08:00 | 2022-06-09 17:00 | 2022-06-09 11:35 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped with STE1ap showing on main board. The lift was at Street level. Reset using maintenance control and lift resumed normal operation.Checked and cleaned encoder rope and encoder sheave groove. Checked inductors SO,SM,and SU and the plug connections to the APO14 board.Checked power supply voltage, 25.2vdc.Found right hand side hoistway door panels not closing fully with the closing spring. Adjusted tight door shoe so that the panel now closes with the door spring. Tested liftoperation without further fault, monitoring SO,SM and SU inductor operation. Returned the lift to serviceclosed out at $0 cost
MSA-DCA | WA5495795 | 1 | TK Elevator Australia Pty Ltd | Basement 2 - Lift 7 Currently not working at all - ongoing issue | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 3.5833 | 2022-06-08 15:14 | 2022-06-09 17:00 | 2022-06-09 08:00 | 2022-06-09 17:00 | 2022-06-09 11:35 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped with STE1ap showing on main board. The lift was at Street level. Reset using maintenance control and lift resumed normal operation.Checked and cleaned encoder rope and encoder sheave groove. Checked inductors SO,SM,and SU and the plug connections to the APO14 board.Checked power supply voltage, 25.2vdc.Found right hand side hoistway door panels not closing fully with the closing spring. Adjusted tight door shoe so that the panel now closes with the door spring. Tested liftoperation without further fault, monitoring SO,SM and SU inductor operation. Returned the lift to service.to be closed out at $0 cost
MSA-DCA | WA6666875 | 1 | GPS Plumbing & Gas Services PtyLtd | Spare Parts Puppet Theatre - Main area/Foyer toilets - Toilet servicing the main foyer area is block | Plumbing & Drainage | Toilets/Cisterns | 400.665 | Pass | Pass | 0 | 0 | 3.5167 | 2023-02-21 13:42 | 2023-02-22 17:00 | 2023-02-22 10:05 | 2023-02-22 17:00 | 2023-02-22 13:36
MSA-DTWD | WA5231344 | 1 | Equans Mechanical Services Australia | Ground and first - Air Conditioning staying in vent mode and not cooling. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 587.85 | Pass | Pass | 0 | 0 | 3.5167 | 2022-03-15 10:42 | 2022-03-16 17:00 | 2022-03-16 09:00 | 2022-03-16 17:00 | 2022-03-16 12:31 |  |  | Met Rory on site went through controls, icon logic completed works an completed reports. Cleaned up and completed paperwork.
MSA-DTWD | WA5570648 | 3 | Water2water Pty Ltd | 2-54 Library Kitchen - No hot water (cold water ok) | Plumbing & Drainage | HWS/Units Electric & Gas | 1294.705 | Pass | Pass | -1 | -1 | 3.5167 | 2022-06-28 13:26 | 2022-07-05 17:00 | 2022-06-30 13:00 | 2022-07-05 17:00 | 2022-06-30 16:31 |  |  | No hot water on arrival. Filter overdue x 7 fault. Changed filter. Didn’t fix the issue. Changed pump and level sensor and loom. Not heating up and coming up with filter change x XA. Replaced front pcb board and changed the element. Normal operation
MSA-DTWD | WA5091891 | 3 | AWB Co. | D Block - Ground - DG06 - Faulty GPO needs to be replaced | Electrical | General Electrical | 672.61 | Pass | Pass | 0 | 0 | 3.5 | 2022-01-27 12:04 | 2022-02-03 17:00 | 2022-02-01 07:15 | 2022-02-03 17:00 | 2022-02-01 10:45 |  |  | Attended site and signed in. Liaised with FM about works going ahead and got confirmation from technician on gpo. Repaired faulty in D Block. Also repaired faulty switch in E block. Notified of completed works. **job complete**
MSA-DTWD | WA5125672 | 0 | AHS Services WA Pty Ltd (Anchor) | North Metro TAFE-eCentral East Perth Campus- Front of Block A - Burst main from below the ground. | Plumbing & Drainage | Water | 1056.045 | Fail | Fail | 0 | 0 | 3.5 | 2022-02-13 15:39 | 2022-02-13 17:39 | 2022-02-14 06:30 | 2022-02-13 19:39 | 2022-02-14 10:00 |  |  | Burst pipe caused by roots pushing on pipe causing it to split. Cut out section of pipe and repair.
MSA-DCA | WA5186890 | 2 | Techworks Electrical | A&A Library Area - Light out requires replacement - see details below | Electrical | General Electrical | 318.47 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-22 09:51 | 2022-02-25 17:00 | 2022-02-23 06:30 | 2022-02-25 17:00 | 2022-02-23 10:00 |  |  | Replaced tubes and starters
MSA-DTWD | WA5187142 | 1 | Equans Mechanical Services Australia | Room F50 - Aircon is not working and the other blowing warm air | Air Conditioning | Room Air Conditioners | 329.65 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-22 11:35 | 2022-02-23 17:00 | 2022-02-23 08:00 | 2022-02-23 17:00 | 2022-02-23 11:30 |  |  | Found one ceiling cassette on auto , the other one was on cooling and once the temperature gets down the first one switches to heating. Set both on cooling and test ran all OK.
MSA-DCA | WA5187795 | 3 | FCT SURFACE CLEANING | Various Locations - Graffiti - see notes below | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 3.5 | 2022-02-22 14:41 | 2022-03-01 17:00 | 2022-02-25 11:00 | 2022-03-01 17:00 | 2022-02-25 14:30 |  |  | Removed various pieces of graffiti from site.
MSA-DCA | WA5216737 | 2 | Techworks Electrical | Exterior wall (closest to Prezel) - light is missing cover & transformer is not covered | Electrical | General Electrical | 914.58 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-11 12:24 | 2022-03-16 17:00 | 2022-03-16 06:30 | 2022-03-16 17:00 | 2022-03-16 10:00 |  | WACCES | Looked into light missing the cover and exposing the transformer. Requires new light as you are unable to replace the light cover itself. Supplied and Replaced led flood light for new - PCC scissor lift used
MSA-DTAG | WA5296673 | 3 | Automatic Fire Protection (ARA) | 1987 - Level 4 - Plantroom - see details below | Fire Protection Services | Fire Protection - Monitor System | 292.88 | Pass | Pass | -1 | -1 | 3.5 | 2022-03-30 14:28 | 2022-04-06 17:00 | 2022-04-02 08:00 | 2022-04-06 17:00 | 2022-04-02 11:30 |  |  | Attended site and preformed isolation for mechanical contractor on Sub Panel and Main panel for 8 am.Contractor finished work at 11am. Reinstated all isolated zones and returned both panels back to normal operating state.
MSA-DTWD | WA5407054 | 2 | M Construction (WA) | D-Block - Canteen store room - replace 6 broken floor tiles | Flooring | Tiling | 811.4 | Pass | Pass | -1 | -1 | 3.5 | 2022-05-11 09:10 | 2022-05-16 17:00 | 2022-05-12 08:00 | 2022-05-16 17:00 | 2022-05-12 11:30 |  |  | Inspected reported damage, sourced materials and repaired tiles as required.
MSA-DTWD | WA5407236 | 2 | ECO PLUMBING AND GAS PTY LTD | Leaking kitchen sink tap and basin leaking underneath | Plumbing & Drainage | Water | 544.09 | Fail | Fail | 5 | 5 | 3.5 | 2022-05-11 10:38 | 2022-05-16 17:00 | 2022-06-17 09:30 | 2022-05-16 17:00 | 2022-06-17 13:00 |  |  | Replaced leaking taps with mixer and leaking trap
MSA-DTWD | WA5460358 | 2 | AWB Co. | Hot water system isnt working | Electrical | General Electrical | 728.865 | Pass | Pass | -1 | -1 | 3.5 | 2022-05-18 13:14 | 2022-05-23 17:00 | 2022-05-19 08:45 | 2022-05-23 17:00 | 2022-05-19 12:15 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located HWS not working. Tested system and element, found to be that it had a faulty thermostat and element. Also noticed that the isolator was cracked and not safe. Left site to get parts required. Returned to site. Installed all new components. Tested to make sure operating correctly. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5496761 | 2 | Precise Air Group | M007 - North Class Rooms AC not running Affecting M4,5,6,& 7 | Air Conditioning | Room Air Conditioners | 574.92 | Pass | Pass | -1 | -1 | 3.5 | 2022-06-09 12:25 | 2022-06-14 17:00 | 2022-06-10 08:00 | 2022-06-14 17:00 | 2022-06-10 11:30 |  |  | Carried out service call in M Block APAC condensing unitno 2 traced all wiring back and tested found controllockout relay to have failed replaced it with another one got unit running and checked classrooms that it was servicing duct heaters had come on with unit at was operating at around 24c AC operating efficiently
MSA-DTAG | WA5565201 | 0 | Total Security Systems Pty Ltd | Security Staff Door - Secure swipe card door - door is not clicking closed after staff have used it | Security | Access Control | 595 | Fail | Fail | 0 | 0 | 3.5 | 2022-06-21 14:43 | 2022-06-21 16:43 | 2022-06-22 14:00 | 2022-06-21 18:43 | 2022-06-22 17:30 |  |  | 21/6/2022 - Jose Pereira travel to site 2pm to 3.30pmtime on site 3.30pm to 4pmtravel from site 4pm to 5.30pmNo issues with the access control, adjusted the door closer to close the door properly .
MSA-DTAG | WA5571130 | 1 | Total Security Systems Pty Ltd | Control room - Monitor has flickering screen - cant see cctv | Security | Monitoring | 595 | Pass | Fail | 0 | 0 | 3.5 | 2022-06-29 09:00 | 2022-06-30 17:00 | 2022-06-30 14:00 | 2022-06-30 17:00 | 2022-06-30 17:30 |  |  | 30/6/2022 - Jose Pereira travel to site 2pm to 3.30pmtime on site 3.30pm to 4pmtravel from site 4pm to 5.30pmInvestigated the issues and found that the graphics card port is failing have moved it to another port which has resolved the issue.
MSA-DTWD | WA5572335 | 1 | Falcetta Plumbing and Gas | Blockage in toilet resulting in it coming up via floor drain in storage room | Plumbing & Drainage | Drainage | 749.105 | Pass | Pass | 0 | 0 | 3.5 | 2022-06-29 17:21 | 2022-06-30 17:00 | 2022-06-30 08:00 | 2022-06-30 17:00 | 2022-06-30 11:30 |  |  | attempt to plunge toilet, drainsflush clear blockage.
MSA-DTWD | WA5608621 | 2 | BAKE-QUIP PTY LTD | Dishwasher has no water flow to machine | Equipment | Cleaning Equipment | 756.3 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-13 10:23 | 2022-07-18 17:00 | 2022-07-15 12:50 | 2022-07-18 17:00 | 2022-07-15 16:20 |  |  | Refer to service report
MSA-DTWD | WA5611890 | 2 | AWB Co. | Southern Corner of C Block - 2 Severe Gutter Leaks | Roofing | Guttering | 700.15 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-14 10:17 | 2022-07-19 17:00 | 2022-07-19 09:30 | 2022-07-19 17:00 | 2022-07-19 13:00 |  |  | Accessed roof of block C to find blocked sumps in box gutter cleared all blockages in box gutter flushed out downpipes of any blockages. Resealed all gutter joins to make watertight cleaned and packed up site. Job complete
MSA-DTWD | WA5680362 | 2 | BAKE-QUIP PTY LTD | D1 Bakery Kitchen-Rotel 2 Oven needs a new spring on the bottom door | Electrical | General Electrical | 636.7 | Pass | Pass | -1 | -1 | 3.5 | 2022-07-27 11:42 | 2022-08-01 17:00 | 2022-07-27 11:45 | 2022-08-01 17:00 | 2022-07-27 15:15 |  |  | Refer to service report
MSA-DTWD | WA5699390 | 3 | AWB Co. | distribution board - faulty breaker | Electrical | General Electrical | 535.915 | Pass | Pass | -1 | -1 | 3.5 | 2022-08-10 09:01 | 2022-08-17 17:00 | 2022-08-10 11:00 | 2022-08-17 17:00 | 2022-08-10 14:30 |  |  | Attended site signed in jsa completed. found mainswitch off. Investigated and found emergency stop was faulty. Disconnected all stops and found two which were broken. Replaced with two new and tested and operational.Job completed
MSA-DTWD | WA5753031 | 1 | COMMERCIAL PLUMBING AND GAS | U block near Dixon Rd - Stormwater pump control box alarm sounding with high level notification | Plumbing & Drainage | Water | 499.855 | Pass | Pass | 0 | 0 | 3.5 | 2022-08-17 13:21 | 2022-08-18 17:00 | 2022-08-17 17:00 | 2022-08-18 17:00 | 2022-08-17 20:30 |  |  | reset floats to correct position in 2x sumps
MSA-DTAG | WA5791839 | 2 | Water2water Pty Ltd | Staff Kitchen - Level 13 - Boiling water unit is not operational | Plumbing & Drainage | HWS/Units Electric & Gas | 984.94 | Pass | Pass | 0 | 0 | 3.5 | 2022-08-23 09:54 | 2022-08-26 17:00 | 2022-08-23 09:55 | 2022-08-26 17:00 | 2022-08-23 13:25 |  |  | No hot water on arrival. Replaced element and all 3 solenoids. Also removed plv. Drained tank and cleaned out tank and de scaled tank. The gpo has blown at the main board. Used extension cord to fire up unit and checked under pressure. Replaced John guest fitting and tube. Normal operation
MSA-DFES | WA5978027 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Parade ground - near BAT building - water leaks when the hydrant is in use - see notes below | Plumbing & Drainage | Water | 476.75 | Pass | Pass | 0 | 0 | 3.5 | 2022-09-28 08:28 | 2022-09-29 17:00 | 2022-09-28 11:00 | 2022-09-29 17:00 | 2022-09-28 14:30 |  |  | Attended site for fire hydrant leaking when water is turned on and causing water to build up and overflow out of the ground near bat building upon inspection I have found the valve box that was installed with the hydrant last year was never sealed so when it holds water because it cannot be made watertight when in use it causes water to flow out from underneath the valve box and come up ground around causing the sand to disperse and is causing the bitumen to sink it has been like this since it was replaced early this year and has continued to get worse the site is contacting Programmed and the original installers to come out and fix the bitumen that has been affected I have put a waterproof membrane on the inside of the valve box around the bottom of the box the sides of the box and the top of the box but leaving a small section at the lowest point as the drain away so it does not continuously hold water all the time I have confirmed everything with site and they are happy with what ha
MSA-DTWD | WA6077537 | 1 | BAKE-QUIP PTY LTD | The dishwasher element is broken and has tripped out | Equipment | Cleaning Equipment | 570.3 | Pass | Pass | 0 | 0 | 3.5 | 2022-10-18 11:37 | 2022-10-19 17:00 | 2022-10-19 08:00 | 2022-10-19 17:00 | 2022-10-19 11:30 |  |  | Refer to service report
MSA-DTAG | WA6128228 | 3 | Seme Solutions Pty Ltd | Camera issues - Camera 46 needs an IP Upgrade | Security | CCTV Surveillance | 1197.83 | Fail | Fail | 1 | 1 | 3.5 | 2022-10-26 13:30 | 2022-11-02 17:00 | 2022-11-07 08:45 | 2022-11-02 17:00 | 2022-11-07 12:15 |  |  | Cabled and installed new IP camera behind custody bench as per BRAF. Confirmed online and recording.Install interrupted due to inmate movements.
MSA-DTWD | WA6129333 | 3 | AWB Co. | E Block light fabrication W/Shop North facing gutter - roof leaking in 3 spots | Roofing | Guttering | 731.7 | Pass | Pass | 0 | 0 | 3.5 | 2022-10-27 13:51 | 2022-11-03 17:00 | 2022-11-03 08:00 | 2022-11-03 17:00 | 2022-11-03 11:30 |  |  | Works completed
MSA-DTWD | WA6149089 | 2 | AWB Co. | E50 Bentley Bistro Entrance - External wall mount light fitting is full of water | Electrical | General Electrical | 434.98 | Pass | Pass | 0 | 0 | 3.5 | 2022-11-04 11:59 | 2022-11-09 17:00 | 2022-11-09 08:00 | 2022-11-09 17:00 | 2022-11-09 11:30 |  |  | Attended site signed in jsa completed. Found light full of water, isolated removed founf conduit not sealed properly. Siliconed up tight. Installed light and checked operation.Job completed
MSA-DTWD | WA6253597 | 3 | Protek 24/7 Building & Maintenance | Roof Gutters need to be cleaned out | Roofing | Guttering | 591.94 | Pass | Pass | 0 | 0 | 3.5 | 2022-11-22 10:49 | 2022-11-29 17:00 | 2022-11-28 08:45 | 2022-11-29 17:00 | 2022-11-28 12:15 |  |  | Cleaned gutters
MSA-DTWD | WA6256905 | 2 | AWB Co. | B Block - Ground Floor - Store Room - Shelving to be re secured to the wall | Building | General Building | 387.145 | Pass | Pass | 0 | 0 | 3.5 | 2022-11-24 10:01 | 2022-11-29 17:00 | 2022-11-28 10:15 | 2022-11-29 17:00 | 2022-11-28 13:45 |  |  | Inspected shelving 3 shelving units to be fixed to the wallshelves require spacers to allow the towers to sit in the shelves.Cut timber to sit behind the shelf to match thickness of the architravesRemoved backing plate to allow towers to sit evenly on shelves Job Complete
MSA-DTWD | WA6362631 | 1 | Milners Tree Solutions Pty Ltd | Campus Grounds - Overhanging branches to neighboring residential property – high rick of injury | Landscaping & Gardening | Grounds Maintenance | 2000 | Pass | Pass | 0 | 0 | 3.5 | 2022-12-09 11:38 | 2022-12-12 17:00 | 2022-12-12 06:30 | 2022-12-12 17:00 | 2022-12-12 10:00 |  |  | Tree limbs extending into neighboring property......pruned right back... neighbor spoken with... very happy
MSA-DTWD | WA6405445 | 2 | AWB Co. | G11/14 - Light circuit keeps tripping - see notes below | Electrical | General Electrical | 319.79 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-09 13:55 | 2023-01-12 17:00 | 2023-01-11 11:00 | 2023-01-12 17:00 | 2023-01-11 14:30
MSA-DTWD | WA6407501 | 2 | M Construction (WA) | C208 remove broken wall mounted TV and bracket from wall | Building | General Building | 774.72 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-10 09:20 | 2023-01-13 17:00 | 2023-01-13 06:30 | 2023-01-13 17:00 | 2023-01-13 10:00
MSA-DTWD | WA6407587 | 1 | M Construction (WA) | J004 East Wall - cladding detached off outside of east wall | Building | External Walls | 785.73 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-10 10:03 | 2023-01-11 17:00 | 2023-01-10 11:00 | 2023-01-11 17:00 | 2023-01-10 14:30
MSA-DTWD | WA6407996 | 2 | AWB Co. | Level 2 - Cafeteria - 3 X lights out in Cafeteria | Electrical | Lighting, Internal | 883.62 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-10 13:34 | 2023-01-13 17:00 | 2023-01-13 09:30 | 2023-01-13 17:00 | 2023-01-13 13:00
MSA-DTWD | WA6503823 | 1 | Precise Air Group | Cool Room 6 - E12 above 10 Degrees, not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 2596.875 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-19 11:39 | 2023-01-20 17:00 | 2023-01-19 12:30 | 2023-01-20 17:00 | 2023-01-19 16:00
MSA-DCA | WA6517101 | 0 | EQUANS Mechanical Services (WA) Pty Limited | All locations - Security system not arming | Security | Monitoring | 849.41 | Pass | Fail | 0 | 0 | 3.5 | 2023-01-24 07:41 | 2023-01-24 09:41 | 2023-01-24 09:30 | 2023-01-24 11:41 | 2023-01-24 13:00
MSA-DTWD | WA6522031 | 1 | Australian Airconditioning Services Pty Ltd | Old Unit (South End of Kitchen) - Braemer Evaporative AC Unit Not Working – See notes | Air Conditioning | Package | 591.92 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-30 16:40 | 2023-01-31 17:00 | 2023-01-31 08:00 | 2023-01-31 17:00 | 2023-01-31 11:30
MSA-DTWD | WA6523303 | 2 | AWB Co. | Door soft-closer is not working and is making a very loud bang when it closes | Building | Doors | 640.715 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-31 14:16 | 2023-02-03 17:00 | 2023-02-03 10:15 | 2023-02-03 17:00 | 2023-02-03 13:45
MSA-DTAG | WA6534402 | 0 | Sapio Pty Ltd | Control room - Doors not opening or closing - system fault see notes | Security | Security Management System | 193.68 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-06 12:12 | 2023-02-06 14:12 | 2023-02-06 12:30 | 2023-02-06 16:12 | 2023-02-06 16:00
MSA-DTAG | WA6650839 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Plant Room 1 - Water leaking behind plant room one near Buss P chambers (room MCC1) | Air Conditioning | Evaporative Coolers | 407.39 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-20 13:25 | 2023-02-21 17:00 | 2023-02-21 12:30 | 2023-02-21 17:00 | 2023-02-21 16:00
MSA-DTWD | WA6693294 | 3 | AWB Co. | Ground - Car park lights - Arent turning on | Electrical | Lighting, External | 597.24 | Pass | Pass | -1 | -1 | 3.5 | 2023-03-10 08:51 | 2023-03-17 17:00 | 2023-03-13 06:30 | 2023-03-17 17:00 | 2023-03-13 10:00
MSA-DFES | WA5068691 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Female changerooms (not toilets) - sensor for lights is not working - see details | Electrical | General Electrical | 516.47 | Pass | Pass | 0 | 0 | 3.5 | 2022-01-19 12:14 | 2022-01-27 17:00 | 2022-01-27 07:00 | 2022-01-27 17:00 | 2022-01-27 10:30 |  |  | Arrived on site at 7am. Called Daniel the site contact to give me access. I got access at 730 am. Located faulty motion sensor. The sensor was faulty. There is a wholesaler next to the fire station I got a new sensor from there but after I installed the new sensor it still wasn’t working. The sensor was slightly different to the once’s we normally use. Returned sensor to the wholesaler. Left site to get a different sensor from a different wholesaler. Installed the new sensor and it is now working correctly.
MSA-DTWD | WA5090845 | 1 | WESTERN IRRIGATION PTY LTD | low pressure on the water bore block U and V | Building | Materials | 576.62 | Pass | Pass | 0 | 0 | 3.5 | 2022-01-26 10:52 | 2022-01-27 17:00 | 2022-01-27 09:00 | 2022-01-27 17:00 | 2022-01-27 12:30 |  |  | Investigate low pressure fault, locate faulty solenoid valve and repair. Retested irrigation system for correct operation.
MSA-DTWD | WA5098648 | 1 | AWB Co. | J Block - J100 - Pedestrian Door dropped slightly and unable to lock | Building | General Building | 399.75 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-01 10:25 | 2022-02-02 17:00 | 2022-02-02 11:30 | 2022-02-02 17:00 | 2022-02-02 15:00 |  |  | Works carried out as required to ease sticking door , secure doorframe and supply + install striker plate.
MSA-DTWD | WA5100602 | 3 | Equans Mechanical Services Australia | Level 1 - 108 - low air flow - see details below | Air Conditioning | Room Air Conditioners | 329.65 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-02 15:30 | 2022-02-09 17:00 | 2022-02-09 13:00 | 2022-02-09 17:00 | 2022-02-09 16:30 |  |  | DAMPER NOT OPERATING MANUALLY, PARTS WILL NEED TO BE ORDERED
MSA-DTWD | WA5108394 | 3 | WESTERN IRRIGATION PTY LTD | Black Water Reed Bed Planter retic has ceased working | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 3.5 | 2022-02-08 13:36 | 2022-02-15 17:00 | 2022-02-14 12:00 | 2022-02-15 17:00 | 2022-02-14 15:30 |  | WCAPPR | Attend site to investigate faulty, waiting on technical information to assist in diagnosing the faulty. Steve onsite will advise once he has the information. Chased up Steve Meyer for technician drawing on several occasions with no response.Eric Reedman liaise with site on the 23 August 2023 and was advised that they a evaluating whether to keep or abandon the system and to close off the job.
MSA-DTAG | WA5116252 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Registry - Aircon isn’t working/not on | Air Conditioning | Room Air Conditioners | 737.04 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-11 12:43 | 2022-02-14 17:00 | 2022-02-11 12:45 | 2022-02-14 17:00 | 2022-02-11 16:15 |  |  | Fixed condenser fan issue
MSA-DTWD | WA5127270 | 1 | Precise Air Group | Kendrew- A-Block - A006 - burning smell from FCU unit | Air Conditioning | Room Air Conditioners | 430.005 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-14 12:15 | 2022-02-15 17:00 | 2022-02-15 07:30 | 2022-02-15 17:00 | 2022-02-15 11:00 |  |  | Attended site and completed pre start paperwork andsigned in. Accessed room 006 and inspected fcu. Could notsmell burning at the time of inspection and nothingobvious in ceiling/fcu. Found filters due forreplacement. Organised p.o. and picked up filters fromsupplier. Collected filters and returned to site. Foundsystem running all ok. Replaced filters and left systemoperating. Fm to monitor.
MSA-DCA | WA5142569 | 1 | Techworks Electrical | Green Room - 2 x ceiling fluro lights are not working, EEL above vending machine not working | Electrical | General Electrical | 717.35 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-16 15:28 | 2022-02-17 17:00 | 2022-02-17 07:30 | 2022-02-17 17:00 | 2022-02-17 11:00 |  |  | began fault finding and found the lights were not connected to the rest of the circuit, Ken had informed us that the lights have not been working for some time so it’s unclear why they were disconnected from the circuit.connected them back into R1 and found all lights to be working. Found the switch mech to be nearing the end of its life so we replaced it too.
MSA-DTWD | WA5190061 | 2 | AWB Co. | B1 Lighting circuit repeatedly tripping | Electrical | Lighting, Internal | 455.25 | Pass | Pass | 0 | 0 | 3.5 | 2022-02-24 10:28 | 2022-03-01 17:00 | 2022-02-28 08:30 | 2022-03-01 17:00 | 2022-02-28 12:00 |  |  | Atteded site signed in completed jsa. Spoke with mike about the job in the area. Found two light fittings not working and burnt inside lamps. Replaced one lamp, replaced one light fitting and tested for operation. Site will monitor light circuit and be in touch if problem is resolved as rcd was not tripping when i was on site.***job completed***
MSA-DCA | WA5201293 | 2 | Protek 24/7 Building & Maintenance | Jubilee - Level 1 - Reflections Gallery - see notes below | Building | Doors | 336.99 | Pass | Pass | -1 | -1 | 3.5 | 2022-03-02 13:16 | 2022-03-08 17:00 | 2022-03-04 07:30 | 2022-03-08 17:00 | 2022-03-04 11:00 |  |  | Repair gallery fire door
MSA-DTWD | WA5208538 | 1 | AWB Co. | Car Park lighting - Ground - Circuit red 3 and white 7 - Circuits tripping causing lights to go off | Electrical | General Electrical | 545.96 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-09 09:20 | 2022-03-10 17:00 | 2022-03-10 09:00 | 2022-03-10 17:00 | 2022-03-10 12:30 |  |  | Attended site and signed in. Completed JSA. Located main switchboard. Turned on all lighting controls. All lights are staying on. Isolated and tested the circuits reported tripping. All okay and above minimum. Turned off the control and found lights to trip. Rewired controls to switch double pole on both circuits and tested the current on the circuit when turning off. Found to be having a spike on shut off. Switching both poles has stopped this. RCD tested the RCDs function and found both to be tripping at 16ma. Supply and replaced with new rcbo breakers to both circuits. Retested and all okay no faults found. Reinstated power to lights. Signed out. Job complete
MSA-DTWD | WA5215259 | 2 | Techworks Electrical | Kendrew- D-Block 2nd Floor change all blown lights on floor including plant room | Electrical | General Electrical | 1310.85 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-10 10:46 | 2022-03-15 17:00 | 2022-03-15 09:00 | 2022-03-15 17:00 | 2022-03-15 12:30 |  |  | Replaced light tubes starters holders and down lights in D block level 2 and plant room
MSA-DTWD | WA5217073 | 1 | Equans Mechanical Services Australia | Exhaust fans not working | Air Conditioning | Materials | 758.7 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-11 16:03 | 2022-03-14 17:00 | 2022-03-14 10:00 | 2022-03-14 17:00 | 2022-03-14 13:30 |  |  | Found one v belt broken and second one split. Also found both motor pulleys are worn. Replaced 2 x pulleys and both v belts. Left spares in unit. Checked operation and all ok.
MSA-DTWD | WA5217074 | 3 | AWB Co. | Passage - Light fitting broken | Electrical | Lighting, Internal | 624.72 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-11 15:56 | 2022-03-18 17:00 | 2022-03-15 07:30 | 2022-03-18 17:00 | 2022-03-15 11:00 |  |  | Attended site and signed in. Completed JSA. Located block 2 faulty light fitting. Found to be all brittle and not repairable. Advised site to replace with new led fitting. Picked up new light and spares for site. Supply and replaced with new led surface mount panel lighting. Tested all okay. Left spares with site. Signed out. Job complete
MSA-DTWD | WA5270552 | 2 | AWB Co. | U024.3 - water leaking on roof | Building | General Building | 667.5 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-18 08:41 | 2022-03-23 17:00 | 2022-03-23 07:00 | 2022-03-23 17:00 | 2022-03-23 10:30 |  |  | Attended site with Noel, complete JSA and signed into the campus. Harnes up and began sealing up holes and broken down silicone. Completed PFM signature slip. Job completed
MSA-DTWD | WA5288808 | 2 | Lane's Plumbing | BLD 822 - Flat C - Cracked toilet bowl | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 3.5 | 2022-03-23 13:45 | 2022-03-28 17:00 | 2022-03-28 13:00 | 2022-03-28 17:00 | 2022-03-28 16:30 |  |  | REPLACE CRACKED TOILET BOWL AND CISTERN BLD 822 FLAT C
MSA-DTWD | WA5288899 | 1 | Equans Mechanical Services Australia | First floor - staff office - A/C not working. Showing 06 error code | Air Conditioning | Room Air Conditioners | 329.65 | Pass | Pass | 0 | 0 | 3.5 | 2022-03-23 15:17 | 2022-03-24 17:00 | 2022-03-24 10:00 | 2022-03-24 17:00 | 2022-03-24 13:30 |  |  | INVERTER FAULT, ATTEMPTED TO ACCESS CONDENSING UNIT - ROOF TOO HIGH - WILL REQUIRE REATTENDANCE
MSA-DTWD | WA5294094 | 3 | AWB Co. | Central Courtyard - Paving repair to collapsed soak well C Block | Paving & Roadworks | Paving | 369.5 | Pass | Pass | -1 | -1 | 3.5 | 2022-03-28 12:53 | 2022-04-04 17:00 | 2022-03-29 12:00 | 2022-04-04 17:00 | 2022-03-29 15:30 |  |  | Repaired sunken paving
MSA-MRWA | WA5295217 | 3 | AWB Co. | Server room/comms room - UPS power issue | Electrical | General Electrical | 419.91 | Pass | Pass | -1 | -1 | 3.5 | 2022-03-29 11:51 | 2022-04-05 17:00 | 2022-03-31 06:00 | 2022-04-05 17:00 | 2022-03-31 09:30 |  |  | Attended site and signed in, completed jsa,spoke with fm and site manager about ups issue, switched UPS to charge mode from bypass and had amp meter set up at board on circuit, monitored load on circuit until it tripped , circuit only had a max of 5 amps load before it tripped , removed cable from ups and I.r tested it , results came back 200M ohm on both a-e and n-e , plugged UPS in and re did test, got a failed reading of 0.04M ohm on both a-e and n-e . This could be a false reading as there are circuit boards in ups . Did polarity test on gpo and it passed , tested other GPOs in area to see if they were on separate circuits . 15a gpo seems tone on its own circuit and when it was isolated all other GPOs had voltage , went to wholesaler and picked up 2x plug tops to make up an adaptor lead . Plugged adaptor lead into ups plug and then ran an extension lead to another circuit to see if it would trip, circuit also tripped , packed up leads and plugged in ups putting it back into bypass
MSA-DFES | WA5305422 | 2 | Seme Solutions Pty Ltd | CCTV Camera C8 not working | Security | CCTV Surveillance | 455 | Pass | Pass | 0 | 0 | 3.5 | 2022-04-05 16:01 | 2022-04-08 17:00 | 2022-04-07 07:00 | 2022-04-08 17:00 | 2022-04-07 10:30 |  |  | Camera fully restored.
MSA-DCA | WA5312634 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main gallery RO plant water pressure - value 105.335 and Level 4 Flexible Gallery AHU05 West hu | Air Conditioning | Room Air Conditioners | 583.455 | Pass | Fail | 0 | 0 | 3.5 | 2022-04-11 22:46 | 2022-04-12 00:46 | 2022-04-11 23:30 | 2022-04-12 02:46 | 2022-04-12 03:00 |  |  | Attended callout. Investigated fault on RO plant and humidifier faults on AHU 5. Found flow control on pump had failed causing a low pressure fault to occur. Reset RO plant and tested operation. Checked pre filters and bled air from system, all ok. System is running and alarms cleared. Reset faults on humidifiers 5.1 and 5.2, all ok Fault appeared on humidifier 7, water level low due to RO plant failing. Confirmed water was being fed from RO plant, fault will clear once tank is full. Issues with programmed ah assigning to promaps, completed paperwork.
MSA-DCA | WA5335931 | 0 | EQUANS Mechanical Services (WA) Pty Limited | AC alarm P0 RO plant low water pressure | Air Conditioning | Materials | 583.455 | Pass | Pass | 0 | 0 | 3.5 | 2022-04-16 09:43 | 2022-04-16 11:43 | 2022-04-16 10:00 | 2022-04-16 13:43 | 2022-04-16 13:30 |  |  | Attended callout. Checked over bms to assess fault. RO plant indicating low water limit and alarm for high water limit is still active. Contacted Schneider technician to help resolve issues remotely. Calibrated high water level sensor. Opened bypass to quick fill tanks and clear low-level faults. High water level fault cleared. RO plant operational and faults had cleared. Completed paperwork.
MSA-DTWD | WA5412926 | 2 | Protek 24/7 Building & Maintenance | Roof leak - contractor currently onsite | Roofing | Metal Roofing | 953.5 | Pass | Pass | -1 | -1 | 3.5 | 2022-05-12 07:46 | 2022-05-16 17:00 | 2022-05-12 10:00 | 2022-05-16 17:00 | 2022-05-12 13:30 |  |  | Attend roof leak - Braf Declined
MSA-DTWD | WA5438454 | 2 | JEM Carpentry | House 5 - Faulty outside clothes line | Equipment | Building Equipment |  | Fail | Fail | 0 | 0 | 3.5 | 2022-05-16 14:26 | 2022-05-19 17:00 | 2022-05-20 12:00 | 2022-05-19 17:00 | 2022-05-20 15:30 |  |  | Repairs to cloths line
MSA-DTWD | WA5460184 | 2 | PEEL LOCK SERVICES PTY LTD | Room A24 - Broken internal door handle to entry door | Security | Locksmith |  | Pass | Pass | -1 | -1 | 3.5 | 2022-05-18 11:48 | 2022-05-23 17:00 | 2022-05-18 15:15 | 2022-05-23 17:00 | 2022-05-18 18:45 |  |  | Repairs to door
MSA-DTWD | WA5468691 | 1 | JEM Carpentry | House 804 - Laundry - Faulty Roof Tiles | Roofing | Tiled Roofing |  | Pass | Pass | 0 | 0 | 3.5 | 2022-05-20 11:46 | 2022-05-23 17:00 | 2022-05-20 12:00 | 2022-05-23 17:00 | 2022-05-20 15:30 |  |  | Repairs to roof tiles
MSA-DTAG | WA5472163 | 3 | Gilmour & Jooste Electrical | Reduce the brightness of the lighting in the back office | Electrical | Lighting, Internal | 623.345 | Fail | Fail | 0 | 0 | 3.5 | 2022-05-23 14:57 | 2022-05-30 17:00 | 2022-05-31 06:00 | 2022-05-30 17:00 | 2022-05-31 09:30 |  |  | Attempted to dim office lights however lights are not dimmable.Replaced multiple blown tubes to sally port and custody.
MSA-DTAG | WA5493965 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - Plant room - BMS system has failed | Air Conditioning | Building HVAC Maintenance (Major Plant) | 428.31 | Pass | Pass | -1 | -1 | 3.5 | 2022-06-07 11:38 | 2022-06-14 17:00 | 2022-06-07 12:00 | 2022-06-14 17:00 | 2022-06-07 15:30 |  |  | Pick up spare extension lead from office. Attend site and find nearest GPO. Run lead over pipework to office window. Connect lead to BMS power board and check operation of BMS. Found to start up and work as normal.
MSA-DTWD | WA5563989 | 3 | AWB Co. | D30 - Replace faulty bench lights | Electrical | General Electrical | 695.96 | Pass | Pass | 0 | 0 | 3.5 | 2022-06-21 07:29 | 2022-06-27 17:00 | 2022-06-27 08:30 | 2022-06-27 17:00 | 2022-06-27 12:00 |  |  | Attended site signed in JSAcompleted. Installed five new LED batterns as old lights non repairable. job completed
MSA-DCA | WA5566126 | 1 | Critical Fire Protection & Training | Disabled Fire detector - See notes below | Fire Protection Services | Fire Protection - Monitor System | 771.41 | Pass | Pass | 0 | 0 | 3.5 | 2022-06-22 15:30 | 2022-06-23 17:00 | 2022-06-23 13:20 | 2022-06-23 17:00 | 2022-06-23 16:50 |  |  | Start time: 1:20pmFinish time: 4:50pmInvestigated false alarm activation of duct probe loop 4 device 40.On arrival duct probe still indicating active alarm. Physically investigated duct probe detector enclosure and found no significant moisture or dust ingress. Replacing entire duct probe required. Device left isolated until replacement can be conducted.Replacement duct probe. Replaced entire duct probe including new sample piping with holes closest to A/C duct wall sealed to assist in eliminating false alarm activations. Advised Reese Programmed on site and Ben Hoper that the system be cleaned and filter replacement dates checked.System left with Loop 4/ device 40 duct probe isolated due to potential clean out of A/C duct work.
MSA-DTWD | WA5568050 | 3 | AWB Co. | N107 - weak 24/7 security light tube | Electrical | General Electrical | 899.21 | Pass | Pass | 0 | 0 | 3.5 | 2022-06-24 14:57 | 2022-07-01 17:00 | 2022-06-28 09:00 | 2022-07-01 17:00 | 2022-06-28 12:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm and got lighting list. Counted up lights and figured out where they all were. Went to wholesaler and got parts. Returned to site and worked through list until all were complete. Light fittings all working as intended. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DFES | WA5586841 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Training Room - Downlights Fault, Flickering | Electrical | Lighting, Internal | 475.17 | Pass | Pass | -1 | -1 | 3.5 | 2022-07-06 15:31 | 2022-07-11 17:00 | 2022-07-07 13:00 | 2022-07-11 17:00 | 2022-07-07 16:30 |  |  | Arrived onsite at 13:00 to investigate lights flickering located training room. Found lights were flickering due to faulty globes and drivers. Collected parts from nearest wholesaler and returned to site to install new LED downlights. Installed and tested new lights and informed site of works completed. Left site at 16:30
MSA-DTAG | WA5588270 | 1 | Sapio Pty Ltd | Ground - Registry - Staff back door - Door wont unlock with the swipe cards - See notes below | Security | Access Control | 718.03 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-07 14:05 | 2022-07-08 17:00 | 2022-07-08 09:00 | 2022-07-08 17:00 | 2022-07-08 12:30 |  |  | Attended site and checked lock, can hear strike activating when access is granted. Lock not unlocking. Removed lock andconnected to battery, lock would unlock every 3rd or 4th time. Installed new Lockwood ES2000 and tested door. Lockunlocking every time door is granted access.
MSA-DTWD | WA5613523 | 2 | M Construction (WA) | P Block - P010 -door coming away from its hinges and not self closing | Building | Doors | 415.11 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-14 13:14 | 2022-07-19 17:00 | 2022-07-19 07:00 | 2022-07-19 17:00 | 2022-07-19 10:30 |  |  | Shaved down door PO10 to allow for it to close properly. Adjusted door closer and varnished freshly. Shaved edge of door.
MSA-DTWD | WA5660335 | 2 | Techworks Electrical | Kitchen Area - yellagonga centre the kitchen area above sink has a broken power point | Electrical | General Electrical | 906.16 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-19 09:05 | 2022-07-22 17:00 | 2022-07-20 12:00 | 2022-07-22 17:00 | 2022-07-20 15:30 |  |  | Installed new RCD and single GPO on existing circuit in yellowgonga building for new HWU unit in the kitchen area.
MSA-DTWD | WA5660439 | 2 | Techworks Electrical | workshops flashing overhead light in electro technology | Electrical | Lighting, Internal | 639.715 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-19 09:49 | 2022-07-22 17:00 | 2022-07-22 12:00 | 2022-07-22 17:00 | 2022-07-22 15:30 |  |  | Replaced 2 high bay lights at Clarkson campus with new Parts covered under warranty.
MSA-DTWD | WA5675693 | 3 | AWB Co. | Ground Level - External Wall West - Several Large bricks have been punched in by reversing cars | Building | External Walls | 548.92 | Fail | Fail | 1 | 1 | 3.5 | 2022-07-22 12:57 | 2022-07-29 17:00 | 2022-08-02 07:00 | 2022-07-29 17:00 | 2022-08-02 10:30 |  |  | Ground Level - External Wall West - Several Large bricks have been punched in by reversing cars
MSA-DTWD | WA5676413 | 2 | AWB Co. | LSK kitchen door requires bottom sealing rubber replaced | Building | Doors | 364.87 | Pass | Pass | 0 | 0 | 3.5 | 2022-07-25 08:22 | 2022-07-28 17:00 | 2022-07-26 11:30 | 2022-07-28 17:00 | 2022-07-26 15:00 |  |  | LSK kitchen door requires bottom sealing rubber replaced
MSA-DCA | WA5683127 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Centenary Gallery - Ground - P0 Humidity alarm value 57.2 | Building | General Building | 605.305 | Pass | Fail | 0 | 0 | 3.5 | 2022-07-30 03:56 | 2022-07-30 05:56 | 2022-07-30 04:30 | 2022-07-30 07:56 | 2022-07-30 08:00 |  |  | FCU 3 Onsite 30/7/22. 04.30amChecked operation of equipment and confirmed equipment operations. Measured at FCU Heating water supply 63degHeating water return 50deg Chilled water supply 8.8degChilled water return 11.5deg Confirmed valve and actuator operation for both chilled and heading Confirmed air flow through FCU and air flow pathway clear. Note. Currently there are no displays in gallery as part of roof has caved in. Note. binder test points have hardened over time. BMS data Supply Humidity is 48%Return humidity is 57%Equipment in full dehum mode Note supply humidity rising in gallery as Ambient humidity climbing.
MSA-DTWD | WA5692175 | 2 | Protek 24/7 Building & Maintenance | Water leak down east wall of staircase | Building | Internal Walls | 610.69 | Fail | Fail | 1 | 1 | 3.5 | 2022-08-03 11:00 | 2022-08-08 17:00 | 2022-08-15 12:00 | 2022-08-08 17:00 | 2022-08-15 15:30 |  |  | Remove flashings - cleanout gutter - Reinstall flashings and seal
MSA-DCA | WA5697498 | 0 | Techworks Electrical | Bollard not operating properly | Electrical | General Electrical | 409.475 | Pass | Pass | 0 | 0 | 3.5 | 2022-08-09 09:59 | 2022-08-09 12:00 | 2022-08-09 10:00 | 2022-08-09 14:00 | 2022-08-09 13:30 |  |  | Investigated bollards not working properly. Opened up base to pole not working and adjusted solenoid so bollards lower quicker. Pole still lowering slowly. Tried moving the pole around as it went down which allowed water to escape and the pole lowered much quicker. Tested bollard a few more times and was operating a lot quicker. Due to the amount of rain the bollard may of had excessed water build up below prevent it from dropping.
MSA-DTWD | WA5706793 | 2 | JEM Carpentry | House 15 - Faulty Fence | Building | Steel Fencing & Gates |  | Pass | Pass | 0 | 0 | 3.5 | 2022-08-11 14:02 | 2022-08-16 17:00 | 2022-08-15 08:30 | 2022-08-16 17:00 | 2022-08-15 12:00 |  |  | Repairs to fence
MSA-DTWD | WA5752230 | 2 | AWB Co. | H303 - Water leak next to AC fresh air vent - H303 | Roofing | Metal Roofing | 760.25 | Pass | Pass | 0 | 0 | 3.5 | 2022-08-17 11:38 | 2022-08-22 17:00 | 2022-08-22 10:30 | 2022-08-22 17:00 | 2022-08-22 14:00 |  |  | Investigated roof leakRemoved vent flashingsFound old rotted silicon around vent unitCleaned back dirt/ debris and old siliconOver-sealed around vent unitReinstalled vent flashingsSealed flashingsCleaned and packed up
MSA-DCA | WA5752455 | 3 | Protek 24/7 Building & Maintenance | Level 1 - Corridor - Door into corridor getting stuck. Needs adjustment | Building | Doors | 354.39 | Pass | Pass | 0 | 0 | 3.5 | 2022-08-17 11:50 | 2022-08-24 17:00 | 2022-08-22 07:00 | 2022-08-24 17:00 | 2022-08-22 10:30 |  |  | Removed pins and spindle from door lock . Fitted cover plate to conceal the holes
MSA-DCA | WA5780242 | 0 | FCT SURFACE CLEANING | Entrance/car park - Beaufort St - graffiti on the wall | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 3.5 | 2022-08-19 08:40 | 2022-08-19 10:40 | 2022-08-19 09:00 | 2022-08-19 12:40 | 2022-08-19 12:30 |  |  | Job Completed - Graffiti was removed from all along wall to entrance/car park on Beaufort St.
MSA-DFES | WA5827723 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Roof (ground level roof) - 2 solar systems on roof - The one to the east is leaking - 60L per hour | Plumbing & Drainage | HWS/Units Electric & Gas | 2527.115 | Fail | Fail | 6 | 6 | 3.5 | 2022-09-01 12:31 | 2022-09-06 17:00 | 2022-10-19 07:00 | 2022-09-06 17:00 | 2022-10-19 10:30 |  | WACCES | Install new solar panel. All in good order.
MSA-DCA | WA6014753 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Heat Reclaim Pump not working | Mechanical Services | Pumps | 427.925 | Pass | Pass | 0 | 0 | 3.5 | 2022-10-12 11:44 | 2022-10-13 17:00 | 2022-10-12 12:00 | 2022-10-13 17:00 | 2022-10-12 15:30 |  |  | Investigated hrp-01 showing run status on bms but not running. Checked for power at isolator, no power. Checked at board, power is on but no indicator lights lit. Called techworks to attend to investigate further. Switched run status to hrp-02 and put hrp-01 to out of service. Techworks investigated and got power to the board. Switched to manual operation and checked for power at the motor. Motor now has power but not running. Isolated and checked windings. Motor is electrically faulty and will require repairs. Isolated and tagged out motor and board. Will quote for further works. Carried out paperwork.
MSA-DTWD | WA6041199 | 3 | AHS Services WA Pty Ltd (Anchor) | Leaking Pan first cubicle ( slowly leaking around floor ) | Plumbing & Drainage | Toilets/Cisterns | 436.735 | Pass | Pass | -1 | -1 | 3.5 | 2022-10-17 07:15 | 2022-10-21 17:00 | 2022-10-17 08:30 | 2022-10-21 17:00 | 2022-10-17 12:00 |  |  | Removed pan and found waste line leaking,cut out and replaced with new pan collier.Also found flush pipe had been forced it to the pan.Knocked out new hole and cut flush pipe to fit along with a new rubber connector.Tested then siliconed pan back into position.
MSA-DTWD | WA6108756 | 3 | AWB Co. | Exhaust fan not working | Electrical | General Electrical | 635.705 | Pass | Pass | 0 | 0 | 3.5 | 2022-10-20 10:54 | 2022-10-27 17:00 | 2022-10-25 10:00 | 2022-10-27 17:00 | 2022-10-25 13:30 |  |  | Attended site signed in jsa completed. Reported fan not working. Found no power to switch. Checked rcd and its on. Had to climb onto roof to check isolator. Found isolator off with out of service from AAS. Turned on and turned switch on at ground level and humming sound came on really loud. Electrical is all good need aircon of mechanical company to check fan.Job completed
MSA-DTWD | WA6126125 | 2 | Schneider Electric Australia Pty Ltd | North-Electric locks to be removed- see notes | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 3.5 | 2022-10-25 10:26 | 2022-10-28 17:00 | 2022-10-25 10:30 | 2022-10-28 17:00 | 2022-10-25 14:00 |  |  | Attended site and removed electric locks from the A Block staff Entry Corridor and the Rear Staffentry to A Block.
MSA-DTAG | WA6229691 | 0 | Sapio Pty Ltd | level 4 - room 46 - duress alarm not working | Security | Security Management System | 1148.4 | Fail | Fail | 0 | 0 | 3.5 | 2022-11-18 10:22 | 2022-11-18 12:22 | 2022-11-18 14:30 | 2022-11-18 14:22 | 2022-11-18 18:00 |  |  | Inspected Level 4, Room 46 duress, found that wireless range was insufficient. Installed repeater in Level 4 comms riser. Tested duress, successfully alarmed and restored. Job completed.
MSA-DTWD | WA6229951 | 1 | AWB Co. | Gutter and water leaks in library area | Roofing | Guttering | 752.33 | Pass | Pass | 0 | 0 | 3.5 | 2022-11-18 10:52 | 2022-11-21 17:00 | 2022-11-18 11:30 | 2022-11-21 17:00 | 2022-11-18 15:00 |  |  | Attended site and completed jsa, we had a inspection with a staff member then accessed the roof. We found a poorly sealed sump, all window seals covered in moss, stop ends of the box gutter poorly sealed. We cleaned everything and sealed it all. We also found a apron flashings clogges with mud/leaves, we cleaned it all out.
MSA-DTWD | WA6256908 | 3 | AWB Co. | Ground Floor External - Garden Shed - Damaged down pipe | Roofing | Guttering | 726.77 | Pass | Pass | 0 | 0 | 3.5 | 2022-11-24 10:04 | 2022-12-01 17:00 | 2022-11-29 12:00 | 2022-12-01 17:00 | 2022-11-29 15:30 |  |  | Attended site and met with facilities management. We had a inspection of poor drainage system thatwas causing leaks into shed. Site wanted PVC attached to redirect water away from shed. We installedall correct attachments and PVC required.Job completed
MSA-DTWD | WA6258462 | 2 | Precise Air Group | Loud buzzing sound coming from ceiling - 2nd floor -see notes | Air Conditioning | Room Air Conditioners | 853.555 | Fail | Fail | 2 | 2 | 3.5 | 2022-11-25 12:22 | 2022-11-30 17:00 | 2022-12-12 07:00 | 2022-11-30 17:00 | 2022-12-12 10:30 |  | WACCES | Picked up new VAV Box damper actuator,signed in got passes and all equipment needed ,got into high raked ceiling space and changed actuator,rewired and set up damper controls checked operation all working great again job completed
MSA-DCA | WA6359584 | 2 | Techworks Electrical | External Ground - Wetlands & Museum Plaza - Christmas lights sockets are unsafe – See Notes | Electrical | Lighting, External | 1162.48 | Pass | Pass | 0 | 0 | 3.5 | 2022-12-06 15:33 | 2022-12-09 17:00 | 2022-12-09 08:30 | 2022-12-09 17:00 | 2022-12-09 12:00 |  |  | Installed adaptable boxes to make safe plug connections and timers.
MSA-DTAG | WA6365847 | 2 | Midolo Building Services | 1987-Sherff's office-Bricks loose and uneven at back exit door. Staff member tripped. | Paving & Roadworks | Paving | 328.01 | Pass | Pass | 0 | 0 | 3.5 | 2022-12-13 12:48 | 2022-12-16 17:00 | 2022-12-14 08:30 | 2022-12-16 17:00 | 2022-12-14 12:00 |  |  | paving repaired. Made even
MSA-DTAG | WA6375728 | 0 | Sapio Pty Ltd | L8-L08-07 mediation room 806 duress in 8.3 | Security | Security Management System | 467.87 | Pass | Pass | 0 | 0 | 3.5 | 2022-12-15 10:12 | 2022-12-15 12:12 | 2022-12-15 10:30 | 2022-12-15 14:12 | 2022-12-15 14:00 |  |  | Attended site. Refused entry to building by Mirvac Security. Had to find alternative Parking.Replaced 1 x CR123 battery in duress, duress restored.
MSA-DTWD | WA6384677 | 2 | Damian Rak Electrical Pty Ltd | External Power Point Faulty | Electrical | General Electrical |  | Pass | Pass | -1 | -1 | 3.5 | 2022-12-21 08:35 | 2022-12-28 17:00 | 2022-12-21 09:00 | 2022-12-28 17:00 | 2022-12-21 12:30 |  |  | External powerpoint faultyTradesman Labour Damian 3.5 hrs onsiteDamian 0.5 hrs offsiteMaterials 1 x weatherproof powerpoint 1 x length conduit with cable and fixings Isolate, test, tag
MSA-DFES | WA6393991 | 0 | Australian HVAC Services Pty. Ltd. | CRAC HVAC BMS fault - CRAC 1-2 DB - 14 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 407.39 | Pass | Pass | 0 | 0 | 3.5 | 2022-12-29 14:28 | 2022-12-29 16:28 | 2022-12-29 14:30 | 2022-12-29 18:28 | 2022-12-29 18:00 |  |  | Douglas Posthuma (29/12/2022) - Work NoteAttended site.Found several alarms but common one coming from CRAC 1.1A.Accessed room and found system had tripped on water flow loss.Found common power alarm coming up, checked power supplies to unit and all was ok. Unsure what was causing the power supply issue.Noted fire services contractor also on site looking at a power supply issue at the fire panel.Checked cooling towers and condenser water pumps, all ok.Likely water flow loss due to loss of condenser water pump if the power went off to that controller.Reset and monitored system, all ok.CRAC 1.1A compressors cycled correctly.
MSA-DTWD | WA6402558 | 1 | Lane's Plumbing | Paddock behind House 801 - Burst water pipe | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 3.5 | 2023-01-05 13:08 | 2023-01-06 17:00 | 2023-01-05 13:30 | 2023-01-06 17:00 | 2023-01-05 17:00
MSA-DFES | WA6404682 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Front firefighters dorm - lights not working - see note | Electrical | Lighting, Internal | 393.16 | Pass | Pass | -1 | -1 | 3.5 | 2023-01-09 08:23 | 2023-01-16 17:00 | 2023-01-11 10:30 | 2023-01-16 17:00 | 2023-01-11 14:00
MSA-DFES | WA6415290 | 2 | AWB Co. | External facia sheeting has come loose in recent winds and requires re securing. | Building | External Walls | 395.635 | Fail | Fail | 2 | 2 | 3.5 | 2023-01-11 15:35 | 2023-01-16 17:00 | 2023-01-30 11:30 | 2023-01-16 17:00 | 2023-01-30 15:00
MSA-DTWD | WA6462589 | 2 | AWB Co. | 11 down lights not working | Electrical | Lighting, Internal | 533.865 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-17 09:12 | 2023-01-20 17:00 | 2023-01-20 09:00 | 2023-01-20 17:00 | 2023-01-20 12:30
MSA-DTWD | WA6482631 | 2 | AWB Co. | East side part of the external eve is coming away from the roof section | Building | General Building | 1373.49 | Fail | Fail | 0 | 0 | 3.5 | 2023-01-18 11:47 | 2023-01-23 17:00 | 2023-01-25 10:00 | 2023-01-23 17:00 | 2023-01-25 13:30
MSA-DTWD | WA6516746 | 2 | M Construction (WA) | repair hole in ceiling | Building | Ceiling | 889.31 | Pass | Pass | 0 | 0 | 3.5 | 2023-01-23 14:33 | 2023-01-27 17:00 | 2023-01-25 11:30 | 2023-01-27 17:00 | 2023-01-25 15:00
MSA-DFES | WA6518023 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1- RM 8, 10 & 17 - Bed lamps are damaged and require replacing | Electrical | Lighting, Internal | 626.04 | Pass | Pass | -1 | -1 | 3.5 | 2023-01-24 15:33 | 2023-01-30 17:00 | 2023-01-25 14:15 | 2023-01-30 17:00 | 2023-01-25 17:45
MSA-DTWD | WA6521519 | 0 | Equans Mechanical Services Australia | Rooms 302 & 305 - No air conditioning | Air Conditioning | Room Air Conditioners | 534.915 | Pass | Fail | 0 | 0 | 3.5 | 2023-01-30 11:23 | 2023-01-30 13:23 | 2023-01-30 13:00 | 2023-01-30 15:23 | 2023-01-30 16:30
MSA-DTWD | WA6533842 | 1 | Lane's Plumbing | Building 822 - Flat B - Bathroom - Faulty Hotwater Pipe | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 3.5 | 2023-02-06 09:14 | 2023-02-07 17:00 | 2023-02-06 10:00 | 2023-02-07 17:00 | 2023-02-06 13:30
MSA-DTWD | WA6544681 | 2 | AWB Co. | Room D117 - No power to Large 3 phase Guillotine | Electrical | General Electrical | 337.87 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-10 15:49 | 2023-02-15 17:00 | 2023-02-14 12:00 | 2023-02-15 17:00 | 2023-02-14 15:30
MSA-DCA | WA6579153 | 2 | Protek 24/7 Building & Maintenance | Ground - Chichos Gelato - Right hand side door is sticking | Building | Doors | 463.01 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-15 15:15 | 2023-02-20 17:00 | 2023-02-17 07:30 | 2023-02-20 17:00 | 2023-02-17 11:00
MSA-DFES | WA6604022 | 3 | AWB Co. | SOs Bathroom- Soap dish in station officers shower has broken off - needs replacing/ repair | Building | General Building | 466.635 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-17 14:37 | 2023-02-24 17:00 | 2023-02-22 07:00 | 2023-02-24 17:00 | 2023-02-22 10:30
MSA-DTAG | WA6650001 | 1 | AWB Co. | Family Violence Services - No power to 5 work stations on level 5 | Electrical | Distribution Board | 385.735 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-20 08:47 | 2023-02-21 17:00 | 2023-02-21 08:30 | 2023-02-21 17:00 | 2023-02-21 12:00
MSA-DFES | WA6667774 | 2 | Australian HVAC Services Pty. Ltd. | Store Room - AC leaking considerable amount of water - See notes | Air Conditioning | Evaporative Coolers | 407.39 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-21 14:41 | 2023-02-24 17:00 | 2023-02-24 07:30 | 2023-02-24 17:00 | 2023-02-24 11:00
MSA-DTWD | WA6672317 | 3 | AWB Co. | faulty and deteriorated ceiling lights | Electrical | Lighting, Internal | 964.74 | Pass | Pass | 0 | 0 | 3.5 | 2023-02-23 14:53 | 2023-03-02 17:00 | 2023-02-28 08:30 | 2023-03-02 17:00 | 2023-02-28 12:00
MSA-DCA | WA6684254 | 0 | Techworks Plumbing | Level 3 toilet block - Strong Sewage stench | Plumbing & Drainage | Toilets/Cisterns | 374.44 | Pass | Fail | 0 | 0 | 3.5 | 2023-03-05 13:03 | 2023-03-05 15:03 | 2023-03-05 14:30 | 2023-03-05 17:03 | 2023-03-05 18:00
MSA-DTWD | WA6690292 | 1 | AWB Co. | Outside - Water leak from roof - possible gutter blockage - see notes | Roofing | Guttering | 731.7 | Pass | Pass | 0 | 0 | 3.5 | 2023-03-09 08:31 | 2023-03-10 17:00 | 2023-03-09 09:00 | 2023-03-10 17:00 | 2023-03-09 12:30
MSA-DCA | WA6693579 | 0 | EQUANS Mechanical Services (WA) Pty Limited | admin building - Air con not working | Air Conditioning | Ducted Split System | 627.825 | Pass | Fail | 0 | 0 | 3.5 | 2023-03-10 11:46 | 2023-03-10 13:46 | 2023-03-10 13:30 | 2023-03-10 15:46 | 2023-03-10 17:00
MSA-DTWD | WA6708263 | 1 | Equans Mechanical Services Australia | B131 accessed via B127 - spray booth extraction fan currently not working | Air Conditioning | Room Air Conditioners | 354.735 | Pass | Pass | 0 | 0 | 3.5 | 2023-03-13 14:44 | 2023-03-14 17:00 | 2023-03-14 13:00 | 2023-03-14 17:00 | 2023-03-14 16:30
MSA-DTWD | WA6518013 | 2 | Precise Air Group | A52 A.C Plant Room-Belts squeaking / rubbing on FCU 1 | Air Conditioning | Room Air Conditioners | 552.08 | Pass | Pass | -1 | -1 | 3.4833 | 2023-01-24 15:30 | 2023-01-30 17:00 | 2023-01-25 12:22 | 2023-01-30 17:00 | 2023-01-25 15:51
MSA-DCA | WA5481134 | 0 | GPS Plumbing & Gas Services PtyLtd | kitchen, leaking zip hot tap | Plumbing & Drainage | Water | 824.6175 | Pass | Pass | 0 | 0 | 3.4833 | 2022-05-30 11:11 | 2022-05-30 13:11 | 2022-05-30 11:30 | 2022-05-30 15:11 | 2022-05-30 14:59 |  |  | Replaced leaking zip tap as per work order but after testing the boiler to make sure everything is all good we noticed the that the boiling unit was faulty it looked like the unit leaked onto the mother body and damage the solenoid valve and the unit is 13 years old its on it's way out it's better to replace than to try and repair
MSA-DCA | WA6391938 | 0 | Techworks Electrical | garden bed, Frances street-light pole has been pushed over and exposed wires | Electrical | Lighting, External | 494.79 | Pass | Pass | 0 | 0 | 3.4833 | 2022-12-23 07:28 | 2022-12-23 09:28 | 2022-12-23 07:42 | 2022-12-23 11:28 | 2022-12-23 11:11 |  |  | Ran new conduit up and into bollard light, several services underneath column base would not allow for more concrete, installed multiple fixings in the top as there were several missing
MSA-DTWD | WA6359174 | 1 | Precise Air Group | Block G - 122 - Leaking AC unit | Air Conditioning | Room Air Conditioners | 788.09 | Pass | Pass | 0 | 0 | 3.45 | 2022-12-06 12:58 | 2022-12-07 17:00 | 2022-12-07 08:58 | 2022-12-07 17:00 | 2022-12-07 12:25 |  |  | Changed pump and unit working. Wire inside flow control had failed.
MSA-DCA | WA5230576 | 1 | EQUANS Mechanical Services (WA) Pty Limited | ART GALLERY - Roe street - Level 1- AHU07- Humidity Alarm on | Building | Materials | 345.35 | Pass | Pass | 0 | 0 | 3.45 | 2022-03-15 05:31 | 2022-03-15 17:00 | 2022-03-15 06:06 | 2022-03-15 17:00 | 2022-03-15 09:33 |  |  | Recieved AH call. Attended site gained access and carried out inspection of AHU 7 L1 high humidity alarm. Note when on site there were no active humidity alarms. Checked chilled and heating water to AHU coil and reheats. Confirmed heating water valve operation. AHU running as per design with no active faults. Comms alarm noted to be active on RO plant. Carried out investigations. Reset plant and alarm cleared. Confirmed RO plant operation. Rechecked AHU 7 Confirmed operating OK. Work area left tidy. Site has no active alarms.
MSA-DTAG | WA5993279 | 0 | Seme Solutions Pty Ltd | Security system - alarm going into fault - multiple locations - see notes below | Security | Security Management System | 489.58 | Pass | Fail | 0 | 0 | 3.4206 | 2022-10-05 09:32 | 2022-10-05 11:32 | 2022-10-05 11:00 | 2022-10-05 13:32 | 2022-10-05 14:25 |  |  | Job complete
MSA-DTWD | WA4992503 | 2 | Water2water Pty Ltd | Corridor under G block - drinking fountain not working from buttons | Plumbing & Drainage | Water | 3719.36 | Fail | Fail | 3 | 3 | 3.4167 | 2022-01-06 12:41 | 2022-01-11 17:00 | 2022-02-02 11:30 | 2022-01-11 17:00 | 2022-02-02 14:55 |  |  | Checked unit valve inside unit needs to be replaced-and plate, contacted manufacturers who advised due to age of system they no longer supply parts for this - Quoted to replace unit is estimated to be over 12 years Installed new Asset - Wheelchair Access Fountain Bubbler WCAP8ACY + Gooseneck Faucet as quotedemoved old to tip also changed filter in Maxiflow system - New Serial Number of Fountain Prog A40184357L Manufacturers SN 21118945
MSA-DTAG | WA5790200 | 3 | Gilmour & Jooste Electrical | ground Court Waiting Area-2 down lights need fixing – Waiting area and front pole lights | Electrical | Lighting, Internal | 277.64 | Fail | Fail | 0 | 0 | 3.4167 | 2022-08-22 09:19 | 2022-08-29 17:00 | 2022-09-01 07:00 | 2022-08-29 17:00 | 2022-09-01 10:25 |  |  | Replaced faulty downlights. Tested and working. Will organise for pole lights to be replaced on new quoted job.
MSA-DCA | WA6449968 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Chiller 1 is faulty | Refrigeration | Chiller | 506.75 | Pass | Pass | 0 | 0 | 3.4167 | 2023-01-16 08:38 | 2023-01-16 10:38 | 2023-01-16 09:00 | 2023-01-16 12:38 | 2023-01-16 12:25
MSA-DTWD | WA6573569 | 1 | Equans Mechanical Services Australia | RETROSPECTIVE - DO NOT ATTTEND - No water running through evap cooler - see notes | Air Conditioning | Evaporative Coolers | 399.78 | Fail | Fail | 3 | 3 | 3.4167 | 2023-01-25 14:30 | 2023-01-27 17:00 | 2023-02-14 11:30 | 2023-01-27 17:00 | 2023-02-14 14:55 | 1
MSA-DTWD | WA6044816 | 2 | M Construction (WA) | Walkway between A & D Blocks - Paving is sinking - See notes below | Flooring | Concrete | 408.01 | Pass | Pass | 0 | 0 | 3.4 | 2022-10-17 10:48 | 2022-10-20 17:00 | 2022-10-20 10:00 | 2022-10-20 17:00 | 2022-10-20 13:24 |  | WACCES | Remove Badly Sunken Pavers with pry and filled in hole with blue metal leveled off with cracker dust. Re Laid Pavers Filling in cracks to complete.
MSA-DFES | WA5204436 | 0 | Australian HVAC Services Pty. Ltd. | Chiller 1 - is in fault | Air Conditioning | Room Air Conditioners | 378.6 | Pass | Fail | 0 | 0 | 3.3731 | 2022-03-04 10:40 | 2022-03-04 12:40 | 2022-03-04 12:27 | 2022-03-04 14:40 | 2022-03-04 15:50 |  |  | Attended site and inspected chiller 1. Found chiller tripped on condenser water flow loss. Chiller was operating so cleared the fault and checked over system. Found water flow dp operating. Checked water flow present and water level in tower is correct. Accessed bms and checked over trendlogs. Found water flow was present at time of fault. Monitored operation and found all appears ok.
MSA-DTWD | WA5105244 | 1 | Precise Air Group | faulty AC - see notes | Air Conditioning | Room Air Conditioners | 141.29 | Pass | Pass | 0 | 0 | 3.35 | 2022-02-04 08:55 | 2022-02-07 17:00 | 2022-02-07 12:00 | 2022-02-07 17:00 | 2022-02-07 15:21 |  |  | Attended site and completed pre start paperwork andsigned in. Accessed wall split in g118. Test ran systemand found to start and run with out fault. Fm to monitor
MSA-DTWD | WA5195108 | 0 | ACTION GLASS & ALUMINIUM | Glass door on outside of building has broken a hinge -see notes below | Building | Doors | 300 | Fail | Fail | 0 | 0 | 3.3333 | 2022-02-28 10:44 | 2022-02-28 12:44 | 2022-02-28 13:00 | 2022-02-28 14:44 | 2022-02-28 16:20 |  |  | ATTENDED SITE AND ASSESSED DOOR, RETURNED BACK SAME DAY WITH 2 MEN, ADJUSTED PIN, REFITTED DOOR AND REALIGNED DOOR.
MSA-DTWD | WA5838526 | 2 | Water2water Pty Ltd | Water Fountain - leaking water | Plumbing & Drainage | Water | 468.305 | Pass | Pass | 0 | 0 | 3.3333 | 2022-09-08 14:21 | 2022-09-13 17:00 | 2022-09-12 10:10 | 2022-09-13 17:00 | 2022-09-12 13:30 |  |  | Copper waste line had completely detached from fountain. Removed copper waste off wall to unblock. Leaking on valve train aswell. Pulled apart and re assembled.
MSA-DCA | WA6483069 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground - Dressing Room 4 Ensuite - Basin taps: 1 not working, 1 hard to turn on | Plumbing & Drainage | Water | 546.125 | Pass | Pass | 0 | 0 | 3.3333 | 2023-01-18 12:47 | 2023-01-23 17:00 | 2023-01-23 11:30 | 2023-01-23 17:00 | 2023-01-23 14:50
MSA-DTWD | WA6190901 | 3 | Precise Air Group | Room A108 - Exhaust fan broken | Equipment | Electrical Equipment | 905.72 | Pass | Pass | -1 | -1 | 3.3167 | 2022-11-16 11:27 | 2022-11-23 17:00 | 2022-11-18 11:10 | 2022-11-23 17:00 | 2022-11-18 14:29 |  |  | Checked exhaust fan in plant room found had deteriorated from old age and blades had snapped off replaced with new one same make and model .
MSA-DTWD | WA6190907 | 3 | Precise Air Group | Room A211 - Exhaust fan broken | Equipment | Electrical Equipment | 905.72 | Pass | Pass | -1 | -1 | 3.3 | 2022-11-16 11:31 | 2022-11-23 17:00 | 2022-11-18 11:11 | 2022-11-23 17:00 | 2022-11-18 14:29 |  |  | Found old exhaust fan blades were cracked and broken replace with new exhaust fan of same make and model
MSA-DCA | WA5682553 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Wet storage area - temp has warmed up | Air Conditioning | Room Air Conditioners | 427.925 | Pass | Fail | 0 | 0 | 3.3 | 2022-07-29 09:39 | 2022-07-29 11:39 | 2022-07-29 11:00 | 2022-07-29 13:39 | 2022-07-29 14:18 |  |  | Attended site gained access inspected plant equipment. Chilled water pumps 1 and 2 found to have over current fault active on both VSD. Reset VSD isolated pumps and checked windings. Confirmed ok. Pumps placed into test operation and started as normal fault did not reoccure. Cause of fault suspected to be power spike. Will keep equipment under observation during next PM. Monitored until temps became stable. Work area has been left tidy.
MSA-DTAG | WA5800789 | 1 | Gilmour & Jooste Electrical | Lower Level - Custody - Phone Fault - See notes below | Electrical | General Electrical | 90.09 | Pass | Pass | 0 | 0 | 3.2833 | 2022-08-31 12:26 | 2022-09-01 17:00 | 2022-09-01 07:07 | 2022-09-01 17:00 | 2022-09-01 10:24 |  |  | Investigated comms fault. Found fault switch panel in comms rack located in custody. Iain advised - replacement switch required.
MSA-DCA | WA5112121 | 2 | Precise Air Group | Main Building - Level 3 - WA Opera offices - see details below | Air Conditioning | Room Air Conditioners | 329.67 | Pass | Pass | -1 | -1 | 3.2667 | 2022-02-10 13:29 | 2022-02-15 17:00 | 2022-02-11 08:00 | 2022-02-15 17:00 | 2022-02-11 11:16 |  |  | Travelled to site, gained access, spoke with site contactregarding air conditioning issues, logged onto BMSsystem, made minor adjustments to supply air temp setpoints, checked operation of zone and water actuator onsystem, found no additional issues. Cleared debris fromsite
MSA-DTWD | WA4991838 | 1 | WESTERN IRRIGATION PTY LTD | Ground - Bore & Reticulation - When bore running each station not closing off after set time - note | Landscaping & Gardening | Grounds Maintenance | 507.5 | Pass | Pass | 0 | 0 | 3.25 | 2022-01-05 12:47 | 2022-01-06 17:00 | 2022-01-06 06:00 | 2022-01-06 17:00 | 2022-01-06 09:15 |  |  | Show site how to operate system. Balance and program for best operation.
MSA-DTWD | WA5010447 | 1 | Equans Mechanical Services Australia | Exhaust fans not working - see notes below | Electrical | General Electrical | 505.68 | Fail | Fail | 0 | 0 | 3.25 | 2022-01-12 14:29 | 2022-01-13 17:00 | 2022-01-14 11:15 | 2022-01-13 17:00 | 2022-01-14 14:30 |  |  | TRAVELLED TO SITE. LOGGED ON TO SITE. MET WITH MANAGERAND GAINED ACCESS TO SITE. LOCATED AND CHECKED OPERATIONOF TOILET EXHAUST SYSTEM AND FOUND 1 OF THE LEAD/LAG MOTORS NOT TURNING FAN. GAINED ACCESS TO ROOF AND FOUND V BELTS BROKEN. TRAVELLED TO SUPPLIERS AND PICKED UP PARTS. RETURNED TO SITE AND GAINED ACCESS TO ROOF. REPLACED AND ADJUSTED V BELTS AND CHECKED OPERATION. ALL OK. LEFT SPARE BELTS IN WORKSHOP. CLEARED UP WORK AREA AND DISPOSED OF RUBBISH. COMPLETED PAPERWORK AND LOGGED OFF JOB.
MSA-DTWD | WA5069045 | 3 | Equans Mechanical Services Australia | Air con not working | Air Conditioning | Room Air Conditioners | 449.28 | Pass | Pass | -1 | -1 | 3.25 | 2022-01-19 14:15 | 2022-01-27 17:00 | 2022-01-20 08:45 | 2022-01-27 17:00 | 2022-01-20 12:00 |  |  | TRAVELLED TO SITE AND SIGNED IN. LIASED WITH NICK HE SHOWED A UNIT IN THE LUNCH ROOMTHAT WAS NOT RUNNING AND TRIPPING THE BREAKER. INVESTIGATED UNITNANDNFOUND THATTHE RUN CAPACITOR ON THE COMPRESSOR TO BE FAULTY. TRAVELLED OFFSITE TO PICK-UPSUPPLIES. TRAVELLED BACK TO SITE AND INSTALLED NEW 60UF CAPACITOR AND INSTALLED ANDPROGRAMMED A UNIVERSAL REMOTE. TESTED OPERATION ALL OK.
MSA-DTWD | WA5187650 | 1 | Equans Mechanical Services Australia | AT - Ground - AT248 & AT253 - Air conditioners not working. | Air Conditioning | Room Air Conditioners | 308.72 | Pass | Pass | 0 | 0 | 3.25 | 2022-02-22 14:12 | 2022-02-23 17:00 | 2022-02-23 11:45 | 2022-02-23 17:00 | 2022-02-23 15:00 |  |  | Arrived on site signed in gathered access keys. Gathered tools and equipment, started checks on evaporative units found 248 room in ventilation operation turned to cooling and monitoring all ok. Checked room 253 checked for faults no faults located reset unit operation checked out ok. Monitored both units all ok. Completed paperwork.
MSA-DFES | WA5216385 | 2 | Protek 24/7 Building & Maintenance | Main building - Ground - Internal stair case - see details below | Building | General Building | 567.36 | Pass | Pass | 0 | 0 | 3.25 | 2022-03-11 09:29 | 2022-03-16 17:00 | 2022-03-15 07:30 | 2022-03-16 17:00 | 2022-03-15 10:45 |  |  | Removed & replaced new plugs
MSA-DCA | WA5380125 | 3 | FCT SURFACE CLEANING | Ground Floor - Centenary Gallery - External Wall - Graffiti | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 3.25 | 2022-04-22 08:37 | 2022-05-02 17:00 | 2022-04-27 07:30 | 2022-05-02 17:00 | 2022-04-27 10:45 |  |  | works completed -removed graffiti
MSA-DTWD | WA5383252 | 3 | AWB Co. | South Block - Level 2 - Creche Playground - Missing picket from Creche fence | Building | General Building | 365.875 | Pass | Pass | -1 | -1 | 3.25 | 2022-04-27 13:35 | 2022-05-04 17:00 | 2022-04-28 11:15 | 2022-05-04 17:00 | 2022-04-28 14:30 |  |  | Supplied and install a painted fence paling
MSA-DTWD | WA5396837 | 3 | Protek 24/7 Building & Maintenance | A Block - Doors not closing properly, hinges need to be adjusted - See notes | Building | Doors | 291.625 | Pass | Pass | 0 | 0 | 3.25 | 2022-05-06 11:32 | 2022-05-13 17:00 | 2022-05-10 06:45 | 2022-05-13 17:00 | 2022-05-10 10:00 |  |  | Repair hinges - doors not closing properly
MSA-DCA | WA5578320 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Lift 7 - Displaying out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 3.25 | 2022-07-01 10:35 | 2022-07-04 17:00 | 2022-07-01 12:45 | 2022-07-04 17:00 | 2022-07-01 16:00 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped top floor STElap. Reset using inspection control and lift responded. As the lift was stopped at a different floor, checked the car gatecontacts, replaced both bridging pieces, and cleaned fixed contacts. Found 2 wires of the car gate switches were behind the tightened terminals, not in the terminals. Remadecar gate connections, ensuring all wires were tight in the terminals.Adjusted the mechanical catch for each car door vane assembly to reduce the distance the doors relax, after the doors have fully closed. Replaced the relay for the car lighton the top of car board (contacts burnt) as the car lights turning on was creating electrical interference in the door operator when the doors initially open after the lift has beenidle for a period of time. Tested lift in all combinations of usage to try to reproduce the fault. Lift did not fault while onsite. Left lift in service.
MSA-DTWD | WA5584913 | 3 | AWB Co. | North External Walls - 5 x lights out external walls | Electrical | Lighting, External | 638.1 | Pass | Pass | 0 | 0 | 3.25 | 2022-07-05 11:21 | 2022-07-12 17:00 | 2022-07-11 10:15 | 2022-07-12 17:00 | 2022-07-11 13:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, went and switched override on for external light to check what was working, removed all lights that weren’t working and replaced with new, cleaned up, put rubbish in bin on site, completed paperwork , signed out **job completed**
MSA-DTWD | WA5597515 | 2 | AWB Co. | Front entrance internal ceiling service hatch - Ceiling hatch door keep dropping - See notes below | Building | Ceiling | 536.655 | Pass | Pass | 0 | 0 | 3.25 | 2022-07-11 13:37 | 2022-07-14 17:00 | 2022-07-14 09:30 | 2022-07-14 17:00 | 2022-07-14 12:45 |  |  | Picked up 2.6m platform ladder from yard, attended site, installed L bracket to frame to make secure and line up with door
MSA-DTWD | WA5680056 | 3 | AWB Co. | Exterior Front - Exterior lighting to A Block and visitor carpark are faulty | Electrical | Lighting, External | 714.85 | Pass | Pass | -1 | -1 | 3.25 | 2022-07-27 09:22 | 2022-08-03 17:00 | 2022-07-29 08:45 | 2022-08-03 17:00 | 2022-07-29 12:00 |  |  | Attended site and signed in, completed paperwork,called fm but no answer, security showed us which lights , switched on override and counted up which lights needed replacing, went to wholesaler and picked up materials. Returned to site, replaced globes in pole lights, replaced 2x LEDs at front door, tested all light fittings , everything working as intended, completed paperwork,signed out **job completed **
MSA-DTWD | WA5791589 | 2 | AWB Co. | East End Corridor - Lights not working - A Block Corridor Ground Floor East | Electrical | Lighting, Internal | 1021.8025 | Pass | Pass | 0 | 0 | 3.25 | 2022-08-23 08:36 | 2022-08-26 17:00 | 2022-08-24 12:30 | 2022-08-26 17:00 | 2022-08-24 15:45 |  |  | complete
MSA-DTWD | WA5827939 | 2 | AWB Co. | Lights not working in office | Electrical | Lighting, Internal | 997.8025 | Pass | Pass | 0 | 0 | 3.25 | 2022-09-01 14:32 | 2022-09-06 17:00 | 2022-09-05 06:30 | 2022-09-06 17:00 | 2022-09-05 09:45 |  |  | Job complete
MSA-DTWD | WA5829251 | 3 | Equans Mechanical Services Australia | Level 4 Roof - Chiller Circuit B in Alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 776.42 | Pass | Pass | -1 | -1 | 3.25 | 2022-09-02 11:18 | 2022-09-09 17:00 | 2022-09-05 09:30 | 2022-09-09 17:00 | 2022-09-05 12:45 |  |  | SEE REPORT
MSA-DTWD | WA5854006 | 2 | AWB Co. | W211/213 - Broken power point behind bed No 2 | Electrical | General Electrical | 1069.0525 | Pass | Pass | 0 | 0 | 3.25 | 2022-09-12 12:39 | 2022-09-15 17:00 | 2022-09-14 11:00 | 2022-09-15 17:00 | 2022-09-14 14:15 |  |  | Job complete
MSA-DTWD | WA6080451 | 2 | AWB Co. | North Side - Ground Level - under verandah - Broken Glass - see notes | Building | Windows | 653.25 | Pass | Pass | 0 | 0 | 3.25 | 2022-10-18 13:42 | 2022-10-21 17:00 | 2022-10-20 11:45 | 2022-10-21 17:00 | 2022-10-20 15:00 |  |  | Attended site. Signed into site and was shown location of broken glass. Found broken glass window and measured frame. Picked up materials to cover window. Returned to site cut plywood to size and fixed it to window frame. Site safe. Cleaned and packed up.
MSA-DCA | WA6292735 | 0 | TK Elevator Australia Pty Ltd | Basement Dumb waiter has gone into fault | Lifts | Lifts |  | Pass | Fail | 0 | 0 | 3.25 | 2022-11-29 12:36 | 2022-11-29 14:36 | 2022-11-29 14:15 | 2022-11-29 16:36 | 2022-11-29 17:30 |  |  | Completed - to be closed out at $0 cost
MSA-DTWD | WA6533798 | 1 | Australian Airconditioning Services Pty Ltd | ground -1G11 conference room-R/H Air conditioner leaking water | Air Conditioning | Room Air Conditioners | 930.05 | Pass | Pass | 0 | 0 | 3.25 | 2023-02-06 08:54 | 2023-02-07 17:00 | 2023-02-07 08:45 | 2023-02-07 17:00 | 2023-02-07 12:00
MSA-DTWD | WA6683540 | 2 | AWB Co. | Volumetric pump failed, verified by Liam from AWB Electrical - See Notes | Electrical | General Electrical | 1251.98 | Pass | Pass | 0 | 0 | 3.25 | 2023-03-03 09:45 | 2023-03-09 17:00 | 2023-03-07 08:45 | 2023-03-09 17:00 | 2023-03-07 12:00
MSA-DTWD | WA5098849 | 1 | AWB Co. | Metal Fabrication Building and D building - external lights not coming on at night | Electrical | Lighting, External | 573.885 | Pass | Pass | 0 | 0 | 3.25 | 2022-02-01 11:46 | 2022-02-02 17:00 | 2022-02-02 08:30 | 2022-02-02 17:00 | 2022-02-02 11:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Inspected exterior lights not working in B block. Reset tripped W40 and turned timer to override, went around and inspected lights found to be 1 not working (isn’t of concern), also found cover hanging off light so secured cover back onto fitting. Opened switchboard, megger W40 found to be low reading, can not investigate without an EWP, site has advised us not to go any further at this point in time. Also inspected exterior lights not working on D block. Found to be exterior light RCD was tripped. Pulled down multiple light fittings and put the megger on them. Found to be faulty ballast in light fitting. Replaced all parts required. Replaced few tubes in fittings that required replacing. Placed all fittings back to normal. Tested circuit. All working correctly. **job complete**
MSA-DTWD | WA5099922 | 2 | AWB Co. | faulty fluro light x 8 | Electrical | General Electrical | 881.58 | Fail | Fail | 1 | 1 | 3.25 | 2022-02-02 09:42 | 2022-02-07 17:00 | 2022-02-14 07:00 | 2022-02-07 17:00 | 2022-02-14 10:15 |  |  | Work Done
MSA-DTWD | WA5106609 | 1 | Protek 24/7 Building & Maintenance | Block 3 - Ground - 3G60 Electrical classroom - Window hinges have broken rivets | Building | General Building | 450.5 | Pass | Pass | 0 | 0 | 3.25 | 2022-02-07 09:37 | 2022-02-08 17:00 | 2022-02-08 12:15 | 2022-02-08 17:00 | 2022-02-08 15:30 |  |  | Window Hinges with Broken Rivets
MSA-DTWD | WA5115863 | 1 | Protek 24/7 Building & Maintenance | door vandalised needs repair | Building | Doors | 291.625 | Pass | Pass | 0 | 0 | 3.25 | 2022-02-11 09:45 | 2022-02-14 17:00 | 2022-02-14 08:30 | 2022-02-14 17:00 | 2022-02-14 11:45 |  |  | door vandalised needs repair - Dennis has door on site to be re fitted. Old door removed by Mark Burrows on different work order.
MSA-DFES | WA5199937 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Zambesi Plumbers to return to site and reconfigure the arm on the hose reel | Plumbing & Drainage | Water | 462.3775 | Pass | Pass | 0 | 0 | 3.25 | 2022-03-01 13:06 | 2022-03-04 17:00 | 2022-03-04 08:30 | 2022-03-04 17:00 | 2022-03-04 11:45 |  |  | Located to site to adjust the hose reels they said they were happy with how they are and fixed a-couple of leaks on the reels cause of they are getting pulled fixed and working correctly now.
MSA-DFES | WA5305088 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main Administration - Ground - Staff Change Room - see details below | Electrical | General Electrical | 425.635 | Pass | Pass | -1 | -1 | 3.25 | 2022-04-05 12:03 | 2022-04-12 17:00 | 2022-04-06 12:15 | 2022-04-12 17:00 | 2022-04-06 15:30 |  |  | Located faulty lights. Found two sensors not working in each shower. Left site to get new sensors. Replaced faulty sensors with new. Advised staff of work completed.
MSA-DTWD | WA5735387 | 1 | Techworks Plumbing | Blocked drain in the workshop | Plumbing & Drainage | Drainage | 1344.57 | Pass | Pass | 0 | 0 | 3.25 | 2022-08-16 12:48 | 2022-08-17 17:00 | 2022-08-17 07:45 | 2022-08-17 17:00 | 2022-08-17 11:00 |  |  | Arrived at the yard to pick up tools and Johnny, once we had loaded up majority of the tools we made our way to Bunnings in balcatta to pick up some witches hats as we thought we might be working in an area with students walking past also grabbed a mixer for the drill as we could mix up some concrete with it, we then headed over to Reece to pick up fittings needed for the job and bags of concrete, once we picked up everything we needed we made our way to balga tafe to the front reception to sign in, once we had finished signing in we drove over to the tiling area we begin inspecting the issue and what needed to be done, we then grabbed the wet cut and jack hammer pre paring ourselves to begin cutting, we block off the area we were working in making sure no one would be near where we would be cutting the concrete, once we had finished cutting the concrete around where the pipe was coming out of the ground, we begin to jack hammer around the pipe and where we were wet cutting. When we ha
MSA-DTWD | WA5880252 | 3 | AWB Co. | Both exit signs are out - See notes below | Electrical | Emergency & Exit Lighting | 767.3025 | Pass | Pass | 0 | 0 | 3.25 | 2022-09-15 11:37 | 2022-09-22 17:00 | 2022-09-21 11:30 | 2022-09-22 17:00 | 2022-09-21 14:45 |  |  | Job complete
MSA-DTWD | WA5962296 | 3 | Protek 24/7 Building & Maintenance | Roof leak over barista training entrance - see notes below | Roofing | Tiled Roofing | 727.81 | Pass | Pass | -1 | -1 | 3.25 | 2022-09-19 13:16 | 2022-09-27 17:00 | 2022-09-21 07:00 | 2022-09-27 17:00 | 2022-09-21 10:15 |  |  | Installed custom flashing with materials I had on board re fixed laps in flashing Cleaned of mould on ceiling and applied stain blocker
MSA-DTWD | WA5971194 | 1 | Building Automation & Electrical Services Pty Ltd | Facilities staff unable to access BMS software | Building | General Building |  | Pass | Pass | 0 | 0 | 3.25 | 2022-09-20 12:06 | 2022-09-21 17:00 | 2022-09-20 12:15 | 2022-09-21 17:00 | 2022-09-20 15:30 |  |  | Completed
MSA-DFES | WA5980280 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Officers (SO’s) Bathroom/shower - Lights faulty - See notes below | Electrical | Lighting, Internal | 511.775 | Pass | Pass | 0 | 0 | 3.25 | 2022-09-29 13:50 | 2022-10-04 17:00 | 2022-10-03 07:00 | 2022-10-04 17:00 | 2022-10-03 10:15 |  |  | complete
MSA-DTWD | WA6107454 | 2 | Water2water Pty Ltd | Bubbler at water fountain – not enough pressure - See notes | Plumbing & Drainage | Water | 724.835 | Pass | Pass | 0 | 0 | 3.25 | 2022-10-20 08:53 | 2022-10-25 17:00 | 2022-10-24 13:45 | 2022-10-25 17:00 | 2022-10-24 17:00 |  |  | Fixed issue with bubbler.
MSA-DTWD | WA6184577 | 2 | Lane's Plumbing | Valve to retic faulty | Plumbing & Drainage | Water |  | Fail | Fail | 1 | 1 | 3.25 | 2022-11-15 13:24 | 2022-11-18 17:00 | 2022-11-22 09:15 | 2022-11-18 17:00 | 2022-11-22 12:30 |  |  | repairs to retic
MSA-DFES | WA6377457 | 2 | AWB Co. | Kitchen - cornices in new kitchen have cracked and dropping | Building | Ceiling | 360.4825 | Pass | Pass | 0 | 0 | 3.25 | 2022-12-16 15:30 | 2022-12-21 17:00 | 2022-12-21 07:00 | 2022-12-21 17:00 | 2022-12-21 10:15 |  |  | Reattached cornices to cupboards at top and seal along top and bottomCleaned up work areaNo one on site at completion
MSA-DTWD | WA6522731 | 1 | PEEL LOCK SERVICES PTY LTD | Lock and door handle damaged due to break in | Security | Locksmith |  | Pass | Pass | 0 | 0 | 3.25 | 2023-01-31 09:57 | 2023-02-01 17:00 | 2023-01-31 10:00 | 2023-02-01 17:00 | 2023-01-31 13:15
MSA-MRWA | WA6523295 | 2 | AWB Co. | External lights are on during the day, require timer to be reset | Electrical | Lighting, External | 471.8025 | Pass | Pass | 0 | 0 | 3.25 | 2023-01-31 14:11 | 2023-02-03 17:00 | 2023-02-01 07:00 | 2023-02-03 17:00 | 2023-02-01 10:15
MSA-DTAG | WA6400179 | 0 | GPS Plumbing & Gas Services PtyLtd | Water leak adjacent to Staff Carpark (see notes) | Plumbing & Drainage | Drainage | 690.165 | Pass | Fail | 0 | 0 | 3.2333 | 2023-01-03 10:16 | 2023-01-03 12:16 | 2023-01-03 12:02 | 2023-01-03 14:16 | 2023-01-03 15:16
MSA-DCA | WA5567850 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Basement Level - Communications 01 (Server Room) - see details below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 484.6 | Pass | Pass | 0 | 0 | 3.2167 | 2022-06-24 13:00 | 2022-06-27 17:00 | 2022-06-27 07:00 | 2022-06-27 17:00 | 2022-06-27 10:13 |  |  | Remotely connected to site. Could not find issue with control on basement but there was several controllers offline. Investigated issue. Found CP-IPC controller was not communicating to Point Server. Remotely connect to the controller. FOund operations are ok. Restarted OS inside controller. Found comms restored
MSA-DCA | WA5396565 | 0 | TK Elevator Australia Pty Ltd | Lift 7 - stuck on level 1 back of house | Lifts | Lifts |  | Pass | Fail | 0 | 0 | 3.2 | 2022-05-06 09:55 | 2022-05-06 11:55 | 2022-05-06 10:50 | 2022-05-06 13:55 | 2022-05-06 14:02 |  |  | Lift7 Greem Rm-Hydraulic :Lift at bottom landing with doors open. Display on LISA Unit showed TTELap, SK3 and SK4 interrupt, reset by switching to inspection. Rode car tocheck operation when customer informed me that his colleague had been trapped inside the car at level 3 (street level) earlier on. He used a triangle key to open the landingdoor to release the passenger.I accessed car top and checked SO SM SU pencil switch alignment to magnet and cleaned. Noticed level 3 fast speed door tight in the close so adjusted door shoe to free up.Tried to simulate fault but could not. Ran lift and checked operation.to be closed out at $0 cost
MSA-DTAG | WA5565856 | 3 | Gilmour & Jooste Electrical | Front Counter - Lights above counter causing issues with glare on screens | Electrical | Lighting, Internal | 41.86 | Pass | Pass | 0 | 0 | 3.2 | 2022-06-22 12:01 | 2022-06-29 17:00 | 2022-06-28 07:00 | 2022-06-29 17:00 | 2022-06-28 10:12 |  |  | Lights are causing staff to experience headaches due to being to bright. Disconnected 1x light above desk. Will trial this for now.
MSA-DTWD | WA5694376 | 2 | M Construction (WA) | The exit door on the west of U015 needs repairing as dangerous metal trim is hanging off the lock | Building | Doors | 752.25 | Pass | Pass | 0 | 0 | 3.2 | 2022-08-05 09:38 | 2022-08-10 17:00 | 2022-08-10 10:30 | 2022-08-10 17:00 | 2022-08-10 13:42 |  | WACCES | Have Secure new trims and remove overhang trim to make safe. Im recommending that this door be replaced, will move forward with quote.
MSA-DCA | WA5799324 | 1 | Earth & Water Pty Ltd | RETROSPECTIVE WORK ORDER - Wetlands - Retic system water meter vandalised-Att 23/8 | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 0 | 0 | 3.1833 | 2022-08-23 07:00 | 2022-08-23 17:00 | 2022-08-24 08:19 | 2022-08-23 17:00 | 2022-08-24 11:30 | 1 |  | Nigel and Logan attended site. Wetlands Water meter vandalised. Removed and will replace
MSA-DFES | WA5587825 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Applied training grounds - Overflowing drain - toilets' are blocked | Plumbing & Drainage | Toilets/Cisterns | 392.5 | Pass | Fail | 0 | 0 | 3.1667 | 2022-07-07 11:02 | 2022-07-07 13:02 | 2022-07-07 12:50 | 2022-07-07 15:02 | 2022-07-07 16:00 |  |  | Arrived on site and singed in went toilet located Appiled traing grounds used drain machine down sewer on old block, where the toilet use to be pulled out a rag. Then used drain machine down back of new toilets hit something with 6.5 rods down went to pump pit and tested everything thing did paper test everything was fine
MSA-DCA | WA6231176 | 2 | GPS Plumbing & Gas Services PtyLtd | Toilet leaking at base | Plumbing & Drainage | Toilets/Cisterns | 389.37 | Pass | Pass | 0 | 0 | 3.1667 | 2022-11-18 14:25 | 2022-11-23 17:00 | 2022-11-22 10:10 | 2022-11-23 17:00 | 2022-11-22 13:20 |  |  | Uninstalled toilet, replaced toilet rubber seals, cement toilet back in and re silliconed around toilet flushed multiple times
MSA-DCA | WA5628561 | 3 | TK Elevator Australia Pty Ltd | Ground Floor - Lift - G Button is loose | Lifts | Lifts |  | Fail | Fail | 5 | 5 | 3.15 | 2022-07-15 14:55 | 2022-07-22 17:00 | 2022-08-25 10:50 | 2022-07-22 17:00 | 2022-08-25 13:59 |  |  | Replaced car ground and level 1 call button.Work order is not chargeable, there will be no invoice
MSA-DCA | WA5794949 | 0 | TK Elevator Australia Pty Ltd | Ground Floor - Harry butler center - Lift - Lift is not operational - See notes below | Lifts | Lifts |  | Pass | Fail | 0 | 0 | 3.15 | 2022-08-25 08:56 | 2022-08-25 10:56 | 2022-08-25 10:50 | 2022-08-25 12:56 | 2022-08-25 13:59 |  |  | Found wire trapped in bottom landing indicator that shorted to ground and blown fuse in cabinet for LAN _EXT which was putting lift landing calls out of service.Purchased new fuses and installed. Lift all operating correctly. Replaced ground floor call button. Replaced car ground and level 1 call button.Lift left in service.
MSA-DTWD | WA5400532 | 2 | Techworks Electrical | cutting room has two broken 3 phase power outlets, Bandsaw, mortice m/c | Electrical | General Electrical | 859.94 | Pass | Pass | 0 | 0 | 3.1167 | 2022-05-10 11:22 | 2022-05-13 17:00 | 2022-05-10 12:00 | 2022-05-13 17:00 | 2022-05-10 15:07 |  |  | Inspected broken plugs, sourced replacement plugs. Returned to site and replaced. Some fault finding on machine was required to get machine to work
MSA-DTWD | WA6190939 | 2 | AHS Services WA Pty Ltd (Anchor) | No water coming out of hot water tap | Plumbing & Drainage | Water | 395.67 | Pass | Pass | 0 | 0 | 3.1167 | 2022-11-16 11:41 | 2022-11-21 17:00 | 2022-11-21 07:00 | 2022-11-21 17:00 | 2022-11-21 10:07 |  |  | Changed over hot and cold basin tap set
MSA-DCA | WA5385984 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Conservation Lab - first floor -Hot water in the lab area is coming out lukewarm | Electrical | General Electrical | 345.35 | Pass | Pass | 0 | 0 | 3.1 | 2022-04-29 14:05 | 2022-05-04 17:00 | 2022-05-02 14:13 | 2022-05-04 17:00 | 2022-05-02 17:19 |  |  | Attended site gained access and carried out inspection of domestic hot water pump. Carried our reset of pump and monitor operation. Confirmed equipment restarted and is now providing hot water to labs. Checked and confirmed fault had cleared at BMS. All OK. Work area left tidy.
MSA-DFES | WA5092108 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | second floor - ladies toilet - second cubicle - broken seat | Plumbing & Drainage | Toilets/Cisterns | 705.08 | Pass | Pass | 0 | 0 | 3.1 | 2022-01-27 14:33 | 2022-02-01 17:00 | 2022-01-31 07:00 | 2022-02-01 17:00 | 2022-01-31 10:06 |  |  | Replaced toilet seat in ladies bathroom floor 2 second cubicle or the right test and not moving
MSA-DTWD | WA6708250 | 1 | Precise Air Group | Air con button has broken no air con in the room - customer has a replacement switch | Air Conditioning | Ducted Split System | 208.34 | Pass | Pass | 0 | 0 | 3.1 | 2023-03-13 14:36 | 2023-03-14 17:00 | 2023-03-14 07:00 | 2023-03-14 17:00 | 2023-03-14 10:06
MSA-DTWD | WA5608336 | 0 | SCAVENGER SUPPLIES PTY LTD | fire pumps are running | Fire Protection Services | Fire Protection - Monitor System | 2197.96 | Pass | Fail | 0 | 0 | 3.0833 | 2022-07-13 08:02 | 2022-07-13 10:02 | 2022-07-13 09:16 | 2022-07-13 12:02 | 2022-07-13 12:21 |  |  | COMPLETED- SITE CONFIRMS EXTENSIVE WORK REQUIRED AND DEEMED TOO EXPENSIVE AT THIS STAGEFire ring main losing pressure leak in system,BRAF APPROVEDCLAIM CLOSED-phil porter contacted re further quote as leak could not be detected.
MSA-DTWD | WA6544683 | 2 | AWB Co. | The light in the anti-room were the sink is in the two rooms are not working. | Electrical | Lighting, Internal | 530.005 | Pass | Pass | 0 | 0 | 3.0667 | 2023-02-10 16:07 | 2023-02-15 17:00 | 2023-02-14 09:30 | 2023-02-15 17:00 | 2023-02-14 12:34
MSA-DTWD | WA5101700 | 2 | AHS Services WA Pty Ltd (Anchor) | Female staff toilets not flushing fully | Plumbing & Drainage | Toilets/Cisterns | 387.6727 | Pass | Pass | 0 | 0 | 3.0667 | 2022-02-03 13:55 | 2022-02-08 17:00 | 2022-02-08 13:20 | 2022-02-08 17:00 | 2022-02-08 16:24 |  |  | E block female staff toilets replaced outlet rubber and float valve now to fix the problem
MSA-DTWD | WA5094881 | 1 | Precise Air Group | A Block - Level 1 -A51 - AC not getting to temp setting, checked BMS - see details below | Air Conditioning | Room Air Conditioners | 282.575 | Pass | Pass | 0 | 0 | 3.0333 | 2022-01-31 14:50 | 2022-02-01 17:00 | 2022-02-01 08:00 | 2022-02-01 17:00 | 2022-02-01 11:02 |  |  | Investigated A block temperature issues. Accessed BMS and checked AHU. Found CHWV manualled to 25%. Drove valve open and closed and checked operation. Set to auto and checked operation/ temperatures throughout the day
MSA-DTWD | WA5018149 | 1 | Falcetta Plumbing and Gas | Front north side boundary - External water leak appeared ** See notes | Plumbing & Drainage | Water | 327.56 | Pass | Pass | 0 | 0 | 3.0167 | 2022-01-14 09:31 | 2022-01-17 17:00 | 2022-01-17 09:29 | 2022-01-17 17:00 | 2022-01-17 12:30 |  |  | repaired 20mm blueline poly
MSA-DTAG | WA4983621 | 3 | PPM Project Painting & Maintenance | Ground - Wall next to foot path outside RHS courthouse - graffiti on wall | Cleaning | Graffiti | 495 | Pass | Pass | 0 | 0 | 3 | 2021-12-23 11:11 | 2022-01-04 17:00 | 2022-01-04 08:00 | 2022-01-04 17:00 | 2022-01-04 11:00 |  |  | Remove graffiti
MSA-DTWD | WA5010257 | 2 | AWB Co. | Multiple fluro lights are faulty - see notes below | Electrical | Lighting, Internal | 344.08 | Pass | Pass | 0 | 0 | 3 | 2022-01-12 11:42 | 2022-01-17 17:00 | 2022-01-17 08:30 | 2022-01-17 17:00 | 2022-01-17 11:30 |  |  | Attended site, signed in, completed jsa,spoke to fm about job, set up work area , isolated lighting circuits ,removed old starters and tubes and replaced with new , used 30 tubes and starters in total (20 supplied by site) , disposed of old tubes in allocated disposal boxes on site, re energised circuits, tested lights and all working as intended , completed paperwork,cleaned up, packed up, signed out , **job completed **
MSA-DTAG | WA5017130 | 0 | Sapio Pty Ltd | Security - Cameras are not connecting to the network - urgent | Security | CCTV Surveillance | 370 | Pass | Pass | 0 | 0 | 3 | 2022-01-13 10:41 | 2022-01-13 12:41 | 2022-01-13 11:00 | 2022-01-13 14:41 | 2022-01-13 14:00 |  |  | Attended site and found one server in Custody Hallway that was not powered on after power fail. Reconfigured BIOSsettings to power on if power loss occurs in future. Tested and working. Restored services and clients all logged back inokay.
MSA-DCA | WA5018337 | 0 | Critical Fire Protection & Training | external water tanks - auto fill value on external water tank which feeds the mists pump is passing | Fire Protection Services | Fire Protection - Monitor System | 321.8 | Pass | Pass | 0 | 0 | 3 | 2022-01-14 11:12 | 2022-01-14 13:12 | 2022-01-14 12:00 | 2022-01-14 15:12 | 2022-01-14 15:00 |  |  | Attended site to investigate tank on mist system overflowing.After investigation we determined that the tank was over flowing due to finger straineron infill valve being blocked.Removed finger strainer and cleaned strainer gauze.Put valve back together.Tested, all okay on departure.
MSA-DTWD | WA5038497 | 1 | Equans Mechanical Services Australia | Block 8 - First Floor - Plant Room - A/C 20 not running | Air Conditioning | Room Air Conditioners | 538.95 | Fail | Fail | 0 | 0 | 3 | 2022-01-17 13:46 | 2022-01-18 17:00 | 2022-01-19 11:15 | 2022-01-18 17:00 | 2022-01-19 14:15 |  |  | Gained access to AC unit. Investigated and found stage 2 compressor fuses removed and unit off at interval isolator. Found no tags attached and carried out full integrity check before starting unit. Started unit and found all to be running. Found after some time, compressors tripping out on HP. Checked and found all condenser fans operating but condenser deck in very bad state. Found with both compressors running, and an ambient temperature of +43deg condenser unit unable to cope. Isolated stage 2 compressor and restarted unit. Checked refrigerant pressures and found to be below HP safety setting. Unit running and cooling area. Informed John of outcomes and was requested to submit to get pricing to replace condenser unit.
MSA-DTWD | WA5053291 | 2 | AWB Co. | External - Garden pump - new pump to be connected | Electrical | General Electrical | 266.88 | Pass | Pass | 0 | 0 | 3 | 2022-01-18 14:46 | 2022-01-21 17:00 | 2022-01-19 09:15 | 2022-01-21 17:00 | 2022-01-19 12:15 |  |  | Job complete
MSA-DTAG | WA5067744 | 2 | Australian HVAC Services Pty. Ltd. | Evaporative Cooling - Areas within the building that are uncomfortably warm | Air Conditioning | Evaporative Coolers | 328.89 | Pass | Pass | -1 | -1 | 3 | 2022-01-19 10:49 | 2022-01-24 17:00 | 2022-01-20 08:00 | 2022-01-24 17:00 | 2022-01-20 11:00 |  |  | Arrived on-site, spoke with on-site representative who informed me that common areas throughout the building were slightly uncomfortable yesterday afternoon. Proceeded to BMS room where I accessed building BMS A/C controls, setpoints okay. proceeded to check filters throughout airhandlers as well as perform visual inspections. Proceeded to chiller compound, carried out operational testing on chiller & found chiller to be fully functional. Temperatures are as follows.Evap entering temperature- 16.2cEvap leaving temperature 6.335c ambient conditions24c indoor conditions.Cleaned chiller coils to ease load on condenser, issue is high ambient temps putting large strain on unit, chiller is struggling to maintain temperature, this is due to 42c+ ambient temperatures. Spoke to on-site representative who agreed to remove cooling schedule on chilled water plant & allow chiller to run on all day events, this will greatly improve the systems ability to bring temperatures down overnig
MSA-DTWD | WA5085633 | 3 | Schindler Lifts Australia | Lift 4 - Lift 4 doors sticking 1/2 way open | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 3 | 2022-01-21 09:28 | 2022-01-31 17:00 | 2022-01-21 15:41 | 2022-01-31 17:00 | 2022-01-21 18:41 |  |  | When responding to the callback dated 21.01.2022, the Schindler Technician found that one of the components had been affected byan external influence. Mains power failure/fluctuation to the equipment was identified . Following our attendance, the equipmentwas left in service. Works due to external influence are not covered under the terms of your maintenance agreement, thereforethis site visit will be chargeable
MSA-DTWD | WA5086876 | 2 | AHS Services WA Pty Ltd (Anchor) | D Block - Cafe - floor drains backing up, not draining | Plumbing & Drainage | Drainage | 944.105 | Fail | Fail | 0 | 0 | 3 | 2022-01-21 15:02 | 2022-01-27 17:00 | 2022-01-28 12:00 | 2022-01-27 17:00 | 2022-01-28 15:00 |  |  | unblocked drain and repaired dt mound and grate
MSA-DTWD | WA5099213 | 2 | AWB Co. | P Block yard west - Concrete pit and lid caved in and presenting trip hazard | Electrical | General Electrical | 674.55 | Pass | Pass | 0 | 0 | 3 | 2022-02-01 16:41 | 2022-02-04 17:00 | 2022-02-04 07:00 | 2022-02-04 17:00 | 2022-02-04 10:00 |  |  | Attended site and signed in. Completed JSA. Went to work area and found smashed pit that needed replacing. Measured up pit to determine what size pit we needed. Rang up MM Midland to see if they had any pits in stock, they had. Went to MM to pick up pit and lid. Returned to site. Dug around old pit deep enough so that we could fit new one in. Put new Pit in hole and back filled sand and cleaned up work area, completed paperwork and signed out,job completed
MSA-DFES | WA5101734 | 2 | Water2water Pty Ltd | Kitchen - ZIP Boil Cold water not working | Plumbing & Drainage | Water | 673.23 | Pass | Pass | 0 | 0 | 3 | 2022-02-03 14:13 | 2022-02-08 17:00 | 2022-02-08 09:00 | 2022-02-08 17:00 | 2022-02-08 12:00 |  |  | Zip unit removed and brought back to workshop to be repaired, unable to diagnose and repair onsite.Removed to workshop after installing new pump - tested found cold tank Level Sensors faulty replaced returned unit to site reinstalled A40310111 Zip Hydrotap
MSA-DCA | WA5104652 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS Alarm - Chiller Host 1 Fan 1 BSD Fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 507.58 | Pass | Pass | 0 | 0 | 3 | 2022-02-04 03:45 | 2022-02-04 05:45 | 2022-02-04 04:30 | 2022-02-04 07:45 | 2022-02-04 07:30 |  |  | works completed, looking into programming changes to VSD alarms.
MSA-DTWD | WA5105460 | 2 | Equans Mechanical Services Australia | Building 5 - Level 3 - A357 - Evap cooler noisy on high speed | Air Conditioning | Room Air Conditioners | 287.79 | Fail | Fail | 12 | 12 | 3 | 2022-02-04 11:08 | 2022-02-09 17:00 | 2022-05-04 09:00 | 2022-02-09 17:00 | 2022-05-04 12:00 |  |  | INVESTIGATED NOISE AND FOUND LOOSE TAPE IN VENTS - REMOVED - ALL GOOD
MSA-DCA | WA5106001 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Alarm P0 AC 1 Effecting Galleries 1 and 6 | Air Conditioning | Cooling Tower | 507.58 | Pass | Pass | 0 | 0 | 3 | 2022-02-05 18:14 | 2022-02-05 20:14 | 2022-02-05 19:00 | 2022-02-05 22:14 | 2022-02-05 22:00 |  |  | System running full cooling, due to high ambient alarm hasn't cleared. Temperature is within required temp range but alarm perimeters require adjusting to stop alarms.
MSA-DFES | WA5108357 | 1 | MALCOLM THOMPSON PUMPS PTY LTD | Bottom damn - pumps are not working - 1 foot valve not retaing waters - 2 pump wont turn on | Mechanical Services | Pumps |  | Pass | Pass | 0 | 0 | 3 | 2022-02-08 13:36 | 2022-02-09 17:00 | 2022-02-08 14:00 | 2022-02-09 17:00 | 2022-02-08 17:00 |  |  | job completed - refit foot valve & check valve, fill system & check pumps
MSA-DTWD | WA5109123 | 3 | AWB Co. | A Block - Levels 1, 2, 3 - replace light not working A Block Corrisors Level 1..2 | Electrical | General Electrical | 713.76 | Pass | Pass | -1 | -1 | 3 | 2022-02-09 07:20 | 2022-02-15 17:00 | 2022-02-10 09:30 | 2022-02-15 17:00 | 2022-02-10 12:30 |  |  | Attended site and signed in. Completed JSA. Inspected and checked out all lights throughout A block. Counted up all lamps out on all floors in corridors. Supply and replaced lamps and starters where needed. Tested all okay. Signed out. Job complete
MSA-DFES | WA5109833 | 2 | Go Doors | Engine bay door 5 - Has a roller pin fell off | Building | Roller Shutters | 1378.6 | Pass | Pass | -1 | -1 | 3 | 2022-02-09 13:32 | 2022-02-14 17:00 | 2022-02-10 13:45 | 2022-02-14 17:00 | 2022-02-10 16:45 |  |  | Works completed
MSA-DTWD | WA5115701 | 1 | Nessco Pressure Systems | Carpentry workshop - Compressed air fittings unsafe - replaced with crimped washer type fixings | Equipment | Compressors, Generators |  | Pass | Pass | 0 | 0 | 3 | 2022-02-11 08:37 | 2022-02-14 17:00 | 2022-02-11 13:00 | 2022-02-14 17:00 | 2022-02-11 16:00 |  |  | replaced 14x hose clamps with OTK type
MSA-DTWD | WA5115711 | 2 | AWB Co. | Both stairwell - refit signage | Building | General Building | 559.95 | Pass | Pass | 0 | 0 | 3 | 2022-02-11 08:44 | 2022-02-16 17:00 | 2022-02-16 08:00 | 2022-02-16 17:00 | 2022-02-16 11:00 |  |  | refit signage as requested
MSA-DCA | WA5116500 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Fault light on chiller two and neither boilers seems to be working | Air Conditioning | Room Air Conditioners | 486.65 | Pass | Pass | 0 | 0 | 3 | 2022-02-11 17:35 | 2022-02-12 17:35 | 2022-02-11 18:00 | 2022-02-12 17:35 | 2022-02-11 21:00 |  |  | Attended callout. Investigated fault on chiller 2. Found thermistor relay in fault and chiller 2 in loss of power supply fault. Reset thermistor relay and cleared fault on chiller 2. Unit started up and monitored operation. Unit operating normally. Completed paperwork.
MSA-DCA | WA5116512 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidity alarm for AC 6 Collection store and SCU Centenary Gallery | Air Conditioning | Room Air Conditioners | 507.58 | Pass | Pass | 0 | 0 | 3 | 2022-02-11 22:18 | 2022-02-12 00:18 | 2022-02-11 23:00 | 2022-02-12 02:18 | 2022-02-12 02:00 |  |  | Attended callout and investigated humidity faults on fcu 6 and ac 6. Fcu 6 cleared shortly after arrival. Fcu 6 floating around 52%. Ac 6 staying under 55%. Checked over ac 6 and fcu 6 for correct operation, all ok. Monitored humidity and completed paperwork
MSA-MRWA | WA5126581 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground floor aircon - blowing hot air | Air Conditioning | Room Air Conditioners | 293.025 | Pass | Pass | 0 | 0 | 3 | 2022-02-14 08:55 | 2022-02-15 17:00 | 2022-02-14 09:00 | 2022-02-15 17:00 | 2022-02-14 12:00 |  |  | Travelled to site and signed in. Located ground floor offices and temps were at 24.5 and set point 24. Accessed Innotech controller and adjusted set points to 22 degrees. Monitored temps, temps began to drop. Ground floor area is now cooler and set points at 22 degrees.
MSA-DTWD | WA5127719 | 1 | Falcetta Plumbing and Gas | plant room G200 - break in hot water line | Plumbing & Drainage | Water | 377.56 | Pass | Pass | 0 | 0 | 3 | 2022-02-14 13:54 | 2022-02-15 17:00 | 2022-02-14 15:00 | 2022-02-15 17:00 | 2022-02-14 18:00 |  |  | isolated damaged pipe and brazed to repair
MSA-DCA | WA5142315 | 1 | EQUANS Mechanical Services (WA) Pty Limited | plantroom - Investigate fault on AC3 | Air Conditioning | Room Air Conditioners | 345.35 | Pass | Pass | 0 | 0 | 3 | 2022-02-16 14:21 | 2022-02-17 17:00 | 2022-02-16 14:30 | 2022-02-17 17:00 | 2022-02-16 17:30 |  |  | Attended site, signed in and accessed the bms. Found ahu 3 supply temperature at 28 degrees. Accessed the mechanical plantroom ahu 3 and checked the chilled watervalve. Drove the valve from the bms and found it to be seized. Removed the actuator and forced the valve to 50% open to allow for some cooling. Removed the insulation from the valve and recorded details to quote for replacement.
MSA-DTWD | WA5186555 | 2 | AWB Co. | E Block - Ground - Cafeteria kitchen and female staff toilet -Lights need repair or replacing | Electrical | General Electrical | 558.98 | Pass | Pass | 0 | 0 | 3 | 2022-02-22 08:32 | 2022-02-25 17:00 | 2022-02-23 07:00 | 2022-02-25 17:00 | 2022-02-23 10:00 |  |  | Attended site signed in. Completed jsa and liased with site FM about works at campus. 4 lights faulty in total. Sourced 4 new lights. Isolated circuits to replace fittings. Tested and confirmed working, also set 4 lights on different colour setting as specified by cafe staff. All tested and working.****job completed****
MSA-DTWD | WA5188843 | 2 | Techworks Electrical | Multiple lights are not working | Electrical | Lighting, Internal | 680.39 | Pass | Pass | -1 | -1 | 3 | 2022-02-23 11:58 | 2022-02-28 17:00 | 2022-02-24 09:30 | 2022-02-28 17:00 | 2022-02-24 12:30 |  |  | Replaced tubes and starters in top floors of a block classrooms
MSA-DTWD | WA5188846 | 2 | Techworks Electrical | Multiple lights are not working | Electrical | Lighting, Internal | 680.39 | Pass | Pass | -1 | -1 | 3 | 2022-02-23 12:01 | 2022-02-28 17:00 | 2022-02-24 12:30 | 2022-02-28 17:00 | 2022-02-24 15:30 |  |  | Replaced tubes and starters throughout a block
MSA-DTAG | WA5189723 | 3 | Automatic Fire Protection (ARA) | Basement FIP - Technician to attend at 07.00am on Saturday 26 February 2022 to isolate FIP see notes | Fire Protection Services | Fire Protection - Monitor System | 439.32 | Pass | Pass | -1 | -1 | 3 | 2022-02-24 08:08 | 2022-03-03 17:00 | 2022-02-26 07:00 | 2022-03-03 17:00 | 2022-02-26 10:00 |  |  | 26/2/22 JNIsolated zone 12 for contractor works.Returned 10am to deisolate.
MSA-DTWD | WA5190222 | 2 | Techworks Electrical | shed 1 & 2 - pendant power points not working | Electrical | General Electrical | 303.51 | Pass | Pass | -1 | -1 | 3 | 2022-02-24 12:02 | 2022-03-01 17:00 | 2022-02-25 08:30 | 2022-03-01 17:00 | 2022-02-25 11:30 |  |  | Began investigation into shed power, on arrival found no pendants had power, found the EM stops to be activated in the board, after resetting the EM stops, I went through every pendant gpo and tested for correct polarity, every pendant tested good, then went to the furthest pendant of each circuit and tested for EFL and RCD trip tests, again all pendants tested good with satisfactory results and nothing indicating incorrect wiring or operation or damaged cables etc. Highly likely the problem is people pressing the EM stops around the classrooms, they are the basic push and twist to release kind, not needed the key to reset, furthermore once these EM stops have been pushed, even after resetting the EM stop itself, you need to go to the switchboard where there are EM resets there as well. Just by looking into the DB, all the rcds are on and there are no methods of seeing if a EM stop has been pushed, so just by looking into the db you cannot tell. But the contractors behind the escutch
MSA-DCA | WA5192078 | 0 | Precise Air Group | Down stairs in the Maj - air con faulty - see notes | Air Conditioning | Room Air Conditioners | 486.66 | Pass | Fail | 0 | 0 | 3 | 2022-02-25 11:26 | 2022-02-25 13:26 | 2022-02-25 13:00 | 2022-02-25 15:26 | 2022-02-25 16:00 |  |  | Attended site and completed pre start paperwork and signed in. Located Basement plantroom and inspected package system. Found stage 2 to be operating and stage 1 tagged out with a compressor down to earth. Found a supply air temp of 14c and a return of 22c. 2c short of a 10k split due to system operating on a single stage. Space temp is around 21.5 c . Checked condenser water pump and found operating. Checked fault history on bms and found no faults recorded at 8pm on the 24/2. Only fault recorded relating to the Basement equipment was "ccw failure to follow command" fault occurred at 12 20pm on the 25/2 .This was automatically reset and fault cleared. Controls inspection maybe required. All mechanical equipment related to package system 1 ran with out fault for the duration of the visit. Completed paperwork and packed up equipment. Left unit running with a supply air of 14.4c X
MSA-DTWD | WA5193722 | 2 | AHS Services WA Pty Ltd (Anchor) | A353 - Male toilet - LH basin no water / RH basin tap spins around | Plumbing & Drainage | Materials | 367.605 | Pass | Pass | 0 | 0 | 3 | 2022-02-25 13:27 | 2022-03-02 17:00 | 2022-03-01 08:00 | 2022-03-02 17:00 | 2022-03-01 11:00 |  |  | Inspected found seized taps searched for isolation, cut away corroded tapware installed two new pillar taps tested good
MSA-DTWD | WA5201441 | 2 | AWB Co. | Metal Fab 2 - Drop pendant has no power | Electrical | General Electrical | 409.6 | Pass | Pass | -1 | -1 | 3 | 2022-03-02 15:06 | 2022-03-08 17:00 | 2022-03-04 10:00 | 2022-03-08 17:00 | 2022-03-04 13:00 |  |  | Attended site signed in completed jsa. Spoke with site fm about faulty gpo. Gpo had power so just replaced gpo with new from wholesaler. Works good and tests fine. ***job completed***
MSA-DCA | WA5204448 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - Ground Floor - Plant room - chemical dosing pump leak | Air Conditioning | Room Air Conditioners | 389.94 | Fail | Fail | 1 | 1 | 3 | 2022-03-04 10:50 | 2022-03-04 12:50 | 2022-03-10 08:00 | 2022-03-04 14:50 | 2022-03-10 11:00 |  |  | Whilst carring out the hvac maintenance - noticed a chemical spill near the RO Plant. Leak was coming from the inhibiter dosing pump. Notified Hydrochem to replace the faulty pump. Collected cleaning gear from supplier. Drove to site and carried out floor cleans around the RO Plant. Will need to be moped and bleached around the floor of the RO Plant as it has stained the floor.
MSA-DTWD | WA5204721 | 2 | M Construction (WA) | R-Block pathway has raised pavers causing trip hazards | Paving & Roadworks | Paving | 324.88 | Pass | Pass | 0 | 0 | 3 | 2022-03-04 12:53 | 2022-03-10 17:00 | 2022-03-10 11:30 | 2022-03-10 17:00 | 2022-03-10 14:30 |  |  | Removed pavers, cut out tree roots and installed pavers.
MSA-DTAG | WA5204739 | 3 | Sapio Pty Ltd | Upper basement network fault | Security | Access Control | 461.87 | Pass | Pass | -1 | -1 | 3 | 2022-03-04 12:59 | 2022-03-14 17:00 | 2022-03-08 09:00 | 2022-03-14 17:00 | 2022-03-08 12:00 |  |  | Found network issues in B1 Network Rack. Put in new patch panel and patched new leads in due toexisting poor cable management. Tested, OK.
MSA-DTWD | WA5207431 | 2 | AWB Co. | S Block - S102 - broken toilet door female toilets | Building | General Building | 506.63 | Pass | Pass | 0 | 0 | 3 | 2022-03-08 13:05 | 2022-03-11 17:00 | 2022-03-10 09:30 | 2022-03-11 17:00 | 2022-03-10 12:30 |  |  | Removed existing broken hinges, replaced and fixed with new on stone partition and hung toilet cubicle door.
MSA-DCA | WA5207628 | 3 | Techworks Electrical | Ground - Auditorium - House Lights in auditorium (Dimmer 1, Circuit 12) - see details below | Electrical | General Electrical | 660.17 | Pass | Pass | 0 | 0 | 3 | 2022-03-08 14:51 | 2022-03-15 17:00 | 2022-03-14 09:30 | 2022-03-15 17:00 | 2022-03-14 12:30 |  |  | Arrived and found lamp holder had cut into cable causing fault while the globe was being replaced. Rewired lamp holder and replaced 8x globes on ground floor seating area that where also out. All working well.
MSA-DTWD | WA5209223 | 3 | AWB Co. | Block E - ground - E400 - 2 x Tagged out sockets from test and tag | Electrical | General Electrical | 600 | Pass | Pass | -1 | -1 | 3 | 2022-03-09 15:31 | 2022-03-16 17:00 | 2022-03-11 09:30 | 2022-03-16 17:00 | 2022-03-11 12:30 |  |  | Attended site and signed in,completed jsa,spoke to fm about job, went to e block and located plugtops and gpo needing replacing, took down part numbers, went to wholesaler to pick up parts, returned to site, replaced both plug tops and put test tags on them , isolated power, removed gpo and replaced with new as old one was cracked , re energised circuit and tested gpo, all working as intended , cleaned up, packed up, completed paperwork, signed out Job completed
MSA-DTWD | WA5209240 | 2 | Equans Mechanical Services Australia | Arcus Freestanding Fridge not cooling | Refrigeration | Refrigerators | 464.3 | Pass | Pass | -1 | -1 | 3 | 2022-03-09 15:56 | 2022-03-14 17:00 | 2022-03-10 11:00 | 2022-03-14 17:00 | 2022-03-10 14:00 |  |  | Investigated and Fridge to be reaching set point but taking a long time due to student usage. Found condenser coil to be slightly oily and chemically cleaned. Checked operation and found to be ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DCA | WA5215445 | 0 | Techworks Plumbing | Jubilee building - ground floor - 2x blocked toilets | Plumbing & Drainage | Drainage | 1290.39 | Pass | Pass | 0 | 0 | 3 | 2022-03-10 12:23 | 2022-03-10 14:23 | 2022-03-10 12:30 | 2022-03-10 16:23 | 2022-03-10 15:30 |  |  | Unblocked drain and camera inspected to find misalignment of pvc pipe
MSA-DTWD | WA5216301 | 1 | Precise Air Group | Clarkson - Classrooms 4 & 5 have no airconditioning | Air Conditioning | Room Air Conditioners | 329.67 | Pass | Pass | 0 | 0 | 3 | 2022-03-11 09:11 | 2022-03-14 17:00 | 2022-03-11 10:30 | 2022-03-14 17:00 | 2022-03-11 13:30 |  |  | Inspected Mitsubishi vrf systems x 2. Classroom 4 found to be supplying 15 degree air as specified found but the air discharge and return short cycling back to return air due to directional vanes pointing straight up. Unsure as to this cause possibly Adjusted by others? Adjusted air directions to circulate rooms accordingly. Classroom windows fully open compounding temp issues with high ambient and humidity conditions. Return air dampers sitting at approx 50 %. Need to be altered to 100% for maximum airflow across coil. To be quoted.Classroom 5 found to have blocked return air filters. Adjusted airflow direction as with room 4 to maximise cool air coverage. Return air dampers also at approximately 50 % and should be wound open to maximum to increase air return to coil. To be quoted. 15 degree air off coil as specified. Both rooms sitting at 26_27 degrees before adjustments. Rooms now sitting on 22_23 degrees. Pack up sign off.
MSA-DCA | WA5231345 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Main Building - Level 1 - Main Auditorium - Stage step strip-lighting has been damaged by stage trap | Electrical | General Electrical | 323.79 | Pass | Pass | 0 | 0 | 3 | 2022-03-15 10:45 | 2022-03-16 17:00 | 2022-03-15 12:00 | 2022-03-16 17:00 | 2022-03-15 15:00 |  |  | Attend site at 1200. Investigate why LED step strip isn’t working. Was found that the cable had been worn away by the LED strip enclosure rubbing, aswell as being previously disconnected at current limiter. Reconnected at limiter and rerouted cable leading into strip enclosure, so that it would no longer rub and wear away at cable. I reconnected strip and it is all now working as should. Informed staff and left site at 1500.
MSA-DTWD | WA5238828 | 3 | Techworks Plumbing | Male toilet - Button wont release from flush position. Wont flush water | Plumbing & Drainage | Toilets/Cisterns | 341.01 | Pass | Pass | -1 | -1 | 3 | 2022-03-16 09:21 | 2022-03-23 17:00 | 2022-03-17 06:00 | 2022-03-23 17:00 | 2022-03-17 09:00 |  |  | Attended site and met Martin who let me in and showed me the urinal that wouldn't flush Pulled apart the urinal flush plate to find a little spacer that's supposed to push in and flush the toilet but due to wear and tear, that spacer was too short and didn't reach any more Made a new spacer out of copper that was slightly longer and this made the button work perfectly Put everything back together and cleaned up Did paper work and left site
MSA-DTWD | WA5238829 | 1 | Falcetta Plumbing and Gas | disable toilet - Water leaking through ceiling onto toilet bowl | Plumbing & Drainage | Water | 322.56 | Pass | Pass | 0 | 0 | 3 | 2022-03-16 09:11 | 2022-03-17 17:00 | 2022-03-16 13:00 | 2022-03-17 17:00 | 2022-03-16 16:00 |  |  | repaired floor waste penetration above bathroom
MSA-DFES | WA5239445 | 3 | AWB Co. | Kitchenette - Kitchen cabinet shows extensive Mould growth. - see notes below | Carpentry | Timber (all types) | 342.63 | Pass | Pass | 0 | 0 | 3 | 2022-03-16 12:03 | 2022-03-23 17:00 | 2022-03-22 07:00 | 2022-03-23 17:00 | 2022-03-22 10:00 |  |  | Checked all pipes for leaks in kitchen cabinet, cleaned all mould and installed two vents in cupboard doors.
MSA-DTWD | WA5239665 | 3 | AWB Co. | Block 10 - Ground - Cleaners room - Exhaust fan broken | Electrical | General Electrical | 534.65 | Pass | Pass | 0 | 0 | 3 | 2022-03-16 14:09 | 2022-03-23 17:00 | 2022-03-22 10:00 | 2022-03-23 17:00 | 2022-03-22 13:00 |  |  | Attended site signed in completed jsa. Spoke with john site fm about faulty fan in cleaners room. Had waiting time to turn circuit off as staff needed lighting. Sourced new fan as old one was faulty. Fan replaced and now works perfect.**job completed**
MSA-DCA | WA5257407 | 2 | Critical Fire Protection & Training | Main building - stage door FIP - EWIS audio fault on FIP - level 3 zone 7 | Fire Protection Services | Fire Protection - Monitor System | 429 | Pass | Pass | 0 | 0 | 3 | 2022-03-17 11:50 | 2022-03-22 17:00 | 2022-03-21 07:00 | 2022-03-22 17:00 | 2022-03-21 10:00 |  |  | Faulty EWIS connection in ceiling spacerectified
MSA-DTWD | WA5270472 | 1 | Equans Mechanical Services Australia | Unit 7 - Ground - Kitchen - Freezer door won’t close/lock properly | Air Conditioning | Room Air Conditioners | 659.42 | Fail | Fail | 2 | 2 | 3 | 2022-03-18 08:08 | 2022-03-21 17:00 | 2022-04-06 11:30 | 2022-03-21 17:00 | 2022-04-06 14:30 |  |  | FITTED NEW HINGE
MSA-DTWD | WA5270997 | 2 | Damian Rak Electrical Pty Ltd | BLD 837A - Pool shed - Faulty Power points | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 3 | 2022-03-18 09:05 | 2022-03-23 17:00 | 2022-03-23 08:00 | 2022-03-23 17:00 | 2022-03-23 11:00 |  |  | job copmleted - replaced GPO
MSA-DTWD | WA5276986 | 3 | GRAFFITI FORCE PTY LTD | Ground - Walls & doors - Graffiti on walls and doors, majority William street side | Cleaning | Graffiti | 529.68 | Pass | Pass | -1 | -1 | 3 | 2022-03-18 13:06 | 2022-03-25 17:00 | 2022-03-21 07:00 | 2022-03-25 17:00 | 2022-03-21 10:00 |  |  | removal of graffiti from walls and doors, majority williams street side
MSA-DTAG | WA5278175 | 3 | OCS SERVICES PTY LTD | Retrospective Work Order -Full disinfectant Covid 19 clean required in JSO office, room 3.10 & meeti | Cleaning | Hazardous Materials |  | Pass | Fail | 0 | 0 | 3 | 2022-03-17 17:30 | 2022-03-24 17:00 | 2022-03-24 17:00 | 2022-03-24 17:00 | 2022-03-24 20:00 | 1 |  | JSO office full clean
MSA-DCA | WA5285719 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Hackett Hall - Level 3 - Plant Room 6 - please see details below | Air Conditioning | Room Air Conditioners | 931.025 | Pass | Pass | 0 | 0 | 3 | 2022-03-21 09:51 | 2022-03-22 17:00 | 2022-03-22 13:00 | 2022-03-22 17:00 | 2022-03-22 16:00 |  |  | Attended site, signed and accessed plantroom 6 - ahu 05-01. Checked and tested the humidifier and found working correctly. Found the ahu pre filters blocked.Filter require replacement as soon as possible. Ordered new pre filter, will install once arrive.
MSA-DCA | WA5286223 | 2 | Precise Air Group | Main Building - Plantroom - Cooling tower 1 fan is very noisy | Air Conditioning | Room Air Conditioners | 329.67 | Pass | Pass | 0 | 0 | 3 | 2022-03-21 13:34 | 2022-03-24 17:00 | 2022-03-24 10:00 | 2022-03-24 17:00 | 2022-03-24 13:00 |  |  | Attended site and gained access to cooling towers, foundcooling tower one belts noisy. After further inspectionfound the motor was off level. Isolated cooling tower andtried to re align motor but was unable to due to adjustmentbolts being seized. Lubricated pulley and test, noise hadgone. Will continue to monitor on maintenance. Recommendreplacing motor as it is very old and past it’s lifeexpectancy.
MSA-DFES | WA5286225 | 1 | Critical Fire Protection & Training | Pillar hydrant at rear of Station - unable to turn off and leaking | Fire Protection Services | Fire Protection - Monitor System | 814.6 | Fail | Fail | 0 | 0 | 3 | 2022-03-21 13:37 | 2022-03-22 17:00 | 2022-03-24 07:00 | 2022-03-22 17:00 | 2022-03-24 10:00 |  |  | Attend site and drain down the system, remove existing hydrant landing valves, replacewith new, refill system and test.
MSA-DCA | WA5286332 | 2 | Techworks Electrical | Outside / front entrance - Ground floor - Outside Gantry – Ceiling LED light cover needs replacement | Electrical | Lighting, External | 652.82 | Pass | Pass | 0 | 0 | 3 | 2022-03-21 14:51 | 2022-03-24 17:00 | 2022-03-23 06:00 | 2022-03-24 17:00 | 2022-03-23 09:00 |  |  | Identified and sourced new led baton with diffuser.isolated and replaced light.re-energised circuit, tested and commissioned all of the above works for correct operation.
MSA-DCA | WA5286397 | 1 | Critical Fire Protection & Training | Alexander Library Building - Plant room - detectors, L4D040 and L1D022,to be investigated -see notes | Fire Protection Services | Fire Protection - Monitor System | 327.3 | Pass | Pass | 0 | 0 | 3 | 2022-03-21 15:36 | 2022-03-22 17:00 | 2022-03-22 08:00 | 2022-03-22 17:00 | 2022-03-22 11:00 |  |  | Attend site investigate reported alarms, checked plant room -note dusty detector caused by AHU fan- left disabled / monitor,.replaced detector within store room beneath stairs- all ok
MSA-DFES | WA5287758 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | OUTSIDE TAPS - small leak for about week but the tap completely fell off | Plumbing & Drainage | Water | 353.21 | Pass | Pass | 0 | 0 | 3 | 2022-03-22 15:33 | 2022-03-25 17:00 | 2022-03-23 10:45 | 2022-03-25 17:00 | 2022-03-23 13:45 |  |  | Attended site for laundry taps by the washing machine leaking upon inspection I have found the taps leaking a combination taps for washing machine and a basin wall set. I have installed new wall tops for the laundry sink and moved the old taps behind washing machine on existing water lines as requested by site officer after I’ve tested everything is working correctly everything is cleaned up packed up
MSA-DTWD | WA5288866 | 1 | AWB Co. | C-Block - CC08 - Dynamometer keeps tripping breaker | Electrical | General Electrical | 313.98 | Pass | Pass | 0 | 0 | 3 | 2022-03-23 14:38 | 2022-03-24 17:00 | 2022-03-24 07:00 | 2022-03-24 17:00 | 2022-03-24 10:00 |  |  | Attended site and signed in. Completed JSA. Located Dyno room and faulty Dyno machine. Turned on and machine went pop. Carried out various tests of continuity and IR. No faults found on motors or cabling. Followed cabling and inspected all circuit boards and controls. Isolated module box 1 by one and eliminated the faulty box.Disconnect and removed faulty circuit board inside front load magnet box. Inspected to see if I could see any burn or blow marks and found the solid state relay bolted to the heatsink to be blown. Tech on site advised the board has been repaired recently. It is possible the heat paste was not replaced and has caused issue. Unable to confirm as the board is not in my hands to be repaired. Site has advised they will send back to Dyno manufacturer. Put all other cables and boxes back together. Signed out. Job complete
MSA-DCA | WA5289664 | 2 | FCT SURFACE CLEANING | Urban Orchard - Ground – external -see details below | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 3 | 2022-03-24 11:34 | 2022-03-29 17:00 | 2022-03-28 09:00 | 2022-03-29 17:00 | 2022-03-28 12:00 |  |  | Graffiti removed
MSA-DFES | WA5289886 | 1 | Critical Fire Protection & Training | Ground hydrant rear of fire station in drill yard - ground hydrant spindle is bird | Fire Protection Services | Fire Protection - Monitor System | 348.75 | Pass | Pass | 0 | 0 | 3 | 2022-03-24 13:50 | 2022-03-25 17:00 | 2022-03-25 08:00 | 2022-03-25 17:00 | 2022-03-25 11:00 |  |  | Attended site to investigate hydrant being difficult to turn off.Tested all hydrants in yard multiple times and all opened and closed withease on each try.Spoke with on site staff and they advised it may be the inground hydrants.Tested in ground hydrant multiple times and it opens and closes easily.Advised on site contact of the findings.All okay on departure.
MSA-DTWD | WA5289970 | 3 | Complete Pest Management Services | Block 10 - ground & classrooms - Mosquitoes in classrooms and drains. | Pest Control | General Pest | 1060.52 | Fail | Fail | 1 | 1 | 3 | 2022-03-24 14:54 | 2022-03-31 17:00 | 2022-04-06 09:00 | 2022-03-31 17:00 | 2022-04-06 12:00 |  |  | Sumps behind cafeteria should be inspected regularly.Treated 24 sumps including one at the gate of the offsite daycare centre.4 cups of Vectobac added to water in each drain and drain surface sprayed inside and out to kill harbouring adultmosquitoes
MSA-MRWA | WA5290835 | 2 | AWB Co. | Corridor outside bathrooms - LED unit in corridor outside bathrooms requires replacement. | Electrical | Lighting, Internal | 652.96 | Pass | Pass | 0 | 0 | 3 | 2022-03-25 12:03 | 2022-03-30 17:00 | 2022-03-29 06:00 | 2022-03-30 17:00 | 2022-03-29 09:00 |  |  | Attended site and signed in, completed jsa,located light in air lock ground level outside toilets, light was damaged , tested for voltage and was 0v, removed old light and replaced with new(sal wide base batten with 4x walldogs) , got into roof space and traced cables back to main roof space, located Contactor on ground floor and found there to be no control circuit voltage, traced cables back to basement board , found relay that was contorting voltage, identified that cable needed to be changed to make light work , changed cable and light was working, told fm that it is a programming issue , fm to contact their lighting control contractor . Completed paperwork, packed up, completed paperwork, signed outJob completed
MSA-DTWD | WA5290958 | 2 | M Construction (WA) | Canteen Kitchen has a broken door floor plate | Flooring | Tiling | 325 | Pass | Pass | 0 | 0 | 3 | 2022-03-25 13:13 | 2022-03-30 17:00 | 2022-03-29 09:00 | 2022-03-30 17:00 | 2022-03-29 12:00 |  |  | Investigated and repaired floor plate in canteen kitchen.
MSA-DCA | WA5294205 | 3 | Techworks Electrical | Building / Warehouse - Repairs to the following lighting issues at this site – see diagram next page | Electrical | General Electrical | 333.06 | Pass | Pass | 0 | 0 | 3 | 2022-03-28 13:57 | 2022-04-04 17:00 | 2022-04-01 08:00 | 2022-04-04 17:00 | 2022-04-01 11:00 |  | WCAPPR | Completed rectifications
MSA-DTAG | WA5297835 | 2 | AWB Co. | Level 10 - Marriage interview Room - Light bulb is not working | Electrical | Lighting, Internal | 352.26 | Pass | Pass | 0 | 0 | 3 | 2022-03-31 13:02 | 2022-04-05 17:00 | 2022-04-04 09:15 | 2022-04-05 17:00 | 2022-04-04 12:15 |  |  | Attended site and signed in, completed jsa,went and signed in at security desk, went upstairs to level 10, spoke with site contact about lighting, total of 6 lights needing repair, left site to pick up parts, returned to site, set up work area, removed old tubes and starters and replaced with new, used a total of 12x 18w tubes and 12x s2 starters, tested all fittings and they are working as intended , disposed of old tubes safely, packed up , completed paperwork,signed outJob complete
MSA-DCA | WA5298162 | 1 | Techworks Plumbing | Level 3 - Female Toilet - Blocked Toilet | Plumbing & Drainage | Toilets/Cisterns | 570.45 | Pass | Pass | 0 | 0 | 3 | 2022-03-31 15:27 | 2022-04-01 17:00 | 2022-04-01 09:30 | 2022-04-01 17:00 | 2022-04-01 12:30 |  |  | Attended site and signed in at security in the basement, called Neil to let him know we were on site to unblock the toilet, went to level 3 female toilets and asked a female to check if there was anyone in there before we entered.Upon inspection we found no blocked toilets, so we called Neil to inform him, he told us to check level 2 also just in case they got the floors mixed up but upon inspection there was no blocked toilets either. We let Neil know and he double checked with other staff he also asked us if we could have a look at a toilet on level 1 that occasionally kept running after flushing.We pulled the flush button apart and inspected what the cause was we found one of the air hoses to be kinked once we unkinked it we put it all together and tested it a few times to make sure it wouldn’t happened again, all test flushes worked fine and problem is resolved.Signed out and completed the paperwork
MSA-DCA | WA5302857 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Collection store 2 showing Humidity alarm A/C 6 | Air Conditioning | Room Air Conditioners | 486.65 | Pass | Pass | 0 | 0 | 3 | 2022-04-04 01:37 | 2022-04-04 03:37 | 2022-04-04 02:00 | 2022-04-04 05:37 | 2022-04-04 05:00 |  |  | Attended site, signed in and accessed the BMS. Found the humidity alarms had cleared automatically. Carried out resets of humidifiers, general operation checks and monitored central plant equipment for correct operation.David Green
MSA-DTWD | WA5303969 | 2 | Techworks Electrical | D-Block - 2nd floor - Marketing area and office has lights not working | Electrical | General Electrical | 777.09 | Pass | Pass | 0 | 0 | 3 | 2022-04-04 13:36 | 2022-04-07 17:00 | 2022-04-06 08:00 | 2022-04-07 17:00 | 2022-04-06 11:00 |  |  | Replaced fluro tubes and starters in D block level 2
MSA-DTWD | WA5305758 | 0 | Precise Air Group | Whole Buildiong - has no air conditioning AGAIN | Air Conditioning | Room Air Conditioners | 329.67 | Pass | Pass | 0 | 0 | 3 | 2022-04-06 07:43 | 2022-04-06 09:43 | 2022-04-06 08:30 | 2022-04-06 11:43 | 2022-04-06 11:30 |  |  | Attended site and completed pre start paperwork and signed in. Accessed chiller 1 and found system out on low flow fault. Checked pumps and found both to operate all ok. Reset fault and Test ran system. Found chiller1 to start and run without fault. Monitored system . Found system to cycle off and on all ok. Switched lead chiller to chiller 2. Chiller/pump started and ran with out fault. Switched lead chiller back to system 1. Suspect the incorrect pump tried to start with chiller 1 causing flow fault. Bms due for upgrade. No further works required. Packed up work equipment and returned keys. Left plant operating.
MSA-DTWD | WA5306235 | 3 | AWB Co. | Foyer and main stair case - Lights not working | Electrical | General Electrical | 885.98 | Pass | Pass | 0 | 0 | 3 | 2022-04-06 11:24 | 2022-04-13 17:00 | 2022-04-13 13:30 | 2022-04-13 17:00 | 2022-04-13 16:30 |  | WCAPPR | All lights installed *** job completed ***
MSA-DCA | WA5306323 | 2 | Critical Fire Protection & Training | Alexander Library Building - Control Room - see details below | Fire Protection Services | Fire Protection - Monitor System | 343.2 | Fail | Fail | 0 | 0 | 3 | 2022-04-06 12:11 | 2022-04-11 17:00 | 2022-04-12 11:00 | 2022-04-11 17:00 | 2022-04-12 14:00 |  |  | Attended site early 12th of April (before trade) investigate EWIS.Fitted in line audio balancer unit as trial/ possible intermittentissue with EWIS module/amp.
MSA-DCA | WA5308981 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Art Gallery of WA - James St-Centenary Gallery-Ground Floor-Gallery 1 - Court Room- BMS alarm - | Air Conditioning | Evaporative Coolers | 612.23 | Pass | Pass | 0 | 0 | 3 | 2022-04-09 17:40 | 2022-04-09 19:40 | 2022-04-09 18:00 | 2022-04-09 21:40 | 2022-04-09 21:00 |  |  | FCU 1 humidifier alarm, attempted to reset. Unit alarming due to maintenance requirment, unit still operating as per normal.Dan s Attended site to recheck the FCU 1 humidifier from the after hours callout. Reset the the maintenance checklist and cleaned the humidifier tank. Jason E
MSA-DCA | WA5308988 | 0 | EQUANS Mechanical Services (WA) Pty Limited | A/C 6 collections store 2 humidifier 1 fault | Air Conditioning | Room Air Conditioners | 612.23 | Pass | Pass | 0 | 0 | 3 | 2022-04-09 22:42 | 2022-04-10 00:42 | 2022-04-09 23:00 | 2022-04-10 02:42 | 2022-04-10 02:00 |  |  | R/O plant water low alarm, reset R/O plant. Dan sAttended site to recheck the R/O plant from the after hours callout. Found the Demineralised pump tripped, reset the pump, recorded the amp draws and monitored the running conditions. Pump working as per normal, if pump fails again it is recommended changing the pump/motor out. Jason E
MSA-DCA | WA5311337 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 4-West Humidity Fault alarm AHU05 | Air Conditioning | Materials | 612.23 | Pass | Fail | 0 | 0 | 3 | 2022-04-11 04:03 | 2022-04-11 06:03 | 2022-04-11 06:00 | 2022-04-11 08:03 | 2022-04-11 09:00 |  |  | Fcu 5 Humidifier fault alarm, locate plant room and humidifier, reset power.Dan s Attended site to recheck FCU 5 humidifier and updated maintenance check log andCleaned humidifier tank. Jason E
MSA-DFES | WA5311646 | 1 | Critical Fire Protection & Training | DBA Panel - fault on panel | Fire Protection Services | Fire Protection - Monitor System | 597.9 | Pass | Pass | 0 | 0 | 3 | 2022-04-11 08:20 | 2022-04-12 17:00 | 2022-04-11 10:00 | 2022-04-12 17:00 | 2022-04-11 13:00 |  |  | Attended site 11th April for reported issue with fire system.Reported faulty sounder/strobe module, collected partsreplaced with new . All ok following replacement.
MSA-DTWD | WA5311676 | 0 | Techworks Plumbing | Copper pipe work has been damaged | Plumbing & Drainage | Water | 399.21 | Pass | Pass | 0 | 0 | 3 | 2022-04-11 08:26 | 2022-04-11 10:26 | 2022-04-11 08:30 | 2022-04-11 12:26 | 2022-04-11 11:30 |  |  | Attended site and signed in at Rockingham tafe.Spoke to Dennis and he showed me where the pipe was,Pipe had been cut and stolen over night, we made a list of materials and went to the suplier.Once we returned we began to replace to the water line with new copper and fittings.Once we had replaced the pipe we turned water on and tested for leaks After testing we cleaned up and went to sign out of reception Then completed paperwork
MSA-DTAG | WA5311954 | 1 | AHS Services WA Pty Ltd (Anchor) | Registry - Ground - Staff Registry Female Toilet -not flushing | Plumbing & Drainage | Toilets/Cisterns | 314.6675 | Pass | Pass | 0 | 0 | 3 | 2022-04-11 10:04 | 2022-04-12 17:00 | 2022-04-11 12:30 | 2022-04-12 17:00 | 2022-04-11 15:30 |  |  | Picked up and replaced faulty bellows in the female. Cistern by the office
MSA-DCA | WA5312096 | 0 | Protek 24/7 Building & Maintenance | 3 x wooden planks have been damaged on the stage - see notes below | Carpentry | Timber (all types) | 775.72 | Fail | Fail | 0 | 0 | 3 | 2022-04-11 11:06 | 2022-04-11 13:06 | 2022-04-11 13:30 | 2022-04-11 15:06 | 2022-04-11 16:30 |  | WACCES | Replace damaged wooden planks
MSA-DFES | WA5319177 | 3 | Protek 24/7 Building & Maintenance | Cobblers Lane, Falcon - Rear yard - Large hole in fence at the rea of the yard, behind the RCR pad | Building | General Building | 658.72 | Pass | Pass | 0 | 0 | 3 | 2022-04-12 13:00 | 2022-04-21 17:00 | 2022-04-19 07:00 | 2022-04-21 17:00 | 2022-04-19 10:00 |  |  | Repair Large Hole in Fence
MSA-DCA | WA5324543 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 plant room - Generator alarming - Low level tank | Building | Materials | 507.58 | Pass | Pass | 0 | 0 | 3 | 2022-04-13 23:51 | 2022-04-14 01:51 | 2022-04-14 00:15 | 2022-04-14 03:51 | 2022-04-14 03:15 |  |  | Attended call out. Investigated 2x steam generators in alarm. Found both in low water limit alarms and pump control on ro pump in fault. All tanks low water causing pumps to have air locks in them. Opened up bypass valve to allow water to fill tanks. Bled air from pumps and pre filters. Once tanks at suitable level, reset both 2x steam gens and reset pump control on ro pump. Checked over system on bms and confirmed operation. Completed paperwork.
MSA-DFES | WA5325735 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Main Admin - Reception back outdoor area and ATCO Ablution Block - see notes below | Electrical | Lighting, Internal | 601.89 | Pass | Pass | 0 | 0 | 3 | 2022-04-14 11:47 | 2022-04-21 17:00 | 2022-04-19 13:00 | 2022-04-21 17:00 | 2022-04-19 16:00 |  |  | Located faulty GPO. I found a tripped RCD reset the RCD and test the circuit it was working correctly. Located faulty lights and exhaust fan. Replaced faulty tubes with new. Left site to get a new exhaust fan. Replaced faulty exhaust fan with new and test. The new exhaust fan is working correctly.
MSA-DFES | WA5326015 | 2 | Protek 24/7 Building & Maintenance | Above carpark awning roof - Openings in roof - see notes | Roofing | Metal Roofing | 597.9 | Pass | Pass | 0 | 0 | 3 | 2022-04-14 15:07 | 2022-04-21 17:00 | 2022-04-20 10:00 | 2022-04-21 17:00 | 2022-04-20 13:00 |  |  | Repair openings in Roof
MSA-DCA | WA5330069 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room 4th floor audible alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 507.58 | Pass | Pass | 0 | 0 | 3 | 2022-04-15 22:21 | 2022-04-16 00:21 | 2022-04-15 22:45 | 2022-04-16 02:21 | 2022-04-16 01:45 |  |  | Attended callout. Checked over bms for alarm info. Found high water limit sensor on ro plant on. Low water level on both steam gen and ro plant. Accessed plantroom and found all tanks empty. Opened up hand valve to fill tanks and bled air from system. Reset steam gens and automatic pump control. Blew out steam gens. Alarms cleared and units started, unable to clear high level alarm. Sensor needs to be calibrated or replaced. Closed hand valve and continued to monitor system, all ok. Completed paperwork.
MSA-DCA | WA5369054 | 0 | Techworks Electrical | Water leaking through lighting and switchboards - see notes below | Electrical | General Electrical | 403.86 | Pass | Pass | 0 | 0 | 3 | 2022-04-19 15:41 | 2022-04-19 17:41 | 2022-04-19 16:00 | 2022-04-19 19:41 | 2022-04-19 19:00 |  |  | Water leak from fire system.Replaced water damaged gpo and inspected any water damage to electrical components .
MSA-DCA | WA5378606 | 0 | Automatic Fire Protection (ARA) | Stairwell 2 - Sprinkler pipe leaking - basement | Fire Protection Services | Sprinkler Systems | 585.76 | Pass | Pass | 0 | 0 | 3 | 2022-04-20 22:21 | 2022-04-21 00:21 | 2022-04-20 22:30 | 2022-04-21 02:21 | 2022-04-21 01:30 |  |  | 20/4/22AS-Callout to heath ledger theatre-Arrived on site gained access to building-Fire hydrant in basement stairwell was cracked open flowing onto the ground-Closed hydrant water stopped-I would recommend overhauling hydrantPhotos in documents
MSA-DTWD | WA5381560 | 2 | Falcetta Plumbing and Gas | Level 2 - Male Toilet -Left hand sink flick mixer or supply pipe leaking onto floor | Plumbing & Drainage | Water | 651.24 | Pass | Pass | 0 | 0 | 3 | 2022-04-26 09:51 | 2022-04-29 17:00 | 2022-04-28 16:00 | 2022-04-29 17:00 | 2022-04-28 19:00 |  |  | replaced 2x basin mixers, installed mini stops to isolate
MSA-DTWD | WA5381642 | 2 | AWB Co. | Room A18 - GPO damaged and conduit cracked on circuit Blue 2 | Electrical | General Electrical | 390.66 | Pass | Pass | 0 | 0 | 3 | 2022-04-26 10:29 | 2022-04-29 17:00 | 2022-04-29 11:45 | 2022-04-29 17:00 | 2022-04-29 14:45 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, fm wanted wp gpo installed on back of conference room wall , went to wholesaler to pick up parts, returned to site, isolated circuit, drilled hole and ran cable, mounted gpo to wall, wired cable into existing gpo , re energised circuit, tested gpo, working as intended, cleaned up, packed up, completed paperwork , signed outJob completed
MSA-DTWD | WA5383239 | 2 | Equans Mechanical Services Australia | A Block -South Wing - Level 1 - Faulty Aircon - see notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 500.51 | Pass | Pass | -1 | -1 | 3 | 2022-04-27 13:30 | 2022-05-02 17:00 | 2022-04-28 07:15 | 2022-05-02 17:00 | 2022-04-28 10:15 |  |  | Found CU2 isolator burnt out, picked up parts from the suppliers. Had to wait until the rain stopped, replaced the isolator and test ran all OK
MSA-DTWD | WA5383302 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 1 - Basin tap leaking in Accrod toilet B Block | Plumbing & Drainage | Toilets/Cisterns | 440.73 | Pass | Pass | 0 | 0 | 3 | 2022-04-27 14:08 | 2022-05-02 17:00 | 2022-04-29 10:30 | 2022-05-02 17:00 | 2022-04-29 13:30 |  |  | Found tap seized.Spoke to contact and removed taps and replaced with mixer .Disabled toilet
MSA-DTWD | WA5383903 | 2 | AWB Co. | Ground Level - T Block Executive car park - Hinged lLED lights needs replacing - see notes | Electrical | Lighting, External | 789.26 | Pass | Pass | 0 | 0 | 3 | 2022-04-28 08:14 | 2022-05-03 17:00 | 2022-05-03 06:00 | 2022-05-03 17:00 | 2022-05-03 09:00 |  |  | Attended site signed in jsa completed. Found reported pole light not on. No cables connected to it as the cable between two of them is faulty and no way to run new one. New led light was fitted on corner of building facing that way. Re adjusted timer to turn on earlier. *** job completed ***
MSA-DTWD | WA5383943 | 1 | AWB Co. | Ground - F Block - Security lighting not coming on | Electrical | General Electrical | 313.98 | Pass | Pass | 0 | 0 | 3 | 2022-04-28 08:39 | 2022-04-29 17:00 | 2022-04-28 11:00 | 2022-04-29 17:00 | 2022-04-28 14:00 |  |  | Attended site signed in completed jsa. Spoke with mike about job. all lights in F block board for security were off. Found breaker tripped. Tried to turn on but was a fault. Picked middle light disconnected cables to see which way problem was. Still persisted so moved go pe cell which looked new. Found pe cell working fine and correctly, light next to pe cell disconnected cables and rcd stays on, connected one by one to find cable with issue. Found one cable which has a fault on it. Put in danger tag and disconnected and left in connectors in light, all works well now. *** Job completed***
MSA-DCA | WA5384576 | 2 | Protek 24/7 Building & Maintenance | First Floor - Conservation work area - conservation lab area - roof leaks - water dripping onto | Building | General Building | 502 | Pass | Pass | -1 | -1 | 3 | 2022-04-28 13:52 | 2022-05-03 17:00 | 2022-04-29 11:15 | 2022-05-03 17:00 | 2022-04-29 14:15 |  |  | Repair Roof leaks
MSA-DCA | WA5386043 | 0 | Techworks Plumbing | Ground Floor - Geology Building - Male Toilets - 2x running toilets | Plumbing & Drainage | Toilets/Cisterns | 321.58 | Pass | Pass | 0 | 0 | 3 | 2022-04-29 14:56 | 2022-04-29 16:56 | 2022-04-29 15:00 | 2022-04-29 18:56 | 2022-04-29 18:00 |  |  | Attended Site for leaking toilets. Leaking toilet due to flush button issues. Pulled apart and flushed out. All back to working order.
MSA-DTWD | WA5390600 | 3 | GRAFFITI FORCE PTY LTD | Level 2 - Carpark - Remove graffiti above gas meter enclosure | Cleaning | Graffiti | 666 | Fail | Fail | 8 | 8 | 3 | 2022-05-02 14:05 | 2022-05-09 17:00 | 2022-07-06 13:00 | 2022-05-09 17:00 | 2022-07-06 16:00 |  |  | REMOVAL OF GRAFFITI FROM BRICK WALL ABOVE GAS METER ENCLOSURE
MSA-DFES | WA5392613 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Kitchen - oven - not working maybe electrical | Electrical | General Electrical | 775.05 | Pass | Pass | 0 | 0 | 3 | 2022-05-03 11:00 | 2022-05-04 17:00 | 2022-05-03 19:00 | 2022-05-04 17:00 | 2022-05-03 22:00 |  |  | complete
MSA-DFES | WA5393228 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Rear -Repair a faulty light switch | Electrical | General Electrical | 373.19 | Pass | Pass | 0 | 0 | 3 | 2022-05-03 18:20 | 2022-05-04 18:20 | 2022-05-03 19:00 | 2022-05-04 18:20 | 2022-05-03 22:00 |  |  | Completed
MSA-DTWD | WA5394822 | 1 | Techworks Electrical | Kendrew- A-Block room A108 Electrical switch board has a faulty main switch on EWIS board | Electrical | General Electrical | 1358.64 | Fail | Fail | 8 | 8 | 3 | 2022-05-05 09:22 | 2022-05-06 17:00 | 2022-07-04 06:00 | 2022-05-06 17:00 | 2022-07-04 09:00 |  | WACCES | Replaced two breakers that were faulty
MSA-DTAG | WA5394886 | 1 | Sapio Pty Ltd | Level 10 TRAKA key cabinet in our control room access getting expired and need to add more users on | Security | Access Control | 190 | Pass | Pass | 0 | 0 | 3 | 2022-05-05 09:41 | 2022-05-06 17:00 | 2022-05-05 12:00 | 2022-05-06 17:00 | 2022-05-05 15:00 |  |  | Trakka key cabinet not communicating to Unison and Server PC. Reset network board and checked, OK.Programmed users as required
MSA-DCA | WA5395859 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidifier Alarm - Says open and close | Air Conditioning | Building HVAC Maintenance (Major Plant) | 486.65 | Pass | Pass | 0 | 0 | 3 | 2022-05-06 04:06 | 2022-05-06 06:06 | 2022-05-06 05:00 | 2022-05-06 08:06 | 2022-05-06 08:00 |  |  | See work logs
MSA-DTWD | WA5399160 | 1 | Techworks Plumbing | Blocked toilet water not draining away | Plumbing & Drainage | Toilets/Cisterns | 311.67 | Pass | Pass | 0 | 0 | 3 | 2022-05-09 16:12 | 2022-05-10 17:00 | 2022-05-09 17:00 | 2022-05-10 17:00 | 2022-05-09 20:00 |  |  | Arrive at TafeFound block B Found a cleaner to let me inToilet was filling up and draining very slowSo plunged Made it slightly better Removed the io cap directly outside the toilet block and it flushed perfect.Soon as I put the cap back on it drained slow.Might need to camera or jet line.Maybe venting issue Cleaned up Left.
MSA-DCA | WA5407137 | 1 | Ballantyne Plumbing Gas & Electrical | Basement 2 - Sewer pumps - Sewer controller pumps are going into fault on a high-level alarm | Plumbing & Drainage | Sewer Drains & Septic Systems |  | Pass | Pass | 0 | 0 | 3 | 2022-05-11 10:01 | 2022-05-12 17:00 | 2022-05-11 12:45 | 2022-05-12 17:00 | 2022-05-11 15:45 |  |  | Film on level sensor cleaned tested ok
MSA-DTWD | WA5413492 | 2 | Protek 24/7 Building & Maintenance | Room F61 - Roof Leak | Roofing | Metal Roofing | 573.5 | Pass | Pass | -1 | -1 | 3 | 2022-05-12 11:34 | 2022-05-17 17:00 | 2022-05-13 07:00 | 2022-05-17 17:00 | 2022-05-13 10:00 |  |  | Repair Roof leak room F61
MSA-DCA | WA5413608 | 0 | Building Automation & Electrical Services Pty Ltd | Manin theatre - ground floor - air con issues | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 3 | 2022-05-12 12:22 | 2022-05-12 14:22 | 2022-05-12 12:30 | 2022-05-12 16:22 | 2022-05-12 15:30 |  |  | Repairs to air con
MSA-DCA | WA5454617 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Centerany Gallery - Check mechanical services once power is restored | Mechanical Services | Pumps | 345.35 | Pass | Pass | 0 | 0 | 3 | 2022-05-17 12:47 | 2022-05-18 17:00 | 2022-05-18 07:00 | 2022-05-18 17:00 | 2022-05-18 10:00 |  |  | Attended site, signed in and accessed the centenary gallery roof space walkway.Checked all fan coil units and humidifiers. Found fan coil unit 4 humidifier in fault, investigated and discovered the water float level sensor was sticking. Replaced the float sensor with a spare one site. Found fan coil unit 4 humidifier with a faulty board / display screen. Quote will be submitted in the following weeks.
MSA-DTWD | WA5459854 | 2 | Damian Rak Electrical Pty Ltd | BLD 822 - Hallway - Faulty lights | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 3 | 2022-05-18 09:25 | 2022-05-23 17:00 | 2022-05-23 08:00 | 2022-05-23 17:00 | 2022-05-23 11:00 |  |  | job completed -
MSA-DTWD | WA5462486 | 3 | AWB Co. | 3F test cell switchboard room - Burning smell from main switchboard when Hot Well pump activated. | Electrical | General Electrical | 513.09 | Pass | Pass | 0 | 0 | 3 | 2022-05-19 15:30 | 2022-05-26 17:00 | 2022-05-23 07:00 | 2022-05-26 17:00 | 2022-05-23 10:00 |  | WCAPPR | Milan Barjaktar (23/05/2022) - Work NoteAttended site signed in jsa completed. located board with john that was smoking. Found low level water fault light on, manual overide to get pump to move water from one tank to another. Light then went away. Used the main overide at the operations 5F1 and light came on for coldwell pump failure. Unable to open untill rainless day to do fault finding on the motor.*** job not completed ***Daniel Hume (02/06/2022) - Work NoteClose job, no faults on thermal imaging
MSA-DTAG | WA5468550 | 2 | Australian HVAC Services Pty. Ltd. | Admin - Level 1 - Staff Lunchroom -room isnt heating - HVAC advised that only one unit is working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 487.18 | Pass | Pass | 0 | 0 | 3 | 2022-05-20 10:31 | 2022-05-25 17:00 | 2022-05-23 12:00 | 2022-05-25 17:00 | 2022-05-23 15:00 |  |  | Repairs to EDH in staff lunch room.
MSA-DTWD | WA5471063 | 1 | JEM Carpentry | BLD 822 - Flat C - Faulty roof tiles | Roofing | Tiled Roofing |  | Fail | Fail | 1 | 1 | 3 | 2022-05-23 12:17 | 2022-05-24 17:00 | 2022-05-30 08:00 | 2022-05-24 17:00 | 2022-05-30 11:00 |  |  | repairs to tiles
MSA-DFES | WA5471400 | 1 | Protek 24/7 Building & Maintenance | Roof - Second floor - utility room - wellness office- roof leak | Building | General Building | 522 | Pass | Pass | 0 | 0 | 3 | 2022-05-23 12:51 | 2022-05-24 17:00 | 2022-05-24 07:00 | 2022-05-24 17:00 | 2022-05-24 10:00 |  |  | Repair Roof leak - Second floor - utility room - wellness office
MSA-DTWD | WA5472133 | 3 | AWB Co. | A202 - Roof - A Block - Level 2 Richmond Street Entry - roof leak | Building | General Building | 540 | Pass | Pass | 0 | 0 | 3 | 2022-05-23 14:35 | 2022-05-30 17:00 | 2022-05-30 09:00 | 2022-05-30 17:00 | 2022-05-30 12:00 |  |  | Investigated multiple roof leaks.found blocked gutters and valleys. Multiple broken tiles. Source tiles on site and replaced. Job complete
MSA-DTWD | WA5479406 | 3 | Techworks Electrical | Kendrew- C-Block - G/Floor - Ladies toilets lights not working | Electrical | General Electrical | 1574.94 | Pass | Pass | -1 | -1 | 3 | 2022-05-27 09:27 | 2022-06-03 17:00 | 2022-05-27 09:30 | 2022-06-03 17:00 | 2022-05-27 12:30 |  |  | Replaced failed fluro downlights with new led downlights in C block ground toilets
MSA-DTWD | WA5481105 | 2 | AWB Co. | J Block - Eaves on northern side water damaged - see details below | Building | General Building | 621.89 | Pass | Pass | 0 | 0 | 3 | 2022-05-30 10:54 | 2022-06-02 17:00 | 2022-06-02 13:00 | 2022-06-02 17:00 | 2022-06-02 16:00 |  |  | J block awning which has water damage. Accessed roof to find large amounts of debris built up in gutters. Removed all build up. Also found rust holes and split flashings which was all sealed to make watertight. Have taken numerous photos of awning. 3 standard sheets need replacing and whole awning and facia need repainting. Will provide quote. **BRAF SUBMITTED AND DECLINED**
MSA-DTWD | WA5486440 | 2 | Precise Air Group | A-Block - Chiller compound - chiller in alarm | Refrigeration | Chiller | 486.66 | Pass | Pass | -1 | -1 | 3 | 2022-06-01 08:44 | 2022-06-07 17:00 | 2022-06-02 10:30 | 2022-06-07 17:00 | 2022-06-02 13:30 |  |  | Attended site and completed pre start paperwork and signed in. Acessed bms and inspected alarms. Found alarms on bms to have cleared. Acessed chiller plant and inspected chiller c alarm history. Found alarm "cooler flow switch alarm". Inspected pump operation and water flow and found all ok. Contacted nrp as I suspect it's a control fault. Nrp informed me that this is an ongoing issue that they are having Due to a demand/ load issue and that they have made recommendations. Chiller has no major faults. If issue gets worse suggest nrp attend to reprogram operation.
MSA-DFES | WA5487504 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Burst water pipe water flooding everywhere | Plumbing & Drainage | Water | 484.75 | Pass | Pass | 0 | 0 | 3 | 2022-06-01 20:46 | 2022-06-02 17:00 | 2022-06-02 06:45 | 2022-06-02 17:00 | 2022-06-02 09:45 |  |  | Arrived to site on the 1/6/22 at 6:45 for a burst pipe on the hot pipe isolated the water and power dug it up and replaced the damaged section tested and back filled finished at 9:45
MSA-DTWD | WA5490577 | 1 | GRAFFITI FORCE PTY LTD | D, E and F-Blocks have been graffitied please remove all graffiti | Cleaning | Graffiti | 451.74 | Fail | Fail | 1 | 1 | 3 | 2022-06-03 07:24 | 2022-06-03 17:00 | 2022-06-07 08:30 | 2022-06-03 17:00 | 2022-06-07 11:30 |  |  | REMOVAL OF GRAFFITI FROM D, E, F AND BLOCKS
MSA-DCA | WA5491686 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS in alarm - Chilled plant water supply in alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 486.65 | Pass | Pass | 0 | 0 | 3 | 2022-06-06 05:19 | 2022-06-06 07:19 | 2022-06-06 05:30 | 2022-06-06 09:19 | 2022-06-06 08:30 |  |  | Chilled water plant in alarm, along arrival the alarm had reset and chiller were running. Supply chw 6.7 degrees and return chw 10.3 degrees.
MSA-DFES | WA5504171 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen sink blocked - Kitchen sink is used alot. only sink. | Plumbing & Drainage | Drainage | 463.12 | Pass | Fail | 0 | 0 | 3 | 2022-06-11 11:33 | 2022-06-11 13:33 | 2022-06-11 13:00 | 2022-06-11 15:33 | 2022-06-11 16:00 |  |  | Attended to site for a blocked kitchen sink, very slow to drain, tried plunging with no success. Ran the sanny snake roughly 3 meters down the drain, located IO out the front of the building and could seesolidified far build ups washing down. Tested and in working order. Packed up and cleaned up site.
MSA-DCA | WA5520362 | 2 | Techworks Electrical | Regional Arts Office - Light switch plates x 2 are loose and need replacing - See notes | Electrical | General Electrical | 331.46 | Pass | Pass | 0 | 0 | 3 | 2022-06-15 09:46 | 2022-06-20 17:00 | 2022-06-17 08:30 | 2022-06-20 17:00 | 2022-06-17 11:30 |  |  | Replaced faulty light switches
MSA-DCA | WA5534337 | 1 | Building Automation & Electrical Services Pty Ltd | Retrospective work order - Auditorium - Issue with air con being either too hot or too cold. | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 3 | 2022-06-15 12:00 | 2022-06-16 17:00 | 2022-06-16 09:30 | 2022-06-16 17:00 | 2022-06-16 12:30 | 1 |  | Repairs to air con
MSA-DTWD | WA5534411 | 1 | Falcetta Plumbing and Gas | Water leaking under sink | Plumbing & Drainage | Water | 706.31 | Pass | Pass | 0 | 0 | 3 | 2022-06-16 10:14 | 2022-06-17 17:00 | 2022-06-16 13:00 | 2022-06-17 17:00 | 2022-06-16 16:00 |  |  | repaired leaking waste pipe and replaced cistern
MSA-DFES | WA5534632 | 1 | WA BOILER SPARES & SERVICE | Applied training grounds - Service station Bullet - Air leak | Mechanical Services | Boilers | 450 | Pass | Pass | 0 | 0 | 3 | 2022-06-16 12:37 | 2022-06-17 17:00 | 2022-06-17 07:30 | 2022-06-17 17:00 | 2022-06-17 10:30 |  |  | Replaced faulty air actuated gas valve from customer stock. Tested for correct operation
MSA-DTWD | WA5534706 | 2 | Techworks Electrical | Faulty light bulbs - Following location: Cutting room and walkway North end of building by toilets | Electrical | General Electrical | 971.25 | Pass | Pass | 0 | 0 | 3 | 2022-06-16 13:31 | 2022-06-21 17:00 | 2022-06-20 09:30 | 2022-06-21 17:00 | 2022-06-20 12:30 |  |  | Replaced 5 compact fluro downlights with new 235mm cutout downlights in north workshop block walkways.replaced failed exit sign in woodwork exit.
MSA-DTWD | WA5548782 | 3 | Protek 24/7 Building & Maintenance | A Block Structure carpark - Carpark area - Structure has rust and corrosion at joint needs repair | Building | General Building | 370.54 | Pass | Pass | 0 | 0 | 3 | 2022-06-17 09:36 | 2022-06-24 17:00 | 2022-06-22 08:30 | 2022-06-24 17:00 | 2022-06-22 11:30 |  |  | Remove Rust from car park Structure
MSA-DTWD | WA5563338 | 1 | Falcetta Plumbing and Gas | CG07 Video conferencing Room - please see details below | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 3 | 2022-06-20 14:01 | 2022-06-21 17:00 | 2022-06-21 13:30 | 2022-06-21 17:00 | 2022-06-21 16:30 |  |  | repaired sink waste to stop smells
MSA-DTWD | WA5565391 | 3 | Protek 24/7 Building & Maintenance | Study Room 2 (SR2) in Library - Carpet tiles need re-gluing | Building | General Building | 230.435 | Pass | Pass | -1 | -1 | 3 | 2022-06-22 07:22 | 2022-06-28 17:00 | 2022-06-23 10:00 | 2022-06-28 17:00 | 2022-06-23 13:00 |  |  | Refix Carpet Tiles in Library
MSA-DTWD | WA5565465 | 1 | AWB Co. | R Block -security lights are faulty | Electrical | General Electrical | 648.08 | Pass | Pass | 0 | 0 | 3 | 2022-06-22 08:10 | 2022-06-23 17:00 | 2022-06-22 09:15 | 2022-06-23 17:00 | 2022-06-22 12:15 |  |  | Attended site and signed in. Completed JSA. Located faulty light fittings. Went to board and turned on override. Opened all light fittings to do process of Elimination. After this we found 2x battens were faulty and causing circuit to trip. Went to wholesaler for parts. Returned to site and replaced battens. Everything now working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5565542 | 3 | AWB Co. | Roof gutter above A213 - Rain water leak from gutter | Roofing | Guttering | 626.25 | Pass | Pass | -1 | -1 | 3 | 2022-06-22 08:54 | 2022-06-29 17:00 | 2022-06-23 09:00 | 2022-06-29 17:00 | 2022-06-23 12:00 |  |  | Investigated roofleaks.carried out repairs .
MSA-DTWD | WA5565662 | 1 | Lane's Plumbing | BLD 822 - Room 4 - Faulty Toilet | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 3 | 2022-06-22 09:49 | 2022-06-23 17:00 | 2022-06-22 11:30 | 2022-06-23 17:00 | 2022-06-22 14:30 |  |  | job completed - REPAIRS TO FAULTY TOILET BLD822 room 4
MSA-DTWD | WA5567061 | 3 | AWB Co. | Child Care Centre - screws fell out of hinge | Building | General Building | 292.5 | Pass | Pass | -1 | -1 | 3 | 2022-06-23 14:21 | 2022-06-30 17:00 | 2022-06-24 08:00 | 2022-06-30 17:00 | 2022-06-24 11:00 |  |  | Replaced existing screws in hinges and re installed gate
MSA-DFES | WA5569499 | 2 | Protek 24/7 Building & Maintenance | Station Entrance/Engine Room/kitchen - Issues with doors - See below | Building | Doors | 322 | Pass | Pass | 0 | 0 | 3 | 2022-06-27 15:10 | 2022-06-30 17:00 | 2022-06-28 11:00 | 2022-06-30 17:00 | 2022-06-28 14:00 |  |  | Repair doors - Station Entrance/Engine Room/kitchen
MSA-DTWD | WA5570393 | 3 | AWB Co. | External North - 8 x lights under croft out | Electrical | Lighting, External | 670.56 | Pass | Pass | 0 | 0 | 3 | 2022-06-28 10:39 | 2022-07-05 17:00 | 2022-07-05 11:00 | 2022-07-05 17:00 | 2022-07-05 14:00 |  |  | Attended site and signed in. Completed JSA. Located all lights not working on C block. Found 5x on north end. Supplied and replaced 5 x old fittings with new led battens. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5570510 | 2 | Techworks Electrical | - E-Block SK1 and SK2 range hood lights not working | Electrical | Lighting, External | 903.7 | Pass | Pass | 0 | 0 | 3 | 2022-06-28 12:04 | 2022-07-01 17:00 | 2022-07-01 12:30 | 2022-07-01 17:00 | 2022-07-01 15:30 |  |  | Replaced failed E block sk1 and sk2 range hood fluro lights to led battons
MSA-DTWD | WA5570522 | 2 | Techworks Electrical | E-Block SK1 Ceiling light back of room not working | Electrical | Lighting, Internal | 745.77 | Pass | Pass | 0 | 0 | 3 | 2022-06-28 12:14 | 2022-07-01 17:00 | 2022-07-01 06:30 | 2022-07-01 17:00 | 2022-07-01 09:30 |  |  | Replaced tube and drivers in E block skills kitchens
MSA-DCA | WA5570723 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Retrospective Work Order - Air conditioning issues - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 486.65 | Pass | Pass | 0 | 0 | 3 | 2022-06-25 12:00 | 2022-06-27 17:00 | 2022-06-25 14:00 | 2022-06-27 17:00 | 2022-06-25 17:00 | 1 |  | See work logs
MSA-DTWD | WA5570846 | 3 | Milners Tree Solutions Pty Ltd | Campus Grounds - Staff Carpark along Hayman Rd boundary - Rotted tree | Landscaping & Gardening | Tree Lopping | 1000 | Fail | Fail | 0 | 0 | 3 | 2022-06-28 15:46 | 2022-07-05 17:00 | 2022-07-08 08:30 | 2022-07-05 17:00 | 2022-07-08 11:30 |  |  | TREE REMOVE AND STUMP GRINDING
MSA-DTAG | WA5572145 | 3 | MALCO FLOORING PTY LTD | L2 Sheriff's office-carpet tile lifting near entrance to toilets main walk waly | Flooring | Carpet | 1075 | Fail | Fail | 5 | 5 | 3 | 2022-06-29 14:08 | 2022-07-06 17:00 | 2022-08-13 07:00 | 2022-07-06 17:00 | 2022-08-13 10:00 |  |  | Uplifted and removed water damaged screed and applied new ramping screed and reinstalled carpet tiles.
MSA-DTWD | WA5573031 | 3 | AWB Co. | D8 kitchen - Extraction system in kitchenette needs attention | Equipment | Electrical Equipment | 337.87 | Pass | Pass | 0 | 0 | 3 | 2022-06-30 13:37 | 2022-07-07 17:00 | 2022-07-07 07:00 | 2022-07-07 17:00 | 2022-07-07 10:00 |  |  | Attended site signed in jsa completed.Tested fan to make sure its got enough pull by using a fan meter. Had good results. asked by site to remove and blank off switch to other wall. Moved it to kitchen side and labelled clearly. job completed
MSA-DCA | WA5578345 | 2 | Critical Fire Protection & Training | Ground Floor - Stage Door - Zone 7 EWIS Audio Line in Fault- Light lit up on panel | Fire Protection Services | Fire Protection - Monitor System | 209 | Pass | Pass | 0 | 0 | 3 | 2022-07-01 10:50 | 2022-07-06 17:00 | 2022-07-05 11:00 | 2022-07-06 17:00 | 2022-07-05 14:00 |  |  | Fault on EWISLikely relate to build worksNo fault on arrival as cleared unable to trace as no fault.As advised by Tom Swan fire on site working on system
MSA-DFES | WA5583679 | 3 | Australian HVAC Services Pty. Ltd. | Light indicator - monitored mechanical and electrical fault - eletrican has attend and advised Mecha | Air Conditioning | Room Air Conditioners | 353.9 | Pass | Pass | -1 | -1 | 3 | 2022-07-04 13:56 | 2022-07-11 17:00 | 2022-07-05 09:00 | 2022-07-11 17:00 | 2022-07-05 12:00 |  |  | Jean-Pierre Richards-Shaw (05/07/2022) - Work NoteArrived on-site, signed in, spoke with on-site representative who directed me to mechanical services fault lights on wall on sign in area, located building diagrams & found this switch to be responsible for indicating fault for exhaust fans, traced switch back to MSSB, gained access to mechanical services board & found Exhaust Fan 13 (laundry room) to have tripped the overload, this is indicative of high amperage being drawn from exhaust fan, reset overload and tested exhaust fan & found unit to be fully operational, unable to gain access through to roof space to test amperage draw of fan, this is due to a special key being required to open access panel, fire fighters unaware of whereabouts of access panel key, client directed me to main entrance foyer where another Fujitsu cassette system's louver's are not operational, this is likely due to a failed louver motor or indoor PCB, unable to access board to test due to once again requiri
MSA-DCA | WA5584962 | 3 | Techworks Electrical | Stall Foyer entrance-Downlight not functioning even with replaced globe | Electrical | Lighting, Internal | 338.96 | Pass | Pass | 0 | 0 | 3 | 2022-07-05 11:41 | 2022-07-12 17:00 | 2022-07-11 09:00 | 2022-07-12 17:00 | 2022-07-11 12:00 |  |  | Found that globe that was installed had bent pins meaning it wasn’t making good enough connection to stay in the fitting. Had to replace the lamp holder, replacing it was. Nightmare as these fittings are very old and frail, they crumble as soon as you touch them. I recommend complete replacement of all 4 in the same area.
MSA-DTWD | WA5585225 | 3 | Falcetta Plumbing and Gas | Faulty taps and drain on hand basin | Plumbing & Drainage | Water | 394.06 | Pass | Pass | -1 | -1 | 3 | 2022-07-05 13:39 | 2022-07-12 17:00 | 2022-07-08 14:00 | 2022-07-12 17:00 | 2022-07-08 17:00 |  |  | Sealed plumbing to avoid future issues
MSA-DTWD | WA5586043 | 2 | Lane's Plumbing | Faulty toilet | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | -1 | -1 | 3 | 2022-07-06 10:07 | 2022-07-11 17:00 | 2022-07-06 14:30 | 2022-07-11 17:00 | 2022-07-06 17:30 |  |  | job completed - REPLACE FAULTY TOILET CISTERN AND PIPEWORK DEMPSTER HALL
MSA-DCA | WA5587842 | 2 | Techworks Electrical | Gantry (Murray St side)-External Power Box is damaged | Electrical | General Electrical | 405.33 | Pass | Pass | 0 | 0 | 3 | 2022-07-07 11:07 | 2022-07-12 17:00 | 2022-07-11 13:00 | 2022-07-12 17:00 | 2022-07-11 16:00 |  |  | Came to site and found power box had been kicked in, panel was wedged in place, I did not want to disturb it as it was inches away from touching 300mm mains cabling. Barricaded with tiger tails and safety cones using metal cable ties to prevent tampering. Signage installed to barricades to make others aware.
MSA-DCA | WA5589734 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main stage door - Aircon has switched off | Air Conditioning | Ducted Split System | 546.18 | Pass | Pass | 0 | 0 | 3 | 2022-07-08 16:57 | 2022-07-08 18:57 | 2022-07-08 17:00 | 2022-07-08 20:57 | 2022-07-08 20:00 |  |  | Attended callout. Investigated mainstage ahu 03-05 not turning on. Found ahu showing unoccupied, checked over global schedule and found booking sitting in standby and not enable. Made a new entry and tested operation. Unit started cooling as required. Monitored and completed paperwork, all ok.
MSA-DTWD | WA5628218 | 2 | Damian Rak Electrical Pty Ltd | faulty RCD | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 3 | 2022-07-15 12:14 | 2022-07-20 17:00 | 2022-07-18 08:00 | 2022-07-20 17:00 | 2022-07-18 11:00 |  |  | repairs to RCD
MSA-DTWD | WA5660807 | 3 | AWB Co. | Between F & H Blocks -Covered area - Lights staying on 24 hrs a day- See notes below | Electrical | Lighting, Internal | 354.12 | Pass | Pass | -1 | -1 | 3 | 2022-07-19 12:43 | 2022-07-26 17:00 | 2022-07-21 06:30 | 2022-07-26 17:00 | 2022-07-21 09:30 |  |  | Attended site signed in jsa completed. found 6 lights on constantly between f and h block. Couldnt located switch for them to turn off. Disconnected switch cable and ran new switch wire in dog grooming studio. Now lights turn off as site requested this.Job completed
MSA-DTWD | WA5672879 | 2 | AWB Co. | West End - external light faulty and fixture is faulty as well | Electrical | General Electrical | 1332.04 | Pass | Pass | -1 | -1 | 3 | 2022-07-20 10:03 | 2022-07-25 17:00 | 2022-07-21 07:00 | 2022-07-25 17:00 | 2022-07-21 10:00 |  |  | Attended site and signed in completed jsa. Spoke to fm and technician in area about job. Went to wholesaler to pick up parts. Returned to site. Isolated lighting circuit. Took down old light fittings and replaced with new. Had to relocate one light as technician is planning on putting divider up and light would have been in way. Packed and cleaned up. Took pictures. Completed paperwork. Signed out,Job complete
MSA-DTWD | WA5675201 | 0 | Falcetta Plumbing and Gas | Level 1- Toilet - Female-burst water pipe | Plumbing & Drainage | Water | 732.16 | Pass | Pass | 0 | 0 | 3 | 2022-07-22 06:45 | 2022-07-22 08:45 | 2022-07-22 07:15 | 2022-07-22 10:45 | 2022-07-22 10:15 |  |  | installed mini stops and replaced taps
MSA-DTWD | WA5675348 | 2 | Techworks Electrical | A-Block 2nd Floor Ladies toilets light not working | Electrical | Lighting, Internal | 871.74 | Pass | Pass | 0 | 0 | 3 | 2022-07-22 09:59 | 2022-07-27 17:00 | 2022-07-25 10:30 | 2022-07-27 17:00 | 2022-07-25 13:30 |  |  | Replaced old fluro lights in A222 female toilets with new LED batton lights.
MSA-DTWD | WA5676708 | 3 | AWB Co. | external wall facing Francis St - Water leaking from ceiling wall | Roofing | Metal Roofing | 656.41 | Pass | Pass | -1 | -1 | 3 | 2022-07-25 10:10 | 2022-08-01 17:00 | 2022-07-26 09:30 | 2022-08-01 17:00 | 2022-07-26 12:30 |  |  | Investigated area below and above leak. Viewed area through inspection hatch and found leak to originate around jointin the concrete slab. Found expansion joint in the wall above area silicone was perished through out joint. Scraped backand resealed if leak persists over area there could be an issue with the waterproofing underneath the floating tiles andalternative trades to attend. Once confirmed resolved internal works required.
MSA-DTAG | WA5677265 | 1 | Midolo Building Services | Associate to Justice Mitchell Chambers - Leaking/cracked Ceiling | Building | Ceiling | 413.04 | Pass | Pass | 0 | 0 | 3 | 2022-07-25 13:36 | 2022-07-26 17:00 | 2022-07-26 11:30 | 2022-07-26 17:00 | 2022-07-26 14:30 |  |  | potential leak spots sealed & ROOF SHEET REPLACE & SEALED
MSA-DTWD | WA5679586 | 2 | AWB Co. | 2 out of 3 rows of lights not working. RCD tripping when switched on | Electrical | Lighting, Internal | 337.87 | Pass | Pass | 0 | 0 | 3 | 2022-07-26 15:19 | 2022-07-29 17:00 | 2022-07-29 08:30 | 2022-07-29 17:00 | 2022-07-29 11:30 |  |  | Attended site signed in jsa completed. found lights tripping rcd in classroom. Split circuit and still tripping. Disconnected lights one by one and found issue with last light. took tubes out and found it had a faulty ballast causing it to trip. Disconnected ballast and left two tubes working in light as johns request. Job completed
MSA-DCA | WA5679659 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidity alarm FCU 1 | Air Conditioning | Room Air Conditioners | 523.66 | Pass | Pass | 0 | 0 | 3 | 2022-07-26 21:00 | 2022-07-26 23:00 | 2022-07-26 21:30 | 2022-07-27 01:00 | 2022-07-27 00:30 |  |  | Completed
MSA-DTWD | WA5682724 | 3 | AWB Co. | Faulty reading on 12 volt DC power point | Electrical | General Electrical | 525.76 | Pass | Pass | -1 | -1 | 3 | 2022-07-29 11:15 | 2022-08-05 17:00 | 2022-08-01 10:00 | 2022-08-05 17:00 | 2022-08-01 13:00 |  |  | attended site signed in jsa completed, john showed gpo with 50v DC but says 12V DC outlet so is getting over voltage which means faulty transformer. Took time to find location but found inside switchboard. all the other ones in the room are under the tables so may need to do the same or order specific one like what is there already.photos on jobisolated at board so you can no longer get 50v dc as its dangerous to 12v appliances.old transformer was 240v-12V1KWjob not completed BRAF NEEDEDBRAF declined - costs to date
MSA-DTWD | WA5687244 | 3 | AWB Co. | Rear Carpark - Level 1 - Exterior - Remove old broken Registration 618 carpark signs East Perth | Building | General Building | 378.42 | Pass | Pass | 0 | 0 | 3 | 2022-08-01 14:37 | 2022-08-08 17:00 | 2022-08-05 11:00 | 2022-08-08 17:00 | 2022-08-05 14:00 |  |  | Works completed
MSA-DCA | WA5689787 | 2 | EQUANS Mechanical Services (WA) Pty Limited | old goal-ground-Investigate high temperature fault which occurred in the Old Gaol on the 30/07/2022, | Air Conditioning | Room Air Conditioners | 598.22 | Pass | Pass | 0 | 0 | 3 | 2022-08-02 13:48 | 2022-08-05 17:00 | 2022-08-03 11:30 | 2022-08-05 17:00 | 2022-08-03 14:30 |  |  | Attended site. Checked temps around the building and found a few troubled areas. Checked trends on bms to confirm areas. Found no local control of units causing units to overshoot setpoints. Adjusted settings on bms to allow on and off control and restricted set point control. Tested operation of all units, found fcu OG-06 controller blank. Job has been raised to investigate. All ok. Completed paperwork.
MSA-DTWD | WA5689985 | 1 | Milners Tree Solutions Pty Ltd | Carpark 1 - Damaged overhanging tree - over pathway and carpark light | Landscaping & Gardening | Tree Lopping | 1850 | Fail | Fail | 2 | 2 | 3 | 2022-08-02 16:58 | 2022-08-03 17:00 | 2022-08-20 06:35 | 2022-08-03 17:00 | 2022-08-20 09:35 |  |  | heavy prune
MSA-DFES | WA5692552 | 3 | Dom's Total Grounds Maintenance | Open space – right of the driveway - Fallen Tree - See notes below | Landscaping & Gardening | Tree Lopping | 960 | Fail | Fail | 1 | 1 | 3 | 2022-08-03 14:28 | 2022-08-10 17:00 | 2022-08-14 07:00 | 2022-08-10 17:00 | 2022-08-14 10:00 |  |  | Fallen tree removed by Tree Loppers
MSA-DTWD | WA5693120 | 1 | M Construction (WA) | Glasshouse Ground – high roof-Two panels of core flute blown off hydroponics roof-see notes | Roofing | Metal Roofing | 193.42 | Pass | Pass | 0 | 0 | 3 | 2022-08-04 09:43 | 2022-08-05 17:00 | 2022-08-04 14:00 | 2022-08-05 17:00 | 2022-08-04 17:00 |  |  | Reinstalled sheets, installed additional fixings
MSA-DCA | WA5694395 | 2 | Earth & Water Pty Ltd | Wetlands Not Filling – Requires Investigation | Landscaping & Gardening | Earth Works |  | Pass | Pass | -1 | -1 | 3 | 2022-08-05 09:44 | 2022-08-10 17:00 | 2022-08-05 11:00 | 2022-08-10 17:00 | 2022-08-05 14:00 |  |  | -Check Pond Fill zone 9 is topping up pond-Record flow rate of zone 9 f-Fill out information in billing-Mark as complete
MSA-DFES | WA5694907 | 1 | MALCOLM THOMPSON PUMPS PTY LTD | Top Dam on the applied training grounds - Pump has a leaking cell number 2 | Plumbing & Drainage | Water |  | Fail | Fail | 3 | 3 | 3 | 2022-08-05 14:34 | 2022-08-08 17:00 | 2022-08-29 07:00 | 2022-08-08 17:00 | 2022-08-29 10:00 |  |  | Job is complete - Pump has been replaced
MSA-DTWD | WA5698103 | 1 | Damian Rak Electrical Pty Ltd | BLD 831 - Security light faulty | Electrical | Lighting, Internal |  | Fail | Fail | 7 | 7 | 3 | 2022-08-09 14:36 | 2022-08-10 17:00 | 2022-09-27 08:00 | 2022-08-10 17:00 | 2022-09-27 11:00 |  |  | Repairs to lights
MSA-DFES | WA5698107 | 1 | Workzone Pty Ltd | Fence need repair-photo to follow in an email | Building | Steel Fencing & Gates | 492.49 | Fail | Fail | 0 | 0 | 3 | 2022-08-09 14:37 | 2022-08-10 17:00 | 2022-08-11 09:30 | 2022-08-10 17:00 | 2022-08-11 12:30 |  |  | Repair fence damaged by shed blown over in storms
MSA-DTWD | WA5706241 | 3 | Protek 24/7 Building & Maintenance | Metal Fabrication 2 - louvered window in saw tooth roof coming away from frame | Building | Windows | 577.69 | Pass | Pass | 0 | 0 | 3 | 2022-08-11 09:45 | 2022-08-18 17:00 | 2022-08-16 10:00 | 2022-08-18 17:00 | 2022-08-16 13:00 |  |  | Replace rivets with screws
MSA-DCA | WA5735212 | 0 | Critical Fire Protection & Training | Shop Ground Floor - FIP in alarm - Zone 9 (Education and Offices Classroom) | Fire Protection Services | Fire Protection - Monitor System | 520.18 | Pass | Fail | 0 | 0 | 3 | 2022-08-16 11:53 | 2022-08-16 13:53 | 2022-08-16 13:00 | 2022-08-16 15:53 | 2022-08-16 16:00 |  |  | .
MSA-DTWD | WA5752016 | 2 | Damian Rak Electrical Pty Ltd | Main Carpark - Security Lights out | Electrical | Lighting, External |  | Pass | Pass | -1 | -1 | 3 | 2022-08-17 11:27 | 2022-08-22 17:00 | 2022-08-17 12:00 | 2022-08-22 17:00 | 2022-08-17 15:00 |  |  | Completed
MSA-DTWD | WA5791233 | 3 | GRAFFITI FORCE PTY LTD | Roof top Graffiti | Cleaning | Graffiti | 614 | Fail | Fail | 0 | 0 | 3 | 2022-08-22 16:04 | 2022-08-29 17:00 | 2022-08-31 07:30 | 2022-08-29 17:00 | 2022-08-31 10:30 |  |  | REMOVAL OF GRAFFITI FROM B6 MAIN BUILDING ROOF
MSA-DTWD | WA5799915 | 1 | AWB Co. | Automotive Upholstery - Replace faulty switch on the foam cutting machine | Equipment | Electrical Equipment | 722.4675 | Pass | Pass | 0 | 0 | 3 | 2022-08-30 15:38 | 2022-08-31 17:00 | 2022-08-31 07:00 | 2022-08-31 17:00 | 2022-08-31 10:00 |  |  | Attended site and signed in. Completed JSA. Contacted cleaner to gain access to keys. Liaised with site about works going ahead. Located foam cutting machine. Investigated machine not working correctly. Found a faulty isolator switch, supplied and replaced with new. Also. Found a loose connection on limit switch and switch was covered in dust. Terminated and cleaned switch. Machine now operates correctly. Notified relevant personnel. **job complete**
MSA-DTWD | WA5800403 | 3 | Equans Mechanical Services Australia | No boilers running lag boiler in fault lead boiler normal but not running | Mechanical Services | Boilers | 309.69 | Pass | Pass | -1 | -1 | 3 | 2022-08-31 09:54 | 2022-09-07 17:00 | 2022-09-01 07:15 | 2022-09-07 17:00 | 2022-09-01 10:15 |  |  | BMS FROZEN - RESET
MSA-DTWD | WA5800432 | 2 | M Construction (WA) | Hallway pictures on the wall need re hanging coming away from fittings | Building | Internal Walls | 340.42 | Pass | Pass | -1 | -1 | 3 | 2022-08-31 10:02 | 2022-09-05 17:00 | 2022-09-01 08:00 | 2022-09-05 17:00 | 2022-09-01 11:00 |  |  | Removed paintings made good to wall and rehung all paintings using stronger fixings.
MSA-DFES | WA5801098 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Office - replace 10+ light globes/tubes that have blown in the office | Electrical | Lighting, Internal | 996.79 | Pass | Pass | -1 | -1 | 3 | 2022-08-31 14:25 | 2022-09-07 17:00 | 2022-09-02 07:30 | 2022-09-07 17:00 | 2022-09-02 10:30 |  |  | Repair 14 light fittings as directed
MSA-DFES | WA5801291 | 3 | AWB Co. | Ceiling leak in Engine Room SE corner - see notes below | Building | Ceiling | 336.23 | Pass | Pass | -1 | -1 | 3 | 2022-08-31 14:56 | 2022-09-07 17:00 | 2022-08-31 15:00 | 2022-09-07 17:00 | 2022-08-31 18:00 |  |  | Re-sealed full extraction system to S/E side
MSA-DTAG | WA5829189 | 3 | Midolo Building Services | Court waiting area 1 - fix viewing board to existing wall | Building | Internal Walls | 193.09 | Pass | Pass | -1 | -1 | 3 | 2022-09-02 10:49 | 2022-09-09 17:00 | 2022-09-05 10:45 | 2022-09-09 17:00 | 2022-09-05 13:45 |  |  | Installed white board
MSA-DCA | WA5829622 | 1 | Techworks Electrical | Light switch no longer functional | Electrical | Lighting, Internal | 244.52 | Pass | Pass | 0 | 0 | 3 | 2022-09-02 14:39 | 2022-09-05 17:00 | 2022-09-05 11:30 | 2022-09-05 17:00 | 2022-09-05 14:30 |  |  | Replaced light switch on mezzanine floor
MSA-DFES | WA5832374 | 0 | Critical Fire Protection & Training | Ground Floor - Male Toilets - Smoke detectors and sprinklers to be isolated | Fire Protection Services | Smoke and Heat Detection | 2617.68 | Fail | Fail | 0 | 0 | 3 | 2022-09-05 12:39 | 2022-09-05 14:39 | 2022-09-06 08:00 | 2022-09-05 16:39 | 2022-09-06 11:00 |  |  | Attended site and signed in.Removed2x sprinkler heads installed 2x 10mm plugs.Removed 1x ewis speakerRemoved 1x detector and isolated #59Recommend replacing the detector and speaker when reinstalling.
MSA-DTWD | WA5833301 | 1 | Damian Rak Electrical Pty Ltd | Boardroom - Electrical light fault burning smell | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 3 | 2022-09-06 09:04 | 2022-09-07 17:00 | 2022-09-06 10:30 | 2022-09-07 17:00 | 2022-09-06 13:30 |  |  | Repairs to lights
MSA-DTWD | WA5835453 | 1 | Protek 24/7 Building & Maintenance | Room 6A5 Class room - During heavy rain water dripping onto sill near GPO and computers | Roofing | Metal Roofing | 607.62 | Pass | Pass | 0 | 0 | 3 | 2022-09-07 08:48 | 2022-09-08 17:00 | 2022-09-08 09:45 | 2022-09-08 17:00 | 2022-09-08 12:45 |  |  | Scope site, hose tested box gutter no leak, hose tested roof sheets and leaked. Dried roof and installed byute tape over hole as temp fixBraf Declined
MSA-DTWD | WA5836079 | 1 | Lane's Plumbing | Blocked drain ensuite | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 3 | 2022-09-07 10:01 | 2022-09-08 17:00 | 2022-09-07 11:00 | 2022-09-08 17:00 | 2022-09-07 14:00 |  |  | CLEAR BLOCKAGE TO ENSUITE DRAINS HUGHES HALL 804
MSA-DTWD | WA5836343 | 3 | AWB Co. | Faulty power circuit tripping out | Electrical | General Electrical | 525.76 | Pass | Pass | -1 | -1 | 3 | 2022-09-07 11:27 | 2022-09-14 17:00 | 2022-09-08 08:00 | 2022-09-14 17:00 | 2022-09-08 11:00 |  |  | Attended site and signed in. Completed JSA. Spoke to staff in area to get more information about job. Located gpo and found it to be on, tested all appliances plugged in to circuit and all passed, isolated circuit, tested circuit from the board, found dead short between earth and neutral, went into room to look for more GPOs on circuit, couldn’t find any, found that the hws was on the same circuit, test hws and found fault, removed cables and put in connectors, retested cables from boa4d and test passed, put everything back together, turned breaker on, gpo test passed, completed paperwork ,packed up, signed out, *job completed*
MSA-DTWD | WA5836852 | 2 | AWB Co. | Steel frame paint house - faulty down pipe at south west corner of paint house | Roofing | Guttering | 738.87 | Pass | Pass | 0 | 0 | 3 | 2022-09-07 15:06 | 2022-09-12 17:00 | 2022-09-12 08:15 | 2022-09-12 17:00 | 2022-09-12 11:15 |  |  | Replaced down pipe and directed water away from building to stop erosion. Job complete
MSA-DTAG | WA5838351 | 3 | Midolo Building Services | Level 5 - Server Room - Ceiling tiles damaged and sagging | Building | Ceiling | 498.12 | Pass | Pass | -1 | -1 | 3 | 2022-09-08 12:39 | 2022-09-15 17:00 | 2022-09-09 09:30 | 2022-09-15 17:00 | 2022-09-09 12:30 |  |  | REPAIR GRID CEILING & REPLACE T BARS/CEILING PARTS
MSA-DCA | WA5844669 | 0 | EQUANS Mechanical Services (WA) Pty Limited | faulty light in the planet room | Electrical | Lighting, Internal | 1362.93 | Pass | Pass | 0 | 0 | 3 | 2022-09-11 11:49 | 2022-09-11 13:49 | 2022-09-11 12:00 | 2022-09-11 15:49 | 2022-09-11 15:00 |  |  | Attended site for call out, signed into site. Gain access to chiller 4 in plantroom. Found chiller 4 on compressor a low current alarm. Tried to reset chiller 4. However, unsuccessful to do so. Informed supervisor and requires chiller technician to return and investigate the fault. Sign out of site. - works carried out by Chuan Chia
MSA-DTAG | WA5861693 | 3 | Midolo Building Services | Roof - A/C unit walkway platforms sagging in places | Building | General Building | 488.21 | Fail | Fail | 3 | 3 | 3 | 2022-09-13 10:42 | 2022-09-20 17:00 | 2022-10-12 07:30 | 2022-09-20 17:00 | 2022-10-12 10:30 |  |  | additional bracing welded to walkway & mesh sections
MSA-DCA | WA5869119 | 0 | Techworks Electrical | DG/21 egress button faulty | Electrical | General Electrical | 326.61 | Pass | Pass | 0 | 0 | 3 | 2022-09-14 11:45 | 2022-09-14 13:45 | 2022-09-14 12:30 | 2022-09-14 15:45 | 2022-09-14 15:30 |  |  | Found no problem in the end. Took appart and cleaned to make sure it was all good and put back together.
MSA-DTWD | WA5887628 | 2 | M Construction (WA) | Walkway area - under bench paver has come loose | Paving & Roadworks | Paving | 318.42 | Pass | Pass | 0 | 0 | 3 | 2022-09-16 08:48 | 2022-09-21 17:00 | 2022-09-20 09:30 | 2022-09-21 17:00 | 2022-09-20 12:30 |  |  | Attended site and replaced pavers which had come loose
MSA-DTWD | WA5887797 | 3 | AWB Co. | Rear Garden Wall - Beauty Garden 3 x lights out - require 2 x persons | Electrical | Lighting, External | 1046.17 | Pass | Pass | 0 | 0 | 3 | 2022-09-16 10:11 | 2022-09-23 17:00 | 2022-09-20 10:30 | 2022-09-23 17:00 | 2022-09-20 13:30 |  |  | Job complete
MSA-DTWD | WA5962595 | 2 | Damian Rak Electrical Pty Ltd | Faulty exit lights | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 3 | 2022-09-19 15:37 | 2022-09-22 17:00 | 2022-09-28 10:00 | 2022-09-22 17:00 | 2022-09-28 13:00 |  |  | Repairs to light
MSA-DTWD | WA5972959 | 2 | Techworks Electrical | Restaurant kitchen, ceiling pendant power point broken/ cracked | Electrical | General Electrical | 506.11 | Pass | Pass | -1 | -1 | 3 | 2022-09-21 09:38 | 2022-09-27 17:00 | 2022-09-21 12:30 | 2022-09-27 17:00 | 2022-09-21 15:30 |  |  | Replace 2 x pendant 10A outlets in restaurant pavillion kitchen south side.
MSA-DTWD | WA5973152 | 3 | AWB Co. | 128 to yard - Double steel doors - paint has peeled off - 128 to yard | Painting | Internal | 543.42 | Fail | Fail | 1 | 1 | 3 | 2022-09-21 11:06 | 2022-09-29 17:00 | 2022-10-03 07:00 | 2022-09-29 17:00 | 2022-10-03 10:00 |  |  | painting works completed
MSA-DTWD | WA5974536 | 3 | AWB Co. | Classroom - 6B5 - Exhaust fan in classroom won’t turn off | Equipment | Electrical Equipment | 574.59 | Pass | Pass | 0 | 0 | 3 | 2022-09-23 13:13 | 2022-10-03 17:00 | 2022-10-03 13:00 | 2022-10-03 17:00 | 2022-10-03 16:00 |  |  | Attended site signed in jsa completed. Found fan running in classroom with no switch in class. Traced cable back and found going to gpo. Unplugged and ran a tps from closest light fitting to fan. Also ran a SDI from fan down trunking and to existing light switch as hard active was there already. fit plug base off in roof and plugged fan in. Put two gang plate on wall and tested all working and switching. Job completed
MSA-DFES | WA5977283 | 3 | AWB Co. | Main Administration ground - Female toilet near radio comms - cubiclock is jammed and cant be closed | Building | Doors | 349.86 | Fail | Fail | 0 | 0 | 3 | 2022-09-27 15:13 | 2022-10-04 17:00 | 2022-10-05 12:00 | 2022-10-04 17:00 | 2022-10-05 15:00 |  |  | Works completed
MSA-DTWD | WA5982048 | 3 | COMMERCIAL PLUMBING AND GAS | A260 - Wall mounted Gas Heater not working | Plumbing & Drainage | Gas | 329.06 | Pass | Pass | 0 | 0 | 3 | 2022-09-30 09:49 | 2022-10-07 17:00 | 2022-10-06 11:00 | 2022-10-07 17:00 | 2022-10-06 14:00 |  |  | disposed of faulty heater and installed functioning but unused heater in place
MSA-DTWD | WA5982211 | 3 | AWB Co. | Faulty power point | Electrical | General Electrical | 576.25 | Pass | Pass | 0 | 0 | 3 | 2022-09-30 10:20 | 2022-10-07 17:00 | 2022-10-04 10:00 | 2022-10-07 17:00 | 2022-10-04 13:00 |  |  | Attended site signed in jsa completed. Found faulty power point in class. Cable was faulty and damaged and shorted. Had to replace cable to nearest gpo. Also replaced the broken gpos with new. All tested and works good.Job completed
MSA-DCA | WA5982909 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plantroom has fault light on - Chiller Panel in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 546.18 | Pass | Pass | 0 | 0 | 3 | 2022-10-01 01:23 | 2022-10-01 03:23 | 2022-10-01 01:30 | 2022-10-01 05:23 | 2022-10-01 04:30 |  |  | Murray Biddle attended site. Checked chiller 4, fault circuit A low current. No access to BMS. Checked found no cause, reset chiller at chiller. Chiller fault not showing display went into standby. Monitored while doing paper. Checked history faults. First time fault for this month for low current. Cleaned up and left site.
MSA-MRWA | WA5994244 | 2 | AWB Co. | 5 LED lights out to level 2 - see notes | Electrical | Lighting, Internal | 552.13 | Pass | Pass | 0 | 0 | 3 | 2022-10-05 14:00 | 2022-10-10 17:00 | 2022-10-10 06:00 | 2022-10-10 17:00 | 2022-10-10 09:00 |  |  | Attended site signed in jsa completed. Found 7 lights out on level 2. 6 lights north west and two on east end. Replaced with new drivers two lights wont turn on. have notified site of possible program issue as i reset breakers in board that control. Danika said to close job off as electrical is complete
MSA-DTWD | WA5997514 | 1 | SENTINEL LOCK SERVICE PTY LTD | Faulty padlock to main entrance | Security | Locksmith | 771.25 | Pass | Pass | 0 | 0 | 3 | 2022-10-07 07:15 | 2022-10-07 17:00 | 2022-10-07 08:00 | 2022-10-07 17:00 | 2022-10-07 11:00 |  |  | Faulty padlock to main entrance.Padlock and entry door locks faulty.Padlock replaced - locks repaired - keys replaced.
MSA-DCA | WA5998129 | 3 | Earth & Water Pty Ltd | Retic issues - One broken sprinkler and one sprinkler needs to be lowered about 80mm – under ground | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 3 | 2022-10-07 12:12 | 2022-10-14 17:00 | 2022-10-12 09:30 | 2022-10-14 17:00 | 2022-10-12 12:30 |  |  | Repairs to sprinklers
MSA-DCA | WA6015958 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room lvl 5 - chiller EPS CH4 showing in fault on panel | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Pass | 0 | 0 | 3 | 2022-10-13 01:46 | 2022-10-13 03:46 | 2022-10-13 02:00 | 2022-10-13 05:46 | 2022-10-13 05:00 |  |  | AFTER HOURS C/O FOUND CHILLER FOUR ON FAULT , RESET AND CHECKED ALL OK, CHILLER THREE IS RUNNING AND HOLDING TEMP.
MSA-DTWD | WA6019978 | 2 | Techworks Plumbing | Faulty flush button in the disabled toilet in M011 | Plumbing & Drainage | Toilets/Cisterns | 442.26 | Pass | Pass | -1 | -1 | 3 | 2022-10-13 09:42 | 2022-10-18 17:00 | 2022-10-14 07:00 | 2022-10-18 17:00 | 2022-10-14 10:00 |  |  | Repaired the full flush mechanism as it was broken
MSA-DTWD | WA6022892 | 3 | AWB Co. | Repair GPO in wall damaged in foyer entry to N115 rooms | Electrical | General Electrical | 400.37 | Fail | Fail | 0 | 0 | 3 | 2022-10-14 12:49 | 2022-10-21 17:00 | 2022-10-24 10:00 | 2022-10-21 17:00 | 2022-10-24 13:00 |  |  | Actual start and finish on 20.11.22
MSA-DTWD | WA6074020 | 3 | WESTERN IRRIGATION PTY LTD | broken sprinklers and set for summer watering | Landscaping & Gardening | Grounds Maintenance | 667.39 | Pass | Pass | 0 | 0 | 3 | 2022-10-18 09:29 | 2022-10-25 17:00 | 2022-10-24 10:30 | 2022-10-25 17:00 | 2022-10-24 13:30 |  |  | Repair retic as required
MSA-DTWD | WA6090708 | 2 | Damian Rak Electrical Pty Ltd | Dining room servery - Power point tripping Bain maree | Electrical | General Electrical |  | Pass | Pass | -1 | -1 | 3 | 2022-10-19 13:21 | 2022-10-24 17:00 | 2022-10-20 13:30 | 2022-10-24 17:00 | 2022-10-20 16:30 |  |  | repairs to power point
MSA-DTWD | WA6109122 | 2 | AWB Co. | Blown tubes in 4 x insect zappers in the canteen. | Electrical | General Electrical | 1076.41 | Fail | Fail | 0 | 0 | 3 | 2022-10-20 14:01 | 2022-10-25 17:00 | 2022-10-28 09:00 | 2022-10-25 17:00 | 2022-10-28 12:00 |  | WCAPPR | Attended site and signed in, completed JSA, spoke with fm about works going ahead, picked up new bug zapper for common area, removed old zapper and replaced with new, replaced tubes and starters to remaining bug zappers, cleaned remaining bug zappers , all now working as intended,cleaned up, packed up, completed paperwork,signed out**job completed**
MSA-DTWD | WA6111657 | 2 | JEM Carpentry | BLD 831-outside steps-Faulty non slip tape on steps | Carpentry | Staircases, Balustrades and Handrails |  | Fail | Fail | 1 | 1 | 3 | 2022-10-21 09:53 | 2022-10-26 17:00 | 2022-11-02 08:00 | 2022-10-26 17:00 | 2022-11-02 11:00 |  |  | Clean steps and and install tape
MSA-DTWD | WA6113447 | 3 | AWB Co. | Creche Outdoor Yard - Debris clean from roof and gutters - Could be syringes | Roofing | Guttering | 636.04 | Pass | Pass | -1 | -1 | 3 | 2022-10-24 11:40 | 2022-10-31 17:00 | 2022-10-25 09:00 | 2022-10-31 17:00 | 2022-10-25 12:00 |  |  | Attended site. Signed in and staff showed location of creche room playground where debris and sharps are on patio above play area. Staff removed all kids from area. Bunted off area of work. Accessed roof and took safety procedures to removed 7 syringes from roof space. And also removed all other debris from roof space. Cleaned and packed up site. Job complete
MSA-DCA | WA6113724 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Centenary Galleries - FCU 3 - FCU 3 in fault | Air Conditioning | Room Air Conditioners | 709.45 | Pass | Pass | 0 | 0 | 3 | 2022-10-24 14:23 | 2022-10-25 17:00 | 2022-10-24 14:23 | 2022-10-25 17:00 | 2022-10-24 17:23 |  |  | Investigated high humidity alarm on fcu 3 in the centenary gallery. Unit had a supply of 63% and returning at 58%. manually drove actuators to decrease humidity, no effect. TA checked fcu 3 while I drove actuators from bms, confirmed actuators drove but wasn't much temperature in the pipes. Wound stat valve out and back into position. Supply humidity started decreasing. OA humidity and temp were in range, open outside air damper and return and supply humidity came into required range and temperature was correct. Returned all actuators back to auto and monitored while completing paperwork, all ok.Work order came through late. Issue was raised first thing in the morning
MSA-DCA | WA6126099 | 3 | GPS Plumbing & Gas Services PtyLtd | Ladies bathroom in theatre foyer - Tap at furthest sink as you enter is broken | Plumbing & Drainage | Water | 302.125 | Pass | Pass | -1 | -1 | 3 | 2022-10-25 10:19 | 2022-11-01 17:00 | 2022-10-27 12:30 | 2022-11-01 17:00 | 2022-10-27 15:30 |  |  | Unable to replace tap, tap discontinued, able to isolate hot and cold.
MSA-DTWD | WA6130087 | 3 | AWB Co. | Room 3. Door to outside yard - Top Slide bolt has come away and needs to be reattached | Building | Doors | 331.04 | Pass | Pass | 0 | 0 | 3 | 2022-10-28 09:44 | 2022-11-04 17:00 | 2022-11-03 10:00 | 2022-11-04 17:00 | 2022-11-03 13:00 |  |  | Works completed
MSA-DCA | WA6131102 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Art Gallery of WA - Alarm in plant room is alarming due to a recent power outage | Air Conditioning | Materials | 546.18 | Pass | Pass | 0 | 0 | 3 | 2022-10-30 14:04 | 2022-10-30 16:04 | 2022-10-30 14:30 | 2022-10-30 18:04 | 2022-10-30 17:30 |  |  | Attended call out. Investigated alarms generated from power out. Whole plant went into alarm and required resetting. Accessed plantroom and reset ro plant, steam generator water alarms and air compressor. Checked over bms and reset alarms. Log alarms should clear automatically. All other alarms cleared or awaiting parts. Completed paperwork.
MSA-DTAG | WA6131506 | 1 | Gilmour & Jooste Electrical | 1987 building south east footpath cable is live-contractors on site | Electrical | General Electrical | 602.05 | Pass | Pass | 0 | 0 | 3 | 2022-10-31 08:09 | 2022-11-01 17:00 | 2022-10-31 12:00 | 2022-11-01 17:00 | 2022-10-31 15:00 |  |  | Make cable safe.
MSA-DTWD | WA6142803 | 2 | AWB Co. | C113 - broken inter leaf towel dispensers | Building | Materials | 314.73 | Pass | Pass | 0 | 0 | 3 | 2022-11-01 09:04 | 2022-11-04 17:00 | 2022-11-03 07:00 | 2022-11-04 17:00 | 2022-11-03 10:00 |  |  | Works completed
MSA-DTWD | WA6145732 | 1 | Protek 24/7 Building & Maintenance | Entrance door has no stop bead and opening to far in | Building | Doors | 320.8 | Pass | Pass | 0 | 0 | 3 | 2022-11-02 14:23 | 2022-11-03 17:00 | 2022-11-03 07:00 | 2022-11-03 17:00 | 2022-11-03 10:00 |  |  | Fitted a Ali flat bar to stop the door coming through
MSA-DTAG | WA6145831 | 3 | Seme Solutions Pty Ltd | Camera issues - Camera 13 is faulty - May need replacing - See notes | Security | CCTV Surveillance | 2434.52 | Fail | Fail | 1 | 1 | 3 | 2022-10-26 15:50 | 2022-11-02 17:00 | 2022-11-08 07:00 | 2022-11-02 17:00 | 2022-11-08 10:00 |  |  | Replaced faulty camera as per BRAF.Confirmed online and recording.
MSA-MRWA | WA6147579 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Room 119.2 - Failed ethernet port may require 2 data mech replacement | Electrical | General Electrical | 422.02 | Pass | Pass | -1 | -1 | 3 | 2022-11-03 08:29 | 2022-11-08 17:00 | 2022-11-03 12:15 | 2022-11-08 17:00 | 2022-11-03 15:15 |  |  | Located faulty data points. I found two damaged data points. The data mechs are not a standard type discussed with site and they are happy to cover the exciting holes and install and a new gang plate with mounting block in a new location because there was no length on one of the cables. Installed the new gear and test the cables and they past the test. I also got the person to test there computer and it is now running off the data cable.
MSA-DTWD | WA6148759 | 3 | Building Automation & Electrical Services Pty Ltd | N122-25Ab: BMS Issue - Cannot connect to AHU9 | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Fail | Pass | 1 | 0 | 3 | 2022-11-04 08:54 | 2022-11-11 17:00 | 2022-11-16 07:30 | 2022-11-16 17:00 | 2022-11-16 10:30 |  |  | BAE Services Investigation:• Investigations into why NO access into AHU 9 data / graphics on the BMS was carried out.• Local access was gain into AHU 9 controller, this confirmed data & graphics are healthy.• Access to the BMS system via engineering tool (RC Studio) also found the AHU 9 graphic page and all associated points are displaying on thegraphic correctly. • Backup was taken to engineers PC.• Network access via the HTML web access was then used to see if the problem was on the web access side of the controls display.• Access via system tree to AHU 9 worked, Access via AHU main page worked. Access via floor plan jump tile failed.• AHU 9 hyper link tile was deleted and reinstalled.• Testing on both Engineering tool and web BMS access proved all access to AHU 9 is now in full working order.• Site backup was taken & display of usage to site facilities staff was carried out.• Left site with problem resolved & BMS in full working order.
MSA-DCA | WA6149454 | 0 | Building Automation & Electrical Services Pty Ltd | Aircon is too warm - Urgent | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 3 | 2022-11-04 16:52 | 2022-11-04 18:52 | 2022-11-04 17:00 | 2022-11-04 20:52 | 2022-11-04 20:00 |  |  | Local investigations at the basement plantroom found that plantroom MSSBdistribution board was found with no incoming power to main breaker. This controlpanel is totally without power and plant is not able to run in auto or manual untilpower is reinstated.
MSA-DCA | WA6154572 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Cooling Tower 2 - belts fallen off pulley | Air Conditioning | Cooling Tower | 574.34 | Pass | Fail | 0 | 0 | 3 | 2022-11-07 13:39 | 2022-11-08 17:00 | 2022-11-08 16:00 | 2022-11-08 17:00 | 2022-11-08 19:00 |  |  | Accessed bms and switched chiller 2 into out of service. Once components had ramped down. Isolated call and power to ccwp and cooling tower 2. Removed access panel to cooling tower 2 and accessed belts. Found 1x belt had slipped off pulleys and the other 4 misaligned and worn. Removed 5x v belts and replaced with new spares onsite. Adjusted motor position to get correct tension and restored power to components and switched back to auto on bms tested operation of cooling tower and checked amps, all ok. Completed paperwork.
MSA-DTWD | WA6155604 | 2 | AWB Co. | Level 2 - Disabled Toilet - : Round ceiling light damaged, replace with LED unit | Electrical | Lighting, Internal | 909.29 | Pass | Pass | 0 | 0 | 3 | 2022-11-08 11:44 | 2022-11-11 17:00 | 2022-11-11 11:30 | 2022-11-11 17:00 | 2022-11-11 14:30 |  |  | Attended site and signed in, completed JSA,spoke with fm about job, measured down lights and went to wholesaler to pick up, returned to site, set up work area, removed old lights and replaced with new, tested lights and working as intended, cleaned up, packed up, completed paperwork, signed out**job complete**
MSA-DTWD | WA6156874 | 1 | COMMERCIAL PLUMBING AND GAS | Investigate water supply leak - Possibly a hot water unit or water connection. | Plumbing & Drainage | HWS/Units Electric & Gas | 894.06 | Pass | Pass | 0 | 0 | 3 | 2022-11-09 11:19 | 2022-11-10 17:00 | 2022-11-09 16:00 | 2022-11-10 17:00 | 2022-11-09 19:00 |  | WACCES | unblocked tundish and replaced relief valve
MSA-DCA | WA6172745 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Air conditioned alarm centenary gallery FCU-7 equipment room humidity alarm | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Pass | 0 | 0 | 3 | 2022-11-12 15:00 | 2022-11-12 17:00 | 2022-11-12 15:30 | 2022-11-12 19:00 | 2022-11-12 18:30 |  |  | See work logs
MSA-MRWA | WA6229734 | 3 | AWB Co. | Rear equipment yard - Rear yard pole lights not illuminating at night - see note | Electrical | General Electrical | 380.62 | Pass | Pass | 0 | 0 | 3 | 2022-11-18 10:31 | 2022-11-25 17:00 | 2022-11-23 07:00 | 2022-11-25 17:00 | 2022-11-23 10:00 |  |  | Attended site signed in jsa completed. Tested rear lights and found x9 not working. Also found melted contactor cables, replaced with new and now only x3 not working. Need to send quote to craig for repairs.Job completed
MSA-DTWD | WA6231145 | 2 | AWB Co. | Gutters leaking on bench machinery | Roofing | Guttering | 663.56 | Pass | Pass | 0 | 0 | 3 | 2022-11-18 13:59 | 2022-11-23 17:00 | 2022-11-22 09:15 | 2022-11-23 17:00 | 2022-11-22 12:15 |  |  | Attended site and signed in, we had a inspection with staff members then accessed the roof. We found multiple roof screws thatWe’re not installed correctly, either on odd angles or no rubber seal attached. Also the anchor points we found multiple screwsIncorrectly. We re sealed multiple box gutter joins and cleaned out a heavily blocked gutter outlet.
MSA-DTWD | WA6255357 | 0 | Complete Pest Management Services | Painting Room - Possum trapped in the room | Pest Control | Specialist Pest | 400.81 | Fail | Fail | 0 | 0 | 3 | 2022-11-23 09:59 | 2022-11-23 11:59 | 2022-11-23 12:00 | 2022-11-23 13:59 | 2022-11-23 15:00 |  |  | Removal of Possums from K Block Paint Room
MSA-DTWD | WA6255789 | 2 | JEM Carpentry | Between Houses 813 and 812 - Faulty ringlock fence | Building | Steel Fencing & Gates |  | Pass | Pass | -1 | -1 | 3 | 2022-11-23 13:55 | 2022-11-28 17:00 | 2022-11-23 14:00 | 2022-11-28 17:00 | 2022-11-23 17:00 |  |  | Fence removed from garden
MSA-DCA | WA6256836 | 0 | EQUANS Mechanical Services (WA) Pty Limited | RETROSPECTIVE WORK ORDER-Air con in dressing room are not turning on Section of 4 units in a row | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Fail | 0 | 0 | 3 | 2022-11-23 18:27 | 2022-11-23 20:27 | 2022-11-23 19:30 | 2022-11-23 22:27 | 2022-11-23 22:30 | 1 |  | Attended call-out. Investigated aircons not turning on in dressing room. Found 2/7 units running in occupied but cooling call had been manual off. Checked through controls on bms and relinquished manual controls and changed units over to occupied. All seven units back online. Tested operation and confirmed temps of studio and hlt dressing room fcus. Completed paperwork.
MSA-DTWD | WA6257230 | 2 | Techworks Electrical | Blue 9 circuit trips and will not re set | Electrical | General Electrical | 326.61 | Pass | Pass | -1 | -1 | 3 | 2022-11-24 13:09 | 2022-11-29 17:00 | 2022-11-25 08:00 | 2022-11-29 17:00 | 2022-11-25 11:00 |  |  | nvestigated tripping circuit disconnected circuit as the circuit is no longer in use and they no longer require the use of it
MSA-DCA | WA6257457 | 2 | EQUANS Mechanical Services (WA) Pty Limited | L1-Scott Mitchell’s Office-Air conditioning does not seem to be working-see notes | Air Conditioning | Room Air Conditioners | 371.62 | Pass | Pass | -1 | -1 | 3 | 2022-11-24 15:41 | 2022-11-29 17:00 | 2022-11-25 10:00 | 2022-11-29 17:00 | 2022-11-25 13:00 |  |  | Quoted for repairs. Refrigerant leak in system.
MSA-DTAG | WA6291258 | 3 | Midolo Building Services | Level 7 - Rooms - 7.1, 7.2, 7.3 & 7.4 - See notes | Building | Steel Fencing & Gates | 274.99 | Pass | Pass | -1 | -1 | 3 | 2022-11-28 13:24 | 2022-12-05 17:00 | 2022-11-30 11:30 | 2022-12-05 17:00 | 2022-11-30 14:30 |  |  | gates adjusted & repaired
MSA-DCA | WA6291308 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Plant Room - Chiller 1 in alarm | Refrigeration | Chiller | 371.62 | Pass | Pass | 0 | 0 | 3 | 2022-11-28 13:45 | 2022-11-29 17:00 | 2022-11-29 07:00 | 2022-11-29 17:00 | 2022-11-29 10:00 |  |  | Travelled to site and reset chiller 1 compressor 1B in alarm. Ran and tested chiller. Checked refrigerant pressures, amp draws, voltages and chilled water temperatures entering and leaving. System did not fault again. Advised staff of works carried out.
MSA-DFES | WA6291367 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Outdoor Plant Room near Staff dining - Lights non-operational - See notes | Electrical | Lighting, Internal | 727.6 | Pass | Pass | -1 | -1 | 3 | 2022-11-28 14:12 | 2022-12-05 17:00 | 2022-11-30 08:30 | 2022-12-05 17:00 | 2022-11-30 11:30 |  |  | Tyler Beard (30/11/2022) - Work NoteContinued on site at 0830 to inspect lights not working in outdoor plant room near dining room. After investigation we found the switch and multiple Tubes to be faulty. We collected materials from supplier and replaced switch, and 3 x tubes and starters. All are now working correctly. Informed staff of outcomes and left site at 1130.
MSA-DTAG | WA6292272 | 2 | Australian HVAC Services Pty. Ltd. | Basement - Custody - A/C unit in Sallyport Custody Office has failed | Air Conditioning | Room Air Conditioners | 353.9 | Pass | Pass | 0 | 0 | 3 | 2022-11-29 09:01 | 2022-12-02 17:00 | 2022-11-30 08:00 | 2022-12-02 17:00 | 2022-11-30 11:00 |  |  | Mark Kember (30/11/2022) - Work NoteAttend site. Access level el 6 BMS and check sallyport ac operation. Found no faults on BMS. Access level 4 and organise escort from security to sallyport. Check operation of ac unit. Found unit to turn on and operate as normal. Monitor operation and found unit supply air to reach 10 degrees. Return to level 4. Access Basement and check condensing unit. Found coil clean and unit operation is normal. Unable to find any faults with unit. Unit remotes do require new batteries.
MSA-DTWD | WA6292538 | 2 | COMMERCIAL PLUMBING AND GAS | Ground - Block 6 - Urinal Blocked | Plumbing & Drainage | Toilets/Cisterns | 644.06 | Pass | Pass | 0 | 0 | 3 | 2022-11-29 11:08 | 2022-12-02 17:00 | 2022-11-29 11:30 | 2022-12-02 17:00 | 2022-11-29 14:30 |  |  | cleared urinal to allow use, Drainsflush scour drain to clear
MSA-DTWD | WA6292816 | 1 | Australian Airconditioning Services Pty Ltd | G16 Demo Area - AC not working in this area | Air Conditioning | Room Air Conditioners | 608.94 | Pass | Pass | 0 | 0 | 3 | 2022-11-29 13:28 | 2022-11-30 17:00 | 2022-11-30 12:00 | 2022-11-30 17:00 | 2022-11-30 15:00 |  |  | BMS tech required and attended.
MSA-DTWD | WA6292971 | 1 | Equans Mechanical Services Australia | T Block - Level 1 & 2 - BMS requires adjusting (see notes) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 578.42 | Fail | Fail | 1 | 1 | 3 | 2022-11-29 15:18 | 2022-11-30 17:00 | 2022-12-08 12:40 | 2022-11-30 17:00 | 2022-12-08 15:40 |  |  | SEE REPORT
MSA-DFES | WA6293924 | 2 | Australian HVAC Services Pty. Ltd. | Station Office - Air Con blowng room temp. air only | Air Conditioning | Evaporative Coolers | 539.72 | Pass | Pass | 0 | 0 | 3 | 2022-11-30 11:04 | 2022-12-05 17:00 | 2022-12-05 14:00 | 2022-12-05 17:00 | 2022-12-05 17:00 |  |  | Oscar Holil (05/12/2022) - Work NoteArrived on site and spoke to site representative about the issue with the AC. Found out that the casset unit in the office is just blowing room temp air. After speaking to another technician, was able to locate the MSSB and found technical drawings for the aircon units. While at the MSSB found that CU-5 had tripped. Made my way to the plant room and located CU-5. Dismantled the unit and carried out electrical testing. Found no obvious issues with the unit. Made my way back to MSSB and reset the breaker. CU-5 started up again, Attached gauges and measure amps. Found that pressures and amps are good, however office aircon still is supplying poor cooling. After further investigation, found that the technical drawings were wrong and that CU-5 actually serves the corridor aircon. Found out that CU-4 actually serves the office. Opened up CU-4 and found that the unit is running but not ramping up. Did a powercycle and attached my gauges. After the unit co
MSA-DCA | WA6358183 | 1 | EQUANS Mechanical Services (WA) Pty Limited | TIV and AZ Lab - Temperature too cold (see notes) | Air Conditioning | Package | 523.66 | Pass | Pass | 0 | 0 | 3 | 2022-12-06 08:06 | 2022-12-07 17:00 | 2022-12-06 10:00 | 2022-12-07 17:00 | 2022-12-06 13:00 |  |  | TRAVELLED TO SITE AND SIGNED IN AT HBRC RECEPTION. ACCESSED LEVEL 1 LABS AND CHECKED TEMPS. FOUND ALL LAB TEMPS RANGING FROM 21.6 DEGREES TO 24.2 DEGREES. SET POINT FOR ALL LABS IS 22.5 DEGREES. CHECKED ALL LAB SENSORS AND RECORDED READINGS. ACCESSED BMS AND CHECKED TO SEE IF ACTUAL TEMPS CORRESPOND TO BMS TEMP READINGS AND THEY DO. ASKED VARIOUS STAFF MEMBERS IN THE AREAS IF TOO COLD AND THE RESPONSE WAS NOT TODAY TEMPERATURES ARE ALL GOOD. ADVISED TOM FROM ALLERTON OF FINDINGS AND ALSO ADVISED STAFF THAT LABS TEMPERATURES ARE PERFECT AT THE MOMENT AND IF THERE ARE STILL COMPLAINTS THEN WE WILL NEED TO ENGAGE ALLERTON AGAIN.
MSA-DCA | WA6360775 | 0 | Critical Fire Protection & Training | Ground floor - Fire panel - Making noises | Fire Protection Services | Fire Protection - Monitor System | 570.07 | Pass | Pass | 0 | 0 | 3 | 2022-12-07 14:26 | 2022-12-07 16:26 | 2022-12-07 14:30 | 2022-12-07 18:26 | 2022-12-07 17:30 |  |  | Circuit breaker trip- reset following basic checksCarried out checksVoltages within toleranceBatts no date?Test ewis pa only okMonitor as ok at time of departure
MSA-DTAG | WA6361427 | 1 | Australian HVAC Services Pty. Ltd. | Level 3 - Court 32 - Air con isn't working, court is quite warm | Air Conditioning | Room Air Conditioners | 320.94 | Pass | Pass | 0 | 0 | 3 | 2022-12-08 09:51 | 2022-12-09 17:00 | 2022-12-08 12:30 | 2022-12-09 17:00 | 2022-12-08 15:30 |  |  | Attend site. Access BMS and check operation of court 32. Check temps and found temp in court to be 22.5 degrees. Court 32 is served by VAV 3.12 ,Setpoint is 21.5. Cooling demand 66%. Box is currently supplying 580l/s. Drive box to min and max to test damper operation, working ok. Access court room and check calibration of sensor, ok. Monitor operation and found to be working as normal. AC is working as normal at time of inspection.
MSA-DTAG | WA6364202 | 3 | Midolo Building Services | Level 4 - Adult community services - 3x ceiling tiles in staff kitchen water damaged | Building | Internal Walls | 420.33 | Pass | Pass | -1 | -1 | 3 | 2022-12-12 10:06 | 2022-12-19 17:00 | 2022-12-13 09:15 | 2022-12-19 17:00 | 2022-12-13 12:15 |  |  | ceiling tiles replaced
MSA-DTAG | WA6375717 | 0 | Sapio Pty Ltd | L7-L07-12-hearing room 7.10 duress W in 7.8 | Security | Security Management System | 403.31 | Pass | Pass | 0 | 0 | 3 | 2022-12-15 10:08 | 2022-12-15 12:08 | 2022-12-15 11:00 | 2022-12-15 14:08 | 2022-12-15 14:00 |  |  | Investigated reported issue with Duress button.Replaced battery.Tested ok.
MSA-DTWD | WA6376898 | 2 | AWB Co. | JL03 & JL10 - Lighting to storeroom reported not working - Circuit breaker cannot be reset | Electrical | General Electrical | 519.16 | Pass | Pass | 0 | 0 | 3 | 2022-12-16 09:21 | 2022-12-21 17:00 | 2022-12-21 11:00 | 2022-12-21 17:00 | 2022-12-21 14:00 |  |  | Attended site signed in jsa completed, found rcd not able to be reset. Found faulty light in tech office. Removed and got lights back on for technician. Job completed
MSA-DTWD | WA6377432 | 3 | AWB Co. | RETROSPECTIVE - Faulty lighting | Electrical | Lighting, Internal | 696.87 | Pass | Pass | -1 | -1 | 3 | 2022-05-11 06:56 | 2022-05-17 17:00 | 2022-05-12 12:00 | 2022-05-17 17:00 | 2022-05-12 15:00 | 1 |  | Attended site signed in jsa completed. Spoke to Dave gaff about jobs and got keys and list of lights out in B2 building. Replaced various tubes in building. All tested fine and working.*** job completed ****
MSA-DCA | WA6383635 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller in alarm - see notes | Refrigeration | Chiller | 371.62 | Pass | Pass | 0 | 0 | 3 | 2022-12-20 11:54 | 2022-12-21 17:00 | 2022-12-20 12:00 | 2022-12-21 17:00 | 2022-12-20 15:00 |  |  | Travelled to site and signed in. Carried out take 5. Chiller 1 had tripped on water flow fault. Reset fault and checked water flow. Couldn't find a fault but will monitor unit.
MSA-DTAG | WA6392172 | 1 | Schindler Lifts Australia | Judicial Lift #6 - Consistent beeping sound coming from inside lift - see notes | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 3 | 2022-12-23 10:32 | 2022-12-28 17:00 | 2022-12-23 11:12 | 2022-12-28 17:00 | 2022-12-23 14:12 |  |  | Phone beeping. Changed EM.
MSA-DFES | WA6393334 | 2 | Australian HVAC Services Pty. Ltd. | DO office-A/C in District Officer Mike Teraci’s office making loud noise and not cooling correctly | Air Conditioning | Room Air Conditioners | 646.01 | Pass | Pass | -1 | -1 | 3 | 2022-12-28 12:38 | 2023-01-03 17:00 | 2022-12-29 07:30 | 2023-01-03 17:00 | 2022-12-29 10:30
MSA-DTWD | WA6401663 | 2 | AWB Co. | Beaufort street access gate - Gate pins not holding gate locked to ground securely | Building | Steel Fencing & Gates | 750.22 | Fail | Fail | 1 | 1 | 3 | 2023-01-04 14:51 | 2023-01-09 17:00 | 2023-01-16 08:00 | 2023-01-09 17:00 | 2023-01-16 11:00
MSA-DTWD | WA6402377 | 2 | M Construction (WA) | Door has come away from its hinges and cannot close | Building | Doors | 412.12 | Pass | Pass | 0 | 0 | 3 | 2023-01-05 10:38 | 2023-01-10 17:00 | 2023-01-09 09:00 | 2023-01-10 17:00 | 2023-01-09 12:00
MSA-DTWD | WA6405124 | 2 | Precise Air Group | Skills kitchen 3 - fridges tripping RCD | Refrigeration | Refrigerators | 354.73 | Pass | Pass | 0 | 0 | 3 | 2023-01-09 11:38 | 2023-01-12 17:00 | 2023-01-11 09:30 | 2023-01-12 17:00 | 2023-01-11 12:30
MSA-DTWD | WA6407416 | 1 | Precise Air Group | the under bench fridge has stopped working | Refrigeration | Refrigerators | 354.73 | Pass | Pass | 0 | 0 | 3 | 2023-01-10 08:42 | 2023-01-11 17:00 | 2023-01-11 12:30 | 2023-01-11 17:00 | 2023-01-11 15:30
MSA-DFES | WA6408122 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Hot Water System is leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 666.27 | Pass | Pass | 0 | 0 | 3 | 2023-01-10 14:56 | 2023-01-11 17:00 | 2023-01-11 11:00 | 2023-01-11 17:00 | 2023-01-11 14:00
MSA-DCA | WA6414562 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Harry Butler Centre - Chiller 2 Fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 394.14 | Pass | Fail | 0 | 0 | 3 | 2023-01-11 08:31 | 2023-01-11 10:31 | 2023-01-11 10:00 | 2023-01-11 12:31 | 2023-01-11 13:00
MSA-DTAG | WA6425357 | 2 | Midolo Building Services | Ground floor - Plumbing Duct - Remove timber door frame to allow access for new HWU – 07:00am Friday | Building | Doors | 355.92 | Pass | Pass | -1 | -1 | 3 | 2023-01-12 09:25 | 2023-01-17 17:00 | 2023-01-13 07:00 | 2023-01-17 17:00 | 2023-01-13 10:00
MSA-DTWD | WA6430866 | 2 | M Construction (WA) | the door closer leaking oil and door not closing | Building | Doors | 984.66 | Pass | Pass | 0 | 0 | 3 | 2023-01-13 09:47 | 2023-01-18 17:00 | 2023-01-17 06:30 | 2023-01-18 17:00 | 2023-01-17 09:30
MSA-DCA | WA6438869 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Chilled water plant - power status alarm. | Building | Materials | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-01-14 09:34 | 2023-01-14 11:34 | 2023-01-14 10:00 | 2023-01-14 13:34 | 2023-01-14 13:00
MSA-DCA | WA6438894 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 - Plant Room - Boiler has failed | Building | General Building | 546.18 | Pass | Fail | 0 | 0 | 3 | 2023-01-14 11:56 | 2023-01-14 13:56 | 2023-01-14 13:00 | 2023-01-14 15:56 | 2023-01-14 16:00
MSA-DTWD | WA6450570 | 2 | CONNECT SECURITY SYSTEMS | Common room alarm not arming | Security | Access Control | 1333.44 | Pass | Pass | 0 | 0 | 3 | 2023-01-16 12:18 | 2023-01-19 17:00 | 2023-01-17 07:30 | 2023-01-19 17:00 | 2023-01-17 10:30
MSA-DCA | WA6450907 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Gallery 2 & 4- Level 2 - AC 3 alarm humidity | Air Conditioning | Ducted Split System | 546.18 | Fail | Fail | 0 | 0 | 3 | 2023-01-16 17:01 | 2023-01-16 19:01 | 2023-01-16 20:00 | 2023-01-16 21:01 | 2023-01-16 23:00
MSA-DTWD | WA6463461 | 2 | M Construction (WA) | Door lock mechanism will not lock or unlock using the external locking tumbler | Building | Doors | 360.98 | Pass | Pass | 0 | 0 | 3 | 2023-01-17 09:47 | 2023-01-20 17:00 | 2023-01-20 06:30 | 2023-01-20 17:00 | 2023-01-20 09:30
MSA-DTWD | WA6463463 | 2 | AWB Co. | Disabled toilets - faulty door closers - see notes below | Building | Doors | 398.73 | Pass | Pass | 0 | 0 | 3 | 2023-01-17 09:55 | 2023-01-20 17:00 | 2023-01-17 12:00 | 2023-01-20 17:00 | 2023-01-17 15:00
MSA-DCA | WA6482257 | 1 | Critical Fire Protection & Training | Loading Dock Plant Room - Water is passing through fire hydrant pipes. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 772.38 | Pass | Pass | 0 | 0 | 3 | 2023-01-18 08:45 | 2023-01-19 17:00 | 2023-01-18 13:00 | 2023-01-19 17:00 | 2023-01-18 16:00
MSA-DTWD | WA6504410 | 2 | AWB Co. | B207- GPO damaged | Electrical | Lighting, Internal | 624.37 | Pass | Pass | 0 | 0 | 3 | 2023-01-19 15:42 | 2023-01-24 17:00 | 2023-01-24 09:00 | 2023-01-24 17:00 | 2023-01-24 12:00
MSA-DTWD | WA6509764 | 3 | Equans Mechanical Services Australia | BMS - Faulty chilled water bypass valve | Air Conditioning | Building HVAC Maintenance (Major Plant) | 567.42 | Pass | Pass | -1 | -1 | 3 | 2023-01-20 14:58 | 2023-01-30 17:00 | 2023-01-24 13:00 | 2023-01-30 17:00 | 2023-01-24 16:00
MSA-DCA | WA6515576 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Art Gallery of WA - James St-Centenary Gallery-Level 1 -Gallery 14 - Workshop - Room air humidity. | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Fail | 0 | 0 | 3 | 2023-01-22 17:37 | 2023-01-22 19:37 | 2023-01-22 18:50 | 2023-01-22 21:37 | 2023-01-22 21:50
MSA-DCA | WA6519135 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Level - Wearhouse molecular lab 2 - Aircon not working | Air Conditioning | Room Air Conditioners | 523.66 | Pass | Pass | 0 | 0 | 3 | 2023-01-25 13:20 | 2023-01-27 17:00 | 2023-01-27 09:00 | 2023-01-27 17:00 | 2023-01-27 12:00
MSA-DCA | WA6520560 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Gallery 7 - The AC unit is not working. | Air Conditioning | Ducted Split System | 523.66 | Pass | Pass | 0 | 0 | 3 | 2023-01-27 17:42 | 2023-01-28 17:42 | 2023-01-27 18:00 | 2023-01-28 17:42 | 2023-01-27 21:00
MSA-DFES | WA6521389 | 2 | AWB Co. | Dorm 17 - Under bed locker 17.4 - Front of draw has come off | Furniture | Indoor Furniture | 323.145 | Pass | Pass | 0 | 0 | 3 | 2023-01-30 10:22 | 2023-02-02 17:00 | 2023-01-30 12:00 | 2023-02-02 17:00 | 2023-01-30 15:00
MSA-DTWD | WA6526784 | 2 | GRAFFITI FORCE PTY LTD | Male toilets behind Plumbing/Carpentry - Graffiti | Cleaning | Graffiti | 588 | Pass | Pass | 0 | 0 | 3 | 2023-02-01 10:47 | 2023-02-06 17:00 | 2023-02-03 11:30 | 2023-02-06 17:00 | 2023-02-03 14:30
MSA-DTWD | WA6528267 | 2 | Techworks Electrical | fluorescent lights pointing at the whiteboard are all defective | Electrical | Lighting, Internal | 347.39 | Pass | Pass | 0 | 0 | 3 | 2023-02-02 10:15 | 2023-02-07 17:00 | 2023-02-07 07:00 | 2023-02-07 17:00 | 2023-02-07 10:00
MSA-DTWD | WA6528982 | 2 | Complete Pest Management Services | ground-All – Inside and Outside-Mosquito plague | Pest Control | General Pest | 1572.58 | Pass | Pass | 0 | 0 | 3 | 2023-02-02 13:22 | 2023-02-07 17:00 | 2023-02-06 15:00 | 2023-02-07 17:00 | 2023-02-06 18:00
MSA-DCA | WA6533085 | 1 | EQUANS Mechanical Services (WA) Pty Limited | FSU1 Alarm coming from Centenary Gallery - Morning Attendance okay. | Fire Protection Services | Fire Protection - Monitor System | 446.29 | Pass | Pass | 0 | 0 | 3 | 2023-02-04 00:35 | 2023-02-05 00:35 | 2023-02-04 05:00 | 2023-02-05 00:35 | 2023-02-04 08:00
MSA-DTWD | WA6534399 | 1 | WESTERN IRRIGATION PTY LTD | outside D32-retic broken-burst retic line | Landscaping & Gardening | Grounds Maintenance | 591.69 | Pass | Pass | 0 | 0 | 3 | 2023-02-06 12:10 | 2023-02-07 17:00 | 2023-02-07 06:00 | 2023-02-07 17:00 | 2023-02-07 09:00
MSA-DCA | WA6537764 | 0 | EQUANS Mechanical Services (WA) Pty Limited | A/C - steam, generator 2 boiler failed program alarm | Air Conditioning | Materials | 1114.45 | Pass | Pass | 0 | 0 | 3 | 2023-02-07 11:34 | 2023-02-07 13:34 | 2023-02-07 12:00 | 2023-02-07 15:34 | 2023-02-07 15:00
MSA-DCA | WA6538988 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Room Humidity Alarm - Alarming | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-02-08 09:45 | 2023-02-08 11:45 | 2023-02-08 10:00 | 2023-02-08 13:45 | 2023-02-08 13:00
MSA-DTWD | WA6539438 | 3 | Milners Tree Solutions Pty Ltd | Student/Visitor Carpark – Hayman Road End - Tree limbs are interfering with the carpark lighting | Landscaping & Gardening | Tree Lopping | 1350 | Pass | Pass | 0 | 0 | 3 | 2023-02-08 13:11 | 2023-02-15 17:00 | 2023-02-12 09:00 | 2023-02-15 17:00 | 2023-02-12 12:00
MSA-DCA | WA6539774 | 0 | EQUANS Mechanical Services (WA) Pty Limited | AC - Room Humidity Alarm - Alarming | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-02-09 01:00 | 2023-02-09 03:00 | 2023-02-09 01:30 | 2023-02-09 05:00 | 2023-02-09 04:30
MSA-DTWD | WA6540174 | 1 | COMMERCIAL PLUMBING AND GAS | Faulty tap - Contractor aware. | Plumbing & Drainage | Water | 479.17 | Pass | Pass | 0 | 0 | 3 | 2023-02-09 08:56 | 2023-02-10 17:00 | 2023-02-09 17:00 | 2023-02-10 17:00 | 2023-02-09 20:00
MSA-DTWD | WA6540605 | 2 | Protek 24/7 Building & Maintenance | Room 10G5 - threshold tread plate broken on entry door | Flooring | Carpet | 281.06 | Pass | Pass | 0 | 0 | 3 | 2023-02-09 11:57 | 2023-02-14 17:00 | 2023-02-14 08:00 | 2023-02-14 17:00 | 2023-02-14 11:00
MSA-DCA | WA6540826 | 1 | EQUANS Mechanical Services (WA) Pty Limited | SLWA - Level 5 - Plant Room - Boiler 3 going into alarm every 20mins and not producing notifications | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 3 | 2023-02-09 14:44 | 2023-02-10 17:00 | 2023-02-10 07:00 | 2023-02-10 17:00 | 2023-02-10 10:00
MSA-DTWD | WA6540860 | 1 | AHS Services WA Pty Ltd (Anchor) | Broken toilet system | Plumbing & Drainage | Toilets/Cisterns | 1419.48 | Fail | Fail | 1 | 1 | 3 | 2023-02-09 15:09 | 2023-02-10 17:00 | 2023-02-20 13:00 | 2023-02-10 17:00 | 2023-02-20 16:00
MSA-DTWD | WA6543626 | 1 | Equans Mechanical Services Australia | Freezer in kitchen running warm not freezing | Refrigeration | Freezers | 362.11 | Pass | Pass | 0 | 0 | 3 | 2023-02-10 07:24 | 2023-02-10 17:00 | 2023-02-10 12:00 | 2023-02-10 17:00 | 2023-02-10 15:00
MSA-DTWD | WA6560262 | 2 | AWB Co. | Ground floor - Block C - Cleaners room - faulty Fluorescent light with LED light. | Electrical | Lighting, Internal | 596.66 | Pass | Pass | 0 | 0 | 3 | 2023-02-13 08:58 | 2023-02-16 17:00 | 2023-02-13 12:00 | 2023-02-16 17:00 | 2023-02-13 15:00
MSA-DCA | WA6560361 | 2 | Techworks Electrical | M Block - reattach light fitting | Electrical | Lighting, Internal | 401.96 | Pass | Pass | 0 | 0 | 3 | 2023-02-13 09:36 | 2023-02-16 17:00 | 2023-02-16 08:30 | 2023-02-16 17:00 | 2023-02-16 11:30
MSA-DTWD | WA6560974 | 2 | AWB Co. | Loading Bay - next to admin has a hole in the asphalt (see notes) | Paving & Roadworks | Asphalt | 680.92 | Fail | Fail | 0 | 0 | 3 | 2023-02-13 15:12 | 2023-02-16 17:00 | 2023-02-17 07:30 | 2023-02-16 17:00 | 2023-02-17 10:30
MSA-DTWD | WA6572928 | 0 | Jako Industries Pty Ltd | U022-blocked duct extraction machine | Mechanical Services | Pumps |  | Pass | Pass | 0 | 0 | 3 | 2023-02-14 09:40 | 2023-02-14 11:40 | 2023-02-14 10:30 | 2023-02-14 13:40 | 2023-02-14 13:30
MSA-DCA | WA6573777 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 4 Plant room- BMS alarm Steam generator 2 boiler 2 fail programmed alarm | Air Conditioning | Cooling Tower | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-02-14 17:12 | 2023-02-14 19:12 | 2023-02-14 18:00 | 2023-02-14 21:12 | 2023-02-14 21:00
MSA-DTWD | WA6578906 | 1 | Australian Airconditioning Services Pty Ltd | BMS showing a ‘Communication Fault’ on Chiller 2 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 577.5 | Pass | Pass | 0 | 0 | 3 | 2023-02-15 13:02 | 2023-02-16 17:00 | 2023-02-16 11:30 | 2023-02-16 17:00 | 2023-02-16 14:30
MSA-DTWD | WA6586188 | 1 | BAKE-QUIP PTY LTD | Demo Kitchen - Waste away pipe leaking ( see notes) | Plumbing & Drainage | Drainage | 472.5 | Pass | Pass | 0 | 0 | 3 | 2023-02-16 14:08 | 2023-02-17 17:00 | 2023-02-17 07:30 | 2023-02-17 17:00 | 2023-02-17 10:30
MSA-DCA | WA6595654 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidity Alarm AC 6 - Collection Stores - Humidity Alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 444.82 | Pass | Pass | 0 | 0 | 3 | 2023-02-17 04:57 | 2023-02-17 06:57 | 2023-02-17 05:00 | 2023-02-17 08:57 | 2023-02-17 08:00
MSA-DTWD | WA6654076 | 2 | M Construction (WA) | E21-door has sagged and now does not close in its door frame unable to lock the door | Building | Doors | 316.88 | Pass | Pass | 0 | 0 | 3 | 2023-02-21 09:30 | 2023-02-24 17:00 | 2023-02-22 09:45 | 2023-02-24 17:00 | 2023-02-22 12:45
MSA-DTAG | WA6654102 | 0 | AWB Co. | ground court room 2-Air lock area light out-see notes | Electrical | Lighting, Internal | 519.16 | Pass | Fail | 0 | 0 | 3 | 2023-02-21 09:43 | 2023-02-21 11:43 | 2023-02-21 10:45 | 2023-02-21 13:43 | 2023-02-21 13:45
MSA-DCA | WA6667780 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Supply Air Fan 1 - water leaking Outside air chamber | Air Conditioning | Room Air Conditioners | 396.62 | Pass | Pass | 0 | 0 | 3 | 2023-02-21 14:47 | 2023-02-24 17:00 | 2023-02-22 08:00 | 2023-02-24 17:00 | 2023-02-22 11:00
MSA-DCA | WA6669243 | 1 | Techworks Electrical | HMT - Level 1 - Light and fixture falling from ceiling | Electrical | General Electrical | 95.73 | Pass | Pass | 0 | 0 | 3 | 2023-02-22 16:20 | 2023-02-23 17:00 | 2023-02-22 17:30 | 2023-02-23 17:00 | 2023-02-22 20:30
MSA-DCA | WA6672417 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main building - Leve 1 Plant Room - Humidifyer one fault ac 6 - Collection Stores | Air Conditioning | Building HVAC Maintenance (Major Plant) | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-02-24 00:24 | 2023-02-24 02:24 | 2023-02-24 00:32 | 2023-02-24 04:24 | 2023-02-24 03:32
MSA-DTAG | WA6673423 | 2 | Sapio Pty Ltd | Court of Appeal Registry - Duress alarm no 20 - Failed | Security | Security Management System | 398.12 | Pass | Pass | 0 | 0 | 3 | 2023-02-24 13:40 | 2023-03-01 17:00 | 2023-02-28 09:00 | 2023-03-01 17:00 | 2023-02-28 12:00
MSA-DTWD | WA6674673 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire Alarm - See notes | Fire Protection Services | Fire Protection - Monitor System | 720.08 | Pass | Pass | 0 | 0 | 3 | 2023-02-27 11:28 | 2023-02-28 17:00 | 2023-02-27 12:00 | 2023-02-28 17:00 | 2023-02-27 15:00
MSA-DFES | WA6675120 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - Car Park A & B - Lights | Electrical | Lighting, Internal | 635.36 | Pass | Pass | -1 | -1 | 3 | 2023-02-27 15:30 | 2023-03-07 17:00 | 2023-03-03 11:00 | 2023-03-07 17:00 | 2023-03-03 14:00
MSA-DCA | WA6675198 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Humidifier 1 is in fault - Related to AC6 (ongoing problem) | Air Conditioning | Ducted Split System | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-02-27 23:05 | 2023-02-28 01:05 | 2023-02-28 | 2023-02-28 03:05 | 2023-02-28 03:00
MSA-DTWD | WA6681719 | 2 | AHS Services WA Pty Ltd (Anchor) | Café prep room N106b - Leaking kitchen tap | Plumbing & Drainage | Drainage | 348.18 | Pass | Pass | 0 | 0 | 3 | 2023-03-02 11:00 | 2023-03-08 17:00 | 2023-03-07 07:30 | 2023-03-08 17:00 | 2023-03-07 10:30
MSA-DTWD | WA6681856 | 2 | Techworks Electrical | the emergency exit sign to the eastern side door has missing covers so the exit is not indicated | Electrical | Emergency & Exit Lighting | 378.13 | Pass | Pass | 0 | 0 | 3 | 2023-02-27 12:25 | 2023-03-02 17:00 | 2023-03-02 08:30 | 2023-03-02 17:00 | 2023-03-02 11:30
MSA-DTWD | WA6683638 | 0 | LD TOTAL | RETROSPECTIVE WO - DO NOT ATTEND - External area - near B block - broken retic controller for pond | Plumbing & Drainage | Water | 402.8 | Pass | Pass | 0 | 0 | 3 | 2023-03-02 10:00 | 2023-03-02 12:00 | 2023-03-02 10:00 | 2023-03-02 14:00 | 2023-03-02 13:00 | 1
MSA-DCA | WA6684069 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main Gallery-Air condition BMS alarm Humidity out of range AHU07 | Air Conditioning | Room Air Conditioners | 546.18 | Pass | Pass | 0 | 0 | 3 | 2023-03-03 17:04 | 2023-03-03 19:04 | 2023-03-03 17:30 | 2023-03-03 21:04 | 2023-03-03 20:30
MSA-DTWD | WA6689002 | 2 | AWB Co. | lights tripping | Electrical | Lighting, Internal | 372.87 | Pass | Pass | 0 | 0 | 3 | 2023-03-08 08:33 | 2023-03-13 17:00 | 2023-03-10 07:00 | 2023-03-13 17:00 | 2023-03-10 10:00
MSA-DCA | WA6689601 | 2 | Techworks Electrical | The lock on the external power source has been broken/ unable to secure. | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 3 | 2023-03-08 13:27 | 2023-03-13 17:00 | 2023-03-10 06:30 | 2023-03-13 17:00 | 2023-03-10 09:30
MSA-DTWD | WA6693600 | 2 | Equans Mechanical Services Australia | Exhaust fan 4 Insulator cover damaged, requires changing - allowing water into motor assy | Air Conditioning | Ducted Split System | 445.825 | Pass | Pass | -1 | -1 | 3 | 2023-03-10 11:53 | 2023-03-15 17:00 | 2023-03-10 13:00 | 2023-03-15 17:00 | 2023-03-10 16:00
MSA-DTWD | WA6708350 | 2 | AWB Co. | The exhaust fan has stopped working, may need replacing. | Electrical | General Electrical | 519.16 | Pass | Pass | 0 | 0 | 3 | 2023-03-13 17:01 | 2023-03-16 17:00 | 2023-03-14 09:30 | 2023-03-16 17:00 | 2023-03-14 12:30
MSA-DTWD | WA6721592 | 1 | AHS Services WA Pty Ltd (Anchor) | end toilet continuously running wont flush and 1st basin has loose taps | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 3 | 2023-03-14 10:05 | 2023-03-15 17:00 | 2023-03-14 10:30 | 2023-03-15 17:00 | 2023-03-14 13:30
MSA-DCA | WA5672385 | 0 | TK Elevator Australia Pty Ltd | Lift 7 - Stuck on basement level 2 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.9833 | 2022-07-20 09:36 | 2022-07-20 11:36 | 2022-07-20 10:27 | 2022-07-20 13:36 | 2022-07-20 13:26 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped at bottom landing, doors fully open. TTElap fault on controller display. Reset using controller inspection and lift responded.Checked car gate contacts, gave contacts a wipe. With a second person due to very high doors, checked bottom landing lock assemblies. Proceeded on my own to checkother landing lock assemblies. On the Street level, found the potential (small internal plastic keeper pin) for a lock contact to to "hang" up due to fatigued keeper pin. Returnedto the office and obtained 4 lock assemblies. Replaced 1 on Street Level, 2 on Main Stage level, and 1 on Studio Foyer level.Tested lift operation without further fault. Returned the lift to service.
MSA-DTWD | WA5112117 | 2 | Techworks Plumbing | Ground floor - A block - female toilets - Sewage smell coming from sink drains | Plumbing & Drainage | Drainage | 368.95 | Pass | Pass | -1 | -1 | 2.95 | 2022-02-10 13:03 | 2022-02-15 17:00 | 2022-02-10 13:03 | 2022-02-15 17:00 | 2022-02-10 16:00 |  |  | Ran water down all wastes and fixtures, cleaned some basins and floor wastes of hair, no sewer smell just frequently used toilets
MSA-DFES | WA6130468 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | L1 in the MOC whole area has lost power | Electrical | General Electrical | 80.97 | Pass | Pass | 0 | 0 | 2.95 | 2022-10-28 12:28 | 2022-10-31 17:00 | 2022-10-28 13:16 | 2022-10-31 17:00 | 2022-10-28 16:13 |  |  | Terry Webb (28/10/2022) - Work NoteAttended site and located power out to desks, found Tripped rcd, tested and all in working order. Notified staff to monitor.
MSA-DFES | WA5250055 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Dorm 3 - Hot water in bathroom only luke warm | Plumbing & Drainage | HWS/Units Electric & Gas | 666.22 | Pass | Pass | 0 | 0 | 2.9333 | 2022-03-17 07:49 | 2022-03-21 17:00 | 2022-03-18 07:19 | 2022-03-21 17:00 | 2022-03-18 10:15 |  |  | HAD TO REPLACES A TMV VALVE IN ROOF SPACE 15mm
MSA-DTWD | WA6258418 | 1 | CONNECT SECURITY SYSTEMS | swipe card not working also 2 in A/block staff area no room numbers-see notes | Security | Security Management System | 482.89 | Pass | Pass | 0 | 0 | 2.9333 | 2022-11-25 12:03 | 2022-11-28 17:00 | 2022-11-28 07:26 | 2022-11-28 17:00 | 2022-11-28 10:22 |  |  | reprogrammed electric lock doors and corrected errors
MSA-DTWD | WA6482653 | 3 | M Construction (WA) | ECO 1&2- x2 hand towel dispensers have come away from the wall | Building | General Building | 303.76 | Pass | Pass | -1 | -1 | 2.9167 | 2023-01-18 11:58 | 2023-01-25 17:00 | 2023-01-20 08:35 | 2023-01-25 17:00 | 2023-01-20 11:30
MSA-DTWD | WA5977002 | 2 | AHS Services WA Pty Ltd (Anchor) | L2 A 254 male toilet-Tap is spinning on hand basin | Plumbing & Drainage | Water | 476.98 | Fail | Fail | 0 | 0 | 2.9167 | 2022-09-27 13:01 | 2022-09-30 17:00 | 2022-10-03 12:35 | 2022-09-30 17:00 | 2022-10-03 15:30 |  |  | Completed
MSA-DTWD | WA5706898 | 2 | AWB Co. | 3D4 fuel injection room - Water has entered new LED light causing it to flash | Electrical | Lighting, Internal | 194.275 | Pass | Pass | -1 | -1 | 2.9 | 2022-08-11 14:13 | 2022-08-16 17:00 | 2022-08-12 10:30 | 2022-08-16 17:00 | 2022-08-12 13:24 |  |  | Attended site signed in jsa completed. Lights tripped in board R4 due to water in light. Disconnected and replaced with one from site store. Cleaned dried light and mopped floor. Job completed
MSA-DTAG | WA6111831 | 3 | Gilmour & Jooste Electrical | Court Room 2 and Upper Custody-lights need changing - see notes | Electrical | Lighting, Internal | 161.26 | Pass | Pass | 0 | 0 | 2.9 | 2022-10-21 10:46 | 2022-10-28 17:00 | 2022-10-25 07:00 | 2022-10-28 17:00 | 2022-10-25 09:54 |  |  | Repaired lights to court 1 and upper custody. Tested and working.
MSA-DTWD | WA5288510 | 2 | ECO PLUMBING AND GAS PTY LTD | E49 Office - External - Grease Arrestor Pit 4 – Outlet square damaged | Plumbing & Drainage | Materials | 345.265 | Pass | Pass | 0 | 0 | 2.8833 | 2022-03-23 11:15 | 2022-03-28 17:00 | 2022-03-28 11:25 | 2022-03-28 17:00 | 2022-03-28 14:18 |  |  | Replaced curved square in grease pit outlet
MSA-DCA | WA5068961 | 1 | Techworks Plumbing | Jubilee Building - Ground Floor - Plant room 3 - Storm water pump controller fault | Plumbing & Drainage | Drainage | 997.04 | Pass | Pass | 0 | 0 | 2.8667 | 2022-01-19 13:08 | 2022-01-20 17:00 | 2022-01-19 13:08 | 2022-01-20 17:00 | 2022-01-19 16:00 |  |  | Inspected pump board to find overload alarm, Reset alarm and tested, both pump switch on, Searched and found pump pit, visual inspection of pump and find both working, Possible issue with submersible transducer causing wrong levels ,
MSA-DCA | WA5833807 | 2 | TK Elevator Australia Pty Ltd | Lift 5 - Out of order illuminated on display screen | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.8667 | 2022-09-06 11:57 | 2022-09-09 17:00 | 2022-09-06 13:49 | 2022-09-09 17:00 | 2022-09-06 16:41 |  |  | Lift stopped lvl 4, safety line open, found eta relays up inspected tape reader and reset repaired wiring to reader head, inspected controller,tested and reset system, lift back in service.
MSA-DFES | WA6414403 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | accounting error in the ProMAP claim - Relating to WA5687329 - Please do not attend | Plumbing & Drainage | Drainage | 3904.65 | Pass | Pass | 0 | 0 | 2.8667 | 2023-01-11 07:20 | 2023-01-13 17:00 | 2023-01-13 08:00 | 2023-01-13 17:00 | 2023-01-13 10:52
MSA-DCA | WA5497166 | 2 | Earth & Water Pty Ltd | Wet lands- Ground External - Water level of Wetlands is approx. 100mm lower than usual. | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 2.85 | 2022-06-09 15:07 | 2022-06-14 17:00 | 2022-06-10 11:39 | 2022-06-14 17:00 | 2022-06-10 14:30 |  |  | JOB COPMLETED -
MSA-DTWD | WA5215449 | 2 | Precise Air Group | Block C - room C44 - Chiller plant circuit 2 not running | Refrigeration | Chiller | 13736.6 | Fail | Fail | 7 | 7 | 2.8333 | 2022-03-10 12:20 | 2022-03-15 17:00 | 2022-05-05 11:27 | 2022-03-15 17:00 | 2022-05-05 14:17 |  |  | Subcontractor has completed works - service report to follow.
MSA-DCA | WA5496306 | 1 | Techworks Electrical | James Street entrance - Ground – external - Issues with bollards - See notes below | Equipment | Electrical Equipment | 303.51 | Pass | Pass | 0 | 0 | 2.8333 | 2022-06-09 09:06 | 2022-06-10 17:00 | 2022-06-09 09:10 | 2022-06-10 17:00 | 2022-06-09 12:00 |  |  | Opened base of Ballard and found the pressure relief valve, cracked that open a touch more to let more air out on the way down to make it quicker. Tested and all working well.
MSA-DCA | WA5569263 | 0 | Techworks Plumbing | Ground Floor - Jubilee building -UAC - blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 998.59 | Pass | Pass | 0 | 0 | 2.8333 | 2022-06-27 13:09 | 2022-06-27 15:09 | 2022-06-27 13:10 | 2022-06-27 17:09 | 2022-06-27 16:00 |  |  | Attended site and signed in at security Went to jubilee building to unblock the drainsWe used the drain machine to unblock the drains the blockage was quite far down the drain After it was unblocked we did a camera inspection and located a section of pipe with a rubber joiner where the pipe has not been pushed all the way in so a lot of toilet paper gets caught there we have marked it on the floor we also found the drain was holding alot of water and debri possibly because of lack of fallCompleted a dilapidation report Cleaned up and left site Completed paperwork
MSA-DFES | WA4992251 | 1 | ADVANCED LOCK & KEY | Unable to gain access in the site - keys arent working - see notes below | Security | Locksmith | 907.5 | Pass | Pass | 0 | 0 | 2.8333 | 2022-01-06 09:06 | 2022-01-07 17:00 | 2022-01-07 08:50 | 2022-01-07 17:00 | 2022-01-07 11:40 |  |  | LOST KEYSUnable to gain access, Re-key site, make keys
MSA-DTWD | WA5385521 | 3 | AHS Services WA Pty Ltd (Anchor) | Tap to Male toilet A Block West End Ground floor basin leaking | Plumbing & Drainage | Toilets/Cisterns | 531.1275 | Pass | Pass | -1 | -1 | 2.8333 | 2022-04-29 10:21 | 2022-05-06 17:00 | 2022-05-02 10:00 | 2022-05-06 17:00 | 2022-05-02 12:50 |  |  | Took a while to isolate water.Reseated and fitted new washers to hot and cold taps male toilets grad floor
MSA-DTWD | WA5613519 | 2 | Water2water Pty Ltd | F-Shed (Yellagonga Room) wall mounted Zip urn has no hot water | Plumbing & Drainage | Water | 385.005 | Pass | Pass | 0 | 0 | 2.8333 | 2022-07-14 13:09 | 2022-07-19 17:00 | 2022-07-18 12:40 | 2022-07-19 17:00 | 2022-07-18 15:30 |  |  | Taken unit apart and removed blockage Taken apart and cleaned solenoids to restore normal flowTested and checked, now all ok.
MSA-DCA | WA5839074 | 0 | TK Elevator Australia Pty Ltd | Main Passenger Lift is stuck on level 1 | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 2.8333 | 2022-09-09 09:07 | 2022-09-09 11:07 | 2022-09-09 11:28 | 2022-09-09 13:07 | 2022-09-09 14:18 |  |  | On arrival, lift at ground floor,car doors slightly open. Test tool reading "door stall" and DTC. DO contactor pulling in, dropping out, but thedoors are not moving. Lowered lift car to access the OVL door operator. Checked motor brushes, all ok. Checked finger contacts in the control box. Some contacts had pipsthat had formed with use. Cleaned all contacts that are being used in the door circuit. Tested door operation, doors opening and closing. Checked through the site history aslift has had numerous callouts. Replaced LV1,LV2 and LVC relays. Replaced all 4 tape head guides.Removed the car operating panel to check button type. The ground floor button pressule was unserviceable. Fitted temporary replacement, replacement pressules to besourced and fitted. Cleared the event log and returned the lift to service.
MSA-DTWD | WA5699446 | 2 | AWB Co. | Bay 27 - faulty 3 phase power socket | Electrical | General Electrical | 486.17 | Pass | Pass | 0 | 0 | 2.8167 | 2022-08-10 09:43 | 2022-08-15 17:00 | 2022-08-15 10:15 | 2022-08-15 17:00 | 2022-08-15 13:04 |  |  | Attended site and signed in. Located F block and found gpo with no power after further fault finding located fuses in service duct with 2 blown fuses. Located spare fuses and replaced. All now working. Informed site
MSA-DCA | WA5567689 | 1 | GPS Plumbing & Gas Services PtyLtd | Male public toilet - Broken toilet seat and leak at base from degraded seal | Plumbing & Drainage | Toilets/Cisterns | 1886.9925 | Fail | Fail | 0 | 0 | 2.8 | 2022-06-24 11:31 | 2022-06-27 17:00 | 2022-06-28 09:30 | 2022-06-27 17:00 | 2022-06-28 12:18 |  | WACCES | Replaced leaking toilet pan and seat to male toilets ground floor 2nd cubicle.
MSA-DTAG | WA4994948 | 0 | Seme Solutions Pty Ltd | Justice Side - security system isn't working - see notes below | Security | CCTV Surveillance | 227.5 | Pass | Pass | 0 | 0 | 2.7833 | 2022-01-10 09:08 | 2022-01-10 11:08 | 2022-01-10 10:00 | 2022-01-10 13:08 | 2022-01-10 12:47 |  |  | Found GMS server undergoing system software failure after power failure. Found system frozen with GMS in boot mode, power cycled server and checked system restore correctly, started system software on workstation 1 on 2.Also found CCTV software offline booted system and populated images.System all ok
MSA-DCA | WA6425845 | 1 | SCAVENGER SUPPLIES PTY LTD | Hackatt Hall - Ground Floor - Studio 1 - Leaking fire sprinkler | Fire Protection Services | Smoke and Heat Detection | 664.08 | Pass | Pass | 0 | 0 | 2.7833 | 2023-01-12 12:15 | 2023-01-13 17:00 | 2023-01-12 15:13 | 2023-01-13 17:00 | 2023-01-12 18:00 |  | WACCES
MSA-DTWD | WA6529079 | 2 | Techworks Plumbing | first toilet when you walk in - Toilet leaking at the back | Plumbing & Drainage | Toilets/Cisterns | 539.6 | Pass | Pass | -1 | -1 | 2.7833 | 2023-02-02 14:19 | 2023-02-07 17:00 | 2023-02-03 07:00 | 2023-02-07 17:00 | 2023-02-03 09:47
MSA-DTWD | WA5092574 | 3 | AWB Co. | B5 - Level 2 - A254 - Replace 10 x blown fluros | Electrical | Lighting, Internal | 735.54 | Pass | Pass | 0 | 0 | 2.75 | 2022-01-28 08:08 | 2022-02-04 17:00 | 2022-02-03 08:00 | 2022-02-04 17:00 | 2022-02-03 10:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Walked around site and counted how may Fluros were out in B5. Went to wholesaler and picked up tubes and starters for job. Also picked up 10x 2pin 18w compact Fluros as requested by fm. ( as per Po ). Returned to site and went through to change all faulty tubes and starters. Took before and after pictures of fittings. Packed up. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5093431 | 2 | AWB Co. | E Block - Ground level - E30 Small scale kitchen - Faulty 3 phase power outlet | Electrical | General Electrical | 512.93 | Pass | Pass | 0 | 0 | 2.75 | 2022-01-28 14:41 | 2022-02-02 17:00 | 2022-02-01 11:00 | 2022-02-02 17:00 | 2022-02-01 13:45 |  |  | Attended site and signed in. Completed JSA. Located faulty switch in e30 for oven. Supply and replace 32amp switch to outlet B15, tested all okay. Repaired light in hallway with new tombstones tube and starters as asked by site. Signed out. Job complete
MSA-DTWD | WA5115931 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 3 - lights not on at night | Electrical | General Electrical | 298.935 | Pass | Pass | 0 | 0 | 2.75 | 2022-02-11 10:02 | 2022-02-16 17:00 | 2022-02-16 12:30 | 2022-02-16 17:00 | 2022-02-16 15:15 |  |  | Arrived on site at 12:30. Went and spoke with mark and he explained lights at top of stairs above landing on level 3 have been turning off around 8pm while classes are sill running. located replay in level 4 switchboard that controls lights went to cbus computer in basement and edited schedule controlling the relay. Deleted old off signals for night and re added them. Left site at 15:15
MSA-DTWD | WA5133392 | 1 | Equans Mechanical Services Australia | E Block - Ground - Room/Office - E74 Asian Cooking Kitchen - Evap Unit not cooling – North end | Air Conditioning | Room Air Conditioners | 455.23 | Pass | Pass | 0 | 0 | 2.75 | 2022-02-15 10:26 | 2022-02-16 17:00 | 2022-02-16 08:00 | 2022-02-16 17:00 | 2022-02-16 10:45 |  |  | Water pipes had fallen off water distribution trays above pads. Refitted and secured pipes and checked operation. All ok
MSA-DTWD | WA5193725 | 2 | AWB Co. | E200 - Pedestal Grinder #69 in E Block has a damaged E-Stop switch and cover. Tagged out of service | Electrical | General Electrical | 565.37 | Pass | Pass | 0 | 0 | 2.75 | 2022-02-25 13:31 | 2022-03-02 17:00 | 2022-02-28 08:45 | 2022-03-02 17:00 | 2022-02-28 11:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located grinder with out of service tag in E200 Fitting and machining. De energised circuit. Figured out what we needed to get from wholesaler. Went to wholesaler to pick up parts. Returned to site and put together new face plate for stop and start button. Took off old one. Put new one on. Re energised circuit. Tested stop and start buttons. Both are working as intended. Packed and cleaned up work area. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5194932 | 1 | Equans Mechanical Services Australia | Air Conditioner still not working, blowing warm air - see notes below | Air Conditioning | Room Air Conditioners | 266.86 | Pass | Pass | 0 | 0 | 2.75 | 2022-02-28 09:39 | 2022-03-01 17:00 | 2022-02-28 13:15 | 2022-03-01 17:00 | 2022-02-28 16:00 |  |  | CHECKED UNITFOUND ROOM AT 22DEG ALL OK, CHECKED UNIT OPERATION ALL OK NO FAULTS LOCATED. NORESETS REQUIRED. AS DISCUSSED PREPARING QUOTE TO CHANGE UNIT OUT, POSSIBLE AGERUNNING LOW CAPACITY THAN REQUIRED FOR ROOM. CLEANED UP TAKEN UNIT DETAILS TOREPLACE UNIT. ALSO ON OFF SWITCH TO BE REPLACED AND CONTROL BOARD TO TB PRESENTAND PLACED IN CEILING NEXT EVAPORATIVE UNIT. COMPLETED PAPERWORK AND SIGNED OUT.CALL OUT COMPLETED
MSA-DFES | WA5207524 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Gym and Main area - 2 x fluros are faulty and check for tohers please s | Electrical | General Electrical | 968.305 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-08 13:43 | 2022-03-09 17:00 | 2022-03-08 14:45 | 2022-03-09 17:00 | 2022-03-08 17:30 |  |  | Arrived on site at 1445. Located 28 faulty fluorescent tube lights in gym/main area and replaced/re-energised them. Discovered faulty ballast within 1 of the light fittings. Informed client of completed works and faulty ballast and left site at 1730.
MSA-MRWA | WA5208520 | 2 | Water2water Pty Ltd | Billie Hot / Cold Tap loose at base (LHS) | Plumbing & Drainage | Water | 696.0275 | Pass | Pass | -1 | -1 | 2.75 | 2022-03-09 09:13 | 2022-03-14 17:00 | 2022-03-09 11:00 | 2022-03-14 17:00 | 2022-03-09 13:45 |  |  | Replaced tap & button base - Billi Quadra.
MSA-DTWD | WA5390357 | 0 | ECO PLUMBING AND GAS PTY LTD | All toilets on ground floor, C block over flowing | Plumbing & Drainage | Drainage | 480.265 | Pass | Pass | 0 | 0 | 2.75 | 2022-05-02 12:13 | 2022-05-02 14:13 | 2022-05-02 13:15 | 2022-05-02 16:13 | 2022-05-02 16:00 |  |  | Cleared blockage using jetter
MSA-DTWD | WA5400398 | 3 | Equans Mechanical Services Australia | Roof void-Opening in ducting is blowing air into roof void - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 266.86 | Fail | Fail | 0 | 0 | 2.75 | 2022-05-10 09:56 | 2022-05-17 17:00 | 2022-05-18 13:15 | 2022-05-17 17:00 | 2022-05-18 16:00 |  |  | Gathered ladder inspection done on ceiling space located exposed ducting. Air blowing through closed damper. Gathered required tools, returned and blocked and sealed diffuser. Sealed with silver tape. Small miscellaneous charge on van stock. Checked works all completed cleaned up work area. Completed paperwork and signed out.
MSA-DTWD | WA5479282 | 3 | AWB Co. | South Block - Level 1 - Gardens at SW corner of building - Repairs required to log fencing | Building | General Building | 380.435 | Pass | Pass | 0 | 0 | 2.75 | 2022-05-27 08:40 | 2022-06-03 17:00 | 2022-06-03 08:00 | 2022-06-03 17:00 | 2022-06-03 10:45 |  |  | Refix loose fencing back together.
MSA-DCA | WA5494351 | 2 | Protek 24/7 Building & Maintenance | Ground Floor - Ladies Bathroom - Door is rubbing on floor, very hard to open | Building | General Building | 463.75 | Fail | Fail | 1 | 1 | 2.75 | 2022-06-07 14:16 | 2022-06-10 17:00 | 2022-06-14 12:30 | 2022-06-10 17:00 | 2022-06-14 15:15 |  |  | Repair door in ladies toilet
MSA-DTWD | WA5534701 | 2 | AWB Co. | V Block - Security Lights faulty - external | Electrical | Lighting, Internal | 692.7 | Pass | Pass | 0 | 0 | 2.75 | 2022-06-16 13:28 | 2022-06-21 17:00 | 2022-06-20 13:15 | 2022-06-21 17:00 | 2022-06-20 16:00 |  |  | Attended site and signed in, completed jsa,located security lighting in v block, tested lighting and working as intended,checked that timer is programmed right, found 1x light not working above toilet doors, opened light and internals had been removed, spoke to fm and he wanted light to be replaced, went to wholesaler and picked up parts, returned to site, removed old light and fitted new, disposed of old light in bin, packed up, tested light and working as intended, completed paperwork, signed out ***job completed***
MSA-DTAG | WA5548136 | 3 | Midolo Building Services | Waiting area - Several ceiling tiles show old water stains | Flooring | Tiling | 531.33 | Pass | Pass | -1 | -1 | 2.75 | 2022-06-17 08:16 | 2022-06-24 17:00 | 2022-06-20 11:45 | 2022-06-24 17:00 | 2022-06-20 14:30 |  |  | NEW CEILING TILES INSTALLED
MSA-DTWD | WA5676976 | 2 | AWB Co. | Faulty 3 Phase plug on oven needs to be replaced | Electrical | General Electrical | 766.8825 | Pass | Pass | 0 | 0 | 2.75 | 2022-07-25 11:46 | 2022-07-28 17:00 | 2022-07-27 08:45 | 2022-07-28 17:00 | 2022-07-27 11:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located room. Found to be faulty power outlet and kiln missing plug. Left site to pick up parts. Returned and replaced 1x 56series outlet and 1x 20a plug to suit. Tested for correct operation. Notified relevant personnel of works completed, **job complete**
MSA-DTWD | WA5790652 | 3 | AWB Co. | B127 - Dust Extractor not automatically coming on | Equipment | Electrical Equipment | 529.92 | Pass | Pass | -1 | -1 | 2.75 | 2022-08-22 11:49 | 2022-08-29 17:00 | 2022-08-24 11:45 | 2022-08-29 17:00 | 2022-08-24 14:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located woodwork room with faulty exhaust fan. Located Contactor box and control box, tested contactors and followed cables back to control box, found that relay was faulty , went to wholesaler and picked up parts, returned to site, and replaced relay, tested fan and working as intended , site happy, packed up cleaned up. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5862164 | 2 | AWB Co. | Damaged bracket that supports TV monitor | Building | Internal Walls | 465.0975 | Pass | Pass | 0 | 0 | 2.75 | 2022-09-13 14:12 | 2022-09-16 17:00 | 2022-09-16 13:15 | 2022-09-16 17:00 | 2022-09-16 16:00 |  |  | Remove existing bracket for pull down screen, install new bracket for tv, attach tv
MSA-DFES | WA6357019 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - Aircons tripping over night - breakers have been reset | Electrical | General Electrical | 417.445 | Pass | Pass | 0 | 0 | 2.75 | 2022-12-05 10:27 | 2022-12-06 17:00 | 2022-12-05 14:00 | 2022-12-06 17:00 | 2022-12-05 16:45 |  |  | Arrived onsite and signed in at 14:00 to investigate breaker tripping in GF DB. Found that the 40A breaker was tripping at roughly 7A and had a loose blue phase connection. Picked up parts from wholesaler 15:30-16:15 and replaced with new 40A NHP breaker and tested that all Aircons worked properly whilst onsite. Notified staff and left site at 16:45.
MSA-DTAG | WA6357242 | 1 | Midolo Building Services | Custody - Cell 4 and surround - Leak (see notes) | Plumbing & Drainage | Water | 293.21 | Pass | Pass | 0 | 0 | 2.75 | 2022-12-05 11:50 | 2022-12-06 17:00 | 2022-12-06 07:15 | 2022-12-06 17:00 | 2022-12-06 10:00 |  | WACCES | No evidence of leaking - Email sent to site asking if it is. Email attached from site confirming that it is not. - INSPECT ONLY
MSA-DTWD | WA6360263 | 3 | AWB Co. | Room 240 - Light out in IT office | Electrical | Lighting, Internal | 634.32 | Pass | Pass | 0 | 0 | 2.75 | 2022-12-07 09:57 | 2022-12-14 17:00 | 2022-12-12 11:45 | 2022-12-14 17:00 | 2022-12-12 14:30 |  |  | Attended site and signed in,completed jsa , spoke with fm about job, went to location of site to identify correct new lights needed. Check storage and found no spares, went to wholesaler to purchase new lights as lamps weren’t standard . Returned to site. Went back and replaced faulty lamps, All lights now working as intended, Completed paper work, signed out. ***Job complete***
MSA-DFES | WA6362173 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Administration - TV aerial on roof has fallen over - see notes | ICT/Audiovisual | Hardware / Equipment | 428.5575 | Pass | Pass | -1 | -1 | 2.75 | 2022-12-09 08:03 | 2022-12-16 17:00 | 2022-12-09 14:00 | 2022-12-16 17:00 | 2022-12-09 16:45 |  |  | 8/12/2022 Attended site at 14:15. Proceeded to investigate fallen antenna. We found that the brick supporting the antenna was quiteold and has come away from the mortar causing the antenna to lay on the roof. DUe to the age and frailty of thesurrounding bricks and flashing I don’t think remounting via a hockey stick mount is appropriate, however using a tin roofmount may suit better. Informed staff of need to return with parts and left site at 15:00.9/12/2022Arrived on site at 1400, replaced mounting for TV antenna and tested signal. All in good order. Alerted staff and signed out at 1600.
MSA-DTWD | WA6402725 | 2 | AWB Co. | F30 - External - Damaged external fluro fitting | Electrical | General Electrical | 651.93 | Pass | Pass | 0 | 0 | 2.75 | 2023-01-05 16:04 | 2023-01-10 17:00 | 2023-01-09 11:00 | 2023-01-10 17:00 | 2023-01-09 13:45
MSA-DTWD | WA6414715 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 1 - East Level - Male Toilets - Toilet Blocked | Plumbing & Drainage | Toilets/Cisterns | 852.3125 | Pass | Pass | -1 | -1 | 2.75 | 2023-01-11 09:31 | 2023-01-16 17:00 | 2023-01-12 12:30 | 2023-01-16 17:00 | 2023-01-12 15:15
MSA-DTWD | WA6693615 | 2 | AWB Co. | S block - Open plan room with beds - Rain water leak towards back of open plan with beds | Plumbing & Drainage | Drainage | 181.575 | Pass | Pass | 0 | 0 | 2.75 | 2023-03-10 12:08 | 2023-03-15 17:00 | 2023-03-13 12:30 | 2023-03-15 17:00 | 2023-03-13 15:15
MSA-DCA | WA4995655 | 3 | FCT SURFACE CLEANING | Outside – near stairwell 5 - Graffiti | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 2.75 | 2022-01-10 14:41 | 2022-01-17 17:00 | 2022-01-11 10:30 | 2022-01-17 17:00 | 2022-01-11 13:15 |  |  | Attended site and removed graffiti from State Library outside — near stairwell 5.
MSA-DTWD | WA5081577 | 3 | AWB Co. | Level 5 - W 507 - Replace broken electrical skirting | Electrical | General Electrical | 291.74 | Pass | Pass | 0 | 0 | 2.75 | 2022-01-20 16:32 | 2022-01-28 17:00 | 2022-01-28 07:00 | 2022-01-28 17:00 | 2022-01-28 09:45 |  |  | Attended site and signed in. Completed JSA. Located all rooms in west block level 5. Checked out where missing covers where. Found 3 rooms to have electrical cabling exposed by missing covers. Went through and found spare duct covers on site. Cut and fitted to exposed wiring in duct over various rooms. Made safe all cables. Parts of duct still open but no hazard exists. All ducts are okay. Signed out. Job complete
MSA-DFES | WA5107170 | 3 | Protek 24/7 Building & Maintenance | kitchen area - Door needs repair/replacement door handle /latch set. Lock is jammed & see notes. | Building | Doors | 351.465 | Pass | Pass | -1 | -1 | 2.75 | 2022-02-07 15:08 | 2022-02-14 17:00 | 2022-02-09 08:15 | 2022-02-14 17:00 | 2022-02-09 11:00 |  |  | Replaced sets
MSA-DTAG | WA5151189 | 2 | AWB Co. | Level 10 -Various - Replace fluros in wedding rooms -2 x Banksia ceremony room -1 x grevillea wa | Electrical | General Electrical | 486.55 | Pass | Pass | 0 | 0 | 2.75 | 2022-02-17 11:20 | 2022-02-22 17:00 | 2022-02-21 07:00 | 2022-02-22 17:00 | 2022-02-21 09:45 |  |  | Attended site, signed in, completed jsa,went to security office and signed in, called contact number at 7.09am and left message , went and got materials for job , returned to site and called site contact, site contact came down and took us up to level 10, went around to wedding rooms and found lights which were out , replaced 2x lamps in banksia room, replaced 2x down lights in feature light area of wedding rooms , had issues with ceiling panels as insulation was jammed in between, got all ceiling panels back in place, all lights working as intended, packed up, cleaned up, completed paperwork,signed out Job completed
MSA-DTWD | WA5176323 | 2 | AWB Co. | D Block -Replace lights not working in D111 Expo area | Electrical | General Electrical | 851.99 | Pass | Pass | 0 | 0 | 2.75 | 2022-02-21 14:03 | 2022-02-24 17:00 | 2022-02-22 10:00 | 2022-02-24 17:00 | 2022-02-22 12:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located lights that were faulty in D block. Contacted fm and got remote off of him so we could lower lights. Lowered one light and took globe out of it to see what we needed to pick up from pro lamps. Went to pro lamps to pick up parts as per po. Returned to site and replaced 3x globes in the entrance foyer area. Went up to level 2 and 3 and replaced faulty globes with new ones. Went to main area on ground floor and used remote to lower lights so we could replace globes. Last light we did ( number 13 ) would not lower properly with remote. Light number 6 was not making contact with holder and there for didn’t work , tried to jiggle light with conduit out to see if we could nudge it over a little so it would make contact and turn on. This was unsuccessful. Spoke to fm to notify him about the issue with light number 6 and 13. Took pictures. Completed paperwork. Signed out ***Job completed***
MSA-DTWD | WA5201218 | 2 | AWB Co. | Water dripping into room inside classroom door | Roofing | Tiled Roofing | 574.98 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-02 12:46 | 2022-03-08 17:00 | 2022-03-08 06:45 | 2022-03-08 17:00 | 2022-03-08 09:30 |  |  | Sourse leak b6 . I believe there could be multiple reasons this is happening.Seals on window some damage on window frame seals.I sealed the ridge flashing the flashing that goes up under neath the windows. We cleaned back refixed and resealed the box gutter joints
MSA-DFES | WA5208558 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - bush fire technical services - 4x lights out | Electrical | Lighting, Internal | 563.829 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-09 09:24 | 2022-03-14 17:00 | 2022-03-14 09:45 | 2022-03-14 17:00 | 2022-03-14 12:30 |  |  | Attend site 0945. Was show to bushfire technical Services open office area where lights were reported to not be working, as well as the passage ways leading to the office space. I found 13 fittings to not be working in the open area office and 4 fittings not working in the passageways. I replaced 13 tubes in the office space and 8 lamps in the passageways, lights were tested and working okay. Informed site rep of outcomes and left site at 1230.
MSA-DTWD | WA5209161 | 1 | AWB Co. | N block - ground - Outside security lights not coming on | Electrical | Lighting, External | 346.28 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-09 14:11 | 2022-03-10 17:00 | 2022-03-10 13:00 | 2022-03-10 17:00 | 2022-03-10 15:45 |  |  | Attended site and signed in. Completed JSA. Located N block and found lights along walkway outside doors and toilets, tested none coming on. Tested pe cell and all okay. Checked out lights and found all to have dead lamps. Supply and replace all 5 lights with new lamps, 1 light needed tombstones, replaced them also. Supply and replace light at toilets with new bunker as it had fallen apart. Retested to all come on pe cell. All okay. Signed out. Job complete
MSA-DCA | WA5226933 | 3 | FCT SURFACE CLEANING | Alexander Library Building - Ground - Outside – near stairwell 5 - and to the substation entry door | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 2.75 | 2022-03-14 15:35 | 2022-03-21 17:00 | 2022-03-24 06:45 | 2022-03-21 17:00 | 2022-03-24 09:30 |  |  | Removed graffiti from Alexander Library Building - Ground - Outside — near stairwell 5 - and to the substation entry door.
MSA-DFES | WA5231362 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Front Offices - Level 2 - Reception - see details below | Electrical | Lighting, External | 298.935 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-15 10:51 | 2022-03-18 17:00 | 2022-03-18 09:15 | 2022-03-18 17:00 | 2022-03-18 12:00 |  |  | Arrived onsite at 9:15 to investigate lights not working correctly, found lights were controlled by sensor with a light switch connected as means of an override to switch lights off. Sensors are installed into too large of an area to constantly sense motion when staff are working in office and resulted in lights turning off while staff are in office moving around. Upon investigating how to bypass sensors had difficulty finding where it was all switched from to change configuration of wiring but was able to locate where it was all controlled from and rewired the circuit to bypass the sensor and purely only work from the light switch. Lights are now always on when switch is on and staff are happy with result. Left site at 12:00
MSA-DFES | WA5231848 | 3 | Australian HVAC Services Pty. Ltd. | Room 6 – communal area - A/C 12 (a DAIKON unit) is not working - see details below | Air Conditioning | Room Air Conditioners | 304.035 | Pass | Pass | -1 | -1 | 2.75 | 2022-03-15 15:58 | 2022-03-22 17:00 | 2022-03-16 10:00 | 2022-03-22 17:00 | 2022-03-16 12:45 |  |  | Ac working well
MSA-DTWD | WA5290957 | 2 | AWB Co. | E315 - 6x Damaged double Fluorescent lights with broken covers | Electrical | General Electrical | 873.29 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-25 13:17 | 2022-03-30 17:00 | 2022-03-28 07:00 | 2022-03-30 17:00 | 2022-03-28 09:45 |  |  | Attended site and signed in. Completed JSA. Went to work area. Looked at job and figured out what we needed for job. Went to wholesaler to pick up parts. Returned to site. Prepared all lights and disposed of rubbish. Isolated circuit. Took down old lights and replaced with new LED fittings. Cleaned up work area and packed up. Turned circuit back on. Lights are all working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5296798 | 1 | AWB Co. | Damaged extraction control box and has exposed wires as well | Electrical | General Electrical | 385.3 | Pass | Pass | 0 | 0 | 2.75 | 2022-03-30 16:17 | 2022-03-31 17:00 | 2022-03-31 07:00 | 2022-03-31 17:00 | 2022-03-31 09:45 |  |  | Attended site signed in completed jsa. Spoke with frank site fm about job. Found faulty switch in auto sparky workshop. Sourced new switch and replaced. Tested correctly and all lamps on.*** job completed ***
MSA-DFES | WA5395671 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Laundry - Washing machine tap/hose leaking inside cabinet | Plumbing & Drainage | Water | 341.08 | Fail | Fail | 0 | 0 | 2.75 | 2022-05-05 14:53 | 2022-05-10 17:00 | 2022-05-11 12:00 | 2022-05-10 17:00 | 2022-05-11 14:45 |  |  | Arrived on site and singed in and had to replaces a dishwasher hose had to go to Reece and pick one up
MSA-DFES | WA5400417 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Faulty lights various locations - see notes below | Electrical | Lighting, Internal | 463.785 | Pass | Pass | 0 | 0 | 2.75 | 2022-05-10 10:14 | 2022-05-13 17:00 | 2022-05-13 09:45 | 2022-05-13 17:00 | 2022-05-13 12:30 |  |  | Arrived onsite at 9:45 to investigate lights not working located watch house and dorms. Found 2 x small fluros faulty beyond reasonable repair. Collected 2 x new LED lights from nearest wholesaler and installed and tested. Left site at 12:30
MSA-DTWD | WA5459760 | 0 | Falcetta Plumbing and Gas | Leaking water pipe in the ceiling - see notes below | Plumbing & Drainage | Water | 654.86 | Pass | Fail | 0 | 0 | 2.75 | 2022-05-18 08:42 | 2022-05-18 10:42 | 2022-05-18 10:30 | 2022-05-18 12:42 | 2022-05-18 13:15 |  |  | Repaired leaking pipe
MSA-DTWD | WA5461652 | 3 | AWB Co. | B30 - Faulty light time clock in B30 power board | Electrical | General Electrical | 485.78 | Pass | Pass | -1 | -1 | 2.75 | 2022-05-19 07:48 | 2022-05-25 17:00 | 2022-05-19 08:15 | 2022-05-25 17:00 | 2022-05-19 11:00 |  |  | Attended site signed in jsa completed. Located timer as per petes directions. Removed cover isolated circuit and found a faulty time clock. also had a power outage and as timer is not on battery backup it looses time and programs. sourced new timer as per sites request re programmed and works perfect now. Also re programmed other boards as it was turning off at 6am now turns of at 7am*** job completed ***
MSA-DTWD | WA5470481 | 1 | Protek 24/7 Building & Maintenance | 1G20 Jobs and Skills office - Water leak on to desk and floor | Building | General Building | 463.75 | Pass | Pass | 0 | 0 | 2.75 | 2022-05-23 10:28 | 2022-05-24 17:00 | 2022-05-23 11:30 | 2022-05-24 17:00 | 2022-05-23 14:15 |  |  | Record/Report - BRAF Declined
MSA-DFES | WA5480067 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | ground FF Dorm 4 and Gym multiple fluro lights not working and covers missing | Electrical | Lighting, Internal | 328.63 | Pass | Pass | 0 | 0 | 2.75 | 2022-05-27 15:19 | 2022-06-01 17:00 | 2022-06-01 07:00 | 2022-06-01 17:00 | 2022-06-01 09:45 |  |  | Picked up gear from office and arrived on site at 0700 to replace 1 x emergency exit in gym and 1 x oyster light in dorm 4. Replaced and reenergised both fittings and continued work on site at 0800.
MSA-DTWD | WA5488370 | 2 | AHS Services WA Pty Ltd (Anchor) | Female toilets - B Block - Level 2- buttons not working | Plumbing & Drainage | Toilets/Cisterns | 451.0325 | Pass | Pass | 0 | 0 | 2.75 | 2022-06-02 12:14 | 2022-06-08 17:00 | 2022-06-07 13:00 | 2022-06-08 17:00 | 2022-06-07 15:45 |  |  | Serviced 5x cisterns in toilet block
MSA-DTWD | WA5496182 | 0 | AWB Co. | Carpentry & Joinery Room - Roof leak leaking onto electrical machines | Roofing | Metal Roofing | 540 | Fail | Fail | 0 | 0 | 2.75 | 2022-06-09 08:16 | 2022-06-09 10:16 | 2022-06-09 10:30 | 2022-06-09 12:16 | 2022-06-09 13:15 |  |  | Investigated roof leak and found multiple issues with cappings not sealed to small holes in sheets along first screwline carried out all repairs
MSA-DTWD | WA5498857 | 1 | Lane's Plumbing | Male Toilet - Blocked Toilet | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 2.75 | 2022-06-10 08:07 | 2022-06-13 17:00 | 2022-06-10 09:00 | 2022-06-13 17:00 | 2022-06-10 11:45 |  |  | job completed - CLEAR BLOCKAGE TO MENS TOILET AND REPAIR CISTERN TO UNIT 839
MSA-DTWD | WA5522377 | 3 | Protek 24/7 Building & Maintenance | Nth Carpark -Centre entrance - Damaged Pavers in divider at centre entrance Eddie Barron Drv | Flooring | Concrete | 352.575 | Pass | Pass | -1 | -1 | 2.75 | 2022-06-15 14:52 | 2022-06-22 17:00 | 2022-06-17 09:00 | 2022-06-22 17:00 | 2022-06-17 11:45 |  |  | Repair dislodged pavers
MSA-DTWD | WA5565369 | 3 | AHS Services WA Pty Ltd (Anchor) | kitchen taps need new washers , mixing spout doesn't swivel | Plumbing & Drainage | Water | 372.6625 | Pass | Pass | -1 | -1 | 2.75 | 2022-06-22 07:06 | 2022-06-28 17:00 | 2022-06-22 08:30 | 2022-06-28 17:00 | 2022-06-22 11:15 |  |  | Replaced isolation valves and pupework under sink. Serviced both kitchen taps and replaced spout.
MSA-DFES | WA5574103 | 0 | Go Doors | Front Engie Room Door - door is broken and the chain is jammed and unable to secure station | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 2.75 | 2022-06-30 14:45 | 2022-06-30 16:45 | 2022-06-30 15:45 | 2022-06-30 18:45 | 2022-06-30 18:30 |  |  | Please see attachments.
MSA-DTAG | WA5673449 | 1 | Midolo Building Services | Entrance to Court 2 – Judicial side - Balustrade from corridor side is very loose from wall | Carpentry | Staircases, Balustrades and Handrails | 379.07 | Pass | Pass | 0 | 0 | 2.75 | 2022-07-20 15:27 | 2022-07-21 17:00 | 2022-07-21 08:30 | 2022-07-21 17:00 | 2022-07-21 11:15 |  |  | relocated handrail/re secured & patched wall
MSA-DTWD | WA5675210 | 1 | AWB Co. | gate to back of building - padlock on gate to be cut open as unable to use keys | Carpentry | Materials | 369.8175 | Pass | Pass | 0 | 0 | 2.75 | 2022-07-22 08:24 | 2022-07-25 17:00 | 2022-07-22 10:30 | 2022-07-25 17:00 | 2022-07-22 13:15 |  |  | Arrived onsite and completed works 22/07/2022Remove old padlock that was seized.Drop bolts siezed in closed position and had to be freed up and got into open position.Fitted new padlock to fit the 42886 key as supplied by receptionist.Job Complete
MSA-DTWD | WA5687993 | 3 | Protek 24/7 Building & Maintenance | A & B - Ground and First - Hallways - Roof Leak | Roofing | Metal Roofing | 476.7 | Pass | Pass | -1 | -1 | 2.75 | 2022-08-02 09:06 | 2022-08-09 17:00 | 2022-08-05 07:30 | 2022-08-09 17:00 | 2022-08-05 10:15 |  |  | Instructions by site to close job
MSA-DFES | WA5694168 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | FF Dorm 3 -FF Dorm 3 (dorm closest to gym). Circular LED light is not working. | Electrical | Lighting, Internal | 381.285 | Pass | Pass | 0 | 0 | 2.75 | 2022-08-05 08:32 | 2022-08-12 17:00 | 2022-08-12 12:45 | 2022-08-12 17:00 | 2022-08-12 15:30 |  |  | Arrived onsite at 12:45 to investigate lights not working located dorm 3. Found LED failure within light fitting. Collected parts from nearest wholesaler and returned to site. Installed and tested new LED oyster and notified staff of works completed. Left site at 15:30
MSA-DCA | WA5727792 | 3 | FCT SURFACE CLEANING | Graffiti in various locations - see notes-photo's to follow in email | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 2.75 | 2022-08-15 12:06 | 2022-08-22 17:00 | 2022-08-17 13:30 | 2022-08-22 17:00 | 2022-08-17 16:15 |  |  | Removal of graffiti
MSA-DCA | WA5728002 | 2 | Protek 24/7 Building & Maintenance | wooden door at the main entrance of the Dolls House - see notes | Building | Doors | 395.475 | Pass | Pass | 0 | 0 | 2.75 | 2022-08-15 13:44 | 2022-08-18 17:00 | 2022-08-16 07:00 | 2022-08-18 17:00 | 2022-08-16 09:45 |  |  | Eased door hinges and planed off some of the door at the bottom
MSA-DTWD | WA5752860 | 3 | AWB Co. | 3 Phase socket / Circuit intermittent problems, welding bay 22 | Electrical | General Electrical | 431.7775 | Pass | Pass | 0 | 0 | 2.75 | 2022-08-17 12:23 | 2022-08-24 17:00 | 2022-08-22 08:15 | 2022-08-24 17:00 | 2022-08-22 11:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located faulty gpo in welding bay 22, visually inspected gpo and found arcing marks on L2 (damage), tested for voltage and all voltage seemed good , went to wholesaler to get parts , returned to site, isolated power circuit and replaced gpo, tested v9ltage and all tested good, got technician to test with welder , welding fault came up again. Pulled apart black box above gpo and found contacts were dirty, cleaned contacts and pushed back in, got lecturer to test welder again and now was working as intended, packed up, completed paperwork, cleaned up, signed out **job completed**
MSA-DFES | WA5769013 | 2 | AWB Co. | Engine Room - Roof Leak - previously raised under WA5676552 - see notes below | Roofing | Metal Roofing | 581.655 | Pass | Pass | 0 | 0 | 2.75 | 2022-08-18 15:30 | 2022-08-23 17:00 | 2022-08-23 06:45 | 2022-08-23 17:00 | 2022-08-23 09:30 |  |  | Attended and sealed 3 x dektites above leak area first indicated. Second leak coming down structural struts in wall,cleaned and re-sealed two areas around struts. If persist may need parapet flashing and aprons installing.
MSA-DTWD | WA5834237 | 3 | AHS Services WA Pty Ltd (Anchor) | Repair tap connections to Dishwasher | Plumbing & Drainage | Water | 355.0425 | Pass | Pass | -1 | -1 | 2.75 | 2022-09-06 14:30 | 2022-09-13 17:00 | 2022-09-07 12:00 | 2022-09-13 17:00 | 2022-09-07 14:45 |  |  | .
MSA-DTWD | WA5836178 | 1 | Protek 24/7 Building & Maintenance | Water ingress through roof - adjacent to evap unit | Roofing | Tiled Roofing | 524.55 | Pass | Pass | 0 | 0 | 2.75 | 2022-09-07 10:29 | 2022-09-08 17:00 | 2022-09-08 07:00 | 2022-09-08 17:00 | 2022-09-08 09:45 |  |  | Water tested roof, found leak points. Installed silicone and byute tape as temp fix. Measured up to replaceBraf Submitted and declined
MSA-DTWD | WA5887835 | 3 | AWB Co. | External Nth East stairs -Rear stairs - 2 x lights out | Electrical | Lighting, External | 1211.9375 | Pass | Pass | 0 | 0 | 2.75 | 2022-09-16 10:33 | 2022-09-23 17:00 | 2022-09-20 13:30 | 2022-09-23 17:00 | 2022-09-20 16:15 |  |  | Job complete
MSA-DTWD | WA5972749 | 2 | AWB Co. | Emergency lights not working near stair well under mezzanine floor | Electrical | Emergency & Exit Lighting | 603.4475 | Pass | Pass | -1 | -1 | 2.75 | 2022-09-21 08:24 | 2022-09-27 17:00 | 2022-09-21 13:00 | 2022-09-27 17:00 | 2022-09-21 15:45 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Located fitting and machining. Upon investigation found to be poor emergency lighting on stair well. Installed 1x twin flood at top of stairs. Tested for correct operation. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5990426 | 3 | SENTINEL LOCK SERVICE PTY LTD | C20 Customer Service - External door handle broken - See notes below | Security | Locksmith | 738.07 | Fail | Fail | 6 | 6 | 2.75 | 2022-10-04 13:51 | 2022-10-11 17:00 | 2022-11-24 09:00 | 2022-10-11 17:00 | 2022-11-24 11:45 |  | WACCES | C20 - digital lock broken - external lockLock replaced.
MSA-DFES | WA5993108 | 2 | AWB Co. | Level 1 - Firefighters Shower #2 - Soap holder has cracked and broken from tiled shower | Building | Internal Walls | 343.7975 | Pass | Pass | 0 | 0 | 2.75 | 2022-10-05 08:30 | 2022-10-10 17:00 | 2022-10-07 14:15 | 2022-10-10 17:00 | 2022-10-07 17:00 |  |  | Works completed
MSA-DFES | WA5998197 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Office/admin - faulty light globes - see notes below | Electrical | Lighting, Internal | 977.775 | Pass | Pass | 0 | 0 | 2.75 | 2022-10-07 12:34 | 2022-10-12 17:00 | 2022-10-11 12:00 | 2022-10-12 17:00 | 2022-10-11 14:45 |  |  | Arrived on site at 1200. Located faulty lights. Found several lights with faulty tubes. The tubes are LED tubes and they are not easy to get. Replaced faulty lights with LED panel lights. Left site at 1415 to take all of the old lights to the Insight office to put in the Bin. Finished at the work shop at 1445.
MSA-DTWD | WA6014415 | 3 | AWB Co. | room 104-chalk and cheese café-faulty GPO | Electrical | General Electrical | 631.3375 | Pass | Pass | -1 | -1 | 2.75 | 2022-10-12 09:02 | 2022-10-19 17:00 | 2022-10-13 06:45 | 2022-10-19 17:00 | 2022-10-13 09:30 |  |  | Job complete
MSA-DCA | WA6022751 | 2 | Protek 24/7 Building & Maintenance | Exterior-Fencing behind PICA Car Park-Fencing behind PICA Car Park-see notes | Building | Steel Fencing & Gates | 810.91 | Pass | Pass | 0 | 0 | 2.75 | 2022-10-14 11:42 | 2022-10-19 17:00 | 2022-10-18 07:00 | 2022-10-19 17:00 | 2022-10-18 09:45 |  |  | Remove and replace chainmesh to fixed panel
MSA-DTWD | WA6145822 | 2 | AWB Co. | Room U022.5 - Fluro lights not working | Electrical | Lighting, Internal | 486.17 | Pass | Pass | 0 | 0 | 2.75 | 2022-11-02 15:32 | 2022-11-07 17:00 | 2022-11-04 07:00 | 2022-11-07 17:00 | 2022-11-04 09:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located faulty light fitting in workshop. Replaced tubes and starters. Tested. Fitting failed, drivers were faulty. Went to a block to get fitting that is the same. Put new light up. Working as intended. Took pic. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA6149340 | 1 | Protek 24/7 Building & Maintenance | N Block decking -Broken slat needs replacing, and other slats re-screwed to make secure | Building | General Building | 291.715 | Pass | Pass | 0 | 0 | 2.75 | 2022-11-04 14:16 | 2022-11-07 17:00 | 2022-11-07 10:30 | 2022-11-07 17:00 | 2022-11-07 13:15 |  |  | Replaced damaged board and reduced boards.
MSA-DCA | WA6157331 | 3 | Protek 24/7 Building & Maintenance | Both umbrellas in Urban Orchard are loose, please resecure. | Building | Steel Work | 341.54 | Pass | Pass | -1 | -1 | 2.75 | 2022-11-09 15:26 | 2022-11-16 17:00 | 2022-11-11 07:00 | 2022-11-16 17:00 | 2022-11-11 09:45 |  |  | Remove old and install larger bolts
MSA-DTWD | WA6249660 | 2 | AWB Co. | Canteen - GPO's needs replacing. | Electrical | General Electrical | 260.685 | Pass | Pass | 0 | 0 | 2.75 | 2022-11-21 13:36 | 2022-11-24 17:00 | 2022-11-24 07:00 | 2022-11-24 17:00 | 2022-11-24 09:45 |  |  | Attended site and signed in. Completed JSA. Located canteen and liaised with stafff about faulty GPOs. Found to be 2x GPOs in an unsafe condition. Isolated circuit. Removed and replaced faulty GPOs with 2x new DGPO. Energised circuit and tested. All working correctly. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6253973 | 2 | BAKE-QUIP PTY LTD | Mt Lawley Kitchen/ Cafe - Dishwasher releasing smoke | Equipment | Catering Equipment | 587 | Pass | Pass | 0 | 0 | 2.75 | 2022-11-22 13:36 | 2022-11-25 17:00 | 2022-11-23 08:15 | 2022-11-25 17:00 | 2022-11-23 11:00 |  |  | Refer to service report
MSA-DTWD | WA6362312 | 2 | AWB Co. | 2 X main AC switches need to be moved from ground level to shoulder level. | Building | General Building | 302.245 | Pass | Pass | 0 | 0 | 2.75 | 2022-12-09 09:32 | 2022-12-14 17:00 | 2022-12-14 08:30 | 2022-12-14 17:00 | 2022-12-14 11:15 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Located AC isolators. Isolated circuits. Relocated isolators too a more suitable height. Energised. Made sure ACs were working. Notified relevant personnel. **job complete**
MSA-DFES | WA6374846 | 1 | AWB Co. | ground-kitchen-Latch on sliding doors to kitchen dining is not functioning-see note | Building | Doors | 1016.42 | Fail | Fail | 2 | 2 | 2.75 | 2022-12-15 07:21 | 2022-12-15 17:00 | 2022-12-28 10:30 | 2022-12-15 17:00 | 2022-12-28 13:15 |  |  | Attended site with 2 menand adjusted sliding doors to rear of lunch room.Adjusted rollers to both doors and lock and lubricated with silicone spray.Lock was sticky but working well now after removal, clean up and lubricating
MSA-DTAG | WA6390817 | 1 | Water2water Pty Ltd | Level 4 - GCIP Office - South East Corner - Zip tap fault - see notes below | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 2.75 | 2022-12-22 13:07 | 2022-12-23 17:00 | 2022-12-23 11:55 | 2022-12-23 17:00 | 2022-12-23 14:40 |  |  | Reported leak couldn't find leak. Unit 14 years old Recommend replacement
MSA-DFES | WA6403274 | 1 | Critical Fire Protection & Training | Ground floor - Fire panel - Battery faulty | Fire Protection Services | Fire Protection - Monitor System | 1269.53 | Pass | Pass | 0 | 0 | 2.75 | 2023-01-06 09:34 | 2023-01-09 17:00 | 2023-01-06 10:50 | 2023-01-09 17:00 | 2023-01-06 13:35
MSA-DTWD | WA6467640 | 2 | GRAFFITI FORCE PTY LTD | Gilmore Ave entrance- Ground Level- Exterior walls - Graffiti removal | Cleaning | Graffiti | 545.5 | Fail | Fail | 2 | 2 | 2.75 | 2023-01-17 15:06 | 2023-01-20 17:00 | 2023-01-31 07:30 | 2023-01-20 17:00 | 2023-01-31 10:15
MSA-DFES | WA6519035 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Shed (near safety shower 6) - No Power to GPO | Electrical | General Electrical | 692.565 | Pass | Pass | 0 | 0 | 2.75 | 2023-01-25 12:23 | 2023-02-02 17:00 | 2023-02-01 08:30 | 2023-02-02 17:00 | 2023-02-01 11:15
MSA-DTWD | WA6527279 | 2 | AWB Co. | West stairwell L2 and L6 - x4 Fittings | Electrical | General Electrical | 853.37 | Pass | Pass | 0 | 0 | 2.75 | 2023-02-01 15:32 | 2023-02-06 17:00 | 2023-02-06 11:15 | 2023-02-06 17:00 | 2023-02-06 14:00
MSA-DTWD | WA6539244 | 2 | AWB Co. | Two rows of lights keep tripping out | Electrical | Lighting, Internal | 771.28 | Pass | Pass | 0 | 0 | 2.75 | 2023-02-08 11:27 | 2023-02-13 17:00 | 2023-02-13 07:00 | 2023-02-13 17:00 | 2023-02-13 09:45
MSA-DTWD | WA6539628 | 2 | Equans Mechanical Services Australia | AHU5 leaking excess water from drip trays | Air Conditioning | Room Air Conditioners | 302.8175 | Fail | Fail | 0 | 0 | 2.75 | 2023-02-08 14:57 | 2023-02-13 17:00 | 2023-02-14 11:15 | 2023-02-13 17:00 | 2023-02-14 14:00
MSA-MRWA | WA6540861 | 1 | Dormakaba Australia Pty Ltd | auto door is stuck open | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 2.75 | 2023-02-09 15:16 | 2023-02-10 17:00 | 2023-02-10 09:45 | 2023-02-10 17:00 | 2023-02-10 12:30
MSA-DTWD | WA6601081 | 3 | AWB Co. | Level 1 - disable toilets door closer is faulty (see notes) | Building | Doors | 292.5375 | Pass | Pass | 0 | 0 | 2.75 | 2023-02-17 10:02 | 2023-02-24 17:00 | 2023-02-24 06:45 | 2023-02-24 17:00 | 2023-02-24 09:30
MSA-DTAG | WA6673417 | 2 | Midolo Building Services | Sheriff’s Office - Level 1 - soap dispensers need to be re-attached to toilet walls | Building | Materials | 349.4 | Pass | Pass | 0 | 0 | 2.75 | 2023-02-24 13:58 | 2023-03-01 17:00 | 2023-02-27 09:15 | 2023-03-01 17:00 | 2023-02-27 12:00
MSA-DFES | WA6674011 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Low pressure on both hot and cold and limited hot water flow | Plumbing & Drainage | Water | 456.6075 | Pass | Pass | 0 | 0 | 2.75 | 2023-02-27 07:24 | 2023-03-03 17:00 | 2023-02-28 13:30 | 2023-03-03 17:00 | 2023-02-28 16:15
MSA-DTWD | WA6674378 | 2 | WESTERN IRRIGATION PTY LTD | Sprinkler broken on footpath behind D block (see notes) | Plumbing & Drainage | Water | 730.96 | Pass | Pass | 0 | 0 | 2.75 | 2023-02-27 09:38 | 2023-03-02 17:00 | 2023-03-01 10:30 | 2023-03-02 17:00 | 2023-03-01 13:15
MSA-DTWD | WA6683964 | 2 | AHS Services WA Pty Ltd (Anchor) | Last cubicle, cistern not working correctly | Plumbing & Drainage | Toilets/Cisterns | 887.8825 | Pass | Pass | 0 | 0 | 2.75 | 2023-03-03 14:29 | 2023-03-09 17:00 | 2023-03-07 09:00 | 2023-03-09 17:00 | 2023-03-07 11:45
MSA-DTWD | WA6693499 | 2 | AWB Co. | faulty GPO | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2.75 | 2023-03-10 10:59 | 2023-03-15 17:00 | 2023-03-13 07:00 | 2023-03-15 17:00 | 2023-03-13 09:45
MSA-DTWD | WA5111811 | 2 | Techworks Electrical | Kendrew- E-Block room E58 and Restaurant ceiling lights not working | Electrical | General Electrical | 413.23 | Pass | Pass | -1 | -1 | 2.7333 | 2022-02-10 10:48 | 2022-02-15 17:00 | 2022-02-10 12:00 | 2022-02-15 17:00 | 2022-02-10 14:44 |  |  | Replaced light in e block kitchen prep and lights in restaurant kitchen
MSA-DTAG | WA5795060 | 1 | Australian HVAC Services Pty. Ltd. | Court - Sewage smell coming through air conditioner | Air Conditioning | Room Air Conditioners | 505.39 | Pass | Pass | 0 | 0 | 2.7092 | 2022-08-25 09:29 | 2022-08-26 17:00 | 2022-08-26 08:17 | 2022-08-26 17:00 | 2022-08-26 11:00 |  |  | Attended site and inspected aircon serving courtroom 2. Found odour appears to be coming from dry floor wastes. Flushed floor waste with water to prevent odour. Odour appeared to clear. Recommend Installing fresh air sponge into ahu's to clean air. Submitted braf and installed fresh air sponges into ahu's.
MSA-DTWD | WA5207305 | 2 | Dormakaba Australia Pty Ltd | Electric sliding door to library won’t close | Building | Automatic Doors | 615.06 | Pass | Pass | 0 | 0 | 2.7 | 2022-03-08 12:09 | 2022-03-11 17:00 | 2022-03-09 10:05 | 2022-03-11 17:00 | 2022-03-09 12:47 |  |  | 1086319 Find the auto door will not open or closed. Find the ES200 PD board was faulty replaced PD board. Tested auto door working ok.
MSA-DCA | WA5231923 | 0 | Techworks Electrical | Level 2 - Store room- Water leaking through light fitting | Electrical | General Electrical | 429.99 | Pass | Pass | 0 | 0 | 2.7 | 2022-03-15 17:08 | 2022-03-15 19:08 | 2022-03-15 17:09 | 2022-03-15 21:08 | 2022-03-15 19:51 |  |  | Made safe 1 x light. No safe access available. Will need ceiling taken down to investigate fault
MSA-DCA | WA5583929 | 0 | EQUANS Mechanical Services (WA) Pty Limited | 2x humidity alarms | Security | Monitoring | 371.62 | Fail | Fail | 0 | 0 | 2.7 | 2022-07-05 05:08 | 2022-07-05 07:08 | 2022-07-05 07:30 | 2022-07-05 09:08 | 2022-07-05 10:12 |  |  | Recieved AH call attended site gained access and carried out inspection of equipment with reports humidity alarm issues. Noted FCU 3 humidity alarm had cleared. Before arriving. Noted FCU 4 humidity alarm was still active. Confirmed humidifier was active and humidity being added to room. Gained access to plant room on level 4 and confirmed no ro plant operation OK and steam gen active. Returned to BMS and checked humidity sensors on FCU 4 and found humidity to be rising slowly and coming back into range. Equipment confirmed as working with no active alarms. Work area has been left tidy.
MSA-DTWD | WA5474648 | 2 | ADVANCED LOCK & KEY | West entrance door lock faulty | Security | Locksmith | 200 | Pass | Pass | -1 | -1 | 2.6833 | 2022-05-25 08:22 | 2022-05-30 17:00 | 2022-05-26 10:25 | 2022-05-30 17:00 | 2022-05-26 13:06 |  |  | Re-pin lock
MSA-DTWD | WA5098770 | 3 | CARRIER AUSTRALIA PTY LTD | Chiller 1 - BMS Sensor fuse for water flow requires replacing on chiller one | Refrigeration | Chiller |  | Pass | Pass | -1 | -1 | 2.6667 | 2022-02-01 11:15 | 2022-02-08 17:00 | 2022-02-01 11:20 | 2022-02-08 17:00 | 2022-02-01 14:00 |  |  | job completed -investigated to find multiple problems. found that chw evaporator DP was reading very low as was flowmeter. found that chw leg had giant air blockage prior to entering of chiller which was causing no flow.bled all air at both high points and at pump housing to ensure removed, ran up with better flow andreadings. also found that chw flow reading was not being represented on bms but was reading correctlocally, BAE currently looking into issue. ran up chiller to ensure operating well, all OK
MSA-DFES | WA5394654 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | External - Pillar hydrant - Drain is blocked (causing sink to fill) | Plumbing & Drainage | Drainage | 309.3 | Pass | Pass | 0 | 0 | 2.6667 | 2022-05-05 08:09 | 2022-05-06 17:00 | 2022-05-05 12:50 | 2022-05-06 17:00 | 2022-05-05 15:30 |  |  | Located to site due to the gully at the back of the station is blocked up plunged and clear the blockage ran water and draining away
MSA-DTAG | WA5488679 | 3 | MALCO FLOORING PTY LTD | Office 217 - Damaged carpet after ceiling water leak | Flooring | Carpet | 1795 | Fail | Fail | 1 | 1 | 2.6667 | 2022-06-02 14:50 | 2022-06-10 17:00 | 2022-06-14 07:00 | 2022-06-10 17:00 | 2022-06-14 09:40 |  |  | Replaced water damaged carpet tiles after ceiling leak
MSA-DTWD | WA5988465 | 2 | Water2water Pty Ltd | hot water is not heating | Plumbing & Drainage | HWS/Units Electric & Gas | 1998.535 | Pass | Pass | 0 | 0 | 2.6667 | 2022-10-04 09:19 | 2022-10-07 17:00 | 2022-10-07 13:25 | 2022-10-07 17:00 | 2022-10-07 16:05 |  |  | Replaced dead unit with new unit with filtration system checked and tested all okay
MSA-DTAG | WA6362440 | 1 | SCAVENGER SUPPLIES PTY LTD | EWIS System - System needs to be checked - See Notes Below | Fire Protection Services | Fire Protection - Monitor System | 102.95 | Pass | Pass | 0 | 0 | 2.65 | 2022-12-09 10:42 | 2022-12-12 17:00 | 2022-12-09 13:00 | 2022-12-12 17:00 | 2022-12-09 15:39 |  |  | Fire alarm was activated in the morning due to someone vaping in the Lvl 8 bathrooms of thebuilding.The building was evacuated and the fire brigade attended site, the fireman then isolated the alarmsand EWIS system to allow entry back into the building.After inspecting the FIP I can confirm that the detector in the level 8 toilets adjacent judges lift (S53,Z108, L5)was put into alarm.The isolation has since been de-isolated and reset and the FIP/EWIS systems are working normal.Completed 09/12/2022
MSA-MRWA | WA5209175 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 3 - Men’s toilets – basin and left cubicle - see details | Plumbing & Drainage | Materials | 682.2625 | Pass | Pass | 0 | 0 | 2.6333 | 2022-03-09 14:49 | 2022-03-14 17:00 | 2022-03-11 12:18 | 2022-03-14 17:00 | 2022-03-11 14:56 |  |  | Replaced seized basin mixers x 2 to male toilet level 3
MSA-DCA | WA5390331 | 3 | GPS Plumbing & Gas Services PtyLtd | Ladies Toilet - Loading Bay 7- left hand cubicle - Toilet pan is moving and will require new bolts | Plumbing & Drainage | Toilets/Cisterns | 636.065 | Pass | Pass | 0 | 0 | 2.6333 | 2022-05-02 11:59 | 2022-05-09 17:00 | 2022-05-09 11:17 | 2022-05-09 17:00 | 2022-05-09 13:55 |  |  | Toile cracked whilst being uninstalled. Cistern leaking. Agreed with Frank to install new tpilet suite. Pan not to be used till the 10/5
MSA-DTWD | WA5325689 | 3 | Techworks Plumbing | Outside East Side Of Building - Blockage of overflowed drain for water fountain | Plumbing & Drainage | Drainage | 269.83 | Pass | Pass | -1 | -1 | 2.6167 | 2022-04-14 11:26 | 2022-04-26 17:00 | 2022-04-21 08:00 | 2022-04-26 17:00 | 2022-04-21 10:37 |  |  | Attend site to unblock waste connected to the drink fountain and emergency shower and eyewash. Tundish line was filled with debris built up over time. Remove wastes above tundish to allow the Use of drain rods and plunger to clear blockage. Once blockage cleared reinstated wastes above line and test.
MSA-DTWD | WA5706026 | 2 | AHS Services WA Pty Ltd (Anchor) | Repair basin Tap Male toilet B Block Ground Floor | Plumbing & Drainage | Water | 287.395 | Pass | Pass | -1 | -1 | 2.6167 | 2022-08-11 08:06 | 2022-08-16 17:00 | 2022-08-12 10:30 | 2022-08-16 17:00 | 2022-08-12 13:07 |  |  | Isolate water to B block, Dismantle tapware to first basin make toilet ground floor, supply and install service kit to tapware and test on completion
MSA-DCA | WA4994783 | 0 | TK Elevator Australia Pty Ltd | Centenary Gallery - Lift - Out of order | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 2.6 | 2022-01-10 07:26 | 2022-01-10 09:26 | 2022-01-11 12:22 | 2022-01-10 11:26 | 2022-01-11 14:58 |  |  | Replaced damaged door lock rollers on level 1 as reported. Landing door operation very tight, noticed rubber on hanger rollers peeling free. Ordered 4 hanger rollers andreplaced. Checked operation and placed lift back into service.
MSA-DTAG | WA6523067 | 2 | Gilmour & Jooste Electrical | External - Damage to lights on exterior of building | Electrical | Lighting, External | 69.77 | Fail | Fail | 1 | 1 | 2.6 | 2023-01-31 12:10 | 2023-02-03 17:00 | 2023-02-09 05:30 | 2023-02-03 17:00 | 2023-02-09 08:06
MSA-DTWD | WA5289763 | 0 | SCAVENGER SUPPLIES PTY LTD | T, U & V Blocks - Ground Floor - EWIS speakers not working - see notes below | Fire Protection Services | Fire Protection - Monitor System | 334.72 | Pass | Pass | 0 | 0 | 2.5833 | 2022-03-24 12:40 | 2022-03-24 14:40 | 2022-03-24 13:30 | 2022-03-24 16:40 | 2022-03-24 16:05 |  |  | completed 24/3/22Further work order to be issued for additional time/ parts required to repair.
MSA-MRWA | WA5596522 | 1 | Water2water Pty Ltd | Kitchen - Billi tap hot water tap is faulty | Plumbing & Drainage | Water | 570.185 | Pass | Pass | 0 | 0 | 2.5833 | 2022-07-11 08:54 | 2022-07-12 17:00 | 2022-07-11 09:45 | 2022-07-12 17:00 | 2022-07-11 12:20 |  |  | No water on arrival. Checked water from filter to the float tank. Replaced float in tank and John guest fitting. Drained tank from bottom. Also had to replace zip tap. Waited to get to temp. Normal operation
MSA-DTWD | WA5797540 | 1 | AHS Services WA Pty Ltd (Anchor) | Burst Pipe outside S102 in garden | Plumbing & Drainage | Water | 380.7825 | Pass | Pass | 0 | 0 | 2.5833 | 2022-08-29 09:03 | 2022-08-30 17:00 | 2022-08-29 10:15 | 2022-08-30 17:00 | 2022-08-29 12:50 |  |  | Completed
MSA-DCA | WA5977323 | 2 | GPS Plumbing & Gas Services PtyLtd | L3 mail toilets - Toilet is not flushing properly | Plumbing & Drainage | Toilets/Cisterns | 718.2075 | Pass | Pass | 0 | 0 | 2.5833 | 2022-09-27 15:32 | 2022-09-30 17:00 | 2022-09-28 14:00 | 2022-09-30 17:00 | 2022-09-28 16:35 |  |  | Replaced broken outlet valve and inlet valve. Struggled to uninstalled cistern. Cistern and toilet can nw be normally used.
MSA-DTWD | WA6130244 | 1 | Water2water Pty Ltd | Staff room kitchen-Hot water unit faulty | Plumbing & Drainage | Water | 1184.855 | Pass | Pass | 0 | 0 | 2.5833 | 2022-10-28 10:57 | 2022-10-31 17:00 | 2022-10-31 10:15 | 2022-10-31 17:00 | 2022-10-31 12:50 |  |  | Unit full of water on arrival. Removed cover and put it through tests. Both tanks were overfilling and leak signs from flow meter. Also faulty stirrer pump and hot levels not kicking in. Replaced all solenoids and level sensors, stirrer pump and o’rings and flow meter. Ran through further tests, waited to get to temp. Normal operation
MSA-DTWD | WA6585503 | 2 | AWB Co. | Room A126 - East End - Swipe door wont lock | Building | General Building | 250.92 | Pass | Pass | 0 | 0 | 2.5833 | 2023-02-16 07:57 | 2023-02-20 17:00 | 2023-02-20 10:40 | 2023-02-20 17:00 | 2023-02-20 13:15
MSA-DTWD | WA6667685 | 1 | Australian Airconditioning Services Pty Ltd | Main plant room - Air conditioning Chiller tripped out | Air Conditioning | Package | 295.9 | Pass | Pass | 0 | 0 | 2.5669 | 2023-02-21 13:52 | 2023-02-22 17:00 | 2023-02-22 07:26 | 2023-02-22 17:00 | 2023-02-22 10:00
MSA-DFES | WA5053122 | 1 | Australian HVAC Services Pty. Ltd. | BMS Control - Off line | Air Conditioning | Room Air Conditioners | 781.46 | Pass | Pass | 0 | 0 | 2.56 | 2022-01-18 13:20 | 2022-01-19 17:00 | 2022-01-18 13:29 | 2022-01-19 17:00 | 2022-01-18 16:03 |  |  | While onsite found bms controllers were offline on bms. Called mizco to inspect. Reset pc and found all controllers were powered on but no communication was restored. Mizco investigated fault a rectified issue. Confirmed correct operation of bms and controllers.
MSA-DCA | WA5325409 | 2 | Techworks Plumbing | Ground Level - Cloak Room/ UAT Area - Faulty filter to Zip Tap | Plumbing & Drainage | Water | 435.03 | Pass | Pass | -1 | -1 | 2.5333 | 2022-04-14 09:09 | 2022-04-21 17:00 | 2022-04-14 11:58 | 2022-04-21 17:00 | 2022-04-14 14:30 |  |  | Attended site and signed in. Security showed me the tap that wasn't working properlyRemoved filter which had no date on it and looked like it had been there for a while. Went to Reece to get a new filter and then went back to site to re install. Installed, tested and signed out
MSA-DTWD | WA5107957 | 1 | Precise Air Group | Kendrew- E-Block Restaurant Kitchen airconditioning switch not working | Air Conditioning | Room Air Conditioners | 460.495 | Pass | Pass | 0 | 0 | 2.5333 | 2022-02-08 10:38 | 2022-02-09 17:00 | 2022-02-08 13:00 | 2022-02-09 17:00 | 2022-02-08 15:32 |  |  | Attended site, found location of air conditioning unit not operating, required apprentice for safe access into roof, waited for apprentice, gained access into roof, found no water in sump of evap cooler, required new solenoid valve, picked up solenoid valve, traveled back to site, isolated unit, replaced solenoid, checked operation all running to specs. Cleared debris from site
MSA-DTWD | WA5107773 | 1 | Precise Air Group | Q-Block - chiller in alarm again after new parts were fitted last week | Air Conditioning | Room Air Conditioners | 413.4 | Pass | Pass | 0 | 0 | 2.5167 | 2022-02-08 09:16 | 2022-02-09 17:00 | 2022-02-08 11:00 | 2022-02-09 17:00 | 2022-02-08 13:31 |  |  | Attended site and completed pre start paperwork and signed in. Reset chiller. Observed system run and cycle on and off multiple times. Fm to monitor
MSA-DTAG | WA5303699 | 3 | AHS Services WA Pty Ltd (Anchor) | Aircon ducting causing flooding to female toilet block | Plumbing & Drainage | Toilets/Cisterns | 317.755 | Pass | Pass | -1 | -1 | 2.5167 | 2022-04-04 11:54 | 2022-04-11 17:00 | 2022-04-06 07:24 | 2022-04-11 17:00 | 2022-04-06 09:55 |  |  | Completed
MSA-DTWD | WA4993219 | 1 | Critical Fire Protection & Training | Fire Panel Alarm activation - resetting required | Fire Protection Services | Fire Protection - Monitor System | 683 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-07 11:02 | 2022-01-10 17:00 | 2022-01-07 11:40 | 2022-01-10 17:00 | 2022-01-07 14:10 |  |  | Callout to activated detector in freezer areaReplaced with water resistant detector
MSA-DTWD | WA4995071 | 3 | AWB Co. | A03 - 2 X lights require tombstones | Electrical | Lighting, Internal | 488.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-10 09:52 | 2022-01-17 17:00 | 2022-01-14 08:00 | 2022-01-17 17:00 | 2022-01-14 10:30 |  |  | Attended site, signed in, completed jsa,spoke with fm about job , inspected lights that were faulty, went to wholesaler to pick up lights , returned to site, isolated lighting circuits, removed old fittings , replaced with new, reenergised lights, tested lights and they are working as intended, cleaned up , packed up, completed paperwork, signed out ***job completed***
MSA-DFES | WA5001313 | 1 | Facilities First Australia Pty Ltd | Comcen - Deep Bio clean to 2 x chairs | Furniture | Indoor Furniture | 237.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-11 11:08 | 2022-01-12 17:00 | 2022-01-12 08:00 | 2022-01-12 17:00 | 2022-01-12 10:30 |  |  | Chairs cleaned as requested
MSA-DTWD | WA5010192 | 3 | CAPS AUSTRALIA PTY LTD | compressor has faulty belts | Equipment | Compressors, Generators |  | Pass | Pass | -1 | -1 | 2.5 | 2022-01-12 11:06 | 2022-01-19 17:00 | 2022-01-12 12:00 | 2022-01-19 17:00 | 2022-01-12 14:30 |  |  | job completed -Belts needed tensioning took cover of found one bracket was broken I was told the compressor was not touched in 11 yrs but I checked the oil and belts they were new then noticed a service sticker by another company told customer if he can get it wielded together and he said if I can put a big washer to hold it I was not happy how it held but could not do more the cover was slightly rubbin
MSA-DTWD | WA5081497 | 3 | AWB Co. | Spot welder not working damaged connector | Electrical | General Electrical | 269.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-20 14:45 | 2022-01-28 17:00 | 2022-01-28 10:30 | 2022-01-28 17:00 | 2022-01-28 13:00 |  |  | Attended site and signed in. Completed JSA. Located faulty spot welder. Disconnect and make safe old unit, new unit was on site. Site to contact manufacturer on wiring as it seems to not be suited for Australia. Old spot welder safe. Signed out. Job complete
MSA-DTWD | WA5089852 | 1 | Equans Mechanical Services Australia | CG42 Comms room - A/C dripping onto switch and electrical equipment | Air Conditioning | Room Air Conditioners | 245.93 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-25 07:04 | 2022-01-25 17:00 | 2022-01-25 13:30 | 2022-01-25 17:00 | 2022-01-25 16:00 |  |  | Arrived on site signed in gathered tools and equipment started checks on controls and operation and cleaned filters where required. Cleaned up and completed paperwork and signed out.
MSA-DFES | WA5090194 | 1 | Australian HVAC Services Pty. Ltd. | Kitchen - Office - 4 x units air conditioning not working | Air Conditioning | Room Air Conditioners | 279.18 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-25 10:00 | 2022-01-27 17:00 | 2022-01-25 10:01 | 2022-01-27 17:00 | 2022-01-25 12:31 |  |  | Attended service call, signed in & began speaking to on-site representative who informed me that two units had not been operating (A/C 1 & A/C 5). found both indoor units to be out on a U4 fault (communication error), began removing both condensing units fascia panels and inspecting outdoor PCB boards, no issues found. Both indoor units will work on fan only. No issues found with indoor PCB board. Began inspecting Interconnect connections to outdoor units & found terminals to be very loose. Tightened connections & reset isolator to each unit. Began operational testing & found both units to be fully functional. Watched units for 30 mins & both units in working order.
MSA-DTWD | WA5091418 | 1 | Techworks Plumbing | Ground - B16 Staff Room Kitchen - Sink is blocked / Slow running | Plumbing & Drainage | Water | 262.04 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-27 08:49 | 2022-01-28 17:00 | 2022-01-27 09:00 | 2022-01-28 17:00 | 2022-01-27 11:30 |  |  | Kitchen staff room was draining poor, disconnected gully out the back was full so unblocked the gully with afew rrods and the sink is flowing freely again all cleared
MSA-DTWD | WA5091488 | 1 | M Construction (WA) | C Block - Level 1 - C111 - broken white board come away from the wall | Building | General Building | 603.09 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-27 09:19 | 2022-01-28 17:00 | 2022-01-27 12:00 | 2022-01-28 17:00 | 2022-01-27 14:30 |  |  | Relocate 1 whiteboard and 2 pin-up boards.
MSA-DFES | WA5094913 | 3 | Australian HVAC Services Pty. Ltd. | Meeting room - air conditioning is not working properly | Air Conditioning | Room Air Conditioners | 324.18 | Pass | Pass | -1 | -1 | 2.5 | 2022-01-31 15:39 | 2022-02-07 17:00 | 2022-02-02 08:00 | 2022-02-07 17:00 | 2022-02-02 10:30 |  |  | Arrived on site due to service call, spoke to site representative about the issue.Upon investigation I found the coil was blocked and full of dirt. Split / coil clean was performed, unit re tested and is now working great.
MSA-DCA | WA5098735 | 1 | Automatic Fire Protection (ARA) | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Fire Protection Services | Fire Protection - Monitor System | 392.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-27 12:00 | 2022-01-28 17:00 | 2022-01-27 12:00 | 2022-01-28 17:00 | 2022-01-27 14:30 | 1 |  | 27/1/22 JNAttended site and replaced L1 D11 FSP smoke detector due to false alarm. Reset and deisolated at clients request. All ok.
MSA-DTWD | WA5099006 | 3 | AWB Co. | 3 x lights out | Electrical | Lighting, Internal | 421 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-01 13:17 | 2022-02-08 17:00 | 2022-02-08 14:00 | 2022-02-08 17:00 | 2022-02-08 16:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about the job. Located male toilet with faulty light fittings. Rang Fm and discussed options. He said he wants 4x LED battens to replace. Went to wholesaler to gets parts ( for 2 jobs ). Returned to site. Set up work area. Isolated lighting circuit. Took all lights down and put new led battens up. Re energised lighting circuit. Everything working as intended. Took picture of lights after. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5099029 | 2 | Equans Mechanical Services Australia | Aircon not working properly not cold enough | Air Conditioning | Room Air Conditioners | 470.76 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-01 13:23 | 2022-02-04 17:00 | 2022-02-02 12:30 | 2022-02-04 17:00 | 2022-02-02 15:00 |  |  | Found one of the ceiling cassettes in the server room short of gas. Found a leak on the condenser, picked up gas from the suppliers, regaled and also put sealant in the system . Ran up and test ran all OK.
MSA-DFES | WA5101778 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Multiple faulty lights - see locations below | Electrical | General Electrical | 582.17 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-03 14:42 | 2022-02-08 17:00 | 2022-02-08 10:30 | 2022-02-08 17:00 | 2022-02-08 13:00 |  |  | Arrived on site at 10:30. Went to so office and located faulty led battern that is flickering, replaced with new fitting from wholesaler and tested all okay. Replaced faulty dimmer from incandescent to new led dimmer to suit lights in dorm room. Left site at 13:00Materials - 1 x sal led battern, 1 x Clipsal led dimmer 400w
MSA-DFES | WA5107870 | 1 | Australian HVAC Services Pty. Ltd. | North plant room - BMS Login inactive and level 1 SOC is warm | Air Conditioning | Room Air Conditioners | 653.18 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-08 10:03 | 2022-02-09 17:00 | 2022-02-08 11:00 | 2022-02-09 17:00 | 2022-02-08 13:30 |  |  | Attend site. Access bms and found not able to log in. Organise Mizco to attend site and check BMS issue. Found NCE controllers in fault. AHU 4,5,6,7 and 8 not running. Carry out power cycle of each controller and found to come back online. Found all AHUs to start and work as normal. Monitor operation until building temp reaches setpoint. AC now working as normal. Possible cause of fault most likely power surge. No other faults found.
MSA-DTWD | WA5126549 | 0 | WESTERN IRRIGATION PTY LTD | External irrigation (near horticulture) - leaking - losing 20L a minutes | Plumbing & Drainage | Water | 580.64 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-14 08:42 | 2022-02-14 10:42 | 2022-02-14 09:30 | 2022-02-14 12:42 | 2022-02-14 12:00 |  |  | Located faulty solenoid valve and repair, test for correct operation.
MSA-DTWD | WA5133353 | 1 | Lane's Plumbing | BLD 832 - 1st Floor - Water leak | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2.5 | 2022-02-15 10:02 | 2022-02-16 17:00 | 2022-02-15 10:30 | 2022-02-16 17:00 | 2022-02-15 13:00 |  |  | REPAIR LEAKING WATER PIPE TO FIRST FLOOR BLD832
MSA-DTWD | WA5163649 | 2 | GRAFFITI FORCE PTY LTD | Front of Building - Graffiti | Cleaning | Cleaning | 394.92 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-18 10:49 | 2022-02-23 17:00 | 2022-02-21 10:30 | 2022-02-23 17:00 | 2022-02-21 13:00 |  |  | REMOVAL OF GRAFFITI FROM FRONT OF BUILDING
MSA-DTWD | WA5163761 | 1 | Equans Mechanical Services Australia | O Block Glass House - Compartment 3 - No water flow to the Air Conditioning unit on the West end | Plumbing & Drainage | Water | 342.73 | Fail | Fail | 0 | 0 | 2.5 | 2022-02-18 11:49 | 2022-02-21 17:00 | 2022-02-22 13:30 | 2022-02-21 17:00 | 2022-02-22 16:00 |  |  | Locate a/c unit and inspect, found solenoid valve blocked. Also found solenoid split on the unit next to the one I was working on, replace both solenoids. Check operation, all ok at this time.
MSA-DTWD | WA5163947 | 1 | AWB Co. | H10 - Aircon tripping out, reset it & then after period of time trips again (loose wire maybe) | Electrical | General Electrical | 525.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-18 13:48 | 2022-02-21 17:00 | 2022-02-21 12:00 | 2022-02-21 17:00 | 2022-02-21 14:30 |  | WACCES | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Investigated A/C keeps tripping. Found to be faulty isolator due to water damage. Also found to be faulty circuit breaker. Supplied and replaced both. Tested for correct operation. **job complete**
MSA-DFES | WA5195046 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Room 20 - Exhaust fan stopped running. Fit new and install separate switch. | Electrical | General Electrical | 703.49 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-28 10:28 | 2022-03-03 17:00 | 2022-02-28 12:30 | 2022-03-03 17:00 | 2022-02-28 15:00 |  |  | Attended site at 1230. Works requested were “ Room 20 - Exhaust fan stopped running. Fit new and install separate switch. (currently co-switched with light)”. This was found onsite as being the male restroom. We ran cable and replaced the existing 1 Gang switch with a 2 gang switch, and altered the lighting junction to allow the fan to be switched separately from lights, we also replaced the faulty exhaust fan. All is now working as intended. Left site 1500.
MSA-DTWD | WA5195737 | 2 | Falcetta Plumbing and Gas | Cistern leaking | Plumbing & Drainage | Toilets/Cisterns | 419.14 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-28 15:07 | 2022-03-03 17:00 | 2022-03-02 15:00 | 2022-03-03 17:00 | 2022-03-02 17:30 |  |  | repaired 2x disabled cisterns
MSA-DTAG | WA5200807 | 0 | Midolo Building Services | Courtside - Female public toilets - Roof is leaking | Roofing | Tiled Roofing | 250 | Pass | Fail | 0 | 0 | 2.5 | 2022-03-02 09:16 | 2022-03-02 11:16 | 2022-03-02 11:00 | 2022-03-02 13:16 | 2022-03-02 13:30 |  | WACCES & WCAPPR | QUOTES TO BE OBTAINED TO RESOLVE THIS ISSUE - CLOSE OFF COST TO DATE
MSA-DCA | WA5201442 | 0 | EQUANS Mechanical Services (WA) Pty Limited | High humidity | Air Conditioning | Building HVAC Maintenance (Major Plant) | 293.025 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-02 15:07 | 2022-03-02 17:07 | 2022-03-02 15:30 | 2022-03-02 19:07 | 2022-03-02 18:00 |  |  | Attended site, signed in and accessed the affected fan coil units with humidity issues. Checked and tested units and, found humidifiers working as per normal with no faults. Checked the bms and found the supply chilled water temperature from the ETS sitting around 9.0 degrees. Accessed the state library plant room and found chiller 2 condenser water pump in alarm with a high current draw fault. Reset the vsd alarm and bms alarms. Checked, tested and ran condenser water pump 2 and found no further faults to report. Will monitor running conditions of the pump during the routine HVAC maintenance.
MSA-DCA | WA5201531 | 1 | Techworks Plumbing | Jubelia - Ground Floor - critical failure storm water pump faulty | Plumbing & Drainage | Water | 125.59 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-02 16:08 | 2022-03-03 17:00 | 2022-03-03 06:30 | 2022-03-03 17:00 | 2022-03-03 09:00 |  |  | Attend site for pump issue.sign into security office and then spoke with neil for cultural centre, locate pump room and control box, he described an issue with the stormwater pumps bringing up a faulty on the BMS. The pump was not alarming nor was the red light on so I opened up the pump pit outside, tank was almost empty and I could not do much more.
MSA-DCA | WA5205114 | 0 | EQUANS Mechanical Services (WA) Pty Limited | one of the plant room - chiller 2 and 3 - to be reset - AC not working. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 562.525 | Pass | Fail | 0 | 0 | 2.5 | 2022-03-06 13:18 | 2022-03-06 15:18 | 2022-03-06 15:00 | 2022-03-06 17:18 | 2022-03-06 17:30 |  |  | Travelled to site and signed in. Signed out key and located plantation and found chiller 2 and 3 in fault. Chiller 2 had a phase loss fault and a chilled water interlock fault. Checked power all phases present. Power cycled chiller and chiller began to run as required. Chiller 3 was required to run but was not starting. Located and accessed BMS and found Dp sensor issue with CHW pump 3. BMS won't bring in chiller 3 because it can't detect flow from CHW pump 3. Dp sensor needs to be investigated/replaced. Chiller 2 currently running and is slowly bringing down temperatures.
MSA-DTAG | WA5208500 | 2 | AWB Co. | Registry of Births, Deaths and Marriages - Level 10 - Various - see details below | Electrical | Lighting, Internal | 301.4 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-09 09:09 | 2022-03-14 17:00 | 2022-03-10 12:30 | 2022-03-14 17:00 | 2022-03-10 15:00 |  |  | Attended site,signed in at security office,completed jsa went up to level 10 and spoke with site contact, walked around and located light fittings that are out, went to wholesaler and picked up materials , returned to site, set up work area, moved furniture to gain access to lights, removed old tubes /starters and replaced with new, disposed of tubes in designated bin , tested all lights , all are working as intended , completed paperwork , signed out at security officeJob complete
MSA-DFES | WA5208787 | 3 | Protek 24/7 Building & Maintenance | Main Administration - External Disabled Toilet - Broken soap dispenser in the disabled toilet | Building | Internal Walls | 516.95 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-09 10:52 | 2022-03-16 17:00 | 2022-03-14 08:00 | 2022-03-16 17:00 | 2022-03-14 10:30 |  |  | Replace dispenser
MSA-DTWD | WA5226895 | 2 | Precise Air Group | A-Block - Level 2 - A208 - Kendrew- A-Block A208 faulty aircon button | Air Conditioning | Room Air Conditioners | 512.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-14 14:47 | 2022-03-17 17:00 | 2022-03-15 10:30 | 2022-03-17 17:00 | 2022-03-15 13:00 |  |  | Attended site and completed pre start paperwork and signed in. Inspected sensor and found button to be broken. Picked up new sensor and returned to site. Fitted new wall push button and test ran. Left system operating in good working order. No further works required.
MSA-DTWD | WA5231812 | 2 | AWB Co. | Fluro lights are making a buzzing sound | Electrical | Lighting, Internal | 330.9 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-15 15:18 | 2022-03-18 17:00 | 2022-03-16 12:00 | 2022-03-18 17:00 | 2022-03-16 14:30 |  |  | Attended site and signed in,completed jsa, spoke to fm about job, located room and spoke to lecturer, she said that buzzing noise was coming from lights near whiteboard, multiple tubes needed replacing in room , liaised with lecturer about access , went to wholesaler and picked up parts , returned to site, waited 10 minutes for class to be over , set up work area and removed old tubes and starters , fo7nd a burnt ou starter in one of the lights lecturer said was buzzing, checked all ballasts and all looked good, replaced all tubes and starters, cleaned out light covers of bugs and dust, all lights now working as intended, disposed of tubes in allocated Fluro boxes on site, completed paperwork, packed up, signed out ,Job completed
MSA-DFES | WA5231818 | 2 | Go Doors | Access gate near RCR Pad will not close correctly - see further notes below | Building | Automatic Doors | 497.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-15 15:23 | 2022-03-18 17:00 | 2022-03-17 14:00 | 2022-03-18 17:00 | 2022-03-17 16:30 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5239698 | 2 | Techworks Plumbing | Geology Building - Level 1 - Female toilets - Replace 2x damaged Geberit cistern flush plates. | Plumbing & Drainage | Water | 490.23 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-16 14:33 | 2022-03-21 17:00 | 2022-03-18 11:00 | 2022-03-21 17:00 | 2022-03-18 13:30 |  |  | Picked up and replaced flush buttons on 2 female toilets. Found an issue with the flushing mechanism. Called Neil and informed of the seperate issue
MSA-MRWA | WA5255700 | 1 | EQUANS Mechanical Services (WA) Pty Limited | AC 2 - condensation drain blocked | Air Conditioning | Room Air Conditioners | 293.025 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-17 10:32 | 2022-03-18 17:00 | 2022-03-17 14:00 | 2022-03-18 17:00 | 2022-03-17 16:30 |  |  | Attended site, signed in and carried out the building induction. Accessed the lift motor room and and located affected Ducted units. Removed the p traps from both unit and flushed out. Vacummed the main drain line to clear any restrictions. Cleared and cleaned the condensate tray. Fitted p traps and tested with water and is now drainning correctly.
MSA-DFES | WA5275619 | 3 | Protek 24/7 Building & Maintenance | Watch Room to engine room door, screw has fallen out of securing lock mechanism & can't be put back | Building | Doors | 215.8 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-18 12:08 | 2022-03-25 17:00 | 2022-03-21 11:45 | 2022-03-25 17:00 | 2022-03-21 14:15 |  |  | New mount & reinstall striker plate
MSA-DTWD | WA5276873 | 3 | AWB Co. | Level 1 - Room B101 - power outlet broken *Contact John for location | Electrical | General Electrical | 475.69 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-18 12:55 | 2022-03-25 17:00 | 2022-03-23 12:30 | 2022-03-25 17:00 | 2022-03-23 15:00 |  |  | Attended site signed in completed jsa. Spoke with john site fm about job. Needed to replaced ducting and cable and gpo as was faulty and non operational. Tested and works now.**job completed**
MSA-DTWD | WA5287611 | 0 | Techworks Plumbing | GROUND - Behind S block - RO water is not working | Plumbing & Drainage | Water | 283.03 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-22 13:44 | 2022-03-22 15:44 | 2022-03-22 14:00 | 2022-03-22 17:44 | 2022-03-22 16:30 |  |  | Water not filtering through system properly, cleaned filters and reset electrics. System working again
MSA-DTWD | WA5296024 | 1 | Falcetta Plumbing and Gas | A Block - Female Toilets First floor and Male Toilets Ground Floor - blocked toilets | Plumbing & Drainage | Toilets/Cisterns | 450.97 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-30 08:41 | 2022-03-31 17:00 | 2022-03-31 13:30 | 2022-03-31 17:00 | 2022-03-31 16:00 |  |  | unblocked 2x toilets, 1x urinal, replaced 1x cistern
MSA-DTWD | WA5296432 | 2 | Damian Rak Electrical Pty Ltd | BLD 835 - Outside First Aid Room - Faulty Light | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2.5 | 2022-03-30 12:23 | 2022-04-04 17:00 | 2022-04-01 09:45 | 2022-04-04 17:00 | 2022-04-01 12:15 |  |  | job completed - replaced PR call night switch
MSA-DTWD | WA5301929 | 2 | WESTERN IRRIGATION PTY LTD | A-Block - external South side garden bed has a broken off sprinkler head | Plumbing & Drainage | Water | 569.12 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-01 14:40 | 2022-04-06 17:00 | 2022-04-05 13:30 | 2022-04-06 17:00 | 2022-04-05 16:00 |  |  | Locate and repair broken sprinklers throughout the irrigation system.
MSA-DTWD | WA5304166 | 2 | Lane's Plumbing | BLD 811 - Kitchen - blocked drain | Plumbing & Drainage | Drainage |  | Fail | Fail | 1 | 1 | 2.5 | 2022-04-04 15:21 | 2022-04-07 17:00 | 2022-04-11 09:30 | 2022-04-07 17:00 | 2022-04-11 12:00 |  |  | CLEAR BLOCKAGE TO DRAIN HOUSE 11
MSA-DTWD | WA5306550 | 2 | Precise Air Group | B-Block - B001 - aircon's not working | Air Conditioning | Room Air Conditioners | 266.88 | Pass | Pass | -1 | -1 | 2.5 | 2022-04-06 14:20 | 2022-04-11 17:00 | 2022-04-07 07:30 | 2022-04-11 17:00 | 2022-04-07 10:00 |  |  | Attended site and completed pre start paperwork and singed in. Acessed units in b001/b002. Test ran systems on cooling. Found to start and run. Checked indoor components and washed return air filters. Checked sensor settings and programmed controller to read from the return air sensor. Monitored system and found to unit to cycle on and off at Set point as required. Packed up work equipment and completed paperwork. Left systems operating all ok. No further works required.
MSA-DTWD | WA5306924 | 2 | M Construction (WA) | T-Block - Room T108 - has a hand towel dispencer come off the wall | Building | General Building | 333.25 | Pass | Pass | -1 | -1 | 2.5 | 2022-04-07 08:47 | 2022-04-12 17:00 | 2022-04-07 12:00 | 2022-04-12 17:00 | 2022-04-07 14:30 |  |  | Install hand towel dispenser with correct fixings.
MSA-DTWD | WA5308370 | 2 | Ronley Holdings Pty Ltd | E500 - Plasma Cutter Extraction Fan not coming on when called for | Building | General Building | 450 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-08 11:13 | 2022-04-13 17:00 | 2022-04-13 07:30 | 2022-04-13 17:00 | 2022-04-13 10:00 |  |  | We completed an inspection and service of the controls and switches that operate the extraction fan and the extraction unit. We can confirm the motor is in good running order but we were unable to test the VSD on completion as the machine had a lock tag. The TAFE has confirmed that the VSD in now running as it should. The filter cartridges in this unit are in urgent need of replacement. They are in very poor condition and have suffered water damage. See attached photos.There is water and debris inside the filter chamber. Defects Report and quotation uploaded in work logs.
MSA-DTAG | WA5325807 | 0 | Sapio Pty Ltd | Level 19 DOTL alarms no working. Foyer sliding doors and goods lift lobby doors tested with no alarm | Security | Monitoring | 250 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-14 12:33 | 2022-04-14 14:33 | 2022-04-14 13:15 | 2022-04-14 16:33 | 2022-04-14 15:45 |  |  | Found firmware problem restoring default reader properties. Checked and tested all doors after entiredoor and reader changes. No issues to report.
MSA-DTWD | WA5368369 | 2 | AHS Services WA Pty Ltd (Anchor) | East Female toilets leaking Again | Plumbing & Drainage | Toilets/Cisterns | 300.495 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-19 11:08 | 2022-04-22 17:00 | 2022-04-19 12:45 | 2022-04-22 17:00 | 2022-04-19 15:15 |  |  | Completed
MSA-DTWD | WA5380178 | 3 | GRAFFITI FORCE PTY LTD | Level 1 - External doors and walls - Graffiti | Cleaning | Graffiti | 434.76 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-22 09:09 | 2022-05-02 17:00 | 2022-05-02 13:10 | 2022-05-02 17:00 | 2022-05-02 15:40 |  |  | REMOVAL OF GRAFFITI FROM CAMPUS B1 EXTERNAL AREA
MSA-DTWD | WA5384085 | 3 | AWB Co. | Block 7 - Cafeteria - Lights tripping due to roof leak | Electrical | Lighting, Internal | 269.5 | Pass | Pass | -1 | -1 | 2.5 | 2022-04-28 09:42 | 2022-05-05 17:00 | 2022-04-29 06:00 | 2022-05-05 17:00 | 2022-04-29 08:30 |  |  | Attended site signed in jsa completed. Gained access with keys given day before. identified light with water in it. Disconnected and made redundant as its no longer in use. Left track up to cover the hole as requested. Massive leak in roof insulation wet*** job completed ***
MSA-DTWD | WA5384345 | 3 | AWB Co. | water leak far side of room from orange pipe approx 3rd window from left | Building | Windows | 509.88 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-28 12:07 | 2022-05-05 17:00 | 2022-05-05 10:15 | 2022-05-05 17:00 | 2022-05-05 12:45 |  |  | Attended, several possibilities, sealed flashing at ridge, box gutter joint below windows, sealed in corners of windowseals. Checked below roof sheet for damp, found a large elongated fixing hole. Repairs made. Job Complete.
MSA-DTWD | WA5385272 | 0 | Techworks Plumbing | Manin workshop - tap is gushing water | Plumbing & Drainage | Materials | 263.3 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-29 08:48 | 2022-04-29 10:48 | 2022-04-29 09:00 | 2022-04-29 12:48 | 2022-04-29 11:30 |  |  | Attended site to fix leaking tap. Signed in and had a look at the issueWas unable to find water isolation so I had to unlock the water meter cage out the front and isolate the whole campus for a few minutes Locked cage back up after I'd done the tap service and turned the water back on. Tested tap and flushed all off the air and dirty water out. Tap is working fine cleaned up, signed out and did paper work
MSA-DTWD | WA5393536 | 2 | M Construction (WA) | D-Block External loose step paver leading to lake side North West corner | Paving & Roadworks | Paving | 279.35 | Fail | Fail | 0 | 0 | 2.5 | 2022-05-04 08:42 | 2022-05-09 17:00 | 2022-05-10 08:45 | 2022-05-09 17:00 | 2022-05-10 11:15 |  |  | Attend site to investigate, dig out mortar from broken paver. Relay new one with sand/cement. Cut new corner paver and relay with sand/cement.
MSA-DTWD | WA5393820 | 3 | Techworks Plumbing | Vessel centre - ground - Ladies toilet - Toilet leaking - please check details below | Plumbing & Drainage | Toilets/Cisterns | 447.41 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-04 10:16 | 2022-05-11 17:00 | 2022-05-09 12:30 | 2022-05-11 17:00 | 2022-05-09 15:00 |  |  | Fixed leaking toilet
MSA-DTWD | WA5396141 | 2 | M Construction (WA) | D Block - marketing area - assemble flat pack staff desk to replace broken desk | Furniture | Office Furniture | 296.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-06 08:45 | 2022-05-11 17:00 | 2022-05-09 11:15 | 2022-05-11 17:00 | 2022-05-09 13:45 |  |  | Assemble flat pack desk, dispose of rubbish.
MSA-DTWD | WA5413504 | 3 | AWB Co. | Flickering Light in Client services - Light requires tombstone | Electrical | Lighting, Internal | 712.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-12 11:37 | 2022-05-19 17:00 | 2022-05-17 11:00 | 2022-05-19 17:00 | 2022-05-17 13:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Located faulty lighting. Found there were 13x lights out. Moved all old lights to front ready for back ones to be replaced with LED downlights. Went to wholesaler to pick up parts. Returned to site and wired in all led downlights to cabling. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5413582 | 2 | AWB Co. | Spotlights used to see hair colour have faded to yellow and need replacing x 8 | Electrical | Lighting, Internal | 980.64 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-12 12:06 | 2022-05-17 17:00 | 2022-05-17 13:30 | 2022-05-17 17:00 | 2022-05-17 16:00 |  |  | Attended site signed in. Completed jsa. Spoke to receiptionist about job. She wanted all globes in all salons replaced. Spoke to fm. Went to wholesaler for parts. Changed out all faulty globes for new ones. Took pictures after. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5454370 | 3 | Water2water Pty Ltd | South Block - Level 2 - S216 -Boilling/Chilled water unit failed | Plumbing & Drainage | Water | 557.785 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-17 10:43 | 2022-05-24 17:00 | 2022-05-24 13:30 | 2022-05-24 17:00 | 2022-05-24 16:00 |  |  | Replaced element, cleaned hot tank out
MSA-DTWD | WA5462107 | 1 | Equans Mechanical Services Australia | T110 - Inconsistent room temperature / BMS issue | Air Conditioning | Building HVAC Maintenance (Major Plant) | 476.63 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-19 11:19 | 2022-05-20 17:00 | 2022-05-19 13:30 | 2022-05-20 17:00 | 2022-05-19 16:00 |  |  | SYSTEMS SET TO AUTO - SEE REPORT
MSA-DFES | WA5462318 | 3 | Protek 24/7 Building & Maintenance | Ground Level - Male Staff Changerooms - Leak in roof - damage due to leak near exit door to PPE area | Roofing | Metal Roofing | 462.9 | Pass | Pass | -1 | -1 | 2.5 | 2022-05-19 13:30 | 2022-05-26 17:00 | 2022-05-20 11:45 | 2022-05-26 17:00 | 2022-05-20 14:15 |  |  | Repair Roof leak - Male Changerooms
MSA-DTWD | WA5476792 | 2 | AHS Services WA Pty Ltd (Anchor) | A112 - Café toilets - toilets are at the back of the café - hot and cold taps leaking | Plumbing & Drainage | Materials | 272.105 | Fail | Fail | 0 | 0 | 2.5 | 2022-05-25 11:42 | 2022-05-30 17:00 | 2022-06-01 08:00 | 2022-05-30 17:00 | 2022-06-01 10:30 |  |  | Repaired isolation valve in plumbing duct to isolate water supply so I could service the basin taps.
MSA-DTWD | WA5479772 | 3 | AWB Co. | East/ West walls - D block external - 2 x lights out | Electrical | Lighting, External | 391.95 | Fail | Fail | 2 | 2 | 2.5 | 2022-05-27 11:40 | 2022-06-03 17:00 | 2022-06-15 12:00 | 2022-06-03 17:00 | 2022-06-15 14:30 |  | WACCES | Attended site and signed in, completed jsa,spoke to fm about job , removed old lights and replaced with new, tested lights and working as intended, completed paperwork,cleaned up, packed up, signed out**job complete***
MSA-DCA | WA5480214 | 1 | Techworks Electrical | Perth Cultural Centre Precinct - Cultural Centre Square- loose cable hanging in front of the living | Electrical | General Electrical | 363.13 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-28 13:46 | 2022-05-30 17:00 | 2022-05-28 15:30 | 2022-05-30 17:00 | 2022-05-28 18:00 |  |  | loose light hanging in front of the livingstones. Disconnected light and made safe. New fitting required
MSA-DTAG | WA5491388 | 1 | Sapio Pty Ltd | Ground - Custody - Sally Port Access Door & Middle Gate not latching - See notes below | Security | Access Control | 450 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-03 15:20 | 2022-06-07 17:00 | 2022-06-06 09:30 | 2022-06-07 17:00 | 2022-06-06 12:00 |  |  | Modified locks and resealed
MSA-DCA | WA5495014 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Alexander Library Building - Level 3 - 10 degree stack - BMS Alarm – low humidity | Air Conditioning | Building HVAC Maintenance (Major Plant) | 450 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-08 08:56 | 2022-06-09 17:00 | 2022-06-08 12:00 | 2022-06-09 17:00 | 2022-06-08 14:30 |  |  | Attended site, signed in and accessed level 3, 10 degreee stack coolroom. Accessed the ceiling space on top of the cool room and found the dehumidifier running. Checked the wiring and controls signal and found the control relay faulty. Ordered and collected a new relay from the supplier, returned to site and installed and tested the relay and dehumidifier. 10 degree stack coolroom now operating as per normal.
MSA-DTWD | WA5495647 | 2 | AWB Co. | P Block - Main floor -3 phase power socket tagged out due to RCD RWB12 faulty | Electrical | General Electrical | 332 | Pass | Pass | -1 | -1 | 2.5 | 2022-06-08 13:49 | 2022-06-13 17:00 | 2022-06-09 09:30 | 2022-06-13 17:00 | 2022-06-09 12:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located rcd that was faulty, tested all other RCDs in workshop as per fm request, went to wholesaler and picked up new rcd , returned to site, isolated power circuit and replaced rcd , re energised circuit and tested rcd, everything working as intended, packed up, cleaned up, completed paperwork, signed out *** job completed***
MSA-DCA | WA5498982 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor -Plant room - really loud noise from hot water unit | Plumbing & Drainage | HWS/Units Electric & Gas | 293.025 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-10 09:06 | 2022-06-10 11:06 | 2022-06-10 09:30 | 2022-06-10 13:06 | 2022-06-10 12:00 |  |  | Unable to log into ProMAPs due to outage.Attended site. Investigated noise coming from ground floor plantroom. Found alarm on heat exchanger sounding. Reset power and tested operation of unit, actuators and pump, all ok. Confirmed operation through bms. Unit feeds hot water to labs upstairs, checked, all ok. Completed paperwork
MSA-DCA | WA5522052 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 5 - Plant Room - Chiller 3 Failure | Air Conditioning | Building HVAC Maintenance (Major Plant) | 293.025 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-15 12:13 | 2022-06-16 17:00 | 2022-06-15 14:00 | 2022-06-16 17:00 | 2022-06-15 16:30 |  |  | Attended site, signed in and accessed level 5 chiller plantroom. Found Chiller 3 with a (ALM-417 ISM - Motor amps not sensed). Reset, tested and monitored running conditions. Recorded the amp draws and all with in range. Will notify Airvision during there next maintenance visit of the fault.
MSA-DTWD | WA5522217 | 2 | AWB Co. | High level ceiling lights Not working in the passage | Electrical | Lighting, Internal | 342.37 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-15 13:29 | 2022-06-20 17:00 | 2022-06-20 09:30 | 2022-06-20 17:00 | 2022-06-20 12:00 |  |  | Attended site and signed in. Completed JSA. Located C block walkway. Turned out lights and nothing happened. Got large ladder out to access the lights. And found dead lamps in all of the fittings. Supply and replaced all lamps in the fittings. Tested all okay. Signed out. Job complete
MSA-DCA | WA5522373 | 2 | Techworks Plumbing | Ground Level - Hacket Hall - Male Toilet - Toilet Blocked - See notes | Plumbing & Drainage | Toilets/Cisterns | 177.92 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-15 14:50 | 2022-06-20 17:00 | 2022-06-17 14:00 | 2022-06-20 17:00 | 2022-06-17 16:30 |  |  | Attended and checked mens toilets neither of the toilets would block up. Tested multiple times with toilet paper, attended other job then returned to this one, still no toilets would block up
MSA-DTWD | WA5534711 | 2 | Techworks Electrical | Blown Lights throughout admin building need replacement | Electrical | Lighting, Internal | 841.48 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-16 13:36 | 2022-06-21 17:00 | 2022-06-20 12:30 | 2022-06-21 17:00 | 2022-06-20 15:00 |  |  | 5x lights replaced - Replaced compact ?uro downlights with new led downlights in admin male bathroom
MSA-DCA | WA5563440 | 1 | GPS Plumbing & Gas Services PtyLtd | M Block (rear) - M block window - Plumbing leak at rear of block | Plumbing & Drainage | Drainage | 514.86 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-20 14:44 | 2022-06-21 17:00 | 2022-06-21 11:20 | 2022-06-21 17:00 | 2022-06-21 13:50 |  |  | Investigate water leak to M building.Found the leaking pipe in the roof.Shut the water supply off but leak did not stop.Further investigate pipes in the roof and found that the pipe is a fire pipe.Advised programmed and was told to leave as is.They will get a fire contractor to fix.
MSA-DTWD | WA5564560 | 1 | CLEVELAND COMPRESSED AIR SERVICES | External - Between H & T-Block - please read details below | Equipment | Compressors, Generators | 264 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-21 11:26 | 2022-06-22 17:00 | 2022-06-22 07:30 | 2022-06-22 17:00 | 2022-06-22 10:00 |  |  | Issue was with the Auto DrainAuto drain was cleaned and tested, worked well after cleanIf issues happens again, auto drain will need to be replaced
MSA-DTWD | WA5567386 | 2 | AWB Co. | E-Block - Deli - roof leak above coffee machine | Building | General Building | 492.42 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-24 08:35 | 2022-06-29 17:00 | 2022-06-28 11:00 | 2022-06-29 17:00 | 2022-06-28 13:30 |  |  | Investigated roof leakFound broken silicon/decktie on anchor point above roof leakCleaned back old silicon and applied new over sealCleaned and packed up
MSA-DTWD | WA5567389 | 2 | M Construction (WA) | T009 - has broken disposable curtain - new supplied curtains to be re hung | Building | General Building | 270 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-24 08:38 | 2022-06-29 17:00 | 2022-06-28 09:30 | 2022-06-29 17:00 | 2022-06-28 12:00 |  |  | Attended site to re-hang new curtain in T Block Room.
MSA-DTWD | WA5570523 | 2 | Techworks Electrical | Restaurant Ceiling light rusted/ faulty | Electrical | Lighting, Internal | 600.8 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-28 12:16 | 2022-07-01 17:00 | 2022-07-01 10:30 | 2022-07-01 17:00 | 2022-07-01 13:00 |  |  | Replaced damaged flickering light in E block restaurant kitchen with new led panel light and frame
MSA-DCA | WA5570939 | 0 | EQUANS Mechanical Services (WA) Pty Limited | St James Art Gallery - Level 4 - Steam plant low water alarm | Building | Materials | 620.075 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-28 22:00 | 2022-06-29 | 2022-06-28 22:30 | 2022-06-29 02:00 | 2022-06-29 01:00 |  |  | Checked out faults on BMS.Ro plant had failed steam generators.Reset RO plant and checked tanks and pumps.Reset air compressors.Reset steam generators and humidifiers.
MSA-DTAG | WA5585045 | 1 | Seme Solutions Pty Ltd | Magistrate under desk duress stuck in active position (possible warranty) | Security | Security Management System | 402.1 | Fail | Fail | 0 | 0 | 2.5 | 2022-07-05 12:00 | 2022-07-06 17:00 | 2022-07-07 12:30 | 2022-07-06 17:00 | 2022-07-07 15:00 |  |  | Replaced the faulty duress button and tested it ok after replacement. Leave one spare duress button on site in security comms cabinet in comms room. PA2ESR X 2.
MSA-DTWD | WA5586629 | 3 | AWB Co. | Downpipe in walkway behind A212 start of walkway 100mm downpipe leaking | Roofing | Metal Roofing | 548.12 | Pass | Pass | -1 | -1 | 2.5 | 2022-07-06 13:07 | 2022-07-13 17:00 | 2022-07-07 09:30 | 2022-07-13 17:00 | 2022-07-07 12:00 |  |  | Removed rusted 100mm outlet, cleaned back area and Installed new 100mm outlet.Found un sealed flashing over area, cleaned back old silicon and re sealed flashing
MSA-DCA | WA5603963 | 0 | Techworks Electrical | Murray ST Entrance - The Gantry - Cables are coming out from lights - drooping down | Electrical | Lighting, External | 400.945 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-12 14:33 | 2022-07-12 16:33 | 2022-07-12 15:00 | 2022-07-12 18:33 | 2022-07-12 17:30 |  |  | replaced cabling in effected lightsResecured conduit with extra staggered saddlesSilicone fittings
MSA-DTWD | WA5608917 | 1 | Falcetta Plumbing and Gas | External - main water line is leaking | Plumbing & Drainage | Water | 319.015 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-13 12:40 | 2022-07-14 17:00 | 2022-07-13 15:30 | 2022-07-14 17:00 | 2022-07-13 18:00 |  |  | dig to expose, cut and replace section of 20mm copper
MSA-DTWD | WA5674904 | 3 | AWB Co. | Spot welder closes to roller door not working. | Electrical | General Electrical | 291.205 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-21 15:22 | 2022-07-28 17:00 | 2022-07-26 10:30 | 2022-07-28 17:00 | 2022-07-26 13:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located spot welder and discussed operation and problems with lecturer, tested circuit and voltage is good, tested limit switch and working as intended, tested fuse and still good, inpsected circuit board and looked like some damage was present, called fm and discussed options, tagged out isolator, fm said to close job off and he will sort out, packed up, cleaned up, completed paperwork, signed out **job completed**
MSA-DTWD | WA5692033 | 1 | Equans Mechanical Services Australia | Seminar ADHD1 - Not Heating | Air Conditioning | Room Air Conditioners | 348.365 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-03 09:49 | 2022-08-04 17:00 | 2022-08-03 13:30 | 2022-08-04 17:00 | 2022-08-03 16:00 |  |  | ATTENDED SITE AND STARTED INVESTIGATION - THIS JOB HAS ALREADY BEEN ATTENDED ON WA5570622 AND BRAF'ED
MSA-DTAG | WA5697743 | 1 | Midolo Building Services | ground/L1-Leak from ceiling where the 1903 building and 1987 wing meet (judicial corridor | Roofing | Metal Roofing | 291 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-09 11:38 | 2022-08-10 17:00 | 2022-08-10 09:30 | 2022-08-10 17:00 | 2022-08-10 12:00 |  |  | assessed roof. cleaned up area as that may be a potential for leaks
MSA-DTWD | WA5699372 | 2 | AWB Co. | external-Replace damaged sensor unit G block security lights-see notes | Electrical | Lighting, Internal | 440.005 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-10 09:16 | 2022-08-15 17:00 | 2022-08-12 08:00 | 2022-08-15 17:00 | 2022-08-12 10:30 |  |  | Attended site and signed in. Completed JSA. Located lights around g block. Tested to find some lights operating. Checked out timer and Pe cell control and all seems to be operating correctly. Supply and replaced 2 x lights on walls that were not working. Reset the control system. Clean and tidy site. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5706110 | 3 | Protek 24/7 Building & Maintenance | Courtyard - Water leak at East and West entrances to courtyard | Roofing | Metal Roofing | 437.57 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-11 08:48 | 2022-08-18 17:00 | 2022-08-15 07:30 | 2022-08-18 17:00 | 2022-08-15 10:00 |  |  | Carried out report and advised john that overflow pops x 2 on each side to remove issue of box gutters overflowing to inside of buildingBRAF Declined
MSA-MRWA | WA5715002 | 2 | AWB Co. | Car Park Security Lighting - Lighting is not working | Electrical | Lighting, Internal | 290.005 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-12 10:12 | 2022-08-17 17:00 | 2022-08-16 11:45 | 2022-08-17 17:00 | 2022-08-16 14:15 |  |  | Attended site and signed in, completed jsa,spoke with operator on level 1 about lights , found exterior lighting circuits in ground floor board, turned on overrides to see what was operational, no lights were on, turned off overrides and found all circuits isolated with danger tags in board, called number on tag to speak with contractor, called Danika and explained situation, fowarded all info about contractors to Danika, located 2nd switchboard with security light circuit, tested override and carpark lights turned on, opened up board and found timer had been disconnected, looked outside for p.e cell and couldn’t see one, re wired timer to control lights, lights now working as intended, Danika said to close job off, packed up, completed paperwork , signed out *job complete*
MSA-DCA | WA5735065 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Kirsten Lab - Temperature reading 16 degrees at present time | Air Conditioning | Room Air Conditioners | 315.315 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-16 11:10 | 2022-08-17 17:00 | 2022-08-16 12:30 | 2022-08-17 17:00 | 2022-08-16 15:00 |  |  | Attended site. Signed in, gained keys. Investigated Kirsten's lab located collections. Checked bms and found loss of comms to heating water plant. Power outage yesterday afternoon possible cause. Reset comms, system still off-line. Schneider dialled into site and accessed carried out another reset to both ends and tested operation. Heating water plant back online. Plant operating. Completed paperwork
MSA-DCA | WA5735761 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Remove and replace/repair the blocked sediment filters on the DI system | Air Conditioning | Room Air Conditioners | 315.315 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-16 15:32 | 2022-08-19 17:00 | 2022-08-18 09:00 | 2022-08-19 17:00 | 2022-08-18 11:30 |  |  | Attended site, accessed the basement RO Plant DI system and checked operation. Removed the sediment and carbon filters and replaced with new ones. Checked PPM supply and outlet levels. Will monitor system and recheck in a couple days.
MSA-DCA | WA5751663 | 1 | SPECIALISED LIFTING SERVICE | Lower ground floor - Loading Bay - Hoist is not operating | Lifts | Vehicle hoists | 536.82 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-17 11:09 | 2022-08-18 17:00 | 2022-08-18 10:30 | 2022-08-18 17:00 | 2022-08-18 13:00 |  |  | INSPECTED CHAIN BLOCK, SERVICED AND ADVISED PFM COORDINATOR
MSA-DCA | WA5751870 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 -HLT Stage -Honeywell Management System Global Scheduling having recurring faults -See notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 610.19 | Fail | Fail | 1 | 1 | 2.5 | 2022-08-17 11:17 | 2022-08-22 17:00 | 2022-08-30 08:00 | 2022-08-22 17:00 | 2022-08-30 10:30 |  |  | Honeywell carried out works. Honeywell service report attached.
MSA-DCA | WA5761991 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Loud hum coming from the ceiling space of the Executive Suite on level three. | Air Conditioning | Room Air Conditioners | 315.315 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-18 12:16 | 2022-08-25 17:00 | 2022-08-24 13:30 | 2022-08-25 17:00 | 2022-08-24 16:00 |  |  | Attended site, signed in and accessed level 3 affected area. Could not here any humming noises at the time of visit. Located vavs in the affected area and manually switched on the vav heater fans. Discovered a humming noise coming from the return air duct filter access. Removed the return air filter and found a piece of silver tape wedged in-between the return air filter and frame. Removed the silver tape and switched the fan back on which had stopped the humming noise. Cleaned the return air filter and switched the fan back to auto.
MSA-DTWD | WA5780243 | 2 | Australian Airconditioning Services Pty Ltd | B2308 - Faulty AC Unit - AC unit is the one closest to the entrance to the classroom | Air Conditioning | Room Air Conditioners | 387.36 | Pass | Pass | -1 | -1 | 2.5 | 2022-08-19 08:44 | 2022-08-24 17:00 | 2022-08-19 13:30 | 2022-08-24 17:00 | 2022-08-19 16:00 |  |  | complete
MSA-DTWD | WA5790033 | 2 | Techworks Electrical | D Block - Level 2 - Chiller compound - landing area on roof has a loose light fitting wires exposed | Electrical | Lighting, Internal | 482.435 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-22 08:33 | 2022-08-25 17:00 | 2022-08-23 11:00 | 2022-08-25 17:00 | 2022-08-23 13:30 |  |  | Replaced fluros on chiller deck
MSA-DFES | WA5794270 | 3 | AWB Co. | Level 1 - Engine Room - Door does not close properly - See notes below | Building | Doors | 378.42 | Pass | Fail | 0 | 0 | 2.5 | 2022-08-24 13:38 | 2022-08-31 17:00 | 2022-08-31 15:30 | 2022-08-31 17:00 | 2022-08-31 18:00 |  |  | adjust hinge, latch and door closer to make the door latch properly
MSA-DCA | WA5799110 | 1 | Protek 24/7 Building & Maintenance | Boardwalk - Wire fencing strip has detached. | Building | Steel Fencing & Gates | 512.92 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-30 09:39 | 2022-08-31 17:00 | 2022-08-30 12:30 | 2022-08-31 17:00 | 2022-08-30 15:00 |  |  | Cables reconnected Loctite applied to secure cable
MSA-DTWD | WA5800807 | 2 | M Construction (WA) | C Block - Reception - Refit cupboard door, hinges are faulty | Furniture | Office Furniture | 335.15 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-31 12:29 | 2022-09-05 17:00 | 2022-09-05 09:30 | 2022-09-05 17:00 | 2022-09-05 12:00 |  |  | Removed old hinges. Fitted new hinges and installed door catch.
MSA-DTWD | WA5800828 | 2 | AWB Co. | Blown Light needing replacement in Room N001 | Electrical | Lighting, Internal | 277.095 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-31 12:43 | 2022-09-05 17:00 | 2022-09-05 09:00 | 2022-09-05 17:00 | 2022-09-05 11:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located N block. Set up work area. Isolated circuit. Replaced multiple tubes in class. Energised and tested. Packed up. Went over to c block and set up work area. Isolated power. Replaced multiple lamps and ballast. Energised and tested. Packed up. Notified relevant personnel of works completed. **job complete**
MSA-DTAG | WA5801313 | 3 | Australian HVAC Services Pty. Ltd. | BMS faulty - not displaying A/C readings - see note below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 729.41 | Fail | Fail | 1 | 1 | 2.5 | 2022-08-31 15:19 | 2022-09-07 17:00 | 2022-09-16 09:30 | 2022-09-07 17:00 | 2022-09-16 12:00 |  |  | Attended site with bms technician, found site had tested bms with another monitor. Tech found the fault was with the pc restored signal to the monitor. Tested bms operation & settings ok.
MSA-DCA | WA5834282 | 0 | Techworks Electrical | Bollards not responding and stuck in the up position | Building | Steel Fencing & Gates | 930.385 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-06 14:44 | 2022-09-06 16:44 | 2022-09-06 15:30 | 2022-09-06 18:44 | 2022-09-06 18:00 |  |  | Re aligned bollards so that they are in sync. Cleaned out bases underneath bollards. Re calibrated so they operate at the same time.
MSA-DTWD | WA5834309 | 2 | Protek 24/7 Building & Maintenance | RHT2 machine workshop - Roof Leak | Roofing | Metal Roofing | 651.97 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-06 14:58 | 2022-09-09 17:00 | 2022-09-09 13:15 | 2022-09-09 17:00 | 2022-09-09 15:45 |  |  | Water tested area of leak , Cleaned and re sealed apron join and flashing connections , re water tested to confirm
MSA-DTWD | WA5839110 | 2 | AWB Co. | Vehicle Body building - Faulty Pendant GPO | Electrical | General Electrical | 628.055 | Pass | Pass | -1 | -1 | 2.5 | 2022-09-09 09:28 | 2022-09-14 17:00 | 2022-09-09 09:30 | 2022-09-14 17:00 | 2022-09-09 12:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located vehicle body building. Isolated power. Set up work area. Removed faulty plug. Supplied and installed new outlet with switch. Energised. Packed and cleaned up site. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5853681 | 2 | Techworks Electrical | R-Block power to computer keeps turning off | Electrical | General Electrical | 278.745 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-12 09:59 | 2022-09-15 17:00 | 2022-09-14 08:00 | 2022-09-15 17:00 | 2022-09-14 10:30 |  |  | Investigated power issues with computers in theatre room 1. Tested data outlets and gpo’s in room. No issues. Final issue was the settings on the computer with sleep mode being set on 15 minutes. Adjusted to every 3 hours. No issues since.
MSA-DFES | WA5861362 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Motion light sensors in various rooms not working - See notes below | Electrical | Lighting, Internal | 437.73 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-13 08:53 | 2022-09-16 17:00 | 2022-09-13 13:30 | 2022-09-16 17:00 | 2022-09-13 16:00 |  |  | Arrived onsite at 13:30 to investigate sensor issue, was told that sensors in certain areas are causing nuisance due to turning off whilst some is in room. Disconnected sensors and installed 3x switches in Admin, office and store. Tested ok, advised staff of works and left site at 16:00.
MSA-DTWD | WA5861594 | 2 | AWB Co. | Roof leaking onto electrical equipment | Roofing | Metal Roofing | 539.78 | Fail | Fail | 0 | 0 | 2.5 | 2022-09-13 10:13 | 2022-09-16 17:00 | 2022-09-19 07:30 | 2022-09-16 17:00 | 2022-09-19 10:00 |  |  | Investigated leak found apron flashing not sealed at joints, carried out prep and seal
MSA-DFES | WA5867309 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Workshop/Yard - outside yard toilet block - urinal blocked in men's toilet | Plumbing & Drainage | Toilets/Cisterns | 348.08 | Pass | Pass | -1 | -1 | 2.5 | 2022-09-14 09:38 | 2022-09-19 17:00 | 2022-09-15 09:45 | 2022-09-19 17:00 | 2022-09-15 12:15 |  |  | Arrived on site and singed in went to blocked urinal located outside year near work shop plung urinal could not clear blockage went outside found, IO life lid blockage was further down the line used drain machine hit something 1.5 rods down did not pull out anything. Urinal was still blocked used bowl guard urinal stated to run. Tested everything with water everything was fine.
MSA-DCA | WA5961793 | 2 | Protek 24/7 Building & Maintenance | Server room - Door handle damaged | Building | Doors | 268.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-19 09:42 | 2022-09-22 17:00 | 2022-09-20 09:00 | 2022-09-22 17:00 | 2022-09-20 11:30 |  |  | Install new circlip and tested
MSA-DTWD | WA5962556 | 2 | AHS Services WA Pty Ltd (Anchor) | A Block East - Male Toilets - Toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 476.7575 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-19 15:06 | 2022-09-22 17:00 | 2022-09-21 12:30 | 2022-09-22 17:00 | 2022-09-21 15:00 |  |  | Blocked toilets
MSA-DTWD | WA5962563 | 2 | AHS Services WA Pty Ltd (Anchor) | Gym Female toilets blocked | Plumbing & Drainage | Toilets/Cisterns | 190.0375 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-19 15:13 | 2022-09-22 17:00 | 2022-09-21 12:30 | 2022-09-22 17:00 | 2022-09-21 15:00 |  |  | Blocked toilets in gym and kitchen
MSA-DTWD | WA5971089 | 1 | COMMERCIAL PLUMBING AND GAS | The mixer tap will not stop running. | Plumbing & Drainage | Water | 493.685 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-20 11:32 | 2022-09-21 17:00 | 2022-09-20 15:00 | 2022-09-21 17:00 | 2022-09-20 17:30 |  |  | replaced mixer and installed mini stops
MSA-DCA | WA5972528 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Fault Light on the ETS boiler 2 -Plant Room | Equipment | Electrical Equipment | 337.835 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-21 06:10 | 2022-09-21 08:10 | 2022-09-21 07:30 | 2022-09-21 10:10 | 2022-09-21 10:00 |  |  | Attended site, signed in and gained access. Investigated boiler 2 in fault. Found boiler 2 in no start fault. Checked over nothing tripped. Reset and switched boiler 2 to lead. Reset alarms on bms. Tested operation, boiler operating as required. Continued to monitor and completed paperwork.
MSA-DTWD | WA5973431 | 2 | Techworks Plumbing | Faulty sink hose sprays taps - See notes below | Plumbing & Drainage | Water | 880.42 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-21 13:09 | 2022-09-27 17:00 | 2022-09-27 06:30 | 2022-09-27 17:00 | 2022-09-27 09:00 |  |  | Ross bennett 27/9/22arrived on site and signed in at the office then met Kevin and he opened up the classrooms for us 3 taps had been broken and snapped in the Flexi hoses we got given 3 new tap hand pieces from Kevin.we removed the old Flexi hoses and weight then we installed the new Flexi hose and tap hand pice for 3 of the basins then we tested them to see if they were working well and the Flexi is sliding through the tap smoothly we had to drill out abit of the bench on one of the tap to make the Flexi slide smoothly to avoid breaking any more of the taps.once completed we called Kevin and he came and had a look and he was happy we cleaned up all mess and tools then signed out and left sote completed paperwork
MSA-DTWD | WA5976342 | 1 | AWB Co. | Belt splicing workshop - Damaged plug on belt cutting machine | Equipment | Electrical Equipment | 684.8 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-27 08:52 | 2022-09-28 17:00 | 2022-09-27 10:30 | 2022-09-28 17:00 | 2022-09-27 13:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Plug tops needed adding onto leads. Went to wholesaler for parts. Returned to site. Fit off all required plugs. Test and tagged. Tested extension leads. Took pics. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5976968 | 1 | AWB Co. | Belt slicing workshop - damaged plugs and extension cords | Electrical | General Electrical | 1873.38 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-27 12:40 | 2022-09-28 17:00 | 2022-09-27 13:30 | 2022-09-28 17:00 | 2022-09-27 16:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Plug tops needed adding onto leads. Went to wholesaler for parts. Returned to site. Fit off all required plugs. Test and tagged. Tested extension leads. Took pics. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5977300 | 2 | EQUANS Mechanical Services (WA) Pty Limited | L5 state library-boiler 2 failure | Mechanical Services | Boilers | 999.165 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-27 15:31 | 2022-09-30 17:00 | 2022-09-28 12:00 | 2022-09-30 17:00 | 2022-09-28 14:30 |  |  | Met Tomlinson on-site and carried out fault finding on ets boiler 2. Accessed bms and switched boiler 1 off to test operation of boiler 2. Found flame detector to be faulty and carried out replacement. Tested operation, unit didn't fault. Reinstated boiler 1, plant all in auto. Completed paperwork
MSA-DTWD | WA5978318 | 3 | AWB Co. | Block A & B - faulty lighting - various locations in the buildings - please see Kim onsite | Electrical | Lighting, Internal | 510.555 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-28 10:10 | 2022-10-05 17:00 | 2022-10-03 10:30 | 2022-10-05 17:00 | 2022-10-03 13:00 |  |  | Attended site signed in jsa completed.spoke with site contact about jobs in areas. Replaced 16 tubes in various places on site. All tested and working job completed
MSA-DTWD | WA5980049 | 2 | Equans Mechanical Services Australia | Issues with the BMS. - see notes | Air Conditioning | Room Air Conditioners | 506.92 | Fail | Fail | 0 | 0 | 2.5 | 2022-09-29 12:11 | 2022-10-04 17:00 | 2022-10-07 12:00 | 2022-10-04 17:00 | 2022-10-07 14:30 |  |  | SEE REPORT
MSA-DTWD | WA5994864 | 2 | AHS Services WA Pty Ltd (Anchor) | A 352 Unisex toilet - Flexible hoses are leaking | Plumbing & Drainage | Water | 347.505 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-06 09:22 | 2022-10-11 17:00 | 2022-10-10 12:45 | 2022-10-11 17:00 | 2022-10-10 15:15 |  |  | .
MSA-DTWD | WA5995059 | 3 | AWB Co. | Pedestal grinder has no emergency stop button | Equipment | Electrical Equipment | 452.505 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-06 10:13 | 2022-10-13 17:00 | 2022-10-12 08:00 | 2022-10-13 17:00 | 2022-10-12 10:30 |  |  | Attended site signed in jsa completed. Found non compliant fixed machinary with no E STOP for grinder. Swapped gpo as buttons were stuck on. Put e stop for gpo and testedAll safe and workingJob completed
MSA-DFES | WA5995558 | 3 | Go Doors | RETOSPECTIVE WORK ORDER-Ground Floor - Pump Room - Issues with Roller Door - See notes below | Building | Automatic Doors | 1462.72 | Fail | Fail | 11 | 11 | 2.5 | 2022-08-11 14:00 | 2022-08-18 17:00 | 2022-10-31 13:30 | 2022-08-18 17:00 | 2022-10-31 16:00 |  |  | Completed works as quoted.
MSA-DTWD | WA5995656 | 2 | Australian Airconditioning Services Pty Ltd | There is water leaking from the corner of the LG cassette unit | Air Conditioning | Room Air Conditioners | 355.08 | Pass | Pass | -1 | -1 | 2.5 | 2022-10-06 14:26 | 2022-10-11 17:00 | 2022-10-07 13:30 | 2022-10-11 17:00 | 2022-10-07 16:00 |  |  | Investigated unit and found roof leak to be the likely cause of drip. Unit is fully operational and not leaking.
MSA-DTAG | WA6000657 | 3 | PPM Project Painting & Maintenance | Ground Floor - Male Public Toilets - Graffiti | Cleaning | Graffiti |  | Fail | Fail | 6 | 6 | 2.5 | 2022-10-10 09:30 | 2022-10-17 17:00 | 2022-12-01 09:30 | 2022-10-17 17:00 | 2022-12-01 12:00 |  |  | Removal of graffiti
MSA-DTWD | WA6015076 | 2 | Australian Airconditioning Services Pty Ltd | ground-2G20 Maintenance Officers office.-Main B.M.S. not connecting-see notes | Air Conditioning | Room Air Conditioners | 416.68 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-12 14:39 | 2022-10-17 17:00 | 2022-10-14 12:30 | 2022-10-17 17:00 | 2022-10-14 15:00 |  |  | On investigation of PC an error was generated when trying to login. The master controller was then checked, and it was found to have no power. An investigation was carried out at the mechanical switchboard and it was found that there was no 24VAC power in the panel at all.Panel had 240V power which feeds a UPS (Battery Backup System) and this in turn fed the 24VAC transformer. Power was checked on the outgoing side of the UPS and there was no voltage. On the ingoing side of UPS there was 240V. Panel was powered down and UPS was bypassed by rewiring the connection in the panel so that the transformer is fed direct from the panel 240V. Panel was powered back up and 24VAC checked. There was now 24VAC at the transformer. The BMS login was tried again and this time it worked. Checks were carried out on BMS, and it was found that all plant was online and operating.The UPS is old and therefore most likely the batteries have failed in it. This has happened previously onsite and we have just
MSA-DTWD | WA6020189 | 2 | COMMERCIAL PLUMBING AND GAS | Level 4 - B2457 Male Toilet - Toilet Flush not working in first cubicle | Plumbing & Drainage | Toilets/Cisterns | 349.015 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-13 11:13 | 2022-10-18 17:00 | 2022-10-17 15:30 | 2022-10-18 17:00 | 2022-10-17 18:00 |  |  | repaired 2x cisterns
MSA-DFES | WA6022868 | 2 | SONTEC WA PTY LTD | CCTV Camera – C8 Disconnected | Security | CCTV Surveillance | 550 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-14 12:34 | 2022-10-19 17:00 | 2022-10-19 13:15 | 2022-10-19 17:00 | 2022-10-19 15:45 |  |  | 19/10/22 - Dean SimpsonC8 disconnectedReset password on NVR and connected NVR to UPS.
MSA-DCA | WA6113145 | 3 | EQUANS Mechanical Services (WA) Pty Limited | B2-03 New chilled water actuator needed on FCU B2-03, old one condensating onto roof. | Air Conditioning | Room Air Conditioners | 661.22 | Pass | Pass | -1 | -1 | 2.5 | 2022-10-24 09:14 | 2022-10-31 17:00 | 2022-10-24 13:30 | 2022-10-31 17:00 | 2022-10-24 16:00 |  |  | ATTENDED SITE WITH PARTS. FOUND CHILLED WATER ACTUATOR CONDENSATION HEAVILY. CUT BACK INSULATION AND UNSCREWED CHILLED WATER ACTUATOR. CHECKED OVER VALVE AND STEM FOR LEAKS, NO SIGNS OF LEAKS AND DRIP IS SOLELY FROM CONDENSATION. ACCESSED THE BMS TO CHECK OPERATION OF CHILLED WATER ACTUATOR, ALL OK. CLEANED STEM AND ACTUATOR AND SCREWED BACK INTO PLACE. REINSULATED PIPEWORK AND MADE AN AIR TIGHT SEAL TO STOP CONDENSATION. TESTED ACTUATOR AGAIN NOW THAT IT'S SEATED ON THE VALVE, ALL OK. CLEANED WORK AREA AND CARRIED OUT PAPERWORK.
MSA-DFES | WA6126914 | 2 | Protek 24/7 Building & Maintenance | Ground - between Captain and Lieutenant office space - upper door frame has water pooling at the top | Roofing | Tiled Roofing | 492.59 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-25 14:19 | 2022-10-28 17:00 | 2022-10-26 13:30 | 2022-10-28 17:00 | 2022-10-26 16:00 |  |  | Water test, Cut back lap joins to stop capillary action, silicone all holes due to high amount of cables behind. Water test to confirm
MSA-DCA | WA6130590 | 1 | EQUANS Mechanical Services (WA) Pty Limited | B1 Basement Level - Security Control Room - Door NG-64, Mag-lock fault - See notes | Security | Security Management System | 543.64 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-28 13:14 | 2022-10-31 17:00 | 2022-10-31 12:00 | 2022-10-31 17:00 | 2022-10-31 14:30 |  |  | Engaged Honeywell to attend site. Checked EBI Point and found door set to unlock. Reset door locking point. Checked door lock operation. All now ok. Also edited graphic page and added combo box. Shown security officer. All now ok.
MSA-DTWD | WA6132593 | 2 | Building Automation & Electrical Services Pty Ltd | BMS is not switching on lights to all building - Since power outage over weekend | Building | General Building |  | Pass | Pass | 0 | 0 | 2.5 | 2022-10-31 15:46 | 2022-11-03 17:00 | 2022-10-31 16:30 | 2022-11-03 17:00 | 2022-10-31 19:00 |  |  | - Investigations found BMS computer in full working order.- Tests on the network found comm's loss to network lighting controlleron the grd flr.- Local investigations found the 24v AC breaker had tripped & was foundin the off position. I was informed by facilities management team thatthey had tried to reset breaker but at no success.- Output cards were powered OFF and 24v breaker was reinstated.Each output card had its power returned one at a time. Load sheddingthe power back on enabled all the lighting circuits to return to fullworking conditions.- This is the second time the breaker has failed on a power failuresituation. I would advise this breaker to be changed and also a ampdraw reading collected as to advise the size of breaker required forreplacement
MSA-DTAG | WA6143813 | 1 | Australian HVAC Services Pty. Ltd. | Switchroom (Courtroom side) - Aircon unit in switch room not working. | Air Conditioning | Room Air Conditioners | 267.45 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-01 15:23 | 2022-11-02 17:00 | 2022-11-02 13:30 | 2022-11-02 17:00 | 2022-11-02 16:00 |  |  | F8xed
MSA-DTWD | WA6148803 | 3 | AWB Co. | Welding Technology 3G5-Broken light fitting above bay 2 | Electrical | Lighting, Internal | 357.505 | Pass | Pass | -1 | -1 | 2.5 | 2022-11-04 09:20 | 2022-11-11 17:00 | 2022-11-04 11:00 | 2022-11-11 17:00 | 2022-11-04 13:30 |  |  | Attended site signed in jsa completed. Found broken light inside welding bay. Removed and replaced with led vandal proof fitting. Tested and operational.Job completed
MSA-DTWD | WA6154644 | 2 | AWB Co. | U Block - Workshop U009 - Repair or replace light switch which has been pushed in. | Electrical | Lighting, Internal | 479.08 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-07 14:38 | 2022-11-10 17:00 | 2022-11-09 12:00 | 2022-11-10 17:00 | 2022-11-09 14:30 |  |  | Attended site and signed in. Completed JSA. spoke to fm, he said there are a few more light switches faulty. Replaced 2x switch mechs. Lecturer said 2 more were very warm. Replaced mech as they were making arcing sounds when switched and warm, fixed switch in R block, all working as intended, completed paperwork,signed out , job completed
MSA-DTAG | WA6156668 | 0 | Sapio Pty Ltd | Level 1 - all keypads not functional | Security | Access Control | 322.8 | Fail | Fail | 0 | 0 | 2.5 | 2022-11-09 09:39 | 2022-11-09 11:39 | 2022-11-09 12:00 | 2022-11-09 13:39 | 2022-11-09 14:30 |  |  | Replaced faulty power supply
MSA-DTWD | WA6157120 | 2 | AHS Services WA Pty Ltd (Anchor) | Kitchen - Sink is blocked | Plumbing & Drainage | Drainage | 272.105 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-09 13:06 | 2022-11-14 17:00 | 2022-11-11 13:30 | 2022-11-14 17:00 | 2022-11-11 16:00 |  |  | Unable to clear blockage with hand snake or drain machine.Cut out blocked pipe by the main stack.Cleaned out then reconnected and tested.
MSA-DFES | WA6157179 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Multiple lights not working - see note | Electrical | Lighting, Internal | 1468.19 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-09 13:28 | 2022-11-16 17:00 | 2022-11-16 09:45 | 2022-11-16 17:00 | 2022-11-16 12:15 |  | WACCES | Arrived onsite at 9:45 to repair lights in engine bay and hose room, replaced 6x fluro tubes at faulty engine bay fittings, all engine bay fluros now working, replaced faulty fluro fitting in hose room with new LED baton, both hose room lights now working, advised staff of works and left site at 12:15.
MSA-DTWD | WA6184698 | 1 | Lane's Plumbing | Paddock - Burst Water Pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2.5 | 2022-11-15 14:41 | 2022-11-16 17:00 | 2022-11-15 15:00 | 2022-11-16 17:00 | 2022-11-15 17:30 |  |  | Completed
MSA-DFES | WA6208247 | 3 | Go Doors | Fleet Stores - Faulty roller door - see notes below | Building | Doors | 2001.53 | Fail | Fail | 2 | 2 | 2.5 | 2022-11-17 14:59 | 2022-11-24 17:00 | 2022-12-06 14:00 | 2022-11-24 17:00 | 2022-12-06 16:30 |  |  | COMPLETED QUOTED WORKS.
MSA-DTAG | WA6229703 | 0 | Sapio Pty Ltd | Level 8 - room 816 - duress alarm not working | Security | Security Management System | 338.75 | Pass | Fail | 0 | 0 | 2.5 | 2022-11-18 10:29 | 2022-11-18 12:29 | 2022-11-18 12:00 | 2022-11-18 14:29 | 2022-11-18 14:30 |  |  | Attended site. Inspected Level 8, Room 816 duress button. Found to have low battery, replaced battery. Tested, duress button, alarms and restores. Job completed.
MSA-DFES | WA6253751 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Electrical Lighting Faults - See Notes | Electrical | Lighting, Internal | 651.93 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-22 11:47 | 2022-11-25 17:00 | 2022-11-23 10:30 | 2022-11-25 17:00 | 2022-11-23 13:00 |  |  | Joel Harvey (23/11/2022) - Work NoteOnsite to investigate dull lights in male/female toilets, main walkway & kitchen. Replaced all 840 tubes with 865 tubes to give off a brighter colour as requested. Changed 26x tubes and 4x starters in total. Notified staff on site and left at 13:00. (Had to use 840 globes in female disabled toilet as I ran out of tubes no one will notice though) have also told client to request another job for pole light as it will be over budget on a breakdown.
MSA-DFES | WA6256797 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | DO Perth under cover parking - Near engine room doors - Under cover security light does not work | Electrical | Lighting, External | 369.93 | Pass | Pass | -1 | -1 | 2.5 | 2022-11-24 09:04 | 2022-11-29 17:00 | 2022-11-24 15:00 | 2022-11-29 17:00 | 2022-11-24 17:30 |  |  | Onsite from previous job starting at 15:00 to investigate faulty light in DO carpark. Found that the LED fitting had gone faulty and was not working. Replaced with new light fitting and notified staff/DO of works performed and left site at 17:00.
MSA-DTWD | WA6293899 | 3 | Protek 24/7 Building & Maintenance | G Block - Room G34 - Cornice falling off ceiling and along wall damaged | Building | Internal Walls | 275.78 | Pass | Pass | -1 | -1 | 2.5 | 2022-11-30 10:58 | 2022-12-07 17:00 | 2022-12-02 11:00 | 2022-12-07 17:00 | 2022-12-02 13:30 |  |  | Refixed cornice trim
MSA-DTWD | WA6299911 | 2 | Lane's Plumbing | WC - Faulty leaking Pan | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | -1 | -1 | 2.5 | 2022-12-02 08:34 | 2022-12-07 17:00 | 2022-12-02 12:00 | 2022-12-07 17:00 | 2022-12-02 14:30 |  |  | Repairs to toilet
MSA-DTAG | WA6364209 | 1 | Elec Power Technologies | Ground Floor - UPS Failure is setting off alarms - Zone 58,59,108 failures | Electrical | UPS System Maintenance |  | Pass | Pass | 0 | 0 | 2.5 | 2022-12-12 10:15 | 2022-12-13 17:00 | 2022-12-12 12:00 | 2022-12-13 17:00 | 2022-12-12 14:30 |  |  | Repairs to UPS
MSA-DTWD | WA6381832 | 1 | Icon Logic Pty Ltd | air con BMS-Aircon is cooling some zones and not others | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 2.5 | 2022-12-19 15:02 | 2022-12-20 17:00 | 2022-12-20 11:00 | 2022-12-20 17:00 | 2022-12-20 13:30 |  |  | Completed
MSA-DTWD | WA6383630 | 2 | Lane's Plumbing | BLD 816 - Bathroom - Vanity basin steel auto plug faulty and drain blocked | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2.5 | 2022-12-20 11:56 | 2022-12-23 17:00 | 2022-12-21 11:00 | 2022-12-23 17:00 | 2022-12-21 13:30 |  |  | repairs to plug
MSA-DTWD | WA6393067 | 1 | Critical Fire Protection & Training | East-Fire alarm activated, fire brigade attended and isolated Zone 2-see notes | Fire Protection Services | Fire Protection - Monitor System | 493.53 | Pass | Pass | 0 | 0 | 2.5 | 2022-12-28 09:13 | 2022-12-29 17:00 | 2022-12-28 10:30 | 2022-12-29 17:00 | 2022-12-28 13:00 |  | WCAPPR | Upon arrival, it was found the fire panel had a fault - second floor west, zone 12, in ceiling.The fire brigade had isolated zone 12.Critical Fire have isolated the code red and all warning signals and bells while undertaking investigation.After looking throughout the roof space for a detector light on, it found in class A234.The faulty detector was removed and replaced with a new smoke detector and base.Once this was complete, the fire panel was reset and the fault had cleared.
MSA-DFES | WA6415088 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | External Area - Copper pipe that supplies water has been stolen - Water has been isolated | Plumbing & Drainage | Water | 376.23 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-11 12:30 | 2023-01-11 14:30 | 2023-01-11 13:15 | 2023-01-11 16:30 | 2023-01-11 15:45
MSA-DTWD | WA6415132 | 2 | AWB Co. | Creche Yard - Draw Bolt on metal gate broken | Building | Steel Fencing & Gates | 370.845 | Fail | Fail | 1 | 1 | 2.5 | 2023-01-11 13:06 | 2023-01-16 17:00 | 2023-01-20 09:00 | 2023-01-16 17:00 | 2023-01-20 11:30
MSA-DTWD | WA6450206 | 2 | M Construction (WA) | vinyl floor has trip hazards where joins are lifting | Flooring | Vinyl | 384.3 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-16 09:57 | 2023-01-19 17:00 | 2023-01-17 09:30 | 2023-01-19 17:00 | 2023-01-17 12:00
MSA-DTWD | WA6509536 | 2 | AWB Co. | Office lights not working and some very dim - please investigate | Electrical | Lighting, Internal | 607.39 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-20 11:53 | 2023-01-25 17:00 | 2023-01-24 12:00 | 2023-01-25 17:00 | 2023-01-24 14:30
MSA-DTAG | WA6516840 | 1 | Sapio Pty Ltd | After swiping card and entering number the door does not release | Security | Access Control | 434.66 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-23 16:01 | 2023-01-24 17:00 | 2023-01-24 09:30 | 2023-01-24 17:00 | 2023-01-24 12:00
MSA-DTWD | WA6521319 | 3 | AWB Co. | faulty GPO | Electrical | General Electrical | 571.62 | Pass | Pass | -1 | -1 | 2.5 | 2023-01-30 09:56 | 2023-02-06 17:00 | 2023-02-01 12:00 | 2023-02-06 17:00 | 2023-02-01 14:30
MSA-DTWD | WA6521496 | 2 | AWB Co. | 8 ceiling tiles to be replaced due to water damage - see notes | Building | Ceiling | 292.345 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-30 11:15 | 2023-02-02 17:00 | 2023-01-31 09:00 | 2023-02-02 17:00 | 2023-01-31 11:30
MSA-DTWD | WA6521504 | 2 | AWB Co. | Ceiling tiles stained - replace - Replacement ceiling tiles on site | Building | Ceiling | 303.345 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-30 11:19 | 2023-02-02 17:00 | 2023-01-31 06:30 | 2023-02-02 17:00 | 2023-01-31 09:00
MSA-DCA | WA6523238 | 2 | Protek 24/7 Building & Maintenance | Broken windows - Need boarding | Painting | Internal | 404.96 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-31 13:36 | 2023-02-03 17:00 | 2023-02-02 11:00 | 2023-02-03 17:00 | 2023-02-02 13:30
MSA-DTWD | WA6527331 | 2 | AWB Co. | E200 - Broken 3 phase socket and plug | Electrical | General Electrical | 731.62 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-01 16:16 | 2023-02-06 17:00 | 2023-02-06 14:15 | 2023-02-06 17:00 | 2023-02-06 16:45
MSA-DTWD | WA6528808 | 2 | AWB Co. | G Block Lecture Theatre - G02 - Lights flickering need tubes replaced | Electrical | Lighting, Internal | 290.005 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-02 12:36 | 2023-02-07 17:00 | 2023-02-07 12:30 | 2023-02-07 17:00 | 2023-02-07 15:00
MSA-DTWD | WA6531571 | 2 | WESTERN IRRIGATION PTY LTD | Station 17 Corner Museum and Francis-solenoid stuck open /master valve now turned off | Landscaping & Gardening | Grounds Maintenance | 1045.31 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-03 12:35 | 2023-02-08 17:00 | 2023-02-07 09:30 | 2023-02-08 17:00 | 2023-02-07 12:00
MSA-DTWD | WA6540173 | 2 | AWB Co. | Faulty ceiling lights | Electrical | Lighting, Internal | 441.08 | Pass | Pass | -1 | -1 | 2.5 | 2023-02-09 08:57 | 2023-02-14 17:00 | 2023-02-09 11:00 | 2023-02-14 17:00 | 2023-02-09 13:30
MSA-DTWD | WA6540300 | 2 | Techworks Electrical | Male toilets - 1 bulb blown and another flashing off and on. | Electrical | Lighting, Internal | 1035.23 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-09 09:56 | 2023-02-14 17:00 | 2023-02-13 09:00 | 2023-02-14 17:00 | 2023-02-13 11:30
MSA-DTWD | WA6560897 | 3 | AWB Co. | Outside B Block East fed from L Block - Fix faulty isolator switch | Electrical | Distribution Board | 441.08 | Pass | Pass | -1 | -1 | 2.5 | 2023-02-13 14:08 | 2023-02-20 17:00 | 2023-02-14 12:30 | 2023-02-20 17:00 | 2023-02-14 15:00
MSA-DTWD | WA6573233 | 1 | AWB Co. | Store room - Lights Faulty | Electrical | Lighting, Internal | 486.58 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-14 11:54 | 2023-02-15 17:00 | 2023-02-15 06:30 | 2023-02-15 17:00 | 2023-02-15 09:00
MSA-DCA | WA6578493 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chilled water pipe - Leaking | Air Conditioning | Room Air Conditioners | 335.315 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-15 09:41 | 2023-02-16 17:00 | 2023-02-15 10:30 | 2023-02-16 17:00 | 2023-02-15 13:00
MSA-DCA | WA6604042 | 2 | Techworks Electrical | WAYTCO studio - Three gang wall switch requires replacing - broken | Electrical | General Electrical | 537.07 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-17 15:11 | 2023-02-22 17:00 | 2023-02-22 11:00 | 2023-02-22 17:00 | 2023-02-22 13:30
MSA-DFES | WA6654849 | 0 | Australian HVAC Services Pty. Ltd. | Study room - Aircon - leaking | Air Conditioning | Building HVAC Maintenance (Major Plant) | 300.41 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-21 10:06 | 2023-02-21 12:06 | 2023-02-21 11:00 | 2023-02-21 14:06 | 2023-02-21 13:30
MSA-DTWD | WA6655855 | 2 | SPECIALISED TREE SERVICE | Dangerous tree in driveway | Landscaping & Gardening | Tree Lopping |  | Pass | Pass | 0 | 0 | 2.5 | 2023-02-21 10:32 | 2023-02-24 17:00 | 2023-02-22 13:30 | 2023-02-24 17:00 | 2023-02-22 16:00
MSA-DTWD | WA6668481 | 2 | Australian Airconditioning Services Pty Ltd | Leaking Wall Split AC | Air Conditioning | Ducted Split System | 588.35 | Pass | Pass | -1 | -1 | 2.5 | 2023-02-22 09:38 | 2023-02-27 17:00 | 2023-02-22 12:30 | 2023-02-27 17:00 | 2023-02-22 15:00
MSA-DTWD | WA6668658 | 2 | SPECIALISED TREE SERVICE | Road to Piggery along top Stable - Trees overhanging | Landscaping & Gardening | Tree Lopping |  | Pass | Pass | -1 | -1 | 2.5 | 2023-02-22 10:51 | 2023-02-27 17:00 | 2023-02-22 11:00 | 2023-02-27 17:00 | 2023-02-22 13:30
MSA-DFES | WA6669231 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main admin - Ground - Male toilet - Light cover broken and dull lights | Electrical | Lighting, Internal | 487.43 | Pass | Pass | -1 | -1 | 2.5 | 2023-02-22 15:53 | 2023-03-01 17:00 | 2023-02-23 12:45 | 2023-03-01 17:00 | 2023-02-23 15:15
MSA-DCA | WA6671419 | 0 | EQUANS Mechanical Services (WA) Pty Limited | chiller not running | Air Conditioning | Room Air Conditioners | 947.03 | Fail | Fail | 0 | 0 | 2.5 | 2023-02-23 07:40 | 2023-02-23 09:40 | 2023-02-23 14:00 | 2023-02-23 11:40 | 2023-02-23 16:30
MSA-DFES | WA6671810 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - Staff change room - Male Lockers - LED needs replacing-see notes | Electrical | Lighting, Internal | 647.805 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-23 10:49 | 2023-02-28 17:00 | 2023-02-27 09:00 | 2023-02-28 17:00 | 2023-02-27 11:30
MSA-DTWD | WA6674244 | 1 | AWB Co. | GPO - Bench 10 - Not working | Electrical | General Electrical | 441.08 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-27 09:01 | 2023-02-28 17:00 | 2023-02-27 10:30 | 2023-02-28 17:00 | 2023-02-27 13:00
MSA-DTWD | WA6674567 | 2 | AWB Co. | E111 Electrical work shop - 2x single phase GPO's faulty | Electrical | General Electrical | 500.88 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-27 10:45 | 2023-03-02 17:00 | 2023-02-28 09:45 | 2023-03-02 17:00 | 2023-02-28 12:15
MSA-DTWD | WA6681690 | 0 | COMMERCIAL PLUMBING AND GAS | Corridor - B150 - Drinking fountain leaking/flooding | Plumbing & Drainage | HWS/Units Electric & Gas | 949.24 | Pass | Pass | 0 | 0 | 2.5 | 2023-03-02 11:02 | 2023-03-02 13:02 | 2023-03-02 12:30 | 2023-03-02 15:02 | 2023-03-02 15:00
MSA-MRWA | WA6683971 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Warehouse / Venture Smart office - A/C in Warehouse office is not providing cold air | Air Conditioning | Ducted Split System |  | Fail | Fail | 0 | 0 | 2.5 | 2023-03-03 14:40 | 2023-03-13 17:00 | 2023-03-14 07:30 | 2023-03-13 17:00 | 2023-03-14 10:00
MSA-DTWD | WA6693745 | 3 | AWB Co. | Seat torn off wall in shower | Building | General Building | 284.095 | Pass | Pass | -1 | -1 | 2.5 | 2023-03-10 14:01 | 2023-03-17 17:00 | 2023-03-13 12:00 | 2023-03-17 17:00 | 2023-03-13 14:30
MSA-DTAG | WA4994983 | 2 | Sapio Pty Ltd | BB Hay St Fire (172.21.254.208) & BB Mezz Floor (172.21.254.196) cameras are offline. | Security | CCTV Surveillance | 300 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-10 09:24 | 2022-01-13 17:00 | 2022-01-10 13:00 | 2022-01-13 17:00 | 2022-01-10 15:30 |  |  | Found switch fault in Mezz Comms Riser due to electrical testing. Reset and restored 2 x cameras back on line.Job completed.
MSA-DFES | WA5001688 | 2 | Dom's Total Grounds Maintenance | 2 x branches fallen onto the ground | Landscaping & Gardening | Grounds Maintenance | 580 | Fail | Fail | 0 | 0 | 2.5 | 2022-01-11 15:00 | 2022-01-14 17:00 | 2022-01-17 07:00 | 2022-01-14 17:00 | 2022-01-17 09:30 |  |  | Tree Loppers to remove fallen branches
MSA-DTWD | WA5010052 | 2 | WESTERN IRRIGATION PTY LTD | P Block - Staff car park - Grounds - re - tic gear sprinkler has broke off in grass area | Plumbing & Drainage | Water | 464.78 | Pass | Pass | -1 | -1 | 2.5 | 2022-01-12 09:53 | 2022-01-17 17:00 | 2022-01-13 13:00 | 2022-01-17 17:00 | 2022-01-13 15:30 |  |  | Locate damage sprinkler, replace sprinkler, flush and test.
MSA-DTWD | WA5038513 | 1 | AWB Co. | Block 10 - Ground - North wing - Security lights wont turn off during day | Electrical | General Electrical | 349.99 | Pass | Pass | 0 | 0 | 2.5 | 2022-01-17 13:53 | 2022-01-18 17:00 | 2022-01-18 07:00 | 2022-01-18 17:00 | 2022-01-18 09:30 |  | WACCES | Attended site and signed in. Completed JSA. Located block 10 north lights staying on. Investigated switchboards to find feed. Found to controlled near toilets. Removed switchboard cover to access timer. Found to in reset mode. Unable to set times or clear screen. Timer faulty. Supply and replace with new timer. Rewired to suit new timer. Set times for on and off. Tested override and off function. Set timer to last increment and waited to ensure timer turning off. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5053093 | 3 | Total Security Systems Pty Ltd | PIR 22 B1 associate room constantly activating (possible warranty) | Security | Monitoring | 580 | Fail | Fail | 3 | 3 | 2.5 | 2022-01-18 13:03 | 2022-01-25 17:00 | 2022-02-15 10:00 | 2022-01-25 17:00 | 2022-02-15 12:30 |  |  | Check issue with PIR PIR faulting from vertical blinds movementApproval from Matt from TSS to relocate PIR to appropriate corner not looking directly at window to resolve issue.Not covered under warranty as not a fault of the sensor.PIR relocated and no longer getting alarms from blinds.
MSA-DTWD | WA5066828 | 1 | Lane's Plumbing | Hughes Hall - Downstairs - A wing bathrooms - Toilets blocked in A Wing bathrooms, possibly showers | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 2.5 | 2022-01-19 09:40 | 2022-01-20 17:00 | 2022-01-19 10:00 | 2022-01-20 17:00 | 2022-01-19 12:30 |  |  | CLEAR BLOCKAGE TO HUGHES HAL
MSA-DTWD | WA5081547 | 3 | Precise Air Group | Aircon isnt cooling | Air Conditioning | Room Air Conditioners | 413.4 | Pass | Pass | -1 | -1 | 2.5 | 2022-01-20 15:25 | 2022-01-28 17:00 | 2022-01-21 10:00 | 2022-01-28 17:00 | 2022-01-21 12:30 |  |  | Attended site gained access and signed in. Found reported location and noticed room was cool. 18 degrees at outlets. Went up and assessed all four package units none had any fault codes and all in cooling. Checked filters and mech equipment and all seem fine and working. Did find package unit down the same end of the floor was not switched on at controller. Will monitor area on future maintenance.
MSA-DTWD | WA5100308 | 2 | Protek 24/7 Building & Maintenance | North Entrance - Gate has come away from the brickwork - brick work has been repaired | Building | Steel Fencing & Gates | 489.92 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-02 12:25 | 2022-02-07 17:00 | 2022-02-04 10:00 | 2022-02-07 17:00 | 2022-02-04 12:30 |  |  | Make safe to gate that has come away from Brick Pillar
MSA-DTWD | WA5105834 | 3 | Falcetta Plumbing and Gas | Chilled water unit has no water pressure | Plumbing & Drainage | Water | 295.7 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-04 14:55 | 2022-02-11 17:00 | 2022-02-09 11:30 | 2022-02-11 17:00 | 2022-02-09 14:00 |  |  | repair drinking unit
MSA-DTWD | WA5109129 | 3 | AWB Co. | B Block - Levels 1, 2, 3 - Replace lights not working B Block Corridors | Electrical | General Electrical | 831.73 | Pass | Pass | -1 | -1 | 2.5 | 2022-02-09 07:25 | 2022-02-15 17:00 | 2022-02-10 13:00 | 2022-02-15 17:00 | 2022-02-10 15:30 |  |  | Attended site and signed in. Completed JSA. Inspected and checked out all lights throughout B block. Counted up all lamps out on all floors in corridors. Supply and replaced lamps and starters where needed. Tested all okay besides the eastern end of B block on level 2, where there is a electrical fault on light circuit referring to the DAS. Notified site. Signed out. Job complete
MSA-MRWA | WA5116359 | 3 | AWB Co. | Ground - Bridge compound - Replace gate control lockable switch | Electrical | General Electrical | 554.28 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-11 14:11 | 2022-02-18 17:00 | 2022-02-17 07:00 | 2022-02-18 17:00 | 2022-02-17 09:30 |  |  | Attended site and signed in. Completed JSA. Located gate on western side on site. Had to go through site to get to gate motor. Found isolator to spin round and round. Isolated and locked out feed to gate. Supply and replaced faulty isolator with new key switch isolator. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5126889 | 3 | AWB Co. | Level 3 - room A305 staff room - blown flurors | Electrical | Lighting, Internal | 422.5 | Pass | Pass | -1 | -1 | 2.5 | 2022-02-14 10:27 | 2022-02-21 17:00 | 2022-02-17 11:30 | 2022-02-21 17:00 | 2022-02-17 14:00 |  |  | Attended site signed in completed jsa. Contacted site fm about job location. Replaced various tubes on site level 3. 36w tubes used rest left on site in switchboard level 3**job completed**
MSA-DCA | WA5133796 | 2 | Earth & Water Pty Ltd | Garden Beds – Beaufort st end - 2 x broken sprinklers in garden bed zone 12, Beaufort st end | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2.5 | 2022-02-15 14:17 | 2022-02-18 17:00 | 2022-02-16 14:30 | 2022-02-18 17:00 | 2022-02-16 17:00 |  |  | job completed - Exposed broken sprinklers- Replaced sprinklers- Tested sprinklers- Left area tidy.
MSA-DTWD | WA5187099 | 2 | Techworks Electrical | Workshops - Ground -North end of workshops building exterior, water tank has a broken power box | Electrical | General Electrical | 578.07 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-22 10:52 | 2022-02-25 17:00 | 2022-02-23 13:00 | 2022-02-25 17:00 | 2022-02-23 15:30 |  |  | Replaced damaged weatherproof box with new weatherproof box and siliconed around
MSA-DTWD | WA5188825 | 3 | Equans Mechanical Services Australia | Condensation leaking on to floor from A/C 2 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 285.93 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-23 11:42 | 2022-03-02 17:00 | 2022-03-02 07:00 | 2022-03-02 17:00 | 2022-03-02 09:30 |  |  | UNBLOCK EVAPORATOR DRAINS AND 'P' TRAPS ON BOTH A/C UNITS. ACCESS PLANTROOM AND INSPECT, FOUND EVAPORATOR DRAINBLOCKED AGAIN. UNBLOCK DRAIN WITH DRY NITROGEN, TEST DRAIN OPERATION AND MONITOR FOR LEAKS FOR A PERIOD OF TIME, ALLOK AT THIS TIME.
MSA-DCA | WA5190051 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Main entrance foyer - Revolving doors repeatedly stops - see notes below | Building | Automatic Doors | 572.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-02-24 10:15 | 2022-02-25 17:00 | 2022-02-24 10:45 | 2022-02-25 17:00 | 2022-02-24 13:15
MSA-DCA | WA5199135 | 2 | FCT SURFACE CLEANING | Polly café & Beaufort street garden beds - Graffiti tags | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2.5 | 2022-03-01 07:58 | 2022-03-03 17:00 | 2022-03-01 10:00 | 2022-03-03 17:00 | 2022-03-01 12:30 |  |  | job completed - Attended site and removed graffiti from Polly Cafe and Beaufort Street garden beds.
MSA-DFES | WA5199770 | 1 | Australian HVAC Services Pty. Ltd. | Dorm 8 - air con is leaking | Air Conditioning | Room Air Conditioners | 363.89 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-01 11:37 | 2022-03-02 17:00 | 2022-03-01 13:00 | 2022-03-02 17:00 | 2022-03-01 15:30 |  |  | Unblocked condensate drain for Dorm 8 AC. Modified condensate drain to prevent further leaks
MSA-DTWD | WA5201425 | 2 | Techworks Plumbing | T block - C.L - Cafe - how water to cafe kitchen sink is not heating up - see notes | Plumbing & Drainage | Water | 269.83 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-02 14:47 | 2022-03-08 17:00 | 2022-03-03 07:00 | 2022-03-08 17:00 | 2022-03-03 09:30 |  |  | Attended sight tested hot water at cafe and fine, inspected plant room hwu to find everything in operating how it should the reset that Dennis did on the heat pumps the week before has rebooted the system and working fine again could not fault anything.
MSA-DTWD | WA5202907 | 2 | AWB Co. | U019 - Faulty GPO requires attention | Electrical | General Electrical | 500.53 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-03 09:17 | 2022-03-09 17:00 | 2022-03-08 08:30 | 2022-03-09 17:00 | 2022-03-08 11:00 |  |  | Attended site and signed in. Completed JSA. Rang cleaner so she could let us in building. Looked around room U019 for tagged out / faulty GPO. Couldn’t see one. Rang Silvio to clarify what was needing to be done. Gpo and stop button begging gyprock needed to be moved and disconnected ,went to wholesaler to pickup parts, Took off PowerPoint cover. Ran cable to other side of mock kitchens. Ran conduit and mounted gpo on wall, removed stop button , joined cables together and put stop button back on wall with out of service tag as discussed with Silvio , tested gpo and working as intended , completed paperwork, signed out Job completed
MSA-DTWD | WA5203378 | 2 | Precise Air Group | E block North wing - Evap units dump valves not operating on North wing | Air Conditioning | Evaporative Coolers | 413.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-03 12:25 | 2022-03-09 17:00 | 2022-03-08 10:00 | 2022-03-09 17:00 | 2022-03-08 12:30 |  |  | Attended site and completed pre start paperwork and signed in. Completed working at heights permit. Acessed roof of e block and inspected evap float vlaves/ drains. Adjusted float valves as some units over filling. Adjusted pads as some water running off retainers and on to roof. Set bleed off's and monitored units. Found excess water run off to have improved. Left systems operating all ok.
MSA-DTWD | WA5204845 | 3 | AWB Co. | A block - Level 2 - A229 - Door is sticking and is hard to close | Building | General Building | 457.5 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-04 14:08 | 2022-03-14 17:00 | 2022-03-10 13:00 | 2022-03-14 17:00 | 2022-03-10 15:30 |  |  | Attended site and fixed tightly bound double door. Planed down door edge and re attached hinges to be re hung
MSA-DTWD | WA5207508 | 3 | AWB Co. | C block - C47 - flickering fluoro Midland Hairdressing | Electrical | General Electrical | 269.5 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-08 13:33 | 2022-03-15 17:00 | 2022-03-11 07:00 | 2022-03-15 17:00 | 2022-03-11 09:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, replaced tubes and starters that were flickering, re tubed complete salon area so all salons have 865 tubes, put all tubes in allocated disposal boxes , tested all lights and working as intended , took photos , turned all lights off, locked up area, completed paperwork , packed up (all tubes and starters supplied by site)Job completed
MSA-DTWD | WA5215536 | 3 | AWB Co. | Client Services - S106 - Reinstall three pin boards in Client Services that are loose on wall S106 | Building | Internal Walls | 286.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-10 13:16 | 2022-03-17 17:00 | 2022-03-16 08:30 | 2022-03-17 17:00 | 2022-03-16 11:00 |  |  | secured pin boards to walls
MSA-DTWD | WA5231332 | 1 | Precise Air Group | Kendrew- E-Block E-Vap continuously dumping water | Air Conditioning | Room Air Conditioners | 433.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-15 10:36 | 2022-03-16 17:00 | 2022-03-15 13:00 | 2022-03-16 17:00 | 2022-03-15 15:30 |  |  | Attended site and completed pre start paperwork and signed in. Acessed unit on roof and inspected unit. With reports of system continually dumping water. Found water supply pipe to be split causing unit to over flow. Went to suppliers and collected new hose. Returned to site and fitted. Test ran system and left unit operating all OK. No further works required.
MSA-DTWD | WA5239646 | 1 | M Construction (WA) | C-Block - paving steps leading to staff car park have come loose causing a trip hazard | Building | General Building | 379.38 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-16 13:46 | 2022-03-17 17:00 | 2022-03-17 07:00 | 2022-03-17 17:00 | 2022-03-17 09:30 |  |  | Repair Loose Paver
MSA-DTWD | WA5251977 | 2 | AWB Co. | Block P - G13 (P13) - Playgroup room - lights not working | Electrical | General Electrical | 480.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-17 08:29 | 2022-03-22 17:00 | 2022-03-21 07:00 | 2022-03-22 17:00 | 2022-03-21 09:30 |  |  | Attended site and signed in, completed jsa, located lighting in playgroup area, grabbed tubes from h block , replaced tubes and starters, went to whole saler and picked up parts, retuned to site and fit led batten. put old tubes in disposal boxes , replaced 1x light with led batten , Cleaned up m packed up, completed paperwork (all tubes and starters supplied by site)Job complete
MSA-DTWD | WA5257513 | 1 | Equans Mechanical Services Australia | First Floor Classrooms - Strong electrical smell coming from air cons (splits) in classrooms | Air Conditioning | Room Air Conditioners | 245.93 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-17 12:49 | 2022-03-18 17:00 | 2022-03-18 08:30 | 2022-03-18 17:00 | 2022-03-18 11:00 |  |  | MOTOR DRWAING EXCESSIVE AMPS - NEED QUOTING
MSA-DCA | WA5258179 | 2 | Techworks Plumbing | Hackett Hall - Ground Level - Cleaners Room - see notes below | Plumbing & Drainage | Water | 174.34 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-17 16:22 | 2022-03-22 17:00 | 2022-03-22 07:00 | 2022-03-22 17:00 | 2022-03-22 09:30 |  |  | Attended site for leaking hot tap. On arrival the hot water had been isolated but the hot tap was turn on full and stuck in that location. I managed to get the spindle operational then removed it and checked the washer. The rubber seat on the washer had torn allowing the tap to run constantly. I removed and serviced the spindle then replaced with a new tap washer. Turned the power and water back on the the hot water unit and tested
MSA-DCA | WA5287708 | 3 | Techworks Electrical | Main building - Ground - BOH Stage - see details below | Electrical | General Electrical | 277.14 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-22 14:44 | 2022-03-29 17:00 | 2022-03-25 07:00 | 2022-03-29 17:00 | 2022-03-25 09:30 |  |  | Replaced faulty Arcitrave switch. All working well.
MSA-DTWD | WA5290937 | 2 | Techworks Electrical | aircon function switch cover is broken and fallen off | Electrical | General Electrical | 333.39 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-25 12:50 | 2022-03-30 17:00 | 2022-03-30 13:00 | 2022-03-30 17:00 | 2022-03-30 15:30 |  |  | Replaced switch plate cover
MSA-DTWD | WA5294128 | 2 | AWB Co. | T block plant room - L3 - Stair well lights not working on level 3 on sensor when exiting via stair | Electrical | Lighting, Internal | 485 | Pass | Pass | 0 | 0 | 2.5 | 2022-03-28 13:10 | 2022-03-31 17:00 | 2022-03-30 08:30 | 2022-03-31 17:00 | 2022-03-30 11:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works. Located lights not working. Investigated sensor. Found to be no power. Went to board n removed escutcheon. Found to be fed from W1. Traced cables n tested all contacts. All working correctly. Reset power. Power now reinstated to sensor. Lights still not working. Found to be globes faulty. Supplied and replaced 4x pl-t lamps. Tested all for correct operation. **job complete**
MSA-DTWD | WA5296283 | 2 | AWB Co. | Workshops - Classroom 4 - has a water leak down wall below windows | Building | General Building | 474 | Pass | Pass | -1 | -1 | 2.5 | 2022-03-30 10:58 | 2022-04-04 17:00 | 2022-03-30 13:00 | 2022-04-04 17:00 | 2022-03-30 15:30 |  |  | Attended site. Inspected leak to classroom 4. Gained access to roof. Upon inspection found multiple splits on barge flashing and worn rubber seals on screws. Sealed to make water tight. Job complete
MSA-DTWD | WA5301463 | 3 | AWB Co. | Gardening Store - Replace broken light on wall of Gardening Store North Block | Electrical | Lighting, Internal | 573.52 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-01 09:14 | 2022-04-08 17:00 | 2022-04-05 07:00 | 2022-04-08 17:00 | 2022-04-05 09:30 |  |  | Attended site signed in completed jsa. Spoke with site about job with broken light. Found broken light due to vandalism and old PE cell. Replaced light with new weatherproof fitting and also replaced PE cell as instructed. All tested ok *** job completed ***
MSA-DTWD | WA5304144 | 2 | Techworks Electrical | Workshops carpentry - Mortice machine rotating the wrong way | Equipment | Power Tools | 481.43 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-04 15:09 | 2022-04-07 17:00 | 2022-04-07 10:00 | 2022-04-07 17:00 | 2022-04-07 12:30 |  |  | Drill press Motor starting capacitor giving high reading causing auxiliary winding to burn out and trip circuit.
MSA-DTWD | WA5383462 | 3 | Equans Mechanical Services Australia | Level 1 - B150 -Air conditioner copper drain pipe vandalised street side | Air Conditioning | Room Air Conditioners | 293.14 | Pass | Pass | -1 | -1 | 2.5 | 2022-04-27 15:31 | 2022-05-04 17:00 | 2022-04-28 11:30 | 2022-05-04 17:00 | 2022-04-28 14:00 |  |  | Found the drain hose on the out side wall had been twisted so it could be removed. Re-run the drain in pvc and secured to the wall with saddles.
MSA-DTWD | WA5384332 | 2 | Techworks Electrical | P-Block room P109 has a flickering light | Electrical | Lighting, Internal | 587.87 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-28 12:00 | 2022-05-03 17:00 | 2022-05-03 07:00 | 2022-05-03 17:00 | 2022-05-03 09:30 |  |  | Replaced flickering fluro tubes in P and Q block at McCarty campus
MSA-DTWD | WA5385572 | 2 | AWB Co. | Lights constantly tripping | Electrical | Lighting, Internal | 269.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-29 10:52 | 2022-05-04 17:00 | 2022-05-04 07:00 | 2022-05-04 17:00 | 2022-05-04 09:30 |  |  | Attended site and signed in, completed jsa, called cleaner to open o block ,spoke with fm about job,located lighting, removed tubes fitting by fitting and re energised circuit, determined which light was causing circuit to trip, replaced ballast, re tubes all fittings, re energised circuit and all lights working as intended, completed paperwork,packed up, signed out , ** job completed **
MSA-DTWD | WA5386063 | 2 | WA BOILER SPARES & SERVICE | Block 9 - Not heating back work area – (it doesn’t have a number) Suspected boiler fault | Mechanical Services | Boilers | 548 | Pass | Pass | 0 | 0 | 2.5 | 2022-04-29 15:21 | 2022-05-04 17:00 | 2022-05-02 08:30 | 2022-05-04 17:00 | 2022-05-02 11:00 |  |  | Replaced faulty temperature controller on gas hot water boiler
MSA-DTWD | WA5390491 | 1 | AHS Services WA Pty Ltd (Anchor) | V-Block - water rising up through floor waste drain in Kitchen area | Plumbing & Drainage | Drainage | 472.285 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-02 13:13 | 2022-05-03 17:00 | 2022-05-03 10:00 | 2022-05-03 17:00 | 2022-05-03 12:30 |  |  | Use drain acid to clear blockage to kitchen floor waste line. Tested on completion
MSA-DCA | WA5392828 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis Street building - Level 2 - Plant room 7 - Humidifier to handling unit 6.01 is faulty | Air Conditioning | Materials | 293.025 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-03 12:58 | 2022-05-04 17:00 | 2022-05-03 13:00 | 2022-05-04 17:00 | 2022-05-03 15:30 |  |  | Attended site, signed in and accessed plant room 7 and checked humidifier 6.01. Found the unit with little to no water pressure. Cleared humidifier fault and isolated unit. Traced mains supply water back and discovered the carbon sediment filter blocked. Drove to supplier to collect new filter, returned to site, fitted filter and checked the humidifier for correct operation. Ordered Spares carbon filters and left on site.
MSA-DFES | WA5395224 | 3 | AWB Co. | Sim Centre - Ground - Communications Centre - Door has broken Air grill | Building | Doors | 288.04 | Pass | Pass | -1 | -1 | 2.5 | 2022-05-05 11:29 | 2022-05-12 17:00 | 2022-05-05 13:00 | 2022-05-12 17:00 | 2022-05-05 15:30 |  |  | Adjusted door grill and screwed in to place
MSA-DFES | WA5395254 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | SimCentre - Ground -Communication Centre - RCD on GPO tripped | Electrical | General Electrical | 704.355 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-05 11:26 | 2022-05-06 17:00 | 2022-05-06 13:45 | 2022-05-06 17:00 | 2022-05-06 16:15 |  |  | Picked up RCDGPOs from mm electrical at 1345 in Northbridge as this was closest wholesaler. Attended site and replaced 2 DGPO to RCDGPO and tested. Installed 2 fixings to cable duct to secure lid to duct. Demonstrated to Carlos The operation of RCDs and notified of work outcome. Signed out and left site at 1615
MSA-DCA | WA5413216 | 1 | SCAVENGER SUPPLIES PTY LTD | Old Gaol - Level 1 - Old CO’s office - Broken Smoke Detector -hanging from ceiling - See notes | Fire Protection Services | Smoke and Heat Detection | 287.65 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-12 09:41 | 2022-05-13 17:00 | 2022-05-12 13:00 | 2022-05-13 17:00 | 2022-05-12 15:30 |  |  | COMPLETED 12/5/22** NOTE: AS PROMAP WAS OFFLINE & WE HAD NO ACCESS 13/5/22 CLAIM WAS UNABLE TO BE LODGED. A REQUEST WAS SENT FOR RCT WORK ORDERS TO BE EXTENDED.
MSA-DTWD | WA5438026 | 2 | Protek 24/7 Building & Maintenance | Ground Level - Room D1 - Entry door to room sagging - unable to lock and close properly | Building | Doors | 256.33 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-16 12:10 | 2022-05-19 17:00 | 2022-05-19 08:30 | 2022-05-19 17:00 | 2022-05-19 11:00 |  |  | Repair sagging door
MSA-DTWD | WA5462500 | 3 | AWB Co. | Level 3 - Corridor - power to corridor GPOS not working | Electrical | General Electrical | 270.4 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-19 15:40 | 2022-05-26 17:00 | 2022-05-24 07:00 | 2022-05-26 17:00 | 2022-05-24 09:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located rcd for circuit , rcd wouldn’t reset, walked around and located all GPOs on circuit, found water fountain was the only thing plugged in , unplugged it and reset rcd, tested water fountain and found it was faulty, called fm and discussed options, he said to close job off and he would get contractor that services the water fountains to rectify, completed paperwork, placed out of service tag on water fountain , signed out ***job completed**
MSA-DTWD | WA5462513 | 2 | AWB Co. | Ground Level - Walkway lights - All undercover walkway lights out between O and N block | Electrical | Lighting, External | 296.56 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-19 15:48 | 2022-05-24 17:00 | 2022-05-24 11:30 | 2022-05-24 17:00 | 2022-05-24 14:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located lighting,called security to disarm o block, turned on override and tested lighting, found that all the tubes needed replacing, replaced tubes, found that security override only turned on 1 light out of the 4, called fm and asked if he wanted all lights to come on with the override, he did, re wired other lights into override, tested lights and all working as intended, reset override and adjusted timer to suit night time hours , completed paperwork, packed up, signed out***job completed***
MSA-DTAG | WA5462543 | 1 | Midolo Building Services | 2nd Magistrates Office - Dry carpet due to water leakage - Very smelly | Flooring | Carpet | 630 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-19 16:18 | 2022-05-20 17:00 | 2022-05-20 11:30 | 2022-05-20 17:00 | 2022-05-20 14:00 |  |  | CARPET CLEANED & DRIED
MSA-DTWD | WA5472458 | 2 | Precise Air Group | A Block Boiler trips out every day on high temp | Mechanical Services | Boilers | 282.575 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-24 07:54 | 2022-05-26 17:00 | 2022-05-25 11:30 | 2022-05-26 17:00 | 2022-05-25 14:00 |  |  | Attended site and completed pre start paperwork and signed in. Accessed bms and inspected boiler operation on a block. Found all heating valves to be 100% with heating call enabled. Accessed boiler on roof plant room. Found out on high temp cut off. Reset boiler, Checked water flow and found all ok. Found boiler to start and run. Monitored for a little while. Boiler looked to be operating all ok, eventually temp went up and kept climbing. Opened bypass valve manually and found temp to stabilise. Checked bypass valve operation on bms and found it to be manually closed. Put back to auto and monitored boiler operation. While on site checked operation of b block boiler as all valves were at 100% but no heating. Accessed b block boiler and found burner off and boiler not operating. Reset boiler a couple of times and eventually boiler lit and ran up. Monitored boilers for the remainder of visit. Fm to monitor if issues with b block boiler continue boiler tech required.
MSA-DTWD | WA5476101 | 1 | AWB Co. | A 250 - Lights in the lecture theartre are not working | Electrical | General Electrical | 383.615 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-25 10:33 | 2022-05-26 17:00 | 2022-05-26 14:30 | 2022-05-26 17:00 | 2022-05-26 17:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,went to lecture theatre and fo7nd tha5 only lights on were downlights on side walls of lecture theatre, opened control board and found no 240v to lights, closed up box and investigated at dB, found blown fuses to lighting circuit, tested cable and cables passed, left site to pick up fuses from workshop, returned to site and replaced fuses, completed paperwork, packed up,signed out **job complete**
MSA-DTAG | WA5478946 | 1 | SONTEC WA PTY LTD | Custody Centre - Duress alarm noise is broken in custody center | Security | Monitoring | 470 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-26 15:35 | 2022-05-27 17:00 | 2022-05-27 07:45 | 2022-05-27 17:00 | 2022-05-27 10:15 |  |  | 27/5/22 - Dean SimpsonTested buzzer and traced cables.Reterminated cable and tested.All working correctly.
MSA-DCA | WA5479710 | 2 | Techworks Electrical | DSATM - emergency exit sign DSATM was not illuminated | Electrical | General Electrical | 473.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-27 11:10 | 2022-06-01 17:00 | 2022-05-30 13:00 | 2022-06-01 17:00 | 2022-05-30 15:30 |  |  | Inspected exit light, found to be missing the blade with running man. Sourced new exit light and replaced for new
MSA-DTWD | WA5481665 | 2 | Falcetta Plumbing and Gas | Creche Childrens bathroom - Floor waste blocked | Plumbing & Drainage | Drainage | 274.015 | Pass | Pass | 0 | 0 | 2.5 | 2022-05-30 15:47 | 2022-06-02 17:00 | 2022-06-01 16:00 | 2022-06-02 17:00 | 2022-06-01 18:30 |  | WACCES | unblocked dry wastes at rear
MSA-DTWD | WA5486732 | 1 | AWB Co. | Room E54 - 3 Phase plug not working in Welding Bay Sheet metal workshop - see notes below | Electrical | General Electrical | 411.07 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-01 09:56 | 2022-06-02 17:00 | 2022-06-01 12:15 | 2022-06-02 17:00 | 2022-06-01 14:45 |  |  | Attended site and signed in. Completed JSA. Located E500 and spoke to staff regarding which welding bay was faulty. Bay 11. Found tagged out. Investigated and tested to find no blue phase. Plugged welder in and tested the load and didn’t rattle when I was on site but didn’t correctly work. Supply and replace 3 phase outlet. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5496269 | 2 | M Construction (WA) | C014 - two large boards needs re-fixing to the wall | Building | General Building | 275 | Pass | Pass | -1 | -1 | 2.5 | 2022-06-09 08:48 | 2022-06-14 17:00 | 2022-06-10 07:00 | 2022-06-14 17:00 | 2022-06-10 09:30 |  |  | Installed 2 Large picture frames on wall in C014 utilsing studs as fixings.
MSA-DFES | WA5496342 | 2 | Protek 24/7 Building & Maintenance | Level 2 - Spray Painter Bay - Roof leaks from Chimney | Roofing | Metal Roofing | 456.3 | Fail | Fail | 0 | 0 | 2.5 | 2022-06-09 09:21 | 2022-06-14 17:00 | 2022-06-15 07:00 | 2022-06-14 17:00 | 2022-06-15 09:30 |  |  | Repair roof leaks to chimney in Spray painter Bay
MSA-DTWD | WA5521263 | 3 | WESTERN IRRIGATION PTY LTD | Nursery-Shade Shed -One of the solenoids feeding shade cloth shed is stuck and water wont turn off | Equipment | Electrical Equipment | 467.76 | Pass | Pass | -1 | -1 | 2.5 | 2022-06-15 10:24 | 2022-06-22 17:00 | 2022-06-17 07:00 | 2022-06-22 17:00 | 2022-06-17 09:30 |  |  | Locate and repair faulty solenoid valve, test for correct operation.
MSA-DTWD | WA5549224 | 3 | AWB Co. | : Re install easel brackets following wall repairs in room B305 | Building | General Building | 281.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-17 14:52 | 2022-06-24 17:00 | 2022-06-21 13:00 | 2022-06-24 17:00 | 2022-06-21 15:30 |  |  | Install 2 x easel brackets to wall in classroom B305
MSA-DCA | WA5574113 | 1 | Techworks Electrical | First Floor - Main Auditorium - Issus with ramp lights and exterior lights cutting out - See notes | Electrical | Lighting, External | 398.91 | Pass | Pass | 0 | 0 | 2.5 | 2022-06-30 15:00 | 2022-07-01 17:00 | 2022-07-01 08:30 | 2022-07-01 17:00 | 2022-07-01 11:00 |  |  | Inspected lights tripping. Turned circuit back on and circuit stayed on. Was informed that all the exterior lighting had been replaced recently as well as the exterior floods but was informed that the lights tripped at around 5-6pm which is when the sun goes down so i suspected it was a pe cell and security light issue. I inspected exterior floods, i found that the PE cell was cracked and the conduit work was very poor. I have replaced the pe cell and i have put small drainage holes in the inspection boxes as a temporary fix to prevent any water build up. Re-glued corrugated conduit into inspection box which was hanging out when i arrived. I recommend replacing the conduit and refixing the lights as it has been done very poorly to prevent further water electrical faults
MSA-DTAG | WA5578222 | 1 | Seme Solutions Pty Ltd | Adult Corrections duress activated and key now stuck upon reset attempt - See notes | Security | Security Management System | 363.37 | Fail | Fail | 0 | 0 | 2.5 | 2022-07-01 09:51 | 2022-07-04 17:00 | 2022-07-07 10:00 | 2022-07-04 17:00 | 2022-07-07 12:30 |  |  | Attended site to replace the faulty duress button. Tested all ok after replacement. PA2ESR X 1.
MSA-DTWD | WA5585057 | 2 | AWB Co. | Water Leaking through the roof | Roofing | Metal Roofing | 457.5 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-05 12:20 | 2022-07-08 17:00 | 2022-07-06 07:00 | 2022-07-08 17:00 | 2022-07-06 09:30 |  |  | Investigated area of leak, stripped section of tiled roof found broken tile replaced with tile on site
MSA-DTWD | WA5603965 | 3 | AWB Co. | Replace Exit light not working C102 | Electrical | Emergency & Exit Lighting | 386.255 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-12 14:35 | 2022-07-19 17:00 | 2022-07-18 07:00 | 2022-07-19 17:00 | 2022-07-18 09:30 |  |  | Attended site and signed in. Completed JSA. Located faulty exit due to water ingress from the weather. Supply and replace exit and relocated to off the brick wall and Mounted to the bean of the roof. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5609632 | 2 | Midolo Building Services | Level 1 - LINKS office/Child Protection office -Noticeboards (3) and brochure holders to be secured | Building | General Building | 309.52 | Fail | Fail | 0 | 0 | 2.5 | 2022-07-13 15:26 | 2022-07-18 17:00 | 2022-07-20 07:00 | 2022-07-18 17:00 | 2022-07-20 09:30 |  |  | all items secured
MSA-DTWD | WA5611919 | 2 | AWB Co. | North East Corner - External - blocked down pipe | Roofing | Metal Roofing | 511.02 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-14 10:30 | 2022-07-19 17:00 | 2022-07-19 07:00 | 2022-07-19 17:00 | 2022-07-19 09:30 |  |  | Accessed roof to find blocked box gutter. Cleared blockage and debris from box gutter to stop overflow of gutter
MSA-DTWD | WA5656587 | 2 | Falcetta Plumbing and Gas | Rinnai 200I Domestic gas HW not running | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2.5 | 2022-07-18 15:06 | 2022-07-21 17:00 | 2022-07-20 13:00 | 2022-07-21 17:00 | 2022-07-20 15:30 |  | WACCES | unit isolated due to other works, will discuss rectification with campus
MSA-DTWD | WA5672880 | 2 | Techworks Electrical | Faulty lighting | Electrical | Lighting, Internal | 796.67 | Pass | Pass | -1 | -1 | 2.5 | 2022-07-20 09:56 | 2022-07-25 17:00 | 2022-07-20 10:00 | 2022-07-25 17:00 | 2022-07-20 12:30 |  |  | Replaced tubes and starters in D block library, C block level 1 and replaced Em light fitting in A block staircase
MSA-DTWD | WA5680697 | 3 | AWB Co. | N108 Repair and reinstall damaged Brochure Holders above Beds | Building | Internal Walls | 270.345 | Pass | Pass | 0 | 0 | 2.5 | 2022-07-27 14:47 | 2022-08-03 17:00 | 2022-08-01 07:00 | 2022-08-03 17:00 | 2022-08-01 09:30 |  |  | Removed 9 x brochure holders from existing place and re installed new location
MSA-DTWD | WA5687924 | 1 | CLEVELAND COMPRESSED AIR SERVICES | Compressor enclosure, rear G Block - Faulty scavenger line & Unloader valve - See notes below | Equipment | Compressors, Generators | 736.25 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-02 08:25 | 2022-08-03 17:00 | 2022-08-03 08:30 | 2022-08-03 17:00 | 2022-08-03 11:00 |  |  | As another company completed the last service, we do not have the service records are are not able to advise if the part was replaced in the last service
MSA-DTWD | WA5688194 | 3 | GRAFFITI FORCE PTY LTD | Ground Floor - Lipfirt St - Tagging on wall next to gas meter Lipfirt St | Cleaning | Graffiti | 555 | Pass | Pass | -1 | -1 | 2.5 | 2022-08-02 10:29 | 2022-08-09 17:00 | 2022-08-03 13:00 | 2022-08-09 17:00 | 2022-08-03 15:30 |  |  | REMOVAL OF GRAFFITI FROM WALLS NEAR GAS METER ON LIPFRIT STREET
MSA-DTAG | WA5692554 | 1 | Seme Solutions Pty Ltd | Public door for courtroom one does not function correctly-see notes | Security | Security Management System | 2243.76 | Fail | Fail | 0 | 0 | 2.5 | 2022-08-03 14:26 | 2022-08-04 17:00 | 2022-08-05 10:00 | 2022-08-04 17:00 | 2022-08-05 12:30 |  |  | Attended site checked and found Courtroom 1 public entry REX button faulty. Replaced the REX button and tested it ok. Also relocated the Meeting room 6 under desk duress button as customer requested. Tested ok after work. SECURITY PRODUCT X2-EXIT-002 X 1.
MSA-DCA | WA5693125 | 3 | FCT SURFACE CLEANING | Exterior of AGWA - Graffiti needing removal - See notes below | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 2.5 | 2022-08-04 09:41 | 2022-08-11 17:00 | 2022-08-04 10:00 | 2022-08-11 17:00 | 2022-08-04 12:30 |  |  | Removed graffiti from the following areas:- entrance to AGWA carpark- window sill along Beaufort Street Centenary building- bollard as you come into the AGWA carpark- AGWA carpark gate
MSA-DTWD | WA5693278 | 1 | Lane's Plumbing | Horse stable road toward piggery - Burst water pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2.5 | 2022-08-04 10:59 | 2022-08-05 17:00 | 2022-08-04 11:30 | 2022-08-05 17:00 | 2022-08-04 14:00 |  |  | repairs to pipe
MSA-DTWD | WA5698156 | 2 | Protek 24/7 Building & Maintenance | 3B Auto Workshop - Water leak over Valve Grinding machines | Building | Ceiling | 456.32 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-09 15:06 | 2022-08-12 17:00 | 2022-08-10 08:30 | 2022-08-12 17:00 | 2022-08-10 11:00 |  |  | Sealed up bottom of gutter to stop water entry
MSA-DTWD | WA5706014 | 2 | AWB Co. | A230 - replace/repair light tubes not working | Electrical | Lighting, Internal | 733.205 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-11 08:00 | 2022-08-16 17:00 | 2022-08-16 14:30 | 2022-08-16 17:00 | 2022-08-16 17:00 |  |  | Job complete
MSA-DTWD | WA5734657 | 2 | AWB Co. | U022.4 - machine room - 4x roof leaks - 1 above D630 machine, 1 entry door, 1 above roblan Z500 saw | Building | Ceiling | 530.77 | Pass | Pass | 0 | 0 | 2.5 | 2022-08-16 08:40 | 2022-08-19 17:00 | 2022-08-17 10:45 | 2022-08-19 17:00 | 2022-08-17 13:15 |  |  | Investigated 4 x roof leaks.found small rust holes in ends of sheets.found flashing around anchor with perished silicone.found large louvred vent with perished silicone.foundrubber gasket repair thats possibly allowing water to enter.carried out all repairs
MSA-DTWD | WA5761794 | 2 | AWB Co. | Lights out in classroom including emergency exit | Electrical | Lighting, Internal | 1016.17 | Fail | Fail | 2 | 2 | 2.5 | 2022-08-18 11:50 | 2022-08-23 17:00 | 2022-09-09 07:00 | 2022-08-23 17:00 | 2022-09-09 09:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located room 3E13. Set up work area. Isolated power. Went through and replaced all old lights with new LED panels. Also replaced 1x exit sign with new. Energised circuit. Tested for correct operation. Packed and cleaned up site. Disposed of rubbish correctly. Notified relevant personnel of works completed. **job complete**
MSA-DCA | WA5793942 | 0 | TK Elevator Australia Pty Ltd | Lift 1 - Someone is stuck in the lift | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.5 | 2022-08-24 11:12 | 2022-08-24 13:12 | 2022-08-24 11:30 | 2022-08-24 15:12 | 2022-08-24 14:00 |  |  | Lift1 PICA-Elevator > MRL > Gearless :Lift through bottom limit. Moved the lift up on recall to enable the passenger in a mobility chair to exit the lift.Work order to be closed out at $0 cost
MSA-DTAG | WA5829022 | 0 | Schindler Lifts Australia | Lift 9 -someone is stuck in the lift | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.5 | 2022-09-02 09:52 | 2022-09-02 11:52 | 2022-09-02 10:00 | 2022-09-02 13:52 | 2022-09-02 12:30 |  |  | Roller crumbled causing it to jam Replaced car door roller and tested lift
MSA-DTWD | WA5832156 | 2 | BOC | Gas leak from oxygen manifold on gas retic system for G Block | Plumbing & Drainage | Gas | 500 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-05 11:26 | 2022-09-08 17:00 | 2022-09-05 13:00 | 2022-09-08 17:00 | 2022-09-05 15:30 |  |  | Attended site and inspected manifold, found small crack in brass fitting on manifold outlet.Replaced brass fitting, repressurised system, performed a leak check and found that the fault has been rectified. No further action required.
MSA-DFES | WA5832559 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Engine Bays - Multiple charger cable pulleys not working - See notes below | Electrical | General Electrical | 294.93 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-05 13:55 | 2022-09-12 17:00 | 2022-09-09 07:00 | 2022-09-12 17:00 | 2022-09-09 09:30 |  |  | Arrived on site at 0700 to investigate Ground Floor - Engine Bays - Multiple charger cable pulleys not working. Assessed all Pulley systems and discovered no equipment electrical related. Awaited relevant staff to arrive on site to follow up more detail of fault reported. Staff were unaware of fault being irrelevant to any electrical work. Staff requested to sign off job. Left site at 0930.
MSA-DTWD | WA5832582 | 2 | JEM Carpentry | Back door roof leak - faulty roof tiles | Roofing | Tiled Roofing |  | Fail | Fail | 1 | 1 | 2.5 | 2022-09-05 14:08 | 2022-09-08 17:00 | 2022-09-14 13:00 | 2022-09-08 17:00 | 2022-09-14 15:30 |  |  | Repairs
MSA-DTWD | WA5835984 | 2 | Techworks Electrical | L1 Library-3 round lights towards the back not working | Electrical | Lighting, Internal | 714.375 | Pass | Pass | -1 | -1 | 2.5 | 2022-09-07 09:31 | 2022-09-12 17:00 | 2022-09-08 11:30 | 2022-09-12 17:00 | 2022-09-08 14:00 |  |  | Replaced lamps
MSA-DTAG | WA5836092 | 1 | Schindler Lifts Australia | Level 2 - Lift 3 - Lift is missing floors and doors are are intermittently closing and opening | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.5 | 2022-09-07 10:03 | 2022-09-08 17:00 | 2022-09-07 13:00 | 2022-09-08 17:00 | 2022-09-07 15:30 |  |  | Lift ROA with Error 149 and 10 in error log. Found LHS skate loose and front car door roller deteriorating. Levelled/ tightenedskate and replaced car door roller. Tested lift and returned to service.
MSA-DTWD | WA5839727 | 2 | AWB Co. | lights tripping | Electrical | Lighting, Internal | 427.18 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-09 15:21 | 2022-09-14 17:00 | 2022-09-13 11:30 | 2022-09-14 17:00 | 2022-09-13 14:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Located faulty/tripping lighting. Dave said it hadn’t done it for a while. Suspected that there could have been water in a fitting. Replaced all tubes and starters in fittings that required it. Replaced faulty switch in classroom also. All working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5841273 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire curtain has dropped, needs to be attended to urgently | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 403.925 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-10 19:59 | 2022-09-10 21:59 | 2022-09-10 20:30 | 2022-09-10 23:59 | 2022-09-10 23:00 |  |  | Arrived on site to the W.A. Museum at 9:29 pm main fire indicator panel was isolated due to VESDAdetection of smoke had placed FIP ain Alarm. Fire Brigade had attended.Found the curtain had not lifted back into raised position due to the frame work of a display paneltwisting the base out of alignment.Reset panel and curtain raised back into position.Unfortunately the VESDA was still in alarm when curtain raised and had the EWIS alarm for 4seconds but immediately isolated.Left the building at 11 pm with the VESDA in isolation but remained fully functional in all otherzones.
MSA-DCA | WA5879794 | 2 | Techworks Plumbing | Ground Floor - UAT - Sink detached from wall | Plumbing & Drainage | Water | 883.48 | Pass | Pass | -1 | -1 | 2.5 | 2022-09-15 09:12 | 2022-09-20 17:00 | 2022-09-16 07:00 | 2022-09-20 17:00 | 2022-09-16 09:30 |  |  | Wall basin loose on the wall, on inspection it was quite loose so I begin removing the wall basin off the wall, once it was off I begin to inspect why it was loose the rod wasn’t secure in the wall properly due to how far the noggin inside the wall.
MSA-DTWD | WA5888298 | 2 | Lane's Plumbing | Blocked toilet | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 2.5 | 2022-09-16 15:09 | 2022-09-21 17:00 | 2022-09-19 14:30 | 2022-09-21 17:00 | 2022-09-19 17:00 |  |  | cleared blockage
MSA-DCA | WA5971906 | 2 | Protek 24/7 Building & Maintenance | Hackett Hall - Level 1 - Male toilet - door latch/striker broken - see notes below | Building | Doors | 256.32 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-20 16:14 | 2022-09-23 17:00 | 2022-09-23 07:00 | 2022-09-23 17:00 | 2022-09-23 09:30 |  |  | Installed a striker plate
MSA-DFES | WA5974174 | 2 | AWB Co. | Door to Station Officers PPC Storage room in Engine Room has come off the track.-see notes | Building | Automatic Doors | 369.345 | Pass | Pass | -1 | -1 | 2.5 | 2022-09-23 08:46 | 2022-09-29 17:00 | 2022-09-23 13:00 | 2022-09-29 17:00 | 2022-09-23 15:30 |  |  | Attend Site repaired broken track
MSA-DTWD | WA5977333 | 2 | AWB Co. | The lights are not working in machine shop U0017. | Electrical | Lighting, Internal | 474.49 | Pass | Pass | 0 | 0 | 2.5 | 2022-09-27 16:12 | 2022-09-30 17:00 | 2022-09-29 14:30 | 2022-09-30 17:00 | 2022-09-29 17:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Found bank of lights was tripped. Fault found until found the light causing issue. Went to wholesaler for part. Returned to site. Took down old light. Wired in plug. Secured light. Plugged in. Working as intended. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5977924 | 3 | GRAFFITI FORCE PTY LTD | Nth Wall courtyard-Graffiti Tagging Courtyard | Building | External Walls | 529 | Pass | Pass | -1 | -1 | 2.5 | 2022-09-28 07:29 | 2022-10-04 17:00 | 2022-09-29 07:00 | 2022-10-04 17:00 | 2022-09-29 09:30 |  |  | REMOVAL OF GRAFFITI FROM WALLS IN COURTYARD
MSA-DCA | WA6000543 | 0 | TK Elevator Australia Pty Ltd | Ground - Lift 7 - out of service | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.5 | 2022-10-10 08:47 | 2022-10-10 10:47 | 2022-10-10 10:00 | 2022-10-10 12:47 | 2022-10-10 12:30 |  |  | Lift7 Greem Rm-Elevator > MR > Hydraulic :Lift stopped on level 2 with doors open. STE Lap on controller with FR relay dropping in and out, metered out safety circuit andfound lock fault, further investigation found access device spring missing and lock arm not allowing lock arm to drop. Adjusted and took a sample spring away to orderreplacement, checked all doors and found G floor lock housing different to left hand door, replaced with Spare parts from onsite. Ran and tested lift extensively without fail andreturned to service.
MSA-DTWD | WA6008310 | 2 | Techworks Electrical | Restaurant-3 down lights not working the restaurant and 6 lights broken in the bar main fridge | Electrical | Lighting, Internal | 298.165 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-11 13:21 | 2022-10-14 17:00 | 2022-10-12 10:00 | 2022-10-14 17:00 | 2022-10-12 12:30 |  |  | Replaced tubes in fridge All downlights working in restaurant Material used 3x 58W 865 tubes3x S10 Starters
MSA-DTWD | WA6014616 | 1 | AWB Co. | Room D09 - Fault description Door latch forced off frame / Latch repair & door frame reinforcing | Building | Doors | 270.345 | Pass | Pass | 0 | 0 | 2.5 | 2022-10-12 10:33 | 2022-10-13 17:00 | 2022-10-12 11:30 | 2022-10-13 17:00 | 2022-10-12 14:00 |  |  | Repairs to metal door frame entrance to control roomRepair door frame to control roomStrip, fix and reinstate aluminium frame
MSA-DTWD | WA6051613 | 3 | Lane's Plumbing | Check gas regulator for possible leak and if the regulator needs updating or not | Plumbing & Drainage | Gas |  | Pass | Pass | -1 | -1 | 2.5 | 2022-10-17 16:20 | 2022-10-24 17:00 | 2022-10-18 10:00 | 2022-10-24 17:00 | 2022-10-18 12:30 |  |  | Completed
MSA-DCA | WA6077913 | 2 | FCT SURFACE CLEANING | Graffiti on front of building | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2.5 | 2022-10-18 11:51 | 2022-10-21 17:00 | 2022-10-18 13:00 | 2022-10-21 17:00 | 2022-10-18 15:30 |  |  | Removal of graffiti
MSA-DCA | WA6082996 | 3 | Protek 24/7 Building & Maintenance | W Block - Pad locks on site are seized and difficult to open - See notes | Security | Keys & Access | 258.57 | Pass | Pass | -1 | -1 | 2.5 | 2022-10-18 16:17 | 2022-10-25 17:00 | 2022-10-21 07:00 | 2022-10-25 17:00 | 2022-10-21 09:30 |  |  | Lubricated all padlocks on site and checked they are in working order
MSA-DTWD | WA6113579 | 2 | Lane's Plumbing | Faulty gas regulator | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 2.5 | 2022-10-24 12:50 | 2022-10-27 17:00 | 2022-10-27 11:30 | 2022-10-27 17:00 | 2022-10-27 14:00 |  |  | job completed - REPLACE FAULTY REGULATOR AND INSTALL CONCRETE SLABS FOR BOTTLES HOUSE 13
MSA-DTWD | WA6143775 | 2 | AWB Co. | Faulty fluro fittings | Electrical | Lighting, Internal | 446.58 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-01 14:51 | 2022-11-04 17:00 | 2022-11-03 07:00 | 2022-11-04 17:00 | 2022-11-03 09:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Replaced tubes starters and tombstones. All are now working as intended. Took pics. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA6148704 | 3 | AWB Co. | ground-metal fab 2-Broken 15 amp power point | Electrical | General Electrical | 383.485 | Pass | Pass | -1 | -1 | 2.5 | 2022-11-04 08:18 | 2022-11-11 17:00 | 2022-11-04 08:30 | 2022-11-11 17:00 | 2022-11-04 11:00 |  |  | Attended site signed in jsa completed. Found broken gpo outside. Tapped out of circuit to move onto wall inside to remove extention lead. Tested and operational.Job completed
MSA-DTWD | WA6158801 | 1 | Equans Mechanical Services Australia | outside air fan ahu6 not running and ahu7 supply fan not running | Air Conditioning | Room Air Conditioners | 264.645 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-10 09:14 | 2022-11-11 17:00 | 2022-11-10 10:00 | 2022-11-11 17:00 | 2022-11-10 12:30 |  |  | BREAKER OFF -RESET AND TESTED
MSA-DCA | WA6258660 | 3 | GPS Plumbing & Gas Services PtyLtd | Courtyard door UAT & Studio Underground Male Toilets - Broken toilet seats - See Notes | Plumbing & Drainage | Toilets/Cisterns | 1122.33 | Pass | Pass | 0 | 0 | 2.5 | 2022-11-25 14:36 | 2022-12-02 17:00 | 2022-11-30 11:10 | 2022-12-02 17:00 | 2022-11-30 13:40 |  |  | Installed 2 new toilet seats, one normal in underground male toilet, and a disabled one in the foyer area disabled toilet
MSA-DTWD | WA6400218 | 1 | Lane's Plumbing | Burst water pipe | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 2.5 | 2023-01-03 10:32 | 2023-01-04 17:00 | 2023-01-03 13:00 | 2023-01-04 17:00 | 2023-01-03 15:30
MSA-DCA | WA6403674 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 2 - Loading Dock/ Winch Room - Leaking Air con | Air Conditioning | Room Air Conditioners | 512.39 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-06 13:39 | 2023-01-09 17:00 | 2023-01-09 07:00 | 2023-01-09 17:00 | 2023-01-09 09:30
MSA-DCA | WA6404823 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Chiller 2 - Alarm is showing a fault | Refrigeration | Chiller | 281.53 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-09 09:24 | 2023-01-09 11:24 | 2023-01-09 10:00 | 2023-01-09 13:24 | 2023-01-09 12:30
MSA-DTWD | WA6404864 | 2 | AWB Co. | A126 - Staff male toilet - Door closer faulty | Building | Doors | 991.715 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-09 09:44 | 2023-01-12 17:00 | 2023-01-11 10:00 | 2023-01-12 17:00 | 2023-01-11 12:30
MSA-DTWD | WA6504034 | 1 | Precise Air Group | D Block Library - A/C is not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 304.055 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-19 12:57 | 2023-01-20 17:00 | 2023-01-20 07:00 | 2023-01-20 17:00 | 2023-01-20 09:30
MSA-DFES | WA6504281 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Pump bay ceiling- Urban Pump- Breakaway plug for trickle charger keeps separating | Electrical | General Electrical | 998.08 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-19 14:31 | 2023-01-24 17:00 | 2023-01-23 08:30 | 2023-01-24 17:00 | 2023-01-23 11:00
MSA-DTWD | WA6516466 | 2 | BJ SYSTEMS | Main auto door not opening when swiped with card | Security | Access Control | 450 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-23 11:56 | 2023-01-27 17:00 | 2023-01-24 07:00 | 2023-01-27 17:00 | 2023-01-24 09:30
MSA-DTWD | WA6517517 | 2 | AWB Co. | One light circuit (Fluro's) is tripping out - Over 2m height | Electrical | Lighting, Internal | 508.58 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-24 10:37 | 2023-01-30 17:00 | 2023-01-30 11:30 | 2023-01-30 17:00 | 2023-01-30 14:00
MSA-DCA | WA6519307 | 0 | Precise Air Group | Level 1-performing lines contact-air is leaking through fire sprinkler | Air Conditioning | Room Air Conditioners | 1326.875 | Fail | Fail | 2 | 2 | 2.5 | 2023-01-25 15:08 | 2023-01-25 17:08 | 2023-02-09 11:30 | 2023-01-25 19:08 | 2023-02-09 14:00
MSA-DCA | WA6519338 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Air con fault - Temperatures high on level 1 & 2 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 557.43 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-25 15:44 | 2023-01-25 17:44 | 2023-01-25 16:00 | 2023-01-25 19:44 | 2023-01-25 18:30
MSA-DCA | WA6520289 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Geology L2-Gallery 7 (AHU.06.01) - air con hot and stuffy - see notes | Air Conditioning | Room Air Conditioners | 360.37 | Pass | Pass | 0 | 0 | 2.5 | 2023-01-27 12:27 | 2023-01-30 17:00 | 2023-01-27 13:00 | 2023-01-30 17:00 | 2023-01-27 15:30
MSA-DCA | WA6522628 | 3 | SCAVENGER SUPPLIES PTY LTD | Level 7 - Roof void - Fire Zone 413 VESDA fault - see notes | Fire Protection Services | Fire Protection - Monitor System | 451.53 | Pass | Pass | -1 | -1 | 2.5 | 2023-01-31 09:10 | 2023-02-07 17:00 | 2023-02-01 08:30 | 2023-02-07 17:00 | 2023-02-01 11:00
MSA-DTWD | WA6522682 | 2 | Precise Air Group | Canteen - Evaporative Aircon - water overflowing continuously | Air Conditioning | Evaporative Coolers |  | Pass | Pass | 0 | 0 | 2.5 | 2023-01-31 09:20 | 2023-02-03 17:00 | 2023-02-03 07:00 | 2023-02-03 17:00 | 2023-02-03 09:30
MSA-DTWD | WA6526789 | 2 | AWB Co. | C702 - @0 tubes damaged 10 fittings | Electrical | General Electrical | 648.72 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-01 10:46 | 2023-02-06 17:00 | 2023-02-06 07:00 | 2023-02-06 17:00 | 2023-02-06 09:30
MSA-DTWD | WA6539619 | 1 | Australian Airconditioning Services Pty Ltd | 7G7 canteen-Chilled food display cabinet leaking water | Air Conditioning | Room Air Conditioners | 410.08 | Fail | Fail | 0 | 0 | 2.5 | 2023-02-08 14:49 | 2023-02-09 17:00 | 2023-02-10 12:15 | 2023-02-09 17:00 | 2023-02-10 14:45
MSA-DTWD | WA6544536 | 2 | LIGHTHOUSE LOCKSMITHS | faulty lock | Security | Locksmith | 696 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-10 13:40 | 2023-02-15 17:00 | 2023-02-13 13:00 | 2023-02-15 17:00 | 2023-02-13 15:30
MSA-DTWD | WA6572875 | 1 | AWB Co. | Faulty lights tripping RCD and in store and affecting 4F15 classroom lights | Electrical | General Electrical | 247.14 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-14 09:21 | 2023-02-15 17:00 | 2023-02-15 07:00 | 2023-02-15 17:00 | 2023-02-15 09:30
MSA-DTWD | WA6600905 | 2 | AWB Co. | Room Creche yard verandah - Down lights under eaves not working 2 out of 7 | Electrical | Lighting, External | 779.83 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-17 09:51 | 2023-02-22 17:00 | 2023-02-21 11:30 | 2023-02-22 17:00 | 2023-02-21 14:00
MSA-DTWD | WA6669216 | 2 | Techworks Plumbing | Ground floor kitchenette & Disabled toilet - Water coming up in drain and toilet | Plumbing & Drainage | Water | 318.72 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-22 15:40 | 2023-02-27 17:00 | 2023-02-24 07:00 | 2023-02-27 17:00 | 2023-02-24 09:30
MSA-DTWD | WA6671710 | 3 | AWB Co. | 7 x lights out in classroom | Electrical | Lighting, Internal | 555.73 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-23 09:52 | 2023-03-02 17:00 | 2023-02-27 07:00 | 2023-03-02 17:00 | 2023-02-27 09:30
MSA-DTWD | WA6674347 | 1 | AWB Co. | Tower Block - Level 4 - Flickering light | Electrical | Lighting, External | 406.575 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-27 09:33 | 2023-02-28 17:00 | 2023-02-28 07:00 | 2023-02-28 17:00 | 2023-02-28 09:30
MSA-DTAG | WA6674351 | 2 | Water2water Pty Ltd | Level 5 - Family Violence Services - Kitchen - chilled/boiling water tap Faulty | Plumbing & Drainage | Water | 537.98 | Pass | Pass | 0 | 0 | 2.5 | 2023-02-27 09:27 | 2023-03-02 17:00 | 2023-03-02 08:30 | 2023-03-02 17:00 | 2023-03-02 11:00
MSA-DTAG | WA6680822 | 2 | Midolo Building Services | Stair tread nosings are loose – staircase leading to Courts 10 & 11 | Building | Internal Walls | 301.89 | Pass | Pass | 0 | 0 | 2.5 | 2023-03-01 14:59 | 2023-03-07 17:00 | 2023-03-07 11:30 | 2023-03-07 17:00 | 2023-03-07 14:00
MSA-DTWD | WA6682085 | 2 | Equans Mechanical Services Australia | Noisy motor in roof space / Air con damper | Air Conditioning | Ducted Split System | 264.645 | Pass | Pass | -1 | -1 | 2.5 | 2023-03-02 15:09 | 2023-03-08 17:00 | 2023-03-03 08:30 | 2023-03-08 17:00 | 2023-03-03 11:00
MSA-DTWD | WA6687932 | 2 | AHS Services WA Pty Ltd (Anchor) | east tap handle missing | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 2.5 | 2023-03-07 10:42 | 2023-03-10 17:00 | 2023-03-08 13:00 | 2023-03-10 17:00 | 2023-03-08 15:30
MSA-DCA | WA5105313 | 1 | Techworks Electrical | Ground - Reception Area - Issue with power supply to intercom system, intercom not working | Electrical | General Electrical | 303.51 | Pass | Pass | 0 | 0 | 2.4833 | 2022-02-04 09:22 | 2022-02-07 17:00 | 2022-02-04 09:31 | 2022-02-07 17:00 | 2022-02-04 12:00 |  |  | Identified and began fault finding on the intercom system.tested incoming ELV cable for continuity and correct operation, all good results apart from cable not recieving POE.re patched cable into new port and reset existing intercom to factory settings.intercom powered up and began working in correct order.tested unit with receptionist and confirmed transmitting and receiving audio messaging.
MSA-DTWD | WA5190279 | 3 | Falcetta Plumbing and Gas | Faulty tap | Plumbing & Drainage | Water | 469.41 | Pass | Pass | 0 | 0 | 2.4833 | 2022-02-24 12:16 | 2022-03-03 17:00 | 2022-03-03 14:30 | 2022-03-03 17:00 | 2022-03-03 16:59 |  |  | replaced 2x wall assemblies
MSA-DTWD | WA5751354 | 2 | AHS Services WA Pty Ltd (Anchor) | Female Toilets ( Student ) E-Block Female Student toilets the first basin tap underside has a leak | Plumbing & Drainage | Water | 456.325 | Pass | Pass | 0 | 0 | 2.4833 | 2022-08-17 10:41 | 2022-08-22 17:00 | 2022-08-22 07:30 | 2022-08-22 17:00 | 2022-08-22 09:59 |  |  | Completed
MSA-DCA | WA6021494 | 0 | TK Elevator Australia Pty Ltd | Lift 7 - out of order | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 2.4667 | 2022-10-14 08:24 | 2022-10-14 10:24 | 2022-10-14 13:21 | 2022-10-14 12:24 | 2022-10-14 15:49 |  |  | Lift ooo on street level, door pins needed adjusting, adjusted car door tension wire, male/female pins, terminals. Lift in service.
MSA-DCA | WA6578292 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Gallery-West - AHU.03.03 (Temp Gallery-West) Humidifier Fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 146.4 | Pass | Pass | 0 | 0 | 2.4667 | 2023-02-15 09:03 | 2023-02-16 17:00 | 2023-02-15 11:32 | 2023-02-16 17:00 | 2023-02-15 14:00
MSA-DCA | WA5549174 | 0 | Techworks Plumbing | Ground Floor - Jubilee Building - Accessible Toilet - Blocked Toilet | Plumbing & Drainage | Toilets/Cisterns | 267.19 | Pass | Pass | 0 | 0 | 2.45 | 2022-06-17 14:03 | 2022-06-17 16:03 | 2022-06-17 14:03 | 2022-06-17 18:03 | 2022-06-17 16:30 |  |  | Attend to clear drain blockage. Both bathrooms blocked in this area, work completed from plant room as we have access to COP. Drain blocked with what we could assume as toilet paper waste. Unblocked with drain rods and continues to flush through using all fixtures from the bathrooms, a 20l bucket filled from hose tap in plant room was us multiple time to flush everything through from the plant room.
MSA-DTWD | WA6537368 | 0 | CONNECT SECURITY SYSTEMS | Faulty alarm panels | Security | Security Management System | 581.78 | Fail | Fail | 0 | 0 | 2.45 | 2023-02-07 08:59 | 2023-02-07 10:59 | 2023-02-07 11:57 | 2023-02-07 12:59 | 2023-02-07 14:24
MSA-DCA | WA5286087 | 0 | TK Elevator Australia Pty Ltd | Lift 2 - stuck on level 1 and not moving | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.4333 | 2022-03-21 12:27 | 2022-03-21 14:27 | 2022-03-21 13:22 | 2022-03-21 16:27 | 2022-03-21 15:48 |  |  | Lift 2 Art-Kitchen-Geared :Arrived on site and found lift stopped traced fault to top floor door locks not dropping fully, adjusted lock arms and lubricated door gear, serviced allhoistway doors. Further works to be carried out to pneumatic actuator on access device top and bottom.Ran lift extensively and returned to service.Closed out at $0 cost
MSA-DCA | WA5700048 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis Street - Basement 1 - Security Control Room - Controller and adapter fault | Security | Security Management System | 610.19 | Pass | Pass | 0 | 0 | 2.4333 | 2022-08-10 14:30 | 2022-08-11 17:00 | 2022-08-11 13:00 | 2022-08-11 17:00 | 2022-08-11 15:26 |  |  | rest units, restored comms
MSA-DFES | WA5995741 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Men's Toilet - Broken toilet seat ground floor mens toilet last cubical. | Plumbing & Drainage | Toilets/Cisterns | 659.2 | Pass | Pass | -1 | -1 | 2.4333 | 2022-10-06 15:52 | 2022-10-11 17:00 | 2022-10-07 11:20 | 2022-10-11 17:00 | 2022-10-07 13:46 |  |  | Replaced toilet seat.
MSA-DTWD | WA6687901 | 2 | AHS Services WA Pty Ltd (Anchor) | far toilet leaking where toilet pipe meets wall | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 2.4333 | 2023-03-07 10:33 | 2023-03-10 17:00 | 2023-03-09 07:00 | 2023-03-10 17:00 | 2023-03-09 09:26
MSA-DTAG | WA5105404 | 3 | PPM Project Painting & Maintenance | Ground - Side wall – Courthouse - Graffitti on the side wall (RHS) of courthouse | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 2.4167 | 2022-02-04 10:25 | 2022-02-11 17:00 | 2022-02-12 08:00 | 2022-02-11 17:00 | 2022-02-12 10:25 |  |  | job completed - Prepare by cleaning surface. Apply one coat of oil based sealer to stop graffiti from bleeding through.Apply two coats of acrylic low sheen to match existing
MSA-DTWD | WA5287010 | 1 | AHS Services WA Pty Ltd (Anchor) | Kitchen Area - V-Block tap constantly running in kitchen area | Plumbing & Drainage | Water | 380.515 | Pass | Pass | 0 | 0 | 2.4167 | 2022-03-22 09:25 | 2022-03-23 17:00 | 2022-03-22 09:30 | 2022-03-23 17:00 | 2022-03-22 11:55 |  |  | Completed
MSA-DTAG | WA5675369 | 0 | Gilmour & Jooste Electrical | Zone 8 emergency lighting - LED fault - see notes | Electrical | General Electrical | 372.64 | Pass | Pass | 0 | 0 | 2.4167 | 2022-07-22 10:03 | 2022-07-22 12:03 | 2022-07-22 10:15 | 2022-07-22 14:03 | 2022-07-22 12:40 |  |  | Investigated fault to burning smell in zone eight. Checked light fittings and roof voids throughout zone eight. No direct burning smell found. Replaced four fluoro’s in waiting area.
MSA-DTWD | WA5069196 | 2 | CONNECT SECURITY SYSTEMS | B Block - camera facing plant faulty | Security | Monitoring | 576.22 | Pass | Pass | 0 | 0 | 2.4167 | 2022-01-19 16:36 | 2022-01-24 17:00 | 2022-01-21 09:25 | 2022-01-24 17:00 | 2022-01-21 11:50 |  |  | Job completed 21/1/2022
MSA-DFES | WA5288878 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Safety Shower 7 - loses pressure for Shower | Plumbing & Drainage | Water | 280.25 | Fail | Fail | 0 | 0 | 2.4167 | 2022-03-23 15:08 | 2022-03-28 17:00 | 2022-03-29 13:08 | 2022-03-28 17:00 | 2022-03-29 15:33 |  |  | Cleaned safety shower
MSA-DTWD | WA5312410 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block - LSK bakery area has a blocked floor drain | Plumbing & Drainage | Drainage | 309.605 | Pass | Pass | 0 | 0 | 2.4167 | 2022-04-11 13:32 | 2022-04-14 17:00 | 2022-04-13 11:35 | 2022-04-14 17:00 | 2022-04-13 14:00 |  |  | Completed
MSA-DCA | WA5394263 | 2 | Techworks Electrical | Light switch broken. Lights will not turn off. | Electrical | Lighting, Internal | 236.26 | Pass | Pass | -1 | -1 | 2.4167 | 2022-05-04 14:27 | 2022-05-09 17:00 | 2022-05-05 11:35 | 2022-05-09 17:00 | 2022-05-05 14:00 |  |  | Replaced two gang switch in dress room
MSA-DFES | WA5522449 | 3 | AWB Co. | Radio Comms - Various Offices - water leaks - see notes below | Building | Ceiling | 484.4 | Pass | Pass | -1 | -1 | 2.4167 | 2022-06-15 16:16 | 2022-06-22 17:00 | 2022-06-17 09:00 | 2022-06-22 17:00 | 2022-06-17 11:25 |  |  | Attended and un blocked downpipes, cleared back and re-sealed pops. Re-sealed unit above kitchen, if persists larger works for dry pans may be required.
MSA-DCA | WA6159339 | 2 | GPS Plumbing & Gas Services PtyLtd | Dripping tap - see notes | Plumbing & Drainage | Water | 390.415 | Pass | Pass | -1 | -1 | 2.4167 | 2022-11-10 14:26 | 2022-11-15 17:00 | 2022-11-11 15:00 | 2022-11-15 17:00 | 2022-11-11 17:25 |  |  | Assesed dripping tap serviced them including reseated but spindles and tap very worn down cold tap wont even turn on so recommended new wall top assembley and installed like for like mo leaks on testing and taps smooth
MSA-DFES | WA6298586 | 1 | SONTEC WA PTY LTD | Reception - needing footage from cctv | Security | CCTV Surveillance | 550 | Pass | Pass | 0 | 0 | 2.4167 | 2022-12-01 10:59 | 2022-12-02 17:00 | 2022-12-01 14:30 | 2022-12-02 17:00 | 2022-12-01 16:55 |  |  | 1/12/22 - Joshua ParkExported footage from Camera 17 as requested.
MSA-DCA | WA5295323 | 1 | TK Elevator Australia Pty Ltd | Main Building - Basement 1 - Lift 1 - doors are shuddering when opening and closing. - SEE DETAILS | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.4 | 2022-03-29 12:41 | 2022-03-30 17:00 | 2022-03-29 13:19 | 2022-03-30 17:00 | 2022-03-29 15:43 |  |  | Lift1 Main Foyer-MRL :Replaced 2 damaged car door roller on left door,tested and left lift runningto be closed out at $0 cost
MSA-DCA | WA5798240 | 2 | GPS Plumbing & Gas Services PtyLtd | Female Public Toilet - Replace leaking cistern. | Plumbing & Drainage | Toilets/Cisterns | 760.215 | Pass | Pass | 0 | 0 | 2.4 | 2022-08-29 13:03 | 2022-09-01 17:00 | 2022-08-30 10:00 | 2022-09-01 17:00 | 2022-08-30 12:24 |  |  | New invisi cistern in female public toilet
MSA-DTAG | WA6529107 | 3 | Schindler Lifts Australia | Lift 3 - Intermittent issues doors not closing, loud beeping as if something is in the way. see note | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 2.3956 | 2023-02-02 14:40 | 2023-02-09 17:00 | 2023-02-03 06:02 | 2023-02-09 17:00 | 2023-02-03 08:26
MSA-DCA | WA5053339 | 1 | EQUANS Mechanical Services (WA) Pty Limited | CRC Warehouse - Ground - Plant Room - Chiller 1 in fault | Refrigeration | Chiller | 920.925 | Pass | Pass | 0 | 0 | 2.3833 | 2022-01-18 16:16 | 2022-01-19 17:00 | 2022-01-19 13:46 | 2022-01-19 17:00 | 2022-01-19 16:09 |  |  | Attended site gained access and carried out inspection of chiller 1 due to reported fault. Stage 1B was found to have comms suction fault active. Carried out hard reset of equipment and placed into operation lead mode. Confirmed operation and fault did not reoccur. Will recheck during site PM inspection. If fault reoccurring chiller specialist will need to investiagte. Work area left tidy.
MSA-DCA | WA5994055 | 2 | GPS Plumbing & Gas Services PtyLtd | Solar Panel on roof is leaking water, needs isolating from hot water unit. | Plumbing & Drainage | Water | 378.415 | Pass | Pass | 0 | 0 | 2.3833 | 2022-10-05 13:08 | 2022-10-10 17:00 | 2022-10-07 07:52 | 2022-10-10 17:00 | 2022-10-07 10:15 |  |  | Capped off solar on the roof as instructed by client.
MSA-DTAG | WA5393928 | 2 | AHS Services WA Pty Ltd (Anchor) | Registry Staff Toilet - Far right staff toilet is not flushing properly - water constantly running | Plumbing & Drainage | Toilets/Cisterns | 274.0575 | Pass | Pass | -1 | -1 | 2.3667 | 2022-05-04 11:20 | 2022-05-09 17:00 | 2022-05-04 12:00 | 2022-05-09 17:00 | 2022-05-04 14:22 |  |  | Picked up and replaced bellows, inlet valve and outlet washer to right hand side female staff toilet on the grid floor
MSA-DCA | WA5696745 | 1 | SCAVENGER SUPPLIES PTY LTD | Level 2 - Changes Gallery - leaking fire sprinkler - See notes below | Fire Protection Services | Sprinkler Systems | 208.23 | Pass | Pass | 0 | 0 | 2.35 | 2022-08-08 14:13 | 2022-08-09 17:00 | 2022-08-09 07:00 | 2022-08-09 17:00 | 2022-08-09 09:21 |  |  | STARTED 7.00AM 09/08/2022 JA1. CALL OUT ATTENDED 7.00AM 09/08/2022NORMAL LABOUR: 7.00AM-8.30AM2. SIG SLIP SENT TO NEIL DUCHAN 12.00 PM 09/08/2022completed
MSA-DCA | WA5202958 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Level M - Female toilets - Both basins blocked. | Plumbing & Drainage | Toilets/Cisterns | 251.395 | Pass | Pass | 0 | 0 | 2.3333 | 2022-03-03 09:33 | 2022-03-09 17:00 | 2022-03-08 08:00 | 2022-03-09 17:00 | 2022-03-08 10:20 |  |  | Unblocked sink drain with the drain machine
MSA-DCA | WA5677252 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Function Room Kitchen - Pipes under the two hand wash basins are leaking | Plumbing & Drainage | Water | 704.975 | Pass | Pass | 0 | 0 | 2.3333 | 2022-07-25 13:32 | 2022-07-26 17:00 | 2022-07-25 15:30 | 2022-07-26 17:00 | 2022-07-25 17:50 |  |  | Replaced faulty and leaking knee operated valve. Struggled to find the isolation valves for the kitchen. No hydraulic plans available. Tightened loosen trap
MSA-DTAG | WA5699522 | 0 | GPS Plumbing & Gas Services PtyLtd | Usher Room - Court Room 8 - leaking boiler | Plumbing & Drainage | Water | 1050.485 | Pass | Pass | 0 | 0 | 2.3333 | 2022-08-10 10:11 | 2022-08-10 12:11 | 2022-08-10 11:27 | 2022-08-10 14:11 | 2022-08-10 13:47 |  |  | Replaced leaking hot water unit in court yard next to usher room court 8
MSA-DCA | WA6021566 | 1 | SCAVENGER SUPPLIES PTY LTD | Francis St Building - Ground floor - Main entrance lobby - Check faults on fire indicator panel | Fire Protection Services | Fire Protection - Monitor System | 292.309 | Pass | Pass | 0 | 0 | 2.3333 | 2022-10-14 09:05 | 2022-10-17 17:00 | 2022-10-14 09:30 | 2022-10-17 17:00 | 2022-10-14 11:50 |  | WCAPPR | INITIAL VISIT - 14/10/22 - NO FURTHER WORK REQUIRED.
MSA-DTAG | WA5108448 | 0 | Sapio Pty Ltd | entry & exit carpark gates for migrates are not opening with swipe cards | Security | Security Management System | 360 | Pass | Pass | 0 | 0 | 2.3333 | 2022-02-08 14:10 | 2022-02-08 16:10 | 2022-02-08 14:10 | 2022-02-08 18:10 | 2022-02-08 16:30 |  |  | Controller lost of configDown load the configuration from pc but controller would not accept itDefault controller factory set upManual pit in ip addressDown load controller configurationAnd checked
MSA-DFES | WA5195340 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Workshop - Mens Bathroom - 1 x blocked urinal & tap leaking on urinal | Plumbing & Drainage | Toilets/Cisterns | 352.32 | Pass | Pass | 0 | 0 | 2.3333 | 2022-02-28 12:05 | 2022-02-28 14:05 | 2022-02-28 12:53 | 2022-02-28 16:05 | 2022-02-28 15:13 |  |  | Located to male toilets due to left hand side toilet is blocked plunged the toilet and cleared the blockage. In the male toilets as well the washing machine stop was leaking the tap was unserviceable tried to remove it but the spud in the wall snapped chipped it out of the wall and installed a new one mudded up tested working correctly now
MSA-DFES | WA5482617 | 1 | WA BOILER SPARES & SERVICE | Tower 3 - Applied training grounds - Emergency stop switch is leaking air through valves | Plumbing & Drainage | Gas | 598 | Pass | Pass | 0 | 0 | 2.3333 | 2022-05-31 13:41 | 2022-06-01 17:00 | 2022-06-01 07:10 | 2022-06-01 17:00 | 2022-06-01 09:30 |  |  | Replaced faulty E-Stop on fire fighting training unit
MSA-DTWD | WA6022368 | 2 | Water2water Pty Ltd | G120-Water fountain tap broken/ loose | Plumbing & Drainage | Water | 469.72 | Pass | Pass | 0 | 0 | 2.3333 | 2022-10-14 11:29 | 2022-10-19 17:00 | 2022-10-18 09:00 | 2022-10-19 17:00 | 2022-10-18 11:20 |  |  | Locking nut underneath tap had come loose, tubing was leaking, filter had partially come off unit re-screwed back on, silicone around underside tap for a better seal, flexi was damaged, checked and tested all okay on departure.
MSA-MRWA | WA6090623 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Floor - Room G04 - Air con not working | Air Conditioning | Room Air Conditioners | 259.01 | Pass | Pass | 0 | 0 | 2.3167 | 2022-10-19 12:34 | 2022-10-20 17:00 | 2022-10-19 12:35 | 2022-10-20 17:00 | 2022-10-19 14:54 |  |  | Attended job, room still in use. Accessed BMS to check layout and if any issues via BMS. Returned to room gained access found room cool and unit on fan only, checked system turn on to cooling. Lady using room appeared and advised the unit was running okay and that the issues was caused by operator. Left running will monitor. Checked later, all good.
MSA-DCA | WA6166471 | 2 | GPS Plumbing & Gas Services PtyLtd | Toilet leaking at base | Plumbing & Drainage | Toilets/Cisterns | 425.415 | Pass | Pass | 0 | 0 | 2.3167 | 2022-11-11 16:28 | 2022-11-16 17:00 | 2022-11-15 10:00 | 2022-11-16 17:00 | 2022-11-15 12:19 |  |  | Upon arrival found drenched floor around concealed P pan. Pulled off cistern and found split and bad silicone kee seal from cistern to pan. Replace leak kee seal and flush pipe. Put abck together. All seemed ok but could not confirm if pan collar is leaking or not as floor was so wet from split pipe and kee seal, water kept pooling out from under pan concrete due to saturation. Shut off toilet for a day or so to get to dry out, then instructed staff to open toilet cubical and flush and check. If still leaking, pan will need to be removed and possible replaced
MSA-DCA | WA5791720 | 1 | Earth & Water Pty Ltd | Fault description Wetlands level is too low. Pump is gurgling (I think due to the level) - see note | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 2.3 | 2022-08-23 09:17 | 2022-08-24 17:00 | 2022-08-23 10:15 | 2022-08-24 17:00 | 2022-08-23 12:33 |  |  | Job is completed - The water level has been fixed
MSA-DFES | WA6682037 | 3 | Australian HVAC Services Pty. Ltd. | Water cooler on ground floor near front door - Tepid water coming through cold tap (see notes) | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 2.3 | 2023-03-02 14:21 | 2023-03-10 17:00 | 2023-03-07 07:15 | 2023-03-10 17:00 | 2023-03-07 09:33
MSA-DFES | WA6667832 | 2 | Australian HVAC Services Pty. Ltd. | Ceiling - Air con configuration reported to have discharge if insects onto a work station (see notes | Air Conditioning | Ducted Split System | 193.43 | Pass | Pass | 0 | 0 | 2.3 | 2023-02-21 15:21 | 2023-02-24 17:00 | 2023-02-23 11:30 | 2023-02-24 17:00 | 2023-02-23 13:48
MSA-DFES | WA6675911 | 1 | Seme Solutions Pty Ltd | Security Alarm panel - Showing Fault | Security | Security Management System | 524.55 | Pass | Pass | 0 | 0 | 2.3 | 2023-02-28 10:27 | 2023-03-01 17:00 | 2023-02-28 10:27 | 2023-03-01 17:00 | 2023-02-28 12:45
MSA-DFES | WA4993160 | 2 | Australian HVAC Services Pty. Ltd. | Administration - LR1 & 2 Administration - see notes below | Air Conditioning | Room Air Conditioners | 453.165 | Pass | Pass | -1 | -1 | 2.2833 | 2022-01-07 10:12 | 2022-01-12 17:00 | 2022-01-07 10:45 | 2022-01-12 17:00 | 2022-01-07 13:02 |  |  | Cu3 up and running no further faults found
MSA-DCA | WA5100173 | 3 | GPS Plumbing & Gas Services PtyLtd | Theatre Foyer disabled unisex toilet - Toilet Pan Cracked | Plumbing & Drainage | Toilets/Cisterns | 764.6275 | Pass | Pass | -1 | -1 | 2.2833 | 2022-02-02 11:25 | 2022-02-09 17:00 | 2022-02-03 10:16 | 2022-02-09 17:00 | 2022-02-03 12:33 |  |  | Replace cracked pan with new
MSA-DCA | WA5109459 | 0 | Techworks Electrical | level 1 - circuit 7 on dimmer 2 of house lights are tripping - | Electrical | General Electrical | 240.71 | Pass | Pass | 0 | 0 | 2.2833 | 2022-02-09 09:48 | 2022-02-09 11:48 | 2022-02-09 10:28 | 2022-02-09 13:48 | 2022-02-09 12:45 |  |  | Investigated fault and tried to create fault again was no luck found a couple of possible causes so we are keeping an eye out on certain fittings if it happens again
MSA-DCA | WA5499264 | 1 | Precise Air Group | Ground Level - Food & Beverage Kitchen Office - Sewerage smell leaking through air con- See notes | Air Conditioning | Room Air Conditioners | 268.91 | Pass | Pass | 0 | 0 | 2.2833 | 2022-06-10 12:03 | 2022-06-13 17:00 | 2022-06-10 13:43 | 2022-06-13 17:00 | 2022-06-10 16:00 |  |  | Notes Gained access to site, found duct work had leaking air from system causing bad smell to go into area, picked up required equipment to patch, patched up equipment,cleared debris from site
MSA-MRWA | WA5513616 | 2 | Water2water Pty Ltd | Level 1 - Kitchen - Billy boiler unit not working - See notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 390.415 | Pass | Pass | 0 | 0 | 2.2833 | 2022-06-14 11:54 | 2022-06-17 17:00 | 2022-06-15 13:15 | 2022-06-17 17:00 | 2022-06-15 15:32 |  |  | -Level 6 water fountain drained, internally cleaned and flushed. Also replaced water filter. All ok.-Level 1 wall mounted hot water unit has failed due to multiple part failure (element, solenoid, level sensors, rusted tank) Recommend to replace as 13+ years old. Water2Water will quote for replacement.
MSA-MRWA | WA5574037 | 2 | AWB Co. | Ground Level - Oil Water separator Bitumen Spray Shed- Sump pump motor trips circuit | Equipment | Electrical Equipment | 357.76 | Pass | Pass | -1 | -1 | 2.2833 | 2022-06-30 14:26 | 2022-07-05 17:00 | 2022-07-01 08:30 | 2022-07-05 17:00 | 2022-07-01 10:47 |  |  | Attended site and signed in. Completed JSA. Located sump pump. Opened up control gear and tested electrical components. All tested ok. Opened oil tank. Tested windings and phases all testing fine. Ran motor and tested. Motor is drawing 9amps. All electrical components are operating correctly. Motor is not operating correctly. Have notified relevant personal of works. Will need to send a quote in to replace motor. Completed paperwork. Signed out *job complete**
MSA-DTAG | WA5853881 | 1 | Water2water Pty Ltd | Level 12 - Kitchen - Billi Unit left of kitchen faulty - See notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 619.09 | Pass | Pass | 0 | 0 | 2.2667 | 2022-09-12 11:50 | 2022-09-13 17:00 | 2022-09-13 11:40 | 2022-09-13 17:00 | 2022-09-13 13:56 |  |  | System tagged out on arrival. Disconnected element and didn’t blow the power. Fault log showing tap loom error. Replaced element, tap pcb loom and inlet solenoid. Ran machine back to temp. Normal operation
MSA-DTWD | WA5018286 | 1 | SCAVENGER SUPPLIES PTY LTD | Retrospective work order - B Block - Ground & 1st floor - see details below | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 2.2667 | 2022-01-13 14:00 | 2022-01-14 17:00 | 2022-01-14 07:45 | 2022-01-14 17:00 | 2022-01-14 10:01 | 1 |  | COMPLETED 14/01/2022
MSA-DFES | WA4990136 | 1 | Go Doors | Hope Valley-Engine room door is not working- The one which lifts up | Building | Doors | 1305 | Pass | Pass | 0 | 0 | 2.25 | 2022-01-03 13:19 | 2022-01-04 13:19 | 2022-01-03 14:45 | 2022-01-04 13:19 | 2022-01-03 17:00 |  |  | Works completed
MSA-DTWD | WA4991085 | 1 | WESTERN IRRIGATION PTY LTD | D2 Nursing - Reticulation under pavement South of D2 has ruptured. | Plumbing & Drainage | Water | 380.36 | Pass | Pass | 0 | 0 | 2.25 | 2022-01-04 14:55 | 2022-01-05 17:00 | 2022-01-05 07:30 | 2022-01-05 17:00 | 2022-01-05 09:45 |  |  | Locate and repair broken reticulation pipe
MSA-DFES | WA5038647 | 1 | SONTEC WA PTY LTD | Electric Fence - energizer is in alarm - please see details below | Security | Monitoring | 510 | Pass | Pass | 0 | 0 | 2.25 | 2022-01-17 16:41 | 2022-01-18 17:00 | 2022-01-18 10:00 | 2022-01-18 17:00 | 2022-01-18 12:15 |  |  | Dylan Parslow - 18/01/22Investigated issues with electric fence, found metal pole shorting fence.removed & testedall working
MSA-DTAG | WA5081567 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 12 - staff female toilet on left - Toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 425.9875 | Fail | Fail | 1 | 1 | 2.25 | 2022-01-20 15:56 | 2022-01-25 17:00 | 2022-01-31 14:00 | 2022-01-25 17:00 | 2022-01-31 16:15 |  |  | Replaced bellows, flush rubber and inlet valve in conceiled cister . Trip to supplier required
MSA-DFES | WA5093531 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Downlight blown at the end of corridor leading out in to the underground carpark. | Electrical | Lighting, Internal | 409.325 | Pass | Pass | 0 | 0 | 2.25 | 2022-01-28 16:02 | 2022-02-02 17:00 | 2022-02-01 14:15 | 2022-02-02 17:00 | 2022-02-01 16:30 |  |  | Continued onsite at 14:15 to investigate light not working at end of hallway leading to underground carpark. Replaced blown globes and tested that everything works.
MSA-DFES | WA5094926 | 1 | Seme Solutions Pty Ltd | Office - Zone 8 and Zone 5 - alarming at different time | Security | Monitoring | 884 | Pass | Pass | 0 | 0 | 2.25 | 2022-01-31 16:15 | 2022-02-01 17:00 | 2022-02-01 13:00 | 2022-02-01 17:00 | 2022-02-01 15:15 |  |  | Arrive on site and wait for keysIdentify devices for zones 5 and 8 - shed 2 pirs East and west.Test inputs in tecom - appear okay.Clean out devices of debris etc.Unable to replicate initial fault, zones appear to be functional whilst on site.Recommendation - Devices are quite old and worn, possibly near end of life. Given multiple false alarms recently suggest to replace 5x PIRs on site to reduce false alarms and provide reliability.
MSA-DTWD | WA5099028 | 2 | AWB Co. | Level 2 - Creche toddlers 2 - Door handle faulty | Building | Doors | 247.565 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-01 13:23 | 2022-02-04 17:00 | 2022-02-03 10:15 | 2022-02-04 17:00 | 2022-02-03 12:30 |  |  | Attended site and installed new passage door handle. Job complete
MSA-DFES | WA5099978 | 1 | SONTEC WA PTY LTD | Main entrance - alarm sensor - keeps going off for no reason | Security | Monitoring | 553.25 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-02 10:08 | 2022-02-03 17:00 | 2022-02-02 11:15 | 2022-02-03 17:00 | 2022-02-02 13:30 |  |  | 2/2/22 - Dean SimpsonReplaced faulty PIR.Removed card reader and cable from door as requested.
MSA-DTWD | WA5105573 | 2 | AHS Services WA Pty Ltd (Anchor) | Tap in basin running. auto Handle wont turn off | Plumbing & Drainage | Water | 560.7075 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-04 12:16 | 2022-02-09 17:00 | 2022-02-08 10:00 | 2022-02-09 17:00 | 2022-02-08 12:15 |  |  | Found middle tap in male toilets on level 2 runningLocated , picked up and installed new tap.testez
MSA-DTWD | WA5107719 | 0 | AWB Co. | Store Shed - Compressor has no power | Electrical | General Electrical | 482.945 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-08 08:52 | 2022-02-08 10:52 | 2022-02-08 09:15 | 2022-02-08 12:52 | 2022-02-08 11:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Site directed us to compressor which was not functioning correctly. Tested to see if we had feed coming in. Had correct voltage being supplied. Went through and tested all electrical components. Found to be NC contact was not operating due to bit of dust n wear. Cleaned out. All working properly now. Also found to be damaged cable on horizontal band saw. Which was causing a fault. Repaired cable and tested and tagged out appliance. Notified FM of works completed. **job complete**
MSA-DFES | WA5108630 | 2 | Australian HVAC Services Pty. Ltd. | Main Administration - Below ground - Lecture Theatre NE Metro - see notes below | Air Conditioning | Room Air Conditioners | 179.76 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-08 15:26 | 2022-02-11 17:00 | 2022-02-09 08:30 | 2022-02-11 17:00 | 2022-02-09 10:45 |  |  | Arrived onsite, signed in & spoke to onsite representative who directed me.to lecture room where A/C had not been working, located wall controller and found it to have no power, unable to turn unit on. Located Outdoor condensing unit & found that it had not been isolated and is receiving 240v, proceeded to locate indoor evaporator unit in plant room where after performing a visual inspection I had found this unit to be very new, spoke with onsite representative who informed me unit was only a couple months old. Daikin unit in lecture theatre is still under warranty with installer (not.Australian HVAC Services) installation company.must be contacted to resolve issues with A/C under warranty.
MSA-DTAG | WA5109578 | 3 | Midolo Building Services | Courtroom 5 Entrance Hall - faulty door handle and door stop - see notes | Building | Doors | 262.73 | Pass | Pass | -1 | -1 | 2.25 | 2022-02-09 11:32 | 2022-02-16 17:00 | 2022-02-11 09:30 | 2022-02-16 17:00 | 2022-02-11 11:45 |  |  | HANDLE SCREWE REPLACED, NEW DOOR STOP INSTALLED
MSA-DCA | WA5112313 | 2 | Assa Abloy Entrance Systems Aust P/L-WA | Ground - Main entrance - Front entry door beeping intermittently. | Building | Automatic Doors | 638.97 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-10 16:27 | 2022-02-15 17:00 | 2022-02-14 11:00 | 2022-02-15 17:00 | 2022-02-14 13:15 |  |  | Found battery flat causing door to beep intermittently. Removed old battery and replaced withnew, carried out full test of operation ok.NOTE: old operator, worn out components. Recommend upgrading and replacing track wheels.
MSA-DFES | WA5127588 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - FF End Dormitory Room 13 - see details below | Electrical | Lighting, External | 322.805 | Pass | Pass | 0 | 0 | 2.25 | 2022-02-14 13:19 | 2022-02-21 17:00 | 2022-02-18 07:00 | 2022-02-21 17:00 | 2022-02-18 09:15 |  |  | Arrived on site 0700, proceeded to locate faulty Fluro oyster light in Dorm 18.Unable to locate supplier stocking correct fittings to fix fluro.Proceeded to purchase LED Oyster light from supplier and replaced an adjacent room, with a working Fluro fitting, with the LED Light. I then replaced the faulty Fluro Fitting with the working fitting that had been replaced in the adjacent room. All lights are now working correctly. Informed staff of works completed, and left site at 0915
MSA-DTWD | WA5141694 | 2 | AWB Co. | E Block - Ground - E200 - Damaged lead to Radial Arm drill press | Electrical | General Electrical | 378.21 | Pass | Pass | -1 | -1 | 2.25 | 2022-02-16 11:50 | 2022-02-21 17:00 | 2022-02-17 12:45 | 2022-02-21 17:00 | 2022-02-17 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Fm said both machines need to be bolted down. Drove around to E block. Spoke to technician. Found nuts to suit rag bolts. Fixed grinder to floor. Identified circuits for grinder and drill press. Isolated circuits. Connected up isolators. Re energised circuits. Made sure machines were running the correct way. Packed and cleaned up. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5199569 | 2 | Equans Mechanical Services Australia | issue with our chiller unit on the Binary Distillation Unit - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 225 | Pass | Pass | 0 | 0 | 2.25 | 2022-03-01 10:16 | 2022-03-04 17:00 | 2022-03-03 09:15 | 2022-03-04 17:00 | 2022-03-03 11:30 |  |  | Works completed, unit working no faults located. Unit undersized to its Working conditions. BRAF BEEN RAISED,previously still in system. Completed paperwork.
MSA-DTWD | WA5201213 | 3 | AWB Co. | 6x faulty paper tower dispenser in Kitchens - require replacement | Building | Internal Walls | 343.61 | Pass | Pass | -1 | -1 | 2.25 | 2022-03-02 12:45 | 2022-03-10 17:00 | 2022-03-03 09:30 | 2022-03-10 17:00 | 2022-03-03 11:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Fm showed us where he wanted new paper towel dispensers fitted. Went around site and replaced all faulty dispensers with new ones. Took pictures and cleaned up all work areas. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5201440 | 2 | AWB Co. | T block - G - T027 - The ceiling lights are not remaining on, when switched on. | Electrical | General Electrical | 385.095 | Pass | Pass | 0 | 0 | 2.25 | 2022-03-02 15:03 | 2022-03-08 17:00 | 2022-03-08 07:00 | 2022-03-08 17:00 | 2022-03-08 09:15 |  |  | Attended site signed in completed jsa. Spoke with site FM about job on site. sensor keeps turning lights off every 2 hrs and staff getting annoyed by it. By passed sensor and left connected via switch on wall B12. Client happy and ***job completed***
MSA-DTWD | WA5203101 | 2 | AWB Co. | Carpark – Pump House - A Block - Footpath down by A Block lighting not working | Electrical | Lighting, External | 247.26 | Pass | Pass | -1 | -1 | 2.25 | 2022-03-03 10:42 | 2022-03-09 17:00 | 2022-03-04 07:00 | 2022-03-09 17:00 | 2022-03-04 09:15 |  | WCAPPR | Attended site signed in completed jsa. Spoke with Sharyn about works on site. reported outside car park lights not working. Pe cell tested fine all lights on. Override test lights turn on fine. As night shift security reported fault, proper handover needs to be done to dayshift about what lights are out. Advised site to take photos or draw on a site map for us to have a better focus area as all works when i test. Job will be left open and they will monitor over the week and call us early next week with a verdict.**Site have advised to close this out at cost to date. Email attached**
MSA-DTWD | WA5209204 | 1 | Equans Mechanical Services Australia | Block E - Ground - Kitchen - timer switch not working - replace/ repair | Refrigeration | Refrigerators | 358.91 | Pass | Pass | 0 | 0 | 2.25 | 2022-03-09 15:15 | 2022-03-10 17:00 | 2022-03-10 09:45 | 2022-03-10 17:00 | 2022-03-10 12:00 |  |  | PICKED UP NEW DEFROST TIMER, WENT TO SITE. SIGNED IN CHECKED IN WITH DENNIS.GATHERED TO AND EQUIPMENT. REMOVED OLD DEFROST TIMER AND REPLACED WITH NEW.TESTED OPERATION ALL OK MONITORED OPERATION CLEANED UP COMPLETED PAPERWORKAND SIGNED OUT
MSA-DTWD | WA5231785 | 3 | Assa Abloy Entrance Systems Aust P/L-WA | A block - L1 - Expo Area - Auto Door is opening & causing serious noise when fully open | Building | Automatic Doors | 540 | Pass | Pass | 0 | 0 | 2.25 | 2022-03-15 14:40 | 2022-03-22 17:00 | 2022-03-21 09:00 | 2022-03-22 17:00 | 2022-03-21 11:15 |  |  | Attended site and inspected auto door. Noted door operations and found banging. Required to reset the door and altered programing. Managed to reduce banging. Tested operations all OK.
MSA-DTWD | WA5239642 | 2 | Protek 24/7 Building & Maintenance | block 1 - North west entry door - Door closer catching on frame | Building | Doors | 215.125 | Pass | Pass | -1 | -1 | 2.25 | 2022-03-16 13:53 | 2022-03-21 17:00 | 2022-03-17 12:45 | 2022-03-21 17:00 | 2022-03-17 15:00 |  |  | Adjust door closer
MSA-DFES | WA5257628 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ablution Block - Light & Fan not working in room 1 of ATCO ablution block on Applied Training Ground | Electrical | General Electrical | 680.055 | Pass | Pass | 0 | 0 | 2.25 | 2022-03-17 13:06 | 2022-03-22 17:00 | 2022-03-22 13:45 | 2022-03-22 17:00 | 2022-03-22 16:00 |  |  | Arrived onsite at 13:45 to investigate light and fan not working located absolution blocks toilet #1. Found fan does not work due to fault and light is intermittently faulty. Will return to site with parts as fan is not a common part and will need to be ordered in. Left site at 16:00
MSA-DTWD | WA5287212 | 3 | AWB Co. | Level 2 - Library - 15 Fluro light not working | Electrical | Lighting, Internal | 833.71 | Pass | Pass | -1 | -1 | 2.25 | 2022-03-22 11:06 | 2022-03-29 17:00 | 2022-03-25 12:15 | 2022-03-29 17:00 | 2022-03-25 14:30 |  |  | Attended site and signed in. Completed paperwork. Located faulty lights in library. Took before picture. Counted up lights. Went to wholesaler to pick up parts. Replaced all faulty lights in library area. All lights now working as intended. Took after picture. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5288458 | 2 | Total Security Systems Pty Ltd | T block - Ground level - T054 / Massage 02 - G01 southwest faulty PIR needs replacing | Security | Monitoring | 518.06 | Fail | Fail | 1 | 1 | 2.25 | 2022-03-23 10:56 | 2022-03-28 17:00 | 2022-04-05 07:00 | 2022-03-28 17:00 | 2022-04-05 09:15 |  |  | 5/4/2022 - Michael Higginbotham - 7am to 9.15amChanged PIR, commissioned and tested. Told Christy to monitor for new alarms after 9am today. Left open for 2 weeks and no further issues received from this PIR.
MSA-DTWD | WA5307888 | 2 | AWB Co. | N100 - Repair power on East Wall not working in N100 | Electrical | General Electrical | 247.26 | Pass | Pass | -1 | -1 | 2.25 | 2022-04-08 07:14 | 2022-04-12 17:00 | 2022-04-08 13:15 | 2022-04-12 17:00 | 2022-04-08 15:30 |  |  | Attended site and signed in. Completed JSA. Located N100. Found gpo not working in middle of room. Traced cabling back to switchboard and found 3 x isolated circuits inside board. Tested to find the circuit needed. Reinstated to B1 RCD as per legend. Turned out power and tested gpo. All working okay. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA5308429 | 3 | AWB Co. | B Block - Level 3 - B2311 Fashion Classroom - GPO no longer functioning | Electrical | General Electrical | 438.51 | Pass | Pass | -1 | -1 | 2.25 | 2022-04-08 11:49 | 2022-04-19 17:00 | 2022-04-14 06:00 | 2022-04-19 17:00 | 2022-04-14 08:15 |  |  | Attended site signed in completed jsa. Located cleaner to open up B block as per site instructions. Found one broken power point. Replaced powerpoint. Also moved one gpo and installed as site is having desks put in around class. Also blanked one gpo off as per site instructions. All tested and works fine. *** job completed ***
MSA-DTWD | WA5318156 | 2 | AWB Co. | Room C105 - Lights not working | Electrical | Lighting, Internal | 337.26 | Pass | Pass | -1 | -1 | 2.25 | 2022-04-12 08:52 | 2022-04-19 17:00 | 2022-04-12 12:45 | 2022-04-19 17:00 | 2022-04-12 15:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located rooms with faulty lights and turned all switches off , went to board and tried to reset rcd, rcd was faulty, isolated board, removed old rcd and replaced with new, re energised board and tested rcd , went to rooms with lighting and tested all lights, all lights now working as intended, packed up, cleaned up, completed paperwork, signed out Job completed
MSA-DTWD | WA5323693 | 2 | AWB Co. | B207 - Replace broken AV Screen - new screen to replace at East perth | Building | General Building | 378.21 | Pass | Pass | 0 | 0 | 2.25 | 2022-04-13 10:16 | 2022-04-20 17:00 | 2022-04-19 14:15 | 2022-04-20 17:00 | 2022-04-19 16:30 |  |  | Attended site and signed in. Completed JSA. Spoke to Steve and he showed us where new projector screen was. Took it up to room. Took down old projector screen. Lofted new one up to see if it would fit. It wouldn’t. Had to moth both speakers outwards 200mm. Took down old brackets and installed new brackets for projector. Put up projector and re connected everything. Cleaned up. Took picture. Completed paperwork, signed out.** job complete ***
MSA-DTAG | WA5379169 | 2 | AWB Co. | Level 10 - Various Lights need replacing - see notes below | Electrical | Lighting, Internal | 324.77 | Pass | Pass | 0 | 0 | 2.25 | 2022-04-21 08:56 | 2022-04-27 17:00 | 2022-04-27 09:30 | 2022-04-27 17:00 | 2022-04-27 11:45 |  |  | Attended site and signed in, completed jsa,spoke with client about job, located all lights on level10 , went to wholesaler to pick up materials,returned to site, replaced all lights , packed up, cleaned up, completed paperwork,signed out, Job completed
MSA-DTWD | WA5382245 | 2 | Protek 24/7 Building & Maintenance | Campus Entry (Hayman Road) - Security Gatehouse - Door has dropped - Hard to close/lock | Building | Doors | 222.125 | Pass | Pass | 0 | 0 | 2.25 | 2022-04-26 16:21 | 2022-04-29 17:00 | 2022-04-27 09:30 | 2022-04-29 17:00 | 2022-04-27 11:45 |  |  | Repair dropped door
MSA-DTWD | WA5383274 | 2 | Lane's Plumbing | Right hand side Cistern is leaking | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | -1 | -1 | 2.25 | 2022-04-27 13:47 | 2022-05-02 17:00 | 2022-04-28 14:30 | 2022-05-02 17:00 | 2022-04-28 16:45 |  |  | job completed - replaced faulty cistern
MSA-DTWD | WA5385247 | 2 | M Construction (WA) | Q Block - 4 brackets need re fitting to wall - See notes | Building | General Building | 368.98 | Pass | Pass | 0 | 0 | 2.25 | 2022-04-29 08:37 | 2022-05-04 17:00 | 2022-05-03 13:30 | 2022-05-04 17:00 | 2022-05-03 15:45 |  |  | Fix 4 soup dispensers to walls
MSA-DTWD | WA5394193 | 2 | MR POTHOLE | Block 3 – Heavy Auto Workshop - Large crack and deterioration of concrete control joint | Paving & Roadworks | Concreting |  | Fail | Fail | 1 | 1 | 2.25 | 2022-05-04 13:42 | 2022-05-09 17:00 | 2022-05-18 09:30 | 2022-05-09 17:00 | 2022-05-18 11:45 |  |  | Repairs to cracks
MSA-DCA | WA5394718 | 1 | Protek 24/7 Building & Maintenance | Public walkway - on the museum side - paver has collapsed - please make safe | Building | General Building | 400.74 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-05 08:32 | 2022-05-06 17:00 | 2022-05-05 12:15 | 2022-05-06 17:00 | 2022-05-05 14:30 |  |  | Replaced collapsed Pavers
MSA-DTWD | WA5412930 | 2 | AWB Co. | Level 1 - B Block Carpark - Lights keep tripping out | Electrical | Lighting, External | 772.38 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-12 07:39 | 2022-05-16 17:00 | 2022-05-16 07:00 | 2022-05-16 17:00 | 2022-05-16 09:15 |  |  | Attended site and signed in. Located B block carpark lights. Got keys to switchboard. Investigated carpark lighting. Switched on overrides to control system and all lights work. Inspected pe cell to be working correctly. Inspected timer to be 5 hours behind in time. Timer has no battery reserve. Advised to replace timer to battery backup type. Tested circuits of carpark lights and found no faults present and RCD switching off at random types when the timer switches then off in auto mode. Supply and replaced both RCD to B1 and timer to carpark lights. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5413700 | 0 | Protek 24/7 Building & Maintenance | Water leaking through ingress into the storeroom | Roofing | Metal Roofing | 387.25 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-12 13:01 | 2022-05-12 15:01 | 2022-05-12 13:30 | 2022-05-12 17:01 | 2022-05-12 15:45 |  |  | repair water leak to storeroom
MSA-DCA | WA5454897 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Studio 3 & Large meeting room - Emergency Light exit faulty - flickering and broken | Electrical | Emergency & Exit Lighting | 572.4325 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-17 16:07 | 2022-05-18 17:00 | 2022-05-18 08:00 | 2022-05-18 17:00 | 2022-05-18 10:15 |  |  | Arrived on site at 0800 to investigate Level 1 - Studio 3 & Large meeting room - Emergency Light exit faulty - flickering and broken. Waited for staff to gain access to site, was required to sign in down the road in order to get key. Obtained keys and headed back to site. Found 2 x exits requiring replacement, left site at 0845 and picked up gear from wholesaler. Returned to site at 0915 and replaced/reenergised both exits. Notified staff of outcome left site to return keys and signed out at 1015.
MSA-DTWD | WA5468952 | 1 | Protek 24/7 Building & Maintenance | F Block - F47 - Roof leak in centre of room | Building | General Building | 463.75 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-20 13:47 | 2022-05-23 17:00 | 2022-05-23 07:00 | 2022-05-23 17:00 | 2022-05-23 09:15 |  |  | Repair Roof leak - F Block - F47
MSA-DTAG | WA5468996 | 1 | FSA (WA) Pty Ltd | Retrospective Work Order - Pump Room - DO NOT ATTEND - see notes below | Fire Protection Services | Fire Protection - Monitor System | 381.79 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-19 18:15 | 2022-05-20 17:00 | 2022-05-19 19:00 | 2022-05-20 17:00 | 2022-05-19 21:15 | 1 |  | Arrived on site, sprinkler system pumps isolated by fire brigadeJacking pump not working properly in auto position, isolated and investigated loose connection found on control circuit, reconnected working as it should now.pumped system back up to 1050kpa, losing pressure, system drops to 800kpa in 15 min.Sprinkler systems isolated in the hydrant pump room, system still dropping. Followed pipe work in the sub basement from sprinkler pump room to hydrant pump room no visible leaks along pipework. water visible below system 5 under the false floor in the hydrant pump room. system made safe to not activate alarm, sprinkler fitter to attend friday morning to locate and rectify.
MSA-DTAG | WA5470510 | 2 | Midolo Building Services | Level 15 - Male Toilet - Doors not closing properly | Building | Doors | 780.89 | Fail | Fail | 0 | 0 | 2.25 | 2022-05-23 10:32 | 2022-05-26 17:00 | 2022-05-27 11:15 | 2022-05-26 17:00 | 2022-05-27 13:30 |  |  | adjustments made & new door closer installed
MSA-DTWD | WA5470541 | 2 | Protek 24/7 Building & Maintenance | E47 Disabled Toilets - Water Leak | Roofing | Roof Safety Systems | 387.25 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-23 10:52 | 2022-05-26 17:00 | 2022-05-25 13:45 | 2022-05-26 17:00 | 2022-05-25 16:00 |  |  | Attended Water Leak - did not proceed with Repair
MSA-DFES | WA5471287 | 3 | Water2water Pty Ltd | Outside Gym - Drink Fountain is leaking from Bottle Fille | Plumbing & Drainage | Water | 388.8975 | Pass | Pass | -1 | -1 | 2.25 | 2022-05-23 12:31 | 2022-05-30 17:00 | 2022-05-25 09:00 | 2022-05-30 17:00 | 2022-05-25 11:15 |  |  | REPLACED FAUCET, TUBING & ISOLATION VALVE. ALL OKAY
MSA-DTWD | WA5479230 | 2 | AWB Co. | Kendrew- E-Block ceiling man hole covers broken in stores and deli area need replacing | Roofing | Metal Roofing | 241.985 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-27 08:14 | 2022-06-01 17:00 | 2022-05-30 12:00 | 2022-06-01 17:00 | 2022-05-30 14:15 |  |  | Cut and Installed 2 man hole covers
MSA-DTWD | WA5479769 | 3 | AWB Co. | J Block - Sth wall - 5 x lights out | Electrical | Lighting, Internal | 728.2825 | Pass | Pass | -1 | -1 | 2.25 | 2022-05-27 11:39 | 2022-06-03 17:00 | 2022-05-30 12:30 | 2022-06-03 17:00 | 2022-05-30 14:45 |  |  | Attended site and signed in. Completed JSA. Located J block lights not working. Found out what parts we need. Left site to pick up parts. Returned and replaced 5x lights not working with new LED fittings. Also replaced 1x tube and starter supplied by site. Disposed of all rubbish. Tested to make sure they’re all working correctly. **job complete**
MSA-DTAG | WA5481219 | 2 | AHS Services WA Pty Ltd (Anchor) | Ceiling in Centre of office - Water pipe rusted and broken in ceiling space, has caused water damage | Plumbing & Drainage | Water | 393.245 | Pass | Pass | 0 | 0 | 2.25 | 2022-05-30 11:26 | 2022-06-02 17:00 | 2022-06-01 10:45 | 2022-06-02 17:00 | 2022-06-01 13:00 |  |  | Resealed inspection opening on sewer bend that was causing a small drip to the ceiling below.
MSA-DTAG | WA5481640 | 3 | FSA (WA) Pty Ltd | RETROSPECTOVE WORKORDER - SEE DETAILS BELOW | Fire Protection Services | Fire Protection - Monitor System | 381.79 | Pass | Pass | -1 | -1 | 2.25 | 2022-05-14 12:45 | 2022-05-20 17:00 | 2022-05-14 13:20 | 2022-05-20 17:00 | 2022-05-14 15:35 |  |  | After hours call out to isolate and de-isolate zones for hot works in ceiling
MSA-DTWD | WA5496243 | 1 | AWB Co. | Dust extraction pipe leaking water from the roof | Roofing | Metal Roofing | 510.82 | Pass | Pass | 0 | 0 | 2.25 | 2022-06-09 08:36 | 2022-06-10 17:00 | 2022-06-10 07:00 | 2022-06-10 17:00 | 2022-06-10 09:15 |  |  | Two leaks - one from large round duct work. Repaired with butane tape and resealed base flashing. Second leak from compression pipework repaired. Job complete.
MSA-DTWD | WA5549179 | 3 | Securex Security Systems & Services | CCTV not working | Security | CCTV Surveillance | 231 | Fail | Fail | 4 | 4 | 2.25 | 2022-06-17 14:06 | 2022-06-24 17:00 | 2022-07-19 09:00 | 2022-06-24 17:00 | 2022-07-19 11:15 |  | WCAPPR | There was a delay waiting for the IT guys to be ready before being able to do this job.19/07/2022, 900-1115Worked along side Micheal in getting the cameras and NVR changed over to the new IP range. 3 cameras aren’tworking Micheal n facility have decided to leave it n will look at replacing at a later date.
MSA-DTWD | WA5567766 | 2 | AWB Co. | LED batten light not working | Electrical | Lighting, Internal | 268.93 | Pass | Pass | 0 | 0 | 2.25 | 2022-06-24 12:11 | 2022-06-29 17:00 | 2022-06-29 09:45 | 2022-06-29 17:00 | 2022-06-29 12:00 |  |  | Attended site and signed in. liaised with site about works going ahead. Located room E58. Found faulty batten over sink. Supplied and replaced with new LED batten. Tested all ok. Cleaned up site. Signed out. **job complete**
MSA-DCA | WA5578502 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Rear of Art Gallery between wall and Roe St - Testing of backflow valve | Plumbing & Drainage | Water | 272.8525 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-01 12:32 | 2022-07-04 17:00 | 2022-07-01 12:40 | 2022-07-04 17:00 | 2022-07-01 14:55 |  |  | Tested RPZD valve on boundary,valve started leaking constantly and had to do a temp repair to get water to the building. Valve needs repairs which will be done on different work order.
MSA-DCA | WA5580728 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Level 4 - Air conditioning humidity alarm and alarm from steam generators active. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 514.6375 | Fail | Fail | 0 | 0 | 2.25 | 2022-07-02 17:55 | 2022-07-02 19:55 | 2022-07-02 20:15 | 2022-07-02 21:55 | 2022-07-02 22:30 |  |  | Checked out BMS.Found Ro plant, steam generators and humidifiers in fault.Filled water tanks manually and manualled the RO plant on via bms.Reset steam generators and all humidifiers.All OK.
MSA-DCA | WA5584737 | 2 | FCT SURFACE CLEANING | Ground Floor Exterior -Gantry (Murray St side) | Cleaning | Graffiti |  | Fail | Fail | 1 | 1 | 2.25 | 2022-07-05 09:49 | 2022-07-08 17:00 | 2022-07-13 06:30 | 2022-07-08 17:00 | 2022-07-13 08:45 |  |  | Attended site and carried out pressure washing of paving and graffiti removal from barricades.
MSA-DCA | WA5585150 | 0 | Assa Abloy Entrance Systems Aust P/L-WA | loading dock, roller door 1 of it is run and will not close | Building | Doors | 930 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-05 12:52 | 2022-07-05 14:52 | 2022-07-05 14:15 | 2022-07-05 16:52 | 2022-07-05 16:30 |  |  | Attended site and inspected roller shutter, noted shutter impacted by truck and bottom rail and slats bent and jamming door operations. Required to cut bottom rail and slats and bend straight to allow shutter operations. Quoted 17/10/2022 to replace bottom rail and slats
MSA-DCA | WA5608684 | 3 | Earth & Water Pty Ltd | Amphitheatre -Leaking sprinkler. Please investigate | Equipment | Gardening / Landscaping Equipment |  | Pass | Pass | -1 | -1 | 2.25 | 2022-07-13 10:54 | 2022-07-20 17:00 | 2022-07-14 10:15 | 2022-07-20 17:00 | 2022-07-14 12:30 |  |  | Ran zone 13- takes approx 2 minutes for the sprinklers to start once the zone is running. Once zone is turned off; takes around 4minutes for the sprinklers to turn off; even though the solenoid valve is clicking shut.I expect this to be because of the downward slop of this zone. The bottom sprinkler stays on the longest.After all of the water was drained out of the line, the sprinkler isn't leaking any water.
MSA-DTWD | WA5609625 | 2 | AWB Co. | Faulty GPOS | Electrical | Lighting, Internal | 266.0725 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-13 15:20 | 2022-07-18 17:00 | 2022-07-18 10:15 | 2022-07-18 17:00 | 2022-07-18 12:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, fm said 2 RCDs were tripping when compressor was plugged in, went to board and found RCDs (r110 and r112) traced cables back to RCDs and found neutrals were crossed, fixed neutrals and tested both circuits, all working as intended , completed paperwork, signed out **job completed**
MSA-DTWD | WA5655812 | 0 | Techworks Plumbing | student toilets blocked | Plumbing & Drainage | HWS/Units Electric & Gas | 344.64 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-18 10:38 | 2022-07-18 12:38 | 2022-07-18 10:45 | 2022-07-18 14:38 | 2022-07-18 13:00 |  |  | attended site and signed in at office then spoke to the facilities manager, he showed me where block f was .all the drains were blocked in the block f toilets and coming up out of the floor waste.I tried using a plunger to unblock the toilets but it would just come up out the floor wastethe faculties manager told gave me a rough location of an IO that might be under the ground, I dug around but could not find it. Found other IOS but they weren’t connected to that drain.We went and tried plunging the toilets again and eventually got it after unblocking we ran water down all the drains and I put some momar bowl guard down the urinal drain the clear any debris.the facilities manager asked me if I could plunge all the sinks as well because they were slow to drain.and he also asked me to sort out a toilet that didn’t have a full flush button working, so I sorted that was just an issue with the air hoses.after I was happy the drains were fully free I signed out and got a signature s
MSA-DTAG | WA5669361 | 2 | AWB Co. | Level 10 - Lift Area - Lights need replacing in lift lobby area | Electrical | Lighting, Internal | 462.48 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-20 07:07 | 2022-07-22 17:00 | 2022-07-21 13:15 | 2022-07-22 17:00 | 2022-07-21 15:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about works, counted up materials and went to wholesaler, returned to site , replaced lamps in front of lift and both wedding rooms as per fm request, replaced downlight in wedding room with new led , all lights now working as intended, completed paperwork , packed up, signed out **job completed **
MSA-DTWD | WA5672293 | 1 | ADVANCED LOCK & KEY | Door lock mech broken and cleaners unable to access equipment | Security | Locksmith | 217 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-20 09:32 | 2022-07-21 17:00 | 2022-07-20 12:45 | 2022-07-21 17:00 | 2022-07-20 15:00 |  |  | Attend site to repair damaged lock on refuse store
MSA-DTWD | WA5673131 | 2 | AWB Co. | Tile Cutting Room - exhaust extraction fan faulty | Electrical | General Electrical | 406.99 | Pass | Pass | 0 | 0 | 2.25 | 2022-07-20 12:27 | 2022-07-25 17:00 | 2022-07-25 12:45 | 2022-07-25 17:00 | 2022-07-25 15:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about issue. Fm explained he wanted to find out if van was working to full capacity. Turned fan on and tested suction. Inspected ambient air vent. Inspected exhaust fan ducting. Inspected fan blades. Everything all clear. Found 10mm of built up dust around ambient air inlet. Told fm and told him it’s an issue as fresh air going into room will have dust in it. Fan seems to be sucking to full capacity as everything checked was fine. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5681224 | 3 | AWB Co. | L10-Registry of Births, Deaths and Marriages-various lights out-see notes | Electrical | Lighting, Internal | 354.7325 | Pass | Pass | -1 | -1 | 2.25 | 2022-07-28 10:06 | 2022-08-04 17:00 | 2022-07-29 10:45 | 2022-08-04 17:00 | 2022-07-29 13:00 |  |  | Attended site and signed in. Completed JSA. Located areas of lighting needing repairs. Supply and replace lamps to all fittings reported out. 1 fitting had lost it clips and needed to be refitted and secured into ceiling. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5683079 | 2 | Lane's Plumbing | Faulty Dishwasher | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 2.25 | 2022-07-29 15:58 | 2022-08-03 17:00 | 2022-08-01 11:15 | 2022-08-03 17:00 | 2022-08-01 13:30 |  |  | Repairs to dishwasher
MSA-DFES | WA5687147 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | L1 FF toilets-RHS urinal is slow to drain | Plumbing & Drainage | Drainage | 333.74 | Pass | Pass | -1 | -1 | 2.25 | 2022-08-01 10:05 | 2022-08-08 17:00 | 2022-08-03 11:00 | 2022-08-08 17:00 | 2022-08-03 13:15 |  |  | Unblocked the urinals.
MSA-DCA | WA5688080 | 1 | Protek 24/7 Building & Maintenance | Fault description: The “ opening latch ‘ of the Electrical cover [ in the Amphitheatre ] broken | Building | Foundations | 421.79 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-02 09:24 | 2022-08-03 17:00 | 2022-08-03 07:00 | 2022-08-03 17:00 | 2022-08-03 09:15 |  |  | installed a metal plate patch over the broken latch and secured it to the cover with reverts.
MSA-DTWD | WA5693339 | 2 | AWB Co. | Hallway - Flickering Fluoros - Tombstones are broken | Electrical | Lighting, Internal | 266.0725 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-04 11:32 | 2022-08-09 17:00 | 2022-08-09 13:30 | 2022-08-09 17:00 | 2022-08-09 15:45 |  |  | Attended site and signed in. Completed JSA. Located faulty light in A block in the staff area. Found the lights to be all broken tombstones. Used site supplied stock to replace as many tombstones and tubes as possible. 8 x starter ends and 9 x single ends. Site has run out of tombstones and there is more lamps to go but not enough parts. Have advised site that they need more parts so we can replace the rest of the lights. Requires minimum of 20 of each end for the rest of this area only. Lights I have fixed are all working and okay. Signed out. Job complete
MSA-DTWD | WA5694516 | 3 | AWB Co. | Correct faulty wiring to switches - 213 | Electrical | General Electrical | 427.26 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-05 11:04 | 2022-08-12 17:00 | 2022-08-12 13:15 | 2022-08-12 17:00 | 2022-08-12 15:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located room and pushed up panels around lights to see if a cable was linking lights, couldn’t find a cable doing that, located feed for switch one and ran cable to front 3 lights to have them switch on separately to the back lights , tested,lights and working as intended, cleaned up, packed up, completed paperwork, signed out , *job completed*
MSA-DFES | WA5695868 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - opposite service desk - flashing/flickering light | Electrical | General Electrical | 480.675 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-08 08:14 | 2022-08-09 17:00 | 2022-08-08 10:45 | 2022-08-09 17:00 | 2022-08-08 13:00 |  |  | Arrived onsite at 10:45 to investigate light flickering located IT help desk. Found 2 x lights not working out of 3. Found nearestlight that worked had already been swapped to a ROBUS LED downlight. Collected 2 x ROBUS LED downlights fromwholesaler to make all the same. Upon reconnecting 2 faulty lights worker located near lights notified that lights were nowtoo bright as only one out of threee previously worked. All lights have now been repaired and work fine but too bright, willquote to install dimmer switch to only the 3 x lights affecting worker. Will need to return with parts to fix. Left site at 13:00
MSA-DTWD | WA5734736 | 1 | AWB Co. | A230 replace light tubes not working | Electrical | Lighting, Internal | 691.5725 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-16 09:08 | 2022-08-17 17:00 | 2022-08-16 12:15 | 2022-08-17 17:00 | 2022-08-16 14:30 |  |  | Job complete
MSA-DTWD | WA5790631 | 1 | Australian Airconditioning Services Pty Ltd | A/C unit making loud noise | Air Conditioning | Room Air Conditioners | 325.49 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-22 11:39 | 2022-08-23 17:00 | 2022-08-23 07:45 | 2022-08-23 17:00 | 2022-08-23 10:00 |  |  | Suspect sound if defrost activating. Defrost is activating more often than normal as only one compressor is currently operating causing compressor to run for longer periods. New compressor has already been quoted.
MSA-DFES | WA5798365 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - Male toilets - Cubicle 2 broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 735.6 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-29 13:53 | 2022-09-01 17:00 | 2022-08-31 13:15 | 2022-09-01 17:00 | 2022-08-31 15:30 |  |  | Had install a new toilet seat located level 2 male toilets cubicle 2 had to pick up from Reece
MSA-DFES | WA5798605 | 3 | AWB Co. | Driveway - Down pipe in driveway is damaged | Roofing | Guttering | 639.555 | Pass | Pass | 0 | 0 | 2.25 | 2022-08-29 16:09 | 2022-09-05 17:00 | 2022-09-05 12:15 | 2022-09-05 17:00 | 2022-09-05 14:30 |  |  | Attended and removed damaged copper downpipe. Sourced materials and replaced downpipe.no one on site at station to sign
MSA-DTWD | WA5800645 | 3 | GRAFFITI FORCE PTY LTD | Graffiti at height east end | Cleaning | Graffiti | 486.5 | Fail | Fail | 3 | 3 | 2.25 | 2022-08-31 11:24 | 2022-09-07 17:00 | 2022-09-27 11:45 | 2022-09-07 17:00 | 2022-09-27 14:00 |  |  | REMOVAL OF GRAFFITI FROM EAST END ROOF.
MSA-DFES | WA5861704 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | all of station, have lost power half gpo's,auto gates not working | Electrical | General Electrical | 268.185 | Pass | Pass | 0 | 0 | 2.25 | 2022-09-13 10:47 | 2022-09-13 12:47 | 2022-09-13 11:15 | 2022-09-13 14:47 | 2022-09-13 13:30 |  |  | Arrived onsite at 11:15 to investigate no power to station. Found there had been a crash nearby affecting power poles and various western power outages affecting supply to station. Confirmed issue is not site related and no way to restore all power by means of temporary fixes. Found 1/3 power at station is working and ran supply for internet and phones to a point that works to keep phones running. Power keeps cycling in and out of what works and doesn’t work and isn’t much help until western power has fully cleared the fault on the network. Notified staff of all relevant information and left site at 13:30
MSA-DFES | WA5880498 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilet - Sink tap is leaking -See notes below | Plumbing & Drainage | Water | 295.06 | Pass | Pass | 0 | 0 | 2.25 | 2022-09-15 13:43 | 2022-09-22 17:00 | 2022-09-19 14:30 | 2022-09-22 17:00 | 2022-09-19 16:45 |  |  | All complete
MSA-DFES | WA5962616 | 2 | AWB Co. | PPC Store - Appliance Bay - Forward door jamming rear door has loose handle | Building | Doors | 347.1525 | Fail | Fail | 0 | 0 | 2.25 | 2022-09-19 15:48 | 2022-09-22 17:00 | 2022-09-23 10:45 | 2022-09-22 17:00 | 2022-09-23 13:00 |  |  | repair door and track
MSA-DTWD | WA5978350 | 3 | AWB Co. | L3 Foyer & West Corridor - Foyer 3 x downlights Corridor 6 x Fluoro’s | Electrical | Lighting, Internal | 894.49 | Pass | Pass | 0 | 0 | 2.25 | 2022-09-28 10:24 | 2022-10-05 17:00 | 2022-10-03 14:00 | 2022-10-05 17:00 | 2022-10-03 16:15 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Counted up parts we needed. Went to wholesaler. Returned to site and changed over all faulty lighting with new LED. took pictures. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5982804 | 3 | COMMERCIAL PLUMBING AND GAS | Room CG47A -The toilet flush continues to run slowly after flush | Plumbing & Drainage | Toilets/Cisterns | 711.7325 | Pass | Pass | 0 | 0 | 2.25 | 2022-09-30 14:39 | 2022-10-07 17:00 | 2022-10-06 14:45 | 2022-10-07 17:00 | 2022-10-06 17:00 |  |  | replaced invisi cistern, refixed button assembly
MSA-DFES | WA5987523 | 0 | Securex Security Systems & Services | Main Administration Building - Electric fencing keeps alarming - the whole fence | Security | Monitoring | 470 | Pass | Fail | 0 | 0 | 2.25 | 2022-10-03 12:02 | 2022-10-03 14:02 | 2022-10-03 14:00 | 2022-10-03 16:02 | 2022-10-03 16:15 |  |  | 03/10/2022, 1400-1615Electric Fence zone 68 alarming . Check Tecom panel , Check Electric Fence energiser . Stuck in alarm . Inspect whole academy electric fence . Found Truck has reverse and hit electric fence . Got them to move afire truck . All alarms restored . Will do PFM docket in office and email client . Completed
MSA-DTWD | WA5994819 | 2 | BAKE-QUIP PTY LTD | Two gas ovens and stovetops don't have gas coming out-see notes | Plumbing & Drainage | Gas | 470.5 | Pass | Pass | 0 | 0 | 2.25 | 2022-10-06 08:59 | 2022-10-11 17:00 | 2022-10-11 07:45 | 2022-10-11 17:00 | 2022-10-11 10:00 |  |  | Refer to service report
MSA-DTWD | WA6105969 | 2 | AWB Co. | Re fix white board and pin up boards in D Block | Building | General Building | 395.6725 | Pass | Pass | 0 | 0 | 2.25 | 2022-10-20 07:42 | 2022-10-24 17:00 | 2022-10-24 14:45 | 2022-10-24 17:00 | 2022-10-24 17:00 |  |  | Works completed
MSA-DTWD | WA6111457 | 3 | AWB Co. | E 208 faulty Door handle | Building | Doors | 259.4025 | Pass | Pass | 0 | 0 | 2.25 | 2022-10-21 07:35 | 2022-10-27 17:00 | 2022-10-24 12:30 | 2022-10-27 17:00 | 2022-10-24 14:45 |  |  | door works completed
MSA-DTWD | WA6127388 | 2 | AWB Co. | Roof leak in D Block passageway level 1 | Roofing | Metal Roofing | 489.145 | Pass | Pass | 0 | 0 | 2.25 | 2022-10-26 07:03 | 2022-10-28 17:00 | 2022-10-27 13:00 | 2022-10-28 17:00 | 2022-10-27 15:15 |  |  | Works completed
MSA-DCA | WA6132146 | 3 | FCT SURFACE CLEANING | PCC exterior - Graffiti in various locations - see notes below | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2.25 | 2022-10-31 11:59 | 2022-11-07 17:00 | 2022-11-04 09:30 | 2022-11-07 17:00 | 2022-11-04 11:45 |  |  | Removal of graffiti
MSA-DTAG | WA6144701 | 3 | Midolo Building Services | Court 35 - Several seat screws are missing or loose - See notes | Furniture | Office Furniture | 277.68 | Pass | Pass | 0 | 0 | 2.25 | 2022-11-02 08:42 | 2022-11-09 17:00 | 2022-11-08 07:00 | 2022-11-09 17:00 | 2022-11-08 09:15 |  |  | CHAIRS RE SECURED
MSA-DCA | WA6145563 | 3 | Protek 24/7 Building & Maintenance | Ground - Courtyard Door, Stairwell 1 - Fire Door is swollen and doesn’t close properly | Building | Fire Door | 427.63 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-02 12:45 | 2022-11-09 17:00 | 2022-11-04 09:15 | 2022-11-09 17:00 | 2022-11-04 11:30 |  |  | Fixed more rivets into bottom channel.Eased hinges so the door doesn’t bind on the latch side
MSA-DTWD | WA6147968 | 2 | GRAFFITI FORCE PTY LTD | G24 Exterior - Graffiti painted on metal sheeting on Fleet Street shed wall | Cleaning | Graffiti | 486.5 | Fail | Fail | 0 | 0 | 2.25 | 2022-11-03 11:12 | 2022-11-08 17:00 | 2022-11-11 07:00 | 2022-11-08 17:00 | 2022-11-11 09:15 |  |  | REMOVAL OF GRAFFITI FROM METAL SHEETING ON G24
MSA-DFES | WA6149052 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level 2-male toilet-hand dryer not operating correctly | Electrical | General Electrical | 268.185 | Pass | Pass | 0 | 0 | 2.25 | 2022-11-04 11:50 | 2022-11-07 17:00 | 2022-11-04 13:00 | 2022-11-07 17:00 | 2022-11-04 15:15 |  | WACCES | Joel Harvey (04/11/2022) - Work NoteOnsite to investigate faulty hand dryer on level 2 in male toilets. Found there to be something wrong with the sensor/timer in the unit causing it to come on and off whilst your hands are underneath. Upon further inspection of other hand dryers I found there to be another one on level 1 which was having the same issue. Will need to return to install new units/parts.Sensor/timer is located inside a CPU which is will not allow for part replacements nor can parts be ordered for it as the units are quite old.I have spoken to Beau in regards to getting/installing 2x new units in LEVEL 1&2 MALE TOILETS.Beau has also spoken to Deb in about the issue and will be sorting out parts.Have notified Deb of the issue and our plan forward and so has Beau.
MSA-DTAG | WA6156858 | 3 | AWB Co. | Courts 3 & 4 stairwell light has failed - see notes below | Electrical | Lighting, Internal | 266.0725 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-09 11:12 | 2022-11-16 17:00 | 2022-11-11 11:30 | 2022-11-16 17:00 | 2022-11-11 13:45 |  |  | Job complete
MSA-DTWD | WA6157263 | 2 | BJ SYSTEMS | Ground Level - Security panel - Battery failures on 1380 - 067 & 073 | Security | Security Management System | 645 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-09 14:35 | 2022-11-14 17:00 | 2022-11-10 10:00 | 2022-11-14 17:00 | 2022-11-10 12:15 |  |  | Replaced dead batteries in DGP's 1, 3, 9 and PSU adjacent to DGP 3. Tested with ED Sec, all ok
MSA-DTWD | WA6158562 | 2 | AWB Co. | Car Park - Car Park lighting not operating | Electrical | Lighting, External | 406.99 | Pass | Pass | 0 | 0 | 2.25 | 2022-11-10 07:09 | 2022-11-14 17:00 | 2022-11-14 10:45 | 2022-11-14 17:00 | 2022-11-14 13:00 |  |  | Went to Kendrew got keys and signed in. Drove to McCarty. Completed jsa. Went around all boards to try and find timer for carpark lighting. Was unsuccessful in doing that. Found a stand alone dB. Didn’t have key for it. Had to go back to Kendrew and get special key. Came back and opened up dB. Located timer and read instructions. Set timer to correct times etc. time on timer was out by 4 hours. Adjusted time to correct time. Working as intended. Took picture. Completed paperwork. Signed out.Job complete
MSA-DFES | WA6179112 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Applied Training - Electric Fence - number of plastic insulators have melted and will need replacing | Electrical | General Electrical | 268.185 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-14 16:04 | 2022-11-21 17:00 | 2022-11-15 13:15 | 2022-11-21 17:00 | 2022-11-15 15:30 |  |  | Arrived on site at 1315 to attend Applied Training - Electric Fence - number of plastic insulators have melted and will needreplacing. Located relevant staff aware of situation and trailed perimeter to assess defects along electric fence. Identifiedseveral area’s requiring re-insulating. Sought permission and further details on restrictions of works to be carried out. Wasmade aware works were to be completed by necessary contractors. Informed staff of situation and left site at 1530.
MSA-DTAG | WA6190311 | 3 | Total Security Systems Pty Ltd | Videowall auto log on not working | Security | Monitoring | 232 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-16 07:13 | 2022-11-22 17:00 | 2022-11-16 15:00 | 2022-11-22 17:00 | 2022-11-16 17:15 |  |  | 16/11/2022 - Comtec Contractor - KarrathaUser password was incorrect, logged into NVR and changed user's password.
MSA-DTAG | WA6190317 | 3 | Total Security Systems Pty Ltd | Time sync issue present across all CCTV devices, error in IV NVMS | Security | Monitoring | 232 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-16 07:32 | 2022-11-22 17:00 | 2022-11-16 15:00 | 2022-11-22 17:00 | 2022-11-16 17:15 |  |  | 16/11/2022 - Comtec KarrathaTime sync alerts due to date & time incorrect. Change time on NVR and PC. Jose from TSS assisted. All working now.
MSA-DTAG | WA6190320 | 3 | Total Security Systems Pty Ltd | Unable to log into Gallagher from maintenance terminal - See Notes | Security | Monitoring | 232 | Pass | Pass | -1 | -1 | 2.25 | 2022-11-16 07:35 | 2022-11-22 17:00 | 2022-11-16 15:00 | 2022-11-22 17:00 | 2022-11-16 17:15 |  |  | 16/11/2022 - Comtec KarrathaNeeded new licence from Gallagher, this has been applied.
MSA-DTWD | WA6254054 | 2 | AWB Co. | R020-Repair holes in R block roof | Roofing | Metal Roofing | 489.145 | Pass | Pass | 0 | 0 | 2.25 | 2022-11-22 14:41 | 2022-11-25 17:00 | 2022-11-25 12:00 | 2022-11-25 17:00 | 2022-11-25 14:15 |  |  | Mason Burdon (25/11/2022) - Work NoteAttended site and completed jsa, we had a inspection with facility manager and then accessed the roof. We discovered 4 safety anchor points that had been removed then very poorly sealed up afterwards. Also found multiple decktites that where poorly sealed. We cleaned up and re sealed all faulty areas.Job completed
MSA-DTWD | WA6257168 | 1 | Australian Airconditioning Services Pty Ltd | air con has gone into fault | Air Conditioning | Room Air Conditioners | 325.49 | Pass | Pass | 0 | 0 | 2.25 | 2022-11-24 12:34 | 2022-11-25 17:00 | 2022-11-24 13:45 | 2022-11-25 17:00 | 2022-11-24 16:00 |  |  | complete
MSA-DTWD | WA6299901 | 2 | Lane's Plumbing | Laundry - Leaking drain under trough | Plumbing & Drainage | Drainage |  | Pass | Pass | -1 | -1 | 2.25 | 2022-12-02 08:25 | 2022-12-07 17:00 | 2022-12-02 09:45 | 2022-12-07 17:00 | 2022-12-02 12:00 |  |  | Repairs to leak
MSA-DTWD | WA6375599 | 2 | JEM Carpentry | Roof - Faulty gutter | Roofing | Guttering |  | Pass | Pass | -1 | -1 | 2.25 | 2022-12-15 09:07 | 2022-12-20 17:00 | 2022-12-15 09:15 | 2022-12-20 17:00 | 2022-12-15 11:30 |  |  | Gutter cleaning
MSA-DFES | WA6376431 | 2 | Protek 24/7 Building & Maintenance | Ground - Training room - Roof leak - see notes | Roofing | Tiled Roofing | 415.13 | Fail | Fail | 0 | 0 | 2.25 | 2022-12-15 15:10 | 2022-12-20 17:00 | 2022-12-21 11:45 | 2022-12-20 17:00 | 2022-12-21 14:00 |  |  | We hose tested various area of roof and couldn’t make leak at all. Found rust hole and couldn’t make leak, due to insulation it could take a few hours for leak to occur.
MSA-DFES | WA6384357 | 0 | Anvil Doors | Ground Floor - Engine Room - Roller door has electrical fault - Not going up | Building | Automatic Doors | 723.5 | Fail | Fail | 0 | 0 | 2.25 | 2022-12-21 08:13 | 2022-12-21 10:13 | 2022-12-21 12:16 | 2022-12-21 12:13 | 2022-12-21 14:31 |  |  | checked all doors - found all ok - could be remotes
MSA-DTWD | WA6401209 | 2 | COMMERCIAL PLUMBING AND GAS | Level 2 & 3 - Male and female toilets have seven broken seats | Plumbing & Drainage | Toilets/Cisterns | 747.6525 | Fail | Fail | 1 | 1 | 2.25 | 2023-01-04 09:52 | 2023-01-09 17:00 | 2023-01-16 06:30 | 2023-01-09 17:00 | 2023-01-16 08:45
MSA-DTWD | WA6482440 | 3 | AWB Co. | A block - Admin area - electric hot water system not working | Plumbing & Drainage | HWS/Units Electric & Gas | 338.1925 | Pass | Pass | 0 | 0 | 2.25 | 2023-01-18 10:26 | 2023-01-25 17:00 | 2023-01-24 07:00 | 2023-01-25 17:00 | 2023-01-24 09:15
MSA-DFES | WA6482503 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Balcony light is out 2x globes | Electrical | General Electrical | 475.055 | Pass | Pass | 0 | 0 | 2.25 | 2023-01-18 10:53 | 2023-01-25 17:00 | 2023-01-23 11:45 | 2023-01-25 17:00 | 2023-01-23 14:00
MSA-DTWD | WA6538175 | 2 | AWB Co. | Rectify faulty GPO's | Electrical | General Electrical | 629.54 | Pass | Pass | 0 | 0 | 2.25 | 2023-02-07 15:42 | 2023-02-10 17:00 | 2023-02-09 08:45 | 2023-02-10 17:00 | 2023-02-09 11:00
MSA-DCA | WA6540062 | 1 | Dormakaba Australia Pty Ltd | Level 4 - West Side leading to rooftop - Glass sliding door is banging shut (See notes) | Building | Doors |  | Pass | Pass | 0 | 0 | 2.25 | 2023-02-09 07:56 | 2023-02-09 17:00 | 2023-02-09 12:00 | 2023-02-09 17:00 | 2023-02-09 14:15
MSA-DTWD | WA6543982 | 2 | AHS Services WA Pty Ltd (Anchor) | Male toilets West - Water leaking from toilet onto floor | Plumbing & Drainage | Toilets/Cisterns | 280.2275 | Pass | Pass | -1 | -1 | 2.25 | 2023-02-10 09:15 | 2023-02-15 17:00 | 2023-02-10 10:00 | 2023-02-15 17:00 | 2023-02-10 12:15
MSA-DTWD | WA6573420 | 2 | GRAFFITI FORCE PTY LTD | Various locations - Graffiti | Cleaning | Graffiti | 363.28 | Pass | Pass | 0 | 0 | 2.25 | 2023-02-14 13:17 | 2023-02-17 17:00 | 2023-02-16 09:00 | 2023-02-17 17:00 | 2023-02-16 11:15
MSA-DTWD | WA6649890 | 1 | GRAFFITI FORCE PTY LTD | Graffiti off L3 Balcony above Creche yard | Cleaning | Graffiti | 460.5 | Fail | Fail | 0 | 0 | 2.25 | 2023-02-20 07:50 | 2023-02-20 17:00 | 2023-02-21 10:05 | 2023-02-20 17:00 | 2023-02-21 12:20
MSA-DTWD | WA6668216 | 1 | AHS Services WA Pty Ltd (Anchor) | Toilet flush button not working - Female toilet flush button not working | Plumbing & Drainage | Toilets/Cisterns | 264.6675 | Pass | Pass | 0 | 0 | 2.25 | 2023-02-22 07:31 | 2023-02-22 17:00 | 2023-02-22 08:55 | 2023-02-22 17:00 | 2023-02-22 11:10
MSA-DTWD | WA6690873 | 2 | COMMERCIAL PLUMBING AND GAS | Blocked grease trap | Plumbing & Drainage | Drainage |  | Pass | Pass | -1 | -1 | 2.25 | 2023-03-09 13:12 | 2023-03-14 17:00 | 2023-03-09 16:15 | 2023-03-14 17:00 | 2023-03-09 18:30
MSA-DCA | WA6393054 | 1 | Techworks Electrical | Ground level - Damaged light | Electrical | General Electrical | 411.46 | Pass | Pass | 0 | 0 | 2.2333 | 2022-12-28 09:12 | 2022-12-29 17:00 | 2022-12-29 12:36 | 2022-12-29 17:00 | 2022-12-29 14:50 |  |  | Replaced Vandalised fitting with 4 foot Batten. will need to look at an anti ligature style fitting moving forward, all tested and OK
MSA-DTWD | WA5734815 | 0 | SCAVENGER SUPPLIES PTY LTD | fire alarm activated - false - fault | Fire Protection Services | Fire Protection - Monitor System | 258.87 | Pass | Pass | 0 | 0 | 2.2167 | 2022-08-16 09:45 | 2022-08-16 11:45 | 2022-08-16 11:30 | 2022-08-16 13:45 | 2022-08-16 13:43 |  |  | COMPLETED-NO FURTHER WORK REQUIRED16/08/2022 STARTED=BW
MSA-DCA | WA6526748 | 1 | TK Elevator Australia Pty Ltd | Main Goods - Goods hoist lift stuck on level one with elevated work platform inside | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 2.2167 | 2023-02-01 10:28 | 2023-02-02 17:00 | 2023-02-01 12:02 | 2023-02-02 17:00 | 2023-02-01 14:15
MSA-MRWA | WA6148781 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Auto Dialer has failed | Air Conditioning | Building HVAC Maintenance (Major Plant) | 386.31 | Pass | Pass | 0 | 0 | 2.2 | 2022-11-04 09:10 | 2022-11-04 11:10 | 2022-11-04 10:48 | 2022-11-04 13:10 | 2022-11-04 13:00 |  |  | Works completed
MSA-DFES | WA6372444 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | First floor - Accessible toilet - Tap wont turn on | Plumbing & Drainage | Water | 145.1475 | Pass | Pass | 0 | 0 | 2.2 | 2022-12-14 12:05 | 2022-12-15 17:00 | 2022-12-15 07:45 | 2022-12-15 17:00 | 2022-12-15 09:57 |  |  | Went to accessible toilet on first floor to check toilets and taps had put handle back on basin mixer everything was fine, check all floors male and female toilets and taps, nothing was running, all functioning correctly
MSA-DTWD | WA5655496 | 0 | Dormakaba Australia Pty Ltd | B block - rear court yard ear sliding gate - stopped working | Building | Automatic Doors | 600 | Pass | Pass | 0 | 0 | 2.2 | 2022-07-18 08:44 | 2022-07-18 10:44 | 2022-07-18 10:27 | 2022-07-18 12:44 | 2022-07-18 12:39 |  |  | Gate is back to normal operation, cleaned and terminated wiring, cleaned safety beams.possible problem was corrosion build up. Gate will require full upgrade in near future due to multiple corroded parts - 2 techs
MSA-DTWD | WA5109873 | 2 | ECO PLUMBING AND GAS PTY LTD | L10 - Bench top gas valve stuck and unable to open and concerns over forcing it in case pipe cracks | Plumbing & Drainage | Gas | 318.975 | Pass | Pass | -1 | -1 | 2.1667 | 2022-02-09 14:00 | 2022-02-14 17:00 | 2022-02-10 11:20 | 2022-02-14 17:00 | 2022-02-10 13:30 |  |  | Installed isolation valve on gas line.
MSA-DCA | WA5133797 | 1 | FCT SURFACE CLEANING | Ground/external - Urban Orchard garden bed -Graffiti tag to be removed from garden bed,see notes | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2.1667 | 2022-02-15 14:15 | 2022-02-16 17:00 | 2022-02-16 12:20 | 2022-02-16 17:00 | 2022-02-16 14:30 |  |  | Job completed - Removed graffiti from garden bed and sign.
MSA-DTWD | WA6393423 | 0 | AHS Services WA Pty Ltd (Anchor) | Water fountain between Green skills and Main Building - D&E Block - Significant Water Leak at mains | Plumbing & Drainage | Water | 324.9575 | Pass | Pass | 0 | 0 | 2.1667 | 2022-12-28 14:20 | 2022-12-28 16:20 | 2022-12-28 14:20 | 2022-12-28 18:20 | 2022-12-28 16:30 |  |  | Supply and install 2m of 20mm copper with fittings as required to repair burst 25mm water line supplying water feature in rear courtyard.Tested on completion
MSA-DCA | WA6401359 | 0 | Dormakaba Australia Pty Ltd | Door Not responding to key swipe or door control | Building | Automatic Doors | 884.99 | Fail | Fail | 0 | 0 | 2.1667 | 2023-01-04 11:23 | 2023-01-04 13:23 | 2023-01-04 13:50 | 2023-01-04 15:23 | 2023-01-04 16:00
MSA-DCA | WA6667759 | 1 | GPS Plumbing & Gas Services PtyLtd | Staff Ladies Toilet - Leaking cistern | Plumbing & Drainage | Toilets/Cisterns | 360.8525 | Pass | Pass | 0 | 0 | 2.1667 | 2023-02-21 14:25 | 2023-02-22 17:00 | 2023-02-22 13:35 | 2023-02-22 17:00 | 2023-02-22 15:45
MSA-DCA | WA5585409 | 1 | TK Elevator Australia Pty Ltd | Not working and stuck on ground floor | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2.1667 | 2022-07-05 16:24 | 2022-07-06 17:00 | 2022-07-06 08:03 | 2022-07-06 17:00 | 2022-07-06 10:13 |  |  | :Lift stopped at ground floor with doors closed Found top floor landinglocks binding on lock housing, adjusted and tested, Re programmed phone to TK and tested. Cleaned car gate switches and all hoistway locks. Ran lift extensively and cleared errors, returned to service
MSA-DFES | WA6249331 | 2 | Dom's Total Grounds Maintenance | Station Reticulation System not working properly - see notes | Plumbing & Drainage | Water | 361 | Fail | Fail | 2 | 2 | 2.1667 | 2022-11-21 11:24 | 2022-11-24 17:00 | 2022-12-05 08:30 | 2022-11-24 17:00 | 2022-12-05 10:40 |  |  | Jim Duggan attended and has repaired retic
MSA-DTAG | WA6687925 | 0 | Schindler Lifts Australia | Lift call button panel detached from wall – lifts cannot be used | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 2.1667 | 2023-03-07 10:40 | 2023-03-07 12:40 | 2023-03-08 11:05 | 2023-03-07 14:40 | 2023-03-08 13:15
MSA-DFES | WA5311902 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level- Outdoor- Burst pipe on station 1 - see notes | Plumbing & Drainage | Water | 340.5475 | Pass | Pass | 0 | 0 | 2.15 | 2022-04-11 09:33 | 2022-04-14 17:00 | 2022-04-14 08:52 | 2022-04-14 17:00 | 2022-04-14 11:01 |  |  | Repaired burst pipe on the reticulation line
MSA-DCA | WA6359267 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - Chiller 1 in alarm | Air Conditioning | Room Air Conditioners | 371.62 | Pass | Pass | 0 | 0 | 2.15 | 2022-12-06 13:51 | 2022-12-07 17:00 | 2022-12-06 13:51 | 2022-12-07 17:00 | 2022-12-06 16:00 |  |  | TRAVELLED TO SITE AND SIGNED IN AT RECEPTION. ACCESSED PLANT ROOM AND FOUND CHILLER 2 IN LOCK OUT ALARM. RESET CHILLER AND ALSO RESET BMS INSIDE BUILDING TO ENSURE NO FURTHER ALARMS OR FAULTS. CHECKED TO SEE IF ANY FURTHER ISSUES AND FOUND THAT BOILER 2 HAD E01 FAULT. ADVISED KIRSTINE FROM BOILERTRONICS OF ISSUE. BOILERTRONICS ARE QUOTING TO REPAIR FAULT WITH BOILER 2.
MSA-DCA | WA4992319 | 1 | GPS Plumbing & Gas Services PtyLtd | Public Male Toilet - Urinal drain tube to be cleared | Plumbing & Drainage | Toilets/Cisterns | 309.795 | Pass | Pass | 0 | 0 | 2.15 | 2022-01-06 10:08 | 2022-01-07 17:00 | 2022-01-06 11:31 | 2022-01-07 17:00 | 2022-01-06 13:40 |  |  | Unblocked badly blocked drain and cleaned trap
MSA-DCA | WA5417540 | 2 | GPS Plumbing & Gas Services PtyLtd | Female Staff Toilets - Level 4 - Blocked Toilet - Cistern Leaking | Plumbing & Drainage | Toilets/Cisterns | 341.555 | Pass | Pass | 0 | 0 | 2.15 | 2022-05-13 13:44 | 2022-05-18 17:00 | 2022-05-16 13:50 | 2022-05-18 17:00 | 2022-05-16 15:59 |  |  | Cleared blocked toilet pan, replaced inlet valve and outlet sealing washers to female disabled toilet level 1 public.
MSA-DTWD | WA5190868 | 2 | Precise Air Group | The room is warmer than the one next to it a quite warm 1 of the 2 diffusers is missing | Air Conditioning | Room Air Conditioners | 235.48 | Fail | Fail | 0 | 0 | 2.15 | 2022-02-24 16:13 | 2022-03-01 17:00 | 2022-03-02 07:21 | 2022-03-01 17:00 | 2022-03-02 09:30 |  |  | Attended site and completed pre start paperwork and singed in. Acessed room b54 and inspected air flow. Found room to have 2 outlets with air coming out of both of them. Room B54 is supplied via ahu 8 on ground floor. Multiple quotes are required on ahu. Filters are blocked. 2 have been removed by previous tech to remove stress from motor as motor has bearing issues. This causing dirt to build up on coil. Ahu 8 also has a failed damper. Damper is rusty and actuator is only moving one blade. Quotation details submitted
MSA-DTWD | WA5693352 | 2 | M Construction (WA) | Flashing coming off near sliding door | Building | Doors | 254.96 | Pass | Pass | 0 | 0 | 2.15 | 2022-08-04 11:38 | 2022-08-09 17:00 | 2022-08-08 09:00 | 2022-08-09 17:00 | 2022-08-08 11:09 |  |  | Attend site and repaired.
MSA-DTWD | WA5389837 | 1 | Dormakaba Australia Pty Ltd | A126 - auto door wont close | Building | Automatic Doors | 360 | Pass | Pass | 0 | 0 | 2.1333 | 2022-05-02 08:10 | 2022-05-03 17:00 | 2022-05-02 09:24 | 2022-05-03 17:00 | 2022-05-02 11:32 |  |  | 605088 Find the auto door will not close checked exit button ok. Bridge PE input on the controller to find the after hour relay is not energised. Steve will get access control to after hour on there system.
MSA-DTWD | WA5570808 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block SK3 L/H side sink 5 tap broken and leaking | Plumbing & Drainage | Water | 126.49 | Pass | Pass | 0 | 0 | 2.1333 | 2022-06-28 15:07 | 2022-07-01 17:00 | 2022-06-29 08:22 | 2022-07-01 17:00 | 2022-06-29 10:30 |  |  | Job completed
MSA-DTWD | WA6292415 | 2 | AHS Services WA Pty Ltd (Anchor) | A419 Leaking toilet pan adaptor | Plumbing & Drainage | Toilets/Cisterns | 314.62 | Fail | Fail | 0 | 0 | 2.1333 | 2022-11-29 10:06 | 2022-12-02 17:00 | 2022-12-05 06:30 | 2022-12-02 17:00 | 2022-12-05 08:38 |  |  | Repaired leaking pan collar by installing silicone seal. Supplied and installed new toilet seat as the old one had perished.
MSA-DFES | WA6578624 | 1 | Australian HVAC Services Pty. Ltd. | HVAC - Crack unit - Server room - Alarm - AirCon | Air Conditioning | Building HVAC Maintenance (Major Plant) | 246.92 | Pass | Pass | 0 | 0 | 2.1297 | 2023-02-15 10:57 | 2023-02-16 17:00 | 2023-02-15 11:49 | 2023-02-16 17:00 | 2023-02-15 13:57
MSA-DTWD | WA5384155 | 0 | Precise Air Group | Cooling tower 1 and Cooling tower 2 - constantly dumping water | Air Conditioning | Building HVAC Maintenance (Major Plant) | 235.48 | Pass | Pass | 0 | 0 | 2.1167 | 2022-04-28 10:15 | 2022-04-28 12:15 | 2022-04-28 11:00 | 2022-04-28 14:15 | 2022-04-28 13:07 |  |  | Found floats needed adjusting and a valve was sticking slightly. Made corrections to floats and applied a lubricant to valve.
MSA-DTWD | WA5200539 | 1 | OTIS ELEVATOR COMPANY PTY LTD | B block - passenger lift -lift door sensor faulty | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 2.1167 | 2022-03-02 07:10 | 2022-03-02 17:00 | 2022-03-03 12:45 | 2022-03-02 17:00 | 2022-03-03 14:52 |  |  | DOORS/ENTRANCES - LOCK HOUSING - COMPONENT OUT OF ADJUSTMENT
MSA-DFES | WA4993476 | 1 | Dom's Total Grounds Maintenance | applied training - burst retic pipe | Plumbing & Drainage | Water | 400.5 | Pass | Pass | 0 | 0 | 2.1 | 2022-01-07 14:39 | 2022-01-10 17:00 | 2022-01-07 14:39 | 2022-01-10 17:00 | 2022-01-07 16:45 |  |  | Emergency Call OutSupply Pipe fittings & Glue
MSA-DFES | WA5115981 | 0 | Kone Elevators Pty Ltd | hallway - lift - it is stuck - stuck on level 1 | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 2.1 | 2022-02-11 10:29 | 2022-02-11 12:29 | 2022-02-11 12:48 | 2022-02-11 14:29 | 2022-02-11 14:54 |  |  | No charge for the call out
MSA-DTWD | WA6154474 | 3 | CONNECT SECURITY SYSTEMS | Level 1 - C/Block staff room auto swipe card not working | Security | Access Control | 346.1 | Pass | Pass | -1 | -1 | 2.1 | 2022-11-07 12:52 | 2022-11-14 17:00 | 2022-11-10 08:27 | 2022-11-14 17:00 | 2022-11-10 10:33 |  |  | reprogrammed reader for door not operating correctly
MSA-DCA | WA6522627 | 3 | Dormakaba Australia Pty Ltd | L3 - Terrace auto door, scraping when opening or closing | Building | Automatic Doors | 640 | Pass | Pass | 0 | 0 | 2.1 | 2023-01-31 09:06 | 2023-02-07 17:00 | 2023-02-07 08:16 | 2023-02-07 17:00 | 2023-02-07 10:22
MSA-DCA | WA5829459 | 2 | GPS Plumbing & Gas Services PtyLtd | Blocked floor drain | Plumbing & Drainage | Drainage | 201.73 | Pass | Pass | 0 | 0 | 2.0833 | 2022-09-02 13:38 | 2022-09-07 17:00 | 2022-09-05 13:35 | 2022-09-07 17:00 | 2022-09-05 15:40 |  |  | Unblocked drain, inspected other drains and flushed them with buckets of water, no drains are blocked.
MSA-DCA | WA5979739 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground / upper car park - Theatre foyer toilets - Water leak from foyer toilet pipework - See notes | Plumbing & Drainage | Water | 461.2025 | Pass | Pass | -1 | -1 | 2.0833 | 2022-09-29 09:46 | 2022-10-04 17:00 | 2022-09-29 10:35 | 2022-10-04 17:00 | 2022-09-29 12:40 |  |  | Investigated leak in car park. FLOOR in the Duct on gr floor wet due to leaking filter. Replaced leakinf filter. I believe that was the cause of the wate leak in the car park as rhe water was travelling along the pipe from the duct. Denise advised.
MSA-DTWD | WA5396086 | 2 | M Construction (WA) | Ground Floor - Decking Area - decking under pepper tree has a loose edge paver | Paving & Roadworks | Paving | 357.37 | Fail | Fail | 2 | 2 | 2.0833 | 2022-05-06 08:17 | 2022-05-11 17:00 | 2022-05-25 09:00 | 2022-05-11 17:00 | 2022-05-25 11:05 |  |  | Block paver missing on steps, dig out sand/cement from previous block paver. Find spare block paver on campus. fill withsand/cement. Re-point edges. clean up.
MSA-DFES | WA5570378 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Applied training grounds - Overflowing drain - toilets' are blocked | Plumbing & Drainage | Drainage | 321.85 | Pass | Fail | 0 | 0 | 2.0833 | 2022-06-28 10:28 | 2022-06-28 12:28 | 2022-06-28 12:25 | 2022-06-28 14:28 | 2022-06-28 14:30 |  |  | Used drain machine down sewer hit something 8 rose down did not pull out anything run water from 20min did paper test everything is fine nothing was backing up
MSA-DCA | WA6359355 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground Exterior - Courtyard to west of SLWA - Tap needs to be reinstated | Plumbing & Drainage | Water | 236.73 | Pass | Pass | 0 | 0 | 2.0833 | 2022-12-06 15:00 | 2022-12-09 17:00 | 2022-12-07 13:55 | 2022-12-09 17:00 | 2022-12-07 16:00 |  |  | Replaced t head on hose tap outside library on the LHS
MSA-DTAG | WA6450702 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Men toilets cubicle 2 - Water in toilet keeps running | Plumbing & Drainage | Toilets/Cisterns | 404.6025 | Pass | Pass | 0 | 0 | 2.0833 | 2023-01-16 13:11 | 2023-01-19 17:00 | 2023-01-17 12:30 | 2023-01-19 17:00 | 2023-01-17 14:35
MSA-DTWD | WA6540244 | 1 | AHS Services WA Pty Ltd (Anchor) | A126 - A Block - Ground Floor - Urinal not working | Plumbing & Drainage | Water | 259.108 | Pass | Pass | 0 | 0 | 2.0833 | 2023-02-09 09:29 | 2023-02-10 17:00 | 2023-02-09 11:25 | 2023-02-10 17:00 | 2023-02-09 13:30
MSA-DFES | WA5108695 | 2 | Dom's Total Grounds Maintenance | Garden Retic - seems to have a broken pipe or faulty valve, gardens and lawn are dying. | Plumbing & Drainage | Water | 493 | Pass | Pass | 0 | 0 | 2.0833 | 2022-02-08 16:50 | 2022-02-11 17:00 | 2022-02-09 17:35 | 2022-02-11 17:00 | 2022-02-09 19:40 |  |  | Repair 12 x Breakages & Reset Controller
MSA-DTWD | WA5401067 | 2 | AHS Services WA Pty Ltd (Anchor) | Male toilets East blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 376.8775 | Pass | Pass | 0 | 0 | 2.0833 | 2022-05-10 15:33 | 2022-05-13 17:00 | 2022-05-12 09:35 | 2022-05-13 17:00 | 2022-05-12 11:40 |  |  | Completed
MSA-DCA | WA5574125 | 3 | ADVANCED LOCK & KEY | PCC Exterior - West Car Park Entrance - Sharps Boxes needing new keys - See notes below | Security | Locksmith | 360 | Pass | Pass | -1 | -1 | 2.0833 | 2022-06-30 15:09 | 2022-07-07 17:00 | 2022-07-01 08:50 | 2022-07-07 17:00 | 2022-07-01 10:55 |  |  | Rekeyed 2 sharp boxes, west of state library and urban orchid (west) to sharp box key LF31R- 057- 31312 8:50-10:55 2x LF31R rekeys
MSA-DFES | WA5390423 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - rear yard - please see details below | Plumbing & Drainage | Materials | 229.4 | Pass | Pass | 0 | 0 | 2.0833 | 2022-05-02 12:42 | 2022-05-09 17:00 | 2022-05-06 10:45 | 2022-05-09 17:00 | 2022-05-06 12:50 |  |  | Replace two fire hydrant heads in the rear yard site supplied
MSA-DTWD | WA5495553 | 2 | ECO PLUMBING AND GAS PTY LTD | AG27b - student male toilets - First sink tap broken | Plumbing & Drainage | Materials |  | Fail | Fail | 1 | 1 | 2.0833 | 2022-06-08 13:01 | 2022-06-13 17:00 | 2022-06-20 09:40 | 2022-06-13 17:00 | 2022-06-20 11:45 |  |  | Replaced 2x basin mixers
MSA-DTAG | WA5655801 | 2 | Water2water Pty Ltd | Kitchen L11- | Plumbing & Drainage | Water | 775.055 | Pass | Pass | 0 | 0 | 2.0833 | 2022-07-18 10:27 | 2022-07-21 17:00 | 2022-07-18 14:55 | 2022-07-21 17:00 | 2022-07-18 17:00 |  |  | replaced front PCB & element
MSA-DCA | WA6414928 | 1 | GPS Plumbing & Gas Services PtyLtd | Harry Butler Centre - Wet Processing Lab - No suction in down draft sinks in the labs - see notes | Plumbing & Drainage | Drainage | 272.8525 | Pass | Pass | 0 | 0 | 2.0833 | 2023-01-11 10:45 | 2023-01-12 17:00 | 2023-01-12 09:15 | 2023-01-12 17:00 | 2023-01-12 11:20
MSA-DFES | WA6528214 | 1 | SONTEC WA PTY LTD | Faulty - security alarm system | Security | Security Management System | 510 | Pass | Pass | 0 | 0 | 2.0833 | 2023-02-02 09:48 | 2023-02-03 17:00 | 2023-02-02 11:10 | 2023-02-03 17:00 | 2023-02-02 13:15
MSA-DTWD | WA6050114 | 1 | AWB Co. | L Block - Horticulture Hallway - Loud buzzing from switchboard | Electrical | Distribution Board | 218.2075 | Pass | Pass | 0 | 0 | 2.0667 | 2022-10-17 14:56 | 2022-10-18 17:00 | 2022-10-17 15:26 | 2022-10-18 17:00 | 2022-10-17 17:30 |  |  | Attended site signed in jsa completed. Found really loud sound coming from board. Started switching breakers off till it stopped. W12 does preparation rooms in L block. switched it on and off 50 times and no sound coming from it now. Screwed it back abit more to stop future buzzing.Job completed
MSA-DCA | WA6126583 | 3 | Techworks Electrical | 2 bulb fixtures in chandelier in stalls not working. - See notes | Electrical | Lighting, Internal | 230.88 | Pass | Pass | 0 | 0 | 2.0667 | 2022-10-25 12:10 | 2022-11-01 17:00 | 2022-10-31 14:00 | 2022-11-01 17:00 | 2022-10-31 16:04 |  |  | Investigated pendant light with globes not working. Removed globes not working and one of the globes currently working and compared. Appeared to be a different globe so i located store room with spare globes and found the correct globes to for the light. All globes now work
MSA-DFES | WA6128968 | 1 | Australian HVAC Services Pty. Ltd. | Server room - left hand air-conditioner unit gone into error | Air Conditioning | Room Air Conditioners | 413.03 | Pass | Pass | 0 | 0 | 2.0667 | 2022-10-27 09:40 | 2022-10-28 17:00 | 2022-10-27 14:30 | 2022-10-28 17:00 | 2022-10-27 16:34 |  |  | Running need replacement
MSA-DTWD | WA6149062 | 1 | SCAVENGER SUPPLIES PTY LTD | next to fire alarm panel-Re-set the fire alarm (break glass) front of A block next to fire alarm pan | Fire Protection Services | Fire Protection - Monitor System | 153.6 | Pass | Pass | 0 | 0 | 2.0667 | 2022-11-04 11:55 | 2022-11-07 17:00 | 2022-11-04 12:20 | 2022-11-07 17:00 | 2022-11-04 14:24 |  |  | Attended site at 12:20 pm and found that the MCP located adjacent the FIP was in alarm yet the button was not depressed. The FIP was inspected and I had noticed that there was no alarm on the panel. I had used the reset tool to try and rotate the dial yet the red alarm light was still lit. A master reset was conducted on the FIP and I had noticed that the MCP was disabled and isolated. After re-enabling the MCP and completing another master reset on the panel that the red alarm light on the MCP had now cleared. After calling John from Facilities he claimed that after DFES arrived they had reset it but the alarm light would reappear instantly. Brett from Facilities met me at the FIP and told me that because the light has not reappeared after I've reset it he is happy to leave it as is. All systems have been returned to normal. There are still currently issues with the panels including disables and loop faults. Left site at 1.30pmCompleted04/11/2022
MSA-DCA | WA6149393 | 0 | Techworks Electrical | Outside PICA - Power recess - one of the plug is tagged out of order - please check | Electrical | Distribution Board | 230.88 | Pass | Pass | 0 | 0 | 2.0667 | 2022-11-04 14:56 | 2022-11-04 16:56 | 2022-11-04 15:30 | 2022-11-04 18:56 | 2022-11-04 17:34 |  |  | Investigated out of service 3 phase outlet. The out of service tag details were that the circuit had been disconnected from the DB and was make safe above PCC main DB. Found cable in junction box above PCC DB and investigated db to find that it was full and had no room to reconnect cable. Suggested to event organisers to extend the cable floor duct to the further service pit where there is a 3 phase outlet that is live.
MSA-MRWA | WA6660928 | 2 | Water2water Pty Ltd | Warehouse - Ground - Ice machine only making ice shells | Refrigeration | Ice machine | 187.84 | Pass | Pass | 0 | 0 | 2.0667 | 2023-02-21 12:23 | 2023-02-24 17:00 | 2023-02-23 08:00 | 2023-02-24 17:00 | 2023-02-23 10:04
MSA-DTAG | WA6560872 | 1 | GPS Plumbing & Gas Services PtyLtd | Dishwasher is leaking – massive puddle on the kitchen floor (which has since been cleaned up) | Plumbing & Drainage | Drainage | 272.8525 | Pass | Pass | 0 | 0 | 2.05 | 2023-02-13 13:45 | 2023-02-14 17:00 | 2023-02-14 06:37 | 2023-02-14 17:00 | 2023-02-14 08:40
MSA-DCA | WA4991595 | 1 | GPS Plumbing & Gas Services PtyLtd | Vandalism-water in the male toilet is jammed on and unable to turn off - see notes below | Plumbing & Drainage | Water | 650.935 | Pass | Pass | 0 | 0 | 2.05 | 2022-01-05 09:59 | 2022-01-06 17:00 | 2022-01-05 12:00 | 2022-01-06 17:00 | 2022-01-05 14:03 |  |  | Replaced timeflow basin tap to LHS basin male public toilet
MSA-DTAG | WA5093547 | 0 | Australian HVAC Services Pty. Ltd. | Family Voilience room - CCTV room - water leak | Air Conditioning | Building HVAC Maintenance (Major Plant) | 271.34 | Pass | Pass | 0 | 0 | 2.05 | 2022-01-28 16:56 | 2022-01-28 18:56 | 2022-01-28 16:57 | 2022-01-28 20:56 | 2022-01-28 19:00 |  |  | Received callout and travelled to joondalup courthouse.Inspected water leak and found leak is from first floor toilets or toilet pipework. Reported to onsite staff and completed job. Requires plumber.
MSA-DFES | WA5677332 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Workshop whole facilities-No hot water coming out of the hot water Taps | Plumbing & Drainage | Water | 250.46 | Pass | Pass | 0 | 0 | 2.05 | 2022-07-25 13:59 | 2022-07-26 17:00 | 2022-07-26 06:57 | 2022-07-26 17:00 | 2022-07-26 09:00 |  |  | Hot water unit repair
MSA-DTAG | WA6405299 | 1 | Dormakaba Australia Pty Ltd | Old reception area - Glass auto doors leading to Irwin Street require attention (see notes) | Building | Automatic Doors | 881.12 | Pass | Pass | 0 | 0 | 2.05 | 2023-01-09 12:24 | 2023-01-10 17:00 | 2023-01-09 12:47 | 2023-01-10 17:00 | 2023-01-09 14:50
MSA-DCA | WA5499201 | 2 | GPS Plumbing & Gas Services PtyLtd | Shipwrights Office (New office space) - Ambulant toilets - Toilet seat is missing locking screw | Plumbing & Drainage | Toilets/Cisterns | 659.805 | Pass | Pass | 0 | 0 | 2.05 | 2022-06-10 11:17 | 2022-06-15 17:00 | 2022-06-13 11:37 | 2022-06-15 17:00 | 2022-06-13 13:40 |  |  | Replaced damaged seat. Job took longer as i struggled to uninstall toggle kit without damaging the pan.
MSA-DTWD | WA5660582 | 2 | M Construction (WA) | External steps from staff car park- Pavers loose from step | Building | General Building | 247.69 | Fail | Fail | 0 | 0 | 2.05 | 2022-07-19 10:51 | 2022-07-22 17:00 | 2022-07-25 07:00 | 2022-07-22 17:00 | 2022-07-25 09:03 |  |  | Removed loose pavers, cleaned out debris and reinstalled pavers with external masonary adhesive.
MSA-DTAG | WA5880709 | 2 | AWB Co. | Custody - Non-Contact Interview Room - flickering light | Electrical | Lighting, Internal | 224.21 | Pass | Pass | 0 | 0 | 2.05 | 2022-09-15 15:46 | 2022-09-20 17:00 | 2022-09-19 07:00 | 2022-09-20 17:00 | 2022-09-19 09:03 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located interview room. Set up work area. Supplied and replaced faulty fluro tubes with new. Packed up. Notified relevant personnel. **job complete**
MSA-DTWD | WA5017476 | 2 | Techworks Plumbing | F1 to F4 Flower bed - Ground - see notes below | Plumbing & Drainage | Water | 760.29 | Pass | Pass | 0 | 0 | 2.0333 | 2022-01-13 15:01 | 2022-01-18 17:00 | 2022-01-18 10:02 | 2022-01-18 17:00 | 2022-01-18 12:04 |  |  | Modified retic line to connect to retic in garden bed
MSA-DTAG | WA6407853 | 0 | Dormakaba Australia Pty Ltd | Custody - Basement - roller door to the sally port has come out of the railings and is unusable | Building | Automatic Doors | 366.95 | Pass | Pass | 0 | 0 | 2.0167 | 2023-01-10 11:51 | 2023-01-10 13:51 | 2023-01-10 13:33 | 2023-01-10 15:51 | 2023-01-10 15:34
MSA-DTWD | WA5305946 | 2 | ECO PLUMBING AND GAS PTY LTD | D block - D02 - Urinal Blocked | Plumbing & Drainage | Toilets/Cisterns | 270.7 | Pass | Pass | 0 | 0 | 2.0167 | 2022-04-06 09:01 | 2022-04-11 17:00 | 2022-04-11 14:00 | 2022-04-11 17:00 | 2022-04-11 16:01 |  |  | cleared blockage
MSA-DTWD | WA5544803 | 0 | FSA (WA) Pty Ltd | Fire system booster in alarm and is pumping water out | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Fail | Fail | 0 | 0 | 2.0167 | 2022-06-17 05:41 | 2022-06-17 07:41 | 2022-06-17 08:30 | 2022-06-17 09:41 | 2022-06-17 10:31 |  |  | Found electric pump running on arrival. Turned off and isolated. Drained a sump pit where John thought the leak was. Found no cause of water pressure drop. Checked site for water loss. Found on leaks or reason for pumps to start. System sitting normal
MSA-DCA | WA6408104 | 2 | Techworks Electrical | Power point switch on dressing table loose, marked with a red cross - See Notes | Electrical | General Electrical | 142.96 | Pass | Pass | 0 | 0 | 2.0167 | 2023-01-10 14:42 | 2023-01-13 17:00 | 2023-01-11 13:00 | 2023-01-13 17:00 | 2023-01-11 15:01
MSA-DTAG | WA6408137 | 1 | Australian HVAC Services Pty. Ltd. | Next to custody - Aircon not cooling | Air Conditioning | Room Air Conditioners | 370.8 | Pass | Pass | 0 | 0 | 2.0075 | 2023-01-10 15:08 | 2023-01-11 17:00 | 2023-01-11 07:51 | 2023-01-11 17:00 | 2023-01-11 09:52
MSA-DFES | WA4990920 | 3 | AWB Co. | Nosie Barrier sliding door roller between kitchen & fridge/food storage area broken see notes | Building | Doors | 236.95 | Pass | Pass | -1 | -1 | 2 | 2022-01-04 13:08 | 2022-01-11 17:00 | 2022-01-06 09:30 | 2022-01-11 17:00 | 2022-01-06 11:30 |  |  | Fix sliding door
MSA-DCA | WA4991417 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 3 - Executive suite - South east side - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 491.875 | Fail | Fail | 1 | 1 | 2 | 2022-01-05 08:05 | 2022-01-06 17:00 | 2022-01-10 09:30 | 2022-01-06 17:00 | 2022-01-10 11:30 |  |  | Attended site, signed in and accessed level 3 checked and recorded room temperatures around 24.0 degrees. Checked ahu 8 and found working as per normal, the economy dampers were slightly open allowing outside air to come through - restroked dampers. Could not get access to the bms to check chilled water supply temperaturs to ahus. Honeywell later investigated and found a seized valve on ahu 3.
MSA-DTWD | WA5001460 | 2 | GRAFFITI FORCE PTY LTD | East external wall and assembly sign has graffiti | Cleaning | Graffiti | 359.76 | Pass | Pass | 0 | 0 | 2 | 2022-01-11 12:20 | 2022-01-14 17:00 | 2022-01-14 11:00 | 2022-01-14 17:00 | 2022-01-14 13:00 |  |  | REMOVAL OF GRAFFITI FROM EAST EXTERNAL WALL AND ASSEMBLY SIGN
MSA-DTWD | WA5010138 | 2 | Techworks Electrical | E-Block - Restaurant kitchen - has 4 ceiling lights out and the fly zapper fluro is out | Electrical | Lighting, Internal | 474.38 | Pass | Pass | -1 | -1 | 2 | 2022-01-12 10:25 | 2022-01-17 17:00 | 2022-01-12 14:00 | 2022-01-17 17:00 | 2022-01-12 16:00 |  |  | Replaced light tubes in E block restaurant kitchen
MSA-DFES | WA5010364 | 2 | Australian HVAC Services Pty. Ltd. | Main building - near cleaners room - possible water leak from air con | Air Conditioning | Building HVAC Maintenance (Major Plant) | 229.47 | Pass | Pass | -1 | -1 | 2 | 2022-01-12 13:07 | 2022-01-17 17:00 | 2022-01-12 14:00 | 2022-01-17 17:00 | 2022-01-12 16:00 |  |  | No further issued found possible old roof leak.
MSA-DCA | WA5038339 | 2 | Precise Air Group | Café - air con leaking water | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-01-17 12:22 | 2022-01-20 17:00 | 2022-01-18 08:00 | 2022-01-20 17:00 | 2022-01-18 10:00 |  |  | Travelled to site gained access. Located reported asset and assessed condition. Removed covers and found a joint installed previously on drain line which could have been a possible failure point. Due to location of unit in the Cafe we flushed drain tray and blew out drain lines for any blockages and debris. Reconnected join with glue and tested drain. Unit left operational. I would recommend considering replacing unit as it has deteriorated quicker due to location and the fact that it runs 24/7
MSA-DFES | WA5038598 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | External Trough - hot water tap is not working | Plumbing & Drainage | HWS/Units Electric & Gas | 328.9 | Fail | Fail | 0 | 0 | 2 | 2022-01-17 15:02 | 2022-01-24 17:00 | 2022-01-27 09:30 | 2022-01-24 17:00 | 2022-01-27 11:30 |  |  | Attend site to investigate broken tap on out side trough, located laundry trough with washing machine conversation taps that are damaged due to lack of maintenance. Unfortunately theses taps are. It servciable and need to be replaced. Supply and install new washing machine conversion taps. Tested and checked all working correctly
MSA-DTWD | WA5038631 | 1 | Mizco Pty Ltd | Admin Building 832 - Ground Floor - Conference Room - see details below | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 2 | 2022-01-17 15:50 | 2022-01-18 17:00 | 2022-01-18 08:00 | 2022-01-18 17:00 | 2022-01-18 10:00 |  |  | Attempted to dial in but could not RDP to computer. Reported this to DTWD.• Shortly after had response from RDP, and after some time was able to dial in to the PC.• Saw that All AC Units were running other than AC3, which was being enabled but had no status.• Called Graeme, who investigated the unit and said that it appeared to be running.• It seems that the program had an interlock that would not allow the CHW Valve to open unlessthe Fan Status was On.• Graeme inspected the control panel, and after changing some settings the status cam back on.• Observed the CHVVV open to 100%, and the temperature in the room being to coo down.
MSA-DTWD | WA5053302 | 2 | Equans Mechanical Services Australia | Staff Office W204 - Rectify VAV - W2-01 Damper unit. Room too cold | Air Conditioning | Room Air Conditioners | 371.51 | Pass | Pass | 0 | 0 | 2 | 2022-01-18 15:19 | 2022-01-21 17:00 | 2022-01-20 14:00 | 2022-01-21 17:00 | 2022-01-20 16:00 |  |  | REPLACED PART ON VAV ACTUATOR - TESTED - ALL OK
MSA-DTWD | WA5069104 | 2 | M Construction (WA) | library chairs that have broken screws in the base of the swivel mechanics | Furniture | Office Furniture | 282.4 | Pass | Pass | -1 | -1 | 2 | 2022-01-19 14:59 | 2022-01-24 17:00 | 2022-01-20 12:30 | 2022-01-24 17:00 | 2022-01-20 14:30 |  |  | Inspected and located damaged chairs and repaired.
MSA-DTWD | WA5081058 | 1 | Equans Mechanical Services Australia | Ground - Rooms215,216,217,219,229 & 229 - BMS aircon - running warm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 204.07 | Pass | Pass | 0 | 0 | 2 | 2022-01-20 10:37 | 2022-01-21 17:00 | 2022-01-20 14:00 | 2022-01-21 17:00 | 2022-01-20 16:00 |  |  | Arrived on site signed in. Checked all operating units found vrv waiting on daikin to investigate fault. Master has been taken out of service. Working on the two slave units. Server room currently temp 23deg in room which is OK. As outside temperature 40deg unit doing as good as possible while Master unit off line. Have been asked to request quote for two stand alone splits to be installed. Information sent to Simon for quotation. Checked operation on other VRV unit all OK. Cleaned up and completed paperwork and signed out.
MSA-DTWD | WA5081327 | 3 | Schindler Lifts Australia | Lifts 5 & 6 - main button selection panel not working. | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 2 | 2022-01-20 12:59 | 2022-01-28 17:00 | 2022-01-20 14:45 | 2022-01-28 17:00 | 2022-01-20 16:45 |  |  | job completed - Lifts have suffered a mains power loss causing lifts to experience problems. Reset all lifts back to normal
MSA-DTWD | WA5085544 | 2 | Precise Air Group | u022 - Evap A/C constantly dumping water | Air Conditioning | Evaporative Coolers | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-01-21 08:39 | 2022-01-27 17:00 | 2022-01-27 08:00 | 2022-01-27 17:00 | 2022-01-27 10:00 |  |  | Traveled to site gained access and signed in. Filled out roof work permits. Located reported area and checked all units attached to that drain line. Found one with bleed too high and in the overflow pipe. Fixed issue and left units operational
MSA-DTWD | WA5086497 | 2 | Techworks Electrical | D Block - Level 1 - Male toilets - lights not working | Electrical | General Electrical | 579.31 | Pass | Pass | 0 | 0 | 2 | 2022-01-21 11:02 | 2022-01-27 17:00 | 2022-01-27 12:30 | 2022-01-27 17:00 | 2022-01-27 14:30 |  |  | Replaced faulty lights with new LED downlights
MSA-DTAG | WA5090635 | 2 | Australian HVAC Services Pty. Ltd. | Level 15 - Magistrates Chambers A/C controls are not responding | Air Conditioning | Room Air Conditioners | 2759.47 | Pass | Pass | -1 | -1 | 2 | 2022-01-25 14:33 | 2022-01-31 17:00 | 2022-01-27 08:00 | 2022-01-31 17:00 | 2022-01-27 10:00 |  |  | #40464Temporary a/c units installed until replacement unit is completed.
MSA-DCA | WA5090927 | 1 | EQUANS Mechanical Services (WA) Pty Limited | BMS alarm is going off for the A/C | Air Conditioning | Materials | 554.65 | Pass | Pass | 0 | 0 | 2 | 2022-01-26 14:20 | 2022-01-27 17:00 | 2022-01-27 08:00 | 2022-01-27 17:00 | 2022-01-27 10:00 |  |  | Attended site, signed in and carried out checks on RO storage tank. Found water level on tank at 80% full. Carried out resets on the BMS and monitored the tank levels whilst operational. Possible faulty sensor, will monitor during routine maintenance.
MSA-DTWD | WA5091655 | 3 | Protek 24/7 Building & Maintenance | Car park 1 - Garrison Fence - personnel gate dropped | Building | Steel Fencing & Gates | 211 | Pass | Pass | 0 | 0 | 2 | 2022-01-27 09:55 | 2022-02-03 17:00 | 2022-01-31 09:30 | 2022-02-03 17:00 | 2022-01-31 11:30 |  |  | Repair gate
MSA-DTWD | WA5092798 | 2 | Protek 24/7 Building & Maintenance | T Block - Ground Level -Covered walkway east side external - Ceramic tiles falling façade | Building | General Building | 196 | Pass | Pass | 0 | 0 | 2 | 2022-01-28 10:10 | 2022-02-02 17:00 | 2022-02-02 06:30 | 2022-02-02 17:00 | 2022-02-02 08:30 |  | WACCES | Make safe
MSA-DCA | WA5093228 | 0 | Precise Air Group | air con leaking into dressing room 7 | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | 0 | 0 | 2 | 2022-01-28 12:44 | 2022-01-28 14:44 | 2022-01-28 14:00 | 2022-01-28 16:44 | 2022-01-28 16:00 |  |  | Attended site gained access and signed it. Found area reported. Found no active leak while attending at this time. Did find a tab holding up a corner of the drip tray was broken and causing it to sag to the opposite corner to the drain and pooling some water. Re fixed tray up to unit and attempted to raise unit to allow for more fall for the drain. No condensation present on attendance. Unit left operational
MSA-DTWD | WA5093530 | 2 | Assa Abloy Entrance Systems Aust P/L-WA | A Block - Level 1 - A107 - Replace broken Remote to Cafe Roller Shutter A | Security | Access Control | 642.49 | Pass | Pass | 0 | 0 | 2 | 2022-01-28 15:53 | 2022-02-02 17:00 | 2022-02-02 11:45 | 2022-02-02 17:00 | 2022-02-02 13:45 |  |  | Attended site and inspected roller shutter remote. Noted unit faulty. Required to program newremote to shutter. Tested door operations all ok. Left remote with Cafe as advised by Steve.
MSA-DTWD | WA5094885 | 3 | AWB Co. | Block 9 - Ground Floor - Flashing emergency light in fitting next to Librarians office | Electrical | General Electrical | 347.54 | Pass | Pass | -1 | -1 | 2 | 2022-01-31 14:58 | 2022-02-07 17:00 | 2022-02-03 12:30 | 2022-02-07 17:00 | 2022-02-03 14:30 |  |  | Attended site and signed in. Completed JSA. Located flashing light in library. Found to be emergency fitting. Supply and replace with new led fitting internal of the fluro in library. Connected to existing battery supply. Reconnected cabling at circuit breaker. Tested all okay. Light working as it should. Signed out. Job complete
MSA-DTWD | WA5098183 | 2 | Equans Mechanical Services Australia | Hitachi Split AC is showing a fault | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 2 | 2022-02-01 07:22 | 2022-02-03 17:00 | 2022-02-02 14:00 | 2022-02-03 17:00 | 2022-02-02 16:00 |  |  | Located room B2218 server room. Waited for security to access room. Found Hitachi under ceiling cassette in fault 041. Checked over unit and power cycled unit. Monitored and no faults present. Possible cause is high ambient temperatures.
MSA-DFES | WA5105191 | 1 | Critical Fire Protection & Training | Main Building - Entrance - fire panel indicating it has low battery | Fire Protection Services | Fire Protection - Monitor System | 880.58 | Pass | Pass | 0 | 0 | 2 | 2022-02-04 08:40 | 2022-02-07 17:00 | 2022-02-04 09:30 | 2022-02-07 17:00 | 2022-02-04 11:30 |  |  | Start time: 9:30amFinish time: 11:30amBattery fault on FIP - Notifier 3030. Firmware requires update. 4x 26 a/h batteries changed out. System normal.
MSA-DTWD | WA5105484 | 3 | Equans Mechanical Services Australia | E523 - Air flow noisy | Air Conditioning | Room Air Conditioners | 204.07 | Fail | Fail | 5 | 5 | 2 | 2022-02-04 11:18 | 2022-02-11 17:00 | 2022-03-15 11:00 | 2022-02-11 17:00 | 2022-03-15 13:00 |  |  | ATTENDED SITE, SIGNED IN AND ACCESSED BUILDING B1 ROOM E523. ACCESSED VAVCONTROLLER AND CHECKED POWER AND CONTROL SIGNAL. DROVE THE CONTROLLER FROMTHE BMS AND CHECKED FOR CORRECT VOLTAGE AT CONTROLLER, ALL OK. THERE IS A FAULTWITH THE ACTUATOR OR CARD, BAE (EMPLOYED DIRECT THROUGH THE CAMPUS) TO INVESTIGATE AND RECTIFY AS IT IS STILL UNDER THEWARRANTY PERIOD.LOCKED THE AIRFLOW AND 40% OPEN UNTIL FURTHER INVESTIGATION IS CARRIED OUT.
MSA-DTWD | WA5106701 | 2 | Equans Mechanical Services Australia | Cafe - Cool room Fridge not working | Refrigeration | Coolroom | 204.07 | Pass | Pass | 0 | 0 | 2 | 2022-02-07 10:32 | 2022-02-10 17:00 | 2022-02-08 12:30 | 2022-02-10 17:00 | 2022-02-08 14:30 |  |  | FOUND CONDENSER BADLY BLOCKED, WASHED OUT COILS. FREEZER COMPRESSOR INEFFICIENT. COOLROOM TRIPPING HP SWITCH - REQUIRES REPLACEMENT
MSA-DTWD | WA5106912 | 2 | Equans Mechanical Services Australia | Rodent has chewed through outlet/condensation hose. I have repaired temporarily. | Air Conditioning | Room Air Conditioners | 236.21 | Pass | Pass | 0 | 0 | 2 | 2022-02-07 12:42 | 2022-02-10 17:00 | 2022-02-09 11:00 | 2022-02-10 17:00 | 2022-02-09 13:00 |  |  | A block: outside ground floor class room in passage way water is leaking through the ceiling tiles, accessed the ceiling space and found that a romantic had chewed the drain hose from the high wall split and pulled it out of the pvc pipe. Fitted a sleeve over the pipe and secured in the pvc pipe , wrapped in aluminium tape to prevent any more damage.
MSA-DTWD | WA5107217 | 1 | ECO PLUMBING AND GAS PTY LTD | Canteen - unisex toilet - is blocked | Plumbing & Drainage | Toilets/Cisterns | 423.6 | Pass | Pass | 0 | 0 | 2 | 2022-02-07 15:48 | 2022-02-08 17:00 | 2022-02-08 14:45 | 2022-02-08 17:00 | 2022-02-08 16:45 |  |  | Used drain machine to clear blockage at canteen toilets
MSA-DTWD | WA5110057 | 1 | Precise Air Group | Glazing work shop room U015* - evap aircon constantly dumping | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | 0 | 0 | 2 | 2022-02-09 15:46 | 2022-02-10 17:00 | 2022-02-10 09:30 | 2022-02-10 17:00 | 2022-02-10 11:30 |  |  | Adjusted floats and bleed valves. Issues rectified
MSA-DTWD | WA5126481 | 1 | Techworks Plumbing | T block, Male toiles - Urinal auto flush not working | Plumbing & Drainage | Toilets/Cisterns | 257.15 | Pass | Pass | 0 | 0 | 2 | 2022-02-14 08:09 | 2022-02-15 17:00 | 2022-02-14 11:00 | 2022-02-15 17:00 | 2022-02-14 13:00 |  |  | Debris in bottom of cistern, cleaned out and reposition the old flush rubber put back together and recommissioned it seems to be working fine
MSA-DTWD | WA5127621 | 1 | Equans Mechanical Services Australia | J12 - aircon not working | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 2 | 2022-02-14 13:33 | 2022-02-15 17:00 | 2022-02-14 14:00 | 2022-02-15 17:00 | 2022-02-14 16:00 |  |  | Gathered tools and equipment started fault check on evaporative a/c. Found to be working all OK. Due to humidity performance not efficient. Reported findings to Dennis. Completed paperwork and signed out.
MSA-DTWD | WA5127972 | 2 | Equans Mechanical Services Australia | G Block - GF7 - Aircon leaking water from inside unit and not working properly | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 2 | 2022-02-14 15:10 | 2022-02-17 17:00 | 2022-02-15 08:00 | 2022-02-17 17:00 | 2022-02-15 10:00 |  |  | Found the ceiling cassette in GF7 leaking water . Unblocked the drain , checked the operation of condenser running OK, watched it go through several cycles all OK.
MSA-DTWD | WA5133557 | 2 | Equans Mechanical Services Australia | C Block - Ground - CG10 Workshop - Evap constantly leaking water | Air Conditioning | Evaporative Coolers | 778.81 | Fail | Fail | 1 | 1 | 2 | 2022-02-15 11:51 | 2022-02-18 17:00 | 2022-02-23 14:00 | 2022-02-18 17:00 | 2022-02-23 16:00 |  |  | FOUND EC 10 SUMP DUMP VALVE FAILED AND OVER FLOWING UNITAND EC 12 HAS FAILED WATER SOLENOID VALVE AND TRANSFORMER. PICKED UP PARTS FROM SUPPLIERS AND RETURNED TO SITE. REPLACED SUMP DUMP ON EC 10 AND REPLACED WATER SOLINOID VALVE AND TRANSFORMER ON EC12. CHECKED OPERATION OF BOTH UNITS AND THAT WATER NO LONGER LEAKING. ALL OK. CLEANED UP WORK AREA AND DISPOSED OF RUBBISH. COMPLETED PAPERWORK AND LOGGED OFF JOB.
MSA-DTWD | WA5142594 | 1 | Precise Air Group | A block - Level 1 - A51 - see details | Air Conditioning | Room Air Conditioners | 235.48 | Fail | Fail | 0 | 0 | 2 | 2022-02-16 16:07 | 2022-02-17 17:00 | 2022-02-18 14:00 | 2022-02-17 17:00 | 2022-02-18 16:00 |  |  | Attended site signed in and located reported area. Assessed BMS and air handling unit found dampers closed opened up and retored air flow to area. Unsure if damper motors are intentionally off-line or need repairs. Will speak to regular technician and monitor and will provide a quote if necessary
MSA-DTWD | WA5151012 | 2 | Techworks Plumbing | G Block - Male student toilet - Male toilet cubicle is constantly flowing and cistern wont fill | Plumbing & Drainage | Toilets/Cisterns | 222.23 | Pass | Pass | -1 | -1 | 2 | 2022-02-17 10:03 | 2022-02-22 17:00 | 2022-02-17 11:00 | 2022-02-22 17:00 | 2022-02-17 13:00 |  |  | Cistern kept overfilling into bowl, debris was under the flush rubber so cleaned that out and re calibrated the rubber seems to be working fine
MSA-DCA | WA5151187 | 3 | Techworks Electrical | faulty light in female toilet and ANTE room | Electrical | Lighting, Internal | 756.3 | Pass | Pass | 0 | 0 | 2 | 2022-02-17 11:25 | 2022-02-24 17:00 | 2022-02-23 06:30 | 2022-02-24 17:00 | 2022-02-23 08:30 |  |  | Changed faulty light fitting to led in female toilets.Spare lights left on site.
MSA-DTAG | WA5163740 | 2 | Australian HVAC Services Pty. Ltd. | Lvl 4 - Court Room 41 - Air con doesn’t appear to be working, courtroom is warm | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Pass | 0 | 0 | 2 | 2022-02-18 11:40 | 2022-02-23 17:00 | 2022-02-21 08:00 | 2022-02-23 17:00 | 2022-02-21 10:00 |  |  | Attend site. Access level 4 court 41. Found court in session. Access bms and check temps. Found temps to be reading 22.5 degrees. Check vav box operation and found to be working as normal. Access court 41 and check sensor calibration, all ok. Possible cause warm weekend.
MSA-DCA | WA5163895 | 2 | Techworks Electrical | external - Poster box at James Street tunnel entrance - lights not working. driver to be relaced | Electrical | General Electrical | 392.47 | Pass | Pass | 0 | 0 | 2 | 2022-02-18 13:06 | 2022-02-23 17:00 | 2022-02-22 11:00 | 2022-02-23 17:00 | 2022-02-22 13:00 |  |  | Walked through with Ken, engaged overrides and we found the side tubes and each poster box was on and working fine, no action taken as no fault found
MSA-DTWD | WA5175104 | 1 | Equans Mechanical Services Australia | Aicon south side T/block not cooling | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 2 | 2022-02-21 10:21 | 2022-02-22 17:00 | 2022-02-22 11:00 | 2022-02-22 17:00 | 2022-02-22 13:00 |  |  | ROOM THERMOSTAT IN THE WRONG PLACE, RELOCATED.
MSA-DCA | WA5190004 | 2 | EQUANS Mechanical Services (WA) Pty Limited | South West Room (SRO meeting room) - Split system AC fails to switch on using wall controller | Air Conditioning | Room Air Conditioners | 240.7 | Pass | Pass | -1 | -1 | 2 | 2022-02-24 09:56 | 2022-03-01 17:00 | 2022-02-25 08:00 | 2022-03-01 17:00 | 2022-02-25 10:00 |  |  | Found the isolator on the outdoor unit switched off. Reinstated power to the unit and checked the operation, cleaned filters and unit ran correctly with no faults to report.
MSA-DTWD | WA5191547 | 2 | Falcetta Plumbing and Gas | G Block - Male student toilet - Male toilet cubicle is constantly flowing and cistern wont fill | Plumbing & Drainage | Toilets/Cisterns | 616.5 | Pass | Pass | 0 | 0 | 2 | 2022-02-25 07:11 | 2022-03-01 17:00 | 2022-03-01 14:00 | 2022-03-01 17:00 | 2022-03-01 16:00 |  |  | Replaced invisi cistern
MSA-DTWD | WA5193736 | 2 | Precise Air Group | E203 - AC not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-02-25 13:38 | 2022-03-02 17:00 | 2022-03-01 14:00 | 2022-03-02 17:00 | 2022-03-01 16:00 |  |  | Travelled to site, gained acces found room 203 in fault,began fault finding system found units in U4 fault commaerror between indoor and outdoor boards. Checked allconnection, reset system, checked operation. Recommendedto staff that they make sure system is off after the dayand not kept on 18. Cleared debris from site
MSA-DTWD | WA5200117 | 1 | BAKE-QUIP PTY LTD | combi oven is leaking at the tap | Equipment | Catering Equipment | 946.9 | Pass | Pass | 0 | 0 | 2 | 2022-03-01 14:11 | 2022-03-02 17:00 | 2022-03-02 08:20 | 2022-03-02 17:00 | 2022-03-02 10:20 |  |  | See service report
MSA-DTWD | WA5203468 | 1 | SCAVENGER SUPPLIES PTY LTD | car park facing Oak street in front of Customer Service - fire hydrant head leaking pretty badly | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 247.68 | Pass | Pass | 0 | 0 | 2 | 2022-03-03 13:06 | 2022-03-04 17:00 | 2022-03-03 14:00 | 2022-03-04 17:00 | 2022-03-03 16:00 |  |  | COMPLETED 03/03/2022Replaced seat washer.Isolated water and pumpsPriority 1, 2 hours on siteTHIS SITE ALREADY HAD BEEN QUOTED FOR A 5 YEARLY OVERHAUL OF ALL HYDRANTS-AWAITING APPROVAL-STRONGLY REQUEST APPROVAL SO AS TO AVOID FURTHER CALL OUTS TO FAILURES.
MSA-DTAG | WA5203712 | 3 | Australian HVAC Services Pty. Ltd. | Meeting Room 3 - Aircon very cold and unable to regulate - Notes below | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Pass | 0 | 0 | 2 | 2022-03-03 15:37 | 2022-03-11 17:00 | 2022-03-08 08:00 | 2022-03-11 17:00 | 2022-03-08 10:00 |  |  | Gained access to bms and interview room 3, found that the outlet dampers to the room was fully opened and pumping out a lot of air, closed both dampers quiet a bit and spoke to the woman she was happy with the amount now, also changed the set point from 21 degrees to 22. Said to see how if feels over the next few days and if any problems to call back.
MSA-DTWD | WA5204755 | 1 | Lane's Plumbing | Bathroom C wing - Left basin S bend leak | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 2 | 2022-03-04 12:58 | 2022-03-08 17:00 | 2022-03-04 15:30 | 2022-03-08 17:00 | 2022-03-04 17:30 |  |  | job completed - REPAIR LEAKING PIPES FLAT C DEMPSTER
MSA-DFES | WA5206818 | 2 | Australian HVAC Services Pty. Ltd. | GYM area - Air-conditioning - (Treadmill room) is leaking significant amount of water when on | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Pass | 0 | 0 | 2 | 2022-03-08 09:40 | 2022-03-11 17:00 | 2022-03-09 08:00 | 2022-03-11 17:00 | 2022-03-09 10:00 |  |  | Attended service call, found ac 8 hah over flowed it's driptray. Isolated ac, stripped evap unit covers & cut drainline, used pipe snake to remove obstruction in evap unit. Reconnected drainline & tested with water. Rebuilt evap unit & reinstated power.
MSA-DCA | WA5207031 | 3 | Techworks Electrical | Ground - floor cafe - lights are not working | Electrical | Lighting, Internal | 313.22 | Pass | Pass | -1 | -1 | 2 | 2022-03-08 10:45 | 2022-03-15 17:00 | 2022-03-08 12:30 | 2022-03-15 17:00 | 2022-03-08 14:30 |  |  | Replaced blown globe
MSA-DFES | WA5207719 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | lounge room - antenna - issues with antenna | ICT/Audiovisual | Hardware / Equipment | 240.53 | Pass | Pass | 0 | 0 | 2 | 2022-03-08 13:17 | 2022-03-11 17:00 | 2022-03-10 09:30 | 2022-03-11 17:00 | 2022-03-10 11:30 |  |  | Attended site 0930, proceeded to investigate TV not receiving a proper signal. I found that the TV outlet behind the tv was damaged and would not securely hold TVs antenna cable, I replaced the outlet and this enabled the cable to stay connected securely however the fault was still present in receiving poor signal. After further investigation I found the coax on the roof was disconnected from the antenna, I reconnected the cable securely, and retuned the TV. The TV is now receiving a full catalogue of channels with good signal strength. Informed staff of outcomes and left site at 1130.
MSA-DTWD | WA5215703 | 2 | Equans Mechanical Services Australia | BF15 & BG14 - Airconditioning does not work after hours with set schedule - see notes below | Air Conditioning | Room Air Conditioners | 347.07 | Pass | Pass | 0 | 0 | 2 | 2022-03-10 15:29 | 2022-03-15 17:00 | 2022-03-14 08:00 | 2022-03-15 17:00 | 2022-03-14 10:00 |  |  | Arrived on site signed in. Checked in with Marty gained access keys Checked B Block all operating correctly after Rory's completed checks and report. Monitored. Cleaned up and completed paperwork and signed out.
MSA-DTWD | WA5216132 | 1 | Lane's Plumbing | BLD 830 - Glasshouse - Faulty Retic | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 2 | 2022-03-11 08:10 | 2022-03-14 17:00 | 2022-03-11 11:00 | 2022-03-14 17:00 | 2022-03-11 13:00 |  |  | job completed - REPAIR RETIC TO GLASSHOUSE
MSA-DTWD | WA5216481 | 3 | AWB Co. | Repair pavers dislodged outside S105 | Paving & Roadworks | Paving | 210 | Pass | Pass | 0 | 0 | 2 | 2022-03-11 10:29 | 2022-03-18 17:00 | 2022-03-18 06:30 | 2022-03-18 17:00 | 2022-03-18 08:30 |  |  | Removed four sections of sunk and raised pavers, re levelled with sand and laid existing pavers back.
MSA-DTWD | WA5216776 | 1 | Equans Mechanical Services Australia | damaged Air Con. wall controller | Air Conditioning | Room Air Conditioners | 388.63 | Fail | Fail | 1 | 1 | 2 | 2022-03-11 12:44 | 2022-03-14 17:00 | 2022-03-18 12:30 | 2022-03-14 17:00 | 2022-03-18 14:30 |  |  | Checked the wall sensor in the Hair room T041& found nothing on the display &the front had been pulled off & incorrectly forced back. This had disconnected it from the CO2 module& bent the pins on the module, which in turn inhibited its reconnection to the back plate.Removed front & co2 module, straightened pins &reconnected module. Reinstalled assembly to the back plate, display came up ok checked operation ok
MSA-DCA | WA5231498 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis Street Building - Level 6 - plant room 11 - AHU8.01 mechanical damper control bracket broken | Air Conditioning | Building HVAC Maintenance (Major Plant) | 387.22 | Fail | Fail | 2 | 2 | 2 | 2022-03-15 11:55 | 2022-03-16 17:00 | 2022-03-31 14:00 | 2022-03-16 17:00 | 2022-03-31 16:00 |  |  | Attended site, signed in and accessed plant room 11 ahu 8.01.Found the supply air dampers with a link and washers missing. Drove to a supplier to collect parts and materials, returned to site and fitted new damper link and fittings. Stroked the damper and drove the actuator, dampers are now operating correctly.
MSA-DCA | WA5231811 | 2 | Precise Air Group | Main Building - Level 1 - Administration office 2 - | Air Conditioning | Room Air Conditioners | 393.75 | Pass | Pass | 0 | 0 | 2 | 2022-03-15 15:06 | 2022-03-18 17:00 | 2022-03-17 09:30 | 2022-03-18 17:00 | 2022-03-17 11:30 |  |  | Found unit had dropped over the years, re aligned working ok
MSA-MRWA | WA5249168 | 0 | Siemens Ltd | Rear Entry door - Access control is keeping door open **see notes | Security | Access Control |  | Pass | Pass | 0 | 0 | 2 | 2022-03-17 07:03 | 2022-03-17 09:03 | 2022-03-17 08:00 | 2022-03-17 11:03 | 2022-03-17 10:00 |  |  | Replace faulty breakglass unit and reconnect auto doorto access control. Auto door is now functioning as normal Hour
MSA-DFES | WA5274817 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | First Floor - Mens toilet - leaking sink | Plumbing & Drainage | Water | 414.2 | Pass | Pass | 0 | 0 | 2 | 2022-03-18 11:46 | 2022-03-23 17:00 | 2022-03-22 07:15 | 2022-03-23 17:00 | 2022-03-22 09:15 |  |  | Attended site for first floor males toilet sink leaking upon inspection I have not found a leaking sink but a mixer tap I have replaced the mixer tap with a new tap due to the existing tap being damaged by wear and tear
MSA-DCA | WA5286311 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Investigate steam generator 1 - second low fault alarm - see notes below | Equipment | Compressors, Generators | 645.23 | Fail | Fail | 0 | 0 | 2 | 2022-03-21 14:34 | 2022-03-22 17:00 | 2022-03-24 14:00 | 2022-03-22 17:00 | 2022-03-24 16:00 |  |  | Attended site with Boiler Tronics, signed in and accessed the chiller plantroom. Checked, tested and monitored the steam generator. Found various parts faulty with the steam generator 1and the feed tank. A Quote is being prepared to replace these faulty parts.
MSA-DTWD | WA5287140 | 2 | Techworks Electrical | workshops corridoor outside classroom 9, power point coming away from wall | Electrical | General Electrical | 415.02 | Pass | Pass | 0 | 0 | 2 | 2022-03-22 10:31 | 2022-03-25 17:00 | 2022-03-23 12:30 | 2022-03-25 17:00 | 2022-03-23 14:30 |  |  | Replaced additional damaged gpo in admin kitchenette
MSA-DTWD | WA5289960 | 2 | Precise Air Group | Cafe kitchen Aircon is not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 340.14 | Pass | Pass | -1 | -1 | 2 | 2022-03-24 14:38 | 2022-03-29 17:00 | 2022-03-25 08:00 | 2022-03-29 17:00 | 2022-03-25 10:00 |  |  | Attended site for Cafe unit. Both ran on arrival. Carried out functional and safety checks and found no issues with system during visit on-site, only thing found was a little bhild up of grease on filters from being located in a kitchen but not enough to severely impede operation. Filters cleaned and units operational. Was asked to look at common area unit while on site. Power had tripped to unit. Restored power and ran checks on unit and appeared to be operating normally, will monitor
MSA-DCA | WA5289979 | 2 | Protek 24/7 Building & Maintenance | Jubilee -Ground Level - External Area, Crn James St. & Beaufort St - see details below | Building | General Building | 387.5 | Pass | Pass | 0 | 0 | 2 | 2022-03-24 14:56 | 2022-03-29 17:00 | 2022-03-28 08:00 | 2022-03-29 17:00 | 2022-03-28 10:00 |  |  | Repairs to Street Signage
MSA-DCA | WA5290852 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 3 - server room - AC4 showing error messages | Air Conditioning | Room Air Conditioners | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-03-25 12:15 | 2022-03-30 17:00 | 2022-03-30 14:00 | 2022-03-30 17:00 | 2022-03-30 16:00 |  |  | Attended site, signed and accessed the level 3 comms room. Checked a/c 4 controller and found a E4 error code. Accessed level 4 condensing units and checked the running gas pressures. Gas pressures indicated a gas leak on the system. Collected details and organised a quote to carry out works.
MSA-DTAG | WA5290942 | 3 | Australian HVAC Services Pty. Ltd. | Level 3 - Toilet - A/C ceiling vent has become detached in business services staff toilet – see belo | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Pass | -1 | -1 | 2 | 2022-03-25 13:08 | 2022-04-01 17:00 | 2022-03-28 08:00 | 2022-04-01 17:00 | 2022-03-28 10:00 |  |  | Attend site. Access level 3 toilet and check exhaust grill. Found grill to have fallen out of ceiling. Found grill held in by magnets and one magnet is missing. Drill holes in grill core. Fit grill and screw into frame. Grill now secure.
MSA-DCA | WA5294129 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Old Jail - aircon is leaking | Air Conditioning | Building HVAC Maintenance (Major Plant) | 470.93 | Pass | Pass | 0 | 0 | 2 | 2022-03-28 13:12 | 2022-03-28 15:12 | 2022-03-28 14:00 | 2022-03-28 17:12 | 2022-03-28 16:00 |  |  | Attended site, signed in and accessed the jail affected a/c unit. Isolated unit and removed the front covers, found the condensate tray overflowing. Located the drainline and vacummed out the blockage. Tested the drain line with water and is now draining correctly.
MSA-DTWD | WA5294903 | 2 | ECO PLUMBING AND GAS PTY LTD | Block D - female staff toilets - faulty cistern | Plumbing & Drainage | Water | 415.27 | Pass | Pass | 0 | 0 | 2 | 2022-03-29 09:54 | 2022-04-01 17:00 | 2022-04-01 11:00 | 2022-04-01 17:00 | 2022-04-01 13:00 |  |  | Repaired leaking hot water unit
MSA-DCA | WA5295487 | 2 | Protek 24/7 Building & Maintenance | Main Building - Chaos Rehearsal Room & Old Office Rehearsal room - see details below | Building | General Building | 374.3 | Pass | Pass | 0 | 0 | 2 | 2022-03-29 14:03 | 2022-04-01 17:00 | 2022-03-31 11:00 | 2022-04-01 17:00 | 2022-03-31 13:00 |  |  | Repair window ropes
MSA-DTAG | WA5296168 | 3 | O'Brien Glass With Care | Basement - Cell 3 - Graffiti scratched into window tint | Glazing | Solar Control Film (Tint) |  | Fail | Fail | 3 | 3 | 2 | 2022-03-30 09:53 | 2022-04-06 17:00 | 2022-04-26 06:30 | 2022-04-06 17:00 | 2022-04-26 08:30 |  |  | Replaced scratched film
MSA-DTWD | WA5296613 | 2 | WA BOILER SPARES & SERVICE | B28 Glasshouse Heater Boiler - has no pilot light and cannot been started | Equipment | Compressors, Generators | 330 | Pass | Pass | -1 | -1 | 2 | 2022-03-30 13:39 | 2022-04-04 17:00 | 2022-03-31 08:00 | 2022-04-04 17:00 | 2022-03-31 10:00 |  |  | Attended site, water heating boiler has leaking heat exchanger, parts no longer available as manufacturer has ceased trading. Obtaining quote for replacement unit.
MSA-DTWD | WA5296714 | 1 | Techworks Plumbing | Science Block - S 9.3.1 Male Toilet - Urial continually running ( turned off At stop Cock ) tagged o | Plumbing & Drainage | Toilets/Cisterns | 400.15 | Pass | Pass | 0 | 0 | 2 | 2022-03-30 15:03 | 2022-03-31 17:00 | 2022-03-31 06:30 | 2022-03-31 17:00 | 2022-03-31 08:30 |  |  | Attended constantly running urinal, Founf bug caught in urinal outlet cause the urinal to drain slowly so seemed like it was constantly running. Cleaned and tested urinal which still runs for about 20 seconds and then shuts off.
MSA-DTAG | WA5301951 | 3 | PPM Project Painting & Maintenance | Ground - Graffiti on the wall nearest McIver, | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-04-01 15:12 | 2022-04-08 17:00 | 2022-04-06 11:00 | 2022-04-08 17:00 | 2022-04-06 13:00 |  |  | job completed - Apply stain blocker and repaint walls in exterior low sheen tomatch existing
MSA-DTAG | WA5303088 | 3 | PPM Project Painting & Maintenance | Ground - External wall McIver side - graffiti on the wall nearest McIver | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-04-04 08:11 | 2022-04-11 17:00 | 2022-04-10 11:00 | 2022-04-11 17:00 | 2022-04-10 13:00 |  |  | Removal of graffiti
MSA-DTWD | WA5303879 | 2 | M Construction (WA) | D-Block - Marketing - remove two broken white boards from wall in Marketing | Building | General Building | 228.42 | Fail | Fail | 21 | 21 | 2 | 2022-04-04 13:08 | 2022-04-07 17:00 | 2022-08-29 08:00 | 2022-04-07 17:00 | 2022-08-29 10:00 |  |  | Removed broken whiteboards from wall and made good.
MSA-DTWD | WA5304092 | 2 | Techworks Electrical | Workshops - Carpentry - bench grinder taking too long to stop rotation when turned off | Equipment | Power Tools | 408.97 | Pass | Pass | 0 | 0 | 2 | 2022-04-04 14:32 | 2022-04-07 17:00 | 2022-04-07 08:00 | 2022-04-07 17:00 | 2022-04-07 10:00 |  |  | No electrical fault found on bench grinder. Motor bearing is damaged causing shaft to freely spin. Recommended to replace motor.
MSA-DTWD | WA5304139 | 2 | Techworks Electrical | Workshops Carpentry, bench grinder stop button not working | Equipment | Power Tools | 526.15 | Pass | Pass | 0 | 0 | 2 | 2022-04-04 15:02 | 2022-04-07 17:00 | 2022-04-07 12:30 | 2022-04-07 17:00 | 2022-04-07 14:30 |  |  | Replaced faulty stop button with start and em push stop button.
MSA-DFES | WA5304156 | 2 | Australian HVAC Services Pty. Ltd. | GROUND - DORM 2 - AIR CONDITIONER IN DORM 2 LEAKING WATER | Air Conditioning | Room Air Conditioners | 394.09 | Pass | Pass | 0 | 0 | 2 | 2022-04-04 15:13 | 2022-04-07 17:00 | 2022-04-05 14:00 | 2022-04-07 17:00 | 2022-04-05 16:00 |  |  | Arrived on-site, spoke with on-site representative who directed me to leaking A/C unit in dorm 2, dismantled indoor evaporator unit disconnected drain system from evaporator & drained excess built up water, found dirt build up inside water and attempted clearing blockage with warm water but failed, left site for supplier & obtained nitrogen, using specialist tooling blew out drainwork using nitrogen, reassembled indoor evaporator unit and carried out operational testing, found unit & drainage to be fully functional.
MSA-DTWD | WA5306538 | 2 | Precise Air Group | D201 -Level 2 - Aircon not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | -1 | -1 | 2 | 2022-04-06 14:16 | 2022-04-11 17:00 | 2022-04-07 11:00 | 2022-04-11 17:00 | 2022-04-07 13:00 |  |  | Attended site and completed pre start paperwork and signed in. Accessed bms to inspect operation of fan coil unit serving d201.I was unable to gain any information from bms as most values are question marks. Bms issues for d block need to be rectified as we are unable to get a clear picture of how plant is operating. Accessed classroom and inspected. Switched system on at the pushbutton. Found fcu to start and run with out fault. Monitored and left operating. Bms for d block needs to be rectified and put on the same system as the rest of the tafe. No further works required by PAG.
MSA-DFES | WA5312376 | 3 | MR POTHOLE | Near BA house -Ground - see details | Paving & Roadworks | Asphalt |  | Pass | Pass | -1 | -1 | 2 | 2022-04-11 13:16 | 2022-04-20 17:00 | 2022-04-14 10:15 | 2022-04-20 17:00 | 2022-04-14 12:15 |  |  | job completed - repaired damaged asphalt
MSA-DTWD | WA5318212 | 2 | AWB Co. | Glasshouse - Faulty/ damaged rollers on right side of sliding door - Rollers on door are worn | Building | Doors | 210 | Pass | Pass | -1 | -1 | 2 | 2022-04-12 09:22 | 2022-04-19 17:00 | 2022-04-14 08:00 | 2022-04-19 17:00 | 2022-04-14 10:00 |  |  | top sliding rail welded onto the top of the door which istaking the weight of the door away from the bottom track.Recommend Action Glass Track length 2 doors 4860Braf submitted to replace - brafe declinedinvoiced cost to date
MSA-DTWD | WA5377793 | 3 | Falcetta Plumbing and Gas | Level 2 - Female staff Toilet - Toilet seat loose/ Broken - | Plumbing & Drainage | Toilets/Cisterns | 680.28 | Pass | Pass | 0 | 0 | 2 | 2022-04-20 09:04 | 2022-04-28 17:00 | 2022-04-28 14:00 | 2022-04-28 17:00 | 2022-04-28 16:00 |  |  | replaced toilet seat and repaired 2x cisterns
MSA-DTWD | WA5380141 | 3 | AWB Co. | Level 1 - Lift 2 - Ballast blown in flouro light in lift | Electrical | Lighting, Internal | 399.37 | Pass | Pass | 0 | 0 | 2 | 2022-04-22 08:44 | 2022-05-02 17:00 | 2022-05-02 11:00 | 2022-05-02 17:00 | 2022-05-02 13:00 |  |  | Attended site signed in completed jsa. got keys from Dave for job. Had Dave come show us which lift and also isolate so doors stay open. Isolated lights and power in lift switchboard on top lift motor room. Found it was a ballast and had to source replacement, replaced ballast also tubes. Light now works perfectly. *** job completed ***
MSA-DTWD | WA5381808 | 3 | Equans Mechanical Services Australia | Block 8 - Level 1 - Main Plantroom -Belts are split or missing | Equipment | Building Equipment | 429.02 | Pass | Pass | -1 | -1 | 2 | 2022-04-26 11:46 | 2022-05-03 17:00 | 2022-04-26 14:00 | 2022-05-03 17:00 | 2022-04-26 16:00 |  |  | Found on maintenance and client raised job as urgent as units could fail at any time.2 x AHUs require new v belts. Picked up parts from suppliers and returned to site. Fitted and adjusted belts. Checked operation, all ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5382029 | 0 | Techworks Plumbing | AF10 - Male toilet - water pipe reptured in wall | Plumbing & Drainage | Drainage | 309.95 | Pass | Pass | 0 | 0 | 2 | 2022-04-26 13:15 | 2022-04-26 15:15 | 2022-04-26 14:00 | 2022-04-26 17:15 | 2022-04-26 16:00 |  |  | Burst pipe in A block male toilets level 1 south metro tafe Mandurah, cabinet maker has gone through water pipe and damaged other pipe trying to expose pipes, repaired & fixed both water pipes
MSA-DCA | WA5382903 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Robert Steel work shop - issue with the swtichboard and RCDs tripping - water in switchboard | Electrical | General Electrical | 404.57 | Pass | Pass | 0 | 0 | 2 | 2022-04-27 10:02 | 2022-04-27 12:02 | 2022-04-27 11:45 | 2022-04-27 14:02 | 2022-04-27 13:45 |  | WACCES | Work Order closed by Denise McCartney 10/05/2022
MSA-DTWD | WA5384034 | 3 | Falcetta Plumbing and Gas | H Block - Outside of NE Corner - Valve to water fountain issues - See notes | Plumbing & Drainage | Water | 293.84 | Pass | Pass | 0 | 0 | 2 | 2022-04-28 09:17 | 2022-05-05 17:00 | 2022-05-05 11:00 | 2022-05-05 17:00 | 2022-05-05 13:00 |  |  | removed old valve and leaking fitting, installed new valve, new mi bpress at RPZD inlet and re-clipped
MSA-DTWD | WA5384622 | 2 | Protek 24/7 Building & Maintenance | Roof leak over welding bays | Building | Ceiling | 364.4 | Fail | Fail | 0 | 0 | 2 | 2022-04-28 14:16 | 2022-05-03 17:00 | 2022-05-04 08:00 | 2022-05-03 17:00 | 2022-05-04 10:00 |  |  | Repair roof leak over welding Bays
MSA-DFES | WA5385101 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main Administration - Ground - Campus Services Office - light is buzzing and flickering see notes | Electrical | General Electrical | 404.37 | Pass | Pass | 0 | 0 | 2 | 2022-04-29 07:02 | 2022-05-05 17:00 | 2022-05-05 11:00 | 2022-05-05 17:00 | 2022-05-05 13:00 |  |  | Attended site and found 3 x fluro panel lights not working. Left site to get parts from nearest wholesaler. Returned to site and replaced 3 x fluro panel lights with new LED panel lights and tested. Notified staff and left site.
MSA-DTWD | WA5385262 | 2 | Precise Air Group | A024.8 - Air extraction unit - filters faulty | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-04-29 08:45 | 2022-05-04 17:00 | 2022-05-03 08:00 | 2022-05-04 17:00 | 2022-05-03 10:00 |  |  | Attended site signed in and gained access to the area. Got given filters that were removed by on site staff and gave another clean. Found area with extraction fan and gained access to filter service slot. Reinstalled clean filter and confirmed fan operation.
MSA-MRWA | WA5385282 | 1 | EQUANS Mechanical Services (WA) Pty Limited | CRAC unit - server room - alarm | Air Conditioning | Room Air Conditioners | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-04-29 08:55 | 2022-05-02 17:00 | 2022-04-29 12:30 | 2022-05-02 17:00 | 2022-04-29 14:30 |  |  | Attended site. Investigated crac unit in alarm. Found unit in comp short cycle fault. Reset fault and tested operation. All ok, unit operating normally. Completed paperwork
MSA-DTAG | WA5390591 | 3 | Gilmour & Jooste Electrical | Women's public toilet - light bulb not working | Electrical | General Electrical | 129.67 | Pass | Pass | -1 | -1 | 2 | 2022-05-02 13:58 | 2022-05-09 17:00 | 2022-05-03 13:15 | 2022-05-09 17:00 | 2022-05-03 15:15 |  |  | Inspected court lighting. No lighting out in public toilets. Inspected lighting in area and advised court staff that lights are all working.
MSA-DTWD | WA5390648 | 2 | Schneider Electric Australia Pty Ltd | B209 - swipe reader does not work | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2022-05-02 14:13 | 2022-05-05 17:00 | 2022-05-05 14:00 | 2022-05-05 17:00 | 2022-05-05 16:00 |  |  | job completed - Attended site and inspected fault on level 2 B Block door.Found that the reader is faulty and requires replacing.Also found that both cabinet backup batteries have corroded terminals and will also need batteriesto be replaced as well as re terminating battery connectors.Power supply voltage is still correct and operating.
MSA-DCA | WA5392885 | 2 | FCT SURFACE CLEANING | Ground – external - Out front of State Library - see details below | Cleaning | Cleaning |  | Pass | Pass | 0 | 0 | 2 | 2022-05-03 13:13 | 2022-05-06 17:00 | 2022-05-05 11:00 | 2022-05-06 17:00 | 2022-05-05 13:00 |  |  | Removal of graffiti
MSA-DTWD | WA5401052 | 1 | Techworks Plumbing | Building, Block or Unit Metal fabrication work shop(F/Block) disable toilet is block | Plumbing & Drainage | Toilets/Cisterns | 673.15 | Pass | Pass | 0 | 0 | 2 | 2022-05-10 15:17 | 2022-05-11 17:00 | 2022-05-10 15:30 | 2022-05-11 17:00 | 2022-05-10 17:30 |  |  | Unblocked toilet but need to return to fix pan connector
MSA-DTWD | WA5413488 | 3 | AWB Co. | E313 - Fire damaged outdoor light switch and mounting block | Electrical | General Electrical | 278.51 | Pass | Pass | 0 | 0 | 2 | 2022-05-12 11:28 | 2022-05-19 17:00 | 2022-05-16 12:30 | 2022-05-19 17:00 | 2022-05-16 14:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located light switch , tested light switch and gpo for power, went to wholesaler to pick up parts,returned to site, isolated lighting circuits, removed old switch, used white spirits to clean tile behind switch as good as possible, fitted new ip66 switch , re energised circuit, tested lights and they are working as intended, cleaned up, packed up, completed paperwork, signed out** job completed **
MSA-DTWD | WA5437983 | 2 | BAKE-QUIP PTY LTD | E-Block - SK3 - lecturers oven not working, to be moved out | Equipment | Catering Equipment | 360 | Fail | Fail | 1 | 1 | 2 | 2022-05-16 11:58 | 2022-05-19 17:00 | 2022-05-25 08:00 | 2022-05-19 17:00 | 2022-05-25 10:00 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA5438532 | 2 | AWB Co. | B106 lights in foyer require replacing | Electrical | Lighting, Internal | 286.22 | Pass | Pass | 0 | 0 | 2 | 2022-05-16 15:02 | 2022-05-19 17:00 | 2022-05-17 10:15 | 2022-05-19 17:00 | 2022-05-17 12:15 |  |  | Attended site and signed in. Completed JSA. Located room B106. Found entry lights not working. Supply and replace with new lamps and cleaned out light covers. Tested all okay. Signed out. Job complete
MSA-DCA | WA5451099 | 2 | SCAVENGER SUPPLIES PTY LTD | Old Gaol - Ground Level - Investigate and address the cause of false fire alarm, reoccurrence | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 2 | 2022-05-17 07:36 | 2022-05-19 17:00 | 2022-05-17 11:00 | 2022-05-19 17:00 | 2022-05-17 13:00 |  |  | COMPLETED 19/5/22 - waiting on technician to complete failure codes to complete the claim. He is experiencing issues with his programmed login hence the delay. Apologies.
MSA-DCA | WA5454553 | 0 | Techworks Electrical | Centennary Gallery - has no power | Electrical | General Electrical | 418.63 | Pass | Pass | 0 | 0 | 2 | 2022-05-17 12:19 | 2022-05-17 14:19 | 2022-05-17 12:30 | 2022-05-17 16:19 | 2022-05-17 14:30 |  |  | nvestigated tripped main switch in mech services switchboard. Throughly tested and could not find the issue. Schneider advised us it has been off for a week. Livened back up and all working well
MSA-DTWD | WA5461723 | 3 | AWB Co. | G101 - 7 x lights out in hallway | Electrical | General Electrical | 341.42 | Pass | Pass | 0 | 0 | 2 | 2022-05-19 08:27 | 2022-05-26 17:00 | 2022-05-23 09:30 | 2022-05-26 17:00 | 2022-05-23 11:30 |  |  | Attended site and signed in. Completed JSA. Located area with faulty lighting. Replaced all faulty tubes and starters. Completed paperwork. Signed out. *** Job complete ***
MSA-DTAG | WA5462507 | 2 | Sapio Pty Ltd | Ground - Registry - Monitor on wall is not displaying security feed | Security | Access Control | 370 | Pass | Pass | -1 | -1 | 2 | 2022-05-19 15:45 | 2022-05-24 17:00 | 2022-05-20 08:00 | 2022-05-24 17:00 | 2022-05-20 10:00 |  |  | found indigo had been switched off.switched back on and auto logged in
MSA-DTAG | WA5468810 | 3 | Sapio Pty Ltd | B2 stairwell and lift lobby doors appear to be intermittent | Security | Access Control | 250 | Pass | Pass | -1 | -1 | 2 | 2022-05-20 12:39 | 2022-05-27 17:00 | 2022-05-23 08:45 | 2022-05-27 17:00 | 2022-05-23 10:45 |  |  | Job completed. PFM slip attached. No fault with reader or door, user error. Adjusted permissions to view reports in future of cardholders that experience issues.
MSA-DCA | WA5471141 | 0 | Techworks Electrical | Roof leak coming through light fittings | Electrical | Lighting, Internal | 249.27 | Pass | Pass | 0 | 0 | 2 | 2022-05-23 12:23 | 2022-05-23 14:23 | 2022-05-23 12:30 | 2022-05-23 16:23 | 2022-05-23 14:30 |  |  | Disconected 2x lights.
MSA-DFES | WA5472168 | 2 | Protek 24/7 Building & Maintenance | Workshop Entry - see details below | Building | General Building | 364.4 | Pass | Pass | 0 | 0 | 2 | 2022-05-23 15:02 | 2022-05-26 17:00 | 2022-05-26 09:30 | 2022-05-26 17:00 | 2022-05-26 11:30 |  |  | Repair leaking roof - Workshop Entry
MSA-DTWD | WA5472794 | 1 | BAKE-QUIP PTY LTD | E-Block -SK2 -lecturers oven thermostat sparking and tripping out | Equipment | Catering Equipment | 465.2 | Pass | Pass | 0 | 0 | 2 | 2022-05-24 10:31 | 2022-05-25 17:00 | 2022-05-25 14:00 | 2022-05-25 17:00 | 2022-05-25 16:00 |  |  | Refer to service report
MSA-DTWD | WA5479767 | 3 | AWB Co. | J107 NTH - J block Nth entrance 3 x lights out | Electrical | Lighting, Internal | 545.58 | Pass | Pass | -1 | -1 | 2 | 2022-05-27 11:37 | 2022-06-03 17:00 | 2022-05-30 14:45 | 2022-06-03 17:00 | 2022-05-30 16:45 |  |  | Attended site and signed in. Completed JSA. Located J block lights not working. Found out what parts we need. Left site to pick up parts. Returned and replaced 4x lights not working with new LED fittings. Also replaced 1x ES lamp. Disposed of all rubbish. Tested to make sure they’re all working correctly. **job complete**
MSA-MRWA | WA5481633 | 1 | Water2water Pty Ltd | Level 2 - Kitchenette - wall mounted Hot water urn has failed | Plumbing & Drainage | HWS/Units Electric & Gas | 423.23 | Pass | Fail | 0 | 0 | 2 | 2022-05-30 15:15 | 2022-05-31 17:00 | 2022-05-31 15:10 | 2022-05-31 17:00 | 2022-05-31 17:10 |  |  | Turned off sleep mode and cleared scale build up to restore flow to hot water unit
MSA-DCA | WA5496205 | 3 | Techworks Electrical | Level 3 - Corridor of Puccini Room - Light in the corridor of Puccini Room is faulty | Electrical | General Electrical | 392.47 | Pass | Pass | 0 | 0 | 2 | 2022-06-09 08:28 | 2022-06-16 17:00 | 2022-06-15 08:00 | 2022-06-16 17:00 | 2022-06-15 10:00 |  |  | Repaired light in hallway of Puccini room
MSA-DTWD | WA5513649 | 3 | Precise Air Group | Level 2 - D206 - Noisy aircon when fan motor starts up | Air Conditioning | Room Air Conditioners | 392.14 | Pass | Pass | -1 | -1 | 2 | 2022-06-14 12:12 | 2022-06-21 17:00 | 2022-06-16 09:30 | 2022-06-21 17:00 | 2022-06-16 11:30 |  |  | Replaced blocked filters
MSA-DTWD | WA5521799 | 2 | Precise Air Group | Broken Remote for Air-conditioning | Air Conditioning | Room Air Conditioners | 318.9 | Pass | Pass | 0 | 0 | 2 | 2022-06-15 10:56 | 2022-06-20 17:00 | 2022-06-17 08:00 | 2022-06-20 17:00 | 2022-06-17 10:00 |  |  | Attended site signed in and located reported area.Traveled to supplier and got universal controller.Travelled to site and programmed and test controller.Unit operational
MSA-DTWD | WA5534652 | 3 | Falcetta Plumbing and Gas | Level 2 - Student Toilets - waterless urinal blocked. toilet flushing faulty | Plumbing & Drainage | Toilets/Cisterns | 429.54 | Pass | Pass | 0 | 0 | 2 | 2022-06-16 12:51 | 2022-06-23 17:00 | 2022-06-23 14:00 | 2022-06-23 17:00 | 2022-06-23 16:00 |  |  | unblocked urinal and installed new outlet kit
MSA-MRWA | WA5562639 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Crack unit high pressure alarm - alarming | Air Conditioning | Building HVAC Maintenance (Major Plant) | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-06-20 08:52 | 2022-06-21 17:00 | 2022-06-20 09:30 | 2022-06-21 17:00 | 2022-06-20 11:30 |  |  | Attended site. Investigated alarm on crac units found crac 2a had faulted in loss of power and comp 1 high pressure fault. Crac 2b running. Power cycled to 2a to clear fault. Gained keys from fm to access remote condensers. Found breaker on remote condenser for 2a had tripped. Reset. Accessed server room and switched 2b to standby and tested operation of 2a. Checked amps, all ok. Switched back to auto. Power outage in the city caused the units to trip. Completed paperwork.
MSA-DTWD | WA5562891 | 2 | Lane's Plumbing | Ground floor - Mens Bathroom - Loose Taps | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 2 | 2022-06-20 10:28 | 2022-06-23 17:00 | 2022-06-22 09:30 | 2022-06-23 17:00 | 2022-06-22 11:30 |  |  | job completed - REPAIR LOOSE TAPS TO MENS BATHROOM ADMIN
MSA-DTWD | WA5565806 | 2 | Techworks Electrical | Restaurant walkway - Block external lights on walkway by restaurant not working | Electrical | General Electrical | 996.86 | Pass | Pass | -1 | -1 | 2 | 2022-06-22 11:34 | 2022-06-27 17:00 | 2022-06-23 14:00 | 2022-06-27 17:00 | 2022-06-23 16:00 |  |  | Replaced downlights with new led downlights in E block walkway and D block student service area.
MSA-DCA | WA5565930 | 2 | Techworks Electrical | Main Building - Level 3 - Staff Male Toilets (Tip Toe Alley off Puccini Room)- see details | Electrical | General Electrical | 406.06 | Pass | Pass | 0 | 0 | 2 | 2022-06-22 12:49 | 2022-06-27 17:00 | 2022-06-27 11:00 | 2022-06-27 17:00 | 2022-06-27 13:00 |  |  | Level 3 tip toe alley male bathroom light switch broken, replaced both switches and plate with new and tested lights.
MSA-MRWA | WA5566108 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Server Room - CRAC unit is in alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-06-22 15:14 | 2022-06-23 17:00 | 2022-06-22 15:30 | 2022-06-23 17:00 | 2022-06-22 17:30 |  |  | Attended site. Gained keys. Investigated crac 2 in alarm. Unit in hp alarm on stage 1. Confirmed operation of sump heaters. Checked pressure controls, not tripped. Reset alarm and tested operation. Checked event log. Shown 2 failed starts prior to this reset. Amps ok. Unit operating ok. Left crac 2 as lead to monitor. Completed paperwork
MSA-DFES | WA5566620 | 3 | Australian HVAC Services Pty. Ltd. | External to building East side - AC Unit C4 fan making noise, possible fan bearing failure. | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Pass | 0 | 0 | 2 | 2022-06-23 10:05 | 2022-06-30 17:00 | 2022-06-28 08:00 | 2022-06-30 17:00 | 2022-06-28 10:00 |  |  | Jean-Pierre Richards-Shaw (28/06/2022) - Work NoteArrived on-site, signed in & spoke with on-site representative who directed me to CU4 due to noisy outdoor fan motor, upon further investigation found compressor to be extremely noisy and overheating, viewed previous notes and found previous technician had already observed to unit to have a refrigerant leak, installed gauges to unit and confirmed A/C unit has refrigerant leak, dismantled condensing unit fascia panelling and dismantled compressor wiring assembly, tested resistance across all windings and readings were as follows4.8ohms4.8ohms5.2ohmsWindings failing and compressor is mechanically seizing, as well as having a refrigerant leak and an R22 refrigerant unit, it is recommended 2.5kw unit be replaced.Quotation in progress.Informed client of findings & left site. Quote for replacement unit to follow.
MSA-DCA | WA5568947 | 3 | FCT SURFACE CLEANING | Fiji Room Door - Ground – external - graffiti on external side | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-06-27 10:31 | 2022-07-04 17:00 | 2022-07-04 11:00 | 2022-07-04 17:00 | 2022-07-04 13:00 |  |  | Our aim is to make every customer a repeat, referring customer.
MSA-DTWD | WA5569224 | 2 | Techworks Electrical | A-Block room A139 has lights not working | Electrical | Lighting, Internal | 546.43 | Pass | Pass | 0 | 0 | 2 | 2022-06-27 12:51 | 2022-06-30 17:00 | 2022-06-30 12:30 | 2022-06-30 17:00 | 2022-06-30 14:30 |  |  | Replaced fluros and starters in lights
MSA-DTWD | WA5572864 | 3 | AWB Co. | Lighting fault | Electrical | Lighting, Internal | 284.42 | Pass | Pass | 0 | 0 | 2 | 2022-06-30 11:46 | 2022-07-07 17:00 | 2022-07-04 11:00 | 2022-07-07 17:00 | 2022-07-04 13:00 |  |  | Attended site and signed in. Completed JSA. Located all faulty lamps in B4. Supply and replaced all lamps required. Tested okay. Signed out, job complete
MSA-DTWD | WA5588992 | 3 | Australian Airconditioning Services Pty Ltd | E63 Bistro - Cake Fridge requires coil & condensation tray clean | Refrigeration | Refrigerators | 439.75 | Pass | Pass | -1 | -1 | 2 | 2022-07-08 09:01 | 2022-07-15 17:00 | 2022-07-11 08:00 | 2022-07-15 17:00 | 2022-07-11 10:00 |  |  | complete
MSA-DTWD | WA5589491 | 2 | AWB Co. | Bain Marie Heat Lamps have blown | Electrical | Lighting, Internal | 266.14 | Pass | Pass | 0 | 0 | 2 | 2022-07-08 13:29 | 2022-07-13 17:00 | 2022-07-12 14:45 | 2022-07-13 17:00 | 2022-07-12 16:45 |  |  | Attended site and signed in. Completed JSA. Located Bain Marie not working, 1 x lamp faulty. Supply and replace with new lamps and tested all okay. Left old good lamp on site. Signed out. Job complete
MSA-DFES | WA5597163 | 2 | Protek 24/7 Building & Maintenance | L1 training room-Possible roof leaking-see notes | Building | Ceiling | 373.4 | Pass | Pass | 0 | 0 | 2 | 2022-07-11 12:27 | 2022-07-14 17:00 | 2022-07-14 12:30 | 2022-07-14 17:00 | 2022-07-14 14:30 |  |  | Weathered sheet & reinstall
MSA-DTWD | WA5609636 | 3 | Protek 24/7 Building & Maintenance | Floor damaged at corridor entry | Flooring | Vinyl | 257.14 | Pass | Pass | -1 | -1 | 2 | 2022-07-13 15:32 | 2022-07-20 17:00 | 2022-07-15 12:30 | 2022-07-20 17:00 | 2022-07-15 14:30 |  |  | Repaired Damaged Vinyl floor
MSA-DFES | WA5656596 | 3 | AWB Co. | Level 1 - Room 4 (Disabled toilet) - Disabled Toilet: door closer has come away from the door | Building | Doors | 239.82 | Pass | Pass | 0 | 0 | 2 | 2022-07-18 15:02 | 2022-07-25 17:00 | 2022-07-22 11:45 | 2022-07-25 17:00 | 2022-07-22 13:45 |  |  | Re installed door closure
MSA-DCA | WA5656620 | 3 | Techworks Electrical | Broken Light requiring repair - The light cover is in the cleaning room. | Electrical | Lighting, External | 479.05 | Pass | Pass | -1 | -1 | 2 | 2022-07-18 15:24 | 2022-07-25 17:00 | 2022-07-19 12:30 | 2022-07-25 17:00 | 2022-07-19 14:30 |  |  | Replaved globe and re installed dome
MSA-DTWD | WA5671589 | 2 | Damian Rak Electrical Pty Ltd | First floor - Hallway - 2 faulty Fluro's | Electrical | General Electrical |  | Pass | Pass | -1 | -1 | 2 | 2022-07-20 08:34 | 2022-07-25 17:00 | 2022-07-20 14:00 | 2022-07-25 17:00 | 2022-07-20 16:00 |  |  | Completed
MSA-DTWD | WA5673307 | 1 | AHS Services WA Pty Ltd (Anchor) | Sink not draining away | Plumbing & Drainage | Drainage | 270.78 | Pass | Pass | 0 | 0 | 2 | 2022-07-20 13:49 | 2022-07-21 17:00 | 2022-07-21 08:45 | 2022-07-21 17:00 | 2022-07-21 10:45 |  |  | Blockage was caused by blocked aav , replced 50mm aav
MSA-DTWD | WA5674036 | 2 | AWB Co. | roof leak | Building | Internal Walls | 428.5 | Pass | Pass | -1 | -1 | 2 | 2022-07-21 08:40 | 2022-07-26 17:00 | 2022-07-22 11:00 | 2022-07-26 17:00 | 2022-07-22 13:00 |  |  | Attended, cleaned roof laps to saw toot and replaced fixings. Cleaned out box gutter to allow drainage.
MSA-DTWD | WA5674224 | 2 | BAKE-QUIP PTY LTD | RHS Commercial gas oven cutting out intermittently | Equipment | Catering Equipment | 360 | Fail | Fail | 0 | 0 | 2 | 2022-07-21 09:49 | 2022-07-26 17:00 | 2022-07-27 11:00 | 2022-07-26 17:00 | 2022-07-27 13:00 |  |  | Refer to service report
MSA-DTWD | WA5676785 | 2 | Protek 24/7 Building & Maintenance | Entry-Carpet at entry has a worn hole | Flooring | Carpet | 476.55 | Fail | Fail | 0 | 0 | 2 | 2022-07-25 10:29 | 2022-07-28 17:00 | 2022-07-29 09:30 | 2022-07-28 17:00 | 2022-07-29 11:30 |  |  | repaired hole in carpet provided by site
MSA-DTWD | WA5677360 | 2 | Precise Air Group | Pavillion restaurant cool room not cooling | Refrigeration | Coolroom | 362.42 | Pass | Pass | 0 | 0 | 2 | 2022-07-25 14:11 | 2022-07-28 17:00 | 2022-07-26 08:00 | 2022-07-28 17:00 | 2022-07-26 10:00 |  |  | Fixed pressure switch and returned to normal operationa
MSA-DTWD | WA5681129 | 3 | AWB Co. | 2 x lights out in front of elevators | Electrical | Lighting, Internal | 475.18 | Pass | Pass | -1 | -1 | 2 | 2022-07-28 09:20 | 2022-08-04 17:00 | 2022-07-29 12:30 | 2022-08-04 17:00 | 2022-07-29 14:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, walked around and counted up materials required, sent josh to wholesaler to get parts whilst I changed tubes and starters, returned from wholesaler and completed lighting list , will need to return to replace ballast on level 1 in front of lift . Completed paperwork, packed up, **follow up required**
MSA-DTAG | WA5681255 | 3 | Midolo Building Services | Comms Door in Registry - Comms Room - Difficult to shut | Building | Doors | 295.95 | Pass | Pass | 0 | 0 | 2 | 2022-07-28 10:37 | 2022-08-04 17:00 | 2022-08-02 08:00 | 2022-08-04 17:00 | 2022-08-02 10:00 |  |  | REPAIRS TO DOOR COMPLETED
MSA-DFES | WA5681661 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Various Lights out - See notes below | Electrical | Lighting, Internal | 395.28 | Pass | Pass | 0 | 0 | 2 | 2022-07-28 13:52 | 2022-08-04 17:00 | 2022-08-03 12:30 | 2022-08-04 17:00 | 2022-08-03 14:30 |  |  | Arrived on site at 1230 to investigate lights out in volunteers office shed, north east operations, kitchen area and adminreception. Replaced, reenergised and informed staff. Left site at 1430
MSA-DTWD | WA5689911 | 3 | AWB Co. | Ground - Kitchen staff Toilet-Exhaust fan not working-will need an EWP | Electrical | General Electrical | 402.03 | Pass | Pass | 0 | 0 | 2 | 2022-08-02 15:11 | 2022-08-09 17:00 | 2022-08-09 11:00 | 2022-08-09 17:00 | 2022-08-09 13:00 |  |  | Attended site signed in jsa completed.found exhaust fan with no power. unplugged and removed. opened man hole and found extention lead running from 413 to fan was only plugged in slightly. Plugged back in and put new fan out as fan was broken. all tested and working fine now.Job completed
MSA-DCA | WA5691983 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant room 4 - Mezzanine Level - Faults on air handling units/ Humidifiers | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-08-03 09:29 | 2022-08-04 17:00 | 2022-08-03 09:30 | 2022-08-04 17:00 | 2022-08-03 11:30 |  |  | Attended site. Found faults on humidifiers 03-02 & 03-05, both had faulted on current failure faults most likely caused by the storm. Reset and tested operation. Humidifiers not filling. Isolated water lines and replaced filter. Purged air from system and continued testing, all ok. Completed paperwork.
MSA-DCA | WA5693487 | 1 | Critical Fire Protection & Training | fire zone 5-faulty | Fire Protection Services | Fire Protection - Monitor System | 666.805 | Pass | Pass | 0 | 0 | 2 | 2022-08-04 12:45 | 2022-08-05 17:00 | 2022-08-05 08:00 | 2022-08-05 17:00 | 2022-08-05 10:00 |  |  | .
MSA-DFES | WA5694123 | 2 | AWB Co. | Stationery Area - Roof Water Leak above Stationery Area | Roofing | Metal Roofing | 453 | Pass | Pass | 0 | 0 | 2 | 2022-08-05 08:12 | 2022-08-10 17:00 | 2022-08-09 10:15 | 2022-08-10 17:00 | 2022-08-09 12:15 |  |  | Two leaks, stationary, sealed front of AC ducting.Sever leak, sikaflexed expansion joint to wall
MSA-DTWD | WA5694793 | 2 | Precise Air Group | Extraction not working in cafe N106 | Equipment | Electrical Equipment | 253.38 | Pass | Pass | 0 | 0 | 2 | 2022-08-05 13:27 | 2022-08-10 17:00 | 2022-08-08 08:00 | 2022-08-10 17:00 | 2022-08-08 10:00 |  |  | attended site signed in and gained access to the Cafe. inspected controls and extraction fan on the roof. Found fan to be operational. Tennant informed that filters will be replaced and will help with airflow
MSA-DCA | WA5694950 | 3 | Techworks Electrical | First Floor - Labs - PIR Sensor and Lighting Ballast | Electrical | General Electrical | 518.86 | Pass | Pass | 0 | 0 | 2 | 2022-08-05 15:20 | 2022-08-12 17:00 | 2022-08-11 06:30 | 2022-08-12 17:00 | 2022-08-11 08:30 |  |  | Replaced sensor and faulty ballast to labs
MSA-DTWD | WA5696091 | 2 | CONNECT SECURITY SYSTEMS | A/block East exit door timer for locking or opening not working | Security | Access Control | 329.62 | Pass | Pass | 0 | 0 | 2 | 2022-08-08 09:39 | 2022-08-11 17:00 | 2022-08-11 11:09 | 2022-08-11 17:00 | 2022-08-11 13:09 |  |  | reflashed current firmaware to security system to maintain working order
MSA-DCA | WA5698010 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Level 3 - Conservation - EF29_fan alarm fault - See notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | -1 | -1 | 2 | 2022-08-09 13:41 | 2022-08-16 17:00 | 2022-08-10 08:00 | 2022-08-16 17:00 | 2022-08-10 10:00 |  |  | Attended site, signed in and located fan 29 - conservation lab. Found the fan manualed on the BMS, set fan to auto and checked fan for correct running operation. Recorded amp draws and checked the extraction. Found the fans belts and pulleys worn and require replacement. Reset all alarms on the bms.Accessed level 3 and checked the fan extraction and lighting - all operational with no new faults to report.
MSA-DTAG | WA5714925 | 2 | Schindler Lifts Australia | Goods Lift 4 - Goods lift displaying ‘out of service’, doors not opening | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 2 | 2022-08-12 09:30 | 2022-08-17 17:00 | 2022-08-12 10:40 | 2022-08-17 17:00 | 2022-08-12 12:40 |  |  | When responding to the callback dated 12.08.2022, the Schindler Technician found a problem with your equipment. Electricalcomponents were faulty. Following our attendance, the equipment was left in service
MSA-DTWD | WA5734625 | 2 | AWB Co. | 2 roof leaks - one from air con ducting-one from roof penetration's | Roofing | Metal Roofing | 442 | Pass | Pass | 0 | 0 | 2 | 2022-08-16 08:27 | 2022-08-19 17:00 | 2022-08-17 08:45 | 2022-08-19 17:00 | 2022-08-17 10:45 |  |  | Work Performed:Investigated 2 x leaks.found anchor flashing silicone perished.carried out repair.found apron flashing around ac with perished silicone.carried out repair
MSA-DCA | WA5750105 | 3 | Protek 24/7 Building & Maintenance | Jubilee - Ground Floor - Directors Office - rubber seal has fallen from the bottom of the door | Building | Doors | 394.3 | Pass | Pass | -1 | -1 | 2 | 2022-08-17 09:33 | 2022-08-24 17:00 | 2022-08-17 11:45 | 2022-08-24 17:00 | 2022-08-17 13:45 |  |  | Repaired door
MSA-DTWD | WA5753015 | 2 | AHS Services WA Pty Ltd (Anchor) | Arcal Force gas valve - closed but letting gas through. | Plumbing & Drainage | Gas | 332.81 | Pass | Pass | -1 | -1 | 2 | 2022-08-17 13:14 | 2022-08-22 17:00 | 2022-08-18 08:00 | 2022-08-22 17:00 | 2022-08-18 10:00 |  |  | Supplied and installed new 32mm gas isolation valve as required and tested
MSA-DTWD | WA5762157 | 1 | AHS Services WA Pty Ltd (Anchor) | Front Entrance Oxford Street - RPZ Leaking | Plumbing & Drainage | Water | 227.8 | Pass | Pass | 0 | 0 | 2 | 2022-08-18 13:03 | 2022-08-19 17:00 | 2022-08-18 14:45 | 2022-08-19 17:00 | 2022-08-18 16:45 |  |  | .
MSA-DTAG | WA5790841 | 1 | Sapio Pty Ltd | ground registry-Staff Back door requires new door handle. | Building | Doors | 559.25 | Pass | Pass | 0 | 0 | 2 | 2022-08-22 13:08 | 2022-08-23 17:00 | 2022-08-22 14:00 | 2022-08-23 17:00 | 2022-08-22 16:00 |  |  | Collected new door handle from Locksmith and fitted back at site. New door handle tested ok.Job completed.
MSA-DTWD | WA5796942 | 3 | Equans Mechanical Services Australia | Crèche Kitchen - Faulty Fridge - not running | Refrigeration | Refrigerators | 290.06 | Fail | Fail | 1 | 1 | 2 | 2022-08-26 15:09 | 2022-09-02 17:00 | 2022-09-06 11:00 | 2022-09-02 17:00 | 2022-09-06 13:00 |  |  | ATTENDED SITE AND SHOWN 3 FRIDGES TO HAVE THE GAS RECLAIMED. PURCHASED 3 BULLET PIERCE VALVES TO COMPLETE JOB. JOB WA5853866 WAS RAISED FOR COLLECTION AND DISPOSAL OF FRIDGES
MSA-DCA | WA5797047 | 0 | Automatic Fire Protection (ARA) | ground floor main building, fire sprinkler pipe leaking | Fire Protection Services | Sprinkler Systems | 745.28 | Pass | Pass | 0 | 0 | 2 | 2022-08-27 09:54 | 2022-08-27 11:54 | 2022-08-27 11:00 | 2022-08-27 13:54 | 2022-08-27 13:00 |  |  | -Met Michael hewlett on site-found pin hole on 65 mm range in ceiling space on ground floor-had to lower 100 mm main on the hanger so the range would drop enough to get the clearance for a repair clamp-put 1 x 65 mm repair clamp on
MSA-DTWD | WA5799245 | 1 | Building Automation & Electrical Services Pty Ltd | N129 - BMS Not communicating | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 2 | 2022-08-30 10:32 | 2022-08-31 17:00 | 2022-08-31 08:00 | 2022-08-31 17:00 | 2022-08-31 10:00 |  |  | Completed
MSA-DTAG | WA5800488 | 2 | AWB Co. | Level 14 - 1 x faulty light Chambers administrator office - 1 x light in meeting office | Electrical | Lighting, Internal | 242.14 | Pass | Pass | 0 | 0 | 2 | 2022-08-31 10:27 | 2022-09-05 17:00 | 2022-09-02 12:30 | 2022-09-05 17:00 | 2022-09-02 14:30 |  |  | Job complete
MSA-DTAG | WA5832278 | 2 | AWB Co. | Level 10 - Various locations - faulty lighting - see notes below | Electrical | Lighting, Internal | 558.64 | Pass | Pass | 0 | 0 | 2 | 2022-09-05 12:11 | 2022-09-08 17:00 | 2022-09-07 13:15 | 2022-09-08 17:00 | 2022-09-07 15:15 |  |  | Job complete
MSA-DCA | WA5833833 | 2 | Precise Air Group | Main building - studio 3 - Please check faults in aircon and make sure it isn't damaged | Air Conditioning | Room Air Conditioners | 366 | Pass | Pass | 0 | 0 | 2 | 2022-09-06 12:08 | 2022-09-09 17:00 | 2022-09-07 14:00 | 2022-09-09 17:00 | 2022-09-07 16:00 |  |  | Attended site and spoke to tenants in regional arts about issue with aircon. Accessed unit up on the roof and ran system. After monitoring the unit we found that one of the condenser fan motors was faulty and rotating at a very slow speed, tested capacitor and found that it was still in range. We will need to replace the fan motor, quote to follow for repairs. Unit is very old and past it’s life expectancy, recommend budgeting for upgrade.
MSA-DTWD | WA5834029 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 409.31 | Pass | Pass | 0 | 0 | 2 | 2022-09-06 13:21 | 2022-09-07 17:00 | 2022-09-07 11:00 | 2022-09-07 17:00 | 2022-09-07 13:00 |  |  | Cleaned and re sealed top of dektights
MSA-DFES | WA5836158 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Lounge - Fluro Light in lounge room half out above TV | Electrical | Lighting, Internal | 384.45 | Pass | Pass | -1 | -1 | 2 | 2022-09-07 10:26 | 2022-09-14 17:00 | 2022-09-08 09:30 | 2022-09-14 17:00 | 2022-09-08 11:30 |  |  | Continued on site at 0930to attend Ground Floor - Lounge - Fluro Light in lounge room half out above TV 40. Located light, gathered details and left site at 1000 to pick up parts from wholesaler. Returned to site at 1045, replaced/reenergised fitting, informed staff and left site at 1130.
MSA-DFES | WA5838596 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Light switch is crackling in Conference Room - see notes below | Electrical | Lighting, Internal | 276.84 | Pass | Pass | 0 | 0 | 2 | 2022-09-08 15:15 | 2022-09-13 17:00 | 2022-09-13 11:00 | 2022-09-13 17:00 | 2022-09-13 13:00 |  |  | Arrived onsite at 11:00 to investigate faulty switch, no keys for access to conference rm onsite, picked up key from Dwayne at dfes training center forrestfield. Replaced arcing switch with new one, tested ok, returned key and advised Dwayne of works and left site at 13:00.
MSA-DFES | WA5838600 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Kitchen - mould growing in the cupboard - see notes below | Plumbing & Drainage | Water | 342.32 | Pass | Pass | 0 | 0 | 2 | 2022-09-08 15:17 | 2022-09-15 17:00 | 2022-09-13 10:15 | 2022-09-15 17:00 | 2022-09-13 12:15 |  |  | Arrived on site and singed in went sec voluntary building found sink with mould growing in cupboard could see a Wilson unit under sink tested the relief valve it go stuck in the open position had to go to Reece and pick up a new one. Cleaned up majority of mould.
MSA-DCA | WA5854285 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Guards |  | Fail | Fail | 1 | 1 | 2 | 2022-09-03 12:00 | 2022-09-05 17:00 | 2022-09-12 15:30 | 2022-09-05 17:00 | 2022-09-12 17:30 | 1 |  | Completed
MSA-DTWD | WA5866485 | 2 | Techworks Electrical | Kitchen has a broken pendant power point | Electrical | General Electrical | 414.42 | Pass | Pass | -1 | -1 | 2 | 2022-09-14 08:48 | 2022-09-19 17:00 | 2022-09-15 08:00 | 2022-09-19 17:00 | 2022-09-15 10:00 |  |  | Replaced faulty lights to LED fittings
MSA-DTWD | WA5866854 | 2 | Damian Rak Electrical Pty Ltd | Flat C Bathroom - Faulty Light | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 2 | 2022-09-14 09:12 | 2022-09-19 17:00 | 2022-09-16 14:00 | 2022-09-19 17:00 | 2022-09-16 16:00 |  |  | Completed
MSA-DTWD | WA5866863 | 2 | Techworks Electrical | Ground floor - Passageway - ceiling light not working | Electrical | Lighting, Internal | 257.67 | Pass | Pass | -1 | -1 | 2 | 2022-09-14 09:13 | 2022-09-19 17:00 | 2022-09-15 12:30 | 2022-09-19 17:00 | 2022-09-15 14:30 |  |  | Replace to new LED fitting
MSA-DTWD | WA5866868 | 2 | Techworks Electrical | 1st Floor hallway has a light not working | Electrical | Lighting, Internal | 395.24 | Pass | Pass | -1 | -1 | 2 | 2022-09-14 09:19 | 2022-09-19 17:00 | 2022-09-15 08:00 | 2022-09-19 17:00 | 2022-09-15 10:00 |  |  | Replace with new fitting
MSA-DTWD | WA5867015 | 2 | Techworks Electrical | P-Block G/Floor Passage way has a light not working | Electrical | Lighting, Internal | 248.91 | Pass | Pass | -1 | -1 | 2 | 2022-09-14 09:25 | 2022-09-19 17:00 | 2022-09-15 12:30 | 2022-09-19 17:00 | 2022-09-15 14:30 |  |  | Replace starters and tubes in fitting.
MSA-DTAG | WA5880731 | 1 | Sapio Pty Ltd | Level 7 - Faulty Door switch - See notes below | Security | Access Control | 294.68 | Fail | Fail | 3 | 3 | 2 | 2022-09-15 16:22 | 2022-09-16 17:00 | 2022-10-05 12:30 | 2022-09-16 17:00 | 2022-10-05 14:30 |  |  | Replaced rex
MSA-DTWD | WA5961814 | 3 | Building Automation & Electrical Services Pty Ltd | Time schedules not synchronized on Building Management System | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | -1 | -1 | 2 | 2022-09-19 10:01 | 2022-09-27 17:00 | 2022-09-19 14:00 | 2022-09-27 17:00 | 2022-09-19 16:00 |  |  | Completed
MSA-DTWD | WA5961926 | 1 | Lane's Plumbing | Faulty gas regulator | Plumbing & Drainage | Gas |  | Pass | Pass | 0 | 0 | 2 | 2022-09-19 11:01 | 2022-09-20 17:00 | 2022-09-19 12:30 | 2022-09-20 17:00 | 2022-09-19 14:30 |  |  | REPAIRS COMPLETED
MSA-DTWD | WA5970903 | 2 | Damian Rak Electrical Pty Ltd | 2 x exit lights not working | Electrical | Lighting, External |  | Fail | Fail | 1 | 1 | 2 | 2022-09-20 09:40 | 2022-09-23 17:00 | 2022-09-29 11:00 | 2022-09-23 17:00 | 2022-09-29 13:00 |  |  | 2x LED exit lights
MSA-DTWD | WA5971040 | 2 | Damian Rak Electrical Pty Ltd | faulty emergency light EM5 | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 2 | 2022-09-20 11:14 | 2022-09-23 17:00 | 2022-09-29 08:00 | 2022-09-23 17:00 | 2022-09-29 10:00 |  |  | Repairs to light
MSA-DTWD | WA5971095 | 2 | Damian Rak Electrical Pty Ltd | Entry and exit - 2 faulty exit lights | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 2 | 2022-09-20 11:23 | 2022-09-23 17:00 | 2022-09-28 08:00 | 2022-09-23 17:00 | 2022-09-28 10:00 |  |  | Repairs to lights
MSA-DTWD | WA5978989 | 2 | AWB Co. | Flood light is flicking on and off. PE cell may be faulty | Electrical | Emergency & Exit Lighting | 352.14 | Fail | Fail | 0 | 0 | 2 | 2022-09-28 14:46 | 2022-10-03 17:00 | 2022-10-04 12:30 | 2022-10-03 17:00 | 2022-10-04 14:30 |  |  | Job complete
MSA-DFES | WA5980206 | 0 | Securex Security Systems & Services | Main administration - Multiple doors locked up, cannot access | Security | Access Control | 465.9 | Fail | Fail | 0 | 0 | 2 | 2022-09-29 13:28 | 2022-09-29 15:28 | 2022-09-29 15:30 | 2022-09-29 17:28 | 2022-09-29 17:30 |  |  | 29/09/2022 1530-1730Checked and found 12 doors not working, no power to devices.Checked PSu ok.Found Fire relay boards had blown fuses.Replaced 3 of 2amp fuses and 1 of 10 amp fuse.All doors back online .Tested operation, all ok.
MSA-DCA | WA5980389 | 1 | Automatic Fire Protection (ARA) | Fire panel is faulting releasing door controls-Please call Reese on arrival | Fire Protection Services | Fire Protection - Monitor System | 258.88 | Pass | Pass | 0 | 0 | 2 | 2022-09-29 14:34 | 2022-09-30 17:00 | 2022-09-30 09:30 | 2022-09-30 17:00 | 2022-09-30 11:30 |  |  | Attended site found 2 x fire doors near admin not holding, spoke to client and found dorma had been working on doors before issue occurred.Found door holder fuses had blown in main fip, replaced and returned doors to normal.
MSA-DCA | WA5982641 | 2 | EQUANS Mechanical Services (WA) Pty Limited | First Floor - Plant Room - Chiller 2 in fault | Refrigeration | Chiller | 451.79 | Pass | Pass | 0 | 0 | 2 | 2022-09-30 13:07 | 2022-10-05 17:00 | 2022-10-03 08:00 | 2022-10-05 17:00 | 2022-10-03 10:00 |  |  | Contractor to submit quote to replace Chiller sensor.
MSA-DCA | WA5982777 | 2 | EQUANS Mechanical Services (WA) Pty Limited | B1 Basement Level - Entry Lobby - Security system faults following generator load test - See notes | Security | Security Management System | 486.99 | Pass | Pass | 0 | 0 | 2 | 2022-09-30 14:20 | 2022-10-05 17:00 | 2022-10-04 09:30 | 2022-10-05 17:00 | 2022-10-04 11:30 |  |  | Reset A9 alarm which triggered from generator load test. Now all ok.Cam 5029 and 4027 need further investigation
MSA-DCA | WA5994193 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Fan unit is still too noisy - Please attend Friday | Electrical | General Electrical | 831.01 | Pass | Pass | -1 | -1 | 2 | 2022-10-05 13:25 | 2022-10-10 17:00 | 2022-10-06 08:00 | 2022-10-10 17:00 | 2022-10-06 10:00 |  |  | ICON Logic are quoting to replace 2 x VAV's in Boardroom as parts for existing VAV's are no longer available.
MSA-DCA | WA5994250 | 2 | EQUANS Mechanical Services (WA) Pty Limited | First Floor - Plant Room - Chiller 2 in fault | Refrigeration | Chiller | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-10-05 14:12 | 2022-10-10 17:00 | 2022-10-10 14:00 | 2022-10-10 17:00 | 2022-10-10 16:00 |  |  | Found chiller 1 and 2, and VSD for Chilled water pump 2 in alarm. Reset all equipment and tested operation to ensure no further faults. Checked bms to ensure pumps and chillers both started without alarms or faults.
MSA-DTWD | WA5994817 | 2 | M Construction (WA) | S Block - S010 - Please see notes below | Furniture | Indoor Furniture | 244.92 | Pass | Pass | 0 | 0 | 2 | 2022-10-06 08:53 | 2022-10-11 17:00 | 2022-10-11 11:00 | 2022-10-11 17:00 | 2022-10-11 13:00 |  |  | Pin on Locking atm had been sheard off: Installed new high tensile bolt to fit break
MSA-DCA | WA5998692 | 0 | OTIS ELEVATOR COMPANY PTY LTD | PUBLIC LIFT is out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2 | 2022-10-08 12:11 | 2022-10-08 14:11 | 2022-10-08 12:30 | 2022-10-08 16:11 | 2022-10-08 14:30 |  |  | Repaired under warranty - No charges
MSA-DTWD | WA6000730 | 2 | M Construction (WA) | exit sign that is getting wet from the rain coming from above the door, the floor is also wet | Building | General Building | 180 | Pass | Pass | 0 | 0 | 2 | 2022-10-10 10:05 | 2022-10-13 17:00 | 2022-10-13 09:30 | 2022-10-13 17:00 | 2022-10-13 11:30 |  |  | Inspected area above exit sign, ran water over the entire surface door. Located a few leaks in that process fill holes with silicone.
MSA-DTAG | WA6007854 | 1 | Seme Solutions Pty Ltd | ground-Hard drive has failed in CCTV rack - see notes | Security | Security Management System | 402.76 | Pass | Pass | 0 | 0 | 2 | 2022-10-11 10:52 | 2022-10-12 17:00 | 2022-10-11 11:00 | 2022-10-12 17:00 | 2022-10-11 13:00 |  |  | Identify, order, collect and replace hardrive
MSA-DTWD | WA6008324 | 2 | COMMERCIAL PLUMBING AND GAS | Urinal Cistern leaking at rear connection | Plumbing & Drainage | Toilets/Cisterns | 684.21 | Fail | Fail | 1 | 1 | 2 | 2022-10-11 13:20 | 2022-10-14 17:00 | 2022-10-18 17:00 | 2022-10-14 17:00 | 2022-10-18 19:00 |  |  | replaced cistern and repaired rear connection
MSA-DCA | WA6014315 | 0 | Critical Fire Protection & Training | ground pump room- fire alarm has been activated | Fire Protection Services | Fire Protection - Monitor System | 360.17 | Pass | Pass | 0 | 0 | 2 | 2022-10-12 08:18 | 2022-10-12 10:18 | 2022-10-12 09:30 | 2022-10-12 12:18 | 2022-10-12 11:30 |  |  | Attended site to investigate false alarms to the fire system.Upon arrival it was found that the zone 26 sprinkler DBA was in isolated normal condition after activating twice and calling brigade overnight.After investigating the sprinkler systems, it was found system 1 sprinkler installation pressure very close to the below system pressure. The cause of this was found to be the test valve to installation 1 allowing water to pass likely due to debris/scum in the test valve causing the test valve not to seal properly. This has then allowed low amounts of water to pass and slowly drop system pressure.After re-seating the test valve on system 1 to fully closed position, manually jacked up system pressure to 1250Kpa as is systems static pressure and dropped below system pressure to 950Kpa to ensure no surge of pressure causes further false DBA activations the system returned to normal and no further action is required.
MSA-DTAG | WA6014524 | 3 | Australian HVAC Services Pty. Ltd. | Level 4 - Court 42 - A/C is too hot on level 4 – possible BMS failure | Air Conditioning | Room Air Conditioners | 246.92 | Pass | Pass | -1 | -1 | 2 | 2022-10-12 09:54 | 2022-10-19 17:00 | 2022-10-12 14:00 | 2022-10-19 17:00 | 2022-10-12 16:00 |  |  | Attend site. Access level 4 and found area to be warm. Access level 6 plantroom and check BMS. Found level 4 and 6 to be offline. Access basment and obtain keys. Access level 3 and locate BMS out station. Carry out power cycle of controller. Return keys to Basement. Access level 6 BMS and check floor. Found to start coming back online. Ac appears to be operating normally. Will monitor.
MSA-DTAG | WA6015142 | 2 | PPM Project Painting & Maintenance | Ground - 2 x locations on the outside of the buildings - 2 areas of graffiti - See notes | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 2 | 2022-10-12 15:35 | 2022-10-17 17:00 | 2022-10-18 08:00 | 2022-10-17 17:00 | 2022-10-18 10:00 |  |  | Removal of graffiti
MSA-DTWD | WA6021631 | 3 | Australian Airconditioning Services Pty Ltd | Dump valves leaking on evaporative A/C on roof | Air Conditioning | Evaporative Coolers | 717.42 | Pass | Pass | 0 | 0 | 2 | 2022-10-14 09:37 | 2022-10-21 17:00 | 2022-10-20 09:30 | 2022-10-21 17:00 | 2022-10-20 11:30 |  |  | Replaced 3 x sump Dumps on block 7 evaps Tested units all ok
MSA-DTWD | WA6023076 | 3 | COMMERCIAL PLUMBING AND GAS | Café 2 x sink mixers not working (Between Coffee machines and in back kitchen ) | Plumbing & Drainage | Materials | 436.45 | Pass | Pass | -1 | -1 | 2 | 2022-10-14 16:03 | 2022-10-21 17:00 | 2022-10-14 17:00 | 2022-10-21 17:00 | 2022-10-14 19:00 |  |  | replaced 2x sink mixers
MSA-DFES | WA6024858 | 0 | Go Doors | Roller Doors not operating | Building | Roller Shutters | 581.04 | Pass | Pass | 0 | 0 | 2 | 2022-10-15 10:19 | 2022-10-15 12:19 | 2022-10-15 11:45 | 2022-10-15 14:19 | 2022-10-15 13:45 |  |  | Completed. Please see attachments.
MSA-DTWD | WA6076703 | 1 | Lane's Plumbing | BLD 857-Paddock next to shearing shed-Faulty sheep trough water leak | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-10-18 10:49 | 2022-10-19 17:00 | 2022-10-18 12:30 | 2022-10-19 17:00 | 2022-10-18 14:30 |  |  | Completed
MSA-DTWD | WA6080534 | 2 | AWB Co. | north side, ground level-under verandah-hanging light-see notes | Electrical | Lighting, Internal | 342.14 | Pass | Pass | 0 | 0 | 2 | 2022-10-18 13:51 | 2022-10-21 17:00 | 2022-10-20 08:00 | 2022-10-21 17:00 | 2022-10-20 10:00 |  |  | Job complete
MSA-DCA | WA6080773 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Level 1-plant room-Chiller 1 in fault but no alarms showing on BMS | Refrigeration | Chiller | 1505.31 | Pass | Pass | -1 | -1 | 2 | 2022-10-18 13:56 | 2022-10-25 17:00 | 2022-10-19 08:00 | 2022-10-25 17:00 | 2022-10-19 10:00 |  |  | Subcontractor to attend site and repair chiller
MSA-DTWD | WA6113113 | 1 | COMMERCIAL PLUMBING AND GAS | Northern wall D Block - Water Leak | Plumbing & Drainage | Water | 213.97 | Pass | Pass | 0 | 0 | 2 | 2022-10-24 09:09 | 2022-10-25 17:00 | 2022-10-24 14:00 | 2022-10-25 17:00 | 2022-10-24 16:00 |  |  | adjust sprinkler which was spraying wall, monitor and check meter after hours
MSA-DTWD | WA6126591 | 2 | CLEVELAND COMPRESSED AIR SERVICES | Leak in air compressor suspect water strainer value | Equipment Hire | Compressors, Generators | 721.25 | Pass | Pass | 0 | 0 | 2 | 2022-10-25 12:31 | 2022-10-28 17:00 | 2022-10-28 08:00 | 2022-10-28 17:00 | 2022-10-28 10:00 |  |  | Supply repairs on A/c PD9 Coalescing filter, Leak in air compressor suspect water strainer valueFitted new auto drain on 28/10/22Labour $145.00Part $114.00Mobilisation $462.25
MSA-DTWD | WA6126896 | 2 | AHS Services WA Pty Ltd (Anchor) | Cistern not filling with water - see notes below | Plumbing & Drainage | Toilets/Cisterns | 260.19 | Fail | Fail | 1 | 1 | 2 | 2022-10-25 14:56 | 2022-10-28 17:00 | 2022-11-01 12:30 | 2022-10-28 17:00 | 2022-11-01 14:30 |  |  | nil
MSA-DTAG | WA6127545 | 1 | SCAVENGER SUPPLIES PTY LTD | Detention – Interview - Fire sensor alarm damaged by detainee 25 Oct. FES recommend urgent replace | Fire Protection Services | Fire Protection - Monitor System | 492.9 | Pass | Pass | 0 | 0 | 2 | 2022-10-26 08:33 | 2022-10-27 17:00 | 2022-10-26 09:30 | 2022-10-27 17:00 | 2022-10-26 11:30 |  |  | Completed 26/10/2022
MSA-DTWD | WA6148135 | 2 | Damian Rak Electrical Pty Ltd | Lounge - Faulty Fluro Light | Electrical | Lighting, Internal |  | Pass | Pass | -1 | -1 | 2 | 2022-11-03 12:36 | 2022-11-08 17:00 | 2022-11-04 14:00 | 2022-11-08 17:00 | 2022-11-04 16:00 |  |  | Repairs to light
MSA-DFES | WA6148366 | 3 | Protek 24/7 Building & Maintenance | Main power distribution building - Door is split and difficult to close | Building | Doors | 231.93 | Pass | Pass | -1 | -1 | 2 | 2022-11-03 15:39 | 2022-11-10 17:00 | 2022-11-04 11:00 | 2022-11-10 17:00 | 2022-11-04 13:00 |  |  | Refixed edge timber edge to door, tested all locks all working.Slight weather damage to door but overall good condition
MSA-DTWD | WA6151861 | 2 | Techworks Plumbing | Room T220 - Staff Room - Mixer tap for sink is loose and leaks into cupboard underneath sink | Plumbing & Drainage | Water | 608.56 | Pass | Pass | 0 | 0 | 2 | 2022-11-07 09:20 | 2022-11-10 17:00 | 2022-11-08 09:30 | 2022-11-10 17:00 | 2022-11-08 11:30 |  |  | Replaced mixer tap as old one was loose, leaking and had damaged seals and fixings due to wear and tear. Tightened up othermixer in kitchen to prevent same problem
MSA-DCA | WA6154612 | 3 | Techworks Electrical | Ground Exterior - Courtyard to west of SLWA - Floor lights in area not working. | Electrical | Lighting, External | 395.7 | Pass | Pass | -1 | -1 | 2 | 2022-11-07 14:11 | 2022-11-14 17:00 | 2022-11-09 12:30 | 2022-11-14 17:00 | 2022-11-09 14:30 |  |  | Tasks completed 1. started fault finding and found that all of the lights except 4 had been disconected due to them causing the fuse in the board to pop continually. 2. talked to Denise and she explained that we should leave it now and stop going any further as they will get some fairy lights installed instead.
MSA-DTWD | WA6157255 | 3 | Techworks Electrical | Carpentry workshop - Exit hallway - Loose/damaged gpo | Electrical | General Electrical | 245.36 | Pass | Pass | -1 | -1 | 2 | 2022-11-09 14:25 | 2022-11-16 17:00 | 2022-11-10 14:00 | 2022-11-16 17:00 | 2022-11-10 16:00 |  |  | Attended site found GPO was handing off wallReplaced GPO and mounting box
MSA-DCA | WA6159320 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Guards |  | Pass | Pass | 0 | 0 | 2 | 2022-11-06 09:00 | 2022-11-07 17:00 | 2022-11-06 11:00 | 2022-11-07 17:00 | 2022-11-06 13:00 | 1 |  | Completed
MSA-DTAG | WA6179142 | 3 | Australian HVAC Services Pty. Ltd. | Basement car park - Pump error light stuck on | Mechanical Services | Pumps | 246.92 | Pass | Pass | -1 | -1 | 2 | 2022-11-14 16:48 | 2022-11-21 17:00 | 2022-11-16 08:00 | 2022-11-21 17:00 | 2022-11-16 10:00 |  |  | Attend site. Investigate effluent pump 1 in alarm. Plumbers have previously checked float levels in sump and advised pump requires reset. Access pump control board and reset pump overload. Found no call for pump to run. Manual switch also not working. Push in contactor and check voltages through contactor, ok. Push in contactor and check amp draws. Found motor to be drawing 12 amps per phase. Overload is only set to 4 amps. Pump 2 is drawing 2.8 amps a phase. Pump 1 appears to be seized. Replacement by plumbers required.
MSA-DTWD | WA6229364 | 2 | COMMERCIAL PLUMBING AND GAS | Classroom sink is slow to drain | Plumbing & Drainage | Drainage | 223.97 | Pass | Pass | 0 | 0 | 2 | 2022-11-18 09:45 | 2022-11-23 17:00 | 2022-11-22 17:00 | 2022-11-23 17:00 | 2022-11-22 19:00 |  |  | Unblocked sink
MSA-DFES | WA6229980 | 2 | AWB Co. | Unit 29 - Ground - Sliding door between Dorm 9 bathroom and locker room doesn't slide anymore. | Building | Doors | 225.96 | Pass | Pass | 0 | 0 | 2 | 2022-11-18 10:54 | 2022-11-23 17:00 | 2022-11-22 11:00 | 2022-11-23 17:00 | 2022-11-22 13:00 |  |  | Inspect sliding door between dorm nine and bathroomClean tracks and lubricate bearings clean siteJob complete
MSA-DTWD | WA6256701 | 2 | Critical Fire Protection & Training | Red fire phone constantly beeping. | Fire Protection Services | Fire Protection - Monitor System | 177.275 | Pass | Pass | 0 | 0 | 2 | 2022-11-24 08:11 | 2022-11-29 17:00 | 2022-11-29 14:00 | 2022-11-29 17:00 | 2022-11-29 16:00 |  |  | Attended site and found warden phone on level 1 of C block consistently ringing as if being called by panel. Checked EWIS panel and found no indication of warden phone contact initiated. After using main EWIS phone to establish call to ringing WIP and then hanging up after connection established WIP stopped ringing. No further action required as all systems returned to normal.
MSA-DFES | WA6293884 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Vintage Fleet Workshop - | Electrical | Lighting, Internal | 295.16 | Pass | Pass | -1 | -1 | 2 | 2022-11-30 10:54 | 2022-12-07 17:00 | 2022-12-01 14:00 | 2022-12-07 17:00 | 2022-12-01 16:00 |  |  | Tyler Beard (01/12/2022) - Work NoteOn site already at 1400. Proceeded to investigate broken light fitting in heritage fleet workshop, found light to be beyond repair. Collected an LED variety from wholesaler and replaced the old fitting. All is working correctly, informed staff and left site at 1600.
MSA-DTWD | WA6298367 | 2 | AWB Co. | Block A126 - Male Toilet needs closer replaced | Building | Doors | 705.22 | Pass | Pass | 0 | 0 | 2 | 2022-12-01 09:27 | 2022-12-06 17:00 | 2022-12-05 11:00 | 2022-12-06 17:00 | 2022-12-05 13:00 |  |  | removed damaged closing device installed new closing device
MSA-DFES | WA6301192 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Car Parks A & B - 4 Bollard lights are not working | Electrical | Lighting, External | 510.48 | Pass | Pass | -1 | -1 | 2 | 2022-12-02 14:54 | 2022-12-09 17:00 | 2022-12-05 12:30 | 2022-12-09 17:00 | 2022-12-05 14:30 |  |  | Sebastian Davis (05/12/2022) - Work NoteReplaced globes in bollard lights
MSA-MRWA | WA6357231 | 2 | Automatic Fire Protection (ARA) | Level 10 - Roof - Horn / Fire Alarm Speaker on L10 requires reattaching | Fire Protection Services | Smoke and Heat Detection | 461.48 | Pass | Pass | 0 | 0 | 2 | 2022-12-05 11:51 | 2022-12-08 17:00 | 2022-12-06 12:30 | 2022-12-08 17:00 | 2022-12-06 14:30 |  |  | 6/12/22 EI/DSAttended site & met with MRWA staff.Directed to the level 10 horn speaker that had been knocked off the wall accidentally. Re-installed the horn speaker OK.
MSA-DCA | WA6360744 | 1 | EQUANS Mechanical Services (WA) Pty Limited | SLWA-Level 5-plant room-ETS Condensing Water Pump 3 in fault-see notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-12-07 13:35 | 2022-12-08 17:00 | 2022-12-07 14:00 | 2022-12-08 17:00 | 2022-12-07 16:00 |  |  | Attended site. Investigated condenser water pump 3. Found vsd in overcurrent fault. Powered down and reset. Accessed bms and reset lockout faults on chiller 3 and the pump. Switched chiller 2 to out of service to test operation of chiller 3. Checked over chiller 3 circuit, all ok. Reinstated chiller 2 and plant returned back to normal. Completed paperwork.
MSA-DCA | WA6361142 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 in fault | Refrigeration | Chiller | 506.75 | Pass | Pass | 0 | 0 | 2 | 2022-12-08 07:32 | 2022-12-08 09:32 | 2022-12-08 08:00 | 2022-12-08 11:32 | 2022-12-08 10:00 |  |  | TRAVELLED TO SITE AND SIGNED IN AT RECEPTION. ACCESSED ROOF AND FOUND CHILLER 2 IN FAULT AGAIN. RESET ALARM AND TOOK PHOTO OF FAULT ON INTERFACE OF CHILLER. ACCESSED BMS TO ENSURE CHILLER 1 WAS IN LEAD POSITION. ACCESSED ROOF ONCE AGAIN AND ISOLATED CHILLER 2 CIRCUIT 1 TO PREVENT NUISANCE FAULTS, SO CHILLER 2 CIRCUIT 2 WILL STILL RUN IF REQUIRED AS WELL AS BOTH CIRCUITS ON CHILLER 1. WAITING ON AIRVISION AND DAIKIN TO UPGRADE SOFTWARE ON CHILLER TO ELIMINATE FAULTS.
MSA-DTAG | WA6364055 | 1 | Water2water Pty Ltd | Level 4 - Adult community corrections staff kitchen - No water from Water filter - see notes | Plumbing & Drainage | Water | 700.445 | Pass | Pass | 0 | 0 | 2 | 2022-12-12 09:09 | 2022-12-13 17:00 | 2022-12-12 11:45 | 2022-12-13 17:00 | 2022-12-12 13:45 |  |  | repaired billi unit
MSA-MRWA | WA6365577 | 2 | TASC Digital Control Systems WA | Basement Camera - showing a white screen | Security | CCTV Surveillance | 412.5 | Pass | Pass | 0 | 0 | 2 | 2022-12-13 10:35 | 2022-12-16 17:00 | 2022-12-16 09:30 | 2022-12-16 17:00 | 2022-12-16 11:30 |  |  | 2022-12-16 11:47:19 Michael MelonikWest Car Park Door camera troubleshooting. Tested the POE/Coax adapter all OK. Carried out full restart of the camera which had fixed image fault. Recommending anew camera if fault returns.
MSA-DTAG | WA6379243 | 1 | Sapio Pty Ltd | L6- Main security screen not working-application error | Security | Security Management System | 269 | Pass | Pass | 0 | 0 | 2 | 2022-12-19 10:16 | 2022-12-20 17:00 | 2022-12-19 11:00 | 2022-12-20 17:00 | 2022-12-19 13:00 |  |  | Found PC for cameras in Level 6 back office had crashed. Rebooted PC and loaded up the appropriatecameras.
MSA-DFES | WA6389174 | 1 | Critical Fire Protection & Training | By back Gate - Above ground Hydrant leaking (substantial) by back gate. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 325.78 | Pass | Pass | 0 | 0 | 2 | 2022-12-21 13:57 | 2022-12-22 17:00 | 2022-12-21 14:00 | 2022-12-22 17:00 | 2022-12-21 16:00 |  | WACCES | Found leak on fabricated bull head tee.Stemmed the flow with jubilee clips and a rubber however this is only a temporary fix.We will need to reattend to replace bull head tee and pipe work.
MSA-DCA | WA6389725 | 0 | Earth & Water Pty Ltd | Urban orchid - Retic zone 13 - Solenoid valve broken | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-12-21 15:14 | 2022-12-21 17:14 | 2022-12-21 15:30 | 2022-12-21 19:14 | 2022-12-21 17:30 |  |  | Completed
MSA-DFES | WA6390522 | 2 | Australian HVAC Services Pty. Ltd. | Ground - Lecture Room 2B - Air Conditioner fan is making clicking noise | Air Conditioning | Room Air Conditioners | 237.01 | Pass | Pass | -1 | -1 | 2 | 2022-12-22 10:11 | 2022-12-29 17:00 | 2022-12-23 11:00 | 2022-12-29 17:00 | 2022-12-23 13:00 |  |  | Andrija Skender (23/12/2022) - Work NoteTravelled to site to investigate BA Storeroom Daikin wall not cooling, investigated further and found Ac short of refrigerant.Found leak on service port scharder, charged system with 1 kg of 410a and commissioned operation, all working ok. Also investigated FCU 2b rattling noise, tested system on low and high fan could not pinpoint noise coming from FCU.Spoke to Dwayne from DFES and he said he will monitor.No noise coming from unit found.
MSA-MRWA | WA6402338 | 2 | EQUANS Mechanical Services (WA) Pty Limited | common area-AC 4.1 drain is leaking | Air Conditioning | Room Air Conditioners | 279.01 | Pass | Pass | -1 | -1 | 2 | 2023-01-05 10:21 | 2023-01-10 17:00 | 2023-01-05 11:00 | 2023-01-10 17:00 | 2023-01-05 13:00
MSA-DFES | WA6405331 | 2 | Publik Group | Engine room - DFES sign on roadside is faded and rusted | Signage | General Signage | 3218.25 | Fail | Fail | 5 | 5 | 2 | 2023-01-09 12:39 | 2023-01-12 17:00 | 2023-02-15 08:00 | 2023-01-12 17:00 | 2023-02-15 10:00
MSA-DFES | WA6405547 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Faulty lighting - different locations - see notes below | Electrical | Lighting, Internal | 531.76 | Pass | Pass | -1 | -1 | 2 | 2023-01-09 15:50 | 2023-01-16 17:00 | 2023-01-12 10:15 | 2023-01-16 17:00 | 2023-01-12 12:15
MSA-DTAG | WA6407370 | 2 | Midolo Building Services | Mediation room - Several ceiling tiles - show water stains | Building | Ceiling | 193.68 | Pass | Pass | 0 | 0 | 2 | 2023-01-10 08:27 | 2023-01-13 17:00 | 2023-01-11 12:30 | 2023-01-13 17:00 | 2023-01-11 14:30
MSA-DTWD | WA6415158 | 2 | AWB Co. | Lights out in multiple Rooms - Please see below for Room Locations | Electrical | Lighting, Internal | 442.63 | Pass | Pass | 0 | 0 | 2 | 2023-01-11 13:15 | 2023-01-16 17:00 | 2023-01-16 09:30 | 2023-01-16 17:00 | 2023-01-16 11:30
MSA-DTWD | WA6462212 | 2 | AWB Co. | fit light fittings - see notes | Electrical | Lighting, Internal | 332.785 | Pass | Pass | 0 | 0 | 2 | 2023-01-17 08:37 | 2023-01-20 17:00 | 2023-01-20 14:00 | 2023-01-20 17:00 | 2023-01-20 16:00
MSA-DFES | WA6504186 | 2 | Go Doors | Retrospective WO //WA6130888 - Front RHS bi folding door not closing- Please do not attend | Building | Automatic Doors | 967.04 | Pass | Pass | -1 | -1 | 2 | 2022-10-28 12:00 | 2022-11-02 17:00 | 2022-10-28 20:45 | 2022-11-02 17:00 | 2022-10-28 22:45 | 1 |  | 28/10/2022 Martin KalaReport Fault - Front RHS bi folding door not closing.Fault Found - Transformer was damaged and needed replacing. Work Performed -Replaced the faulty transformer.
MSA-DCA | WA6516191 | 3 | Protek 24/7 Building & Maintenance | External Ground- Outside Sate Library - Uneven paving | Flooring | Tiling | 213.18 | Pass | Pass | -1 | -1 | 2 | 2023-01-23 09:35 | 2023-01-31 17:00 | 2023-01-24 10:15 | 2023-01-31 17:00 | 2023-01-24 12:15
MSA-DTWD | WA6516707 | 1 | AWB Co. | DFES Hardstand - Behind chiller plant - replace pit covers - see notes | Electrical | Distribution Board | 363 | Pass | Pass | 0 | 0 | 2 | 2023-01-23 14:07 | 2023-01-24 17:00 | 2023-01-24 06:30 | 2023-01-24 17:00 | 2023-01-24 08:30
MSA-DTAG | WA6516753 | 2 | Australian HVAC Services Pty. Ltd. | Court 42 and Adult Community Corrections - Air-conditioning not wotking | Air Conditioning | Room Air Conditioners | 246.92 | Pass | Pass | 0 | 0 | 2 | 2023-01-23 14:39 | 2023-01-27 17:00 | 2023-01-24 08:00 | 2023-01-27 17:00 | 2023-01-24 10:00
MSA-DTWD | WA6517560 | 2 | Equans Mechanical Services Australia | Block A - Ground- Eastern Wing - Evaporative air con not working | Air Conditioning | Evaporative Coolers | 619.78 | Pass | Pass | 0 | 0 | 2 | 2023-01-24 10:55 | 2023-01-30 17:00 | 2023-01-30 08:00 | 2023-01-30 17:00 | 2023-01-30 10:00
MSA-DTWD | WA6517884 | 2 | Equans Mechanical Services Australia | Air con in B Block too cold. Can’t adjust via desktop | Air Conditioning | Room Air Conditioners | 399.78 | Pass | Pass | -1 | -1 | 2 | 2023-01-24 13:55 | 2023-01-30 17:00 | 2023-01-25 09:30 | 2023-01-30 17:00 | 2023-01-25 11:30
MSA-DFES | WA6518060 | 1 | Australian HVAC Services Pty. Ltd. | Gym- Air conditioner is dripping water a puddle of water on the floor | Air Conditioning | Room Air Conditioners | 370.8 | Pass | Pass | 0 | 0 | 2 | 2023-01-24 18:49 | 2023-01-25 17:00 | 2023-01-25 07:15 | 2023-01-25 17:00 | 2023-01-25 09:15
MSA-DFES | WA6518186 | 0 | Securex Security Systems & Services | front security gate intermediately leaving itself open - gate unsecure | Security | Access Control | 440 | Fail | Fail | 0 | 0 | 2 | 2023-01-25 05:09 | 2023-01-25 07:09 | 2023-01-25 07:15 | 2023-01-25 09:09 | 2023-01-25 09:15
MSA-DCA | WA6521472 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Chiller 2 - In fault | Refrigeration | Chiller | 281.53 | Fail | Fail | 0 | 0 | 2 | 2023-01-30 11:04 | 2023-01-30 13:04 | 2023-01-30 14:00 | 2023-01-30 15:04 | 2023-01-30 16:00
MSA-DTWD | WA6521554 | 2 | AHS Services WA Pty Ltd (Anchor) | Cleaners room - blocked and leaky basin | Plumbing & Drainage | Water | 250.31 | Pass | Pass | 0 | 0 | 2 | 2023-01-30 11:38 | 2023-02-02 17:00 | 2023-01-30 13:15 | 2023-02-02 17:00 | 2023-01-30 15:15
MSA-DTWD | WA6528191 | 1 | Equans Mechanical Services Australia | AC 5 Air Handler leaking across plant room floor out into common area wetting carpets | Air Conditioning | Evaporative Coolers | 219.6 | Pass | Pass | 0 | 0 | 2 | 2023-02-02 09:27 | 2023-02-03 17:00 | 2023-02-02 12:30 | 2023-02-03 17:00 | 2023-02-02 14:30
MSA-DTWD | WA6529168 | 2 | AWB Co. | repair or replace Wilco 32 amp 3 phase socket | Equipment | Electrical Equipment | 1207.72 | Pass | Fail | 0 | 0 | 2 | 2023-02-02 16:22 | 2023-02-07 17:00 | 2023-02-07 15:30 | 2023-02-07 17:00 | 2023-02-07 17:30
MSA-DCA | WA6533383 | 1 | Techworks Electrical | E Block - no power in the fire pump room. | Electrical | General Electrical | 472.96 | Pass | Pass | 0 | 0 | 2 | 2023-02-05 18:01 | 2023-02-06 17:00 | 2023-02-05 18:30 | 2023-02-06 17:00 | 2023-02-05 20:30
MSA-DTWD | WA6534973 | 2 | AWB Co. | Children's bathroom - Faulty exhaust fan | Electrical | General Electrical | 602.98 | Pass | Pass | 0 | 0 | 2 | 2023-02-06 13:50 | 2023-02-09 17:00 | 2023-02-08 08:00 | 2023-02-09 17:00 | 2023-02-08 10:00
MSA-DTAG | WA6539312 | 3 | Sapio Pty Ltd | Registry room - security screen not working - power failure over W.E | Security | CCTV Surveillance | 269 | Pass | Pass | -1 | -1 | 2 | 2023-02-08 12:10 | 2023-02-15 17:00 | 2023-02-10 09:30 | 2023-02-15 17:00 | 2023-02-10 11:30
MSA-DFES | WA6539696 | 2 | Water2water Pty Ltd | Ground-kitchen-ZIP Water Cooler (A40139083H) is leaking water from unit.-see notes | Plumbing & Drainage | Water | 469.82 | Pass | Pass | 0 | 0 | 2 | 2023-02-08 16:15 | 2023-02-13 17:00 | 2023-02-13 08:00 | 2023-02-13 17:00 | 2023-02-13 10:00
MSA-DCA | WA6540350 | 3 | Techworks Electrical | Admin - Level 1 - Scott Mitchells office - Light switch is difficult to turn on | Electrical | Lighting, Internal | 238.8 | Pass | Pass | 0 | 0 | 2 | 2023-02-09 10:16 | 2023-02-16 17:00 | 2023-02-13 11:00 | 2023-02-16 17:00 | 2023-02-13 13:00
MSA-DTWD | WA6560984 | 2 | Lane's Plumbing | Building: 833 Homestead - Room: Galley - Dishwasher faulty | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 2 | 2023-02-13 15:34 | 2023-02-16 17:00 | 2023-02-14 14:00 | 2023-02-16 17:00 | 2023-02-14 16:00
MSA-DTWD | WA6560990 | 1 | AWB Co. | Lift Foyer - Lift 3 & 4 - Damaged Green doors - Broken Hinges | Building | Doors | 323.71 | Pass | Pass | 0 | 0 | 2 | 2023-02-13 15:40 | 2023-02-14 17:00 | 2023-02-14 09:30 | 2023-02-14 17:00 | 2023-02-14 11:30
MSA-DTWD | WA6573057 | 3 | AWB Co. | Room 6G31 - Cabinet Making work shop - Damaged 3 phase conduit on north wall | Electrical | General Electrical | 247.5 | Pass | Pass | -1 | -1 | 2 | 2023-02-14 10:38 | 2023-02-21 17:00 | 2023-02-15 09:30 | 2023-02-21 17:00 | 2023-02-15 11:30
MSA-DTWD | WA6573379 | 1 | Techworks Plumbing | Whole toilet block is blocked. Gurgling from pipework. Backing up. | Plumbing & Drainage | Toilets/Cisterns | 482.3 | Pass | Pass | 0 | 0 | 2 | 2023-02-14 12:57 | 2023-02-15 17:00 | 2023-02-15 08:00 | 2023-02-15 17:00 | 2023-02-15 10:00
MSA-DTWD | WA6573504 | 1 | BJ SYSTEMS | Access code to electronic keypad needs changing as well as latch | Security | Keys & Access | 1197.35 | Pass | Pass | 0 | 0 | 2 | 2023-02-14 13:56 | 2023-02-15 17:00 | 2023-02-15 08:45 | 2023-02-15 17:00 | 2023-02-15 10:45
MSA-DFES | WA6578825 | 2 | Australian HVAC Services Pty. Ltd. | Station Officers Office- Aircon Leaking OH&S | Air Conditioning | Room Air Conditioners | 246.92 | Pass | Pass | -1 | -1 | 2 | 2023-02-15 12:20 | 2023-02-20 17:00 | 2023-02-16 08:00 | 2023-02-20 17:00 | 2023-02-16 10:00
MSA-DTWD | WA6585523 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, External | 279.3 | Pass | Pass | -1 | -1 | 2 | 2023-02-16 08:23 | 2023-02-21 17:00 | 2023-02-16 12:30 | 2023-02-21 17:00 | 2023-02-16 14:30
MSA-DTWD | WA6585664 | 3 | AWB Co. | East stairs level 3.5 & 4 - x2 Lights out | Electrical | Lighting, Internal | 500.82 | Fail | Fail | 1 | 1 | 2 | 2023-02-16 09:48 | 2023-02-23 17:00 | 2023-03-03 08:00 | 2023-02-23 17:00 | 2023-03-03 10:00
MSA-DCA | WA6586153 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Harry Butler Building - Plant room - Chiller 1 is in fault | Refrigeration | Chiller | 281.53 | Pass | Pass | 0 | 0 | 2 | 2023-02-16 13:49 | 2023-02-16 15:49 | 2023-02-16 14:00 | 2023-02-16 17:49 | 2023-02-16 16:00
MSA-DTWD | WA6655054 | 2 | AWB Co. | Circuit Breaker for Guillotine - tripping out | Electrical | General Electrical | 466.5 | Pass | Pass | 0 | 0 | 2 | 2023-02-21 10:15 | 2023-02-24 17:00 | 2023-02-23 14:45 | 2023-02-24 17:00 | 2023-02-23 16:45
MSA-DCA | WA6667789 | 2 | GPS Plumbing & Gas Services PtyLtd | Furthest cubicle from entry door - seat broken | Plumbing & Drainage | Toilets/Cisterns | 528.43 | Pass | Pass | 0 | 0 | 2 | 2023-02-21 14:53 | 2023-02-24 17:00 | 2023-02-22 08:00 | 2023-02-24 17:00 | 2023-02-22 10:00
MSA-DTWD | WA6671714 | 3 | AWB Co. | Student Mess area - 6 faulty lights | Electrical | Lighting, Internal | 867 | Pass | Pass | 0 | 0 | 2 | 2023-02-23 10:05 | 2023-03-02 17:00 | 2023-02-27 11:00 | 2023-03-02 17:00 | 2023-02-27 13:00
MSA-DCA | WA6671942 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level G - UATs - Exhaust system Faulty- Toilet Smells | Air Conditioning | Ducted Split System | 259.01 | Pass | Pass | 0 | 0 | 2 | 2023-02-23 11:26 | 2023-02-28 17:00 | 2023-02-28 11:00 | 2023-02-28 17:00 | 2023-02-28 13:00
MSA-DTAG | WA6672307 | 3 | Midolo Building Services | Level 8 - Court 85 - Public Gallery - Squeaky Chairs | Building | General Building | 253.47 | Pass | Pass | 0 | 0 | 2 | 2023-02-23 14:42 | 2023-03-02 17:00 | 2023-02-27 07:15 | 2023-03-02 17:00 | 2023-02-27 09:15
MSA-DFES | WA6673314 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor -- Reception - Female toilets - Light Flickering | Electrical | Lighting, Internal | 637.07 | Pass | Pass | 0 | 0 | 2 | 2023-02-24 12:38 | 2023-03-01 17:00 | 2023-02-28 11:45 | 2023-03-01 17:00 | 2023-02-28 13:45
MSA-DCA | WA6674027 | 1 | Techworks Plumbing | Basement B1 - Francis street - Sewer pump failure | Plumbing & Drainage | Sewer Drains & Septic Systems | 422.3 | Pass | Pass | 0 | 0 | 2 | 2023-02-27 07:36 | 2023-02-27 17:00 | 2023-02-27 08:00 | 2023-02-27 17:00 | 2023-02-27 10:00
MSA-DTWD | WA6675925 | 1 | Equans Mechanical Services Australia | Aircon AC1 is on fault not turning on | Air Conditioning | Ducted Split System | 219.6 | Pass | Pass | 0 | 0 | 2 | 2023-02-28 10:31 | 2023-03-01 17:00 | 2023-03-01 14:00 | 2023-03-01 17:00 | 2023-03-01 16:00
MSA-DTWD | WA6681798 | 3 | AWB Co. | Faulty bench top GPO | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2023-03-02 12:06 | 2023-03-10 17:00 | 2023-03-08 12:30 | 2023-03-10 17:00 | 2023-03-08 14:30
MSA-DTAG | WA6707674 | 1 | Australian HVAC Services Pty. Ltd. | Comms room - Air con leaking a massive amount of water, floor is flooded | Air Conditioning | Evaporative Coolers | 320.94 | Pass | Pass | 0 | 0 | 2 | 2023-03-13 08:20 | 2023-03-14 17:00 | 2023-03-13 09:30 | 2023-03-14 17:00 | 2023-03-13 11:30
MSA-DCA | WA6727382 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Ground floor - Georgraf room - bad tempreture | Air Conditioning | Ducted Split System |  | Pass | Pass | -1 | -1 | 2 | 2023-03-15 12:46 | 2023-03-20 17:00 | 2023-03-15 14:00 | 2023-03-20 17:00 | 2023-03-15 16:00
MSA-DCA | WA5453541 | 1 | Schindler Lifts Australia | Lift placed out of service - See notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2 | 2022-05-17 09:58 | 2022-05-18 17:00 | 2022-05-17 14:16 | 2022-05-18 17:00 | 2022-05-17 16:16 |  |  | Lift ROA with overload intermittently coming on with errors 85(10), 1209(0x10040001). LONLMS to be replaced and recommissioned,Unit isolated for new parts to be fitted.
MSA-DTAG | WA6531544 | 2 | Sapio Pty Ltd | Custody - Control Room - intercom from driveway does not disconnect and leaves call open - See Notes | ICT/Audiovisual | General AV works | 139.88 | Pass | Pass | 0 | 0 | 2 | 2023-02-03 12:24 | 2023-02-08 17:00 | 2023-02-06 07:31 | 2023-02-08 17:00 | 2023-02-06 09:31
MSA-DFES | WA4990903 | 1 | Australian HVAC Services Pty. Ltd. | Dorm 5 - blocked air con drain | Air Conditioning | Building HVAC Maintenance (Major Plant) | 229.47 | Pass | Pass | 0 | 0 | 2 | 2022-01-04 12:59 | 2022-01-05 17:00 | 2022-01-04 13:00 | 2022-01-05 17:00 | 2022-01-04 15:00 |  |  | Blockage repaired
MSA-DTWD | WA4991622 | 1 | Critical Fire Protection & Training | fire panel - in fault | Fire Protection Services | Fire Protection - Monitor System | 588.86 | Pass | Pass | 0 | 0 | 2 | 2022-01-05 10:16 | 2022-01-06 17:00 | 2022-01-05 12:00 | 2022-01-06 17:00 | 2022-01-05 14:00 |  |  | Fault E-BlockRodents damaged cable to external Bell - EblockCable to external bell repairedOn attendance D-Block FIP showing fire alarm - Replaced 1x detector D-Block Plant Room
MSA-DTAG | WA4992348 | 2 | Australian HVAC Services Pty. Ltd. | Court Room 2 - Aircon doesn’t seem to be working | Air Conditioning | Room Air Conditioners | 229.47 | Pass | Pass | -1 | -1 | 2 | 2022-01-06 10:35 | 2022-01-11 17:00 | 2022-01-07 07:30 | 2022-01-11 17:00 | 2022-01-07 09:30 |  |  | Attended site, tested pac3 serving court2, found no mechanical problems in it's operation, checked vms controls ports & connections in msb. Checked bms control settings. Checked court 2 temperature ok. No problems with system indicated.
MSA-DTWD | WA4993497 | 2 | Falcetta Plumbing and Gas | Toilet Next to G24 - water running into the bowl of toilet | Plumbing & Drainage | Toilets/Cisterns | 390.85 | Fail | Fail | 1 | 1 | 2 | 2022-01-07 15:43 | 2022-01-12 17:00 | 2022-01-19 10:30 | 2022-01-12 17:00 | 2022-01-19 12:30 |  |  | Replaced toilet cistern
MSA-DTWD | WA4994845 | 3 | Falcetta Plumbing and Gas | East Block - Male Student toilet - Full flush button not working | Plumbing & Drainage | Water | 218.84 | Fail | Fail | 0 | 0 | 2 | 2022-01-10 08:06 | 2022-01-17 17:00 | 2022-01-20 13:00 | 2022-01-17 17:00 | 2022-01-20 15:00 |  |  | repaired flush button and unblocked urinal
MSA-DFES | WA4995570 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ensuite #2 - half hand basin is wobbly | Plumbing & Drainage | Materials | 241.04 | Pass | Pass | 0 | 0 | 2 | 2022-01-10 13:57 | 2022-01-13 17:00 | 2022-01-12 07:30 | 2022-01-13 17:00 | 2022-01-12 09:30 |  |  | Attend site to investigate wobble basin, found China basin loose in counter top, removed basin and cleaned up old sealant, re fitted basin and new sealant, tested and checked. Have left sign on basin not to be used for 24 hours and for fire filters to remove duct tap after 24 hours.
MSA-DTAG | WA5010440 | 3 | Schindler Lifts Australia | Level 10 - Lift 3 - door is opening and is constantly beeping | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 2 | 2022-01-12 14:15 | 2022-01-19 17:00 | 2022-01-12 16:37 | 2022-01-19 17:00 | 2022-01-12 18:37 |  |  | Found car door roller worn out and level 10 LHS pick up rollers out of adjustment. Changed roller, made adjustments to landingdoor pick up rollers, tested and returned lift to service.to be closed out at $0 cost
MSA-DTAG | WA5017244 | 3 | Seme Solutions Pty Ltd | Main Building - Managers Office - access cards faulty - see notes below | Security | Access Control | 520 | Fail | Fail | 3 | 3 | 2 | 2022-01-13 11:51 | 2022-01-20 17:00 | 2022-02-07 14:30 | 2022-01-20 17:00 | 2022-02-07 16:30 |  |  | Tested reported faulty cards. Nil response from reader. The sites access control cards were encrypted. The encryption "timed" out while 4 cards were offsite, failing to update. Ran encryption and installed on reported cards. All OK.
MSA-DTWD | WA5017345 | 2 | Complete Pest Management Services | Ground - corridor rooms F1 to F7 - Spider infestation along entire corridor | Pest Control | General Pest | 264.8 | Pass | Pass | -1 | -1 | 2 | 2022-01-13 13:01 | 2022-01-18 17:00 | 2022-01-14 10:30 | 2022-01-18 17:00 | 2022-01-14 12:30 |  |  | ULV application of residual repellent pesticide internally through F1-F7 corridor and externally to F1-F7 walls, windows, doorways and patios.The entire premises has an extremely severe external spider infestation leading to an infestation internally.A full internal and external treatment of the entire premises is required.
MSA-DTAG | WA5018150 | 3 | Seme Solutions Pty Ltd | Front counter- Reception - Duress alarm key stuck inside after reset (possible warranty) | Security | Keys & Access | 573.35 | Fail | Fail | 2 | 2 | 2 | 2022-01-14 09:30 | 2022-01-21 17:00 | 2022-02-07 09:00 | 2022-01-21 17:00 | 2022-02-07 11:00 |  |  | Inspected duress button, found key still stuck inside the duress mech - removed cover to release key - replaced duress button with new dual press model. Tested duress and confirmed activation, all ok.
MSA-DTWD | WA5018580 | 2 | Techworks Electrical | JSC lights not working | Electrical | Lighting, Internal | 278.08 | Pass | Pass | 0 | 0 | 2 | 2022-01-14 13:09 | 2022-01-19 17:00 | 2022-01-17 14:30 | 2022-01-19 17:00 | 2022-01-17 16:30 |  |  | Attended site and inspected lights. Sourced parts and returned to site to replace
MSA-DCA | WA5038440 | 2 | Techworks Electrical | Tech Store / Outside RR1 - faulty light - see notes below | Electrical | General Electrical | 137.77 | Pass | Pass | 0 | 0 | 2 | 2022-01-17 13:13 | 2022-01-20 17:00 | 2022-01-17 14:30 | 2022-01-20 17:00 | 2022-01-17 16:30 |  |  | Replaced faulty mech for new mech
MSA-DTWD | WA5067848 | 3 | AWB Co. | Level 2 - Creche - Re fit fallen pinboard | Building | General Building | 216 | Pass | Pass | 0 | 0 | 2 | 2022-01-19 11:01 | 2022-01-27 17:00 | 2022-01-25 07:00 | 2022-01-27 17:00 | 2022-01-25 09:00 |  |  | Attended site, filled out JSA, located pin board and installed where instructed.
MSA-DCA | WA5069099 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS - Multiple Alarms | Air Conditioning | Room Air Conditioners | 917.2 | Pass | Pass | 0 | 0 | 2 | 2022-01-19 14:54 | 2022-01-19 16:54 | 2022-01-19 16:00 | 2022-01-19 18:54 | 2022-01-19 18:00 |  |  | Attended site, accessed mechanical plant room and found multiple equipment in alarm. Reset chillers, variable speed drives, pumps, fans etc. Phoned Honeywell to dial in and reset on the building management system. Received confirmation from Honeywell that all central plant equipment for the state library and museum were back online operating as per normal.
MSA-DCA | WA5069172 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Venue Management Office - FCU is in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 287.8 | Fail | Fail | 0 | 0 | 2 | 2022-01-19 15:51 | 2022-01-19 16:21 | 2022-01-19 16:30 | 2022-01-19 17:51 | 2022-01-19 18:30 |  |  | Investigated 2x fcu (2.16 + 2.17) in venue management office. Found saf in fault causing cooling valve to stay shut. Checked over units and fans were running. Reset controls and checked bms. Faults cleared. Units operating as should. Completed paperwork.
MSA-DCA | WA5074848 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Room Temp alarm - Gallery 1, 6 and Perimetre Gallery 6 | Air Conditioning | Room Air Conditioners | 240.7 | Fail | Fail | 3 | 3 | 2 | 2022-01-19 23:28 | 2022-01-20 17:00 | 2022-02-07 12:00 | 2022-01-20 17:00 | 2022-02-07 14:00 |  |  | Attended site and found various ahus with the zone dampers positions driving in the opposite direction, Schneider to instigate and rectify.
MSA-DFES | WA5086850 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Engine Room - Ground - Change Room Number 1 - drain blocked | Plumbing & Drainage | Drainage | 227.65 | Pass | Pass | 0 | 0 | 2 | 2022-01-21 14:30 | 2022-01-27 17:00 | 2022-01-24 07:00 | 2022-01-27 17:00 | 2022-01-24 09:00 |  |  | Arrived on site and singed in went to Change room 1 run sink and shower flush toilet nothing was blocked did paper test everything was fine. Walk around the back and checked DG all good.
MSA-DCA | WA5087040 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Gallery 10 to 13 - FCU 7 - high humidity alarm - 46.925 is value | Air Conditioning | Room Air Conditioners | 334.9 | Fail | Fail | 1 | 1 | 2 | 2022-01-22 22:54 | 2022-01-23 00:54 | 2022-01-27 09:00 | 2022-01-23 02:54 | 2022-01-27 11:00 |  |  | Attended site, signed in and accessed the centenary wing building and located fcu 7.Found the humidifier in alarm with and low level sensor reading. Reset the unit and hours on the humidifier. Checked operation and monitored running conditions. Unit is now working as per normal.
MSA-DTWD | WA5090090 | 2 | Damian Rak Electrical Pty Ltd | BLD 816 - lounge - Faulty Ceiling Fan | Electrical | General Electrical |  | Fail | Fail | 0 | 0 | 2 | 2022-01-25 09:27 | 2022-01-31 17:00 | 2022-02-01 13:00 | 2022-01-31 17:00 | 2022-02-01 15:00 |  |  | job completed - replaced fan
MSA-DTWD | WA5092055 | 0 | AWB Co. | Burning smell coming from the distribution board - see notes below | Electrical | Distribution Board | 357.02 | Pass | Pass | 0 | 0 | 2 | 2022-01-27 13:38 | 2022-01-27 15:38 | 2022-01-27 15:15 | 2022-01-27 17:38 | 2022-01-27 17:15 |  |  | Attended site and signed in. Completed JSA. Spoke to Jeffri about job. Located switchboard in O Block with reported burning smell. De energised board from main switch. Took off covers one by one to look for any obvious signs of burns/melts. Found there was loose connections going into red white and blue main phase fuses. Tightened up all connection points. Took all fuses out and made sure they were tight. Had another look for any burning / melting. Found there was large old connectors at top left of the board that had been burnt and melted. This was due to a loose connection . Replaced it with a connector and replaced all other ones with connectors and this would probably happen again as they were poor terminated and not a good thing to use. Put all covers back on board. Re energised circuit. Everything is okay now. Took pictures of all damage, before and after. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5092078 | 2 | Precise Air Group | S Block - Level 1 - Aircon has stopped working | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | -1 | -1 | 2 | 2022-01-27 13:53 | 2022-02-01 17:00 | 2022-01-28 10:00 | 2022-02-01 17:00 | 2022-01-28 12:00 |  |  | Attended site and signed in. Located reported unit. Found to have a communication error. Isolated and reset the system. After a period of time reinstated power ran unit. Cleared fault and left unit operational
MSA-DTWD | WA5093516 | 0 | SCAVENGER SUPPLIES PTY LTD | External - Block E - Southern End - Fire hydrant is leaking water | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 656.73 | Pass | Pass | 0 | 0 | 2 | 2022-01-28 15:42 | 2022-01-28 17:42 | 2022-01-28 16:30 | 2022-01-28 19:42 | 2022-01-28 18:30 |  |  | COMPLETED 28/01/2022PREVIOUS QUOTE ATTACHED FOR 5 Y OVERHAUL OF HYDRANTS- PREVIOUSLY SENT 5/01/2022FAILURES WILL CONTINUE UNTIL OVERHAUL COMPLETED.
MSA-DTWD | WA5098229 | 2 | Equans Mechanical Services Australia | ET07 - Faulty split system air conditioners, condensers are on the roof - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 371.51 | Pass | Pass | 0 | 0 | 2 | 2022-02-01 07:46 | 2022-02-03 17:00 | 2022-02-01 13:00 | 2022-02-03 17:00 | 2022-02-01 15:00 |  |  | Located room ET07 and found a split system not running and with no power. Accessed roof and found rooftop switchboard and found that the A/c breaker was tripped. Reset breaker and test ran unit. No faults present. Ran through operations all ok. A/c issues could be due to recent construction and refurb works.
MSA-DCA | WA5098916 | 1 | Haz-Ed Services | External - Franics Street side - certify multiple anchor points along francis st behind state librar | Electrical | General Electrical | 640 | Fail | Fail | 1 | 1 | 2 | 2022-02-01 12:29 | 2022-02-02 17:00 | 2022-02-07 11:30 | 2022-02-02 17:00 | 2022-02-07 13:30 |  |  | NA
MSA-DTAG | WA5099204 | 3 | High Tech Pest Control | Cockroaches in court custody and court rooms | Pest Control | General Pest | 389 | Pass | Pass | -1 | -1 | 2 | 2022-02-01 16:17 | 2022-02-08 17:00 | 2022-02-04 16:00 | 2022-02-08 17:00 | 2022-02-04 18:00
MSA-DCA | WA5100592 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plantroom - Chiller 4 is in fault – please note this is part of the Central Energy Plant | Refrigeration | Chiller | 2873.3 | Fail | Fail | 1 | 1 | 2 | 2022-02-02 15:00 | 2022-02-03 17:00 | 2022-02-07 10:00 | 2022-02-03 17:00 | 2022-02-07 12:00 |  |  | Water entering chiller 4 vessel is to hot and trips on high pressure.Airvision attended site and carried out the tube cleans on chiller.Heat exchangers WA to attend site and carry out the heat exchanger clean for chiller 4.
MSA-DTAG | WA5101177 | 1 | Sapio Pty Ltd | Level 4 - Court 42 - In Session Button to court 42 is not functioning correctly - see notes below | Security | Monitoring | 240 | Pass | Pass | 0 | 0 | 2 | 2022-02-03 10:27 | 2022-02-04 17:00 | 2022-02-03 15:00 | 2022-02-04 17:00 | 2022-02-03 17:00 |  |  | Programmed macros and event triggers. Tested, all OK.
MSA-DFES | WA5105260 | 1 | Australian HVAC Services Pty. Ltd. | Main living area - air con has broken down - not working | Air Conditioning | Room Air Conditioners | 344.59 | Pass | Pass | 0 | 0 | 2 | 2022-02-04 08:41 | 2022-02-07 17:00 | 2022-02-04 09:45 | 2022-02-07 17:00 | 2022-02-04 11:45 |  |  | Arrived on site.due to service call of ac in main/kitchen area. Upon investigation I found the unit had been tripped by the mains.It would of tripped due to compressor overheating during the fires, reset and re tested. All working fine.
MSA-DTWD | WA5107072 | 3 | Precise Air Group | G Block - G118 - AC unit trips breaker and when reset comes on in heat mode | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | -1 | -1 | 2 | 2022-02-07 14:08 | 2022-02-14 17:00 | 2022-02-10 07:30 | 2022-02-14 17:00 | 2022-02-10 09:30 |  |  | Attended site and completed pre start paperwork and signed in. Accessed rooms g118 +g117. Test ran systems on full cooling. Systems did not fault out for the duration of the visit. Left units operating. Fm to monitor.
MSA-DTWD | WA5107787 | 2 | Precise Air Group | J006 - air con not working and not turning on | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | 0 | 0 | 2 | 2022-02-08 09:22 | 2022-02-11 17:00 | 2022-02-10 07:30 | 2022-02-11 17:00 | 2022-02-10 09:30 |  |  | Attended site signed in and gained access. Unit had been reset by staff on-site and unit does not hold fault codes. Left running all day unable to get it to go into fault. Suspect it is an intermittent comms error. Will monitor on maintenance going forward
MSA-DTWD | WA5109555 | 1 | Lane's Plumbing | BLD 821 - Flat C - Bathroom - Faulty Cistern | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 2 | 2022-02-09 11:12 | 2022-02-10 17:00 | 2022-02-09 13:00 | 2022-02-10 17:00 | 2022-02-09 15:00 |  |  | job completed - repaired faulty Cistern
MSA-DTAG | WA5126757 | 1 | Australian HVAC Services Pty. Ltd. | Supreme Court – Stirling Gardens Complex - Old Law Museum - Court 8 storage area - see below | Air Conditioning | Room Air Conditioners | 470.85 | Pass | Pass | 0 | 0 | 2 | 2022-02-14 09:49 | 2022-02-15 17:00 | 2022-02-14 10:30 | 2022-02-15 17:00 | 2022-02-14 12:30 |  |  | 40631Travel to site. Sign in and access BMS. Check operation of AHU 8 serving court 8. Found to have 100% chilled water valve, room temp 25 and no static pressure. Access plantroom and check AHU 8, found fan not running. Remove unit panels and check fan. Found Vbelts to have cracked and fallen off. Leave site and pick up new Vbelts from supplier. Return to site and access plantroom. Confirm unit isolation. Access motor mount and loosen. Fit new belts to unit, realign and tension belts. Deisolate unit and test operation, working ok.
MSA-DTWD | WA5126816 | 1 | Lane's Plumbing | Flat B Room 4 - Drain faulty | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 2 | 2022-02-14 09:58 | 2022-02-15 17:00 | 2022-02-14 10:30 | 2022-02-15 17:00 | 2022-02-14 12:30 |  |  | job completed - REPAIRS TO FAULTY DRAIN DEMPSTER HALL FLAT B
MSA-DTWD | WA5128261 | 2 | Lane's Plumbing | BLD 822 - Outside door to reception - Leaking pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-02-14 16:50 | 2022-02-17 17:00 | 2022-02-15 13:00 | 2022-02-17 17:00 | 2022-02-15 15:00 |  |  | job completed - REPAIR LEAKING PIPE RECEPTION
MSA-DTWD | WA5133596 | 1 | Precise Air Group | C Block - Ground - C36 - FCU3 Chilled Water valve motor appears to have disconnected from drive shaf | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | 0 | 0 | 2 | 2022-02-15 12:16 | 2022-02-16 17:00 | 2022-02-16 10:00 | 2022-02-16 17:00 | 2022-02-16 12:00 |  |  | Attended site and completed pre start paperwork and signed in. Located c block ahu 3 and inspected chilled water valve with reports of the stem coming off of the motor. Re attached stem to valve and actuator. Reassembled actuator as lid had been removed. Test ran valve multiple times and monitored. Left system in good working order. No further works required.
MSA-DTWD | WA5133829 | 1 | Techworks Plumbing | T block - Ground floor - male toilets next to café- Urinal block | Plumbing & Drainage | Toilets/Cisterns | 387.98 | Pass | Pass | 0 | 0 | 2 | 2022-02-15 14:45 | 2022-02-16 17:00 | 2022-02-16 07:00 | 2022-02-16 17:00 | 2022-02-16 09:00 |  |  | Attended site and signed inLocated urinal that was blocked. Poured a bottle of momar into urinal and let it sit for a few minutes. Plunged urinal and used a flat head to help break up urine clogged in urinal. Slowly started to drain so repeated this process 2 more times until blockage was fully gone. Tested urinal and everything back in working order. Removed out of order sign from door and signed out. Completed paperworkCompleted work
MSA-DFES | WA5133846 | 2 | Critical Fire Protection & Training | Unit 21- Ground - Shed - see details | Fire Protection Services | Fire Protection - Monitor System | 407 | Pass | Pass | 0 | 0 | 2 | 2022-02-15 15:09 | 2022-02-18 17:00 | 2022-02-16 10:00 | 2022-02-18 17:00 | 2022-02-16 12:00 |  |  | Attended site to investigate leak on hydrant in service yard.After investigation we determined the hydrant washer was split andrequired overhaul.Overhauled 2x hydrant heads on site.All okay on departure.
MSA-DCA | WA5142610 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Multiple Air condition fault- FCU3 &4- AC1,AC 2,AC3&AC6 | Air Conditioning | Room Air Conditioners | 1299.63 | Pass | Pass | 0 | 0 | 2 | 2022-02-16 17:28 | 2022-02-16 19:28 | 2022-02-16 18:00 | 2022-02-16 21:28 | 2022-02-16 20:00 |  |  | Checked art gallery BMS and galleries with high humidity. Found system in local mode with chiller 2 running but no cooling tower fans running and water temperatures high. Manualed the fans on and checked operation, placed back in auto. Went to the state library and checked ETS. Manualed the art gallery to run on the ETS. Humidity and temperature alarms all cleared as system can back into range. System to be looked over in the morning.
MSA-DTWD | WA5150996 | 2 | GRAFFITI FORCE PTY LTD | Bicycle shed has graffiti on walls and tables needs re painting | Cleaning | Graffiti | 319.92 | Pass | Pass | 0 | 0 | 2 | 2022-02-17 09:55 | 2022-02-22 17:00 | 2022-02-22 10:00 | 2022-02-22 17:00 | 2022-02-22 12:00 |  |  | REMOVAL OF GRAFFITI FROM BIKE SHED, WALLS AND TABLES
MSA-DCA | WA5164728 | 0 | EQUANS Mechanical Services (WA) Pty Limited | FCU8 Humidity alarm - value - 44.375 | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 2 | 2022-02-20 00:21 | 2022-02-20 02:21 | 2022-02-20 01:30 | 2022-02-20 04:21 | 2022-02-20 03:30 |  |  | Trent called unable to see work order program:-Checked BMS for faults, found steam generators in fault, and centenary humidified tripped, steam generators in low water fault, found RO pump in fault, reset and run a re-test. Checked RO tank, reset steamed generators and humified in centenary.
MSA-DTWD | WA5176408 | 2 | AWB Co. | D Block - Level 2 - Male toilet - Replace broken toilet roll holers Male Toilet | Building | General Building | 410 | Pass | Pass | 0 | 0 | 2 | 2022-02-21 14:14 | 2022-02-24 17:00 | 2022-02-24 14:30 | 2022-02-24 17:00 | 2022-02-24 16:30 |  |  | Bought toilet roll holdersRemoved existingFitted new holders
MSA-DFES | WA5177223 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Ceiling rose pulled away from fixed position has damaged ceiling & now hanging | Electrical | Lighting, Internal | 224.37 | Pass | Pass | 0 | 0 | 2 | 2022-02-21 16:06 | 2022-02-24 17:00 | 2022-02-24 10:00 | 2022-02-24 17:00 | 2022-02-24 12:00 |  |  | Arrived on site at 1000 to attend damaged ceiling rose in engine room. Identified and isolated battery feeding equipment and relocated ceiling rose. Completed works at 1200 and left site.Notes: workers left site during completion of works and did not retrieve signature slips/maintenance log.
MSA-DTAG | WA5186800 | 3 | Sapio Pty Ltd | Security Office - swipe card system needs to be modified to delete access to a door | Security | Access Control | 250 | Pass | Pass | -1 | -1 | 2 | 2022-02-22 09:25 | 2022-03-01 17:00 | 2022-02-23 13:00 | 2022-03-01 17:00 | 2022-02-23 15:00 |  |  | Modified access to door as per security
MSA-DFES | WA5186931 | 3 | Protek 24/7 Building & Maintenance | SO Shower Area - Soap Dish tile broken and smashed - details below | Building | General Building | 401.52 | Pass | Pass | -1 | -1 | 2 | 2022-02-22 10:00 | 2022-03-01 17:00 | 2022-02-24 07:30 | 2022-03-01 17:00 | 2022-02-24 09:30 |  |  | Broken soap dish
MSA-DTWD | WA5187145 | 2 | Techworks Electrical | C-Block exterior walkway west end has a broken light on the pole | Electrical | General Electrical | 538.37 | Pass | Pass | 0 | 0 | 2 | 2022-02-22 11:41 | 2022-02-25 17:00 | 2022-02-24 07:00 | 2022-02-25 17:00 | 2022-02-24 09:00 |  |  | Replaced globe and pole surround head.
MSA-DTWD | WA5188543 | 3 | AWB Co. | HWS for the Ladies ,Men's toilet & the kitchen trips the breaker switch at least once week | Electrical | General Electrical | 457.03 | Pass | Pass | 0 | 0 | 2 | 2022-02-23 09:40 | 2022-03-02 17:00 | 2022-02-28 13:00 | 2022-03-02 17:00 | 2022-02-28 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job, located HWS with fault. Looked in distribution board and found that circuit breaker was tripped. Tried to turn on circuit breaker and it instantly tripped. Went to HWS and isolated at isolator. Turned water supply off for hot water system and drained water. Took photo of details and went to Reece plumbing to pick up replacement parts. Returned to site. Made sure HWS was completely drained. Removed element and thermostat. Wired in new element and thermostat. Made sure all seals were water tight. Re filled HWS. Water was coming out brown as sediment had been stirred up. Filled up and flushed out hot water system 3 times and water was coming out much clearer. Spoke to fm and he said to let sediment to settle. Filled up HWS. let water heat up. Tested that water was being heated and it was. ( drainage pipe for hws was blocked by wood that hws was sitting on, also drainage pipe was leaking in female toilet - reported to fm,
MSA-DCA | WA5189256 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Air con is not starting | Air Conditioning | Building HVAC Maintenance (Major Plant) | 486.65 | Pass | Pass | 0 | 0 | 2 | 2022-02-23 16:51 | 2022-02-23 18:51 | 2022-02-23 17:30 | 2022-02-23 20:51 | 2022-02-23 19:30 |  |  | See work logs
MSA-DTWD | WA5190283 | 3 | AWB Co. | Door does not close correctly | Building | Doors | 210 | Pass | Pass | 0 | 0 | 2 | 2022-02-24 12:20 | 2022-03-03 17:00 | 2022-02-28 11:30 | 2022-03-03 17:00 | 2022-02-28 13:30 |  |  | Opened and closed cortina doors and showed How to operate correctly
MSA-DTWD | WA5190845 | 1 | WESTERN IRRIGATION PTY LTD | Simpson Avenue side of Campus - Main reticulation bore - see notes below | Landscaping & Gardening | Grounds Maintenance | 435 | Pass | Pass | 0 | 0 | 2 | 2022-02-24 15:27 | 2022-02-25 17:00 | 2022-02-25 13:00 | 2022-02-25 17:00 | 2022-02-25 15:00 |  |  | Investigated fault, found the modem signal had failed, reset modem and tested system, system work correctly.
MSA-MRWA | WA5195760 | 2 | EQUANS Mechanical Services (WA) Pty Limited | G and L1 A/C - Check A/C timers on G floor, Check temp on L1 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-02-28 15:22 | 2022-03-03 17:00 | 2022-03-01 10:00 | 2022-03-03 17:00 | 2022-03-01 12:00 |  |  | Travelled to site and signed in. Adjusted time schedules on the genesis controller as requested by client. New department moving in on the ground floor and time schedules had to be extended.
MSA-DTWD | WA5199703 | 2 | Precise Air Group | Air con is not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-03-01 11:16 | 2022-03-04 17:00 | 2022-03-02 12:00 | 2022-03-04 17:00 | 2022-03-02 14:00 |  |  | Braf declined - closing work order for invoicing
MSA-DTWD | WA5201297 | 3 | AWB Co. | Room A51 - 3 x lights unable to be fixed in house | Electrical | Lighting, Internal | 362.9 | Pass | Pass | -1 | -1 | 2 | 2022-03-02 13:24 | 2022-03-10 17:00 | 2022-03-03 07:00 | 2022-03-10 17:00 | 2022-03-03 09:00 |  |  | Attended site and signed in. Completed JSA. Spoke to Dave about jobs. Replaced tubes and starters in 2x fittings. Both lights are now working as intended. Went upstairs to look at faulty 3 gang light switch. Went to wholesaler to get part for job. Returned to site and changed over light switch. Labelled switch. Lights and switch are all now working as intended. Took pictures before and after. Completed paperwork. Signed out.*** Job Complete ***
MSA-DTWD | WA5206743 | 1 | Milners Tree Solutions Pty Ltd | Garden/Path between A Block and C Block -Large tree branch has fallen across pathway | Landscaping & Gardening | Tree Lopping | 1000 | Pass | Pass | 0 | 0 | 2 | 2022-03-08 09:05 | 2022-03-09 17:00 | 2022-03-08 10:00 | 2022-03-09 17:00 | 2022-03-08 12:00 |  |  | Fallen limb removed.
MSA-DTWD | WA5207158 | 2 | Precise Air Group | Block E - BAY TREE DELI -Side of the sandwich prep fridge is faulty | Refrigeration | Refrigerators | 235.48 | Pass | Pass | 0 | 0 | 2 | 2022-03-08 11:21 | 2022-03-11 17:00 | 2022-03-09 13:30 | 2022-03-11 17:00 | 2022-03-09 15:30 |  |  | Attended site and completed pre start paperwork and signed in. Acessed deli and inspected sandwich fridge. Test ran equipment and found all working OK. Removed side cover and re fitted. Secured with extra tech screws. Packed up and cleaned work area. Completed paperwork and left all ok
MSA-DTWD | WA5207406 | 1 | AWB Co. | E block - E609 - Projector - wall mounted control panel emitting a intermittent beeping sound | Electrical | General Electrical | 300.57 | Pass | Pass | 0 | 0 | 2 | 2022-03-08 12:56 | 2022-03-09 17:00 | 2022-03-09 07:00 | 2022-03-09 17:00 | 2022-03-09 09:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Went to E block and located room with faulty/beeping control panel. Took control panel cover off to look what was behind. Found 2 connections going in. Found there was a battery, suspected that battery was dead, hence the beeping noise. Went to Bunnings to pick up new battery. Replaced battery and issue was still present. Talked to fm and he said not to worry about it as it is an IT job as of now. Took pictures. Put everything back together. Completed paperwork. Signed out.*** Job complete ***
MSA-DCA | WA5207687 | 1 | SCAVENGER SUPPLIES PTY LTD | Jubilee - Level 1 - refection's fire services door - magnetic door catch faulty- cable damaged | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 2 | 2022-03-08 15:37 | 2022-03-09 17:00 | 2022-03-09 08:30 | 2022-03-09 17:00 | 2022-03-09 10:30 |  | WACCES | COMPLETED 09/03/2022
MSA-DTWD | WA5208910 | 2 | Equans Mechanical Services Australia | A Block - Ground - see details below | Air Conditioning | Room Air Conditioners | 474.22 | Pass | Pass | 0 | 0 | 2 | 2022-03-09 11:53 | 2022-03-14 17:00 | 2022-03-11 11:30 | 2022-03-14 17:00 | 2022-03-11 13:30 |  |  | Arrived on site signed in checked in with Dennis. Assisted by Dave with working at heights cleaned evaporative unit added bactierial solution. Tested all ok monitored operation. Cleaned up and completed paperwork.
MSA-DTWD | WA5215725 | 1 | AWB Co. | Level 1 - 106 Store room - Electrics to be disconnected from boiler tank due to water leaking. | Electrical | General Electrical | 232.31 | Pass | Pass | 0 | 0 | 2 | 2022-03-10 15:56 | 2022-03-11 17:00 | 2022-03-11 13:00 | 2022-03-11 17:00 | 2022-03-11 15:00 |  |  | Attended site and signed in,completed jsa,spoke to fm about job , located hws , got lock from facilities to lock out isolator, isolated breaker for hws, removed cables from hws and put in jbox, placed out of service tags on lol points of isolation , cleaned up , packed up , completed paperwork Job completed
MSA-DTWD | WA5215726 | 1 | BAKE-QUIP PTY LTD | Canteen ovens x 2 need repairs to flues and doors | Equipment | Catering Equipment | 360 | Fail | Fail | 0 | 0 | 2 | 2022-03-10 16:02 | 2022-03-11 17:00 | 2022-03-14 09:00 | 2022-03-11 17:00 | 2022-03-14 11:00 |  |  | REFER SERVICE REPORT.
MSA-DTWD | WA5216265 | 1 | Precise Air Group | Kendrew- E-Block Restaurant aircon not cooling | Air Conditioning | Room Air Conditioners | 266.88 | Pass | Pass | 0 | 0 | 2 | 2022-03-11 09:04 | 2022-03-14 17:00 | 2022-03-11 13:30 | 2022-03-14 17:00 | 2022-03-11 15:30 |  |  | Attended site and completed pre start paperwork andsigned in. Completed working at heights permit andacessed evap on restraunt roof. Inspected unit and foundall components operating all ok. Increased water flowover pads. Ambient conditions are really humid causingevap not to have much of an effect. No further worksrequired.
MSA-DTWD | WA5216585 | 3 | AWB Co. | A321 - gas Door closer is leaking | Building | General Building | 309.5 | Pass | Pass | 0 | 0 | 2 | 2022-03-11 11:23 | 2022-03-18 17:00 | 2022-03-18 12:00 | 2022-03-18 17:00 | 2022-03-18 14:00 |  |  | replaced broken door closure with new
MSA-DTWD | WA5216640 | 2 | Techworks Electrical | Kendrew- A-Block 1st Floor East wing - room A133 - light needs replacing not working | Electrical | General Electrical | 239.19 | Pass | Pass | 0 | 0 | 2 | 2022-03-11 11:51 | 2022-03-16 17:00 | 2022-03-16 07:00 | 2022-03-16 17:00 | 2022-03-16 09:00 |  |  | Replaced damaged light globes in A block level 1 east wing
MSA-DTAG | WA5216839 | 3 | Midolo Building Services | Level 1 - Corridor - Passage door closer has seized | Building | General Building | 227.52 | Pass | Pass | -1 | -1 | 2 | 2022-03-11 13:22 | 2022-03-18 17:00 | 2022-03-14 12:00 | 2022-03-18 17:00 | 2022-03-14 14:00 |  |  | lubed, re secured & relocated
MSA-DTAG | WA5216921 | 3 | Midolo Building Services | Ground - Corridor - Door handle in secure corridor is loose | Building | General Building | 227.52 | Pass | Pass | -1 | -1 | 2 | 2022-03-11 14:05 | 2022-03-18 17:00 | 2022-03-14 12:00 | 2022-03-18 17:00 | 2022-03-14 14:00 |  |  | HANDLE RE SECURED & relocate door closer
MSA-DTWD | WA5226521 | 3 | AHS Services WA Pty Ltd (Anchor) | B107 / B108 - Hot water to B107 and toilet basins B108 not working | Plumbing & Drainage | HWS/Units Electric & Gas | 225.01 | Pass | Pass | -1 | -1 | 2 | 2022-03-14 09:37 | 2022-03-21 17:00 | 2022-03-15 10:30 | 2022-03-21 17:00 | 2022-03-15 12:30 |  |  | Completed
MSA-DTAG | WA5226700 | 2 | Dom's Total Grounds Maintenance | Ground - Front garden - Rubbsih at rear of building, water meter ticking quickly, broken retic hose | Landscaping & Gardening | Grounds Maintenance | 278 | Fail | Fail | 1 | 1 | 2 | 2022-03-14 11:36 | 2022-03-17 17:00 | 2022-03-22 07:30 | 2022-03-17 17:00 | 2022-03-22 09:30 |  |  | Call Out & Labour to repair retic & Parts
MSA-DCA | WA5226862 | 1 | Critical Fire Protection & Training | Main Building - Ground - Stage Door - Fault on FIP – zone 37. Area is currently isolated | Fire Protection Services | Fire Protection - Monitor System | 410.35 | Pass | Pass | 0 | 0 | 2 | 2022-03-14 14:00 | 2022-03-15 17:00 | 2022-03-15 09:00 | 2022-03-15 17:00 | 2022-03-15 11:00 |  |  | Multiple faults on FIP
MSA-DTWD | WA5239324 | 3 | AHS Services WA Pty Ltd (Anchor) | Female Toilet West End Ground Floor - A Block Female West ground floor last cubicle button stuck on | Plumbing & Drainage | Water | 179.8675 | Pass | Pass | 0 | 0 | 2 | 2022-03-16 11:15 | 2022-03-23 17:00 | 2022-03-21 12:45 | 2022-03-23 17:00 | 2022-03-21 14:45 |  |  | Inspected found the button loose, refitted button and replaced I let valve as it was broken in two pieces all good
MSA-DTWD | WA5258018 | 3 | Schindler Lifts Australia | Level 2 - Lift 3 - lift stuck on level 2 | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 2 | 2022-03-17 13:39 | 2022-03-24 17:00 | 2022-03-17 14:40 | 2022-03-24 17:00 | 2022-03-17 16:40 |  |  | Adjusted car doors to correct opening position. Found lift key switch for park in door circuit also. So lift would take landingcalls but because it was on park it disabled door circuitto be closed out at $0 cost
MSA-DTWD | WA5285770 | 2 | AWB Co. | A-Block - AG20 - Cover is missing from the ceiling light & the fitting is loose in the male toilets | Electrical | General Electrical | 462.92 | Pass | Pass | 0 | 0 | 2 | 2022-03-21 10:10 | 2022-03-24 17:00 | 2022-03-21 12:00 | 2022-03-24 17:00 | 2022-03-21 14:00 |  |  | Attended site signed in completed jsa. Spoke with frank to replace two lights in library staff toilets. sourced two led oyster lights and installed. ***job completed***
MSA-DTAG | WA5285923 | 0 | Schindler Lifts Australia | Level 8 - Call button panel between lift 2 & 3 has become detached from the wall | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2 | 2022-03-21 11:07 | 2022-03-21 13:07 | 2022-03-21 11:35 | 2022-03-21 15:07 | 2022-03-21 13:35 |  |  | job completed - When responding to the callback dated 21.03.2022, the Schindler Technician found that the equipment had been subjected tovandalism which had affected one of the components. The landing panels! indicators were damaged. Following our attendance, theequipment was left in service. Works due to vandalism are not covered under the terms of your maintenance agreement, thereforethis site visit will be chargeable.
MSA-DFES | WA5286345 | 2 | AWB Co. | Ground - Accessible toilet -Door to the accessible toilet has been separated from its retracting arm | Building | General Building | 210 | Fail | Fail | 0 | 0 | 2 | 2022-03-21 14:57 | 2022-03-24 17:00 | 2022-03-25 07:00 | 2022-03-24 17:00 | 2022-03-25 09:00 |  |  | Located missing parts for door closure, adjusted and re installed.
MSA-DTWD | WA5286365 | 3 | Precise Air Group | B block - room B101 - Check extraction fan working in B101 - faulty | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | -1 | -1 | 2 | 2022-03-21 15:19 | 2022-03-28 17:00 | 2022-03-23 07:30 | 2022-03-28 17:00 | 2022-03-23 09:30 |  |  | Attended site and completed pre start paperwork andsigned in. Located soldering lab. Test ran exhaust fan.Found to start and run with out fault. Monitored and leftrunning all ok.
MSA-DTWD | WA5286410 | 2 | AWB Co. | Ground - F20 Male toilets - Small toilet wall exhaust fan shutters not opening | Electrical | General Electrical | 956.61 | Pass | Pass | 0 | 0 | 2 | 2022-03-21 15:50 | 2022-03-24 17:00 | 2022-03-23 09:00 | 2022-03-24 17:00 | 2022-03-23 11:00 |  | WACCES | Attended site signed in completed jsa. Installed new wall fan for male toilets as instructed. Also replaced two plc lights to LED fittings in restaruant area toilets. *** job completed ***
MSA-DTWD | WA5287041 | 3 | AWB Co. | S Block Exterior - Front of Campus - Repair sign on Harold Street panel lifting off | Building | General Building | 210 | Pass | Pass | -1 | -1 | 2 | 2022-03-22 09:43 | 2022-03-29 17:00 | 2022-03-25 09:00 | 2022-03-29 17:00 | 2022-03-25 11:00 |  |  | Dugout sand cleaned excess glue, re stuck and screwed
MSA-DTWD | WA5287635 | 2 | AWB Co. | Block D - first floor - D210 - fluro diffusers full of dead bees - see notes | Electrical | Lighting, Internal | 347.54 | Pass | Pass | 0 | 0 | 2 | 2022-03-22 14:04 | 2022-03-25 17:00 | 2022-03-23 07:00 | 2022-03-25 17:00 | 2022-03-23 09:00 |  |  | Attended site signed in completed jsa.Spoke with Glenn site fm about job, cleaned all diffusers full off dead insects. *** job completed ***
MSA-DCA | WA5289577 | 1 | Critical Fire Protection & Training | Main Building - Stage door FIP - fire panel is in fault & screen reads "card one - | Fire Protection Services | Fire Protection - Monitor System | 294.3 | Pass | Pass | 0 | 0 | 2 | 2022-03-24 10:47 | 2022-03-25 17:00 | 2022-03-25 10:00 | 2022-03-25 17:00 | 2022-03-25 12:00 |  |  | Attend site 25th March investigate reported issue with fire system.No faults noted on arrival, checked logs , report earth fault earlier but cleared. No fault present torectify/ monitor.
MSA-DTWD | WA5290287 | 2 | AWB Co. | 107 store - reconnect hot water unit | Electrical | General Electrical | 341.42 | Pass | Pass | -1 | -1 | 2 | 2022-03-25 07:38 | 2022-03-29 17:00 | 2022-03-25 08:15 | 2022-03-29 17:00 | 2022-03-25 10:15 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Drove to b2. Located new hws. Pulled panel off. Connected cables. Put cover back on. Screwed corrie to hws. Went to board and took of out of service tag, turned on. Tested hws. Working as intended. Took pictures. Completed paperwork. Signed out. *** job complete ***
MSA-DTAG | WA5290437 | 0 | Sapio Pty Ltd | Secuirty system - multiple faults please see notes | Security | Security Management System | 260 | Fail | Fail | 0 | 0 | 2 | 2022-03-25 09:13 | 2022-03-25 11:13 | 2022-03-25 11:30 | 2022-03-25 13:13 | 2022-03-25 13:30 |  |  | Attended site. Found a broken resistor leg in Input 43. Tested auto arm, all set up correctly. Job completed.
MSA-DTAG | WA5293322 | 2 | PPM Project Painting & Maintenance | External - Graffiti on Irwin Street wall | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-03-28 10:40 | 2022-03-31 17:00 | 2022-03-30 12:00 | 2022-03-31 17:00 | 2022-03-30 14:00 |  |  | job completed - removed graffiti
MSA-DTWD | WA5293503 | 2 | Equans Mechanical Services Australia | Unit temperature can’t be changed. | Air Conditioning | Room Air Conditioners | 371.51 | Fail | Fail | 4 | 4 | 2 | 2022-03-28 10:57 | 2022-03-31 17:00 | 2022-04-26 12:00 | 2022-03-31 17:00 | 2022-04-26 14:00 |  |  | Investigated and found wall controller to be locked and indicating that unit controlled externally. Investigated and failed to locate external controls and was informed that unit should be stand alone operation. Located and found existing interface that was probably previously connected to a bms system. Disconnect interface and checked operation. Unit now runs as stand alone and controller no longer locked. Unit conditions now able to be adjusted as normal.
MSA-DFES | WA5294562 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | ground - RANGE OF LIGHTS /LIGHTING NOT WORKING - see notes for locations | Electrical | General Electrical | 475.67 | Pass | Pass | 0 | 0 | 2 | 2022-03-29 07:39 | 2022-04-04 17:00 | 2022-04-04 09:45 | 2022-04-04 17:00 | 2022-04-04 11:45 |  |  | Arrived on site at 09:45. Replaced 2 x missing tubes in gym fluro and put cover back on light, replaced 1 x blown 18w cfl globe in hallway, replaced 1 x flickering 36w tube and starter in dorm 6 change room, replaced 4 x blown 20w downlight globes in tv room. Left site at 11:45
MSA-DCA | WA5296120 | 0 | Techworks Electrical | Museum Plaza - Beauford Street Entry - see notes below | Electrical | General Electrical | 240.71 | Pass | Pass | 0 | 0 | 2 | 2022-03-30 09:21 | 2022-03-30 11:21 | 2022-03-30 10:00 | 2022-03-30 13:21 | 2022-03-30 12:00 |  | WACCES | Red and green signal lights for bollards have been taken, replacements required, removed other lights from other side to try and find part number, Cables made safe in mean time.Quote will be provided to Denise for repairs.
MSA-DTWD | WA5296130 | 2 | ECO PLUMBING AND GAS PTY LTD | F00 - Kitchen - Faulty electric hotwater system under bench | Plumbing & Drainage | HWS/Units Electric & Gas | 442.7 | Pass | Pass | 0 | 0 | 2 | 2022-03-30 09:29 | 2022-04-04 17:00 | 2022-04-01 09:00 | 2022-04-04 17:00 | 2022-04-01 11:00 |  |  | Repaired hot water unit
MSA-DFES | WA5297632 | 3 | Critical Fire Protection & Training | Fire Suppression System (tank) - Ground -Yard - see details below | Fire Protection Services | Fire Protection - Monitor System | 269.5 | Pass | Pass | -1 | -1 | 2 | 2022-03-31 11:36 | 2022-04-07 17:00 | 2022-03-31 12:00 | 2022-04-07 17:00 | 2022-03-31 14:00 |  |  | Inspected the automatic infill valve and that is not passing and is all okay.Looked inside the fire tank and found that the float valve inside the fire tank was pushedup slightly so the water level was above the outlet of the float valve and the water levelwas just as high as the over flow leading to the water overflowing slightly.I have bent the float valve back down into a good position so the water level is set lowerand In turn will not overflow the fire tank.
MSA-DTWD | WA5297782 | 2 | Lane's Plumbing | Drain blocked outside | Plumbing & Drainage | Drainage |  | Pass | Pass | -1 | -1 | 2 | 2022-03-31 12:46 | 2022-04-05 17:00 | 2022-04-01 11:30 | 2022-04-05 17:00 | 2022-04-01 13:30 |  |  | job completed - CLEAR BLOCKAGE TO DRAIN OUTSIDE HOUSE 2
MSA-DTWD | WA5301906 | 1 | Lane's Plumbing | BLD 833 - outside pit overflowing | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 2 | 2022-04-01 14:23 | 2022-04-04 17:00 | 2022-04-01 16:30 | 2022-04-04 17:00 | 2022-04-01 18:30 |  |  | CLEAR BLOCKAGE TO OUTSIDE PIT AT BLD 833
MSA-DFES | WA5302014 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Light tanker battery charger is not supplying enough charge to light tanker. | Electrical | General Electrical | 237.57 | Pass | Pass | 0 | 0 | 2 | 2022-04-01 18:20 | 2022-04-02 18:20 | 2022-04-02 07:00 | 2022-04-02 18:20 | 2022-04-02 09:00 |  |  | Arrived on site at 07:00 to investigate light tanker not charging correctly and causing iris tablet to run out of battery while plugged into charger. Cable is undersized from charger to tanker causing voltage drop when drawing current. Cable will need to be upgraded to allow for tankers requirements. Moved charger and mounted to wall, re-routed cable temporarily to fix problem and tested all okay. Left site at 09:00
MSA-DTWD | WA5304005 | 2 | Techworks Electrical | D-Block - Room D038 - broken emergency exit light | Electrical | Emergency & Exit Lighting | 489.66 | Pass | Pass | 0 | 0 | 2 | 2022-04-04 13:52 | 2022-04-07 17:00 | 2022-04-05 12:00 | 2022-04-07 17:00 | 2022-04-05 14:00 |  |  | Replaced failed exit sign and fluro tubes in D block ground floor
MSA-DTWD | WA5304163 | 3 | Equans Mechanical Services Australia | Level 4 - 402 - Excessive water running noise through AHU in classroom | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | -1 | -1 | 2 | 2022-04-04 15:19 | 2022-04-11 17:00 | 2022-04-06 10:00 | 2022-04-11 17:00 | 2022-04-06 12:00 |  |  | 6/04/2022 JASON ELLEMENTATTENDED SITE, SIGNED IN AND ACCESSED BUILDING 2. LOCATED CLASSROOM 402 AND NOTICED THE CHILLED WATER VALVE WAS MAKING A WATER HISSING NOISE. DROVE THE CHW VALVE AND THE NOISE STOPS AT 30%. THERE IS NO AIR IN THE SYSTEM CAUSING THE NOISE. IT IS RECOMMENDED ENGAGING ICON LOGIC TO ADJUST CONTROLS LOGIC SO THE CHWV MINIMUM SET POINT IS 30%. THIS WILL STOP THE WATER NOISE.
MSA-DTWD | WA5304649 | 3 | Falcetta Plumbing and Gas | Level 3 west - Male toilet - not flushing properly - end cubicle | Plumbing & Drainage | Toilets/Cisterns | 253.84 | Pass | Pass | 0 | 0 | 2 | 2022-04-05 08:54 | 2022-04-12 17:00 | 2022-04-12 13:00 | 2022-04-12 17:00 | 2022-04-12 15:00 |  |  | repaired cisterns and replaced inlet valve
MSA-DTWD | WA5306295 | 1 | Protek 24/7 Building & Maintenance | F Block - Ground - F48 - Top window pane is loose and bottom window pane can not be locked (broken l | Building | General Building | 198.42 | Pass | Pass | 0 | 0 | 2 | 2022-04-06 11:51 | 2022-04-07 17:00 | 2022-04-06 13:45 | 2022-04-07 17:00 | 2022-04-06 15:45 |  |  | Repair loose window pane
MSA-DTWD | WA5306331 | 3 | Falcetta Plumbing and Gas | Level 3 - Ladies toilet - Cistern not flushing or filling | Plumbing & Drainage | Toilets/Cisterns | 644.07 | Pass | Pass | 0 | 0 | 2 | 2022-04-06 12:25 | 2022-04-13 17:00 | 2022-04-12 15:00 | 2022-04-13 17:00 | 2022-04-12 17:00 |  |  | replaced toilet seat and repaired cistern
MSA-DTWD | WA5306551 | 2 | Precise Air Group | Kendrew- B-Block B002 - aircon's not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | -1 | -1 | 2 | 2022-04-06 14:16 | 2022-04-11 17:00 | 2022-04-07 09:00 | 2022-04-11 17:00 | 2022-04-07 11:00 |  |  | Attended site and completed pre start paperwork and singed in. Acessed units in b001/b002. Test ran systems on cooling. Found to start and run. Checked indoor components and washed return air filters. Checked sensor settings and programmed controller to read from the return air sensor. Monitored system and found to unit to cycle on and off at Set point as required. Packed up work equipment and completed paperwork. Left systems operating all ok. No further works required.
MSA-DTWD | WA5306940 | 2 | M Construction (WA) | T-Block- room T110 - has a soap dispencer come off the wall | Building | General Building | 234.85 | Pass | Pass | 0 | 0 | 2 | 2022-04-07 08:58 | 2022-04-12 17:00 | 2022-04-11 07:30 | 2022-04-12 17:00 | 2022-04-11 09:30 |  |  | Fix soap dispenser on wall with correct screws.
MSA-DFES | WA5307126 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main Administration - Ground - Administration Building - Lights out/work required - see details | Electrical | General Electrical | 468.57 | Pass | Pass | 0 | 0 | 2 | 2022-04-07 10:19 | 2022-04-14 17:00 | 2022-04-12 09:45 | 2022-04-14 17:00 | 2022-04-12 11:45 |  |  | Attended site at 945. Found multiple lights blown in main admin building and 1 storeroom sensor that client wants to stay on longer. Replaced 14 x 36w t8 840 fluros and 12 x s10 starters and tested. Adjusted storeroom sensor to maximum duration and tested. Notified staff and left site at 1145.
MSA-MRWA | WA5308982 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Crac Unit alarm -Please investigate | Air Conditioning | Materials | 515.67 | Pass | Pass | 0 | 0 | 2 | 2022-04-09 17:32 | 2022-04-09 19:32 | 2022-04-09 19:30 | 2022-04-09 21:32 | 2022-04-09 21:30 |  |  | After hours call out, attend and reset system - all ok
MSA-DCA | WA5312028 | 1 | Critical Fire Protection & Training | Stagedoor Fire Panel - Fire panel EWIS system in Alarm | Fire Protection Services | Fire Protection - Monitor System | 305.3 | Pass | Pass | 0 | 0 | 2 | 2022-04-11 10:35 | 2022-04-12 17:00 | 2022-04-11 12:00 | 2022-04-12 17:00 | 2022-04-11 14:00 |  |  | Attended site carried out checks/ activation suspect caused by "manual activation on FIP" incorrectuser operation.Reset all ok following, noted LED on FIP not potentially operating (monitor/check on next config,change)
MSA-DTAG | WA5324274 | 2 | Gilmour & Jooste Electrical | 1987 - Level 2 - Gents Toilet - Light above sink not working | Electrical | General Electrical | 64.84 | Pass | Pass | 0 | 0 | 2 | 2022-04-13 13:36 | 2022-04-20 17:00 | 2022-04-19 07:30 | 2022-04-20 17:00 | 2022-04-19 09:30 |  |  | Replaced 1x blown tube and starter in male toilet
MSA-DTWD | WA5325697 | 3 | AWB Co. | Outside East side of Building - RCD keeps tripping - Outside GPO needs checking - see notes | Electrical | General Electrical | 225.02 | Pass | Pass | -1 | -1 | 2 | 2022-04-14 11:32 | 2022-04-26 17:00 | 2022-04-20 12:00 | 2022-04-26 17:00 | 2022-04-20 14:00 |  |  | Attended site signed in completed jsa. Located security to open to sign in and locate block. Had to wait for permission as no one on site for security to unlock building. Once unlocked found gpo on east wall with a water fountain next to it. It had been tagged out. Power at gpo reads 240 which is normal. Plugged kettle in to test and it works fine. Plugged water cooler in and works for 5 mins then trips B10. Left out of service tag on fountain to not plug in again. ** job completed **
MSA-DTWD | WA5369091 | 2 | Equans Mechanical Services Australia | Canteen lunch room - Water leak from central unit | Air Conditioning | Building HVAC Maintenance (Major Plant) | 402.07 | Pass | Pass | 0 | 0 | 2 | 2022-04-19 16:33 | 2022-04-22 17:00 | 2022-04-21 09:00 | 2022-04-22 17:00 | 2022-04-21 11:00 |  |  | Found unit requires sump dump kit. Picked up parts and returned to site. Fitted new kit and checked operation. All ok
MSA-DTWD | WA5378093 | 2 | Techworks Plumbing | T Block - Level 1 - Male Toilets - toilet cubicle not flushing | Plumbing & Drainage | Toilets/Cisterns | 277.63 | Pass | Pass | -1 | -1 | 2 | 2022-04-20 11:35 | 2022-04-26 17:00 | 2022-04-21 10:00 | 2022-04-26 17:00 | 2022-04-21 12:00 |  |  | Flush button setup would not allow for a full flush. I removed paneling and inserted a spacer on the flush buttons for both men’s toilets allowing for a full depression. This allows better air flow to the pneumatic flush cistern creating a better flush
MSA-DTWD | WA5379713 | 2 | AWB Co. | Ground Level - AT223 - Accessible Toilet wall - Rising damp on wall of toilet | Building | Internal Walls | 210 | Pass | Pass | 0 | 0 | 2 | 2022-04-21 13:43 | 2022-04-27 17:00 | 2022-04-27 10:30 | 2022-04-27 17:00 | 2022-04-27 12:30 |  |  | On inspection of the toilet block I believe that the toilet water supply may may be seeping water and causing the dampness , we can not be sure of this until the pipe work has been exposed to allow us access to see all joints and seeAll evidence would suggest this is the cause but could not we gaurentee this and it would be trial and errorinspection only JSA not required
MSA-DTWD | WA5380050 | 3 | AWB Co. | 4 lights not working | Electrical | Lighting, Internal | 554.69 | Pass | Pass | 0 | 0 | 2 | 2022-04-22 08:05 | 2022-05-02 17:00 | 2022-05-02 09:00 | 2022-05-02 17:00 | 2022-05-02 11:00 |  |  | Attended site signed in completed jsa. located room with various lights out as more than what had been reported was given lighting list by Dave Gaff. replaced 6 t5 28w tubes, installed new LED robus light, and also replaced one 11.5 w globe in feature light. *** job completed***
MSA-DTWD | WA5383212 | 0 | AWB Co. | The Whole Block - power outages with GPO's and Lighting | Electrical | General Electrical | 225.02 | Fail | Fail | 0 | 0 | 2 | 2022-04-27 13:25 | 2022-04-27 15:25 | 2022-04-27 15:45 | 2022-04-27 17:25 | 2022-04-27 17:45 |  |  | Attended site and signed in, completed jsa,met with fm down in L block and walked around to each board to see what was going on, found that dB 2 had no power, went to db1 and identified breaker powering db2 , reset breaker and all power came back on, went back to L block and closed roller doors, completed paperwork,packed up, signed out , signature slip sent to jo for signingJob completed
MSA-DFES | WA5384198 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Staff dining room - hot water system is leaking underneath the sink | Plumbing & Drainage | HWS/Units Electric & Gas | 1405.47 | Fail | Fail | 4 | 4 | 2 | 2022-04-28 10:40 | 2022-04-29 17:00 | 2022-05-27 08:30 | 2022-04-29 17:00 | 2022-05-27 10:30 |  |  | Replaced hot water unit. All working correctly
MSA-DTWD | WA5384378 | 2 | AWB Co. | Roof Leaking | Roofing | Metal Roofing | 421.92 | Pass | Pass | 0 | 0 | 2 | 2022-04-28 12:21 | 2022-05-03 17:00 | 2022-05-03 06:45 | 2022-05-03 17:00 | 2022-05-03 08:45 |  |  | Leak to O block found box gutter joint needed re-sealing, sealed around windows above area of ingress, also noticed bottom rope screws were loose, replaced screws. Job complete
MSA-DFES | WA5384656 | 3 | AWB Co. | Main Admin - lower floor Male toilet - roof leaking through light fitting - see notes below | Roofing | Metal Roofing | 427.38 | Pass | Pass | 0 | 0 | 2 | 2022-04-28 14:40 | 2022-05-05 17:00 | 2022-05-05 12:45 | 2022-05-05 17:00 | 2022-05-05 14:45 |  |  | Attended, leak to male toilets, removed section of gutter mesh, re-sealed outlet and end cap, also sealed up screw holesto where mesh had been previously fixed. Connect light after next rain to once confirmed leak has stopped.
MSA-DTWD | WA5385256 | 2 | Precise Air Group | Vent - Faulty - fell out of the ceiling | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-04-29 08:43 | 2022-05-04 17:00 | 2022-05-03 10:00 | 2022-05-04 17:00 | 2022-05-03 12:00 |  |  | Attended site signed in and gained access to area. Found plastic holders holding the grill to the frame had deteriorated and cracked. Re secured tabs and grill with new screws
MSA-DCA | WA5385551 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant room level 3 - chilled water makeup pressure tank pinhole leak. Leaking into plantroom space | Equipment | Building Equipment | 450 | Pass | Pass | 0 | 0 | 2 | 2022-04-29 10:38 | 2022-05-02 17:00 | 2022-04-29 12:00 | 2022-05-02 17:00 | 2022-04-29 14:00 |  |  | Works carried out by Gerry. Investigated leak on expansion tank. Found leak and isolated water to the tank. Expansion tank to be replaced due to pinhole in body, will quote for replacement. Locked chilled water system to ets on the bms. Completed paperwork.
MSA-DTWD | WA5385636 | 2 | Techworks Plumbing | Male Toilet - Faulty Urinal - Continuously running | Plumbing & Drainage | Toilets/Cisterns | 228.05 | Pass | Pass | 0 | 0 | 2 | 2022-04-29 11:17 | 2022-05-04 17:00 | 2022-05-04 07:30 | 2022-05-04 17:00 | 2022-05-04 09:30 |  |  | Attended site at south metro tafe Signed in and spoke to one of the lecturers who showed me where the toilet was with the running urinalInspected urinal and found the flush valve was sticking and not closing all the way, probably needs a new flush washers also, the inlet valve was leaking and the push buttons on the urinal were broken.Came to conclusion it would be best just to replace the cistern as well to avoid future repairsSigned out and completed paperwork
MSA-DTWD | WA5392207 | 1 | Precise Air Group | T110 - aircon not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 2 | 2022-05-03 08:34 | 2022-05-04 17:00 | 2022-05-03 12:00 | 2022-05-04 17:00 | 2022-05-03 14:00 |  |  | Attended kendrew campus to sign in and receive keys. Traveled to mclarty campus and gained access to area. Found unit in fault. Investigated unit and found power to outdoor unit had been switch off. Tested and restored power and reset indoor controls. Allowed unit to run and carried out functional check to be sure unit was operational. Unit left in working order.
MSA-DTWD | WA5392225 | 2 | Techworks Electrical | C-Block room C205 has a flickering light | Electrical | Lighting, Internal | 292.57 | Pass | Pass | 0 | 0 | 2 | 2022-05-03 08:42 | 2022-05-06 17:00 | 2022-05-05 07:00 | 2022-05-06 17:00 | 2022-05-05 09:00 |  |  | Replaced various fluro tubes in block
MSA-DTWD | WA5392892 | 2 | Techworks Electrical | Lights not working in Q Block - see notes for rooms | Electrical | Lighting, Internal | 270.95 | Pass | Pass | 0 | 0 | 2 | 2022-05-03 13:16 | 2022-05-06 17:00 | 2022-05-05 07:00 | 2022-05-06 17:00 | 2022-05-05 09:00 |  |  | Replaced various lights in block
MSA-DFES | WA5393772 | 2 | SONTEC WA PTY LTD | Exit Boom Gate - isolate the control system - see notes below | Security | Access Control | 390 | Pass | Pass | 0 | 0 | 2 | 2022-05-04 10:14 | 2022-05-09 17:00 | 2022-05-06 09:45 | 2022-05-09 17:00 | 2022-05-06 11:45 |  |  | 6/5/22 - Dylan ParslowIdentified contacts and cables for boom exit relay.Advised door contractor.
MSA-DFES | WA5393803 | 1 | Seme Solutions Pty Ltd | Security Gate - is faulty and circuit breaker keeps tripping | Security | Access Control | 260 | Pass | Pass | 0 | 0 | 2 | 2022-05-04 10:19 | 2022-05-05 17:00 | 2022-05-04 11:30 | 2022-05-05 17:00 | 2022-05-04 13:30 |  |  | Job is complete3rd party electrician is required to repair the gate to resolve issue
MSA-DFES | WA5393846 | 3 | AWB Co. | Ground - Yard - Front door has sagged and is not closing properly. | Building | Doors | 212.5 | Pass | Pass | -1 | -1 | 2 | 2022-05-04 10:38 | 2022-05-11 17:00 | 2022-05-05 10:30 | 2022-05-11 17:00 | 2022-05-05 12:30 |  |  | adjusted front door
MSA-DTWD | WA5394138 | 3 | Falcetta Plumbing and Gas | Room A357d - Dripping tap | Plumbing & Drainage | Water | 248.84 | Pass | Pass | 0 | 0 | 2 | 2022-05-04 13:24 | 2022-05-11 17:00 | 2022-05-10 16:00 | 2022-05-11 17:00 | 2022-05-10 18:00 |  |  | repaired 4x taps
MSA-DCA | WA5394277 | 0 | Critical Fire Protection & Training | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Fire Protection Services | Fire Protection - Monitor System | 820.42 | Pass | Pass | 0 | 0 | 2 | 2022-04-19 16:00 | 2022-04-19 18:00 | 2022-04-19 16:00 | 2022-04-19 20:00 | 2022-04-19 18:00 | 1 |  | Jumper valve on hydrant valve collapsed, causing leak of water.
MSA-DTWD | WA5395078 | 1 | AWB Co. | Room G22 - Faulty GPO for clothes dryer | Electrical | General Electrical | 408.54 | Pass | Pass | 0 | 0 | 2 | 2022-05-05 10:39 | 2022-05-06 17:00 | 2022-05-06 09:00 | 2022-05-06 17:00 | 2022-05-06 11:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located PowerPoint. Found it was a 20A PowerPoint and plug, went to wholesaler for parts. Returned to site. Replaced plug and gpo. Labelled gpo. Completed paperwork. Took pictures. SIgned out.Job complete
MSA-DTWD | WA5399042 | 1 | Falcetta Plumbing and Gas | Creche Toilet blocked, draining very slowly. | Plumbing & Drainage | Toilets/Cisterns | 598.97 | Pass | Pass | 0 | 0 | 2 | 2022-05-09 14:18 | 2022-05-10 17:00 | 2022-05-10 10:00 | 2022-05-10 17:00 | 2022-05-10 12:00 |  |  | unblocked drain, roots in line w/ Drainsflush
MSA-DTWD | WA5400255 | 2 | Techworks Electrical | L1 massage bed far left hand corner, only goes up and not down | Electrical | General Electrical | 392.47 | Pass | Pass | 0 | 0 | 2 | 2022-05-10 08:57 | 2022-05-13 17:00 | 2022-05-13 07:00 | 2022-05-13 17:00 | 2022-05-13 09:00 |  |  | Found cable to be half pulled out from plug due to cable being stuck under feet
MSA-DTWD | WA5400867 | 2 | DCSWA Pty Ltd (Data Cabling Systems) | 4x data input plugs are broken | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2022-05-10 13:44 | 2022-05-13 17:00 | 2022-05-12 14:30 | 2022-05-13 17:00 | 2022-05-12 16:30 |  |  | Re installed data points on mounting blocks
MSA-DTAG | WA5407111 | 0 | Seme Solutions Pty Ltd | Family Violence Office - external door is not locking or shutting | Building | Security Doors | 130 | Pass | Pass | 0 | 0 | 2 | 2022-05-11 09:41 | 2022-05-11 11:41 | 2022-05-11 10:30 | 2022-05-11 13:41 | 2022-05-11 12:30 |  |  | Lock repaired
MSA-DTWD | WA5413098 | 3 | AWB Co. | N100 remove broken extraction fan in window mount | Equipment | Building Equipment | 168.75 | Pass | Pass | -1 | -1 | 2 | 2022-05-12 09:04 | 2022-05-19 17:00 | 2022-05-12 13:30 | 2022-05-19 17:00 | 2022-05-12 15:30 |  |  | Arrived on site and signed in security escorted me to the room I assess the job completed a JSA got my tools and return to the room remove the fan. Signed out
MSA-DFES | WA5413394 | 3 | Protek 24/7 Building & Maintenance | Main Admin - Roof - Near plant room in hallway - Water leaking through ceiling when raining | Roofing | Metal Roofing | 398.5 | Pass | Pass | 0 | 0 | 2 | 2022-05-12 10:44 | 2022-05-19 17:00 | 2022-05-17 07:00 | 2022-05-19 17:00 | 2022-05-17 09:00 |  |  | Repair water leak in ceiling
MSA-DTWD | WA5413864 | 2 | Protek 24/7 Building & Maintenance | Room G16 - Roof Leak | Roofing | Metal Roofing | 349 | Pass | Pass | -1 | -1 | 2 | 2022-05-12 14:24 | 2022-05-17 17:00 | 2022-05-13 12:00 | 2022-05-17 17:00 | 2022-05-13 14:00 |  |  | Repair roof leak Room G16
MSA-DTWD | WA5417225 | 1 | Protek 24/7 Building & Maintenance | Significant roof leak above customer service counter | Roofing | Metal Roofing | 349 | Pass | Pass | 0 | 0 | 2 | 2022-05-13 11:17 | 2022-05-16 17:00 | 2022-05-13 13:30 | 2022-05-16 17:00 | 2022-05-13 15:30 |  |  | Repair roof leak above customer service counter
MSA-DTWD | WA5437866 | 2 | AWB Co. | E201 Faulty Lights | Electrical | Lighting, Internal | 244.52 | Pass | Pass | 0 | 0 | 2 | 2022-05-16 10:45 | 2022-05-19 17:00 | 2022-05-16 12:00 | 2022-05-19 17:00 | 2022-05-16 14:00 |  |  | Attended site and signed in. Located room E201, found faulty lights in staff room. Supply and replace dead lamps with new lamps and starters. Check and tested all okay. Signed out. Job complete
MSA-DTWD | WA5437973 | 3 | AWB Co. | D1 - Circuit tripping on R1 to outside lighting | Electrical | General Electrical | 430.26 | Pass | Pass | 0 | 0 | 2 | 2022-05-16 11:53 | 2022-05-23 17:00 | 2022-05-20 13:00 | 2022-05-23 17:00 | 2022-05-20 15:00 |  |  | Attended site signed in jsa completed. located D block demountables and found fluro full of water outside the building. Disconnected and turn power on and problem solved. Sourced new light and replaced matching. Re routed cable entry as previous was leaking into fitting put this one on the side entry. Tested and all working fine. **** job completed ****
MSA-DTWD | WA5438139 | 2 | Techworks Electrical | Ladies toilets lights not working | Electrical | Lighting, Internal | 986.02 | Pass | Pass | 0 | 0 | 2 | 2022-05-16 12:44 | 2022-05-19 17:00 | 2022-05-18 10:00 | 2022-05-19 17:00 | 2022-05-18 12:00 |  |  | Replaced faulty lights with new led in toilets
MSA-DTWD | WA5451455 | 1 | Protek 24/7 Building & Maintenance | CG01 - Ceiling damage | Building | General Building | 808 | Pass | Pass | 0 | 0 | 2 | 2022-05-17 08:12 | 2022-05-18 17:00 | 2022-05-18 07:00 | 2022-05-18 17:00 | 2022-05-18 09:00 |  |  | Repair Ceiling Damage - CG01
MSA-DTWD | WA5454581 | 2 | Protek 24/7 Building & Maintenance | G Block - Roof - Air con service platform - panel missing from mechanical service platform on roof | Roofing | Metal Roofing | 349 | Pass | Pass | 0 | 0 | 2 | 2022-05-17 12:29 | 2022-05-20 17:00 | 2022-05-20 10:30 | 2022-05-20 17:00 | 2022-05-20 12:30 |  |  | Report/Record BRAF Declined
MSA-DTWD | WA5454701 | 2 | AWB Co. | D14 - Faulty light | Electrical | General Electrical | 436.29 | Pass | Pass | 0 | 0 | 2 | 2022-05-17 13:31 | 2022-05-20 17:00 | 2022-05-20 10:00 | 2022-05-20 17:00 | 2022-05-20 12:00 |  |  | Attended site signed in jsa completed. found faulty light in classroom as per mike’s info. both ballast blown and starters. sourced new led panel for classrom and replaced. All tested fine and ok *** job completed ***
MSA-DTWD | WA5459805 | 0 | AWB Co. | Room C26 - No power to the server room - UPS is failed | Electrical | General Electrical | 225.02 | Pass | Pass | 0 | 0 | 2 | 2022-05-18 08:56 | 2022-05-18 10:56 | 2022-05-18 10:30 | 2022-05-18 12:56 | 2022-05-18 12:30 |  |  | Daniel Hume (18/05/2022) - Work NoteAttended site and signed in. Completed JSA. Located UPS. Found the alarm was beeping and saying on the screen load output too high and internal temperature high. Isolated the batterys and the main feed. Reset the UPS and wait until told to reinstate batteries. It started up and showed odd voltages on the output. Then after a few seconds goes into bypass mode and beeps with a alarm. Says intialise UPS. Tried isolating the load off the UPS and with only some load. Neither will let the UPS work normally. Currently the server is running in bypass and isolated mode and the batteries are isolated. Will await to hear back on replace or repair costs and then return to site. Signed out. Job not completeBRAF declined - invoiced costs to date
MSA-DTWD | WA5461768 | 3 | Equans Mechanical Services Australia | 3F1 - Valve that operates exhaust for Mack engine not working | Air Conditioning | Room Air Conditioners | 227.77 | Pass | Pass | -1 | -1 | 2 | 2022-05-19 08:49 | 2022-05-26 17:00 | 2022-05-20 10:00 | 2022-05-26 17:00 | 2022-05-20 12:00 |  |  | Gear on back of handle has come off due to broken pin. Carried out repairs and checked operation. All ok
MSA-DTWD | WA5470557 | 3 | AWB Co. | E48 MaleToilets - Large Downlights not working | Electrical | Lighting, Internal | 630.76 | Pass | Pass | -1 | -1 | 2 | 2022-05-23 10:57 | 2022-05-30 17:00 | 2022-05-25 12:00 | 2022-05-30 17:00 | 2022-05-25 14:00 |  |  | Attended site signed in jsa completed. found faulty lights in male toilets. Sourced new led replacements same as next door. Replaced with new led 24w lights.All tested and works fine.*** job completed ***
MSA-DTWD | WA5470928 | 2 | Protek 24/7 Building & Maintenance | LG 05 - L Block creche outside door - Door jamming on entry and exit | Building | Doors | 376.5 | Fail | Fail | 0 | 0 | 2 | 2022-05-23 12:10 | 2022-05-26 17:00 | 2022-05-27 07:00 | 2022-05-26 17:00 | 2022-05-27 09:00 |  |  | Repair jamming door -LG 05 - L Block creche outside door
MSA-DFES | WA5472160 | 2 | Protek 24/7 Building & Maintenance | Workshop - Walkway near the cage - see details below | Building | General Building | 364.4 | Pass | Pass | 0 | 0 | 2 | 2022-05-23 14:40 | 2022-05-26 17:00 | 2022-05-26 07:30 | 2022-05-26 17:00 | 2022-05-26 09:30 |  |  | repair leaking roof
MSA-DTWD | WA5472584 | 2 | AWB Co. | Water leak down wall S106 Client Services | Roofing | Metal Roofing | 416.25 | Pass | Pass | 0 | 0 | 2 | 2022-05-24 09:02 | 2022-05-27 17:00 | 2022-05-27 07:00 | 2022-05-27 17:00 | 2022-05-27 09:00 |  |  | Attended and sealed under downpipe clips, fixings, wall cladding, unblocked apron flashing. Job complete
MSA-DTWD | WA5472722 | 1 | Protek 24/7 Building & Maintenance | G35 - Roof Leak | Roofing | Metal Roofing | 349 | Pass | Pass | 0 | 0 | 2 | 2022-05-24 09:56 | 2022-05-25 17:00 | 2022-05-25 07:00 | 2022-05-25 17:00 | 2022-05-25 09:00 |  |  | Repair roof leak to G35
MSA-DTWD | WA5472769 | 1 | BAKE-QUIP PTY LTD | : Kendrew- E-Block restaurant kitchen combi oven does not turn on opp white board | Equipment | Catering Equipment | 365 | Pass | Pass | 0 | 0 | 2 | 2022-05-24 10:26 | 2022-05-25 17:00 | 2022-05-25 12:00 | 2022-05-25 17:00 | 2022-05-25 14:00 |  |  | Refer to service report
MSA-DTWD | WA5472952 | 2 | Techworks Electrical | P-Block room P109 has a flickering light | Electrical | Lighting, Internal | 479.47 | Pass | Pass | 0 | 0 | 2 | 2022-05-24 11:54 | 2022-05-27 17:00 | 2022-05-27 10:00 | 2022-05-27 17:00 | 2022-05-27 12:00 |  |  | Replaced fluro tubes and starters in P block p109
MSA-DTAG | WA5475973 | 2 | EASTERN HILLS ELECTRICAL SERVICE | Custody - Control Room - light has blown | Electrical | General Electrical | 363.58 | Pass | Pass | -1 | -1 | 2 | 2022-05-25 09:34 | 2022-05-30 17:00 | 2022-05-26 09:00 | 2022-05-30 17:00 | 2022-05-26 11:00 |  |  | Replaced 2x lights in custody office with LEDs
MSA-DFES | WA5478309 | 3 | Protek 24/7 Building & Maintenance | Main Admin - Ground - First Aid Room - Sunken pavers outside entrance - potential trip hazard | Flooring | Concrete | 502 | Pass | Pass | 0 | 0 | 2 | 2022-05-26 10:52 | 2022-06-02 17:00 | 2022-06-02 07:00 | 2022-06-02 17:00 | 2022-06-02 09:00 |  |  | Repair sunken pavers outside entrance to Main admin
MSA-DFES | WA5478809 | 1 | Protek 24/7 Building & Maintenance | Roof- Gutters - water is over flowing | Building | General Building | 371 | Pass | Pass | 0 | 0 | 2 | 2022-05-26 13:53 | 2022-05-27 17:00 | 2022-05-27 07:30 | 2022-05-27 17:00 | 2022-05-27 09:30 |  |  | Repair leaking roof gutters
MSA-DFES | WA5481484 | 2 | Protek 24/7 Building & Maintenance | Ground - Gym outside area - Ceiling panel falling down | Building | Ceiling | 363.73 | Fail | Fail | 0 | 0 | 2 | 2022-05-30 13:36 | 2022-06-02 17:00 | 2022-06-03 07:00 | 2022-06-02 17:00 | 2022-06-03 09:00 |  |  | Refix ceiling panels
MSA-DTWD | WA5481624 | 2 | M Construction (WA) | C-Block - G Floor - Install white board back to the wall in room C010 | Building | Internal Walls | 367.58 | Pass | Pass | 0 | 0 | 2 | 2022-05-30 15:05 | 2022-06-02 17:00 | 2022-06-01 10:00 | 2022-06-02 17:00 | 2022-06-01 12:00 |  |  | Attended sit and install white boards as required.
MSA-DTWD | WA5487395 | 2 | AHS Services WA Pty Ltd (Anchor) | L1 110d - Tampering valve not working - further information | Plumbing & Drainage | Water | 482.64 | Pass | Pass | -1 | -1 | 2 | 2022-06-01 14:44 | 2022-06-07 17:00 | 2022-06-02 10:00 | 2022-06-07 17:00 | 2022-06-02 12:00 |  |  | Replaced old tempering valve nd adjusted necessary pipework.
MSA-DTWD | WA5488179 | 3 | AWB Co. | Expo A Block - Replace faulty Lamps in Expo A Block on Western Side- see notes below | Electrical | Lighting, Internal | 225.02 | Pass | Pass | 0 | 0 | 2 | 2022-06-02 11:07 | 2022-06-10 17:00 | 2022-06-09 07:00 | 2022-06-10 17:00 | 2022-06-09 09:00 |  |  | Submitting braf to completebraf declinedinvoice costs to date
MSA-DTWD | WA5490610 | 0 | Nessco Pressure Systems | Oil and Glass plant - Compressor has seized up | Equipment | Compressors, Generators |  | Fail | Fail | 1 | 1 | 2 | 2022-06-03 07:48 | 2022-06-03 09:48 | 2022-06-10 10:30 | 2022-06-03 11:48 | 2022-06-10 12:30 |  |  | install of head gasket and tested
MSA-DTWD | WA5490989 | 2 | ECO PLUMBING AND GAS PTY LTD | C003 - Hairdressing Basin Loose and won’t lock in position | Plumbing & Drainage | Materials | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-06-03 11:02 | 2022-06-09 17:00 | 2022-06-09 07:00 | 2022-06-09 17:00 | 2022-06-09 09:00 |  |  | Adjusted bolts to rectify
MSA-DTWD | WA5491328 | 3 | AWB Co. | North Block - N115 - REPAIR STAINLESS STEEL BENCHES | Building | General Building | 210 | Pass | Pass | -1 | -1 | 2 | 2022-06-03 14:19 | 2022-06-13 17:00 | 2022-06-09 11:30 | 2022-06-13 17:00 | 2022-06-09 13:30 |  |  | Arrived onsite Built stainless bench tables and cleaned work area to complete the jobJob complete
MSA-DTWD | WA5491333 | 3 | AWB Co. | North Block - N119 - repair stainless steel benches | Building | General Building | 210 | Pass | Pass | -1 | -1 | 2 | 2022-06-03 14:25 | 2022-06-13 17:00 | 2022-06-09 13:30 | 2022-06-13 17:00 | 2022-06-09 15:30 |  |  | Arrived onsite Removed as bench work tables and bolted them together.Remove all the laser film then cleaned work area to complete the jobJob completed
MSA-DCA | WA5494360 | 2 | Protek 24/7 Building & Maintenance | Level 5 - External Doors - Doors wedging shut very hard to open | Building | General Building | 364.19 | Fail | Fail | 1 | 1 | 2 | 2022-06-07 14:28 | 2022-06-10 17:00 | 2022-06-14 07:30 | 2022-06-10 17:00 | 2022-06-14 09:30 |  |  | Repair external doors - hard to open
MSA-DTWD | WA5494480 | 3 | AWB Co. | E107 - 2 X lights out | Electrical | Lighting, Internal | 225.02 | Pass | Pass | -1 | -1 | 2 | 2022-06-07 15:48 | 2022-06-14 17:00 | 2022-06-10 12:00 | 2022-06-14 17:00 | 2022-06-10 14:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located lighting in e block and set up work area, removed old tubes and found that tombstones were all broken, replaced tombstones, tubes and starters, light still wasn’t working, found that plug above fitting was loose, pushed plug in tight and light now works, packed up, cleaned up, put old tubes in allocated disposal bins provided on site, completed paperwork,signed out***job completed***
MSA-DFES | WA5494859 | 1 | WA BOILER SPARES & SERVICE | Applied training ground - tower 2 - air line is brittle and is cracked - leaking air | Plumbing & Drainage | Materials | 350 | Fail | Fail | 0 | 0 | 2 | 2022-06-08 07:39 | 2022-06-08 17:00 | 2022-06-09 07:30 | 2022-06-08 17:00 | 2022-06-09 09:30 |  |  | Isolated air supply, removed air pipe from cable tray and junction box, cut back air pipe past damaged area, remade air pipe connections, re-secured air pipe to cable tray and tested for soundness
MSA-DFES | WA5495221 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - East End Hallway - Light sensor for eastern end hallway is not working. | Electrical | General Electrical | 437.76 | Pass | Pass | -1 | -1 | 2 | 2022-06-08 10:20 | 2022-06-13 17:00 | 2022-06-09 13:45 | 2022-06-13 17:00 | 2022-06-09 15:45 |  |  | Arrived onsite at 13:45 to investigate hallway lights not working, found sensor for lighting to be faulty. Left site to collect new sensor from wholesaler in Welshpool. Arrived back on site, installed new sensor and tested all okay. Continued on site at 15:451 x Robus 360 degree sensor
MSA-DTWD | WA5495618 | 3 | Schindler Lifts Australia | North Block - Level 3 - Lift No 4 - Lift stuck - doors open | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 2 | 2022-06-08 13:33 | 2022-06-15 17:00 | 2022-06-08 14:30 | 2022-06-15 17:00 | 2022-06-08 16:30 |  |  | Lift keeps failing out of door zone intermittently, possible over bridging issue. Requires further investigation. Obr raised
MSA-DTWD | WA5496484 | 2 | AHS Services WA Pty Ltd (Anchor) | A147 - shower has little to no hot water please investigate | Plumbing & Drainage | HWS/Units Electric & Gas | 272.51 | Pass | Pass | 0 | 0 | 2 | 2022-06-09 10:31 | 2022-06-14 17:00 | 2022-06-14 11:30 | 2022-06-14 17:00 | 2022-06-14 13:30 |  |  | Unblocked tmv and replaced seized tapware
MSA-DTWD | WA5497034 | 2 | Equans Mechanical Services Australia | Upright freezer is faulty - Freezer isn't reaching required temp and is icing up | Refrigeration | Freezers | 204.07 | Pass | Pass | -1 | -1 | 2 | 2022-06-09 13:53 | 2022-06-14 17:00 | 2022-06-10 07:30 | 2022-06-14 17:00 | 2022-06-10 09:30 |  |  | CHECKED FREEZER, DEFROSTED HEATERS DOWN TO TEMPERATURE. ADJUSTED DOORS AS THERE WAS A GAP - OK
MSA-DTWD | WA5499918 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 373.4 | Fail | Fail | 0 | 0 | 2 | 2022-06-10 15:39 | 2022-06-13 17:00 | 2022-06-14 13:30 | 2022-06-13 17:00 | 2022-06-14 15:30 |  |  | Braf declined attend roof leak
MSA-DTWD | WA5499929 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 372.28 | Fail | Fail | 0 | 0 | 2 | 2022-06-10 15:51 | 2022-06-13 17:00 | 2022-06-14 07:30 | 2022-06-13 17:00 | 2022-06-14 09:30 |  |  | BRAF Declined
MSA-DTWD | WA5511758 | 1 | M Construction (WA) | water dripping from ceiling fan - See notes below | Building | Ceiling | 276.75 | Pass | Pass | 0 | 0 | 2 | 2022-06-13 08:38 | 2022-06-14 17:00 | 2022-06-13 10:00 | 2022-06-14 17:00 | 2022-06-13 12:00 |  |  | Attended site to investigate water dripping ceiling fan, resealed skylight, cleaned skylight diffuser, re-sealed broken dektite.
MSA-DCA | WA5511783 | 0 | Kone Elevators Pty Ltd | Level 1 - Lift 5 - Core button have come off wall - hanging off | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2 | 2022-06-13 09:02 | 2022-06-13 11:02 | 2022-06-13 09:45 | 2022-06-13 13:02 | 2022-06-13 11:45 |  |  | Repairs to lift
MSA-DTAG | WA5511832 | 3 | Automatic Fire Protection (ARA) | Building 1903 - Ground Floor - Staff Corridor - Issues with magnetic fire door - See notes below | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 240.58 | Fail | Fail | 0 | 0 | 2 | 2022-06-13 09:39 | 2022-06-20 17:00 | 2022-06-21 07:00 | 2022-06-20 17:00 | 2022-06-21 09:00 |  |  | Attended site and found door holders removed from mountings and un wired.Re wired in and re mounted to walks and tested ok.Left doors normal
MSA-DCA | WA5513628 | 1 | Automatic Fire Protection (ARA) | Ground Floor - Rear of Kitchen lift - Faulty fire door, damaged when repairing kitchen lift | Building | Fire Door | 540.58 | Pass | Pass | 0 | 0 | 2 | 2022-06-14 11:56 | 2022-06-15 17:00 | 2022-06-15 10:00 | 2022-06-15 17:00 | 2022-06-15 12:00 |  |  | Replaced Lift Motor Room Fire Door Mortice and Barrel Set
MSA-DTWD | WA5513784 | 1 | AWB Co. | Ground Level - Entry - Outside senor lights breaker in distribution board won’t reset - see notes | Electrical | Distribution Board | 225.02 | Pass | Pass | 0 | 0 | 2 | 2022-06-14 13:09 | 2022-06-15 17:00 | 2022-06-15 12:00 | 2022-06-15 17:00 | 2022-06-15 14:00 |  |  | Attended site signed in jsa completed. Security lights breaker tripped wont reset, disconnected all lights to split circuit. Found two lights not on. Looked above light and found junction with water in it. Re sealed and moved to different spot. All working now*** job completed ***
MSA-DCA | WA5522328 | 0 | Techworks Electrical | Puccini Room - flickering lights | Electrical | Lighting, Internal | 253.26 | Pass | Pass | 0 | 0 | 2 | 2022-06-15 14:15 | 2022-06-15 16:15 | 2022-06-15 14:30 | 2022-06-15 18:15 | 2022-06-15 16:30 |  |  | Attended site and job, isolated supply to lights, made safe.
MSA-DTWD | WA5548769 | 3 | Securex Security Systems & Services | Security Alarm panel and sensor not working | Security | Monitoring | 462.73 | Pass | Pass | 0 | 0 | 2 | 2022-06-17 09:31 | 2022-06-24 17:00 | 2022-06-23 09:45 | 2022-06-24 17:00 | 2022-06-23 11:45 |  |  | 23/06/2022, 945-1145Installed new motion sensor to existing cable.Powered up system in Block C. RAS on area 6 working.Armed/Disarmed area 6.
MSA-DTWD | WA5549090 | 3 | Falcetta Plumbing and Gas | Passageway - Blocked drain on non-chilled water dispencer | Plumbing & Drainage | Drainage | 283.97 | Pass | Pass | 0 | 0 | 2 | 2022-06-17 12:46 | 2022-06-24 17:00 | 2022-06-24 14:30 | 2022-06-24 17:00 | 2022-06-24 16:30 |  |  | replaced drain with larger diameter
MSA-DCA | WA5549211 | 2 | FCT SURFACE CLEANING | Main Building - Ground Floor - Gantry - External Graffiti | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-06-17 14:34 | 2022-06-22 17:00 | 2022-06-21 10:00 | 2022-06-22 17:00 | 2022-06-21 12:00 |  |  | Graffiti
MSA-DTWD | WA5549256 | 3 | AWB Co. | Lift lobby - blown fluoro's & globes - | Electrical | General Electrical | 311.42 | Pass | Pass | 0 | 0 | 2 | 2022-06-17 15:33 | 2022-06-24 17:00 | 2022-06-21 10:00 | 2022-06-24 17:00 | 2022-06-21 12:00 |  |  | Attended site signed in Jsa completed. Spoke to Dave Gaff from facilities about jobs needed to be completed. Received lighting list for B2 and replaced 16 28w tubes in various sections of the building.**** job completed ****
MSA-DCA | WA5562944 | 3 | Techworks Electrical | Basement - Female Toilets in Corridor - Lights in the ladies bathroom in the corridor are flickering | Electrical | General Electrical | 740.32 | Pass | Pass | 0 | 0 | 2 | 2022-06-20 10:54 | 2022-06-27 17:00 | 2022-06-27 09:00 | 2022-06-27 17:00 | 2022-06-27 11:00 |  | WACCES | Replaced flickering lights with new LEDs in basement corridor female toilets.
MSA-DTWD | WA5563204 | 1 | JEM Carpentry | BLD 820 - Level 1 - Foyer - Leaking roof | Building | General Building |  | Pass | Pass | 0 | 0 | 2 | 2022-06-20 12:49 | 2022-06-21 17:00 | 2022-06-20 13:00 | 2022-06-21 17:00 | 2022-06-20 15:00 |  |  | Repair to roof tiles
MSA-DTWD | WA5564219 | 2 | Damian Rak Electrical Pty Ltd | BLD 831 - Hall - Faulty light | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2022-06-21 09:04 | 2022-06-24 17:00 | 2022-06-21 13:00 | 2022-06-24 17:00 | 2022-06-21 15:00 |  |  | Repairs to lights
MSA-DTWD | WA5565882 | 3 | AWB Co. | 16 sets of two fluorescent globes to be replaced / inset into ceiling - See notes below | Electrical | Lighting, Internal | 432.65 | Pass | Pass | 0 | 0 | 2 | 2022-06-22 12:16 | 2022-06-29 17:00 | 2022-06-27 09:00 | 2022-06-29 17:00 | 2022-06-27 11:00 |  |  | Attended site and signed in. Completed JSA. Located D block and went through and counted up lights out. Supply and replace tubes to fittings and required. 1 x fitting was faulty supply and replaced the fitting with new led panel. Tested all okay. Signed out. Job complete
MSA-DFES | WA5566736 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilet - Shower head dripping - See notes below | Plumbing & Drainage | Water | 238.65 | Pass | Pass | -1 | -1 | 2 | 2022-06-23 10:54 | 2022-06-28 17:00 | 2022-06-24 07:45 | 2022-06-28 17:00 | 2022-06-24 09:45 |  |  | Attended site showerhead dripping in the mail change room on inspection I found the taps need to be serviced I have replaced all the washes and tap washer I’ve taken the spindle extensions out and replace the washer there on both hot and cold I’ve cleaned up the face of the breach I’ve also cleaned out the tap spindle itself as there was a lot of grime and dirt after I reinstalled everything it is now working correctly i’ve also cleaned up the showerhead as there was calcium buildup inside but informed site cleaned up packed up
MSA-DTWD | WA5567797 | 2 | Protek 24/7 Building & Maintenance | Roof leak- possible blocked guttering | Roofing | Metal Roofing | 377.6 | Pass | Pass | 0 | 0 | 2 | 2022-06-24 12:31 | 2022-06-29 17:00 | 2022-06-29 10:00 | 2022-06-29 17:00 | 2022-06-29 12:00 |  |  | Repair Apron Flashing that had come away from wall
MSA-DTWD | WA5570398 | 3 | AWB Co. | External - West Wall - 2 x lights out | Electrical | Lighting, External | 296.72 | Pass | Pass | 0 | 0 | 2 | 2022-06-28 10:43 | 2022-07-05 17:00 | 2022-07-05 09:00 | 2022-07-05 17:00 | 2022-07-05 11:00 |  |  | Attended site and signed in. Completed JSA. Located all lights not working on H block. Found 1mon side on west and 2 at the entry walkway. Supplied and replaced lamp to west side and 2 at entry, supply and replaced new fitting at door controlled by switch. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5571065 | 2 | PPM Project Painting & Maintenance | Front of building - Graffiti Out the front on flag post / bike rack and back wall | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 2 | 2022-06-29 08:12 | 2022-07-04 17:00 | 2022-07-05 10:00 | 2022-07-04 17:00 | 2022-07-05 12:00 |  |  | Job is completed - Graffiti removed from flag post, Bike rack and back wall
MSA-DTWD | WA5571246 | 2 | M Construction (WA) | 8 Brochure holders need re - fixing to the wall | Building | Internal Walls | 239.03 | Pass | Pass | 0 | 0 | 2 | 2022-06-29 09:58 | 2022-07-04 17:00 | 2022-07-01 07:00 | 2022-07-04 17:00 | 2022-07-01 09:00 |  |  | Attended site to refix brochure holders to D block wall, installed brochure holders onto the wall using wall anchors.
MSA-DCA | WA5572857 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Lift 7 - Broken down again - Displaying out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 2 | 2022-06-30 11:39 | 2022-07-01 17:00 | 2022-06-30 13:45 | 2022-07-01 17:00 | 2022-06-30 15:45 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped bottom floor, doors open and perfect floor level. TTELap on display. Reset controller with inspection switch and lift did not fault.Replaced the 12volt battery in the controller that is connected to the KD20 board. Replaced plug in relays K5,K6 and K7 on the Lisa 10-10 board. Adjusted oil heaterthermostat for higher temperature. Monitored oil pressure sensor while the lift was running. Unable to reproduce the fault while onsite. Left lift in service
MSA-DTWD | WA5584620 | 1 | ECO PLUMBING AND GAS PTY LTD | 2 x toilets are not flushing - see notes below | Plumbing & Drainage | Toilets/Cisterns | 240.7 | Pass | Pass | 0 | 0 | 2 | 2022-07-05 09:16 | 2022-07-06 17:00 | 2022-07-06 07:00 | 2022-07-06 17:00 | 2022-07-06 09:00 |  |  | Cleaned and flushed through water lines to cistern
MSA-DTWD | WA5584762 | 3 | GRAFFITI FORCE PTY LTD | Car park-Graffiti on walls | Building | External Walls | 392 | Pass | Pass | -1 | -1 | 2 | 2022-07-05 10:16 | 2022-07-12 17:00 | 2022-07-08 10:30 | 2022-07-12 17:00 | 2022-07-08 12:30 |  |  | REMOVAL OF GRAFFITI FROM CARPARK WALLS BUILDING 2
MSA-DTAG | WA5588301 | 2 | Sapio Pty Ltd | Entrance desk ( Fish bowl ) - PA System is currently not working - See notes bellow | ICT/Audiovisual | General AV works | 269 | Pass | Pass | -1 | -1 | 2 | 2022-07-07 14:22 | 2022-07-12 17:00 | 2022-07-08 08:30 | 2022-07-12 17:00 | 2022-07-08 10:30 |  |  | Attended site. PA sound low. Unable to increase volume. Found new PA console incompatible with old PA soundswitcher. New A4480 Redback Audio Switcher required.Job completed. Works will be completed under WA5566659.
MSA-DTWD | WA5589542 | 3 | AWB Co. | repaired roof leak still leaking | Roofing | Metal Roofing | 460.25 | Pass | Pass | -1 | -1 | 2 | 2022-07-08 14:06 | 2022-07-15 17:00 | 2022-07-11 10:00 | 2022-07-15 17:00 | 2022-07-11 12:00 |  |  | Investigated leak - found rust holes in sheets. Flashing joins unsealed. Cleaned back area and sealed over rust holes and flashing joints
MSA-DFES | WA5596759 | 2 | AWB Co. | Level 1 - Kitchen - Kitchen cupboard faulty - See notes below | Building | General Building | 990 | Fail | Fail | 2 | 2 | 2 | 2022-07-11 10:19 | 2022-07-14 17:00 | 2022-07-25 09:00 | 2022-07-14 17:00 | 2022-07-25 11:00 |  |  | Supply and fit corner cabinet onto door
MSA-DTWD | WA5603320 | 2 | Damian Rak Electrical Pty Ltd | Kitchen -Faulty power point | Electrical | General Electrical |  | Fail | Fail | 1 | 1 | 2 | 2022-07-12 09:43 | 2022-07-15 17:00 | 2022-07-19 13:30 | 2022-07-15 17:00 | 2022-07-19 15:30 |  |  | Completed
MSA-DTWD | WA5603653 | 1 | Protek 24/7 Building & Maintenance | 8G32 - Windows won’t close - See notes below | Building | Windows | 207.64 | Pass | Pass | 0 | 0 | 2 | 2022-07-12 11:53 | 2022-07-13 17:00 | 2022-07-12 12:00 | 2022-07-13 17:00 | 2022-07-12 14:00 |  |  | no action required
MSA-DFES | WA5604109 | 3 | Australian HVAC Services Pty. Ltd. | Engine room, change room 5-Exhaust fan not working properly-see notes | Air Conditioning | Room Air Conditioners | 246.92 | Pass | Pass | 0 | 0 | 2 | 2022-07-12 16:29 | 2022-07-19 17:00 | 2022-07-18 10:00 | 2022-07-19 17:00 | 2022-07-18 12:00 |  |  | Paul Veurink (18/07/2022) - Work NoteTravelled to site. Signed in. Spoke with Amanda. Went to plant room that contains the MSSB. Checked the fan switch and run/fault lights. No fault showing. Checked amps. Good amp readings. 2.0/1.9/2.1.Setup ladder and went to roof. Checked fan. It's running, good airflow. Opened fan. Belts are in good condition.Checked both motors running. They are. Went to reception, got Amanda to check change room 5 (female) is empty and attached 'out of service' sign to door. Checked airflow at grills. They're good. Brushed grills as they're a little dirty. Packed up.Went to reception. Let the staff there know that there was no issue. Got signature slip signed. Wrote report. Left site.
MSA-DTWD | WA5609410 | 3 | Building Automation & Electrical Services Pty Ltd | Room temp 25.8 SA 33.5 VAV. open 100% | Building | General Building |  | Pass | Pass | 0 | 0 | 2 | 2022-07-13 14:55 | 2022-07-20 17:00 | 2022-07-20 10:00 | 2022-07-20 17:00 | 2022-07-20 12:00 |  |  | Completed
MSA-DTWD | WA5609638 | 3 | Protek 24/7 Building & Maintenance | Floor damaged near sink | Flooring | Vinyl | 235.14 | Pass | Pass | -1 | -1 | 2 | 2022-07-13 15:31 | 2022-07-20 17:00 | 2022-07-15 10:30 | 2022-07-20 17:00 | 2022-07-15 12:30 |  |  | replace damaged Lino
MSA-DFES | WA5613695 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Driveway - Drains at front entrance flood when rains heavily | Plumbing & Drainage | Drainage | 486.66 | Pass | Pass | 0 | 0 | 2 | 2022-07-14 15:24 | 2022-07-19 17:00 | 2022-07-19 12:00 | 2022-07-19 17:00 | 2022-07-19 14:00 |  | WACCES | Attend site with pump and pump out car park drain in entry to academy
MSA-DCA | WA5627985 | 1 | Protek 24/7 Building & Maintenance | First Floor (top of stairs) Dutch Wrecks Gallery - Leak over cannon | Building | Ceiling | 390.16 | Pass | Pass | 0 | 0 | 2 | 2022-07-15 09:58 | 2022-07-18 17:00 | 2022-07-15 11:30 | 2022-07-18 17:00 | 2022-07-15 13:30 |  |  | sealed Gaps on roof causing leaking onto Cannon
MSA-DTWD | WA5660435 | 2 | LIGHTHOUSE LOCKSMITHS | workshops exit door south end and classroom door locks sticky difficult to unlock | Security | Locksmith | 470 | Pass | Pass | 0 | 0 | 2 | 2022-07-19 09:46 | 2022-07-22 17:00 | 2022-07-20 10:50 | 2022-07-22 17:00 | 2022-07-20 12:50 |  |  | Replaced side fixing screws in class rooms 1 and 2 and adjusted strike on class room 9, replaced damaged mortice lock on main exit door
MSA-DTWD | WA5672871 | 3 | AHS Services WA Pty Ltd (Anchor) | Female Toilet - Hand basin is leaking | Plumbing & Drainage | Water | 266.26 | Pass | Pass | -1 | -1 | 2 | 2022-07-20 10:01 | 2022-07-27 17:00 | 2022-07-21 10:45 | 2022-07-27 17:00 | 2022-07-21 12:45 |  |  | Replaced leaking plug and waste and okd pipework underneath. Trip to supplier required.
MSA-DCA | WA5673088 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis Street - Basement Server Room - BMS Alarms for FCU not communicating to BMS | Building | General Building | 478.19 | Fail | Fail | 1 | 1 | 2 | 2022-07-20 12:08 | 2022-07-21 17:00 | 2022-07-29 13:00 | 2022-07-21 17:00 | 2022-07-29 15:00 |  |  | Engaged Honeywell to attend site to investigate BMS alarms for FCU. Found IPC controller offline. Located switchboard and reset controller and downloaded binaries. Checked communication and found ok.
MSA-DTWD | WA5673181 | 2 | Lane's Plumbing | Garage - Gutter and downpipe faulty | Roofing | Guttering |  | Pass | Pass | -1 | -1 | 2 | 2022-07-20 12:52 | 2022-07-25 17:00 | 2022-07-20 13:00 | 2022-07-25 17:00 | 2022-07-20 15:00 |  |  | Job completed - REATTACH GUTTER AND DOWNPIPE TO GARAGE HOUSE 16
MSA-DTWD | WA5673218 | 2 | AHS Services WA Pty Ltd (Anchor) | Tap running in Female Toilet B Block Level 2 | Plumbing & Drainage | Toilets/Cisterns | 287.59 | Pass | Pass | -1 | -1 | 2 | 2022-07-20 13:12 | 2022-07-25 17:00 | 2022-07-21 13:00 | 2022-07-25 17:00 | 2022-07-21 15:00 |  |  | Replaced tap set in bathroom.
MSA-DTWD | WA5674033 | 1 | AWB Co. | roof leak x 3 different locations - see notes | Building | Internal Walls | 436.79 | Pass | Pass | 0 | 0 | 2 | 2022-07-21 08:37 | 2022-07-22 17:00 | 2022-07-22 07:00 | 2022-07-22 17:00 | 2022-07-22 09:00 |  |  | Cleaned roof sheet laps, sealed above box gutter out let, replaced teks.
MSA-DTWD | WA5674137 | 1 | AWB Co. | roof leak - leaking in center of room onto electrical bench | Building | Ceiling | 421.69 | Pass | Pass | 0 | 0 | 2 | 2022-07-21 09:17 | 2022-07-22 17:00 | 2022-07-22 09:00 | 2022-07-22 17:00 | 2022-07-22 11:00 |  |  | Attended, box gutter up stand to high causing flexible window flashing allow water ingress trimms box gutter and sealedjoint on flexible top flashing.
MSA-DTWD | WA5674200 | 2 | Protek 24/7 Building & Maintenance | F47-Roof leak in center of classroom | Roofing | Metal Roofing | 422.28 | Pass | Pass | 0 | 0 | 2 | 2022-07-21 09:33 | 2022-07-26 17:00 | 2022-07-26 09:00 | 2022-07-26 17:00 | 2022-07-26 11:00 |  |  | Repaired roof leak
MSA-DTWD | WA5674305 | 1 | SENTINEL LOCK SERVICE PTY LTD | C20 Customer Service Centre - Faulty Keypad Lock on External door | Security | Locksmith | 545.1 | Pass | Pass | 0 | 0 | 2 | 2022-07-21 10:27 | 2022-07-22 17:00 | 2022-07-21 12:00 | 2022-07-22 17:00 | 2022-07-21 14:00 |  |  | C20 - Customer service centre - faulty keypad lock - external door.Deadlock replaced on keypad lock.
MSA-DTWD | WA5674548 | 2 | Protek 24/7 Building & Maintenance | Roof leak along northern side of room near windows - Possible roof flashing | Roofing | Metal Roofing | 403.53 | Pass | Pass | 0 | 0 | 2 | 2022-07-21 12:29 | 2022-07-26 17:00 | 2022-07-26 07:00 | 2022-07-26 17:00 | 2022-07-26 09:00 |  |  | Gap sealing between flashing with Silicone
MSA-DTWD | WA5674724 | 3 | Falcetta Plumbing and Gas | Heavy Plant - Bad smell coming from drink fountain drain in Heavy Plant entrance | Plumbing & Drainage | Water | 228.97 | Pass | Pass | 0 | 0 | 2 | 2022-07-21 13:38 | 2022-07-28 17:00 | 2022-07-27 16:30 | 2022-07-28 17:00 | 2022-07-27 18:30 |  |  | unblocked tundish
MSA-MRWA | WA5675259 | 1 | LYNX INTEGRATED SYSTEMS | intermittent faults on lighting - progrramming issue | Electrical | Lighting, Internal | 317.5 | Pass | Pass | 0 | 0 | 2 | 2022-07-22 09:10 | 2022-07-25 17:00 | 2022-07-25 13:30 | 2022-07-25 17:00 | 2022-07-25 15:30 |  |  | Upon investigation found that existing lights have been moved by client to other areas, causing programming conflicts.L2 Open Area - Light addresses have been unravelled and are working with the exception of 2 x lights west end with new drivers. However, fault is with the light fittings not the drivers. Requires investigation / rectification by electrician.L2 NW Office 2.58 - unravelled, regrouped and tested as the fittings were removed from an existing group on another line.
MSA-DTWD | WA5675343 | 2 | Techworks Electrical | Sk2 right hand side has a Fluro light not working | Electrical | Lighting, Internal | 279.6 | Pass | Pass | 0 | 0 | 2 | 2022-07-22 09:57 | 2022-07-27 17:00 | 2022-07-25 07:00 | 2022-07-27 17:00 | 2022-07-25 09:00 |  |  | Replaced fluro tubes in SK2 E block
MSA-DTAG | WA5677050 | 2 | AHS Services WA Pty Ltd (Anchor) | Caffissimo Café-back kitchen area - Leak from water pipe under the sink | Plumbing & Drainage | Water | 1087.58 | Pass | Pass | 0 | 0 | 2 | 2022-07-25 12:17 | 2022-07-28 17:00 | 2022-07-27 07:00 | 2022-07-28 17:00 | 2022-07-27 09:00 |  |  | Replaced split hot water unit
MSA-DFES | WA5677160 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Moian Block - station officers - bathroom - toilet will not flush | Plumbing & Drainage | Water | 280.77 | Pass | Pass | 0 | 0 | 2 | 2022-07-25 12:56 | 2022-07-26 17:00 | 2022-07-25 16:00 | 2022-07-26 17:00 | 2022-07-25 18:00 |  |  | Clear blockage from IO located station officers toilet. Run machine down IS located at rear of yard.
MSA-DTWD | WA5677286 | 1 | Damian Rak Electrical Pty Ltd | BLD 875 - Piggery pen - Faulty control box - See notes below | Electrical | General Electrical |  | Fail | Fail | 1 | 1 | 2 | 2022-07-25 13:44 | 2022-07-26 17:00 | 2022-07-30 14:30 | 2022-07-26 17:00 | 2022-07-30 16:30 |  |  | Completed
MSA-DCA | WA5677921 | 0 | Techworks Plumbing | Ground Floor - Jubille Building - UAT Toilet - Blocked | Plumbing & Drainage | Toilets/Cisterns | 539.02 | Fail | Fail | 0 | 0 | 2 | 2022-07-26 08:29 | 2022-07-26 10:29 | 2022-07-26 10:30 | 2022-07-26 12:29 | 2022-07-26 12:30 |  |  | Attended sight signed in at security, got a pass to plumbing ducts, on arrival the toilets where blocking up further down the line, opened clean outs to find drain blocked and full so put my rods down to clear it took some time but freed the blockage, ran heaps of water down to clean as much of the drain I could, put the camera down to see if anything is done wrong could see the drain holding water I’d assume it’s back falling within 8m of the back of the toilets. Drains are cleared and running, signed out completed paperwork
MSA-DTWD | WA5679070 | 2 | Lane's Plumbing | Flat C - Bathroom - Faulty hot water taps | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-07-26 10:30 | 2022-07-29 17:00 | 2022-07-27 10:30 | 2022-07-29 17:00 | 2022-07-27 12:30 |  |  | job completed - REPAIR HOT TAPS TO FLAT C ANDCHECKAND REPAIR OTHER FI.ATSBATHROOMS HUGHES HALL
MSA-DTWD | WA5679451 | 1 | Protek 24/7 Building & Maintenance | AT3 - Roof Leak - Daylight visible trough Ceiling | Roofing | Metal Roofing | 421.78 | Pass | Pass | 0 | 0 | 2 | 2022-07-26 13:56 | 2022-07-27 17:00 | 2022-07-27 08:30 | 2022-07-27 17:00 | 2022-07-27 10:30 |  |  | Repair Roof leak
MSA-MRWA | WA5679613 | 3 | TASC Digital Control Systems WA | Carpark 2 Camera out | Security | CCTV Surveillance | 380 | Pass | Pass | -1 | -1 | 2 | 2022-07-26 15:49 | 2022-08-02 17:00 | 2022-07-29 09:15 | 2022-08-02 17:00 | 2022-07-29 11:15 |  |  | Vendor attended 29/07
MSA-DTWD | WA5679982 | 1 | Protek 24/7 Building & Maintenance | Roof is leaking in corner of room near alarm sensor | Roofing | Metal Roofing | 406.35 | Pass | Pass | 0 | 0 | 2 | 2022-07-27 08:48 | 2022-07-28 17:00 | 2022-07-28 09:45 | 2022-07-28 17:00 | 2022-07-28 11:45 |  |  | Gutter flashing cut, sealed it up to make it water tight
MSA-DFES | WA5680065 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | L19-Middle Dorm Shower: Broken shower head bracket. | Plumbing & Drainage | Water | 421.87 | Fail | Fail | 1 | 1 | 2 | 2022-07-27 09:26 | 2022-08-01 17:00 | 2022-08-09 12:45 | 2022-08-01 17:00 | 2022-08-09 14:45 |  |  | Attend site to check out broken shower head. On arrival found shower rail system in middle dorm to be broken and not useable. Removed old broken shower rail and hose, picked up materials from supplier and return to site, drilled new mounting holes in wall and mounted new shower rail. Tested and checked all working correctly. Cleaned up, packed up
MSA-DCA | WA5681096 | 1 | Techworks Electrical | C&K Cool Room - Cool Room LED strip broken. Barely any light in cool room for kitchen staff | Electrical | Lighting, Internal | 336.46 | Pass | Pass | 0 | 0 | 2 | 2022-07-28 08:59 | 2022-07-29 17:00 | 2022-07-28 13:30 | 2022-07-29 17:00 | 2022-07-28 15:30 |  |  | Replaved light fitting with new LED fitting and all working well
MSA-DTWD | WA5681155 | 3 | Precise Air Group | Replace Remote from Aircon in room S121 | Air Conditioning | Room Air Conditioners | 366 | Pass | Pass | 0 | 0 | 2 | 2022-07-28 09:34 | 2022-08-04 17:00 | 2022-08-01 13:00 | 2022-08-04 17:00 | 2022-08-01 15:00 |  |  | Attended site and reprogrammed controls
MSA-DTWD | WA5681307 | 1 | BAKE-QUIP PTY LTD | Dishwasher making bad noise on operation | Equipment | Cleaning Equipment | 360 | Fail | Fail | 1 | 1 | 2 | 2022-07-28 11:09 | 2022-07-29 17:00 | 2022-08-03 11:30 | 2022-07-29 17:00 | 2022-08-03 13:30 |  |  | Refer to service report
MSA-DTWD | WA5682752 | 1 | Techworks Plumbing | Garden Tap is Faulty | Plumbing & Drainage | Water | 438.64 | Pass | Pass | 0 | 0 | 2 | 2022-07-29 11:36 | 2022-08-01 17:00 | 2022-08-01 10:00 | 2022-08-01 17:00 | 2022-08-01 12:00 |  |  | attended site and signed in at office.facilities manager showed us where the faulty tap was we tried isolating water for garden tap but the tap was siezed in the ground so we could not isolate it.we spoke to facilities manager to see if there was another isolation valve anywhere, we had a look around for another valve but could not find one after checking plans and searching, we just decided to do it live we took the tap spindle out and replaced it with a new one from van stock then signed out for a signature slip and left sitecompleted paperwork
MSA-DTAG | WA5683034 | 2 | PPM Project Painting & Maintenance | Between Court rooms 2 & 3 waiting area 2. Flag pole & bike rack out the front- graffiti - see notes | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 2 | 2022-07-29 14:55 | 2022-08-03 17:00 | 2022-08-04 09:00 | 2022-08-03 17:00 | 2022-08-04 11:00 |  |  | Job is completed - Graffiti was removed from the below area:1 Graffiti scratched into paintwork & and wall protection has been burnt with a lighter between courtrooms 2&3 2 Graffiti on flag pole and bike rack out the front of the building
MSA-DTAG | WA5687026 | 0 | Midolo Building Services | Level 1 - Youth Justice - Water Leaks - See notes below | Roofing | Metal Roofing | 245.31 | Pass | Pass | 0 | 0 | 2 | 2022-08-01 12:44 | 2022-08-01 14:44 | 2022-08-01 13:45 | 2022-08-01 16:44 | 2022-08-01 15:45 |  | WCAPPR | closing costs to date - unable to locate leaks and with no rain makes it harder, Iain has advised to close with ctd. See email attached,
MSA-DCA | WA5688125 | 2 | Techworks Electrical | 3 x faulty lights in urban orchard. see notes - photo's to be emailed | Electrical | Lighting, External | 437.59 | Pass | Pass | 0 | 0 | 2 | 2022-08-02 09:56 | 2022-08-05 17:00 | 2022-08-04 13:30 | 2022-08-05 17:00 | 2022-08-04 15:30 |  |  | Attended site and inspected polelights. One light had no top hat and had been made safe on another work order while the light has been ordered for replacement. Another light had been recently vandalised and the cable was hanging out. Retrieve the light from the cleaners store and installed. Fixed light to pole with screws to prevent further vandalism.
MSA-DTWD | WA5689713 | 1 | AWB Co. | Check electrical lighting circuit after roof leak repair. - see notes | Electrical | Lighting, Internal | 389.04 | Pass | Pass | 0 | 0 | 2 | 2022-08-02 13:13 | 2022-08-03 17:00 | 2022-08-03 12:00 | 2022-08-03 17:00 | 2022-08-03 14:00 |  |  | Attended site signed in jsa completed. Roof leak had been in classroom and tripped lights in lecture room. disconnected lights and found one light full of water. isolated cables from fitting and put in junction box and made safe. Job closed off will raise another once leak is fixed in 2 monthsJob completed
MSA-DTWD | WA5689915 | 2 | AWB Co. | Roof leaks above S106 flat roof | Roofing | Metal Roofing | 498 | Pass | Pass | 0 | 0 | 2 | 2022-08-02 15:16 | 2022-08-05 17:00 | 2022-08-04 07:30 | 2022-08-05 17:00 | 2022-08-04 09:30 |  |  | Stripped multiple sheets to find water ingress.Cleaned out box gutters.Changed roof screw in area that had perished seals on sheets .Removed silicone on ridging that was preventing water flow.Sealed splits on sheets.Staining to roof tile evident.
MSA-DTAG | WA5691685 | 0 | Elec Power Technologies | L6 server room-Check server supply due to power surge | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2022-08-03 07:10 | 2022-08-03 09:10 | 2022-08-03 09:00 | 2022-08-03 11:10 | 2022-08-03 11:00 |  |  | Priority 0 - L6 Server Room, Check server supply due to power surge
MSA-DTWD | WA5691862 | 1 | BAKE-QUIP PTY LTD | D32 Kitchen - Oven at back of kitchen has tripped | Equipment | Catering Equipment | 374.8 | Pass | Pass | 0 | 0 | 2 | 2022-08-03 08:34 | 2022-08-04 17:00 | 2022-08-03 09:00 | 2022-08-04 17:00 | 2022-08-03 11:00 |  |  | Refer to service report
MSA-DTWD | WA5692182 | 2 | Protek 24/7 Building & Maintenance | Water leak beside central A/C duct | Building | Internal Walls | 357.16 | Fail | Fail | 1 | 1 | 2 | 2022-08-03 11:10 | 2022-08-08 17:00 | 2022-08-15 10:00 | 2022-08-08 17:00 | 2022-08-15 12:00 |  |  | Braf declined to replace aircon tray
MSA-DTWD | WA5693345 | 2 | AWB Co. | L Block - Horticulture Area -Tunnel green house - Cover has been smashed to pieces | Building | General Building | 225.96 | Pass | Pass | 0 | 0 | 2 | 2022-08-04 11:34 | 2022-08-09 17:00 | 2022-08-09 13:30 | 2022-08-09 17:00 | 2022-08-09 15:30 |  |  | Assessed and measured up green house tunneladvise close costs to dateJSA not required as only measurements taken - no works done
MSA-DTWD | WA5693456 | 2 | AWB Co. | External - Bentley Pines Restaurant illuminated carpark sign not working | Electrical | General Electrical | 375.89 | Fail | Fail | 0 | 0 | 2 | 2022-08-04 12:30 | 2022-08-09 17:00 | 2022-08-10 09:00 | 2022-08-09 17:00 | 2022-08-10 11:00 |  |  | Attended site signed in jsa completed. found lights in sign have blown ballasts all 5 of them out of 8. Spoke to site ripped guts out and installed 20w clipsal LED flood light inside. Tested and working.Job completed
MSA-DTWD | WA5694360 | 3 | AWB Co. | Lights out x 4 | Electrical | Lighting, Internal | 430.08 | Pass | Pass | 0 | 0 | 2 | 2022-08-05 09:33 | 2022-08-12 17:00 | 2022-08-12 11:15 | 2022-08-12 17:00 | 2022-08-12 13:15 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located lighting in b5 that was faulty , replaced tubes and starters , replaced lamps, disposed of old tubes in allocated bin provided by the site, packed up, completed paperwork, signed out *job complete*
MSA-DCA | WA5694626 | 1 | EQUANS Mechanical Services (WA) Pty Limited | RETROPSECTIVE WORK ORDER - AC for AHU 01-01 (public concourse) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-08-05 11:53 | 2022-08-08 17:00 | 2022-08-05 13:30 | 2022-08-08 17:00 | 2022-08-05 15:30 |  |  | ATTENDED SITE. CHECKED OVER TEMP COMPLAINTS FOR AHU 01-01. FOUND BUILDING WAS RUNNING LOCAL AND THE BOILERS HAD FAULTED. BOILERS FAULTED ON NO FLAME FAULT. RESET BOILER 1 AND TESTED OPERATION, ALL OK. SWITCHED CALL TO BOILER 2 AND RESET FAULT. TESTED OPERATION, ALL OK. CHECKED AHU TEMPS, ALL OK. COMPLETED PAPERWORK.
MSA-DTWD | WA5694804 | 3 | AWB Co. | A126-lights not working Female Staff toilet A126 Ground Floor | Electrical | Lighting, Internal | 434.64 | Pass | Pass | -1 | -1 | 2 | 2022-08-05 13:30 | 2022-08-12 17:00 | 2022-08-08 06:00 | 2022-08-12 17:00 | 2022-08-08 08:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located lighting in female staff toilets,went to wholesaler to pick up parts, returned to site, removed old light fittings, replaced with new, had to use timber on each light to mount, tested lights and working as intended , packed up, completed paperwork, signed out ,** job completed **
MSA-DFES | WA5696001 | 2 | Workzone Pty Ltd | ground SO office - Water entering through front door of office - see notes | Roofing | Metal Roofing | 439.43 | Pass | Pass | 0 | 0 | 2 | 2022-08-08 08:56 | 2022-08-11 17:00 | 2022-08-11 07:30 | 2022-08-11 17:00 | 2022-08-11 09:30 |  |  | Unblock and repair drains
MSA-DTWD | WA5696550 | 1 | AWB Co. | Replace broken polycarbonate on the west end of M Block | Roofing | Polycarbonate | 499.71 | Pass | Pass | 0 | 0 | 2 | 2022-08-08 12:35 | 2022-08-09 17:00 | 2022-08-08 14:40 | 2022-08-09 17:00 | 2022-08-08 16:40 |  |  | Attended and installed new skylight sheet, removed old shee
MSA-DFES | WA5697956 | 3 | Australian HVAC Services Pty. Ltd. | Ground Floor - Main Admin - Staff Change rooms - Tempertaure of aircon units are too hot - See notes | Air Conditioning | Room Air Conditioners | 201.88 | Pass | Pass | 0 | 0 | 2 | 2022-08-09 13:12 | 2022-08-16 17:00 | 2022-08-15 10:30 | 2022-08-16 17:00 | 2022-08-15 12:30 |  |  | All working well.
MSA-DFES | WA5698133 | 3 | Critical Fire Protection & Training | Gym - Smoke alarm in gym faulty, is disconnected from mains and battery had been removed. | Fire Protection Services | Smoke and Heat Detection | 417.45 | Pass | Pass | -1 | -1 | 2 | 2022-08-09 14:51 | 2022-08-16 17:00 | 2022-08-12 12:00 | 2022-08-16 17:00 | 2022-08-12 14:00 |  |  | Attended site and replaced detector as required.
MSA-DFES | WA5698150 | 3 | AWB Co. | Ground Floor Door to Undercroft - Floor Matt leading out to undercroft is a trip hazard | Building | General Building | 272.09 | Pass | Pass | 0 | 0 | 2 | 2022-08-09 15:01 | 2022-08-16 17:00 | 2022-08-16 11:55 | 2022-08-16 17:00 | 2022-08-16 13:55 |  |  | applied anti slip tape to rug
MSA-DTWD | WA5699287 | 2 | AHS Services WA Pty Ltd (Anchor) | Rear exterior-Water testing outlet outside Building A is not working | Plumbing & Drainage | Water | 244.83 | Pass | Pass | -1 | -1 | 2 | 2022-08-10 08:32 | 2022-08-15 17:00 | 2022-08-10 11:30 | 2022-08-15 17:00 | 2022-08-10 13:30 |  |  | Service and repaired external water sampling tap as required.
MSA-DCA | WA5699331 | 0 | Techworks Electrical | HISTORY OFFICE/WORKSHOP - light out due to burnt switch | Electrical | General Electrical | 277.45 | Pass | Pass | 0 | 0 | 2 | 2022-08-10 08:55 | 2022-08-10 10:55 | 2022-08-10 09:00 | 2022-08-10 12:55 | 2022-08-10 11:00 |  |  | Replaced burnt intermediate switch mech and plate with new plate and intermediate switch mech.Tested other light switch and terminations .
MSA-DTWD | WA5699741 | 2 | Lane's Plumbing | Blocked Drain | Plumbing & Drainage | Drainage |  | Pass | Pass | -1 | -1 | 2 | 2022-08-10 11:53 | 2022-08-15 17:00 | 2022-08-11 11:30 | 2022-08-15 17:00 | 2022-08-11 13:30 |  |  | cleared blockage
MSA-DTAG | WA5699787 | 1 | Sapio Pty Ltd | Lost visual for custody cells in control room | Security | CCTV Surveillance | 462.68 | Pass | Pass | 0 | 0 | 2 | 2022-08-10 12:10 | 2022-08-11 17:00 | 2022-08-11 10:00 | 2022-08-11 17:00 | 2022-08-11 12:00 |  |  | Found Custody was having problems with CCTV monitors. Re demo Indigo CCTV system to Custody Manager. Also checked Gallagher alarms.Job completed.
MSA-DTAG | WA5700067 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 2 ( ground floor ) - male staff toilet (1st cubicle) toilet flush button faulty | Plumbing & Drainage | Toilets/Cisterns | 224.445 | Pass | Pass | -1 | -1 | 2 | 2022-08-10 14:36 | 2022-08-15 17:00 | 2022-08-11 07:30 | 2022-08-15 17:00 | 2022-08-11 09:30 |  |  | .
MSA-DTAG | WA5728164 | 2 | PPM Project Painting & Maintenance | Various locations outside Perth childrens court graffiti - see notes | Cleaning | Emergency Cleans |  | Fail | Fail | 1 | 1 | 2 | 2022-08-15 14:54 | 2022-08-18 17:00 | 2022-08-22 08:30 | 2022-08-18 17:00 | 2022-08-22 10:30 |  |  | Job is completed - Graffiti removed from external locations
MSA-DFES | WA5749112 | 0 | Go Doors | rear roller doors - wind has taken roller door off the tracks, loose and flapping in the wind | Building | Automatic Doors | 435 | Fail | Fail | 0 | 0 | 2 | 2022-08-17 07:04 | 2022-08-17 09:04 | 2022-08-17 15:45 | 2022-08-17 11:04 | 2022-08-17 17:45 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5749495 | 2 | AWB Co. | roof leak in conference room | Roofing | Metal Roofing | 405.76 | Pass | Pass | 0 | 0 | 2 | 2022-08-17 08:57 | 2022-08-22 17:00 | 2022-08-19 10:00 | 2022-08-22 17:00 | 2022-08-19 12:00 |  |  | Found large gash in roof sheets possibly from falling branch.repaired sheets
MSA-DTWD | WA5751724 | 3 | AWB Co. | ground C35-10 x lights out hairdressing | Electrical | Lighting, Internal | 513.65 | Pass | Pass | -1 | -1 | 2 | 2022-08-17 10:58 | 2022-08-24 17:00 | 2022-08-18 11:15 | 2022-08-24 17:00 | 2022-08-18 13:15 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Spoke to c block admin. Located faulty lighting. Counted parts we needed. Went to wholesaler. Returned to site. Replaced all faulty lighting. Now working as intended. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5753317 | 2 | Protek 24/7 Building & Maintenance | Roof leak from Anchor point | Roofing | Metal Roofing | 388.81 | Pass | Pass | 0 | 0 | 2 | 2022-08-17 15:46 | 2022-08-22 17:00 | 2022-08-22 13:00 | 2022-08-22 17:00 | 2022-08-22 15:00 |  |  | Leak repairedCeiling damage, Susan told us not to worry about ceiling repairs
MSA-DTWD | WA5780465 | 3 | AWB Co. | C16 Facilities office-Steaming Units have damaged plug tops | Electrical | General Electrical | 292.89 | Pass | Pass | 0 | 0 | 2 | 2022-08-19 10:42 | 2022-08-26 17:00 | 2022-08-23 07:00 | 2022-08-26 17:00 | 2022-08-23 09:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located steam machines , went to wholesaler to pick up parts, returned to site, set up work area, removed old plugs and replaced with new, visually inspected cables and machines, tested all machines, all machines passed, wrote out test stickers and put on machines, packed up, completed paperwork,signed out **job completed**
MSA-DTWD | WA5780663 | 2 | Lane's Plumbing | Drinking water fountain faulty | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-08-19 12:08 | 2022-08-24 17:00 | 2022-08-22 10:00 | 2022-08-24 17:00 | 2022-08-22 12:00 |  |  | Job is complete - Faulty Drinking water fountain fixed
MSA-DTWD | WA5790044 | 2 | M Construction (WA) | D Block - Level 2 - Chiller compound - roof has broken bird netting | Building | General Building | 245.15 | Pass | Pass | 0 | 0 | 2 | 2022-08-22 08:37 | 2022-08-25 17:00 | 2022-08-23 09:00 | 2022-08-25 17:00 | 2022-08-23 11:00 |  |  | Attended site and found the roof has a broken grid venting, re-stitched together by re-fixing 2 x zip fees and netting.
MSA-DTWD | WA5790058 | 3 | AWB Co. | 8F2 Main Plant Room - Various lights out - See notes below | Electrical | Lighting, Internal | 384.98 | Pass | Pass | -1 | -1 | 2 | 2022-08-22 08:39 | 2022-08-29 17:00 | 2022-08-23 10:00 | 2022-08-29 17:00 | 2022-08-23 12:00 |  |  | Attended site and signed in. Completed JSA. Located lights in plant room not working. Lights do not have diffusers on them. Was advised to replace them with led battens. Site supplied the 2 x battens. Replaced 2 x lights at the back of the plant room as asked. Tested all okay.Signed out. Job complete
MSA-DTWD | WA5790240 | 3 | M Construction (WA) | Yellagonga - Rooma has a broken hand towel dispenser. Please replace/repair ( Supplied) | Cleaning | Sanitary Services | 241.17 | Pass | Pass | -1 | -1 | 2 | 2022-08-22 09:21 | 2022-08-29 17:00 | 2022-08-23 07:00 | 2022-08-29 17:00 | 2022-08-23 09:00 |  |  | Attended site and found Roma has a broken hand towel dispenser, removed old dispenser, made good to wall and installednew dispenser. Job completed.
MSA-DTWD | WA5791853 | 2 | BJ SYSTEMS | Entrance - F-Block alarm key pad not turning alarm off | Security | Security Management System | 360 | Pass | Pass | 0 | 0 | 2 | 2022-08-23 09:56 | 2022-08-26 17:00 | 2022-08-24 07:30 | 2022-08-26 17:00 | 2022-08-24 09:30 |  |  | Check F Block intruder programming. Inspect alarm keypad terminal, inspect intruder security devices. Set up F Block site plan and devices associated. Keypad arm and disarm ok. LED status on keypad flash indicator alarms in system to be processed
MSA-DCA | WA5792956 | 1 | Techworks Plumbing | Jubilee building - ground floor - accessible toilets - Cistern leaking in the wall | Plumbing & Drainage | Water | 360 | Fail | Fail | 0 | 0 | 2 | 2022-08-23 15:37 | 2022-08-24 17:00 | 2022-08-24 17:30 | 2022-08-24 17:00 | 2022-08-24 19:30 |  |  | Attended call out at Perth museum. Spoke with Neil on the phone about location and what’s been happening. Signed in at security desk and got a swipe key to access jubile toilets. Toilet was constantly running into bowl and water was on the floor in the plant room behind toilet. Checked in roof there is no isolation for the toilet. Took button assembly apart and isolated invisi inside the cistern which stopped the water running through. Went back into plant room and since water has been running for about a week Neil reckons the wall is falling apart, it’s only gyprock. Pulled wall apart to check if it’s the flush pipe leaking but water seems to be coming from higher up could possibly be a cracked cistern. As there isn’t much I can really do at this time of night decided to isolated and someone will need to return to solve the issue at least the wall is easy to cut out and patch. Please note the muddy footprints in the hallway where already there and no one is on site don’t blame me. Ret
MSA-DTWD | WA5794431 | 3 | AWB Co. | Replace faulty lights in toilets | Electrical | Lighting, Internal | 699.08 | Pass | Pass | -1 | -1 | 2 | 2022-08-24 15:17 | 2022-08-31 17:00 | 2022-08-25 08:30 | 2022-08-31 17:00 | 2022-08-25 10:30 |  |  | Attended site and signed in, completed paperwork, located female toilets in J block. Liaised with FM about works going ahead. Left site to collect parts. Returned to site. Set up work area. Replaced 4x old downlight with new LED lights. Tested for correct operation. Packed and cleaned up work area. Notified relevant personnel of works. Completed paperwork. **job complete**
MSA-MRWA | WA5797916 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 9 - Plant Room - Boiler 3 showing F5 Fault | Mechanical Services | Boilers | 321.44 | Pass | Pass | 0 | 0 | 2 | 2022-08-29 11:31 | 2022-09-01 17:00 | 2022-09-01 12:00 | 2022-09-01 17:00 | 2022-09-01 14:00 |  |  | investigation completed, repairs to be carried out on another work order.
MSA-DFES | WA5799089 | 2 | AWB Co. | The box gutter that runs across the entire front of all 3 engine bays has deteriorated-see notes | Roofing | Guttering | 424.13 | Pass | Pass | 0 | 0 | 2 | 2022-08-30 09:20 | 2022-09-02 17:00 | 2022-09-02 12:15 | 2022-09-02 17:00 | 2022-09-02 14:15 |  |  | Attended and re-sealed gutter joints to box gutter and sumps. Box gutter ok cond. Sump downpipes are in the wall cavity. Site to monitor, further inspection may be needed if issue persists.
MSA-DCA | WA5799484 | 2 | Protek 24/7 Building & Maintenance | External ground - Wobbly pavers | Paving & Roadworks | Paving | 260.91 | Pass | Pass | 0 | 0 | 2 | 2022-08-30 12:16 | 2022-09-02 17:00 | 2022-09-01 07:00 | 2022-09-02 17:00 | 2022-09-01 09:00 |  |  | Removed 4 x loose header pavers along storm water grate , removed old adhesive from pavers and substrate,Applied moisture resistant adhesive to underside of pavers and substrate , relayed pavers , applied paving lock to joints around pavers .
MSA-DTWD | WA5799864 | 3 | GRAFFITI FORCE PTY LTD | Building perimeter - Numerous tagging around building | Cleaning | Graffiti | 418 | Fail | Fail | 3 | 3 | 2 | 2022-08-30 15:12 | 2022-09-06 17:00 | 2022-09-27 09:45 | 2022-09-06 17:00 | 2022-09-27 11:45 |  |  | REMOVAL OF GRAFFITI FROM THE PERIMETER OF BUILDING 5
MSA-DTWD | WA5800150 | 0 | Protek 24/7 Building & Maintenance | close to K/G block rear gate-gate has been pulled by vehicle | Building | Steel Fencing & Gates | 281.89 | Pass | Pass | 0 | 0 | 2 | 2022-08-31 07:49 | 2022-08-31 09:49 | 2022-08-31 09:00 | 2022-08-31 11:49 | 2022-08-31 11:00 |  |  | BRAF Declined
MSA-DTAG | WA5800510 | 1 | Sapio Pty Ltd | Ground Floor - Security Office - Monitor to cameras is faulty - See notes below | Security | Monitoring | 423.88 | Pass | Pass | 0 | 0 | 2 | 2022-08-31 10:34 | 2022-09-01 17:00 | 2022-09-01 09:00 | 2022-09-01 17:00 | 2022-09-01 11:00 |  |  | Attended site. Checked reported fault. It's seems to power supply had loose contact. Rectified fault. Tied up cables and lifted power supply of the floor.
MSA-DTWD | WA5800824 | 2 | M Construction (WA) | D Block - Female Staff Toilet -Repair/replace faulty door closer | Building | Doors | 676.76 | Pass | Pass | 0 | 0 | 2 | 2022-08-31 12:39 | 2022-09-05 17:00 | 2022-09-05 07:30 | 2022-09-05 17:00 | 2022-09-05 09:30 |  |  | Installed new door closer and removed/disposed of old.
MSA-DTWD | WA5800879 | 2 | AWB Co. | Replace brown light | Electrical | Lighting, Internal | 373.035 | Pass | Pass | 0 | 0 | 2 | 2022-08-31 13:01 | 2022-09-05 17:00 | 2022-09-05 07:00 | 2022-09-05 17:00 | 2022-09-05 09:00 |  |  | Attended site and signed in. Completed jsa. Located faulty light fitting in p002.4. Went to wholesaler for part. Returned to site. Replaced led batten. Took picture. Completed paperwork. Signed out.Job complete.
MSA-DCA | WA5829100 | 3 | FCT SURFACE CLEANING | Graffiti - see notes below | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-09-02 10:24 | 2022-09-09 17:00 | 2022-09-06 13:00 | 2022-09-09 17:00 | 2022-09-06 15:00 |  |  | Removal of graffiti
MSA-DFES | WA5829247 | 2 | AWB Co. | Ground Floor - Firefighters ensuite -Water coming in through light fitting in ensuite when it rains. | Roofing | Metal Roofing | 451.01 | Pass | Pass | 0 | 0 | 2 | 2022-09-02 11:26 | 2022-09-07 17:00 | 2022-09-05 10:00 | 2022-09-07 17:00 | 2022-09-05 12:00 |  |  | Attended and sealed beneath PVC ventilator fan - may need new fan system site to monitor
MSA-DTWD | WA5829444 | 2 | Protek 24/7 Building & Maintenance | Rear exit door jams on ground when opening. Remove & refit. | Building | Doors | 271.54 | Pass | Pass | 0 | 0 | 2 | 2022-09-02 13:31 | 2022-09-07 17:00 | 2022-09-05 10:30 | 2022-09-07 17:00 | 2022-09-05 12:30 |  |  | Removed door from frame , repaired missing door trim to door , planed down bottom of door including aluminum weather seal , re instated door , test operation, all ok
MSA-DTWD | WA5830094 | 1 | Techworks Plumbing | Sink drain pump making noise when in operation | Plumbing & Drainage | Drainage | 230.86 | Pass | Pass | 0 | 0 | 2 | 2022-09-02 15:10 | 2022-09-05 17:00 | 2022-09-05 07:00 | 2022-09-05 17:00 | 2022-09-05 09:00 |  |  | Arrived at Kwinana automotive tafe, got let through the heavy diesel side of the tafe, spoke to the lecturer regarding the pump making a weird noise he showed me where it was, I then removed the pump and opened up the pump to check for any debris inside, found two bits of debris inside of the pump, i took the pump outside to clean it out with a hose, I then reinstalled the pump and checked if it would still be making the same noise, it didn’t make any funny noises anymore, I then seen that the outlet pipe wasn’t glued so I then had to glue the pipe to unsure it wasn’t going to leak, I then cleaned up the area and checked the pump if it’s operating adequately, I then got a signature slip and went back to the vehicle to write notes.
MSA-DCA | WA5832490 | 3 | Techworks Plumbing | Jubilee - Ground floor - Admin UAT - Water leaking into plant room | Plumbing & Drainage | Water | 422.3 | Pass | Pass | -1 | -1 | 2 | 2022-09-05 13:35 | 2022-09-12 17:00 | 2022-09-06 08:30 | 2022-09-12 17:00 | 2022-09-06 10:30 |  |  | arrived on site and signed in at security and got an access cardwe attended to the jubilee building and spoke to the reception to find about the leak in the plant room had a look in the plant room for the water leak but could not find one.we called Neil and he came down to meet us, he explained to us that they had a leaking cistern that was leaking into the plant room but it was fixed by Dan a week ago he double checked to see if there was anything else it might have been but it was just that leak.we got a signature and signed out completed paperwork
MSA-DTWD | WA5832660 | 2 | COMMERCIAL PLUMBING AND GAS | Gas heater not working - See notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 213.97 | Pass | Pass | 0 | 0 | 2 | 2022-09-05 14:47 | 2022-09-08 17:00 | 2022-09-08 09:00 | 2022-09-08 17:00 | 2022-09-08 11:00 |  |  | reset unit, run to temperature, monitor
MSA-DTWD | WA5833573 | 1 | Protek 24/7 Building & Maintenance | Roof leak around aircon vent | Roofing | Metal Roofing | 359.31 | Pass | Pass | 0 | 0 | 2 | 2022-09-06 10:33 | 2022-09-07 17:00 | 2022-09-07 09:00 | 2022-09-07 17:00 | 2022-09-07 11:00 |  |  | Water tested extensively and found no leaksSite advised to close job off
MSA-DTWD | WA5834343 | 2 | AWB Co. | Security light faulty | Electrical | Lighting, Internal | 454.23 | Pass | Pass | 0 | 0 | 2 | 2022-09-06 15:19 | 2022-09-09 17:00 | 2022-09-09 12:45 | 2022-09-09 17:00 | 2022-09-09 14:45 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Located faulty floodlight, found that it was making a loud buzzing sound. Went to wholesaler to pick up floodlight. Returned to site, de energised circuit. Installed new floodlight. Siliconed to make water tight. Tested. Working as intended. Took picture. completed paperwork. Signed out.Job complete
MSA-DCA | WA5836576 | 1 | Automatic Fire Protection (ARA) | Level 2 - Gallery - Smoke detector in fault – L2S76 | Fire Protection Services | Smoke and Heat Detection | 472.73 | Pass | Pass | 0 | 0 | 2 | 2022-09-07 12:53 | 2022-09-08 17:00 | 2022-09-07 13:30 | 2022-09-08 17:00 | 2022-09-07 15:30 |  |  | Technician NoteAttended site replaced l1s76 smoke detector in gallery 2 in maintenance fault left normal on departure
MSA-DTWD | WA5838007 | 3 | Equans Mechanical Services Australia | Art gallery - Faulty Co2 Sensor Gallery - CB03 | Air Conditioning | Room Air Conditioners | 219.6 | Pass | Pass | -1 | -1 | 2 | 2022-09-08 10:17 | 2022-09-15 17:00 | 2022-09-09 13:00 | 2022-09-15 17:00 | 2022-09-09 15:00 |  |  | Checked the air-conditioning system for a CO2 sensor, looked behind the return air grills, only found data cables and power point supply cables. Checked the electrical system of the aircon and thermostat, went to B1 office and looked through original plans diagrams , and electrical info. No CO2 sensor is on this aircon .
MSA-DFES | WA5839062 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | faulty fluoro light in station officers storeroom - faulty sensor light at rear entrance door | Electrical | Lighting, Internal | 383.36 | Pass | Pass | 0 | 0 | 2 | 2022-09-09 08:54 | 2022-09-14 17:00 | 2022-09-12 10:45 | 2022-09-14 17:00 | 2022-09-12 12:45 |  |  | Signed onto the job at 1045. Located faulty lights. Replaced faulty tubes and starters with new. Replaced faulty flood light with new. Signed out at
MSA-DCA | WA5839357 | 1 | Schneider Electric Australia Pty Ltd | Roof - Flood light fault, will not turn off by BMS – security concerns- See notes below | Electrical | Emergency & Exit Lighting |  | Pass | Pass | 0 | 0 | 2 | 2022-09-09 11:29 | 2022-09-12 17:00 | 2022-09-12 07:30 | 2022-09-12 17:00 | 2022-09-12 09:30 |  |  | Completed
MSA-DFES | WA5839810 | 2 | Protek 24/7 Building & Maintenance | Ground - Flagpole cleat has broken on the left outer hand pole | Building | Steel Work | 210.54 | Pass | Pass | 0 | 0 | 2 | 2022-09-09 16:05 | 2022-09-14 17:00 | 2022-09-13 07:00 | 2022-09-14 17:00 | 2022-09-13 09:00 |  |  | removed and replaced the cleat hook with a new one
MSA-DCA | WA5853826 | 0 | SCAVENGER SUPPLIES PTY LTD | francis street building out side SCG - smoke alarm & smoke curtain dropped and wont retrack | Fire Protection Services | Fire Protection - Monitor System | 588.19 | Pass | Pass | 0 | 0 | 2 | 2022-09-12 11:28 | 2022-09-12 13:28 | 2022-09-12 12:53 | 2022-09-12 15:28 | 2022-09-12 14:53 |  |  | COMPLETED 12/9/22
MSA-DCA | WA5854227 | 1 | Techworks Electrical | Ground Floor / Studio Underground - Large white lights not working in stairwell - See notes below | Electrical | Lighting, Internal | 395.7 | Pass | Pass | 0 | 0 | 2 | 2022-09-12 14:41 | 2022-09-13 17:00 | 2022-09-13 07:30 | 2022-09-13 17:00 | 2022-09-13 09:30 |  |  | Arrived on site and began fault finding lights in stairwell. Both lights had faulty ballests, have replaced the ballests and lights are working.
MSA-DTWD | WA5867014 | 2 | Techworks Electrical | Finance area - fluorescent light not working | Electrical | Lighting, Internal | 507.05 | Pass | Pass | -1 | -1 | 2 | 2022-09-14 09:23 | 2022-09-19 17:00 | 2022-09-15 10:00 | 2022-09-19 17:00 | 2022-09-15 12:00 |  |  | Replace light fitting
MSA-DTWD | WA5878694 | 1 | Techworks Plumbing | female toilets basin is blocked | Plumbing & Drainage | Toilets/Cisterns | 430.46 | Fail | Fail | 1 | 1 | 2 | 2022-09-15 07:46 | 2022-09-15 17:00 | 2022-09-19 14:30 | 2022-09-15 17:00 | 2022-09-19 16:30 |  |  | Investigated blocked sink. Sink was running slow but nothing too major, most likely had something to do with the backed up sewer from the previous week.Plunged waste and cleaned trap out. Tested
MSA-DTWD | WA5880387 | 1 | Lane's Plumbing | Faulty taps | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-09-15 12:35 | 2022-09-16 17:00 | 2022-09-15 14:30 | 2022-09-16 17:00 | 2022-09-15 16:30 |  |  | repairs to taps
MSA-DTWD | WA5962282 | 2 | Lane's Plumbing | Flat D Bathroom - Faulty cistern | Plumbing & Drainage | Toilets/Cisterns |  | Fail | Fail | 0 | 0 | 2 | 2022-09-19 13:02 | 2022-09-22 17:00 | 2022-09-23 13:30 | 2022-09-22 17:00 | 2022-09-23 15:30 |  |  | Repairs to cistern
MSA-DTWD | WA5962600 | 2 | Damian Rak Electrical Pty Ltd | Hallway - faulty exit lights | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 2 | 2022-09-19 15:40 | 2022-09-22 17:00 | 2022-09-28 13:00 | 2022-09-22 17:00 | 2022-09-28 15:00 |  |  | Repairs to light
MSA-DFES | WA5974026 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | SO office LED light fitting faulty | Electrical | Lighting, Internal | 307.44 | Pass | Pass | 0 | 0 | 2 | 2022-09-23 07:21 | 2022-09-30 17:00 | 2022-09-28 11:15 | 2022-09-30 17:00 | 2022-09-28 13:15 |  |  | Arrived on site at 1115 to attend SO office LED light fitting faulty. Located 1 x faulty led. Left site at 1130 to pick up parts. Returned to site at 1230 and replaced faulty led. Informed staff of works and left site at 1315.
MSA-DTWD | WA5974699 | 3 | AWB Co. | Kitchen, passageway and stairwell - tripped power points from faulty iron. See notes | Electrical | General Electrical | 473.86 | Pass | Pass | 0 | 0 | 2 | 2022-09-23 15:23 | 2022-10-03 17:00 | 2022-09-30 13:45 | 2022-10-03 17:00 | 2022-09-30 15:45 |  |  | Attended site and signed in. Completed JSA. Located lights and power not working. Found power to to be tripped to the kitchen. Reset and tested all appliances. No fault found on faulty appliances. Possibly an overload to the kitchen. Supply and replaced faulty tubes to reception. Supply and replace faulty exit sign with new upstairs in hallway. Tested all okay. Signed out. Job complete
MSA-DFES | WA5974727 | 3 | Complete Pest Management Services | Eastern end - Trees near to buildings - Termite infestation risk | Pest Control | Specialist Pest | 4178.3 | Fail | Fail | 2 | 2 | 2 | 2022-09-23 15:52 | 2022-10-03 17:00 | 2022-10-15 12:00 | 2022-10-03 17:00 | 2022-10-15 14:00 |  |  | Termite Inspection - External areas within 50m of buildings - Inspection resulted in identification of termite activity in 26 locations including positive identification of 13 termitenests including 4 termite mounds.
MSA-DTWD | WA5976971 | 2 | Protek 24/7 Building & Maintenance | ground-Flammable liquid store-Door has dropped and dragging on ground | Building | Doors | 200.64 | Pass | Pass | 0 | 0 | 2 | 2022-09-27 12:43 | 2022-09-30 17:00 | 2022-09-28 09:00 | 2022-09-30 17:00 | 2022-09-28 11:00 |  |  | Braf Declined Temp Fix completed
MSA-DTWD | WA5977215 | 3 | AWB Co. | Fume Extraction cupboards 5..8 and 9 have faulty GPOs in them currently tagged out | Electrical | General Electrical | 275.89 | Pass | Pass | 0 | 0 | 2 | 2022-09-27 14:38 | 2022-10-04 17:00 | 2022-10-03 13:45 | 2022-10-04 17:00 | 2022-10-03 15:45 |  |  | Job complete
MSA-DTAG | WA5977326 | 2 | Sapio Pty Ltd | Create a manual override to enable court staff to manually lock entry doors -see notes | Security | Access Control | 269 | Pass | Pass | 0 | 0 | 2 | 2022-09-27 15:45 | 2022-09-30 17:00 | 2022-09-29 10:00 | 2022-09-30 17:00 | 2022-09-29 12:00 |  |  | WA - Sasa Nikolic (29/09/2022) - Work Note Attended site. Programmed public holidays for years 2022-2024. Checked system for an override keyswitch installation.
MSA-DTWD | WA5978286 | 3 | Critical Fire Protection & Training | Smoke detector faulty - zone isolated FESA unable to find faulty smoke detector | Fire Protection Services | Smoke and Heat Detection | 405.2 | Pass | Pass | 0 | 0 | 2 | 2022-09-28 09:57 | 2022-10-05 17:00 | 2022-10-04 10:20 | 2022-10-05 17:00 | 2022-10-04 12:20 |  |  | 2x technicians attended site to investigate. Found to be a historical fire alarm present and isolated on fire panel in level 1 east (mine-sim).After investigating detectors in zone found no sign of triggered detector present. Recommendation would be to re-wire with new cable and detectors attached to an addressable loop (Quote provided in February 2022) as faulty wiring likely to be cause of false alarm in zone. False alarm zone 43 left isolated on departure until further action can be undertaken.
MSA-DCA | WA5979104 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Chester Building - Staircase is very slippery when wet - See notes below | Building | General Building | 474.26 | Pass | Pass | 0 | 0 | 2 | 2022-09-28 16:10 | 2022-09-29 17:00 | 2022-09-29 11:15 | 2022-09-29 17:00 | 2022-09-29 13:15 |  |  | Supply and install non slip stair tread tape to each stair tread
MSA-DTWD | WA5982405 | 3 | SENTINEL LOCK SERVICE PTY LTD | 3G34 - Faulty Key Pad | Security | Locksmith | 809.32 | Pass | Pass | -1 | -1 | 2 | 2022-09-30 10:52 | 2022-10-07 17:00 | 2022-10-03 07:00 | 2022-10-07 17:00 | 2022-10-03 09:00 |  |  | 3G34 - faulty key pad.DX pad & handle replaced - lock serviced.
MSA-DTWD | WA5991872 | 3 | Equans Mechanical Services Australia | VAV 4-2 Feeding room B301 - Issues with BMS - See notes below | Building | General Building | 219.6 | Pass | Pass | -1 | -1 | 2 | 2022-10-04 15:13 | 2022-10-11 17:00 | 2022-10-05 12:00 | 2022-10-11 17:00 | 2022-10-05 14:00 |  |  | Travelled to site. Gained access to site. Investigated issue and found main air plenum in room feeding supply air to VAV and ducting has failed. Main plenum is part of the building infrastructure and requires building maintenance company to repair top of plenum. Checked and found VAV operating correctly. Site maintenance has been informed and has photos of damage. Completed paperwork and logged off job.
MSA-DTWD | WA5995566 | 2 | AWB Co. | Main Car Park - No power to main gate | Electrical | General Electrical | 301.405 | Pass | Pass | 0 | 0 | 2 | 2022-10-06 12:49 | 2022-10-11 17:00 | 2022-10-10 10:30 | 2022-10-11 17:00 | 2022-10-10 12:30 |  |  | Attended site signed in jsa completed. Found gate with no power. Looked in 5 boards couldnt find. Found in library switchboard a CB w18 but in the off position as different brand it switches opposite. Advised site got power to gate. Gate will open on remote but not shut. Frank has advised he will call gate company to fixjob completed
MSA-DCA | WA5995709 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Fan 29 regularly going into alarm on Honeywell BMS - See notes below | Building | General Building | 259.01 | Pass | Pass | -1 | -1 | 2 | 2022-10-06 15:14 | 2022-10-11 17:00 | 2022-10-07 14:30 | 2022-10-11 17:00 | 2022-10-07 16:30 |  |  | Attended site. Investigated exhaust fan 29. Found on security's bms that fan status was cutting in and out but no alarms present. Checked over exhaust fan, found belt had slipped causing the fan status to cut in and out. Changed both belts with last spare set and tested operation, all ok. Will quote to replace belts and pulleys due to grooves forming. Exhaust ducting and frame needs some rust treatment. Completed paperwork.
MSA-DCA | WA5997782 | 1 | Critical Fire Protection & Training | Fire Panel - Sensor Alarm showing on fire panel | Fire Protection Services | Fire Protection - Monitor System | 463.9 | Pass | Pass | 0 | 0 | 2 | 2022-10-07 09:40 | 2022-10-10 17:00 | 2022-10-07 09:40 | 2022-10-10 17:00 | 2022-10-07 11:40 |  |  | Whilst already onsite, we were advised of an overnight fault appearing on the fire panel.After investigation, we found a detector in zone 12 (fridge) was in fault so this was replaced.
MSA-DFES | WA5998089 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | BA Servicing Room -Drying Cabinet electrical fault. Burnt plug. It is an old unit - Images in email | Electrical | General Electrical | 488.74 | Pass | Pass | 0 | 0 | 2 | 2022-10-07 11:55 | 2022-10-14 17:00 | 2022-10-13 10:00 | 2022-10-14 17:00 | 2022-10-13 12:00 |  |  | Continued on site at 10:00 to investigate BA Servicing Room -Drying Cabinet electrical fault. Burnt plug. Went to wholesalerto collect parts. Replaced entire lead and plugtop. Tested all working. Notified staff of outcome and left site at 12:00
MSA-DTWD | WA6008401 | 2 | M Construction (WA) | stainless steel ingredient bin which the lid/flap has broken off from the spot weld points-see notes | Building | Steel Work | 399.1 | Pass | Pass | 0 | 0 | 2 | 2022-10-11 14:07 | 2022-10-14 17:00 | 2022-10-13 09:45 | 2022-10-14 17:00 | 2022-10-13 11:45 |  |  | Reweld stainless steel hinge.
MSA-DCA | WA6019602 | 0 | Earth & Water Pty Ltd | around back of state library-garden bed retic leaking into carpark below | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 0 | 0 | 2 | 2022-10-13 07:00 | 2022-10-13 09:00 | 2022-10-13 09:00 | 2022-10-13 11:00 | 2022-10-13 11:00 |  |  | repairs to retic
MSA-DTWD | WA6020145 | 2 | M Construction (WA) | S block - Ground level - damaged fire cabinet door handle - see notes below | Building | Fire Door | 180 | Pass | Pass | 0 | 0 | 2 | 2022-10-13 10:59 | 2022-10-18 17:00 | 2022-10-17 07:00 | 2022-10-18 17:00 | 2022-10-17 09:00 |  |  | Remove Broken Push to mechanism and installed new D Handle
MSA-DCA | WA6020179 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Loading Bay 7 - humidifier unit is leaking water | Air Conditioning | Building HVAC Maintenance (Major Plant) | 281.53 | Pass | Pass | 0 | 0 | 2 | 2022-10-13 11:21 | 2022-10-13 13:21 | 2022-10-13 12:00 | 2022-10-13 15:21 | 2022-10-13 14:00 |  |  | Humidifier 4 leaking from seals. Sent photo's and details to subcontractor for replacement.
MSA-DCA | WA6020611 | 2 | EQUANS Mechanical Services (WA) Pty Limited | North/East corner-Airflow L3 northeast side workroom impeded. | Air Conditioning | Room Air Conditioners | 484.23 | Pass | Pass | -1 | -1 | 2 | 2022-10-13 14:41 | 2022-10-18 17:00 | 2022-10-14 07:00 | 2022-10-18 17:00 | 2022-10-14 09:00 |  |  | Attended site, signed in and gained access. Investigated temp complaints on level 3 north-east office space. Found vav setpoints at 24°c and units heating the space first thing in the morning. Changed setpoint on all vavs in north east area to 22.5 and tested operation of vavs. Ta carried out floor checks and confirmed vavs operating whilst I made changes through the bms. All operating as required. Checked over sensor calibrations, all ok but found with the fit out sensor location and room location has changed and if issues persist will need to discuss with Honeywell to amend. Will monitor further. Completed paperwork
MSA-DCA | WA6022919 | 0 | EQUANS Mechanical Services (WA) Pty Limited | BMS - Humidity readings are low | Equipment | Building Equipment | 281.53 | Fail | Fail | 1 | 1 | 2 | 2022-10-13 13:37 | 2022-10-13 15:37 | 2022-10-17 13:00 | 2022-10-13 17:37 | 2022-10-17 15:00 |  |  | Reset and tested operation of humidifiers 1 and 2. No fault codes found. Tested all OK at this time.
MSA-DTWD | WA6046639 | 2 | COMMERCIAL PLUMBING AND GAS | Painting and Decorating workshop 6F45 - Sink is blocked | Plumbing & Drainage | Drainage | 233.97 | Pass | Pass | 0 | 0 | 2 | 2022-10-17 11:54 | 2022-10-20 17:00 | 2022-10-19 15:00 | 2022-10-20 17:00 | 2022-10-19 17:00 |  |  | unblocked sink used for paint disposal
MSA-DTWD | WA6048225 | 3 | PEEL LOCK SERVICES PTY LTD | F25 laundry-Repair/replace faulty laundry cabinet locks | Security | Locksmith |  | Pass | Pass | 0 | 0 | 2 | 2022-10-17 13:20 | 2022-10-24 17:00 | 2022-10-21 07:45 | 2022-10-24 17:00 | 2022-10-21 09:45 |  |  | Repairs to locks
MSA-DTWD | WA6080662 | 2 | Techworks Plumbing | C45 - hairdressing laundry - blocked drain again - See notes below | Plumbing & Drainage | Drainage | 917.27 | Pass | Pass | 0 | 0 | 2 | 2022-10-18 13:57 | 2022-10-21 17:00 | 2022-10-19 13:30 | 2022-10-21 17:00 | 2022-10-19 15:30 |  |  | Removed laundry trough trap and cleared blockage with drain machine - tested okFound heavy amounts hair causing blockageReinstated laundry trap
MSA-DCA | WA6088228 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Mechanical Plant Room - Level 3 - Two Chillers & Boiler at fault | Mechanical Services | Boilers | 985.29 | Fail | Fail | 0 | 0 | 2 | 2022-10-19 07:26 | 2022-10-19 09:26 | 2022-10-19 12:00 | 2022-10-19 11:26 | 2022-10-19 14:00 |  |  | Hard reset to both chillers and boiler. Subcontractor is looking at boiler leak to repair.
MSA-DCA | WA6090643 | 2 | Techworks Electrical | First Floor - Balcony - One side of track lighting is faulty. Recurring fault | Electrical | General Electrical | 230.88 | Pass | Pass | 0 | 0 | 2 | 2022-10-19 12:33 | 2022-10-24 17:00 | 2022-10-21 10:00 | 2022-10-24 17:00 | 2022-10-21 12:00 |  |  | Need to get a massive scaffold to get to the light fitting to see the problem. Have power going through the switch. Reece has come down and had a look and is organising a solution.
MSA-DTWD | WA6090703 | 2 | Damian Rak Electrical Pty Ltd | Kitchen / Dining room -Lights tripping | Electrical | Lighting, Internal |  | Fail | Fail | 1 | 1 | 2 | 2022-10-19 13:10 | 2022-10-24 17:00 | 2022-10-31 09:00 | 2022-10-24 17:00 | 2022-10-31 11:00 |  |  | lights faulty
MSA-DTWD | WA6090812 | 2 | Securex Security Systems & Services | Remove Damaged PIR Sensor reinstate in new ceiling | Security | Security Management System | 462.87 | Fail | Fail | 4 | 4 | 2 | 2022-10-19 13:58 | 2022-10-24 17:00 | 2022-11-21 08:15 | 2022-10-24 17:00 | 2022-11-21 10:15 |  |  | 21/11/2022, 815-1015Replaced ceiling mount including eol, reconnected, programmed both zone and separate tamper. All clear on panel.
MSA-DTWD | WA6108981 | 2 | AWB Co. | B2308 Textile Workshop - Faulty 10amp suspension socket & lead | Electrical | General Electrical | 381.53 | Pass | Pass | 0 | 0 | 2 | 2022-10-20 12:36 | 2022-10-25 17:00 | 2022-10-24 12:00 | 2022-10-25 17:00 | 2022-10-24 14:00 |  |  | Attended site and signed in, completed JSA,spoke with fm about job, located pendant gpo with out of service tag, inspected cable and insulation looked in good condition, extended cable out to full length on runner above and found that it put strain on it, put screws in to act as a stopper so cable didn’t do this and still had slack, found support cable to pendant was too short, extend cable to meet standards, inspected gpo and plug top, plugtop didn’t have insulated pins and found that gpo was damaged internally, went to wholesaler top pick up parts, returned to site, isolated circuit and replaced plugtop and gpo, conducted continuity test(pass), I.r test(pass) and rcd injection test(pass) on pendant gpo, all tests passed, packed up, completed paperwork, signed out job complete
MSA-DTWD | WA6111459 | 2 | Precise Air Group | A313 Science Labs - Urgent repair of fume hood In chemistry preparation lab | Air Conditioning | Room Air Conditioners | 366 | Pass | Pass | 0 | 0 | 2 | 2022-10-21 07:40 | 2022-10-25 17:00 | 2022-10-24 10:00 | 2022-10-25 17:00 | 2022-10-24 12:00 |  |  | attended site signed in and filled out nessesary paperwork. located fume cupboard and fans in the roof plantroom. carried out functional checks on the fan motor. Found the fan motor to be me mechanically okay and would run in manual mode but not stay on when set to auto on the bms. Loased with fm on site and agreed to contact bms contractor.
MSA-DTWD | WA6112211 | 2 | AWB Co. | Outside toilet next to C101 - Vandalised toilet C Block East Perth | Cleaning | Graffiti | 244.96 | Fail | Fail | 1 | 1 | 2 | 2022-10-21 13:59 | 2022-10-26 17:00 | 2022-11-01 10:30 | 2022-10-26 17:00 | 2022-11-01 12:30 |  |  | Replaced shower hose
MSA-DCA | WA6113393 | 2 | Techworks Electrical | Basement 1 -next to pump room - GPOs were turned off due to leak, on 12/10 now need to be reinstated | Electrical | General Electrical | 404.67 | Pass | Pass | 0 | 0 | 2 | 2022-10-24 11:22 | 2022-10-27 17:00 | 2022-10-25 07:00 | 2022-10-27 17:00 | 2022-10-25 09:00 |  |  | Reconnected GPO’s as per scope
MSA-DTWD | WA6126238 | 3 | AWB Co. | GPO is hanging loose on Brick wall | Electrical | General Electrical | 384.98 | Pass | Pass | -1 | -1 | 2 | 2022-10-25 11:07 | 2022-11-01 17:00 | 2022-10-27 14:30 | 2022-11-01 17:00 | 2022-10-27 16:30 |  |  | Attended site signed in jsa completed. Found gpo loose in wall as wall box is been pulled out. put wood between box and wall to hold in. jammed and cannot be pulled out as we tested plug in and out 50x job completed
MSA-DFES | WA6127431 | 1 | Anvil Doors | Engie room - Level 1 - Door 3 Spring broken | Building | Doors | 584 | Pass | Pass | 0 | 0 | 2 | 2022-10-26 07:22 | 2022-10-26 17:00 | 2022-10-26 09:00 | 2022-10-26 17:00 | 2022-10-26 11:00 |  |  | LH manual release bearing was shattered. Replaced both LH and RH bearings with new.
MSA-DTAG | WA6128413 | 1 | Codee Cleaning Services | BIO CLEAN CELL 3 - EXTREMELY BAD - RECOMMEND PROTECTIVE CLOTHING AND FACE MASK DUE TO SMELL | Cleaning | Emergency Cleans | 301.28 | Pass | Pass | 0 | 0 | 2 | 2022-10-26 16:19 | 2022-10-27 17:00 | 2022-10-26 18:00 | 2022-10-27 17:00 | 2022-10-26 20:00 |  |  | Completed
MSA-DTAG | WA6129413 | 3 | PPM Project Painting & Maintenance | Level 4 - public toilet - Graffiti on female toilet wall – St Georges Terrace end | Cleaning | Graffiti |  | Fail | Fail | 4 | 4 | 2 | 2022-10-27 14:45 | 2022-11-03 17:00 | 2022-12-01 07:00 | 2022-11-03 17:00 | 2022-12-01 09:00 |  |  | Removal of graffiti
MSA-DFES | WA6129813 | 3 | Go Doors | Level 1 - SOC/MOC - Auto door on level 1 door seal coming away need to be reattached or replaced | Building | Automatic Doors | 874.49 | Fail | Fail | 1 | 1 | 2 | 2022-10-28 07:49 | 2022-11-03 17:00 | 2022-11-08 09:00 | 2022-11-03 17:00 | 2022-11-08 11:00 |  |  | Completed 08/11
MSA-DTWD | WA6130177 | 2 | Water2water Pty Ltd | E58 Large Scale Kitchen - Ice Machine not producing ice | Refrigeration | Ice machine | 1767.55 | Pass | Pass | 0 | 0 | 2 | 2022-10-28 10:28 | 2022-11-02 17:00 | 2022-11-01 09:00 | 2022-11-02 17:00 | 2022-11-01 11:00 |  |  | Our external Ice Machine Technician attended on our behalf to complete repairs
MSA-DCA | WA6130309 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Francis St - Basement Lvl - Security Control room - Please see notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-10-28 11:15 | 2022-10-31 17:00 | 2022-10-28 16:00 | 2022-10-31 17:00 | 2022-10-28 18:00 |  |  | ATTENDED SITE. SIGNED IN, GAINED ACCESS. INVESTIGATED QUACKING NOISE COMING FROM SECURITY SERVER ROOM. FOUND NM-SBS-STN01 TO BE EMITTING THE NOISE. COMPUTER IS LINKEDTO THE LIFTS AND WAS ADVISED BY SECURITY THE EMERGENCY BUTTON WAS PRESSED RECENTLY. FOUND LIFT BMS IN ALARM, WAS ADVISED KONE ALREADY ATTENDED. RESET BMS, QUACKING NOISE STOPPED AND BMS IN NORMAL. COMPLETED PAPERWORK
MSA-DTWD | WA6130628 | 3 | COMMERCIAL PLUMBING AND GAS | AT04 Cleaners Store - RPZ leaking | Plumbing & Drainage | Water | 369.105 | Pass | Pass | -1 | -1 | 2 | 2022-10-28 13:21 | 2022-11-04 17:00 | 2022-10-30 09:00 | 2022-11-04 17:00 | 2022-10-30 11:00 |  |  | purged water main of air
MSA-DCA | WA6130678 | 2 | FCT SURFACE CLEANING | Gantry (Murray St side) - External Graffiti on gantry - See notes | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 2 | 2022-10-28 14:16 | 2022-11-02 17:00 | 2022-10-31 09:00 | 2022-11-02 17:00 | 2022-10-31 11:00 |  |  | Removal of graffiti
MSA-DTWD | WA6132540 | 2 | CONNECT SECURITY SYSTEMS | Faulty CCTV Camera | Security | CCTV Surveillance | 329.62 | Pass | Pass | 0 | 0 | 2 | 2022-10-31 15:09 | 2022-11-03 17:00 | 2022-11-01 09:20 | 2022-11-03 17:00 | 2022-11-01 11:20 |  |  | .
MSA-DTWD | WA6143809 | 2 | AHS Services WA Pty Ltd (Anchor) | A132 - Full flush is not working, half flush does work | Plumbing & Drainage | Water | 275.42 | Pass | Pass | 0 | 0 | 2 | 2022-11-01 15:24 | 2022-11-04 17:00 | 2022-11-02 09:00 | 2022-11-04 17:00 | 2022-11-02 11:00 |  |  | nil
MSA-DFES | WA6143817 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Front Transportable Toilets - Male Toilet - Exhaust fan has stopped working | Electrical | General Electrical | 401.185 | Pass | Pass | -1 | -1 | 2 | 2022-11-01 15:34 | 2022-11-08 17:00 | 2022-11-03 13:45 | 2022-11-08 17:00 | 2022-11-03 15:45 |  |  | Arrived on site at 1345 to attend faulty exhaust fan in male toilet transportable. Located transportable and located voltage atappliance. Left site at 1415 to pick up material from wholesaler. Returned back on site at 1500 and replaced faultyapplianced. Tested/ensured operation. Informed staff of works and left site at 1545
MSA-DCA | WA6147731 | 1 | Protek 24/7 Building & Maintenance | External door - Door damaged, is open and cannot be fully shut | Building | Doors | 357.24 | Pass | Pass | 0 | 0 | 2 | 2022-11-03 09:34 | 2022-11-04 17:00 | 2022-11-04 07:00 | 2022-11-04 17:00 | 2022-11-04 09:00 |  |  | Unable to locate door Please close off the breakdown and I will see if I can get further clarity. Kind regards Denise McCartney
MSA-DTAG | WA6147976 | 1 | Australian HVAC Services Pty. Ltd. | Landing between 1903 Building and 1987 Wing – near lift 4 - Sound of water - See notes | Air Conditioning | Cooling Tower | 353.9 | Pass | Pass | 0 | 0 | 2 | 2022-11-03 11:27 | 2022-11-04 17:00 | 2022-11-03 12:00 | 2022-11-04 17:00 | 2022-11-03 14:00 |  |  | Attend site. Liaise with staff and locate water noise. Found to be comming from ceiling. Further investigation found the chilled water piping to run through that section. Found noise to be air in pipework. This has been cause be the chilled water pipework change over to the portable chiller. Confirm chilled water make-up tank full, ok. Possible existing air bleeds not working correctly. There may have been too much air in the system from the portable hook up. Other contractors are looking into this.
MSA-DTAG | WA6148836 | 1 | Australian HVAC Services Pty. Ltd. | evaporative cooling - extremely warm - see note | Air Conditioning | Evaporative Coolers | 370.8 | Pass | Pass | 0 | 0 | 2 | 2022-11-04 09:34 | 2022-11-07 17:00 | 2022-11-04 10:00 | 2022-11-07 17:00 | 2022-11-04 12:00 |  |  | Attended service call, adjusted setpoints on vav's to summer settings to suit as ambient has changed .checked chiller operation ok
MSA-DCA | WA6149249 | 3 | Techworks Electrical | Fire panel-Issues with fire panel-see notes | Fire Protection Services | Fire Protection - Monitor System | 230.88 | Pass | Pass | 0 | 0 | 2 | 2022-11-04 13:28 | 2022-11-11 17:00 | 2022-11-09 12:00 | 2022-11-11 17:00 | 2022-11-09 14:00 |  |  | Attend site, sign in. -locate MSSB-1 panel. In conjunction with Alerton Technician, test 24AC relays and control circuits to determine source of faults. Cause of faults believed to be the AMPAC unit. -Alerton to prepare and send service report.
MSA-DTWD | WA6153655 | 1 | Water2water Pty Ltd | Hot water system is flushing and not working | Plumbing & Drainage | HWS/Units Electric & Gas | 844.23 | Pass | Pass | 0 | 0 | 2 | 2022-11-07 10:21 | 2022-11-08 17:00 | 2022-11-08 10:30 | 2022-11-08 17:00 | 2022-11-08 12:30 |  |  | Replaced Front LCD Screen & Filter. Re-Calibrated Hot Water Hot Pump Failed- Replaced Hot Pump & O'Rings, Normal Operation All okay on departure
MSA-DCA | WA6154652 | 2 | Earth & Water Pty Ltd | Ground Exterior - Courtyard to west of SLWA - Leaking retic at rear of carp park stairs | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2022-11-07 14:52 | 2022-11-10 17:00 | 2022-11-08 10:00 | 2022-11-10 17:00 | 2022-11-08 12:00 |  |  | repairs to retic
MSA-DCA | WA6155135 | 2 | Protek 24/7 Building & Maintenance | The door handle on the prompt side HLT stage access door is broken (almost falling | Building | Doors | 377.58 | Pass | Pass | 0 | 0 | 2 | 2022-11-08 08:16 | 2022-11-11 17:00 | 2022-11-08 12:00 | 2022-11-11 17:00 | 2022-11-08 14:00 |  |  | Replaced with new handle like for like
MSA-DTWD | WA6155633 | 3 | Equans Mechanical Services Australia | Outside B24 / South side of building - B16 - Change system from heating to cooling | Air Conditioning | Room Air Conditioners | 309.69 | Pass | Pass | -1 | -1 | 2 | 2022-11-08 11:56 | 2022-11-15 17:00 | 2022-11-08 13:00 | 2022-11-15 17:00 | 2022-11-08 15:00 |  |  | ATTENDED SITE, GAIN ACCESS TO B16 APAC AC. ADJUSTED THEMODE AND SET POINT. TESTED AC. ALL OK
MSA-DTAG | WA6156360 | 0 | Sapio Pty Ltd | Ground floor - Front card swipe automatic doors not working | Security | Access Control | 726.92 | Fail | Fail | 0 | 0 | 2 | 2022-11-09 07:23 | 2022-11-09 09:23 | 2022-11-09 10:00 | 2022-11-09 11:23 | 2022-11-09 12:00 |  |  | Replaced faulty power supply
MSA-DTWD | WA6156835 | 2 | AWB Co. | electrical Drop GPO has come away from ceiling mount | Electrical | Lighting, Internal | 242.14 | Pass | Pass | 0 | 0 | 2 | 2022-11-09 10:51 | 2022-11-14 17:00 | 2022-11-11 09:00 | 2022-11-14 17:00 | 2022-11-11 11:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located gpo, isolated circuit, got piece of wood and fixed ceiling rose to it, fixed jack chain, re energised circuit,tested gpo and working as intended, packed up, cleaned up,completed paperwork,signed out **job completed**
MSA-DTWD | WA6156974 | 3 | AWB Co. | Faulty Ethernet point (PP7-P7-18) | Electrical | General Electrical | 367.4 | Pass | Pass | 0 | 0 | 2 | 2022-11-09 11:45 | 2022-11-16 17:00 | 2022-11-14 13:00 | 2022-11-16 17:00 | 2022-11-14 15:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Located faulty switch mech. Found switch mech had been pushed in and was beyond repair. Replaced switch mech with new one. Tested data point. Took pics. Complete paperwork. Signed out.Job complete
MSA-DTWD | WA6159154 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet not flushing - A202 | Plumbing & Drainage | Toilets/Cisterns | 391.99 | Pass | Pass | 0 | 0 | 2 | 2022-11-10 12:17 | 2022-11-15 17:00 | 2022-11-15 13:30 | 2022-11-15 17:00 | 2022-11-15 15:30 |  |  | Completed
MSA-DTWD | WA6159330 | 2 | SCAVENGER SUPPLIES PTY LTD | EWIS Fire Speakers have a humming / static noise coming through | Fire Protection Services | Smoke and Heat Detection | 258.88 | Pass | Pass | -1 | -1 | 2 | 2022-11-10 14:17 | 2022-11-15 17:00 | 2022-11-11 12:00 | 2022-11-15 17:00 | 2022-11-11 14:00 |  | WACCES | Attended site to investigate a humming noise coming from the EWIS speakers in M Block. On arrival I tested the speaker with the P.A system and activating the Alert and EVAC alarms but the speakers worked great and the alarms and messages were loud and clear.The batteries in the EWIS were replaced due to them being 2 years out of date but did not effect or change the humming in the speakers.After further investigation I noticed the speakers only hum when the EWIS is in Automatic mode and not in Isolate, Public Address or Manual Evacuation mode.I tried turning off Mains power to see if the humming is still audible on battery power which it was but I also noticed the system doesn't indicate that it changes to battery power, the 'On Mains' light stays illuminated even when the system is on battery power and the voltage slowly drops. This may mean the system may not be changing to battery power when needed.Called Paul Wyllie and Brian Ryan for recommendations on what the problem could
MSA-DCA | WA6159376 | 1 | Techworks Plumbing | Multiple toilets faulty - see notes for details | Plumbing & Drainage | Water | 422.3 | Pass | Pass | 0 | 0 | 2 | 2022-11-10 14:49 | 2022-11-11 17:00 | 2022-11-11 08:30 | 2022-11-11 17:00 | 2022-11-11 10:30 |  |  | Attended site and signed in completed multiple toilet issues hacket hall male toilet (Broken toilet seat) turned out to be it was just loose we took it off and tightened it Hacket hall female toiletscubicle one - toilet was constantly running, flush valve was getting jammed and one of the Flexi hoses was leaking.we replaced the Flexi hose and greased up the flush valve all is working well now cubicle 2 - (broken toilet seat)toilet seat was loose we tightened basement toilet broken toilet seatwe removed toilet seat and replaced with a new roca toilet seat from the stock in plumbing cabinet signed out and completed paperwork
MSA-DTWD | WA6178210 | 1 | BOC | Simulated Hospital - Medical Gas in alarm | Plumbing & Drainage | Gas | 500 | Pass | Pass | 0 | 0 | 2 | 2022-11-14 09:57 | 2022-11-15 17:00 | 2022-11-14 13:30 | 2022-11-15 17:00 | 2022-11-14 15:30 |  |  | Attended to a callout for an alarming medical gas alarm panel.Medical gas alarm panel in an alarmed state due to the air compressor had suffered an unscheduled shutdown.Air compressor restarted and alarm cleared from the alarm panel.NOTE: Air compressor is running at 800kPa on a simulated medical supply system designed to operate at 420kPa. Recommendation is for air compressor and vacuum suction plant to be serviced and supply pressure to be reduced to 420kPa.
MSA-DFES | WA6204478 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 2 - Leaking cistern | Plumbing & Drainage | Toilets/Cisterns | 340.03 | Pass | Pass | -1 | -1 | 2 | 2022-11-17 09:08 | 2022-11-22 17:00 | 2022-11-17 10:30 | 2022-11-22 17:00 | 2022-11-17 12:30 |  |  | After replacing the inlet valve and the outlet washer everything is working correctly
MSA-DCA | WA6230233 | 1 | Techworks Plumbing | lower roof level - francis st building - syphonic drainage system is blocked | Plumbing & Drainage | Drainage | 230.86 | Pass | Pass | 0 | 0 | 2 | 2022-11-18 11:35 | 2022-11-21 17:00 | 2022-11-18 13:30 | 2022-11-21 17:00 | 2022-11-18 15:30 |  |  | Ross Bennett (18/11/2022) - Technician NoteAttended site and signed in spoke to Neil to get location of blocked box guttertried unblocking from roof but couldn’t get it to unblock spoke to Neil to find out where the syphonage pipes go to but he didn’t have exact location, he is going to raise a job for us to come and find where it is blocked and fix it signed out and left sitecompleted paperwork
MSA-DTWD | WA6231169 | 1 | JEM Carpentry | Flat A-broken roof tile | Roofing | Tiled Roofing |  | Pass | Pass | 0 | 0 | 2 | 2022-11-18 14:22 | 2022-11-21 17:00 | 2022-11-18 14:30 | 2022-11-21 17:00 | 2022-11-18 16:30 |  |  | Replaced broken tiles
MSA-DTWD | WA6248863 | 2 | AWB Co. | B2204, B2209 - 2 x Fluorescent units not switching on - tubes replaced cant locate starters | Electrical | Lighting, Internal | 242.14 | Pass | Pass | 0 | 0 | 2 | 2022-11-21 08:36 | 2022-11-24 17:00 | 2022-11-23 10:30 | 2022-11-24 17:00 | 2022-11-23 12:30 |  |  | Attended site signed in jsa completed. Found 4 faulty tubes. Replaced with tubes from site. Found faulty t8 to t5 converters. Replaced with ones on site and tested operational.Job completed
MSA-DTWD | WA6249697 | 3 | AWB Co. | Light switch worn and crackling. | Electrical | Lighting, Internal | 399.9 | Pass | Pass | -1 | -1 | 2 | 2022-11-21 13:56 | 2022-11-28 17:00 | 2022-11-22 13:00 | 2022-11-28 17:00 | 2022-11-22 15:00 |  |  | Attended site signed in jsa completed. Found crackling switch in class. Replaced with two new 20a mechs.lights operational nowJob complete
MSA-DTWD | WA6253853 | 2 | Techworks Plumbing | Female toilets hand basin tap is leaking enable to shout the water | Plumbing & Drainage | Water | 237.05 | Pass | Pass | 0 | 0 | 2 | 2022-11-22 12:39 | 2022-11-25 17:00 | 2022-11-23 09:00 | 2022-11-25 17:00 | 2022-11-23 11:00 |  |  | Repaired leaking basin
MSA-DTAG | WA6253863 | 2 | Midolo Building Services | Level 15 - Staff kitchen - Door closer is leaking | Building | Doors | 757.44 | Fail | Fail | 1 | 1 | 2 | 2022-11-22 12:45 | 2022-11-25 17:00 | 2022-11-30 08:30 | 2022-11-25 17:00 | 2022-11-30 10:30 |  |  | new closer installed to door
MSA-DTWD | WA6255836 | 3 | AWB Co. | room - 1G27 - light fitting making loud buzzing sound. | Electrical | Lighting, Internal | 596.15 | Fail | Fail | 0 | 0 | 2 | 2022-11-23 14:25 | 2022-11-30 17:00 | 2022-12-01 07:00 | 2022-11-30 17:00 | 2022-12-01 09:00 |  |  | Attended site signed in jsa completed. Removed two lights in office. Replaced with surface mount kits with led panels.Tested operational.Job completed
MSA-DCA | WA6258437 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Labs to cold-Equans on site | Air Conditioning | Room Air Conditioners | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-11-25 12:13 | 2022-11-28 17:00 | 2022-11-25 13:00 | 2022-11-28 17:00 | 2022-11-25 15:00 |  |  | Travelled to site and checked temps in all labs and compared to bms temps to ensure sensors not out of calibration. Also took actual temps from all labs to ensure all working OK. Spoke to Allerton controls to verify lab temps are all good. Also advised Sue Murray on works carried out.
MSA-DCA | WA6291288 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 in fault | Refrigeration | Chiller | 382.89 | Pass | Pass | 0 | 0 | 2 | 2022-11-28 13:36 | 2022-11-28 15:36 | 2022-11-28 15:00 | 2022-11-28 17:36 | 2022-11-28 17:00 |  |  | ATTENDED SITE. INVESTIGATED FAULTS WITH CHILLER. ACCESSED ROOF AND CHECKED OVER CHILLERS. FOUND ONE STAGE ISOLATED ON CHILLER 1 DUE TO KNOWN FAULT, PENDING WORKS. CHECKED OVER CHILLER 2 FOUND A STAGE HAD FAULTED ON HP. RESET AND TESTED OPERATION, ALL OK. CHECKED OVER BMS FAULTS CLEARED ON CHILLER 2, CHILLER 1 REMAINS IN FAULT. COMPLETED PAPERWORK.
MSA-DTAG | WA6292898 | 3 | Dom's Total Grounds Maintenance | outside garden-Garden Bed near ramp to car park-Broken retic pipe splashing out water | Landscaping & Gardening | Grounds Maintenance | 326 | Fail | Fail | 1 | 1 | 2 | 2022-11-29 14:10 | 2022-12-06 17:00 | 2022-12-16 07:00 | 2022-12-06 17:00 | 2022-12-16 09:00 |  |  | Call Out, Labour & Supply Retic Parts
MSA-DCA | WA6292915 | 3 | FCT SURFACE CLEANING | Exterior Roe St Side - Graffiti on side of building | Painting | External |  | Pass | Pass | 0 | 0 | 2 | 2022-11-29 14:26 | 2022-12-06 17:00 | 2022-12-05 08:30 | 2022-12-06 17:00 | 2022-12-05 10:30 |  |  | Removal of graffiti
MSA-DTWD | WA6298892 | 2 | AWB Co. | R0019 - Faulty contactor - Electrical box constantly buzzing | Electrical | Distribution Board | 312.74 | Pass | Pass | 0 | 0 | 2 | 2022-12-01 14:40 | 2022-12-06 17:00 | 2022-12-06 07:00 | 2022-12-06 17:00 | 2022-12-06 09:00 |  |  | Attended site, signed in , completed jsa, spoke with fm about job, located Contactor, switched on and found it to be emitting a loud buzzing sound, isolated Contactor, removed cover and took details of Contactor, went to wholesaler and picked up parts, returned to site, isolated circuit and removed old Contactor, replaced with new, re energised circuit and tested lighting, everything working as intended, packed up, cleaned up, completed paperwork,signed out, **job completed**
MSA-DFES | WA6301079 | 1 | Australian HVAC Services Pty. Ltd. | RETROSPECTIVE WORK ORDER - Kitchen - Platoon Food Fridge not working - (See notes) | Air Conditioning | Evaporative Coolers | 246.92 | Pass | Pass | 0 | 0 | 2 | 2022-12-01 11:24 | 2022-12-02 17:00 | 2022-12-02 10:30 | 2022-12-02 17:00 | 2022-12-02 12:30 | 1 |  | Oscar Holil (02/12/2022) - Work NoteArrived on site and spoke to site representative about the issue with the fridge. Current station personnel don't know about the issue but showed me where the fridge in question is. Cabinet temp currently is 2°C and the compressor has cycled off. Checked the setpoint and found out it was 2°C which is good. Opened up the unit and tested the system. Found that the fridge cycles on at 4°C and cycles off at 2°C which is good. Station personnel came back after calling the one who flagged the issue and notified me that the issue was already resolved by another technician. Reassemble the unit and packed up.
MSA-DTWD | WA6357607 | 0 | Critical Fire Protection & Training | External Car Park - Fire Hydrant leaking (see notes) | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 572.37 | Pass | Pass | 0 | 0 | 2 | 2022-12-05 14:35 | 2022-12-05 16:35 | 2022-12-05 15:00 | 2022-12-05 18:35 | 2022-12-05 17:00 |  |  | Attended site to investigate report of leaking hydrant in the carpark.Upon inspection we noted that the gauge had snapped out of top of booster sprayingwater.Shut off valve the valve.Took old snapped gauge out and installed new one.All okay on departure
MSA-DTWD | WA6358221 | 1 | Dormakaba Australia Pty Ltd | Auto door to cafe is staying open | Building | Automatic Doors | 379.88 | Pass | Pass | 0 | 0 | 2 | 2022-12-06 08:25 | 2022-12-07 17:00 | 2022-12-06 09:45 | 2022-12-07 17:00 | 2022-12-06 11:45 |  |  | Mode Switch Connection Board/ wire terminations corroded. Board/Wires replaced. Door/key switch function tested - PASSED. External key switch didn’t respond - wiring into terminal block corroded and rectified - PASSED
MSA-DFES | WA6359074 | 2 | Australian HVAC Services Pty. Ltd. | 12,6 - Ground and 1 - Down stairs training room and pool table - Air con not working in rooms | Air Conditioning | Room Air Conditioners | 139.94 | Pass | Pass | 0 | 0 | 2 | 2022-12-06 12:14 | 2022-12-09 17:00 | 2022-12-07 11:30 | 2022-12-09 17:00 | 2022-12-07 13:30 |  |  | Rhys Hall (07/12/2022) - Work NoteAttended site and investigated pool/game room ac. AC isn't working but a quote has already been submitted and waiting approval for the fix.The training room ac is working fine, I believe once the electrician returned yesterday, he must have turned the power off and then once the power was back on aircon is working correctly.
MSA-DTAG | WA6361479 | 1 | Sapio Pty Ltd | Cameras locked in position and need changing - C523-L5 & C117-L1 - see notes for locations | Security | CCTV Surveillance | 987.35 | Pass | Pass | 0 | 0 | 2 | 2022-12-08 10:12 | 2022-12-09 17:00 | 2022-12-08 14:30 | 2022-12-09 17:00 | 2022-12-08 16:30 |  |  | Work performed by Ken Moore (08/12/2022) Attended site, replaced Level 1 Patch Room Camera.Refocused and aligned Level 5 Corridor outside Patch Room's camera. All OK.Job completed.
MSA-MRWA | WA6361890 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Retrospective Work Order - Control room - Level 2 - Aircon not working. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-12-08 11:00 | 2022-12-09 17:00 | 2022-12-08 12:00 | 2022-12-09 17:00 | 2022-12-08 14:00 | 1 |  | Attended site, reset units and tested others in office meeting rooms. There had been a wide power surge the day before.
MSA-DCA | WA6361937 | 2 | Techworks Electrical | Ground Exterior - East of SLWA - Lighting is falling out from railing, please secure | Electrical | General Electrical | 230.88 | Pass | Pass | 0 | 0 | 2 | 2022-12-08 16:32 | 2022-12-13 17:00 | 2022-12-13 06:00 | 2022-12-13 17:00 | 2022-12-13 08:00 |  |  | Re secured led strip to handrail
MSA-DCA | WA6362220 | 2 | EQUANS Mechanical Services (WA) Pty Limited | steam unit faulty | Air Conditioning | Building HVAC Maintenance (Major Plant) | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-12-09 08:46 | 2022-12-14 17:00 | 2022-12-12 13:00 | 2022-12-14 17:00 | 2022-12-12 15:00 |  |  | TRAVELLED TO SITE AND SIGNED IN AT RECEPTION. CHECKED PLANT ROOM WHERE HUMIDIFIER WAS AND FOUND CL ERROR CODE ON INTERFACE OF HUMIDIFIER. TRACED INFORMATION TO COUNTER REQUIRES RESETTING AND UNIT REQUIRES DRAINING. RESETCOUNTER AND DRAINED OUT UNIT. ALSO CHECKED FOR LEAKS AND ANY CORROSION. REINSTATED POWER TO UNIT AND TESTED OPERATION. WAITED UNTIL UNIT FILLED UP AND COMMENCED HUMIDIFICATION PROCESS. ALL SEEMS TO WORKING OK AT THIS TIME. NO FURTHER FAULT CODES FOUND. ADVISED PEY-SUE OF WORKS CARRIED OUT.
MSA-DCA | WA6362310 | 1 | EQUANS Mechanical Services (WA) Pty Limited | No air coming from air conditioning grills | Air Conditioning | Ducted Split System | 259.01 | Pass | Pass | 0 | 0 | 2 | 2022-12-09 09:32 | 2022-12-12 17:00 | 2022-12-09 11:30 | 2022-12-12 17:00 | 2022-12-09 13:30 |  |  | Investigated airflow issues in the link way connecting the main gallery to the administration building. Checked over mechanical drawings and found 2x diffusers added onto ahu 1 to feed the linkway. No sensors are located in the linkway and is controlled by the gallery, no cooling is required as ahu is maintaining required setpoint. Completed paperwork.
MSA-DTAG | WA6364205 | 2 | Sapio Pty Ltd | Custody Roller Door - Computer unable to open roller door | Building | Automatic Doors | 269 | Pass | Pass | 0 | 0 | 2 | 2022-12-12 10:12 | 2022-12-15 17:00 | 2022-12-14 07:30 | 2022-12-15 17:00 | 2022-12-14 09:30 |  |  | Work performed by Ryan Craven (14/12/2022)Checked Gallagher programming for Custody Roller Door. Computer is communicating with door. Need a gate technicianto go out and have a look.Job completed.
MSA-DTWD | WA6364306 | 0 | AHS Services WA Pty Ltd (Anchor) | ground east-hot water isolation top to water ceased | Plumbing & Drainage | Water | 311.83 | Pass | Pass | 0 | 0 | 2 | 2022-12-12 10:57 | 2022-12-12 12:57 | 2022-12-12 12:00 | 2022-12-12 14:57 | 2022-12-12 14:00 |  |  | Completed
MSA-DTAG | WA6365722 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Court 6 - Aircon not working correctly. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 246.92 | Pass | Pass | 0 | 0 | 2 | 2022-12-13 11:51 | 2022-12-14 17:00 | 2022-12-13 13:00 | 2022-12-14 17:00 | 2022-12-13 15:00 |  |  | Attend site. Access security and sign in. Access court 6 plantroom and check operation of AC unit. Found indoor fan running but not cooling. Access electrical and check all safety controls. Trace wiring and found cooling call locked out. Found interlock holding off cooling. Trace back to switchboard and found condenser water pump switched of on the electrical panel. Turn pump on and found unit to start cooling. Test operation of unit and found to be working as normal.
MSA-DTAG | WA6373551 | 2 | EASTERN HILLS ELECTRICAL SERVICE | Ground Floor - Various Lighting faults - see notes below | Electrical | Lighting, Internal | 401.51 | Pass | Pass | -1 | -1 | 2 | 2022-12-14 15:23 | 2022-12-19 17:00 | 2022-12-15 07:30 | 2022-12-19 17:00 | 2022-12-15 09:30 |  |  | replaced 3x lights with LED fittings
MSA-DTWD | WA6376281 | 1 | Damian Rak Electrical Pty Ltd | Tool shed - No power | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2022-12-15 13:15 | 2022-12-16 17:00 | 2022-12-16 13:00 | 2022-12-16 17:00 | 2022-12-16 15:00 |  |  | Isolate, test, tag
MSA-MRWA | WA6377330 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Investigate burnt out smell from AC in room 509 | Air Conditioning | Room Air Conditioners | 259.01 | Pass | Pass | -1 | -1 | 2 | 2022-12-16 13:07 | 2022-12-21 17:00 | 2022-12-16 13:30 | 2022-12-21 17:00 | 2022-12-16 15:30 |  |  | Attended site, found room 509 smelt of smoke. Traced smell to indoor fan motor. Tested found down to earth. Will quote to replaced.
MSA-DCA | WA6378868 | 0 | Assa Abloy Entrance Systems Aust P/L-WA | Main Front Door - Revolving door - door isn't working correctly | Building | Automatic Doors | 501 | Fail | Fail | 0 | 0 | 2 | 2022-12-19 08:14 | 2022-12-19 10:14 | 2022-12-20 10:30 | 2022-12-19 12:14 | 2022-12-20 12:30 |  |  | Door not revolving. Problem traced to internal sliding door jammed due to damage to lower guides, likely from impact damage by pedestrian.Straightened guides and fault could be cleared.
MSA-DTWD | WA6380898 | 2 | AWB Co. | Whiteboard has come away from Brick wall | Building | Internal Walls | 247.96 | Pass | Pass | 0 | 0 | 2 | 2022-12-19 12:22 | 2022-12-22 17:00 | 2022-12-20 13:30 | 2022-12-22 17:00 | 2022-12-20 15:30 |  |  | Remove old fixings from brick wall.Repositioned and refix whiteboard back on to wall.Cleaned up work area.Job Complete
MSA-DTAG | WA6390639 | 1 | Australian HVAC Services Pty. Ltd. | Water is leaking from the aircon unit in the bail room onto the carpet. - see note | Air Conditioning | Room Air Conditioners | 545.44 | Pass | Pass | 0 | 0 | 2 | 2022-12-22 11:12 | 2022-12-23 17:00 | 2022-12-23 10:00 | 2022-12-23 17:00 | 2022-12-23 12:00 |  |  | Oscar Holil (23/12/2022) - Work NoteGained access to the basement and spoke to security about the issue with the AC. Found out there was large amounts of water leaking from the bail room AC. Gained access to the bail room and found that the carpet was wet. Removed the pipe cover and found the float and condensate pump, water was leaking out the breather port from the float assembly. Although the condensate pump is working, it seems that it is unable to keep up with the water flow. Concluded that the condensate pump should be replaced with an updated version (currently a EE600 rated for 4L/hr). Travelled to supplier and obtained a EE1000 (rated for 10L/hr). Arrived back on site and replaced the condensate pump. Tested operation and found it seems to be operating good. Packed up and left site.
MSA-DCA | WA6393421 | 3 | Protek 24/7 Building & Maintenance | Plant Room hatch requires securing back into place. | Building | Ceiling | 232.07 | Pass | Pass | 0 | 0 | 2 | 2022-12-28 13:56 | 2023-01-05 17:00 | 2023-01-03 07:45 | 2023-01-05 17:00 | 2023-01-03 09:45
MSA-DCA | WA6402720 | 2 | Techworks Plumbing | Francis Street - level 2 - UAT Bathroom - cistern flush button cover plate damaged | Plumbing & Drainage | Toilets/Cisterns | 544.81 | Pass | Pass | 0 | 0 | 2 | 2023-01-05 15:35 | 2023-01-10 17:00 | 2023-01-10 12:00 | 2023-01-10 17:00 | 2023-01-10 14:00
MSA-DTAG | WA6402724 | 2 | Sapio Pty Ltd | Ground - Ground - Roller Door - Door not working properly - See Notes Below | Building | Doors | 269 | Fail | Fail | 1 | 1 | 2 | 2023-01-05 16:03 | 2023-01-10 17:00 | 2023-01-17 08:30 | 2023-01-10 17:00 | 2023-01-17 10:30
MSA-DTWD | WA6407408 | 2 | Techworks Electrical | A016, A021 - Re-fit damaged electrical skirting ducting cover plates | Electrical | Distribution Board | 230.88 | Pass | Pass | 0 | 0 | 2 | 2023-01-10 08:37 | 2023-01-13 17:00 | 2023-01-13 10:30 | 2023-01-13 17:00 | 2023-01-13 12:30
MSA-DTWD | WA6408146 | 2 | Icon Logic Pty Ltd | Room H12 - Aircon schedule not operating | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 2 | 2023-01-10 15:20 | 2023-01-13 17:00 | 2023-01-12 07:00 | 2023-01-13 17:00 | 2023-01-12 09:00
MSA-DTWD | WA6414892 | 3 | Equans Mechanical Services Australia | Wall mounted air con is leaking water whilst in use. | Air Conditioning | Room Air Conditioners | 399.78 | Pass | Pass | -1 | -1 | 2 | 2023-01-11 10:46 | 2023-01-18 17:00 | 2023-01-12 10:00 | 2023-01-18 17:00 | 2023-01-12 12:00
MSA-DTWD | WA6426093 | 3 | AWB Co. | Faulty sliders for white boards in A317 & A318 - see notes | Building | Internal Walls | 297.5175 | Pass | Pass | 0 | 0 | 2 | 2023-01-12 14:24 | 2023-01-19 17:00 | 2023-01-18 13:30 | 2023-01-19 17:00 | 2023-01-18 15:30
MSA-DTWD | WA6430893 | 3 | AWB Co. | GPO in canteen cracked, near cash registers. | Electrical | General Electrical | 417.4 | Pass | Pass | -1 | -1 | 2 | 2023-01-13 10:00 | 2023-01-20 17:00 | 2023-01-13 13:30 | 2023-01-20 17:00 | 2023-01-13 15:30
MSA-DTWD | WA6467775 | 3 | Equans Mechanical Services Australia | West End Air Con - Return air dampener in AC not opening, West end staff area | Air Conditioning | Building HVAC Maintenance (Major Plant) | 309.69 | Fail | Fail | 0 | 0 | 2 | 2023-01-17 15:30 | 2023-01-24 17:00 | 2023-01-25 13:30 | 2023-01-24 17:00 | 2023-01-25 15:30
MSA-DTWD | WA6482258 | 3 | AWB Co. | light tubes not working Laboratory operations A Block Level 3 | Electrical | Lighting, Internal | 402.42 | Pass | Pass | 0 | 0 | 2 | 2023-01-18 08:32 | 2023-01-25 17:00 | 2023-01-25 12:00 | 2023-01-25 17:00 | 2023-01-25 14:00
MSA-DTWD | WA6488124 | 2 | AWB Co. | Annex area- pedestal grinder not working | Equipment | Power Tools | 363 | Pass | Pass | -1 | -1 | 2 | 2023-01-18 14:17 | 2023-01-23 17:00 | 2023-01-19 13:00 | 2023-01-23 17:00 | 2023-01-19 15:00
MSA-DTWD | WA6493218 | 1 | Equans Mechanical Services Australia | Fault description Top of freezer in cafeteria has water leak - causing freezer to ice up | Refrigeration | Freezers | 219.6 | Pass | Pass | 0 | 0 | 2 | 2023-01-18 15:39 | 2023-01-19 17:00 | 2023-01-19 12:00 | 2023-01-19 17:00 | 2023-01-19 14:00
MSA-DTWD | WA6503876 | 2 | Techworks Electrical | range hood light not working | Electrical | General Electrical | 446.74 | Pass | Pass | 0 | 0 | 2 | 2023-01-19 11:57 | 2023-01-24 17:00 | 2023-01-23 10:00 | 2023-01-24 17:00 | 2023-01-23 12:00
MSA-DCA | WA6503922 | 1 | EQUANS Mechanical Services (WA) Pty Limited | SLWA - Level 5 - Plant Room - Chiller 4 in Fault again (Third time this week) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 451.79 | Fail | Fail | 1 | 1 | 2 | 2023-01-19 12:19 | 2023-01-20 17:00 | 2023-01-24 14:30 | 2023-01-20 17:00 | 2023-01-24 16:30
MSA-DTWD | WA6509290 | 3 | M Construction (WA) | Hallway- carpet tile is loose | Flooring | Carpet | 292.48 | Pass | Pass | -1 | -1 | 2 | 2023-01-20 09:26 | 2023-01-30 17:00 | 2023-01-20 11:30 | 2023-01-30 17:00 | 2023-01-20 13:30
MSA-DTWD | WA6509638 | 2 | AHS Services WA Pty Ltd (Anchor) | Leaking vanity tap | Plumbing & Drainage | Drainage | 506 | Pass | Pass | 0 | 0 | 2 | 2023-01-20 12:59 | 2023-01-25 17:00 | 2023-01-24 10:30 | 2023-01-25 17:00 | 2023-01-24 12:30
MSA-DFES | WA6509768 | 2 | Dom's Total Grounds Maintenance | Removal of vegetation from septic tank area | Landscaping & Gardening | Grounds Maintenance | 800 | Fail | Fail | 0 | 0 | 2 | 2023-01-20 15:06 | 2023-01-25 17:00 | 2023-01-28 09:00 | 2023-01-25 17:00 | 2023-01-28 11:00
MSA-DTWD | WA6516311 | 2 | AWB Co. | F Block - Heavy fabrication - Welding bays 28 to 35 - No single phase | Electrical | Distribution Board | 242.14 | Pass | Pass | 0 | 0 | 2 | 2023-01-23 10:34 | 2023-01-27 17:00 | 2023-01-24 09:15 | 2023-01-27 17:00 | 2023-01-24 11:15
MSA-DTAG | WA6516851 | 1 | Australian HVAC Services Pty. Ltd. | Level 4 - Custody area - Air con doesn’t seem to be working | Air Conditioning | Ducted Split System | 213.96 | Pass | Pass | 0 | 0 | 2 | 2023-01-23 16:18 | 2023-01-24 17:00 | 2023-01-24 10:00 | 2023-01-24 17:00 | 2023-01-24 12:00
MSA-DTWD | WA6518601 | 1 | AWB Co. | Faulty Fluro light - see notes | Electrical | Lighting, Internal | 363 | Pass | Pass | 0 | 0 | 2 | 2023-01-25 09:32 | 2023-01-27 17:00 | 2023-01-25 10:30 | 2023-01-27 17:00 | 2023-01-25 12:30
MSA-DTWD | WA6520975 | 0 | AWB Co. | has lost all power | Electrical | General Electrical | 242.14 | Pass | Pass | 0 | 0 | 2 | 2023-01-30 07:07 | 2023-01-30 09:07 | 2023-01-30 08:15 | 2023-01-30 11:07 | 2023-01-30 10:15
MSA-DCA | WA6521315 | 1 | GPS Plumbing & Gas Services PtyLtd | North Foyer - Ladies Toilet - Full Flush not working | Plumbing & Drainage | Toilets/Cisterns | 689 | Pass | Pass | 0 | 0 | 2 | 2023-01-30 09:54 | 2023-01-31 17:00 | 2023-01-31 13:45 | 2023-01-31 17:00 | 2023-01-31 15:45
MSA-DTWD | WA6522896 | 2 | Equans Mechanical Services Australia | Office does not have any airflow | Air Conditioning | Room Air Conditioners | 243.35 | Pass | Pass | 0 | 0 | 2 | 2023-01-31 10:53 | 2023-02-03 17:00 | 2023-02-02 07:00 | 2023-02-03 17:00 | 2023-02-02 09:00 |  | WCAPPR
MSA-DTWD | WA6523421 | 1 | Equans Mechanical Services Australia | Room F42 - Evap aircon not cooling | Air Conditioning | Evaporative Coolers | 399.78 | Pass | Pass | 0 | 0 | 2 | 2023-01-31 15:44 | 2023-02-01 17:00 | 2023-02-01 10:00 | 2023-02-01 17:00 | 2023-02-01 12:00
MSA-DTWD | WA6523447 | 2 | AWB Co. | Rectify switch board issues | Electrical | General Electrical | 285.45 | Pass | Pass | 0 | 0 | 2 | 2023-01-31 16:31 | 2023-02-03 17:00 | 2023-02-02 12:00 | 2023-02-03 17:00 | 2023-02-02 14:00
MSA-DTWD | WA6526898 | 1 | Equans Mechanical Services Australia | Chiller not working – cannot reset – multiple Alarms | Air Conditioning | Building HVAC Maintenance (Major Plant) | 219.6 | Pass | Pass | 0 | 0 | 2 | 2023-02-01 11:45 | 2023-02-02 17:00 | 2023-02-01 13:30 | 2023-02-02 17:00 | 2023-02-01 15:30
MSA-DCA | WA6527294 | 2 | Techworks Electrical | Level 2 - Shower room - Emergency Exit light dim | Electrical | Emergency & Exit Lighting | 236.27 | Pass | Pass | 0 | 0 | 2 | 2023-02-01 15:41 | 2023-02-06 17:00 | 2023-02-03 06:00 | 2023-02-06 17:00 | 2023-02-03 08:00
MSA-DFES | WA6527650 | 1 | Critical Fire Protection & Training | Sprinkler Room - Fire alarm fault | Fire Protection Services | Fire Protection - Monitor System | 221.28 | Pass | Pass | 0 | 0 | 2 | 2023-02-02 04:04 | 2023-02-02 17:00 | 2023-02-02 12:00 | 2023-02-02 17:00 | 2023-02-02 14:00
MSA-DFES | WA6527988 | 3 | AWB Co. | ground kitchen-Broken handle on kitchen drawer in island bench | Carpentry | Timber (all types) | 282.21 | Pass | Pass | 0 | 0 | 2 | 2023-02-02 08:07 | 2023-02-09 17:00 | 2023-02-07 13:00 | 2023-02-09 17:00 | 2023-02-07 15:00
MSA-DTWD | WA6528205 | 2 | AWB Co. | Loose GPO on wall | Electrical | General Electrical | 279.14 | Pass | Pass | 0 | 0 | 2 | 2023-02-02 09:37 | 2023-02-07 17:00 | 2023-02-07 08:30 | 2023-02-07 17:00 | 2023-02-07 10:30
MSA-DTWD | WA6529114 | 2 | AWB Co. | No power to security gate | Electrical | General Electrical | 242.14 | Pass | Pass | 0 | 0 | 2 | 2023-02-02 14:47 | 2023-02-07 17:00 | 2023-02-06 10:00 | 2023-02-07 17:00 | 2023-02-06 12:00
MSA-DCA | WA6530991 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Basement - Studio Theatre - Fault - Temp not lowering (See notes) | Air Conditioning | Building HVAC Maintenance (Major Plant) | 360.37 | Pass | Pass | 0 | 0 | 2 | 2023-02-03 08:07 | 2023-02-06 17:00 | 2023-02-03 10:00 | 2023-02-06 17:00 | 2023-02-03 12:00
MSA-DTWD | WA6531470 | 1 | Australian Airconditioning Services Pty Ltd | B2417 Fashion Staff Room - Office AC is not cooling effectively | Air Conditioning | Room Air Conditioners | 425.02 | Pass | Pass | 0 | 0 | 2 | 2023-02-03 12:06 | 2023-02-06 17:00 | 2023-02-06 09:00 | 2023-02-06 17:00 | 2023-02-06 11:00
MSA-DCA | WA6533218 | 0 | Dormakaba Australia Pty Ltd | Glass sliding door not working | Building | Doors |  | Fail | Fail | 0 | 0 | 2 | 2023-02-04 14:26 | 2023-02-04 16:26 | 2023-02-06 13:00 | 2023-02-04 18:26 | 2023-02-06 15:00
MSA-DFES | WA6534172 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room-ground-Exhaust Fan above 1st Pump not working in Auto | Electrical | General Electrical | 241.44 | Pass | Pass | 0 | 0 | 2 | 2023-02-06 10:00 | 2023-02-09 17:00 | 2023-02-06 14:30 | 2023-02-09 17:00 | 2023-02-06 16:30
MSA-DTWD | WA6535127 | 2 | Australian Airconditioning Services Pty Ltd | Wall mount split AC - unit condensation down the wall | Air Conditioning | Room Air Conditioners | 400.84 | Pass | Pass | 0 | 0 | 2 | 2023-02-06 14:33 | 2023-02-09 17:00 | 2023-02-08 13:30 | 2023-02-09 17:00 | 2023-02-08 15:30
MSA-DFES | WA6538152 | 3 | AWB Co. | Main building - ground floor - room 17 - Door frame in passage way has come detached from the brick | Building | Doors | 228.49 | Pass | Pass | -1 | -1 | 2 | 2023-02-07 15:18 | 2023-02-14 17:00 | 2023-02-10 07:00 | 2023-02-14 17:00 | 2023-02-10 09:00
MSA-DTWD | WA6538182 | 2 | Water2water Pty Ltd | ET17.1 - BWU on wall not always heating (see notes) | Plumbing & Drainage | HWS/Units Electric & Gas | 2059.32 | Fail | Fail | 4 | 4 | 2 | 2023-02-07 15:46 | 2023-02-10 17:00 | 2023-03-08 10:30 | 2023-02-10 17:00 | 2023-03-08 12:30
MSA-DTWD | WA6539528 | 2 | Precise Air Group | Fridge compressor not starting up | Refrigeration | Refrigerators | 253.38 | Pass | Pass | -1 | -1 | 2 | 2023-02-08 13:47 | 2023-02-13 17:00 | 2023-02-09 12:00 | 2023-02-13 17:00 | 2023-02-09 14:00
MSA-DCA | WA6539611 | 1 | GPS Plumbing & Gas Services PtyLtd | Upper Car Park - Pin hole leak in sewer pipe under foyer toilets (see notes) | Plumbing & Drainage | Sewage Treatment Plant | 463.57 | Pass | Pass | 0 | 0 | 2 | 2023-02-08 14:35 | 2023-02-09 17:00 | 2023-02-09 07:30 | 2023-02-09 17:00 | 2023-02-09 09:30
MSA-DTWD | WA6540450 | 2 | Protek 24/7 Building & Maintenance | Top of door jamming on lintel | Building | Doors | 216.39 | Pass | Pass | 0 | 0 | 2 | 2023-02-09 11:04 | 2023-02-14 17:00 | 2023-02-14 11:30 | 2023-02-14 17:00 | 2023-02-14 13:30
MSA-DTWD | WA6540566 | 2 | Precise Air Group | Restaurant Female toilets has a broken extraction vent cover | Air Conditioning | Materials | 489.12 | Fail | Fail | 1 | 1 | 2 | 2023-02-09 11:51 | 2023-02-14 17:00 | 2023-02-20 07:00 | 2023-02-14 17:00 | 2023-02-20 09:00
MSA-DTWD | WA6540661 | 2 | COMMERCIAL PLUMBING AND GAS | Level 3 - North lift foyer - W2W did attend premises but advised plumber is needed | Plumbing & Drainage | Drainage | 243.97 | Pass | Pass | -1 | -1 | 2 | 2023-02-09 12:29 | 2023-02-14 17:00 | 2023-02-10 13:00 | 2023-02-14 17:00 | 2023-02-10 15:00
MSA-DTWD | WA6544462 | 2 | Techworks Electrical | Emergency exit sign behind double glass doors has fallen and | Electrical | Emergency & Exit Lighting | 408.7 | Pass | Pass | 0 | 0 | 2 | 2023-02-10 13:04 | 2023-02-15 17:00 | 2023-02-15 07:30 | 2023-02-15 17:00 | 2023-02-15 09:30
MSA-DTWD | WA6544508 | 2 | AWB Co. | Replace flicking lights in B208 and photocopy room | Electrical | Lighting, Internal | 303.03 | Pass | Pass | 0 | 0 | 2 | 2023-02-10 13:18 | 2023-02-15 17:00 | 2023-02-13 07:00 | 2023-02-15 17:00 | 2023-02-13 09:00
MSA-DTWD | WA6585685 | 3 | AWB Co. | N122 - Metal gate - dragging on concrete | Building | Steel Fencing & Gates | 225.96 | Pass | Pass | -1 | -1 | 2 | 2023-02-16 09:58 | 2023-02-23 17:00 | 2023-02-16 13:30 | 2023-02-23 17:00 | 2023-02-16 15:30
MSA-DCA | WA6585756 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main building - Ground floor - Conservation Area / cafe - Conservation area too cold / cafe too warm | Air Conditioning | Ducted Split System | 259.01 | Pass | Pass | 0 | 0 | 2 | 2023-02-16 10:36 | 2023-02-17 17:00 | 2023-02-16 11:30 | 2023-02-17 17:00 | 2023-02-16 13:30
MSA-DFES | WA6600693 | 1 | AWB Co. | Wellington Side - Replace - Emergency Vehicle Exit Sign | Signage | General Signage | 524.115 | Fail | Fail | 1 | 1 | 2 | 2023-02-17 09:46 | 2023-02-20 17:00 | 2023-02-24 11:30 | 2023-02-20 17:00 | 2023-02-24 13:30
MSA-DTWD | WA6601170 | 2 | AWB Co. | Balcony lights L1 L2 not coming on | Electrical | Lighting, External | 595.38 | Pass | Pass | 0 | 0 | 2 | 2023-02-17 10:12 | 2023-02-22 17:00 | 2023-02-22 07:00 | 2023-02-22 17:00 | 2023-02-22 09:00
MSA-DTWD | WA6601228 | 2 | AWB Co. | rear of Building - Lights out | Electrical | Lighting, External | 387.96 | Pass | Pass | 0 | 0 | 2 | 2023-02-17 10:14 | 2023-02-22 17:00 | 2023-02-22 09:00 | 2023-02-22 17:00 | 2023-02-22 11:00
MSA-DTWD | WA6602653 | 2 | AWB Co. | Driveway gate - Gate hinge fixings pulled from limestone wall (see notes) | Building | Steel Fencing & Gates | 324.96 | Fail | Fail | 0 | 0 | 2 | 2023-02-17 11:43 | 2023-02-22 17:00 | 2023-02-24 11:30 | 2023-02-22 17:00 | 2023-02-24 13:30
MSA-DTAG | WA6668735 | 1 | Midolo Building Services | Level 3 - Court 35 - Door is not closing correctly | Building | Doors | 246.37 | Pass | Pass | 0 | 0 | 2 | 2023-02-22 11:23 | 2023-02-23 17:00 | 2023-02-22 13:00 | 2023-02-23 17:00 | 2023-02-22 15:00
MSA-DTWD | WA6668852 | 2 | AHS Services WA Pty Ltd (Anchor) | Ground level - West block - W105 - Accessible Toilet cistern leaking into bowl, please repair. | Plumbing & Drainage | Toilets/Cisterns | 537.2 | Fail | Fail | 0 | 0 | 2 | 2023-02-22 12:00 | 2023-02-27 17:00 | 2023-03-02 07:00 | 2023-02-27 17:00 | 2023-03-02 09:00
MSA-DTAG | WA6671684 | 1 | Australian HVAC Services Pty. Ltd. | Plant room 7 (near court 8) - Water leaking due to blocked drain | Air Conditioning | Evaporative Coolers | 300.41 | Pass | Pass | 0 | 0 | 2 | 2023-02-23 09:56 | 2023-02-24 17:00 | 2023-02-23 10:00 | 2023-02-24 17:00 | 2023-02-23 12:00
MSA-DTWD | WA6672131 | 2 | AWB Co. | U011 - Fluro lights x2 out of order | Electrical | Lighting, Internal | 498 | Pass | Pass | 0 | 0 | 2 | 2023-02-23 13:02 | 2023-02-28 17:00 | 2023-02-27 13:00 | 2023-02-28 17:00 | 2023-02-27 15:00
MSA-DCA | WA6672289 | 0 | Techworks Electrical | Ground floor kitchen - Light panel - Not working | Electrical | General Electrical | 259.03 | Pass | Pass | 0 | 0 | 2 | 2023-02-23 14:29 | 2023-02-23 16:29 | 2023-02-23 15:00 | 2023-02-23 18:29 | 2023-02-23 17:00
MSA-DTWD | WA6673223 | 1 | AWB Co. | Disc/bobbin sander & Linisher sander - Machines tagged out, require rectification (see notes) | Electrical | General Electrical | 536.65 | Pass | Pass | 0 | 0 | 2 | 2023-02-24 11:57 | 2023-02-27 17:00 | 2023-02-27 08:30 | 2023-02-27 17:00 | 2023-02-27 10:30
MSA-DCA | WA6674211 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Exhaust fan 5 in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 281.53 | Pass | Pass | 0 | 0 | 2 | 2023-02-27 08:44 | 2023-02-27 10:44 | 2023-02-27 09:40 | 2023-02-27 12:44 | 2023-02-27 11:40
MSA-DTAG | WA6680448 | 3 | Australian HVAC Services Pty. Ltd. | Custody - ground - AC 2 wont stay on | Air Conditioning | Ducted Split System |  | Pass | Pass | -1 | -1 | 2 | 2023-03-01 11:24 | 2023-03-09 17:00 | 2023-03-03 07:30 | 2023-03-09 17:00 | 2023-03-03 09:30
MSA-DTWD | WA6680491 | 1 | AWB Co. | No power to computers . eastern wall of room | Electrical | General Electrical | 363 | Pass | Pass | 0 | 0 | 2 | 2023-03-01 11:48 | 2023-03-02 17:00 | 2023-03-02 07:45 | 2023-03-02 17:00 | 2023-03-02 09:45
MSA-DTWD | WA6680604 | 2 | Precise Air Group | Stores / demo kitchen - Blast Chillers are not running to temp | Air Conditioning | Evaporative Coolers | 253.38 | Pass | Pass | -1 | -1 | 2 | 2023-03-01 12:51 | 2023-03-07 17:00 | 2023-03-02 07:00 | 2023-03-07 17:00 | 2023-03-02 09:00
MSA-DTWD | WA6680881 | 2 | AHS Services WA Pty Ltd (Anchor) | Extenernal sink P trap perished and cracked through | Plumbing & Drainage | Drainage | 256.38 | Pass | Pass | 0 | 0 | 2 | 2023-03-01 15:51 | 2023-03-07 17:00 | 2023-03-07 13:00 | 2023-03-07 17:00 | 2023-03-07 15:00
MSA-DTWD | WA6681617 | 2 | Techworks Electrical | Q Block - Room Q103 - has a light not working | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 2 | 2023-03-02 10:24 | 2023-03-08 17:00 | 2023-03-08 10:00 | 2023-03-08 17:00 | 2023-03-08 12:00
MSA-DTWD | WA6683434 | 1 | Precise Air Group | FCU in fault AGAIN no aircon (see notes) | Air Conditioning | Ducted Split System | 1266.88 | Pass | Pass | 0 | 0 | 2 | 2023-03-03 08:55 | 2023-03-07 17:00 | 2023-03-07 07:00 | 2023-03-07 17:00 | 2023-03-07 09:00
MSA-DTAG | WA6683635 | 1 | Australian HVAC Services Pty. Ltd. | ground - Visiting Judge Area-air con to warm | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 2 | 2023-03-03 10:37 | 2023-03-07 17:00 | 2023-03-04 09:00 | 2023-03-07 17:00 | 2023-03-04 11:00
MSA-DTWD | WA6683976 | 2 | AWB Co. | Staff workroom over the eating area/table - Repair light | Electrical | General Electrical | 434.13 | Pass | Pass | 0 | 0 | 2 | 2023-03-03 14:45 | 2023-03-09 17:00 | 2023-03-08 10:30 | 2023-03-09 17:00 | 2023-03-08 12:30
MSA-DTWD | WA6688182 | 1 | COMMERCIAL PLUMBING AND GAS | Canteen Kitchen - Oven is making noise possibly the fan | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 2 | 2023-03-07 11:43 | 2023-03-08 17:00 | 2023-03-07 16:30 | 2023-03-08 17:00 | 2023-03-07 18:30
MSA-DTWD | WA6688394 | 1 | COMMERCIAL PLUMBING AND GAS | Suspected underground blockage causing water to overflow from floor wastes | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 2 | 2023-03-07 14:13 | 2023-03-08 17:00 | 2023-03-08 07:00 | 2023-03-08 17:00 | 2023-03-08 09:00
MSA-DTWD | WA6688978 | 2 | AWB Co. | 2 Fluro lights turned off at the same time | Electrical | Lighting, Internal | 351.94 | Pass | Pass | -1 | -1 | 2 | 2023-03-08 08:24 | 2023-03-13 17:00 | 2023-03-09 09:00 | 2023-03-13 17:00 | 2023-03-09 11:00
MSA-DTWD | WA6689720 | 1 | COMMERCIAL PLUMBING AND GAS | Toilet severely blocked-Will not flush due to blockage | Plumbing & Drainage | Toilets/Cisterns | 431.45 | Pass | Pass | 0 | 0 | 2 | 2023-03-08 14:35 | 2023-03-09 17:00 | 2023-03-08 15:00 | 2023-03-09 17:00 | 2023-03-08 17:00
MSA-DTWD | WA6690882 | 2 | AWB Co. | C1 Facilities Office - Test & Tag electrical item | Electrical | Testing & Tagging | 243.7 | Pass | Pass | 0 | 0 | 2 | 2023-03-09 13:18 | 2023-03-14 17:00 | 2023-03-13 09:00 | 2023-03-14 17:00 | 2023-03-13 11:00
MSA-DTWD | WA6690883 | 2 | AWB Co. | Faulty Light switch | Electrical | Lighting, Internal | 498.93 | Pass | Pass | 0 | 0 | 2 | 2023-03-09 13:22 | 2023-03-14 17:00 | 2023-03-13 07:00 | 2023-03-14 17:00 | 2023-03-13 09:00
MSA-DCA | WA6690926 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Level 4 - Humidifier In fault | Air Conditioning | Ducted Split System | 281.53 | Pass | Pass | 0 | 0 | 2 | 2023-03-09 14:06 | 2023-03-09 16:06 | 2023-03-09 16:00 | 2023-03-09 18:06 | 2023-03-09 18:00
MSA-DTAG | WA6693493 | 1 | AWB Co. | Ground - Lift 1 -Emergency light in lift 1 requires replacing (Electrician is on site) | Electrical | Lighting, Internal | 1 | Pass | Pass | 0 | 0 | 2 | 2023-03-10 10:51 | 2023-03-13 17:00 | 2023-03-10 11:30 | 2023-03-13 17:00 | 2023-03-10 13:30
MSA-DTWD | WA6721521 | 1 | Techworks Electrical | Exposed wires - see notes | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 2 | 2023-03-14 09:11 | 2023-03-15 17:00 | 2023-03-14 10:00 | 2023-03-15 17:00 | 2023-03-14 12:00
MSA-DCA | WA6721646 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Hackett Hall - Level 2 - Plant room 6 - AHU-05.01 - Noisy | Air Conditioning | Room Air Conditioners |  | Pass | Pass | 0 | 0 | 2 | 2023-03-14 10:35 | 2023-03-17 17:00 | 2023-03-15 12:00 | 2023-03-17 17:00 | 2023-03-15 14:00
MSA-DTWD | WA5112157 | 2 | Falcetta Plumbing and Gas | B1 - Level 4 - Blocked P trap causing leakage from main line | Plumbing & Drainage | Drainage | 258.84 | Pass | Pass | 0 | 0 | 1.9833 | 2022-02-10 13:55 | 2022-02-15 17:00 | 2022-02-15 15:00 | 2022-02-15 17:00 | 2022-02-15 16:59 |  |  | repaired basin and sink, adapted waste to connect
MSA-DTWD | WA6155621 | 2 | AWB Co. | Level 4 - A403 Staff Working Area - Light flickering | Electrical | Lighting, Internal | 224.21 | Pass | Pass | 0 | 0 | 1.9833 | 2022-11-08 11:47 | 2022-11-11 17:00 | 2022-11-11 13:30 | 2022-11-11 17:00 | 2022-11-11 15:29 |  |  | Attended site and signed in, completed JSA,spoke with receptionist and got keys, located faulty light, replaced tubes and starters, light now working as intended, completed paperwork,cleaned up,packed up, signed out**job complete**
MSA-DCA | WA6503878 | 1 | Critical Fire Protection & Training | FM200 Gas bottle to be connected | Fire Protection Services | Fire Protection - Monitor System | 866.68 | Pass | Pass | 0 | 0 | 1.9833 | 2023-01-19 11:55 | 2023-01-20 17:00 | 2023-01-20 12:30 | 2023-01-20 17:00 | 2023-01-20 14:29
MSA-DTWD | WA5380378 | 1 | SCAVENGER SUPPLIES PTY LTD | A Block - Fire panel - Evac system alarm ringing fault | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | -1 | -1 | 1.9667 | 2022-04-22 11:37 | 2022-04-26 17:00 | 2022-04-22 12:30 | 2022-04-26 17:00 | 2022-04-22 14:28 |  |  | Completion 22/04/2022
MSA-DTWD | WA5565540 | 1 | Dormakaba Australia Pty Ltd | 8G1 - auto door set to fine. Staff entering setting it off. Cover appears to have come off mechanism | Building | Automatic Doors | 619.84 | Pass | Pass | 0 | 0 | 1.9667 | 2022-06-22 08:23 | 2022-06-23 17:00 | 2022-06-22 12:12 | 2022-06-23 17:00 | 2022-06-22 14:10 |  |  | Adjusted internal head sensor and fitted 4 new wheels. Tested and inspected operation. Tested battery back up. Checked all fixings, sensors, floor guide, cleaned and lubricated where necessary. Door operating correctly.
MSA-DTWD | WA5692113 | 2 | AHS Services WA Pty Ltd (Anchor) | SK3 - E block SK3 leaking floor waste for sink second on the left hand side | Plumbing & Drainage | Water | 158.32 | Pass | Pass | 0 | 0 | 1.9667 | 2022-08-03 10:39 | 2022-08-08 17:00 | 2022-08-08 14:00 | 2022-08-08 17:00 | 2022-08-08 15:58 |  |  | Job completed
MSA-DTWD | WA5094231 | 1 | AHS Services WA Pty Ltd (Anchor) | B Block - Level 1 - hot tap running constantly | Plumbing & Drainage | Materials | 232.51 | Pass | Pass | 0 | 0 | 1.9667 | 2022-01-31 09:27 | 2022-02-01 17:00 | 2022-02-01 07:30 | 2022-02-01 17:00 | 2022-02-01 09:28 |  |  | Serviced taps in male bathroom lvl 3
MSA-DTWD | WA5472531 | 3 | AWB Co. | Centre Block - Level 3 - Fire escape stair - water leak from window | Building | Windows | 226.5 | Pass | Pass | -1 | -1 | 1.9667 | 2022-05-24 08:29 | 2022-05-31 17:00 | 2022-05-25 09:00 | 2022-05-31 17:00 | 2022-05-25 10:58 |  |  | ATTENDED SITEASSESSED LEAKING GLASS TO STAIRWELL(JOB CLOSED OFF AS ADVISED BY TANIA)
MSA-DCA | WA6539153 | 1 | Automatic Fire Protection (ARA) | Speakers - car park - not emitting sound clearly | Fire Protection Services | Fire Protection - Monitor System | 385.505 | Pass | Pass | 0 | 0 | 1.9667 | 2023-02-08 10:46 | 2023-02-08 12:46 | 2023-02-08 10:47 | 2023-02-08 14:46 | 2023-02-08 12:45
MSA-DTWD | WA5437347 | 0 | SCAVENGER SUPPLIES PTY LTD | Block T - Cafetaria - Fire alarm panel siren going off | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 1.95 | 2022-05-16 07:33 | 2022-05-16 09:33 | 2022-05-16 07:33 | 2022-05-16 11:33 | 2022-05-16 09:30 |  |  | completed 16/5/22 - Please be advised that work was completed on the 16/5/22 as per schedule finish and noted in Signature slip. As we have been experiencing technical issues with our access to Promap (we have advised Promap assist of this and they have advised other vendors are also experiencing issues) the claim was not able to be lodged yesterday. Thank you for your understanding. Regards.
MSA-DTWD | WA5494468 | 0 | Techworks Plumbing | hot water tap is leaking and unable to isolate | Plumbing & Drainage | Water | 398.66 | Pass | Pass | 0 | 0 | 1.95 | 2022-06-07 15:33 | 2022-06-07 17:33 | 2022-06-07 15:33 | 2022-06-07 19:33 | 2022-06-07 17:30 |  |  | Hot tap rubbers worn down too much to isolate. Serviced tap and replaced all rubbers. Tap shutting off now
MSA-DCA | WA6389851 | 1 | TK Elevator Australia Pty Ltd | Foyer - Lift 2 -Light are flashing inside the lift | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.95 | 2022-12-21 18:52 | 2022-12-22 17:00 | 2022-12-22 07:00 | 2022-12-22 17:00 | 2022-12-22 08:57 |  |  | Emergency lighting unit faulty (el50) component obsolete. Lift requires emergency lighting upgrade. Lift left on fire service, out of service docket left on car light and power circuit breaker.
MSA-MRWA | WA5460350 | 1 | Dormakaba Australia Pty Ltd | Eastern car park door is jammed and not working | Building | Doors | 480 | Pass | Pass | 0 | 0 | 1.9333 | 2022-05-18 13:03 | 2022-05-19 17:00 | 2022-05-18 14:15 | 2022-05-19 17:00 | 2022-05-18 16:11 |  |  | Got door back into guides but had to cut a few slats to release the pressure. Please quote to replace curtain and guides. 5705 wide. Guide height welded. 3190. Bottom of drum. 3350. 7 slotted slats. Backwards installed. (Inside garage is front of door. ) color. Paperbark.
MSA-DTWD | WA5971892 | 2 | CONNECT SECURITY SYSTEMS | M13 Staff Office Entrance - Repeat faults showing on alarm panel | Security | Security Management System | 629.75 | Pass | Pass | 0 | 0 | 1.9333 | 2022-09-20 15:53 | 2022-09-23 17:00 | 2022-09-23 10:16 | 2022-09-23 17:00 | 2022-09-23 12:12 |  |  | Corrected loose cabling and replaced 2 x batteries
MSA-DTWD | WA5378359 | 3 | AWB Co. | External - Flood light - PE cell is faulty | Electrical | Lighting, External | 539.25 | Pass | Pass | -1 | -1 | 1.9333 | 2022-04-20 13:34 | 2022-04-28 17:00 | 2022-04-20 13:34 | 2022-04-28 17:00 | 2022-04-20 15:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, set up work area and tested p.e cell, found it was faulty, went to wholesaler to pick up parts , returned to site, isolated lighting circuit, removed old p.e cell, mounted new pe cell, terminated cables, siliconed up all entry points , re energised circuit, tested light and working as intended , cleaned up , packed up, completed paperwork,signed out***job completed**
MSA-DTAG | WA5562660 | 2 | Australian HVAC Services Pty. Ltd. | Air-Con needs to be reset due to power outage | Air Conditioning | Building HVAC Maintenance (Major Plant) | 472.79 | Pass | Pass | 0 | 0 | 1.9333 | 2022-06-20 09:04 | 2022-06-23 17:00 | 2022-06-20 09:04 | 2022-06-23 17:00 | 2022-06-20 11:00 |  |  | Plant not running after power out. Attend site. Access level 6 and check BMS. Found BMS off, turn on and attempt to log in. Unable to log into BMS. Check out station on level 15,6 and Basement. Found circuit breakers tripped. Reset circuit breakers. Found controllers to turn back on. Access level 6 and check BMS and found to now be able to log in. Check operation of plant and found to start. Access level 15 and check boilers, found to start. Monitor plant and check for anything else affected by the power Outage. All plant working as normal.
MSA-DCA | WA5831279 | 0 | Techworks Electrical | Damaged light outside Livingston Cafe | Electrical | Lighting, External | 616.29 | Pass | Pass | 0 | 0 | 1.9333 | 2022-09-03 08:28 | 2022-09-03 08:58 | 2022-09-03 08:30 | 2022-09-03 10:28 | 2022-09-03 10:26 |  |  | Light fitting on pole next to Livingston cafe fell off as grub screws came loose. Re-fitted light fitting to pole spigot and installed 2x extra support screws to prevent light fitting falling again. Test that lights are now functioning correctly.Materials; 2x fixingsNo need to return as job is completed.
MSA-DTAG | WA6362878 | 2 | Dormakaba Australia Pty Ltd | Custody - Lower - Roller door not closing. | Building | Doors | 331.95 | Pass | Pass | 0 | 0 | 1.9333 | 2022-12-09 14:24 | 2022-12-14 17:00 | 2022-12-12 07:00 | 2022-12-14 17:00 | 2022-12-12 08:56 |  |  | Tested door operation, checked both relays and switching, all aspects of door are operating well. Suspect issue is related to access control system. Recommend fitting safety beams to door as door has auto down function and can become a hazard for pedestrian traffic.
MSA-DTWD | WA5140802 | 0 | Milners Tree Solutions Pty Ltd | Tree fallen in the accecss road | Landscaping & Gardening | Tree Lopping | 1000 | Fail | Fail | 0 | 0 | 1.9167 | 2022-02-16 06:55 | 2022-02-16 08:55 | 2022-02-17 07:30 | 2022-02-16 10:55 | 2022-02-17 09:25 |  |  | significant fallen limb removed
MSA-DFES | WA5151432 | 3 | Dom's Total Grounds Maintenance | front garden - multiple faulty sprinklers see notes for locations | Plumbing & Drainage | Water | 485 | Fail | Fail | 0 | 0 | 1.9167 | 2022-02-17 13:03 | 2022-02-24 17:00 | 2022-02-25 15:20 | 2022-02-24 17:00 | 2022-02-25 17:15 |  |  | Replace Sprinklers
MSA-MRWA | WA5163602 | 1 | GPS Plumbing & Gas Services PtyLtd | leaking cistern - right hand side toilet | Plumbing & Drainage | Water | 489.1 | Pass | Pass | 0 | 0 | 1.9167 | 2022-02-18 10:22 | 2022-02-21 17:00 | 2022-02-18 11:45 | 2022-02-21 17:00 | 2022-02-18 13:40 |  |  | Removed toilet pan and replaced leaking pan collar and keeseal.Refitted pan.
MSA-DCA | WA5392240 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Harry Butler Reserach Centre - First Floor Lab - temps are very low 13 degrees | Air Conditioning | Room Air Conditioners | 240.7 | Fail | Fail | 0 | 0 | 1.9167 | 2022-05-03 08:48 | 2022-05-03 10:48 | 2022-05-03 11:30 | 2022-05-03 12:48 | 2022-05-03 13:25 |  |  | Attended site gained access and found heating water boiler to be in fault. Carried out reset of heating water pump VSDs and confirmed pump operation. Reset boiler and operation restored. BMS log indicates that fault occured at 2am this morning. Monitored building and confirmed temps have stabilised. No further action required.
MSA-DTAG | WA5790574 | 3 | Gilmour & Jooste Electrical | Light bulbs need replacing in the FV Kitchen | Electrical | Lighting, Internal | 153.64 | Pass | Pass | 0 | 0 | 1.9167 | 2022-08-22 11:11 | 2022-08-29 17:00 | 2022-08-29 07:26 | 2022-08-29 17:00 | 2022-08-29 09:21 |  |  | Repaired light to family violence kitchen.
MSA-DTWD | WA5800776 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Lift is stuck and not operating | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1.9167 | 2022-08-31 12:14 | 2022-08-31 14:14 | 2022-09-01 12:35 | 2022-08-31 16:14 | 2022-09-01 14:30 |  |  | CONTROLLER - MICROPROCESSOR UNIT - COMPONENT RESET
MSA-DTWD | WA6144755 | 3 | Water2water Pty Ltd | W107 - Billi under bench unit not working | Plumbing & Drainage | Water | 591.19 | Pass | Pass | 0 | 0 | 1.9167 | 2022-11-02 08:59 | 2022-11-09 17:00 | 2022-11-07 14:45 | 2022-11-09 17:00 | 2022-11-07 16:40 |  |  | Replaced failed element and recalibrated. Replace tap loom due to missing decal leaving circuitry exposed.
MSA-DTWD | WA6253803 | 2 | BAKE-QUIP PTY LTD | Bain Marie - damaged gate valve and drain pipe - see notes | Equipment | Catering Equipment | 267.5 | Fail | Fail | 2 | 2 | 1.9167 | 2022-11-22 12:04 | 2022-11-25 17:00 | 2022-12-07 07:30 | 2022-11-25 17:00 | 2022-12-07 09:25 |  |  | Refer to service report
MSA-DFES | WA6368103 | 3 | Dom's Total Grounds Maintenance | Garden-Gear drive sprinklers on front lawn are all broken or nozzles are all blocked up | Landscaping & Gardening | Grounds Maintenance | 508 | Pass | Pass | 0 | 0 | 1.9167 | 2022-12-14 07:17 | 2022-12-20 17:00 | 2022-12-20 06:15 | 2022-12-20 17:00 | 2022-12-20 08:10 |  |  | Call Out & Repair Retic
MSA-DCA | WA5656189 | 2 | Earth & Water Pty Ltd | Burst irrigation pipe in garden bed | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 1 | 1 | 1.9167 | 2022-07-18 12:09 | 2022-07-21 17:00 | 2022-07-25 07:14 | 2022-07-21 17:00 | 2022-07-25 09:09 |  |  | Arrived on site, repaired the drip line that was allocated for todays job.Kevin also pointed out that he had just raised a new job regarding a broken sprinkler.I told him I would fix it on site rather than coming back again and update the billing with the new card.Replaced broken sprinkler and the 15mm poly fittings that were also damaged.
MSA-DTWD | WA5066654 | 3 | AHS Services WA Pty Ltd (Anchor) | Tap is leaking on the hand basin | Plumbing & Drainage | Water | 356.57 | Pass | Pass | 0 | 0 | 1.9 | 2022-01-19 09:20 | 2022-01-27 17:00 | 2022-01-25 10:56 | 2022-01-27 17:00 | 2022-01-25 12:50 |  |  | Completed
MSA-DTWD | WA5997521 | 1 | CONNECT SECURITY SYSTEMS | No signal to security camera | Security | CCTV Surveillance | 309.85 | Pass | Pass | 0 | 0 | 1.8833 | 2022-10-07 07:22 | 2022-10-07 17:00 | 2022-10-07 10:51 | 2022-10-07 17:00 | 2022-10-07 12:44 |  |  | Fixed CCTV system to allow staff to retrieve footage
MSA-DCA | WA6001014 | 1 | Techworks Electrical | Faulty emergency exit light - light is currently on the ground | Electrical | Emergency & Exit Lighting | 144.1 | Pass | Pass | 0 | 0 | 1.8833 | 2022-10-10 11:50 | 2022-10-11 17:00 | 2022-10-10 15:00 | 2022-10-11 17:00 | 2022-10-10 16:53 |  |  | Reinstalled exit light that been knocked down
MSA-DTAG | WA6165709 | 1 | Dormakaba Australia Pty Ltd | Level 1 - Staff Carpark - Gate is opening and closing very slowly | Building | Automatic Doors | 1105.84 | Pass | Pass | 0 | 0 | 1.8833 | 2022-11-11 08:55 | 2022-11-14 17:00 | 2022-11-11 13:05 | 2022-11-14 17:00 | 2022-11-11 14:58 |  |  | Found closed position limit magnet to be missing and the motor banging the gate into the closed stop. This had destroyed the racking. Replaced 7 metres of nylon racking and 1 limit magnet. Reset break positions and set speeds. Tested ok.
MSA-DTAG | WA6528569 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Kitchen - Install new kitchen taps | Plumbing & Drainage | Water | 247.29 | Pass | Pass | -1 | -1 | 1.8667 | 2023-02-02 10:39 | 2023-02-09 17:00 | 2023-02-03 13:48 | 2023-02-09 17:00 | 2023-02-03 15:40
MSA-DTWD | WA5306579 | 2 | Water2water Pty Ltd | b block - ground floor - kitchen - hot water unit - drinking water - faulty filter - see notes | Plumbing & Drainage | Water | 495.3225 | Pass | Pass | 0 | 0 | 1.8667 | 2022-04-06 14:44 | 2022-04-11 17:00 | 2022-04-08 10:15 | 2022-04-11 17:00 | 2022-04-08 12:07 |  |  | Replaced filter, level sensors and solenoid in order to restore flow of water back to unit. Tested and checked all ok.
MSA-DTWD | WA5681714 | 1 | CONNECT SECURITY SYSTEMS | Ground Level - Cleaners Cupboard - Alarm panel for block 1 showing multiple faults | Security | Monitoring | 346.48 | Pass | Pass | 0 | 0 | 1.8667 | 2022-07-28 14:20 | 2022-07-29 17:00 | 2022-07-29 09:28 | 2022-07-29 17:00 | 2022-07-29 11:20 |  |  | repaired damaged cabling to PIR and replaced blown fuse
MSA-MRWA | WA6540793 | 2 | GPS Plumbing & Gas Services PtyLtd | Male Toilet, LHS Cubicle, half flush button not working-see notes | Plumbing & Drainage | Toilets/Cisterns | 441.79 | Pass | Pass | -1 | -1 | 1.85 | 2023-02-09 14:14 | 2023-02-14 17:00 | 2023-02-10 07:24 | 2023-02-14 17:00 | 2023-02-10 09:15
MSA-DTAG | WA6178339 | 1 | GPS Plumbing & Gas Services PtyLtd | Public Male Toilets - 2 x urinal not working, water overflowing | Plumbing & Drainage | Toilets/Cisterns | 326.29 | Pass | Pass | 0 | 0 | 1.85 | 2022-11-14 10:47 | 2022-11-15 17:00 | 2022-11-14 14:30 | 2022-11-15 17:00 | 2022-11-14 16:21 |  |  | Cleared 2 blocked urinals in the male toilet that were overflowing
MSA-DCA | WA6531576 | 2 | GPS Plumbing & Gas Services PtyLtd | Male Bathroom - Discovery Lounge - Urinal constantly running to waste | Plumbing & Drainage | Toilets/Cisterns | 340.29 | Pass | Pass | 0 | 0 | 1.85 | 2023-02-03 13:02 | 2023-02-08 17:00 | 2023-02-07 09:24 | 2023-02-08 17:00 | 2023-02-07 11:15
MSA-DTWD | WA5091586 | 1 | AHS Services WA Pty Ltd (Anchor) | A Block - Level 1 -Male toilets East and west - urinals not flushing | Plumbing & Drainage | Materials | 420.75 | Pass | Pass | 0 | 0 | 1.8333 | 2022-01-27 09:27 | 2022-01-28 17:00 | 2022-01-27 13:35 | 2022-01-28 17:00 | 2022-01-27 15:25 |  |  | Completed
MSA-MRWA | WA5399087 | 3 | GPS Plumbing & Gas Services PtyLtd | Disable toilet - Cistern buttons hard to push / cistern slow to fill | Plumbing & Drainage | Toilets/Cisterns | 330.495 | Pass | Pass | -1 | -1 | 1.8333 | 2022-05-09 14:53 | 2022-05-16 17:00 | 2022-05-11 09:50 | 2022-05-16 17:00 | 2022-05-11 11:40 |  |  | Replaced an inlet valve to the cistern on the left-hand side and also replaced an outlet valve kit
MSA-MRWA | WA5454792 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Female Bathrooms - Faulty Shower Head | Plumbing & Drainage | Water | 359.8 | Pass | Pass | 0 | 0 | 1.8333 | 2022-05-17 14:30 | 2022-05-18 17:00 | 2022-05-18 06:20 | 2022-05-18 17:00 | 2022-05-18 08:10 |  |  | Replaced wall top assembly as i could not service the taps properly due to corrosion. Replaced corroded and leaking shower head. Struggled to find isolation valves.
MSA-DFES | WA6253801 | 3 | AWB Co. | Tunic Room - Large area of mold on the ceiling - Investigate what is causing the mold | Building | Ceiling | 928.42 | Fail | Fail | 1 | 1 | 1.8333 | 2022-11-22 12:05 | 2022-11-29 17:00 | 2022-12-08 09:50 | 2022-11-29 17:00 | 2022-12-08 11:40 |  |  | Works completed
MSA-DTAG | WA5017252 | 3 | Seme Solutions Pty Ltd | Custody - Interlock movement - One of the doors into the four way is no closing properly- see notes | Building | Security Doors | 487.5 | Fail | Fail | 3 | 3 | 1.8333 | 2022-01-13 12:01 | 2022-01-20 17:00 | 2022-02-07 12:30 | 2022-01-20 17:00 | 2022-02-07 14:20 |  |  | Inspected door closer on airlock exit to corridor door. Found door closer not fully latching door. Adjustments were made to closer to allow for full closure. Tested door numerous times and it correctly closes with a 5 second delay.
MSA-DFES | WA5090437 | 1 | SONTEC WA PTY LTD | CCTV - Keeps dropping out and not recording | Security | Monitoring | 593.63 | Pass | Pass | 0 | 0 | 1.8333 | 2022-01-25 12:07 | 2022-01-27 17:00 | 2022-01-25 14:10 | 2022-01-27 17:00 | 2022-01-25 16:00 |  |  | Re-installed DVTEL software onto PC near server room. assisted in exporting footage for policereset server and cameras
MSA-DFES | WA5298215 | 1 | Water2water Pty Ltd | Kitchen - Sink leaking water filter is leaking badly | Plumbing & Drainage | Water | 138.205 | Pass | Pass | 0 | 0 | 1.8333 | 2022-03-31 16:30 | 2022-04-01 17:00 | 2022-04-01 12:30 | 2022-04-01 17:00 | 2022-04-01 14:20 |  |  | 12:30PM ATTENDANCE, NO ONE THERE & NO ANSWER. REATTENDED 2:05PM - REASSEMBLED WATER BLOCK AS WAS LEAKING. NEW 3/4" - 1/4" TAP ADAPTER INSTALLED. ALL WORKING OKAY ON DEPARTURE.
MSA-DCA | WA5390145 | 0 | Techworks Plumbing | Francis street - level 2 - male toilets - toilets blocked and backing up into level 3 up | Plumbing & Drainage | Drainage | 215.74 | Pass | Pass | 0 | 0 | 1.8333 | 2022-05-02 10:38 | 2022-05-02 12:38 | 2022-05-02 10:40 | 2022-05-02 14:38 | 2022-05-02 12:30 |  |  | Attended site signed in at security office, spoke to security and they told me about the toilets and they asked if we could have a look at all of them to make sure they were okay while we were there.Went to level 2 and found the toilets not to be blocked, I tested them and also flushed bundles of toilet paper down to see if it would block up again but it was all good.After that I went and checked all the other toilets in the other floorsFound them all to be good and not blocked just found that some had Brocken toilet seats and on level one a toilet had been constantly running so they had isolated it Spoke to Neil and told him the situation Signed out and completed paperwork
MSA-DCA | WA5486677 | 1 | Dormakaba Australia Pty Ltd | GF Design Store/ Cafe - Doors not automatically opening and closing | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 1.8333 | 2022-06-01 09:36 | 2022-06-02 17:00 | 2022-06-01 13:06 | 2022-06-02 17:00 | 2022-06-01 14:56 |  |  | 1126370. Call to site. Inspect auto door. Check and gain access to equipment. Locate problem to failed combination sensor. Obtain replacement. Install and calibrate. Test operational and safety features - all okay.NO CHARGE FOR THIS CALL OUT - SENSOR HAS BEEN REPLACED UNDER WARRANTY - NO CLAIM WILL BE SUBMITTED
MSA-MRWA | WA5565230 | 1 | Dormakaba Australia Pty Ltd | first roller not responding | Building | Automatic Doors | 380 | Pass | Pass | 0 | 0 | 1.8333 | 2022-06-21 15:18 | 2022-06-22 17:00 | 2022-06-22 09:29 | 2022-06-22 17:00 | 2022-06-22 11:19 |  |  | Assessed door and found right hand side spring in drum has snapped which has caused right hand side of door to balloon out and shift across to motor side forcing motor into overload fault.Repositioned door back to normal. After resetting limits and testing door found no fault on motor all ok. Door will not stay up if put into manual mode. Only the motor can hold the door up due to snapped spring.Please quote for new roller doorColour surf mist, door width 2353, outside of brackets 2550 ,floor to top of bracket 2380
MSA-DFES | WA5694606 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Comcen Kitchen - Kitchen sink traps x2 need to be cleaned out - See notes below | Plumbing & Drainage | Water | 231.31 | Pass | Pass | 0 | 0 | 1.8333 | 2022-08-05 11:42 | 2022-08-08 17:00 | 2022-08-08 06:55 | 2022-08-08 17:00 | 2022-08-08 08:45 |  |  | Cleaned the sink drains in comcen kitchen.
MSA-MRWA | WA5832269 | 1 | GPS Plumbing & Gas Services PtyLtd | ground floor - female toilets - left hand side cubicle - flush button not working properly | Plumbing & Drainage | Toilets/Cisterns | 163.14 | Pass | Pass | 0 | 0 | 1.8333 | 2022-09-05 12:10 | 2022-09-06 17:00 | 2022-09-06 09:10 | 2022-09-06 17:00 | 2022-09-06 11:00 |  |  | Replaced both button rubbers flushed and lubricated multiple times no issues after replacing both rubber buttons
MSA-DTWD | WA5979025 | 2 | SPECIALISED LIFTING SERVICE | Hoist 1 & 2 have faulty top limit switches and no rate capacity signage | Lifts | Vehicle hoists | 504.75 | Fail | Fail | 4 | 4 | 1.8333 | 2022-09-28 15:01 | 2022-10-03 17:00 | 2022-10-31 08:40 | 2022-10-03 17:00 | 2022-10-31 10:30 |  |  | Rectified wiring issues.
MSA-DTAG | WA6014523 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Sheriff’s Office - Tap in cleaners storeroom leaking - located in female toilet | Plumbing & Drainage | Water | 287.29 | Pass | Pass | -1 | -1 | 1.8333 | 2022-10-12 09:51 | 2022-10-17 17:00 | 2022-10-12 11:45 | 2022-10-17 17:00 | 2022-10-12 13:35 |  |  | Rewashed leaking taps. Job delayed due to staff in the toilet. And no parking on site
MSA-DCA | WA6483066 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - HLT Male Toilets - Both hot and cold taps need replacing on cleaners sink - See Notes | Plumbing & Drainage | Water | 347.24 | Pass | Pass | -1 | -1 | 1.8333 | 2023-01-18 12:45 | 2023-01-23 17:00 | 2023-01-19 14:00 | 2023-01-23 17:00 | 2023-01-19 15:50
MSA-DCA | WA5680998 | 0 | TK Elevator Australia Pty Ltd | RETROSPECTIVE WORK ORDER DO NOT ATTEND-Lift 1-No2 button has been pushed all the way though | Lifts | Lifts | 420.98 | Fail | Fail | 0 | 0 | 1.8333 | 2022-07-12 09:32 | 2022-07-12 11:32 | 2022-07-14 13:47 | 2022-07-12 13:32 | 2022-07-14 15:37 | 1 |  | 2nd floor button broken on left Car operating panel. Found button broken replaced button and tested all ok. Left in service
MSA-DTAG | WA5481502 | 3 | AHS Services WA Pty Ltd (Anchor) | Roof - Tap on roof not working and is required for future gutter cleaning | Plumbing & Drainage | Water | 176.8675 | Fail | Fail | 0 | 0 | 1.8167 | 2022-05-30 13:52 | 2022-06-07 17:00 | 2022-06-08 14:13 | 2022-06-07 17:00 | 2022-06-08 16:02 |  |  | found tap siezed, replaced hose tap
MSA-MRWA | WA6143141 | 3 | GPS Plumbing & Gas Services PtyLtd | Leak in 3rd or 4th cubicle | Plumbing & Drainage | Toilets/Cisterns | 338.29 | Pass | Pass | -1 | -1 | 1.8167 | 2022-11-01 10:53 | 2022-11-08 17:00 | 2022-11-04 10:15 | 2022-11-08 17:00 | 2022-11-04 12:04 |  |  | Replaced leaking kee seal and adjusted pipework
MSA-DCA | WA5499228 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - Plant Room - Water leaking from ceiling | Plumbing & Drainage | Water | 495.25 | Pass | Pass | -1 | -1 | 1.8167 | 2022-06-10 11:42 | 2022-06-17 17:00 | 2022-06-13 08:16 | 2022-06-17 17:00 | 2022-06-13 10:05 |  |  | Job delayed as i was waiting for a different contractor to show me the location of the leak.Replaced faulty and leaking inlet valve in male staff toilet on L1 in admin building
MSA-DFES | WA5377765 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - External Toilet, Adjacent rear entry door - Cistern Damaged/ Faulty | Plumbing & Drainage | Toilets/Cisterns | 218.52 | Pass | Pass | 0 | 0 | 1.8 | 2022-04-20 08:53 | 2022-04-26 17:00 | 2022-04-26 07:00 | 2022-04-26 17:00 | 2022-04-26 08:48 |  |  | Located to site to repair back to wall toilet cistern due to the hard flush is not working. Found that the fire fighters have been trying to fix it and was missing the springs. So supplied and installed 2 new springs cleared the line scale off the flush button tested and working correctly now.
MSA-DFES | WA5688103 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Station Officer female toilet - toilet cistern is faulty | Plumbing & Drainage | Toilets/Cisterns | 428.39 | Pass | Pass | 0 | 0 | 1.8 | 2022-08-02 09:48 | 2022-08-03 17:00 | 2022-08-03 09:12 | 2022-08-03 17:00 | 2022-08-03 11:00 |  |  | Replaced toilet cistern
MSA-DCA | WA6404847 | 2 | GPS Plumbing & Gas Services PtyLtd | continual leak from the base of toilet, right cubicle men’s staff toilets | Plumbing & Drainage | Toilets/Cisterns | 307.29 | Pass | Pass | 0 | 0 | 1.8 | 2023-01-09 09:37 | 2023-01-12 17:00 | 2023-01-11 10:47 | 2023-01-12 17:00 | 2023-01-11 12:35
MSA-DTWD | WA5108127 | 3 | AHS Services WA Pty Ltd (Anchor) | Men's Urinal Cistern Broken A101 Staff Training Services | Plumbing & Drainage | Toilets/Cisterns | 354.3425 | Pass | Pass | -1 | -1 | 1.7833 | 2022-02-08 11:38 | 2022-02-15 17:00 | 2022-02-08 12:45 | 2022-02-15 17:00 | 2022-02-08 14:32 |  |  | Located urinal and found inlet valve leaking when flushed.Picked up new inlet valve.and installed along with new flexi
MSA-DTAG | WA5324265 | 2 | GPS Plumbing & Gas Services PtyLtd | 1987 - Level 2 - Gents Toilet -Sink draining slowly | Plumbing & Drainage | Drainage | 318.8 | Pass | Pass | -1 | -1 | 1.7833 | 2022-04-13 13:25 | 2022-04-20 17:00 | 2022-04-14 08:00 | 2022-04-20 17:00 | 2022-04-14 09:47 |  |  | LH basin was blocked. Cleared blockage. RH basin was blocked due to matte black push up plug was jammed. Replaced with new one.
MSA-DFES | WA5383206 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Unisex Toilet half and main flush button not working - See notes | Plumbing & Drainage | Toilets/Cisterns | 317.57 | Pass | Pass | 0 | 0 | 1.7833 | 2022-04-27 13:15 | 2022-05-02 17:00 | 2022-04-29 11:42 | 2022-05-02 17:00 | 2022-04-29 13:29 |  |  | Repaired toilet cistern.
MSA-DFES | WA5304189 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Bunker/Simcen - Male toilet - Light in male toilet not working | Electrical | General Electrical | 469.985 | Pass | Pass | 0 | 0 | 1.7667 | 2022-04-04 15:40 | 2022-04-07 17:00 | 2022-04-05 11:59 | 2022-04-07 17:00 | 2022-04-05 13:45 |  |  | Aos 1159 sign in and inspect area. Left site to collect replacement fitting. Returned and replaced had to do Junction behind light to get cable into light. New light dosnt cover all old hole have made a first patch with plaster will need a followup with a plasterer or painter. Continued with other job on same site at 1345
MSA-DCA | WA5675139 | 0 | Kone Elevators Pty Ltd | lift 4 has jammed and not moving-cleaner has jammed lift with rag | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.7667 | 2022-07-22 08:17 | 2022-07-22 10:17 | 2022-07-22 09:04 | 2022-07-22 12:17 | 2022-07-22 10:50 |  |  | TOP R/H HANDRAIL INLET JAMMED IN AFTER CLEANER HAD RAG CAUGHT IN IT. REPAIRED SAME, CONFIRM OPERATION AND RETURN TO SERVICE
MSA-DTAG | WA5832738 | 2 | Dormakaba Australia Pty Ltd | Marriage room - faulty security door to marriage office - see notes below | Building | Security Doors | 343.75 | Pass | Pass | 0 | 0 | 1.7667 | 2022-09-05 15:51 | 2022-09-08 17:00 | 2022-09-06 08:32 | 2022-09-08 17:00 | 2022-09-06 10:18 |  |  | Adjusted lock position. Repaired damaged wire into lock. Adjusted closed read magnet to prevent alarm from sounding. Tested operation, all ok. The noise the lock is making is normal for that device. If this a problem then another lock type can be fitted. The ticking sound is coming from something else in the ceiling space. Not the door controls.
MSA-DTWD | WA6572891 | 3 | CONNECT SECURITY SYSTEMS | W Block - Door - WM101 - Strike plate missing | Security | Access Control | 355.35 | Pass | Pass | -1 | -1 | 1.7667 | 2023-02-14 09:18 | 2023-02-21 17:00 | 2023-02-16 09:57 | 2023-02-21 17:00 | 2023-02-16 11:43
MSA-DFES | WA4992639 | 3 | Dom's Total Grounds Maintenance | Outside grass area - Retie in the grass / Garden bed areas - rear of station - see details below | Landscaping & Gardening | Grounds Maintenance | 443.5 | Pass | Pass | -1 | -1 | 1.75 | 2022-01-06 14:52 | 2022-01-13 17:00 | 2022-01-09 10:55 | 2022-01-13 17:00 | 2022-01-09 12:40 |  |  | Out of Metro Call OutSupply 3 x large gear drive sprinklers, 8 x microjets & retic fittings
MSA-DTWD | WA4995423 | 2 | WESTERN IRRIGATION PTY LTD | Greenhouse & Plants - water recycling system north - water recycling system is not operating | Landscaping & Gardening | Grounds Maintenance | 397.5 | Fail | Fail | 1 | 1 | 1.75 | 2022-01-10 12:50 | 2022-01-13 17:00 | 2022-01-17 07:30 | 2022-01-13 17:00 | 2022-01-17 09:15 |  |  | Test filtration system, found PLC had lost it memory as power had been turned off. Reprogrammed PLC and tested for correct operation.
MSA-DTAG | WA5038183 | 3 | Bullant Security Pty Ltd | Kitchen - Unable to unlock kitchen door with key or keypad | Security | Locksmith | 750.06 | Fail | Fail | 4 | 4 | 1.75 | 2022-01-17 10:56 | 2022-01-24 17:00 | 2022-02-22 11:15 | 2022-01-24 17:00 | 2022-02-22 13:00 |  | WACCES & WCAPPR | Attended site, unable to repair keypad lock. Installed new mortice lock, internal handle, external handle and oval cylinder eith 4x keys supplied as requested. Date on site: 22/02/2022Time on site: 11:15 - 13:00
MSA-DTAG | WA5053295 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Public disabled toilet - Toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 201.4625 | Fail | Fail | 0 | 0 | 1.75 | 2022-01-18 15:13 | 2022-01-19 17:00 | 2022-01-20 07:30 | 2022-01-19 17:00 | 2022-01-20 09:15 |  |  | Readjusted and alligned concealed cistern behind wall.
MSA-DTWD | WA5094288 | 2 | AWB Co. | Outdoor -Undercover area - security light is faulty | Electrical | Lighting, External | 301.06 | Pass | Pass | 0 | 0 | 1.75 | 2022-01-31 09:30 | 2022-02-03 17:00 | 2022-02-03 12:30 | 2022-02-03 17:00 | 2022-02-03 14:15 |  |  | Attended site, signed in, completed jsa,spoke to fm about lighting issue , went to m block and located 2x timers in main switchboard, put them in override position and checked to see if they controlled the lights in the carpark, lights were not on, went back and checked programming of timers and time set , all working as intended but didn’t control lights in work order , changed timers back to normal operation and searched for timers 8n other switch boards , found an analog timer in dB located in plastering section, put on override and checked lights, all light are working, went back to timer and found that time set on it was wrong and this is why lights were staying on at day time and turning off at night, reset time and checked with fm that lights had been turning on and off daily to verify timer wasn’t faulty , timer now set to proper time and control, locked up dB, packed up , completed paperwork, signed out*** job complete ***
MSA-DTWD | WA5098275 | 2 | Falcetta Plumbing and Gas | Male toilet cubicle is constantly flowing and cistern wont fill. see notes | Plumbing & Drainage | Toilets/Cisterns | 272.91 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-01 08:11 | 2022-02-04 17:00 | 2022-02-03 12:00 | 2022-02-04 17:00 | 2022-02-03 13:45 |  |  | Replaced inlet assembly
MSA-DTWD | WA5098425 | 0 | BJ SYSTEMS | T & V blocks BMS fault - emergency exit doors not working BMS issue | Security | Security Management System | 238.71 | Fail | Fail | 0 | 0 | 1.75 | 2022-02-01 09:08 | 2022-02-01 11:08 | 2022-02-01 14:45 | 2022-02-01 13:08 | 2022-02-01 16:30 |  |  | T, U, V Blocks all auto doors are ok. Replaced reed switch on U Block classroom. T Block controller had lost software, downloaded to controller, all online now. T Block doors are ok now
MSA-DFES | WA5099816 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Multiple Lights faulty - See notes for locations | Electrical | Lighting, Internal | 329.415 | Fail | Fail | 1 | 1 | 1.75 | 2022-02-02 08:56 | 2022-02-07 17:00 | 2022-02-14 08:45 | 2022-02-07 17:00 | 2022-02-14 10:30 |  |  | Arrived on site at 08:45. Located light in so office with blown tube replaced both tubes and starters. Located blown tube in room 10 fluro replaced both the tube and starter. Was shown bunk lights in room 7 by so he explained that the lights are strobing, replaced 4 x tubes and starters tested all okay. Next job on same site continued on at 10:303 x 36w t8 865 tubes 3 x 13w t5 865 tubes 1 x 18w t8 865 tube 7 x s10 starter
MSA-DCA | WA5100454 | 2 | Commercial Aquatics Australia | Francis street - City Room -Mister UV lamp fault - see details below | Electrical | General Electrical | 1000 | Fail | Fail | 8 | 8 | 1.75 | 2022-02-02 13:52 | 2022-02-07 17:00 | 2022-04-01 11:45 | 2022-02-07 17:00 | 2022-04-01 13:30 |  | WACCES | Supplied and installed new UV sensor
MSA-MRWA | WA5100972 | 1 | AWB Co. | Faulty lights | Electrical | Lighting, Internal | 301.06 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-03 08:35 | 2022-02-04 17:00 | 2022-02-04 11:45 | 2022-02-04 17:00 | 2022-02-04 13:30 |  |  | Attended site, signed in, completed jsa, all lights on tripping circuit were working and circuit was energised on arrival, went around to each room and tried to re cause fault on light circuit to determine which light was causing the issue , all light were working and wouldn’t trip, discussed options with fm, unplugged lights in each room and marked lights , fm will monitor if lights trip in the future, completed paperwork, signed out ,job complete
MSA-DTWD | WA5106574 | 1 | Complete Pest Management Services | G Block - Staff Prep Area - G19 - termite infestation | Pest Control | General Pest | 2200 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-07 08:29 | 2022-02-08 17:00 | 2022-02-08 10:15 | 2022-02-08 17:00 | 2022-02-08 12:00 |  |  | Install 2 termite AG bait Stations outside Staff Prep area G blockKitchen cupboards had been completely eaten out buy termites in thr kitchen area of Staff Prep area G19.Also found termite nests in trees outside of H and B blocks
MSA-DTWD | WA5109620 | 2 | AWB Co. | Dry Cure - U024.3 - faulty fluro x 6 | Electrical | Lighting, Internal | 330.15 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-09 11:54 | 2022-02-14 17:00 | 2022-02-14 12:00 | 2022-02-14 17:00 | 2022-02-14 13:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Spoke to fm and he said if ceiling was sagging not to bother with lights. Located room with faulty lighting. Called fm and spoke to him about ceiling, fm met us down at room and we discussed a few options. Fm wants all tubes and starters replaced. Replaced all tubes and starters. Lighting is now working as intended. Took pictures. Completed Paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5111716 | 1 | Equans Mechanical Services Australia | F Block - Ground - FG04 toilets - Toilet Exhaust Fans not working - see details below | Electrical | General Electrical | 202.21 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-10 10:29 | 2022-02-11 17:00 | 2022-02-10 14:45 | 2022-02-11 17:00 | 2022-02-10 16:30 |  |  | CHECKED OPERATION - REPLACE V BELT
MSA-DFES | WA5125685 | 0 | Go Doors | Engine room door #1 not closing | Building | Doors | 540 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-13 17:38 | 2022-02-13 19:38 | 2022-02-13 19:30 | 2022-02-13 21:38 | 2022-02-13 21:15 |  |  | Completed
MSA-DTWD | WA5126471 | 1 | M Construction (WA) | door is falling off hinges - see notes | Building | Doors | 237.74 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-14 08:04 | 2022-02-15 17:00 | 2022-02-14 10:15 | 2022-02-15 17:00 | 2022-02-14 12:00 |  |  | Attended site & located door with hinges that are coming away from frame. Straightened hinges and install rivets so door functions correctly.
MSA-DTWD | WA5141324 | 2 | ECO PLUMBING AND GAS PTY LTD | Hot water system - faulty | Plumbing & Drainage | Water | 215.845 | Fail | Fail | 1 | 1 | 1.75 | 2022-02-16 09:25 | 2022-02-21 17:00 | 2022-03-02 13:15 | 2022-02-21 17:00 | 2022-03-02 15:00 |  |  | Cleaned out tempering valve and cleared blockage in sink.
MSA-DFES | WA5164115 | 2 | Water2water Pty Ltd | Ground - Kitchen - see details below | Plumbing & Drainage | Water | 236.0525 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-18 17:13 | 2022-02-23 17:00 | 2022-02-22 11:15 | 2022-02-23 17:00 | 2022-02-22 13:00 |  |  | Tightened hot tank lid and replaced leaking John guest tubing
MSA-DTWD | WA5193844 | 2 | SENTINEL LOCK SERVICE PTY LTD | Both doors for this office have sticky locks | Security | Locksmith | 531.74 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-25 15:06 | 2022-03-02 17:00 | 2022-03-02 07:30 | 2022-03-02 17:00 | 2022-03-02 09:15 |  |  | B Block - B2437 - both office doors have sticky/faulty locks.Locks repaired and replaced.
MSA-DTWD | WA5201444 | 1 | AWB Co. | Fan switch has exposed wires | Electrical | General Electrical | 288.63 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-02 15:10 | 2022-03-03 17:00 | 2022-03-03 08:15 | 2022-03-03 17:00 | 2022-03-03 10:00 |  |  | Attended site signed in completed jsa. Found faulty switch mech in classroom. Isolated power and swapped out mechs. Tested operation and works fine.***job completed***
MSA-DTWD | WA5208954 | 1 | Protek 24/7 Building & Maintenance | Outer door won’t close | Building | Doors | 511.8 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-09 12:19 | 2022-03-10 17:00 | 2022-03-09 14:45 | 2022-03-10 17:00 | 2022-03-09 16:30 |  |  | Outer door not closing Work order now closed per Andrew Crawford
MSA-MRWA | WA5215276 | 2 | Water2water Pty Ltd | Ground - Courtyard walkway near amenities - Noisy and leaking water fountain | Plumbing & Drainage | Water | 226.9625 | Pass | Pass | -1 | -1 | 1.75 | 2022-03-10 10:54 | 2022-03-15 17:00 | 2022-03-11 09:00 | 2022-03-15 17:00 | 2022-03-11 10:45 |  |  | A401910149 RS40 fountain determined not to be leaking, plumber required for mains leak. Stopped vibration of ice machine.
MSA-DTWD | WA5215728 | 1 | AAA Ability Locksmiths | Faulty Safe Lock | Security | Locksmith | 628.67 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-10 16:06 | 2022-03-11 17:00 | 2022-03-11 09:30 | 2022-03-11 17:00 | 2022-03-11 11:15 |  |  | Attend site, replaced lock on safe.
MSA-DTWD | WA5217071 | 1 | Equans Mechanical Services Australia | Block 4 - plant room - A/C 8 not working | Air Conditioning | Room Air Conditioners | 183.14 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-11 16:01 | 2022-03-14 17:00 | 2022-03-14 08:15 | 2022-03-14 17:00 | 2022-03-14 10:00 |  |  | Unit is showing fault code 5 indicating a sensor issue. Unit is new install and probably under warranty. Simon is following up with manufacturers.
MSA-DFES | WA5226687 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Bins area - Sewage pump controller - fault and alarms going off | Plumbing & Drainage | Water | 204.1 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-14 11:21 | 2022-03-15 17:00 | 2022-03-15 14:15 | 2022-03-15 17:00 | 2022-03-15 16:00 |  |  | Need to replaces probe and cable BRAF - DECLINED
MSA-DFES | WA5231858 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ensuite - SO Dorm - light is damaged | Electrical | Lighting, External | 340.595 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-15 16:13 | 2022-03-16 17:00 | 2022-03-16 12:30 | 2022-03-16 17:00 | 2022-03-16 14:15 |  |  | Attend site 1230. Light in ensuite reported as faulty. Found that the light had sufficient voltage at the fitting however was not operating. I left site at 1300 to pick up materials from the supplier, returning at 1330. I replaced the light unit and tested. The light is now operating as should be. Informed officers on duty of outcomes, and left site at 1415.
MSA-DTWD | WA5253283 | 1 | Equans Mechanical Services Australia | Unit 10 - Ground - 10G76 - see details below | Air Conditioning | Room Air Conditioners | 183.14 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-17 09:04 | 2022-03-18 17:00 | 2022-03-17 14:00 | 2022-03-18 17:00 | 2022-03-17 15:45 |  |  | Investigated and found no issues with drain. Found pipe insulation had come apart in ducting along wall and pipes condensating. Suspect condensation is running along pipe ducting and down wall causing carpet to get damp. Fixed up insulation and re taped. Checked and found no signs of water leaks.
MSA-DTWD | WA5288906 | 2 | AWB Co. | flashing fluro - requires high ladder | Electrical | General Electrical | 506.82 | Pass | Pass | -1 | -1 | 1.75 | 2022-03-23 15:28 | 2022-03-28 17:00 | 2022-03-24 12:45 | 2022-03-28 17:00 | 2022-03-24 14:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located light fitting that needed tubes replacing. Went to wholesaler to pick up parts. Jeffrey said he wanted us to get him a box of tubes and starters ( as per Po ). Got 12ft ladder to work area and set up. Replaced faulty tubes and starters. Light is now working as intended. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5291094 | 2 | AWB Co. | B Block - B107.1 - Light switch needs replacing | Electrical | General Electrical | 350.09 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-25 14:59 | 2022-03-30 17:00 | 2022-03-28 09:45 | 2022-03-30 17:00 | 2022-03-28 11:30 |  |  | Attended site and signed in. Completed JSA. Located room with faulty light switch. Went to wholesaler for parts. Returned to site and changed faulty light switch over. Took pictures. Completed paperwork signed out job complete
MSA-DTWD | WA5297769 | 2 | BAKE-QUIP PTY LTD | E block - Cafeteria - Kitchen - The fan in gas oven is making a rattling noise when switched on. | Equipment | Catering Equipment | 342.5 | Fail | Fail | 2 | 2 | 1.75 | 2022-03-31 12:48 | 2022-04-05 17:00 | 2022-04-19 09:00 | 2022-04-05 17:00 | 2022-04-19 10:45 |  |  | REFERN TO SERVICE REPORT
MSA-DFES | WA5304964 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Main Foyer Outside - light in mall is damaged | Electrical | Lighting, External | 199.515 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-05 11:10 | 2022-04-05 13:10 | 2022-04-05 12:00 | 2022-04-05 15:10 | 2022-04-05 13:45 |  |  | Arrived onsite at 12:00 to investigate broken lights in mall area. Found 1 x flush mount up light had fallen into its recess due to vandalism or wear and tear. Removed all parts of light to inspect what broke and how to resecure light. Screwed light into mounting recess tightly and resealed light upon reassembly of light. Tested light and left site at 13:45
MSA-DTWD | WA5308400 | 1 | Protek 24/7 Building & Maintenance | Room 8F50 -Large pin board detached from wall - Board is large and will require 2 people | Furniture | Office Furniture | 310.75 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-08 11:29 | 2022-04-11 17:00 | 2022-04-11 08:45 | 2022-04-11 17:00 | 2022-04-11 10:30 |  |  | Large Pin Board Detached from Wall
MSA-DFES | WA5325913 | 1 | SONTEC WA PTY LTD | Ground - Engine Room - see details below | Security | Access Control | 797.5 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-14 13:59 | 2022-04-19 17:00 | 2022-04-19 09:30 | 2022-04-19 17:00 | 2022-04-19 11:15 |  |  | 19/4/22 - Dylan ParslowFound door applying pressure against electric strike.Replaced with preloaded strike.Tested all working.
MSA-DTAG | WA5380674 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 5 - Male Public Toilet (Hay St side) -Male urinal is blocked | Plumbing & Drainage | Toilets/Cisterns | 242.6825 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-22 14:53 | 2022-04-28 17:00 | 2022-04-28 12:30 | 2022-04-28 17:00 | 2022-04-28 14:15 |  |  | Used sprit of salts hot water and plunger to clear stubborn blockage
MSA-DTWD | WA5383040 | 2 | AWB Co. | Faulty fluro fitting | Electrical | Lighting, Internal | 266.48 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-27 11:09 | 2022-05-02 17:00 | 2022-05-02 14:00 | 2022-05-02 17:00 | 2022-05-02 15:45 |  |  | Attended site and signed in, completed jsa, spoke to fm about job,located lighting in e block, tested for power , faulty ballast causing light to not work, spoke to fm and he wanted it replaced with led fitting, went to wholesaler to pick up parts,returned to site, isolated lighting circuits,removed old lights and replaced with new, re energised lighting circuit, tested lights and working as intended,cleaned up,packed up, completed paperwork,signed out ***job complete***
MSA-DTWD | WA5384278 | 1 | AWB Co. | Restaurant Kitchen entrance area has a water leak through the ceiling | Roofing | Metal Roofing | 470.81 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-28 11:21 | 2022-04-29 17:00 | 2022-04-29 09:45 | 2022-04-29 17:00 | 2022-04-29 11:30 |  |  | Investigate/repair roof leak
MSA-DTWD | WA5400821 | 2 | BJ SYSTEMS | door not opening when swiped, intermittent fault | Building | Doors | 541.21 | Fail | Fail | 0 | 0 | 1.75 | 2022-05-10 13:05 | 2022-05-13 17:00 | 2022-05-16 08:00 | 2022-05-13 17:00 | 2022-05-16 09:45 |  |  | Sign in FM Joondalup key access. Drive to McLarty site, inspect access control door. Remove and install new electrical strike lock, check door devices associated. Tested swipe access multiple times, working as normal. Door secure. Return key access FM
MSA-DTWD | WA5416782 | 2 | AWB Co. | Campus Grounds - Campus Security lights not coming on | Electrical | Lighting, External | 304.63 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-13 08:26 | 2022-05-18 17:00 | 2022-05-18 14:45 | 2022-05-18 17:00 | 2022-05-18 16:30 |  |  | Attended site signed in completed jsa. Went around site and changed timers to correct times. Tested all lights and they are now working as intended. Completed paperwork signed out.Job complete
MSA-DTWD | WA5451262 | 3 | AHS Services WA Pty Ltd (Anchor) | B208 - Taps in Boardroom Kitchen need replacing | Plumbing & Drainage | Materials | 189.9125 | Pass | Pass | -1 | -1 | 1.75 | 2022-05-17 07:48 | 2022-05-23 17:00 | 2022-05-17 09:30 | 2022-05-23 17:00 | 2022-05-17 11:15 |  |  | Inspected searched for the isolation reseated hot and cold and replaced spout all good
MSA-DTWD | WA5462155 | 3 | ACTION GLASS & ALUMINIUM | Room G25 - Crack in southern windowpane | Glazing | Window Glass | 548.35 | Pass | Pass | -1 | -1 | 1.75 | 2022-05-19 11:59 | 2022-05-26 17:00 | 2022-05-20 10:30 | 2022-05-26 17:00 | 2022-05-20 12:15 |  |  | ATTENDED SITEREGLAZED 2 BROKEN WINDOWS6.38 CLEAR LAMINATED SAFETY GLASS1-769 X 11121-720 X 881PLUS SILICONE AND 3 L/M OF RUBBER
MSA-DTWD | WA5468478 | 1 | Equans Mechanical Services Australia | Cooling tower - Water level to high in tank causing water to overflow | Air Conditioning | Cooling Tower | 183.14 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-20 09:52 | 2022-05-23 17:00 | 2022-05-20 12:00 | 2022-05-23 17:00 | 2022-05-20 13:45 |  |  | Adjustedwater float levels as was too high
MSA-DTWD | WA5472735 | 1 | Protek 24/7 Building & Maintenance | Room F7 - Roof Leak | Roofing | Metal Roofing | 404.63 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-24 10:05 | 2022-05-25 17:00 | 2022-05-25 09:00 | 2022-05-25 17:00 | 2022-05-25 10:45 |  |  | Repair roof leaf - Room F7
MSA-DCA | WA5477250 | 2 | FCT SURFACE CLEANING | Ground – external - West side wall of SLWA - Graffiti on west side wall of SLWA. | Cleaning | Cleaning |  | Fail | Fail | 0 | 0 | 1.75 | 2022-05-25 12:19 | 2022-05-30 17:00 | 2022-06-01 11:45 | 2022-05-30 17:00 | 2022-06-01 13:30 |  |  | Removal of graffiti
MSA-DTAG | WA5480008 | 2 | Automatic Fire Protection (ARA) | 1987 - Level 2 - Alarm Test Training – Tuesday 31/5/22 - see details below | Fire Protection Services | Fire Protection - Monitor System | 217.045 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-27 14:21 | 2022-06-01 17:00 | 2022-05-31 07:30 | 2022-06-01 17:00 | 2022-05-31 09:15 |  |  | Performed panel training for Supreme Court staff as requested.
MSA-DTWD | WA5480026 | 3 | AWB Co. | B2127 Corridor - Lights not working properly - See notes below | Electrical | Lighting, Internal | 202.78 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-27 14:34 | 2022-06-03 17:00 | 2022-06-03 12:00 | 2022-06-03 17:00 | 2022-06-03 13:45 |  |  | Attended site and signed in. Completed JSA. Located hallway switching not working. Investigated wiring and found 3 way switching to do the lights. Rectified and rewired lighting control to work at all 3 switches. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5490908 | 2 | AWB Co. | Electrical connection arcing - | Electrical | General Electrical | 304.63 | Fail | Fail | 1 | 1 | 1.75 | 2022-06-03 10:15 | 2022-06-09 17:00 | 2022-06-13 12:45 | 2022-06-09 17:00 | 2022-06-13 14:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, went to b5 and found lecturer in kilns area, he explained the issue with kiln, removed cover and found a loose connection to element , removed nuts and washers and put heat shrink on cable and remounted to bolt, made sure all connections were tight, spoke with lecturers and explained issue, lecturer wants internals to be updated but said he has a contractor that he uses for it, I.r tested kiln and it passed, earthing to enclosure is fine, packed up, completed paperwork, signed out ***job completed***
MSA-DFES | WA5494313 | 1 | Protek 24/7 Building & Maintenance | Female Locker Room - Water Leak dripping through light fitting - See notes below | Building | Ceiling | 749.65 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-07 13:57 | 2022-06-08 17:00 | 2022-06-08 13:30 | 2022-06-08 17:00 | 2022-06-08 15:15 |  | WACCES | Repair water leak in Female Locker room
MSA-DTWD | WA5497129 | 3 | AWB Co. | Q012 - Hallway next to Q012 has 2 x hanging lights - see details below | Electrical | General Electrical | 304.63 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-09 14:32 | 2022-06-16 17:00 | 2022-06-13 09:45 | 2022-06-16 17:00 | 2022-06-13 11:30 |  |  | Attended site and signed in completed jsa. Located faulty lights near doors. Replaced tubes and starters, both are now working as intended. Located light with faulty ballast. Swapped out new ballast with old faulty one. Light is now working as intended and not buzzing. Took pictures of everything. Completed paperwork. Signed out. Job complete
MSA-DFES | WA5497249 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Fault on BMF - UPS Fault - See notes below | Equipment | Electrical Equipment | 199.515 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-09 16:44 | 2022-06-10 17:00 | 2022-06-10 08:15 | 2022-06-10 17:00 | 2022-06-10 10:00 |  |  | Arrived on site at 0815 to investigate Ground Floor - Fault on BMF - UPS Fault. Located relative ups room and began investigation. Contacted Deborah on site who was aware of situation and informed me that site was only requesting a confirmation check on UPS to verify all systems were working normally since power outage which occurred on 09/06/2022. Searched through both UPS systems event history in GF ups room and could not find anything of concern. Informed staff and left site at 1000.
MSA-DTWD | WA5511947 | 3 | AWB Co. | Flickering Fluro's | Electrical | Lighting, Internal | 260.2 | Pass | Pass | -1 | -1 | 1.75 | 2022-06-13 11:25 | 2022-06-20 17:00 | 2022-06-14 10:30 | 2022-06-20 17:00 | 2022-06-14 12:15 |  | WACCES | Attended site and signed in. Completed JSA. Located areas on lighting list with faulty lights. Counted up materials needed. Supply and replaced tubes and starters as required. Tested all okay. Signed out. Job complete
MSA-DCA | WA5522327 | 2 | Techworks Plumbing | Level 2 - Female Toilet - Toilet in middle cubicle is constantly running | Plumbing & Drainage | Toilets/Cisterns | 392.47 | Pass | Pass | -1 | -1 | 1.75 | 2022-06-15 14:20 | 2022-06-20 17:00 | 2022-06-16 09:45 | 2022-06-20 17:00 | 2022-06-16 11:30 |  |  | Pin on half flush would not recess back into its original place. Removed all parts and trimmed pin where necessary to allow it to recess back into it original seating. Re install all parts and test
MSA-DTAG | WA5549314 | 2 | AHS Services WA Pty Ltd (Anchor) | Ladies public toilets, hay st side - Toilet lid broken, detatched, currently in admin services | Plumbing & Drainage | Toilets/Cisterns | 244.0925 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-17 16:30 | 2022-06-22 17:00 | 2022-06-21 08:00 | 2022-06-22 17:00 | 2022-06-21 09:45 |  |  | Repaired toilet seats on levels 4 and 5.
MSA-DTWD | WA5567116 | 2 | Protek 24/7 Building & Maintenance | C Block - Ground - Laundry - Door gets caught/jammed on the door frame | Building | General Building | 360.25 | Fail | Fail | 0 | 0 | 1.75 | 2022-06-23 14:57 | 2022-06-28 17:00 | 2022-06-29 14:00 | 2022-06-28 17:00 | 2022-06-29 15:45 |  |  | Repair swollen laundry door and replace Handles
MSA-DTWD | WA5567448 | 2 | AWB Co. | Outside Exterior sensor lights not working | Electrical | Lighting, External | 401.5 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-24 09:22 | 2022-06-29 17:00 | 2022-06-28 14:45 | 2022-06-29 17:00 | 2022-06-28 16:30 |  |  | Attended site and signed in. Completed JSA. spoke to fm. Located lights that were not coming on. Tested for power at lights. Lights had power. Found pe cell controlling security lights. Put actives together to bypass pe cell. Figured that pe cell was faulty. Went to wholesaler to pick up parts. Returned to site. Replaced faulty pe cell. Covered up pe cell to see if lights worked. Everything working as intended. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5571663 | 3 | AWB Co. | Level G - K block external - North West corner - LED flood light not working | Electrical | Lighting, External | 278.11 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-29 11:01 | 2022-07-06 17:00 | 2022-07-05 14:00 | 2022-07-06 17:00 | 2022-07-05 15:45 |  |  | Attended site and signed in. Completed JSA. Located k block and turned on all lights. Found flood out the back to not be switching on. Checked for power and is okay. Light is faulty. Supply and replace light with new led flood. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5572314 | 3 | Midolo Building Services | Family Violence - door faulty - see notes below | Building | Doors | 258.2 | Fail | Fail | 1 | 1 | 1.75 | 2022-06-29 16:37 | 2022-07-06 17:00 | 2022-07-11 08:00 | 2022-07-06 17:00 | 2022-07-11 09:45 |  |  | glued carpet down
MSA-DTAG | WA5588945 | 1 | Seme Solutions Pty Ltd | External Sally Port door - Door 36 is not working correctly - See notes below | Security | Access Control | 1109.38 | Pass | Pass | 0 | 0 | 1.75 | 2022-07-08 08:32 | 2022-07-11 17:00 | 2022-07-08 12:45 | 2022-07-11 17:00 | 2022-07-08 14:30 |  |  | Lock initially failing to drop lock 90% of the time. Pulled apart and cleaned thoroughly and lubricated parts. Reinstall and test, unable to recreate failure. Am happy with lock after multie test cycles. However, given the intermittent nature of the fault, should this issue reoccur, will recommend replacing the lock on next attendance.
MSA-DTWD | WA5596743 | 1 | Lane's Plumbing | BLD 837A - Copper pipe leaking | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.75 | 2022-07-11 10:10 | 2022-07-12 17:00 | 2022-07-11 10:15 | 2022-07-12 17:00 | 2022-07-11 12:00 |  |  | REPAIR LEAKING WATER PIPE NEAR GST SQUASH COURT
MSA-DCA | WA5596791 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Theatre Suite - Sinks/tap/pipes making clunking noise - courtyard balcony offices | Plumbing & Drainage | Water | 245.7275 | Pass | Pass | -1 | -1 | 1.75 | 2022-07-11 10:32 | 2022-07-18 17:00 | 2022-07-11 14:45 | 2022-07-18 17:00 | 2022-07-11 16:30 |  |  | Water hammer from sink in theatre suite. Changed mini stop and clipped pipework under sink that was loose
MSA-DTWD | WA5603948 | 3 | AWB Co. | Replace Fluro tubes | Electrical | Lighting, Internal | 239.8075 | Pass | Pass | 0 | 0 | 1.75 | 2022-07-12 14:25 | 2022-07-19 17:00 | 2022-07-18 12:00 | 2022-07-19 17:00 | 2022-07-18 13:45 |  |  | Attended site and signed in. Completed JSA. Located faulty lights. Supply and replace tubes and starters to all lights out in room. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5604044 | 2 | AHS Services WA Pty Ltd (Anchor) | Sewage pipe leaking (connected pipes) | Plumbing & Drainage | Sewer Drains & Septic Systems | 199.8625 | Fail | Fail | 1 | 1 | 1.75 | 2022-07-12 15:23 | 2022-07-15 17:00 | 2022-07-19 09:30 | 2022-07-15 17:00 | 2022-07-19 11:15 |  |  | clean up and reseal pipework
MSA-DTWD | WA5608362 | 2 | BJ SYSTEMS | Swipe access broken | Security | Access Control | 532.83 | Pass | Pass | -1 | -1 | 1.75 | 2022-07-13 08:19 | 2022-07-18 17:00 | 2022-07-14 11:00 | 2022-07-18 17:00 | 2022-07-14 12:45 |  |  | Found electric strike faulty, replaced, tested okNote: Door and door frame is very snug, recommend door and frame to be looked at
MSA-DTWD | WA5608573 | 3 | AWB Co. | GPO with Faulty switch ( do not operate tag ) | Electrical | General Electrical | 383.2175 | Pass | Pass | 0 | 0 | 1.75 | 2022-07-13 09:59 | 2022-07-20 17:00 | 2022-07-18 14:00 | 2022-07-20 17:00 | 2022-07-18 15:45 |  |  | Attended site and signed in. Completed JSA. Located art room and found tagged out gpo. Supply and replaced base plate and replaced 2 switched gpos. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5655378 | 2 | AWB Co. | Rain Leak into S203 Mt Lawley | Roofing | Metal Roofing | 392.115 | Pass | Pass | 0 | 0 | 1.75 | 2022-07-18 07:58 | 2022-07-20 17:00 | 2022-07-18 12:30 | 2022-07-20 17:00 | 2022-07-18 14:15 |  |  | Investigated roof leak.Found holes in silicon in box gutter overflow outlet.cleaned back old silicon. Applied new over seal to outlet.cleaned and packed up
MSA-DFES | WA5673465 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Bedroom 5 - Winding mechanism on bedroom sash window broken. | Building | Windows | 352.78 | Pass | Pass | -1 | -1 | 1.75 | 2022-07-20 15:58 | 2022-07-27 17:00 | 2022-07-21 13:15 | 2022-07-27 17:00 | 2022-07-21 15:00 |  |  | replace broken Window sash mechanism
MSA-DTWD | WA5679984 | 2 | AWB Co. | Repair lights not working entry foyer A258 A Block level 2 | Electrical | Lighting, Internal | 232.9275 | Pass | Pass | -1 | -1 | 1.75 | 2022-07-27 08:53 | 2022-08-01 17:00 | 2022-07-28 11:15 | 2022-08-01 17:00 | 2022-07-28 13:00 |  |  | Attended site and signed in, completed jsa, spoke with Fm and discussed job, located room with faulty lighting, turned all switches on and 2x foyer lights weren’t working, went and checked both boards didn’t have tripped breakers or blown fuses, set up work area, removed tubes and starters , replaced with new, lights now working,packed up, completed paperwork, signed out **job completed**
MSA-DFES | WA5680778 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | broken security lights - see notes | Electrical | Emergency & Exit Lighting | 302.195 | Pass | Pass | 0 | 0 | 1.75 | 2022-07-27 15:59 | 2022-08-03 17:00 | 2022-08-03 09:30 | 2022-08-03 17:00 | 2022-08-03 11:15 |  |  | Replaced faulty light with new
MSA-DTWD | WA5687306 | 3 | Protek 24/7 Building & Maintenance | Undercover Courtyard between H & F Blocks - Roof leak in the middle of the courtyard | Roofing | Metal Roofing | 334.39 | Fail | Fail | 2 | 2 | 1.75 | 2022-08-01 15:36 | 2022-08-08 17:00 | 2022-08-22 10:15 | 2022-08-08 17:00 | 2022-08-22 12:00 |  |  | Blocked gutters and down pipes caused by leavesUnblocked down pipesRegular cleaning required
MSA-DCA | WA5689346 | 1 | Critical Fire Protection & Training | Basement - Studio Underground - Zone 5 fire panel fault going into alarm when isolated | Fire Protection Services | Fire Protection - Monitor System | 233.555 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-02 12:14 | 2022-08-03 17:00 | 2022-08-02 13:30 | 2022-08-03 17:00 | 2022-08-02 15:15 |  |  | .
MSA-DCA | WA5692037 | 1 | Protek 24/7 Building & Maintenance | Ground-Grille at north entry door-Grille cannot be secured as some links have been unscrewed -notes | Security | Access Control | 226.925 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-03 09:50 | 2022-08-04 17:00 | 2022-08-04 07:30 | 2022-08-04 17:00 | 2022-08-04 09:15 |  |  | glass door repaired after attempted break-in
MSA-DFES | WA5699609 | 2 | AWB Co. | ground-dinning room-water leak - see notes | Building | Ceiling | 375.615 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-10 10:43 | 2022-08-15 17:00 | 2022-08-15 07:30 | 2022-08-15 17:00 | 2022-08-15 09:15 |  |  | work completed as per signature slipInvestigated area above suspected leak.found 2 x anchor points directly above area.sealed fixing points of anchors
MSA-DFES | WA5727723 | 1 | Critical Fire Protection & Training | GROUND FLOOR - MAIN BUILDING FIRE PANEL - AUDIO LINE FAULT - SECOND FLOOR PLANT ROOM | Fire Protection Services | Fire Protection - Monitor System | 233.555 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-15 11:39 | 2022-08-16 17:00 | 2022-08-15 12:50 | 2022-08-16 17:00 | 2022-08-15 14:35 |  |  | Attended site to investigate fault to EWIS system panel. On arrival found zone 4 of EWIS system in audio line fault. Second floor and plant rooms are covered by this zone. Confirmed fault still present as is not able to be reset through latched fault reset on EWIS. Due to the nature of a line fault on a speaker system the most efficient way to locate fault point is to generate audible tones, however after speaking with Deb Ridge found external contractors were working in area of fault occurrence at time of fault occurrence. After investigating work conducted by other contractors found cable run of speaker system in plant room was run behind existing external flashing. During replacement of external flashing with new, speaker cable became trapped and screwed directly through causing a break in the white/negative cable of the speaker system. After repairing and joining broken cable fault on EWIS system cleared and reset to normal operation. No further action required.
MSA-DTWD | WA5734624 | 1 | Australian Airconditioning Services Pty Ltd | Student Common room - Water leaking from split hose to roof mounted evaporative air conditioner | Air Conditioning | Room Air Conditioners | 298.9 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-16 08:16 | 2022-08-17 17:00 | 2022-08-17 11:00 | 2022-08-17 17:00 | 2022-08-17 12:45 |  |  | Found flexible hose on evap block 7 common room with pin hole leaks. Replaced flexible hose. All ok
MSA-DCA | WA5790704 | 2 | FCT SURFACE CLEANING | gantry hoardings outside KSAC (Murray St side) - External Graffiti on hoarding | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.75 | 2022-08-22 12:13 | 2022-08-25 17:00 | 2022-08-25 12:00 | 2022-08-25 17:00 | 2022-08-25 13:45 |  |  | Job is completed - Removed Graffiti on external hoardings
MSA-DTWD | WA5791451 | 2 | COMMERCIAL PLUMBING AND GAS | ground BG14-Blocked sink- photo's to follow in email | Plumbing & Drainage | Water | 206.4475 | Fail | Fail | 0 | 0 | 1.75 | 2022-08-23 07:27 | 2022-08-25 17:00 | 2022-08-26 12:45 | 2022-08-25 17:00 | 2022-08-26 14:30 |  |  | unblocked DG outside and cleared sink line
MSA-DTWD | WA5791665 | 1 | Protek 24/7 Building & Maintenance | Ground - Retic Shed - Damage to Retic shed roof, windows etc | Building | General Building | 338.93 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-23 09:01 | 2022-08-24 17:00 | 2022-08-24 12:45 | 2022-08-24 17:00 | 2022-08-24 14:30 |  | WACCES | Braf declined Removed barge that was damaged beyond repair and temp fixed down roof sheet
MSA-DFES | WA5799155 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground heritage shed-Toilet cistern button is sticking staying down intermittently, see notes | Plumbing & Drainage | Toilets/Cisterns | 316.3175 | Fail | Fail | 1 | 1 | 1.75 | 2022-08-30 09:56 | 2022-09-06 17:00 | 2022-09-12 08:00 | 2022-09-06 17:00 | 2022-09-12 09:45 |  |  | Attend site to check out toilet buttons getting stuck on heritage toilet block. On arrival found inlet valve getting stuck and over filling cistern, removed old faulty inlet valve and replaced with new, also replaced flexi hose and outlet rubber.
MSA-DTWD | WA5828929 | 3 | Ronley Holdings Pty Ltd | RETROSPECTIVE WORK ORDER DO NOT ATTEND-Workshops Dust Extraction Unit blocked filters | Electrical | General Electrical | 12610 | Fail | Fail | 16 | 16 | 1.75 | 2022-05-02 07:00 | 2022-05-06 17:00 | 2022-08-29 09:00 | 2022-05-06 17:00 | 2022-08-29 10:45 | 1 |  | 31 new filter cartridges were supplied and installed. The old damaged cartridges were removed and disposed of.
MSA-DCA | WA5831295 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Front revolving door having operation issues | Building | Doors | 501 | Fail | Fail | 0 | 0 | 1.75 | 2022-09-03 10:43 | 2022-09-05 17:00 | 2022-09-06 07:30 | 2022-09-05 17:00 | 2022-09-06 09:15 |  |  | Found ceiling panel fallen out and light cable hanging down. Reconnected light and refitted panel. Carried out full test of operation ok.
MSA-DFES | WA5832367 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Male Toilets - Power to be isolated | Electrical | General Electrical | 214.695 | Pass | Pass | 0 | 0 | 1.75 | 2022-09-05 12:36 | 2022-09-05 14:36 | 2022-09-05 13:15 | 2022-09-05 16:36 | 2022-09-05 15:00 |  |  | Arrived on site at 1315 to attend Ground Floor - Male Toilets - Power to be isolated. Followed up further information with site ops manager and confirmed all power was to be disconnected from wet area affected from pipe burst. Awaited other contractors to clear out of area and disconnected all relative circuits. Will need to return to site once repairs have been completed to reenergise. Informed staff and left site at 1500. Finished day of with vehicle inspection.
MSA-DTAG | WA5838107 | 3 | Midolo Building Services | External Area - Security Gate - Small pothole needing to be repaired - Photo followed by email | Flooring | Concrete | 246.51 | Pass | Pass | 0 | 0 | 1.75 | 2022-09-08 10:58 | 2022-09-15 17:00 | 2022-09-13 11:00 | 2022-09-15 17:00 | 2022-09-13 12:45 |  |  | pothole filled/repaired
MSA-DCA | WA5853847 | 2 | Protek 24/7 Building & Maintenance | Ground Level - Learning Studio 1 / Foyer - Operable wall is not closing - See notes below | Building | General Building | 318.1 | Pass | Pass | 0 | 0 | 1.75 | 2022-09-12 11:35 | 2022-09-15 17:00 | 2022-09-13 11:15 | 2022-09-15 17:00 | 2022-09-13 13:00 |  |  | Pricing for this will be raised under JN 21064 - Neil Duchan 13092022Re positioned hinge to door
MSA-DTAG | WA5880168 | 2 | AHS Services WA Pty Ltd (Anchor) | Ground floor - Public Disable toilet - Blocked toilet & Faulty cistern | Plumbing & Drainage | Toilets/Cisterns | 267.62 | Fail | Fail | 0 | 0 | 1.75 | 2022-09-15 11:00 | 2022-09-20 17:00 | 2022-09-23 07:30 | 2022-09-20 17:00 | 2022-09-23 09:15 |  |  | Adjusted flush level and tested multiple times
MSA-DTWD | WA5962586 | 0 | AWB Co. | Lost power to fire alarms | Electrical | General Electrical | 327.81 | Pass | Pass | 0 | 0 | 1.75 | 2022-09-19 15:28 | 2022-09-19 17:28 | 2022-09-19 16:30 | 2022-09-19 19:28 | 2022-09-19 18:15 |  |  | Attended site and signed in. Completed paperwork. Located fire panel with no power. Went to board and located fire indication panel fuse and tested for voltage. Voltage was present. Had to get key from Darren to open fire panel cabinet. Tested for voltage. Voltage was present. Turned off isolation switch in panel. Flicked back on and fire panel energised. Only lasted 1 minute and looked like voltage was fluctuating and then panel lost power. Isolated circuit from DB. Tested isolation switch in fire panel and found it to be faulty. Bypassed switch to see if fire panel would work with switch removed. Re energised fire panel and fire panel seemed to be working. Resistor on circuit board was very hot so decided to leave it isolated. Fm agreed. Spoke to fm and he said fire company will be likely to engage with electrician. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5990105 | 3 | Equans Mechanical Services Australia | Water treatment tech advises that cooling tower floats need to be adjusted as the tanks are overflow | Air Conditioning | Cooling Tower | 197.0775 | Pass | Pass | -1 | -1 | 1.75 | 2022-10-04 13:02 | 2022-10-11 17:00 | 2022-10-05 14:00 | 2022-10-11 17:00 | 2022-10-05 15:45 |  |  | ON-SITE. INVESTIGATED ISSUE WITH COOLING TOWER REPORTED AS OVERFLOWING DRAIN. FOUND NO EVIDENCE WHEN CHECKING BUTFOUND TOWER 3 FLOAT LEVEL TO BE SLIGHTLY HIGH. LOWEREDFLOAT LEVEL AND CHECKED OPERATION. ALL OK. COMPLETED PAPERWORK AND LOGGED OFF JOB.
MSA-DTWD | WA5995214 | 2 | AHS Services WA Pty Ltd (Anchor) | D - Block G/ Floor - Canteen Kitchen - the flick mixer on the left side basin is broken | Plumbing & Drainage | Water | 329.8525 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-06 11:26 | 2022-10-11 17:00 | 2022-10-10 10:30 | 2022-10-11 17:00 | 2022-10-10 12:15 |  |  | Completed
MSA-DCA | WA6001007 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Open office - Pendant light faulty fitting | Electrical | Lighting, Internal | 214.695 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-10 11:44 | 2022-10-11 17:00 | 2022-10-10 13:15 | 2022-10-11 17:00 | 2022-10-10 15:00 |  |  | Arrived on site and signed in at 13:15 to investigate faulty light fitting in open office. Lamp holder active filament was loose.Screwed it in so there was a tight connection and found light fitting to work normally. Notified staff of works performed andleft site at 15:00.
MSA-DTWD | WA6014478 | 0 | AWB Co. | Room S4 - Student zapped in S4 / need all circuit & 1 x equipment tested - See notes below | Electrical | Testing & Tagging | 218.2075 | Fail | Pass | 0 | 0 | 1.75 | 2022-10-12 09:30 | 2022-10-12 11:30 | 2022-10-12 11:45 | 2022-10-12 13:30 | 2022-10-12 13:30 |  |  | Attended site and signed in. Completed JSA. Located s4 room and found tagged out gpo. Located equipment to be tested. Carried out all relevant testing. No faults found. Called western power to advise. All okay class okay to resume. Replace gpo with broken face plate. Tested all okay. Signed out. Job complete
MSA-DCA | WA6019862 | 2 | Protek 24/7 Building & Maintenance | Alexander Library Bld, Lvl 3 - CEO Office - Door handle leading to exec suite difficult to open | Building | Doors | 181.11 | Pass | Pass | -1 | -1 | 1.75 | 2022-10-13 08:47 | 2022-10-18 17:00 | 2022-10-14 09:00 | 2022-10-18 17:00 | 2022-10-14 10:45 |  |  | Disassembly of handle and striker Lubed parts, filed off burs and imperfections causing stiffness Re assembled handle and locking hardware
MSA-DTWD | WA6048829 | 2 | Water2water Pty Ltd | The hot water boiler is not working in the kitchenette - see notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 550.945 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-17 13:47 | 2022-10-20 17:00 | 2022-10-20 10:15 | 2022-10-20 17:00 | 2022-10-20 12:00 |  |  | Replaced inlet solenoid and element on Rheem hot water unit
MSA-DFES | WA6088774 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | ground-Yard / side of the station-White piping cracked - see notes | Plumbing & Drainage | Water | 280.38 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-19 10:30 | 2022-10-24 17:00 | 2022-10-24 09:30 | 2022-10-24 17:00 | 2022-10-24 11:15 |  |  | Repaired broken 65mm DWV pipework.
MSA-DTWD | WA6109201 | 2 | AWB Co. | Faulty suspended GPO - see notes | Electrical | Lighting, Internal | 426.47 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-20 15:11 | 2022-10-25 17:00 | 2022-10-25 07:15 | 2022-10-25 17:00 | 2022-10-25 09:00 |  |  | Attended site and signed in, completed JSA,located faulty gpo, went to wholesaler to pick up parts, returned to site, isolated circuit, removed faulty pendant gpo , replaced with new, re energised circuit, tested gpo and working as intended , went to d block and raised GPOs and airlines as per fm request, packed up, cleaned up, signed out, job completed
MSA-DTWD | WA6113456 | 3 | AHS Services WA Pty Ltd (Anchor) | Room 213/214 - Koolark Centre Meeting Rooms - Plumbing leak from ceiling | Plumbing & Drainage | Water | 216.7825 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-24 11:47 | 2022-10-31 17:00 | 2022-10-31 10:15 | 2022-10-31 17:00 | 2022-10-31 12:00 |  |  | Found split in dishwasher hose in kitchen above.Sealed and advised to close
MSA-DTAG | WA6127951 | 2 | Midolo Building Services | 1987 - Sheriffs office - Door - See notes | Building | Doors | 760.13 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-26 11:11 | 2022-10-31 17:00 | 2022-10-31 09:00 | 2022-10-31 17:00 | 2022-10-31 10:45 |  |  | new door closer installed
MSA-MRWA | WA6128293 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 8 - MD's Bathroom - Replace failing sensor in MD’s bathroom airlock | Electrical | Lighting, Internal | 230.495 | Fail | Fail | 0 | 0 | 1.75 | 2022-10-26 14:23 | 2022-10-31 17:00 | 2022-11-02 06:00 | 2022-10-31 17:00 | 2022-11-02 07:45 |  |  | Arrived on site at 06:00 to investigate sensor In managing directors bathroom airlock not working. Tested sensors and all functional, light has globe on way out. Left site to collect correct globe from wholesaler. Replaced globe and tested sensor function all okay. Left site at 07:45
MSA-DTWD | WA6128981 | 2 | Damian Rak Electrical Pty Ltd | Outside floodlight faulty | Electrical | Lighting, External |  | Pass | Pass | 0 | 0 | 1.75 | 2022-10-27 09:44 | 2022-11-01 17:00 | 2022-10-31 08:00 | 2022-11-01 17:00 | 2022-10-31 09:45 |  |  | 1x PE cell night switch
MSA-DTWD | WA6132056 | 2 | AWB Co. | Water leak in Rm U019 | Roofing | Tiled Roofing | 400.375 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-31 11:26 | 2022-11-03 17:00 | 2022-11-03 12:00 | 2022-11-03 17:00 | 2022-11-03 13:45 |  |  | attended site, inspected leak above room u19, access roof to find joins around ventilation to be flacking, resealed all joins to make water tight, cleaned and packed up site
MSA-DTWD | WA6147681 | 2 | Water2water Pty Ltd | Level 2-West water drink fountain not working | Plumbing & Drainage | Water | 1019.125 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-03 09:09 | 2022-11-08 17:00 | 2022-11-07 08:00 | 2022-11-08 17:00 | 2022-11-07 09:45 |  |  | Replaced fountain chiller with new due to failure of old unit.
MSA-DTWD | WA6149288 | 2 | BAKE-QUIP PTY LTD | E Block - LSK -Restuarant Kitchen - Dishwasher Leaking - See notes below | Equipment | Cleaning Equipment | 262.5 | Fail | Fail | 0 | 0 | 1.75 | 2022-11-04 13:47 | 2022-11-09 17:00 | 2022-11-10 08:00 | 2022-11-09 17:00 | 2022-11-10 09:45 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA6155809 | 2 | AHS Services WA Pty Ltd (Anchor) | Kitchen next to reception - Water is not draining in the sink - Partially Blocked | Plumbing & Drainage | Water | 140.77 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-08 13:46 | 2022-11-11 17:00 | 2022-11-09 08:45 | 2022-11-11 17:00 | 2022-11-09 10:30 |  |  | Used handsnake to clear -line full of coffee
MSA-DFES | WA6177989 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Academy Store - leak under the kitchen sink and leaking all over the floor | Plumbing & Drainage | Water | 228.44 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-14 08:49 | 2022-11-15 17:00 | 2022-11-14 12:45 | 2022-11-15 17:00 | 2022-11-14 14:30 |  |  | Attend site to check out leak in academy shed. On arrival found water leaking in new cupboards, found water leaking from new water connection under sink. Removed broken fitting and replaced withnew mi cupling, tested and checked all working correctly.
MSA-DTWD | WA6178613 | 1 | CONNECT SECURITY SYSTEMS | Security PIR not working behind the main service counter of the library | Security | Security Management System | 289.33 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-14 12:31 | 2022-11-15 17:00 | 2022-11-15 11:00 | 2022-11-15 17:00 | 2022-11-15 12:45 |  |  | Removed redundant PIR and repaired holes in wall left after removing.
MSA-DFES | WA6184108 | 3 | Protek 24/7 Building & Maintenance | Engine Room - Change room 2 and Gym - Multiple door seals damaged - see notes | Building | Doors | 222.91 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-15 10:10 | 2022-11-22 17:00 | 2022-11-21 12:00 | 2022-11-22 17:00 | 2022-11-21 13:45 |  |  | Replaced 2 x bottom door seals with better suited brush seals
MSA-DTWD | WA6253549 | 1 | BJ SYSTEMS | Faulty Main door entry swipe plus possibly other internal doors | Security | Access Control | 931.1 | Fail | Fail | 0 | 0 | 1.75 | 2022-11-22 10:28 | 2022-11-23 17:00 | 2022-11-25 07:30 | 2022-11-23 17:00 | 2022-11-25 09:15 |  |  | Sign in FM A Block, check Gallagher reports, drive down to McLarty. Inspect controller and devices associated. PSU failed. Replace faulty Gallagher PSU, replace faulty 2018 12V 7AH backup battery. Check, inspect and secure access doors. Resync controller database, sign out
MSA-MRWA | WA6253605 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | power to ground level offices has tripped | Electrical | General Electrical | 214.695 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-22 10:53 | 2022-11-23 17:00 | 2022-11-22 11:45 | 2022-11-23 17:00 | 2022-11-22 13:30 |  |  | Tyler Beard (22/11/2022) - Work NoteAttended site at 1145. Found that RCD B19 was in a de-energised state. The breaker would not reset. I then unplugged some of the power boards on the final sub-circuit and was then shale to re-energise the circuit successfully, I plugged in all the power boards in the field and the circuit remained energised. When attempting the changeover, the RCD trips when all the field power boards are connected however does not trip if they are unplugged, and then reconnected after supply changeover. Left site at 1330.
MSA-DFES | WA6255807 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Front entry - Ground - Soil has dropped around Water Drainage Sump. | Plumbing & Drainage | Drainage | 332.3575 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-23 14:01 | 2022-11-30 17:00 | 2022-11-28 09:30 | 2022-11-30 17:00 | 2022-11-28 11:15 |  |  | Attended site for a sunken soil, upon arrival we parked trailer behind the work area, set up barricades and cones. Them we compacted the sand which was already there, then we unloaded all the yellow sand from the trailer, and compacted all of it nicely around the tank. We then packed up, cleaned up and signed out.
MSA-DCA | WA6292698 | 1 | Earth & Water Pty Ltd | Ground Floor - External Area - Hydrowise app is not operational (see notes) | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.75 | 2022-11-29 12:17 | 2022-11-30 17:00 | 2022-11-29 13:30 | 2022-11-30 17:00 | 2022-11-29 15:15 |  |  | Completed
MSA-DTWD | WA6293583 | 2 | Protek 24/7 Building & Maintenance | 2G2 Staff room - Broken door closer | Building | Doors | 668.695 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-30 09:54 | 2022-12-05 17:00 | 2022-12-02 12:00 | 2022-12-05 17:00 | 2022-12-02 13:45 |  | WACCES | Removed and replaced damaged door closer to block2 staff room
MSA-DTWD | WA6360057 | 3 | GRAFFITI FORCE PTY LTD | Campus pathway entrance Dixon Rd - Graffiti removal | Cleaning | Graffiti | 401.5 | Fail | Fail | 3 | 3 | 1.75 | 2022-12-07 08:26 | 2022-12-14 17:00 | 2023-01-03 07:30 | 2022-12-14 17:00 | 2023-01-03 09:15 |  |  | REMOVAL OF GRAFFITI FROM PATHWAY ENTRANCE ON DIXON RD
MSA-DFES | WA6401429 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | main changing room toilet-Ventilation Fan in Main Changing room toilet is not working | Electrical | General Electrical | 267.195 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-04 11:47 | 2023-01-11 17:00 | 2023-01-09 07:15 | 2023-01-11 17:00 | 2023-01-09 09:00
MSA-DTWD | WA6405486 | 2 | BAKE-QUIP PTY LTD | Canteen kitchen - Dishwasher does not dispense liquids at times | Equipment | Cleaning Equipment | 346.25 | Fail | Fail | 1 | 1 | 1.75 | 2023-01-09 14:20 | 2023-01-12 17:00 | 2023-01-20 07:30 | 2023-01-12 17:00 | 2023-01-20 09:15
MSA-DFES | WA6405597 | 2 | Go Doors | Ground - Engine room - Door is faulty and timer does not work either | Building | Automatic Doors | 552.35 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-09 16:38 | 2023-01-12 17:00 | 2023-01-10 08:00 | 2023-01-12 17:00 | 2023-01-10 09:45
MSA-DTAG | WA6493808 | 1 | AHS Services WA Pty Ltd (Anchor) | Kitchen – Prisoners Review Board side - Blocked kitchen sink – water very slow to go down | Plumbing & Drainage | Drainage | 213.9925 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-18 15:50 | 2023-01-19 17:00 | 2023-01-19 09:00 | 2023-01-19 17:00 | 2023-01-19 10:45
MSA-DFES | WA6509766 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | South Admin block - Lid of septic tank is broken | Plumbing & Drainage | Sewer Drains & Septic Systems | 245.22 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-20 14:57 | 2023-01-25 17:00 | 2023-01-23 10:15 | 2023-01-25 17:00 | 2023-01-23 12:00
MSA-DTAG | WA6516364 | 3 | Midolo Building Services | Rockingham Court - hang picture hooks - see notes | Building | Internal Walls | 241.51 | Fail | Fail | 2 | 2 | 1.75 | 2023-01-23 11:06 | 2023-01-31 17:00 | 2023-02-13 13:30 | 2023-01-31 17:00 | 2023-02-13 15:15
MSA-DFES | WA6518010 | 2 | Protek 24/7 Building & Maintenance | Ground - Secretary Office - Door isnt aligning/hard / difficult to shut and operate. | Building | Doors | 335.71 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-24 15:25 | 2023-01-30 17:00 | 2023-01-27 10:30 | 2023-01-30 17:00 | 2023-01-27 12:15
MSA-DCA | WA6521058 | 0 | TK Elevator Australia Pty Ltd | Lift is stuck | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1.75 | 2023-01-30 07:30 | 2023-01-30 09:30 | 2023-01-30 11:45 | 2023-01-30 11:30 | 2023-01-30 13:30
MSA-DCA | WA6521903 | 0 | Dormakaba Australia Pty Ltd | external sliding auto door will not close-Relay number-249 | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 1.75 | 2023-01-30 14:19 | 2023-01-30 16:19 | 2023-01-30 15:45 | 2023-01-30 18:19 | 2023-01-30 17:30
MSA-DTWD | WA6523278 | 2 | AWB Co. | Repair defective lights | Electrical | Lighting, Internal | 295.6375 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-31 14:00 | 2023-02-03 17:00 | 2023-02-02 09:00 | 2023-02-03 17:00 | 2023-02-02 10:45
MSA-DTWD | WA6526733 | 3 | AWB Co. | Airlock light out | Electrical | Lighting, Internal | 330.7075 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-01 10:21 | 2023-02-08 17:00 | 2023-02-07 14:00 | 2023-02-08 17:00 | 2023-02-07 15:45
MSA-DTWD | WA6526915 | 2 | AWB Co. | GPO with broken Switch | Electrical | General Electrical | 274.0875 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-01 11:56 | 2023-02-06 17:00 | 2023-02-03 15:30 | 2023-02-06 17:00 | 2023-02-03 17:15
MSA-DFES | WA6539545 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Grounds level - various lights not working - see notes | Electrical | Lighting, Internal | 313.935 | Pass | Pass | -1 | -1 | 1.75 | 2023-02-08 13:57 | 2023-02-15 17:00 | 2023-02-10 11:45 | 2023-02-15 17:00 | 2023-02-10 13:30
MSA-DFES | WA6604007 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Operational Delivery & Hallway near TDSC Office - blinking lights | Electrical | Lighting, Internal | 461.325 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-17 14:19 | 2023-02-24 17:00 | 2023-02-21 11:45 | 2023-02-24 17:00 | 2023-02-21 13:30
MSA-DTWD | WA6650899 | 1 | Equans Mechanical Services Australia | South west corner of glasshouse - misting room - Air-con not working | Air Conditioning | Ducted Split System | 197.0775 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-20 14:23 | 2023-02-21 17:00 | 2023-02-21 13:15 | 2023-02-21 17:00 | 2023-02-21 15:00
MSA-DTWD | WA6654087 | 2 | COMMERCIAL PLUMBING AND GAS | toilet seat broken | Plumbing & Drainage | Toilets/Cisterns | 480.7675 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-21 09:37 | 2023-02-24 17:00 | 2023-02-22 13:15 | 2023-02-24 17:00 | 2023-02-22 15:00
MSA-DTWD | WA6671637 | 1 | Critical Fire Protection & Training | Alarm going on after hours | Fire Protection Services | Fire Protection - Monitor System | 408.555 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-23 09:27 | 2023-02-24 17:00 | 2023-02-24 08:15 | 2023-02-24 17:00 | 2023-02-24 10:00
MSA-DTWD | WA6672209 | 3 | SENTINEL LOCK SERVICE PTY LTD | Faulty Lock on office door | Security | Locksmith | 422.54 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-23 13:39 | 2023-03-02 17:00 | 2023-03-01 13:30 | 2023-03-02 17:00 | 2023-03-01 15:15
MSA-DTWD | WA6673224 | 2 | AHS Services WA Pty Ltd (Anchor) | Female Toilets - Left hand toilet flushes and then will not flush again | Plumbing & Drainage | Toilets/Cisterns | 436.9625 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-24 11:53 | 2023-03-01 17:00 | 2023-03-01 07:15 | 2023-03-01 17:00 | 2023-03-01 09:00
MSA-DTWD | WA6674485 | 2 | M Construction (WA) | E block Stores area has 4 signs to be re secured to the wall. | Building | General Building | 231.09 | Fail | Fail | 0 | 0 | 1.75 | 2023-02-27 10:20 | 2023-03-02 17:00 | 2023-03-03 11:00 | 2023-03-02 17:00 | 2023-03-03 12:45
MSA-DTWD | WA6683560 | 1 | AWB Co. | Compressor Room - RO Unit for science labs not working | Electrical | General Electrical | 342.16 | Pass | Pass | -1 | -1 | 1.75 | 2023-03-03 09:55 | 2023-03-07 17:00 | 2023-03-03 12:45 | 2023-03-07 17:00 | 2023-03-03 14:30
MSA-DTWD | WA6689515 | 3 | Protek 24/7 Building & Maintenance | Gutter has come away from roof. | Building | General Building | 355.53 | Pass | Pass | -1 | -1 | 1.75 | 2023-03-08 12:41 | 2023-03-15 17:00 | 2023-03-09 12:45 | 2023-03-15 17:00 | 2023-03-09 14:30
MSA-DTWD | WA5087383 | 1 | Dormakaba Australia Pty Ltd | south entry door - A block - auto door not responding to key or sensor - has to be forces open | Building | Automatic Doors | 995.59 | Pass | Pass | 0 | 0 | 1.75 | 2022-01-24 09:00 | 2022-01-25 17:00 | 2022-01-24 10:29 | 2022-01-25 17:00 | 2022-01-24 12:14 |  |  | Inspected door and found that water had got into the internal activation sensor and that this had faulted the sensor and pcm. Replaced faulty pcm and internal activation sensor as necessary, checked over and tested operation upon completion and left in good working order.
MSA-DTWD | WA5018233 | 1 | AWB Co. | Block 8 - Main plant room - First floor - No power to A/C 4 | Electrical | General Electrical | 202.78 | Pass | Pass | 0 | 0 | 1.75 | 2022-01-14 10:06 | 2022-01-17 17:00 | 2022-01-17 07:00 | 2022-01-17 17:00 | 2022-01-17 08:45 |  |  | Attended site and signed in. Completed JSA. Located block 8 plant room. Investigated power not working to AC 4. Found to be missing supply voltage to blue phase. Went to main distribution board and check and tested power.all mains is okay. Tested at fuses to AC4. Found blue phase to be partially supplying power. Located problem to fuse holder internally had become loose and been arcing and not making contact. Resecured and connect properly. Reinstated power to AC4. Unit did not start, tested internal control box for power and found all the be okay. Went through checks and found overload to compressor tripped due to under voltage supply. Reset and tested all okay. Ran aircon with facilities and all is working correctly. Clean and tidy site. Signed out, job complete
MSA-DTAG | WA5090677 | 3 | AWB Co. | Level 1 - DPP - GPO next to double door frame is not working | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1.75 | 2022-01-25 14:56 | 2022-02-02 17:00 | 2022-01-31 12:15 | 2022-02-02 17:00 | 2022-01-31 14:00 |  |  | Attended site, signed in, completed jsa, spoke to site contact about job, site contact advised that someone up at dpp will show me the gpo that wasn’t working as they reported it, went to dpp and spoke with receptionist, she said person who reported gpo was on annual leave, spoke to others in the area and they weren’t sure, went around to all GPOs in the area and tested them , all GPOs had voltage, checked that all RCDs in distribution board were on , nothing was tripped , packed up , completed paperwork,signed out ***job completed ***
MSA-DTWD | WA5091714 | 2 | AWB Co. | Level 2 0- B2220 - 3x faulty lights | Electrical | Lighting, Internal | 233.49 | Pass | Pass | 0 | 0 | 1.75 | 2022-01-27 10:31 | 2022-02-01 17:00 | 2022-01-31 07:45 | 2022-02-01 17:00 | 2022-01-31 09:30 |  |  | Attended site and signed in. Completed JSA. Located B 2220. Found 4 x lights inside room. 3 lights not working. Supply and replaced lamps to all 4 lights. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5092625 | 2 | AWB Co. | Ground - C1 Horticulture Office - Light fitting disintegrated when changing faulty tube | Electrical | Lighting, Internal | 569.505 | Pass | Pass | 0 | 0 | 1.75 | 2022-01-28 08:34 | 2022-02-02 17:00 | 2022-02-01 14:30 | 2022-02-02 17:00 | 2022-02-01 16:15 |  |  | Attended site and signed in. Completed JSA. Located room C1. Removed 2x faulty light fittings. Supplied and replaced with 2x new led battens. Tested for correct operation. Cleaned up site. **job complete**
MSA-DTWD | WA5098476 | 3 | AWB Co. | Drill Press 62 DOL contactor sticking | Electrical | General Electrical | 384.12 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-01 09:43 | 2022-02-08 17:00 | 2022-02-08 12:15 | 2022-02-08 17:00 | 2022-02-08 14:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Figured out what part we needed. Went to wholesaler to pick up parts ( for 2 jobs ). Returned to site. Set up work area. Isolated drill press , removed old stop/start contactor, mounted new stop/start to drill press and wired it in, tested all components worked including foot pedal isolator , cleaned up work area , packed up, took picture. Completed paperwork, signed out,Job complete
MSA-DCA | WA5105378 | 0 | Automatic Fire Protection (ARA) | fire panel - Fire Brigade attended last night for zone 1 - please investigate need isolated | Fire Protection Services | Fire Protection - Fire Brigade | 146.44 | Fail | Fail | 0 | 0 | 1.75 | 2022-02-04 10:03 | 2022-02-04 12:03 | 2022-02-04 14:30 | 2022-02-04 14:03 | 2022-02-04 16:15 |  |  | Technician Note4/02/22 EILiaised with operation manager & checked history log & detector status.All ok.
MSA-DTWD | WA5108005 | 3 | AWB Co. | ceiling leak water - possibly from box gutter | Building | Ceiling | 368.75 | Pass | Pass | -1 | -1 | 1.75 | 2022-02-08 10:49 | 2022-02-15 17:00 | 2022-02-11 07:00 | 2022-02-15 17:00 | 2022-02-11 08:45 |  |  | Repaired joint to leaking box gutter
MSA-DTWD | WA5109948 | 2 | AWB Co. | Classroom M007 - 3x faulty Fluro lights | Electrical | General Electrical | 371.56 | Pass | Pass | 0 | 0 | 1.75 | 2022-02-09 14:23 | 2022-02-14 17:00 | 2022-02-14 13:45 | 2022-02-14 17:00 | 2022-02-14 15:30 |  |  | Attended site, signed in, completed jsa, spoke to fm about job,isolated lighting circuits, removed old tubes and starters , replaced with new tubes and starters, disposed of tubes in designated tube boxes/bin, reenergised lights and tested , all working as intended, cleaned up work area, packed up , completed paperwork,signed out ***job completed ***
MSA-DTWD | WA5175652 | 3 | AWB Co. | B07 - Light needs new tombstone | Electrical | General Electrical | 304.63 | Pass | Pass | -1 | -1 | 1.75 | 2022-02-21 12:41 | 2022-02-28 17:00 | 2022-02-21 13:45 | 2022-02-28 17:00 | 2022-02-21 15:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located room B07. Found fitting with broken tombstones and found there were 2 fittings that had the wrong colour lighting. Went to H block to grab 2x tombstones, 6x tubes and 6x starters. Returned to room and replaced tubes and starters. Isolated lights to change tombstones and put fitting back together with new tubes. All lights are now working as intended. Packed and cleaned up work area. Took pictures before and after. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5201217 | 3 | AWB Co. | 4x faulty paper tower dispenser in Kitchens - require replacement | Building | Internal Walls | 315.03 | Pass | Pass | -1 | -1 | 1.75 | 2022-03-02 12:47 | 2022-03-10 17:00 | 2022-03-03 12:15 | 2022-03-10 17:00 | 2022-03-03 14:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Fm showed us where he wanted new paper towel dispensers fitted. Went around site and replaced all faulty dispensers with new ones. Took pictures and cleaned up all work areas. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5201511 | 2 | AWB Co. | Two wall fluorescent lights Brocken, and wall switch need removing. - see notes below | Electrical | General Electrical | 202.78 | Fail | Fail | 0 | 0 | 1.75 | 2022-03-02 15:48 | 2022-03-08 17:00 | 2022-03-09 07:00 | 2022-03-08 17:00 | 2022-03-09 08:45 |  |  | Attended site and signed in. Completed JSA. Located faulty lights in wet lab. Spoke with site and was advised to remove and blank off. Disconnected and removed from wall and disposed the lights. Made safe cabling, blanked off cables on wall. Disconnect and made safe light switch on wall. Reinstated power to room. Whilst on site, facilities asked for some investigation onto where a building was fed from, went through and found what site was needing to know. Signed out. Job complete
MSA-DFES | WA5207262 | 0 | Australian HVAC Services Pty. Ltd. | Main unit/ Dorm 1 &2 - Air cons are not working | Air Conditioning | Room Air Conditioners | 305.345 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-08 11:50 | 2022-03-08 13:50 | 2022-03-08 13:00 | 2022-03-08 15:50 | 2022-03-08 14:45 |  |  | Attended service call & met client.tesyed dorm ac 1& 2, & corrected controls to operate at serpoints. Tested ok.Found ac6 on wrong setting & changed settings to suit.Found ac5 not running due to water level. Accessed pump & found float stuck. Freed float to alow fault to clear & pump to run.
MSA-DTWD | WA5226391 | 2 | AWB Co. | Level 1 - Metal Fabrication building night lights around building not coming on room F001/COO1/HOO1 | Electrical | General Electrical | 202.78 | Pass | Pass | 0 | 0 | 1.75 | 2022-03-14 08:31 | 2022-03-17 17:00 | 2022-03-16 07:00 | 2022-03-17 17:00 | 2022-03-16 08:45 |  |  | Attended site signed in completed jsa. spoke with site contact in regards to job. Found tripped cb in board. Turned it on and pushed timer on overide and one circuit tripped W40. Legend says outside lights i assume water or wear and tear. Would be easier and better to replace all as we will need a ewp boom lift to investigate fault anyway. x7 square metal halide box fittings and x1 flood light are off. will need ewp boom lift as uneven grounds and scissor lift will beep unlevel, also gas bottles in the way. One light is behind a few tree’s so will need to get that chopped down to access light fitting.Notified site of this and will send to make a BRAF. **BRAF WAS SUBMITTED AND DECLINED - NO FURTHER WORKS**
MSA-DTWD | WA5226902 | 3 | AWB Co. | B146 - Replace faulty power point | Electrical | General Electrical | 323.73 | Pass | Pass | -1 | -1 | 1.75 | 2022-03-14 15:01 | 2022-03-21 17:00 | 2022-03-16 07:00 | 2022-03-21 17:00 | 2022-03-16 08:45 |  |  | Attended site and signed in, completed jsa, spoke to fm about job, located gpo in B6 , tested gpo and switch wasn’t working, 2 lights also out which fm wanted fixed, went to wholesaler to pick up parts , returned to site, isolated power circuit, removed old gpo and replaced with new, tested gpo and working as intended , replaced 2x lights, tested lights and working as intended , completed paperwork , packed up, signed out Job completed
MSA-DTWD | WA5307149 | 2 | Water2water Pty Ltd | B2220 Staff Office - Water leaking from unit and error on display screen | Plumbing & Drainage | Drainage | 281.4125 | Pass | Pass | 0 | 0 | 1.75 | 2022-04-07 10:39 | 2022-04-12 17:00 | 2022-04-12 09:35 | 2022-04-12 17:00 | 2022-04-12 11:20 |  |  | System off on arrival. Hard wired. No drain on wall mount. Used 2 Flexi hoses and nipple for temporary fix, waiting to see if tap on wall mount stops leaking. Also fixed flow out of fountain tap.
MSA-DTWD | WA5325501 | 3 | AWB Co. | A Block- Accrod Toilet - Damaged Toiler roll holder | Building | General Building | 208.505 | Pass | Pass | -1 | -1 | 1.75 | 2022-04-14 09:39 | 2022-04-26 17:00 | 2022-04-21 13:45 | 2022-04-26 17:00 | 2022-04-21 15:30 |  |  | Purchase new toilet roll holder and swap out damaged one
MSA-DTAG | WA5460307 | 2 | AWB Co. | Level 8 - Area near judicial lifts - Fluorescent lights are missing covers | Electrical | General Electrical | 318.9275 | Pass | Pass | -1 | -1 | 1.75 | 2022-05-18 12:47 | 2022-05-23 17:00 | 2022-05-19 07:00 | 2022-05-23 17:00 | 2022-05-19 08:45 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Located 2x light fittings with missing covers. Went too multiple storerooms/plant rooms looking for covers. We were only able to find one cover that wasn’t damaged. Installed cover to one of the lights. Went down and spoke to Iain he advised us to close out the job as they will rectify on routine maintenance. Packed all gear. **job complete**
MSA-DTWD | WA5470686 | 2 | Protek 24/7 Building & Maintenance | Gutters above BG09 - gutters are rusted - flashing & roof sheets in this area need to be inspected | Roofing | Guttering | 310.75 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-23 11:37 | 2022-05-26 17:00 | 2022-05-26 11:30 | 2022-05-26 17:00 | 2022-05-26 13:15 |  |  | Inspect Rusted gutters above BG09
MSA-DTWD | WA5478570 | 3 | AWB Co. | Lighting RCD tripped - will not reset | Electrical | Lighting, Internal | 202.78 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-26 12:25 | 2022-06-02 17:00 | 2022-06-01 07:00 | 2022-06-02 17:00 | 2022-06-01 08:45 |  |  | Attended site and signed in. Completed JSA. Located room with faulty light circuit. Carried out tests to room and found lights near the door reported with leak to be dry and not effected by the water ingress. Tested light fittings and no fault present. Checked out further lights and found in the back corner has been a big water leaks onto a light and ceiling. It’s high up and will require a new led panel 1200x300mm. Made safe light fitting for leak to be repaired. Notified site. Signed out. Job complete
MSA-DCA | WA5479810 | 2 | FCT SURFACE CLEANING | A Block - Art work attached to fence line on east side - Graffiti on canvas canvas photographic | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.75 | 2022-05-27 11:42 | 2022-06-01 17:00 | 2022-06-01 10:00 | 2022-06-01 17:00 | 2022-06-01 11:45 |  |  | job completed - removed graffiti
MSA-DTWD | WA5481847 | 2 | AWB Co. | Room A126 Training Services - tube lighting faulty | Electrical | Lighting, Internal | 201.5275 | Pass | Pass | 0 | 0 | 1.75 | 2022-05-31 07:18 | 2022-06-02 17:00 | 2022-06-01 13:45 | 2022-06-02 17:00 | 2022-06-01 15:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about accessing Keys. Called FM as he wasn’t on site and liaised about works. Went through and retubed multiple lights. Notified site of works complete. Completed paperwork. Signed out. **job complete**
MSA-DTWD | WA5497035 | 3 | AWB Co. | Between C101 & C102 - water is leaking through round skylight | Building | General Building | 375 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-09 13:54 | 2022-06-16 17:00 | 2022-06-16 13:00 | 2022-06-16 17:00 | 2022-06-16 14:45 |  |  | Attended, c-block 1st floor bank of 4 skylights. Sealed No. 3 from stairwell, if issue continues may need alternativesolution.
MSA-DTWD | WA5498464 | 3 | AWB Co. | A Block - East End Stairs - Lights in Stairwell East End A Block - Faulty | Electrical | General Electrical | 218.46 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-10 07:16 | 2022-06-16 17:00 | 2022-06-14 12:15 | 2022-06-16 17:00 | 2022-06-14 14:00 |  |  | Attended site and signed in. Completed JSA. Located eastern stairwell in A block. Went up all floors to check lights not working. Took large ladder into stairwell. Supply and replaced tubes and starters to lights. Cleaned out diffusers. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5498659 | 1 | AWB Co. | Q008 - water is dripping from the ceiling fan closest to the door | Building | General Building | 375 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-10 07:43 | 2022-06-10 17:00 | 2022-06-10 12:15 | 2022-06-10 17:00 | 2022-06-10 14:00 |  |  | Cleaned and sealed multiple screw penetrations.Sealed multiple loose screwsSealed vent flashing joints
MSA-DTWD | WA5498858 | 3 | Protek 24/7 Building & Maintenance | AF3 - Water leaking through top of window frame | Building | General Building | 326.15 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-10 08:10 | 2022-06-17 17:00 | 2022-06-15 10:00 | 2022-06-17 17:00 | 2022-06-15 11:45 |  |  | Repair water leak coming from top of window frame - reset
MSA-DTWD | WA5564433 | 2 | AWB Co. | J Block - Electrical Board - no power to part of the block | Electrical | General Electrical | 304.63 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-21 10:33 | 2022-06-24 17:00 | 2022-06-21 12:15 | 2022-06-24 17:00 | 2022-06-21 14:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,went to j block and discussed work with John Holland contractor, located pit and found cable origin , checked board and found cable to be isolated , put out of service tag on cable in pit, found faulty circuit in db1 jblock, rcd wouldn’t reset, found fault to be in water fountain, tagged out water fountain and reset circuit, completed paperwork, packed out** job completed**
MSA-DTWD | WA5564615 | 2 | AWB Co. | Roof Leaking | Roofing | Metal Roofing | 368.25 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-21 11:37 | 2022-06-24 17:00 | 2022-06-23 12:15 | 2022-06-24 17:00 | 2022-06-23 14:00 |  |  | Investigated leak over spray booth.found flashing detail with split silicone.cleaned back all perished silicone and renewed
MSA-DCA | WA5566510 | 2 | FCT SURFACE CLEANING | Ground – external - Livingstone’s café pod – northern side - Red graffiti on northern side of café | Cleaning | Graffiti |  | Fail | Fail | 1 | 1 | 1.75 | 2022-06-23 08:56 | 2022-06-28 17:00 | 2022-07-04 13:00 | 2022-06-28 17:00 | 2022-07-04 14:45 |  |  | Removed graffiti from livingstone's café pod — northern side.
MSA-DTWD | WA5567430 | 3 | AWB Co. | N117 -faulty conduit exposed on Bench | Electrical | General Electrical | 202.78 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-24 09:04 | 2022-07-01 17:00 | 2022-06-29 07:00 | 2022-07-01 17:00 | 2022-06-29 08:45 |  |  | Attended site and signed in. Completed JSA. Located N117. Found conduit on wall to be damaged and unrepairable. Spoke with site and advised the cables inside it are redundant. Removed from the wall and cut off at the roof. Patched up hole in wall. Disposed of all parts and cables. Clean and tidy site. Sent pictures to FM. All okay. Signed out. Job complete
MSA-MRWA | WA5569518 | 2 | AWB Co. | Ground Floor - Hallway that runs down back of building - Lights have failed back of building | Electrical | Lighting, Internal | 325.28 | Pass | Pass | 0 | 0 | 1.75 | 2022-06-27 15:22 | 2022-06-30 17:00 | 2022-06-28 11:30 | 2022-06-30 17:00 | 2022-06-28 13:15 |  |  | Attended site and signed in. Completed JSA. Located toilet area lighting. Found to be reported burning smell from the male toilets. Investigated to find faulty light fitting in the toilets. Supply and replaced 2 x battens in male toilet. Tested all okay. Signed out. Job complete
MSA-DFES | WA5571756 | 2 | Go Doors | ground Firefighters Dormitory (Rear LHS)-window roller shutter is down and will not retract | Building | Awnings | 417.91 | Pass | Pass | -1 | -1 | 1.75 | 2022-06-29 12:05 | 2022-07-04 17:00 | 2022-06-30 11:30 | 2022-07-04 17:00 | 2022-06-30 13:15 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5681471 | 3 | AWB Co. | 2x damaged Gpo's | Electrical | Lighting, Internal | 234.8675 | Pass | Pass | 0 | 0 | 1.75 | 2022-07-28 12:19 | 2022-08-04 17:00 | 2022-08-02 10:45 | 2022-08-04 17:00 | 2022-08-02 12:30 |  |  | Attended site and signed in. Completed JSA.located room 314 and 315, found broken gpo and broken mounting plate. Supply and replaced new double gpo and fitted new mounting block to light fitting in bench. Re fitted switch mechs to plate. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5686604 | 3 | Seme Solutions Pty Ltd | Issues with alarm system - See notes below | Security | Monitoring | 227.5 | Pass | Pass | -1 | -1 | 1.75 | 2022-08-01 09:40 | 2022-08-08 17:00 | 2022-08-01 10:00 | 2022-08-08 17:00 | 2022-08-01 11:45 |  |  | Anne-Marie was having trouble arming the system with her user code, after finally finding the area in the Program related to user codes I noticed she was user 2 and not user 1 that she claimed to be. Tested code through key pad all seems fine
MSA-DTWD | WA5686841 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet requires fixing button broken female toilet B Block Ground Floor | Plumbing & Drainage | Toilets/Cisterns | 232.9825 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-01 11:10 | 2022-08-04 17:00 | 2022-08-02 15:15 | 2022-08-04 17:00 | 2022-08-02 17:00 |  |  | .
MSA-DTWD | WA5687875 | 3 | AWB Co. | roof leak | Roofing | Metal Roofing | 492.525 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-02 07:59 | 2022-08-08 17:00 | 2022-08-05 13:00 | 2022-08-08 17:00 | 2022-08-05 14:45 |  |  | Attended and installed flashing over vent piping as existing flashings were rusted through. Added buyte tape underneath.Block A3 A331 caused by heavy weather.Once leak confirmed resolved ceiling tile will need to be replaced.
MSA-DTWD | WA5692517 | 2 | Protek 24/7 Building & Maintenance | Roofing sheet loose and blowing in the wind. | Roofing | Metal Roofing | 318.03 | Pass | Pass | -1 | -1 | 1.75 | 2022-08-03 14:08 | 2022-08-08 17:00 | 2022-08-04 10:45 | 2022-08-08 17:00 | 2022-08-04 12:30 |  |  | BRAF declined for repairs
MSA-DTWD | WA5696339 | 2 | AWB Co. | ET04A classroom - Faulty light switch mech - See notes below | Electrical | General Electrical | 231.9875 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-08 11:05 | 2022-08-11 17:00 | 2022-08-09 07:00 | 2022-08-11 17:00 | 2022-08-09 08:45 |  |  | Attended site and signed in. Completed JSA. Located ET04A. Found tagged out light switch. Supply and replaced1 x light switch. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5696423 | 2 | Protek 24/7 Building & Maintenance | AT03 - Roof leak over computer same area as was reported on 26.07.2022. | Roofing | Metal Roofing | 371.57 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-08 11:33 | 2022-08-11 17:00 | 2022-08-09 13:45 | 2022-08-11 17:00 | 2022-08-09 15:30 |  |  | Clean off and Resealed peeling silicone
MSA-DTWD | WA5706210 | 3 | AWB Co. | Faulty ceiling light. Please replace. | Electrical | Lighting, Internal | 311.9575 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-11 09:31 | 2022-08-18 17:00 | 2022-08-16 07:00 | 2022-08-18 17:00 | 2022-08-16 08:45 |  |  | Attended site and signed in. Completed JSA. Located store room in b block. Found faulty fluro fitting. Tried to change lamps and didn’t work. Supply and replace with new led fitting. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5734613 | 2 | AWB Co. | 3 x roof leaks- 2 roof leaks from air con ducts, 1 from aircon drain pipe - all on eastern side | Building | Ceiling | 349.195 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-16 08:20 | 2022-08-19 17:00 | 2022-08-17 07:00 | 2022-08-19 17:00 | 2022-08-17 08:45 |  |  | Investigated 3 x roofleaks.made repairs with silicone
MSA-DTWD | WA5752103 | 1 | AWB Co. | A258a - replace lights flicking | Electrical | Lighting, Internal | 480.41 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-17 11:30 | 2022-08-18 17:00 | 2022-08-17 14:30 | 2022-08-18 17:00 | 2022-08-17 16:15 |  |  | Attended site and signed in. Completed jsa. Found faulty lighting. Replaced tubes and starters. Light working okay. Took pic. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5790324 | 1 | Schindler Lifts Australia | Level 2 - Lift 3 - Light not working in lift | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.75 | 2022-08-22 10:00 | 2022-08-23 17:00 | 2022-08-22 10:45 | 2022-08-23 17:00 | 2022-08-22 12:30 |  |  | Replaced tubes and starter. All ok
MSA-DTAG | WA5792793 | 2 | AWB Co. | Level 10 - Various Lights out - See below | Electrical | Lighting, Internal | 498.2075 | Pass | Pass | 0 | 0 | 1.75 | 2022-08-23 15:25 | 2022-08-26 17:00 | 2022-08-26 11:30 | 2022-08-26 17:00 | 2022-08-26 13:15 |  |  | Job complete
MSA-DTWD | WA5799299 | 3 | AWB Co. | Pidgeon mesh falling out from position under croft | Roofing | Metal Roofing | 374.065 | Fail | Fail | 0 | 0 | 1.75 | 2022-08-30 10:58 | 2022-09-06 17:00 | 2022-09-08 10:00 | 2022-09-06 17:00 | 2022-09-08 11:45 |  |  | Attended site and completed jsa, met with Theo who showed us where the sign in area is and showed us the job that needed to be done. We accessed the roof with the correct fixings and tools. Secured the bird mesh correctly.Job completed
MSA-DTWD | WA5833869 | 1 | AWB Co. | Track lighting has fallen off ceiling - Single track with three fittings attached | Electrical | Lighting, Internal | 351.825 | Pass | Pass | 0 | 0 | 1.75 | 2022-09-06 12:14 | 2022-09-07 17:00 | 2022-09-06 12:15 | 2022-09-07 17:00 | 2022-09-06 14:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located room with fallen track lighting. Set up work area. Redrilled holes as they were ruined. Installed new toggles. Resecured track lighting to ceiling. Replaced multiple tubes. Packed and cleaned up site. Notified relevant personnel of works completed. **job complete**
MSA-DFES | WA5839643 | 3 | AWB Co. | RETROSPECTIVE-WA5596761-already attend- invoice purposes - Sliding door is stuck open&requires force | Building | Doors | 203.7675 | Fail | Fail | 1 | 1 | 1.75 | 2022-07-11 10:14 | 2022-07-18 17:00 | 2022-07-22 13:45 | 2022-07-18 17:00 | 2022-07-22 15:30 | 1 |  | As per signature slip
MSA-DCA | WA5995181 | 3 | FCT SURFACE CLEANING | Gantry Hoarding - Murray street side - External graffiti on hoarding | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.75 | 2022-10-06 11:04 | 2022-10-13 17:00 | 2022-10-10 10:00 | 2022-10-13 17:00 | 2022-10-10 11:45 |  |  | Removal of graffiti
MSA-DTWD | WA5995546 | 2 | AWB Co. | roof leak | Roofing | Tiled Roofing | 421.005 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-06 12:36 | 2022-10-11 17:00 | 2022-10-10 08:30 | 2022-10-11 17:00 | 2022-10-10 10:15 |  |  | attended site and completed PFM forms and jsa, we met with a staff member and had a inspection of roof leak. We then accessed the roof and discovered a poorly sealed AC unit, the back flashings needed a re seal and we found a small section of surface rust where the silicone was peeling off. Also found a small crack in the skylight roof sheet next to the AC unit. We cleaned and re sealed everything.Job completedAtt
MSA-DCA | WA5997753 | 0 | TK Elevator Australia Pty Ltd | Lift 7 stuck on basement level 2 | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1.75 | 2022-10-07 09:22 | 2022-10-07 11:22 | 2022-10-07 14:30 | 2022-10-07 13:22 | 2022-10-07 16:15 |  |  | Lift7 Greem Rm-Elevator > MR > Hydraulic :Lift stopped on b2 doors open, inspected controller fault log, run time protection tripped, reset and tested. I noticed the downleveling speed was long into the bottom floor checked timing Gnd to B1 door open to door open and then B1 to B2 a 30 second difference was noticed, I adjusted the levelingspeed to allow for a slightly better time into B2, lift was tested extensively and is back in service.Declaration/
MSA-DTWD | WA6000981 | 1 | AHS Services WA Pty Ltd (Anchor) | the urinal is blocked and overflowing onto the floor | Plumbing & Drainage | Toilets/Cisterns | 242.6825 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-10 11:31 | 2022-10-11 17:00 | 2022-10-10 12:15 | 2022-10-11 17:00 | 2022-10-10 14:00 |  |  | Completed
MSA-DTAG | WA6007533 | 3 | Midolo Building Services | Toilet roll holders in both male & female toilets have been vandalised | Building | General Building | 429.46 | Fail | Fail | 0 | 0 | 1.75 | 2022-10-11 08:43 | 2022-10-18 17:00 | 2022-10-21 07:00 | 2022-10-18 17:00 | 2022-10-21 08:45 |  | WACCES | TOILET ROLL HOLDERS REPLACED
MSA-MRWA | WA6020621 | 2 | AWB Co. | room 488-LED light failed | Electrical | Lighting, Internal | 218.2075 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-13 14:53 | 2022-10-18 17:00 | 2022-10-18 12:15 | 2022-10-18 17:00 | 2022-10-18 14:00 |  |  | Sourcing led drivers for stock
MSA-DTWD | WA6048441 | 3 | AWB Co. | T24-Repair/replace faulty ceiling lights | Electrical | Lighting, Internal | 526.9425 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-17 13:26 | 2022-10-24 17:00 | 2022-10-21 11:30 | 2022-10-24 17:00 | 2022-10-21 13:15 |  |  | Attended site signed in jsa completed. Found two lights not working and one hanging with broken diffuser. Replaced with x3 led sal batterns.Job completed
MSA-DFES | WA6088840 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Tap in plant room cannot be turned off | Plumbing & Drainage | Water | 234 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-19 11:10 | 2022-10-20 17:00 | 2022-10-19 13:45 | 2022-10-20 17:00 | 2022-10-19 15:30 |  |  | Arrived on site and singed in went to plant room and had to replaces a 15mm brass garden tap had to go to Reece and pick up part's came back and install it tested everything and running fine.
MSA-DTWD | WA6090882 | 2 | Protek 24/7 Building & Maintenance | Ground - Male Toilet - Bottom door hinge broken | Building | Doors | 212.325 | Pass | Pass | 0 | 0 | 1.75 | 2022-10-19 14:57 | 2022-10-24 17:00 | 2022-10-21 10:45 | 2022-10-24 17:00 | 2022-10-21 12:30 |  |  | Dowel and glue holes, install screws into door
MSA-DCA | WA6145710 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Ground - Foyer - Revolving Door keeps stopping - See notes | Building | Automatic Doors | 501 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-02 14:13 | 2022-11-03 17:00 | 2022-11-03 07:45 | 2022-11-03 17:00 | 2022-11-03 09:30 |  |  | Attended site and inspected revolving door. Tested operations and noted no faults whilst on site. Attempted to simulate fault to no avail. Left door operating all ok. This is not a warranty callout.
MSA-DCA | WA6178451 | 0 | Protek 24/7 Building & Maintenance | Door Across from Reception - door to the tunnel wont close and is a fire door | Building | Fire Door | 240.25 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-14 11:25 | 2022-11-14 13:25 | 2022-11-14 12:15 | 2022-11-14 15:25 | 2022-11-14 14:00 |  |  | Temporarily un seized door hinges , re hung door , planed down door edge to allow door to be opened and latched
MSA-DFES | WA6179102 | 2 | AWB Co. | Gym courtyard external door stop broken | Building | Doors | 215.8575 | Fail | Fail | 0 | 0 | 1.75 | 2022-11-14 16:00 | 2022-11-17 17:00 | 2022-11-18 07:00 | 2022-11-17 17:00 | 2022-11-18 08:45 |  |  | Works completed
MSA-DTWD | WA6190812 | 2 | FCT SURFACE CLEANING | Male Toilet - B002 cubicles has bad graffiti | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 1.75 | 2022-11-16 10:38 | 2022-11-21 17:00 | 2022-11-24 10:00 | 2022-11-21 17:00 | 2022-11-24 11:45 |  |  | Removal of graffiti
MSA-DCA | WA6208059 | 1 | Protek 24/7 Building & Maintenance | Door handle to side of stage has broken off | Building | Doors | 360.53 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-17 12:37 | 2022-11-18 17:00 | 2022-11-18 10:00 | 2022-11-18 17:00 | 2022-11-18 11:45 |  |  | Replaced handle with new one
MSA-DTWD | WA6253844 | 2 | AWB Co. | Block E - Deli - Replace damaged GPO near fridge | Electrical | General Electrical | 191.885 | Pass | Pass | 0 | 0 | 1.75 | 2022-11-22 12:35 | 2022-11-25 17:00 | 2022-11-24 13:45 | 2022-11-25 17:00 | 2022-11-24 15:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located deli block E with faulty gpo. Found to be gpo needed relocating. Moved gpo on other side above fridge. Tested for correct operation. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6292870 | 3 | GRAFFITI FORCE PTY LTD | L2 Ladies toilet - Graffiti tagging. | Cleaning | Graffiti | 375.5 | Pass | Pass | -1 | -1 | 1.75 | 2022-11-29 13:51 | 2022-12-06 17:00 | 2022-12-02 07:00 | 2022-12-06 17:00 | 2022-12-02 08:45 |  |  | REMOVAL OF GRAFFITI FROM L2 LADIES TOILETS
MSA-DTWD | WA6357596 | 2 | Lane's Plumbing | BLD 810 - WC - Water valve to toilet pan faulty | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 1.75 | 2022-12-05 14:29 | 2022-12-08 17:00 | 2022-12-05 15:15 | 2022-12-08 17:00 | 2022-12-05 17:00 |  |  | Completed
MSA-DFES | WA6399972 | 1 | Go Doors | Careers fire station - Front engine room roller door - not closing, has to be closed manually | Building | Automatic Doors | 434.43 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-03 08:38 | 2023-01-04 17:00 | 2023-01-03 13:00 | 2023-01-04 17:00 | 2023-01-03 14:45
MSA-DFES | WA6401630 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Alarm system for pumps activated | Plumbing & Drainage | Drainage | 348.4875 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-04 14:04 | 2023-01-04 16:04 | 2023-01-04 14:30 | 2023-01-04 18:04 | 2023-01-04 16:15
MSA-DTWD | WA6402709 | 2 | Protek 24/7 Building & Maintenance | B1 - Office 706 - Carpet damaged and lifting | Flooring | Carpet | 973.075 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-05 15:20 | 2023-01-10 17:00 | 2023-01-09 09:15 | 2023-01-10 17:00 | 2023-01-09 11:00
MSA-DCA | WA6431325 | 0 | Techworks Electrical | Urban Orchard - Lights has been hit by forklift - Light pole is wobbly - See Notes | Electrical | Lighting, External | 278.745 | Pass | Pass | 0 | 0 | 1.75 | 2023-01-13 12:57 | 2023-01-13 13:27 | 2023-01-13 13:00 | 2023-01-13 14:57 | 2023-01-13 14:45
MSA-DTWD | WA6538869 | 1 | ACTION GLASS & ALUMINIUM | D Block - storage shed - Broken widows | Glazing | Window Glass | 669.73 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-08 08:59 | 2023-02-09 17:00 | 2023-02-08 10:45 | 2023-02-09 17:00 | 2023-02-08 12:30
MSA-DFES | WA6540886 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | ground dorm 6 & SOs office-lights not working - see notes | Electrical | Lighting, Internal | 339.145 | Pass | Pass | 0 | 0 | 1.75 | 2023-02-09 15:43 | 2023-02-14 17:00 | 2023-02-14 07:00 | 2023-02-14 17:00 | 2023-02-14 08:45
MSA-DTAG | WA6668416 | 3 | Midolo Building Services | Detention - Mens staff toilet - Toilet Door has a big split near the top hinge | Building | Doors | 269.8 | Pass | Pass | -1 | -1 | 1.75 | 2023-02-22 09:09 | 2023-03-01 17:00 | 2023-02-23 09:15 | 2023-03-01 17:00 | 2023-02-23 11:00
MSA-DTWD | WA6689643 | 3 | AWB Co. | 10amp drop pendant broken | Electrical | General Electrical | 267.1075 | Pass | Pass | -1 | -1 | 1.75 | 2023-03-08 13:52 | 2023-03-15 17:00 | 2023-03-09 11:30 | 2023-03-15 17:00 | 2023-03-09 13:15
MSA-DTWD | WA5175182 | 0 | Equans Mechanical Services Australia | T114 - AC Exhasut system is now in fault | Air Conditioning | Room Air Conditioners | 183.14 | Fail | Fail | 0 | 0 | 1.7333 | 2022-02-21 10:55 | 2022-02-21 12:55 | 2022-02-22 08:00 | 2022-02-21 14:55 | 2022-02-22 09:44 |  | WACCES | Discussed with maintenance manager and was informed that am attendance the following morning ok. Travelled to site. Logged on to site. Met with maintenance and was informed fault light active in first floor MSSB and T114 room was reported as warmGained access to site. Investigated and found contractor overload had tripped. Reset and started unit. Checked amp draws and tightness of all electrical connections. Checked operation of FCU and monitored. All ok.
MSA-DTAG | WA5286891 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 6 - Secure Male Staff area - PRB - tap handle/spout has broken away from a basin | Plumbing & Drainage | Materials | 319.2725 | Pass | Pass | 0 | 0 | 1.7333 | 2022-03-22 08:43 | 2022-03-25 17:00 | 2022-03-22 12:00 | 2022-03-25 17:00 | 2022-03-22 13:44 |  |  | Picked up and replaced corroded tap -left hand side male toilet level 6
MSA-DTAG | WA6517976 | 3 | GPS Plumbing & Gas Services PtyLtd | Custody-ground-Broken tap and sprinkler within the secure parking area | Plumbing & Drainage | Water | 321.7275 | Pass | Pass | -1 | -1 | 1.7333 | 2023-01-24 14:55 | 2023-02-01 17:00 | 2023-01-27 14:46 | 2023-02-01 17:00 | 2023-01-27 16:30
MSA-MRWA | WA5163954 | 2 | Water2water Pty Ltd | Level 6 - Water Fountain - Black particles in water – please investigate | Plumbing & Drainage | Water | 205.155 | Pass | Pass | 0 | 0 | 1.7333 | 2022-02-18 13:56 | 2022-02-23 17:00 | 2022-02-22 10:44 | 2022-02-23 17:00 | 2022-02-22 12:28 |  |  | Drained and flushed both unitsA40184050B - MAXIFLOW + ARCUS FOUNTAIN BASMENTBLACK PARTICLES IN WATER - COMING FROM INTERNAL FOUNTAIN TANKOR OTHER COMPONENTS DRAINED TANK FLUSHED MAY NEED ARCUSTO INVESTIGATEA40191132A MAXIFLOW + ARCUS FOUNTAIN LEVEL 6 OUTSIDE KITCHENETTENO PARTICLES FOUND DRAINED TANK AND FLUSHED OK
MSA-DFES | WA5378433 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Most of the facility - water pressure is super low | Plumbing & Drainage | Water | 180.55 | Pass | Pass | 0 | 0 | 1.7167 | 2022-04-20 14:10 | 2022-04-21 17:00 | 2022-04-21 10:57 | 2022-04-21 17:00 | 2022-04-21 12:40 |  |  | Arrived to site cause there is no hot water in the male and female toilets went to the hot water system and found the isolation tap was turned off turned it back on and all work correctly so checked all the other tanks to make sure no one else has turn them off as well
MSA-DFES | WA5513839 | 2 | Water2water Pty Ltd | Ground Floor - Kitchen - Zip unit hot/cold not working (Unit on left hand side ) | Plumbing & Drainage | HWS/Units Electric & Gas | 919.9725 | Pass | Pass | 0 | 0 | 1.7167 | 2022-06-14 13:41 | 2022-06-17 17:00 | 2022-06-16 09:25 | 2022-06-17 17:00 | 2022-06-16 11:08 |  |  | Replaced main pcb plv and safety sol
MSA-DTAG | WA5995683 | 2 | Australian HVAC Services Pty. Ltd. | Level 2 - Sheriffs Office - Temperature in SO open plan area is very warm | Air Conditioning | Room Air Conditioners | 460.88 | Pass | Pass | -1 | -1 | 1.7167 | 2022-10-06 14:46 | 2022-10-11 17:00 | 2022-10-06 14:47 | 2022-10-11 17:00 | 2022-10-06 16:30 |  |  | Attend site. Investigate Sherriffs office area too warm. Access BMS and check plant. Found AHU running with call for cooling. Found condenser pump running. Found chilled water pump not starting. Trace through controls and found no overrides on BMS. Locate controllers in switchboard and go through parameters. Found chilled water pump manualed off. Return pump to auto. Found pump to start and run as normal. Found chiller to now start. Monitor operation of plant and found Sherriffs office area cooling down. This manual off of chilled water pump must have been by others during the new works going on in the plantroom.
MSA-DTAG | WA6516154 | 2 | Gilmour & Jooste Electrical | Level 1 - Buss P Chambers - Light flickering above associates desk - see notes | Electrical | Lighting, Internal | 279.08 | Fail | Fail | 1 | 1 | 1.7167 | 2023-01-23 09:26 | 2023-01-27 17:00 | 2023-02-02 06:00 | 2023-01-27 17:00 | 2023-02-02 07:43
MSA-DCA | WA5800409 | 0 | TK Elevator Australia Pty Ltd | Public lift-someone is stuck in the lift-light is on not lift buttons | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.7167 | 2022-08-31 09:55 | 2022-08-31 11:55 | 2022-08-31 10:36 | 2022-08-31 13:55 | 2022-08-31 12:19 |  |  | Upon arrival I found the lift ooo at the ground floor after releasing the swp I suspect the DO relay binding as the staff member who wastrapped said the lift would go up and down however it would not open its doors, when I manually activated the relay the doors opened.
MSA-DTWD | WA6363892 | 0 | Precise Air Group | lecture theatre air con not working | Air Conditioning | Room Air Conditioners | 366 | Fail | Fail | 0 | 0 | 1.7167 | 2022-12-12 08:04 | 2022-12-12 10:04 | 2022-12-12 11:30 | 2022-12-12 12:04 | 2022-12-12 13:13 |  |  | Attended D block at Midland Campus as the AC was reported to be not cooling in the lecture theatre. Accessed air handlers inside the plant room and begun fault finding, we have an 8K split across the coil on AHU 2 that serves the theatre, however the room was still warm. Confirmed actuators on chilled water lines were operating correctly, also confirmed readings on nearby AHU’s as a reference point, all running as per design. Accessed BMS and noticed the set point was at 22.5 degrees and there was 120 adults inside this theatre adding substantial heat load. We have adjusted the set point to 21 degrees and have asked the staff to close the theatre doors while they are using the room, as the conditioned air being supplied to the room has been escaping out the front door and the hot air from outside has been let in.Staff have commented that there is now cool air coming into the room and they are happy with this.Works completed, issue resolved.
MSA-MRWA | WA5238756 | 1 | TK Elevator Australia Pty Ltd | Lift - Not sure what floor lift is stuck - but is not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.7 | 2022-03-16 08:49 | 2022-03-17 17:00 | 2022-03-16 10:15 | 2022-03-17 17:00 | 2022-03-16 11:57 |  |  | Lift1 DAC-Geared :Lift 1 ROA.Lift4 was out of service. Fault recorded are SAF SAF operated. Trace for fault ,found RBC14 board had tripped. Checked switches related torope brake ,all ok. Changed RBC14 board. Run and monitor lift, running ok. Put lift back on service.
MSA-DTAG | WA5697710 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Staff Ladies Toilet - 2x toilets fault - see notes | Plumbing & Drainage | Toilets/Cisterns | 476.2375 | Pass | Pass | 0 | 0 | 1.7 | 2022-08-09 11:22 | 2022-08-16 17:00 | 2022-08-15 11:48 | 2022-08-16 17:00 | 2022-08-15 13:30 |  |  | Replaced Corona push button seal kit water wafer and Corona bellow kit pk2 water wafer
MSA-DTWD | WA5689164 | 2 | Dormakaba Australia Pty Ltd | Entry to F-Block -Auto glass door wont close when set to auto close. Only closes on lock. | Building | Automatic Doors | 1896.91 | Pass | Pass | 0 | 0 | 1.6833 | 2022-08-02 11:19 | 2022-08-05 17:00 | 2022-08-03 14:56 | 2022-08-05 17:00 | 2022-08-03 16:37 |  |  | Note new IP number 1171214, programmed asset A40213814C. Arrived onsite and signed. Found door operating erratically, checked and tested key switch all ok, noticed batteries totally failed and replaced, carried out a full reset on controller but still not operating correctly, fitted new controller and put through learn cycle and tested operation all ok.
MSA-DCA | WA6364840 | 1 | TK Elevator Australia Pty Ltd | Lift 6 - stuck on the mezzanine floor - out of order - no light on the LD's | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 1.6833 | 2022-12-12 16:14 | 2022-12-13 17:00 | 2022-12-13 07:49 | 2022-12-13 17:00 | 2022-12-13 09:30 |  |  | Lift 6 stopped on M floor with doors open and no power on doors. Found lift main breaker off/tripped. Turned power back on.Errors 735, 10, 1051Mains interrupted and FC fault.Checked all relevant circuits all okay. Battery light in contoller on, voltage on battery 10.70-11v.Replaced 7ah battery all okay. Checked all power supplies and adjusted to 24 voltages.Checked lift 6 for errors found same errors as lift 7, mains interrupted, and fc fault. Suspect power spike into main breakers for lift 6 and 7.
MSA-DCA | WA6379071 | 1 | Dormakaba Australia Pty Ltd | Loading Dock - Cable Gate bolt snapped, and box possibly tampered with. | Building | Steel Fencing & Gates | 1357.5 | Pass | Pass | 0 | 0 | 1.6833 | 2022-12-19 08:59 | 2022-12-20 17:00 | 2022-12-20 09:42 | 2022-12-20 17:00 | 2022-12-20 11:23 |  |  | WO-03364664 - Revisit - Replaced snapped cable and sheathing. Tested ok. WO-03364401 -Main drop cable snapped and sheathing damaged. Return visit with replacement parts required.
MSA-DTWD | WA6521540 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 2- West Men's and Ladies Bathroom - toilets overflowing | Plumbing & Drainage | Toilets/Cisterns | 177.3625 | Pass | Pass | 0 | 0 | 1.6833 | 2023-01-30 11:30 | 2023-01-31 17:00 | 2023-01-31 06:30 | 2023-01-31 17:00 | 2023-01-31 08:11
MSA-DCA | WA6673631 | 0 | Dormakaba Australia Pty Ltd | Main Building - Cafe Shop sliding door leading into the foyer - Not responding | Building | Doors | 776.95 | Fail | Fail | 0 | 0 | 1.6833 | 2023-02-25 09:01 | 2023-02-25 11:01 | 2023-02-27 12:06 | 2023-02-25 13:01 | 2023-02-27 13:47
MSA-DTWD | WA5971525 | 2 | AHS Services WA Pty Ltd (Anchor) | S block - Drain appears to be leaking sewerage | Plumbing & Drainage | Drainage | 105.9675 | Pass | Pass | 0 | 0 | 1.6833 | 2022-09-20 14:55 | 2022-09-23 17:00 | 2022-09-21 09:35 | 2022-09-23 17:00 | 2022-09-21 11:16 |  |  | Stormwater down pipes blocked s block ground floor and 1 floor
MSA-DTWD | WA5150734 | 1 | AHS Services WA Pty Ltd (Anchor) | A131 - Male toilet - Urinal overflowing | Plumbing & Drainage | Water | 234.2054 | Pass | Pass | 0 | 0 | 1.6667 | 2022-02-17 08:02 | 2022-02-18 17:00 | 2022-02-17 14:00 | 2022-02-18 17:00 | 2022-02-17 15:40 |  |  | Unblock Urinal using plunger and moflo
MSA-DTAG | WA5499015 | 1 | High Tech Pest Control | Level 10 - Kitchen - Cockroach infestation/pest infestation in kitchen sink and hot/cold water taps | Pest Control | General Pest | 315.7 | Pass | Pass | 0 | 0 | 1.6667 | 2022-06-10 09:23 | 2022-06-13 17:00 | 2022-06-10 15:50 | 2022-06-13 17:00 | 2022-06-10 17:30 |  |  | Cockroach Treatment to Kitchen area and monitoring for German Cockroaches
MSA-DTWD | WA5566034 | 1 | ECO PLUMBING AND GAS PTY LTD | Café Kitchen - Dishwasher Pump | Plumbing & Drainage | Drainage | 1841.405 | Fail | Fail | 4 | 4 | 1.6667 | 2022-06-22 13:58 | 2022-06-23 17:00 | 2022-07-20 14:20 | 2022-06-23 17:00 | 2022-07-20 16:00 |  |  | replaced pump
MSA-DFES | WA5796362 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - Mens Toilets - end cubicle - constantly running and the button isn't stuck | Plumbing & Drainage | Toilets/Cisterns | 219.62 | Pass | Pass | 0 | 0 | 1.6667 | 2022-08-26 10:42 | 2022-08-26 12:42 | 2022-08-26 11:45 | 2022-08-26 14:42 | 2022-08-26 13:25 |  |  | Arrived on site and singed in went to level 2 male toilets end cubicle had to pull out the outlet valve and reposition it back in place tested and everything was fine.
MSA-DTWD | WA5861281 | 2 | AHS Services WA Pty Ltd (Anchor) | 1st cubicle - Leaking toilet pan | Plumbing & Drainage | Toilets/Cisterns | 259.305 | Pass | Pass | 0 | 0 | 1.6667 | 2022-09-13 08:27 | 2022-09-16 17:00 | 2022-09-16 08:00 | 2022-09-16 17:00 | 2022-09-16 09:40 |  |  | Went to site spoke to admin description was wrong it wasn’t leaking it was blocked unblocked toilet block level 3
MSA-DTWD | WA6543659 | 0 | Casa Security Pty Ltd | Through out the campus - Faulty alarm beeping at all panels | Security | Security Management System | 375 | Pass | Pass | 0 | 0 | 1.6667 | 2023-02-10 07:46 | 2023-02-10 09:46 | 2023-02-10 08:45 | 2023-02-10 11:46 | 2023-02-10 10:25
MSA-DCA | WA6721617 | 2 | GPS Plumbing & Gas Services PtyLtd | Levwel 4 - Staff Male toilet - Leaking tap - Hand Basin Right Hand side | Plumbing & Drainage | Water | 445.345 | Pass | Pass | 0 | 0 | 1.6667 | 2023-03-14 10:18 | 2023-03-17 17:00 | 2023-03-15 12:50 | 2023-03-17 17:00 | 2023-03-15 14:30
MSA-DCA | WA5380935 | 1 | EQUANS Mechanical Services (WA) Pty Limited | VESDA has no power | Air Conditioning | Building HVAC Maintenance (Major Plant) | 243.85 | Pass | Pass | 0 | 0 | 1.6667 | 2022-04-25 03:28 | 2022-04-26 17:00 | 2022-04-25 04:10 | 2022-04-26 17:00 | 2022-04-25 05:50 |  |  | Checked out ac 9 OAF with no power on video.Found information tag stating the fan turned off.Checked over system, all ok.
MSA-DCA | WA6292690 | 2 | GPS Plumbing & Gas Services PtyLtd | Plant Room - Boiler room - Faulty non-return valve on domestic hot water line - Needs replacing | Plumbing & Drainage | HWS/Units Electric & Gas | 386.38 | Pass | Pass | 0 | 0 | 1.6667 | 2022-11-29 12:09 | 2022-12-02 17:00 | 2022-12-01 13:40 | 2022-12-02 17:00 | 2022-12-01 15:20 |  |  | Replaced faulty swing check valve
MSA-DTWD | WA4995662 | 2 | OTIS ELEVATOR COMPANY PTY LTD | Passenger Lift button is broken on ground floor | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.6667 | 2022-01-10 14:53 | 2022-01-13 17:00 | 2022-01-11 09:02 | 2022-01-13 17:00 | 2022-01-11 10:42 |  |  | job completed - LANDING CALL FIXTURES - BUTTONS - COMPONENT REPLACED
MSA-DTWD | WA5099115 | 2 | ECO PLUMBING AND GAS PTY LTD | Damaged flexi spout over dog wash up trough | Plumbing & Drainage | Water | 315.835 | Pass | Pass | 0 | 0 | 1.6667 | 2022-02-01 14:37 | 2022-02-04 17:00 | 2022-02-03 14:50 | 2022-02-04 17:00 | 2022-02-03 16:30 |  |  | Replaced hand help spray in dog wash bay
MSA-DTWD | WA5106728 | 2 | LIGHTHOUSE LOCKSMITHS | R-Block - room R003 - the door handle is broken, door not closing | Security | Locksmith | 267.2 | Pass | Pass | 0 | 0 | 1.6667 | 2022-02-07 10:58 | 2022-02-10 17:00 | 2022-02-08 08:30 | 2022-02-10 17:00 | 2022-02-08 10:10 |  |  | Adjusted face plate and serviced lock on door R003
MSA-DTWD | WA5127174 | 1 | CONNECT SECURITY SYSTEMS | Ground - D Block - D6 Store Room - Investigate faulty sensor.. | Security | Keys & Access | 623.59 | Pass | Pass | 0 | 0 | 1.6667 | 2022-02-14 11:37 | 2022-02-15 17:00 | 2022-02-15 10:43 | 2022-02-15 17:00 | 2022-02-15 12:23 |  |  | replaced faulty 27 year old pir in Room D6
MSA-DTWD | WA5296584 | 2 | Water2water Pty Ltd | Beauty Clinic - Billi unit not working | Plumbing & Drainage | Water | 359.6925 | Pass | Pass | 0 | 0 | 1.6667 | 2022-03-30 13:23 | 2022-04-04 17:00 | 2022-04-04 11:50 | 2022-04-04 17:00 | 2022-04-04 13:30 |  |  | Replaced element, fixed leak. Everything running to specs & all okay on departure.
MSA-DTWD | WA5479330 | 3 | AWB Co. | South Block - Level 3 - Roof - shade device damaged by storm | Building | General Building | 864.5 | Fail | Fail | 2 | 2 | 1.6667 | 2022-05-27 08:58 | 2022-06-03 17:00 | 2022-06-15 07:00 | 2022-06-03 17:00 | 2022-06-15 08:40 |  |  | South Block - Level 3 - Roof - shade device damaged by storm
MSA-MRWA | WA5781054 | 1 | Schindler Lifts Australia | Lift 3 stuck on L1 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.6667 | 2022-08-19 12:26 | 2022-08-22 17:00 | 2022-08-22 14:05 | 2022-08-22 17:00 | 2022-08-22 15:45 |  |  | Works completed - close out at $0
MSA-MRWA | WA5987109 | 1 | SONTEC WA PTY LTD | Control Room - Security intercom - Failed ( not working ) | Security | Security Management System | 430 | Pass | Pass | 0 | 0 | 1.6667 | 2022-10-03 07:57 | 2022-10-03 17:00 | 2022-10-03 15:20 | 2022-10-03 17:00 | 2022-10-03 17:00 |  |  | 3/10/22 - Dylan ParslowFound master stations reset to factory settings.Reprogrammed and tested, all working.Unable to lock user access to this.
MSA-DCA | WA6154129 | 1 | CONNECT SECURITY SYSTEMS | Q Block - Ground - Large Meeting Room - Fire Alarm Zone:91 Smoke Detector Fault | Security | Monitoring | 392.83 | Pass | Pass | 0 | 0 | 1.6667 | 2022-11-07 10:39 | 2022-11-08 17:00 | 2022-11-08 07:30 | 2022-11-08 17:00 | 2022-11-08 09:10 |  |  | Replaced faulty smoke detector zone 91
MSA-DFES | WA5394655 | 2 | ADVANCED LOCK & KEY | Main Building - Ground - Dorms 4,6,7,9 - Bathroom door locks require adjustment, w | Security | Locksmith | 303.1 | Fail | Fail | 0 | 0 | 1.65 | 2022-05-05 07:54 | 2022-05-09 17:00 | 2022-05-10 12:33 | 2022-05-09 17:00 | 2022-05-10 14:12 |  |  | 1367/insc Serviced 3573 on dorms 4,6,7,9 and supplied 1 1367 as it was missing on dorms 4 lock
MSA-DCA | WA5495806 | 1 | GPS Plumbing & Gas Services PtyLtd | Pretzel sea container shop -The RPZD valve that feeds Pretzel is faulty. | Plumbing & Drainage | Water | 767.035 | Pass | Pass | 0 | 0 | 1.65 | 2022-06-08 15:57 | 2022-06-09 17:00 | 2022-06-09 10:36 | 2022-06-09 17:00 | 2022-06-09 12:15 |  |  | Replaced backflow device (RPZD) next to water meter Pretzel shop
MSA-DTWD | WA6256786 | 1 | Precise Air Group | Communications room - AirCon Equipment Failure - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 444.83 | Pass | Pass | 0 | 0 | 1.65 | 2022-11-24 08:50 | 2022-11-25 17:00 | 2022-11-24 13:30 | 2022-11-25 17:00 | 2022-11-24 15:09 |  |  | Travelled to site found a1 fault light on and outside high temp sensor light on.Was advised campus had major power black outs and power surges 2 days ago reset all controls and test run both units ,temp at 20c in communication room all running well again
MSA-DCA | WA5017432 | 1 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - 2nd Floor corridor near CS workroom - ladies toilets - 3 taps faulty | Plumbing & Drainage | Materials | 949.3975 | Pass | Pass | 0 | 0 | 1.6333 | 2022-01-13 14:21 | 2022-01-14 17:00 | 2022-01-14 11:07 | 2022-01-14 17:00 | 2022-01-14 12:45 |  |  | Replaced 2 taps. tighten the loose tap on the left side and adjust the flow of water.
MSA-DTWD | WA6676575 | 2 | Precise Air Group | Ceiling Vent needs replacing | Air Conditioning | Ducted Split System | 286.96 | Pass | Pass | 0 | 0 | 1.6333 | 2023-02-28 15:14 | 2023-03-03 17:00 | 2023-03-01 08:31 | 2023-03-03 17:00 | 2023-03-01 10:09
MSA-MRWA | WA5188760 | 1 | GPS Plumbing & Gas Services PtyLtd | Leaking tap x2 - please contact Craig for locations | Plumbing & Drainage | Water | 324.045 | Pass | Pass | 0 | 0 | 1.6167 | 2022-02-23 11:24 | 2022-02-24 17:00 | 2022-02-24 10:00 | 2022-02-24 17:00 | 2022-02-24 11:37 |  |  | Replaced faulty outdoor tap, and rewashed 2x taps in the female toilet
MSA-DTWD | WA5838419 | 2 | AWB Co. | A Block - 1st Level - Female Toilets - Exhaust fans not working - See notes below | Equipment | Electrical Equipment | 301.405 | Fail | Fail | 0 | 0 | 1.6167 | 2022-09-08 13:06 | 2022-09-13 17:00 | 2022-09-16 14:00 | 2022-09-13 17:00 | 2022-09-16 15:37 |  | WCAPPR | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Replaced 1x belt as it had a crack and the other one was ok. Turned switch on and tested motors. All running ok. Packed up site. Notified of works completed. **job complete**
MSA-DTWD | WA5486380 | 2 | CAPS AUSTRALIA PTY LTD | Workshops - Level 1 - Compressor room - the compressor timer is faulty | Equipment | Compressors, Generators | 784.94 | Fail | Fail | 0 | 0 | 1.6 | 2022-06-01 08:19 | 2022-06-07 17:00 | 2022-06-08 13:24 | 2022-06-07 17:00 | 2022-06-08 15:00 |  |  | Replacement of timer.
MSA-DTWD | WA5832621 | 2 | M Construction (WA) | Open area - Picture has come away from wall | Building | Internal Walls | 214.57 | Pass | Pass | 0 | 0 | 1.6 | 2022-09-05 14:21 | 2022-09-08 17:00 | 2022-09-08 06:30 | 2022-09-08 17:00 | 2022-09-08 08:06 |  |  | Attended site and refixed picture to wall with screws and wall anchors. Job completed.
MSA-DTAG | WA6178431 | 2 | Sapio Pty Ltd | Ground - Registry - Back door not locking correctly - See Notes | Security | Access Control | 204.44 | Pass | Pass | 0 | 0 | 1.6 | 2022-11-14 11:12 | 2022-11-17 17:00 | 2022-11-15 13:32 | 2022-11-17 17:00 | 2022-11-15 15:08 |  |  | Replaced lock and tested.
MSA-DTWD | WA6560397 | 1 | AHS Services WA Pty Ltd (Anchor) | room A222 Ladies toilet continuously running cant flush the system | Plumbing & Drainage | Toilets/Cisterns | 204.8625 | Fail | Fail | 0 | 0 | 1.6 | 2023-02-13 09:46 | 2023-02-14 17:00 | 2023-02-15 07:33 | 2023-02-14 17:00 | 2023-02-15 09:09
MSA-DCA | WA5496322 | 0 | Techworks Plumbing | Ground - Jubilee Building - UAT - Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 779.74 | Pass | Pass | 0 | 0 | 1.6 | 2022-06-09 09:13 | 2022-06-09 11:13 | 2022-06-09 10:54 | 2022-06-09 13:13 | 2022-06-09 12:30 |  |  | Ross bennett/ finlay sambelattended site and signed at security office got a swipe card for access.went to jubilee building to try unblock toilet we started out by plunging the toilets as the blockage didn’t look that bad,plunging didn’t work so we went into the plant room and used drain rods to try unblock the drain through the inspection openings had a fair go with the rods but they wouldn’t budge anything.we went and picked up the drain machine from the yard and once returned to site we used the drain machine to clear the blockage. what we did find tho throughout trying to unblock the drain, that there was a lot of sand in the pipesPossibly is broken down the line somewhere? Drain has been camera inspected before by multiple people would be worth going back and seeing what the footage looks like. we Cleaned up site and signed outthen completed paperwork
MSA-DFES | WA6509425 | 0 | Australian HVAC Services Pty. Ltd. | CRAC Unit - is leaking in the data center on level one | Air Conditioning | Building HVAC Maintenance (Major Plant) | 316.34 | Pass | Pass | 0 | 0 | 1.5972 | 2023-01-20 10:47 | 2023-01-20 12:47 | 2023-01-20 11:22 | 2023-01-20 14:47 | 2023-01-20 12:57
MSA-DCA | WA5175187 | 0 | Techworks Electrical | James street entry - Bollard stuck in down position | Electrical | General Electrical | 200.51 | Pass | Pass | 0 | 0 | 1.5833 | 2022-02-21 10:56 | 2022-02-21 12:56 | 2022-02-21 12:55 | 2022-02-21 14:56 | 2022-02-21 14:30 |  |  | Began investigation and found no power going to the bollard controls, went back to Fiji room and found MCB was tripped. After investigation I have found that the issue was one of the motors on the compressor, when opening the door and looking at the motor tank setup, the motor on the right has failed and has shorted windings causing the motor to fail and the safety devices to trip from overload, I have isolated the right motor leaving the remaining left motor to pump up the tank individually so the bollards still work. It pumps up to the desired PSI fine just takes longer but it’s won’t be an issue for the bollards to operate normally.
MSA-DCA | WA5696516 | 1 | Dormakaba Australia Pty Ltd | entrance sliding door sensor beeping every 10 seconds or so. | Building | Automatic Doors | 462.56 | Pass | Pass | 0 | 0 | 1.5833 | 2022-08-08 12:21 | 2022-08-09 17:00 | 2022-08-09 08:25 | 2022-08-09 17:00 | 2022-08-09 10:00 |  |  | Work Performed: Site not open till 9:30am, return for works. Returned to site at 9:30am and replaced batteries. Tested door all ok
MSA-DTWD | WA5761362 | 2 | Water2water Pty Ltd | hot water boiler water tastes like salt | Plumbing & Drainage | HWS/Units Electric & Gas | 500.31 | Pass | Pass | -1 | -1 | 1.5833 | 2022-08-18 08:35 | 2022-08-23 17:00 | 2022-08-19 08:00 | 2022-08-23 17:00 | 2022-08-19 09:35 |  |  | Emptied hot water unit of all waterAdded maxiflow scale filterRefilled and flushed hot water unit
MSA-DTAG | WA5800367 | 2 | Water2water Pty Ltd | Level 10 - Registration Kitchen - The hot water Tap does not dispensing hot water properly. | Plumbing & Drainage | Water | 430.665 | Pass | Pass | -1 | -1 | 1.5833 | 2022-08-31 09:38 | 2022-09-05 17:00 | 2022-08-31 15:10 | 2022-09-05 17:00 | 2022-08-31 16:45 |  |  | Replaced fault element. Recalibrated. All ok
MSA-DTAG | WA5838134 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Ladies Toilet - Water keeps flushing - See notes below | Plumbing & Drainage | Toilets/Cisterns | 266.7275 | Pass | Pass | 0 | 0 | 1.5833 | 2022-09-08 11:08 | 2022-09-09 17:00 | 2022-09-09 06:55 | 2022-09-09 17:00 | 2022-09-09 08:30 |  |  | Inspected thoroughly all 4x cisterns. Flushed them multiple times. Videos have been taken as well. Replaced outler rubber on the lhs female cubicle. No other issues found-therefore no other actions have been taken.
MSA-DTWD | WA6402564 | 2 | PEEL LOCK SERVICES PTY LTD | East wall door - Bi Door lock broken – key and internal handle will not turn | Security | Keys & Access |  | Pass | Pass | 0 | 0 | 1.5833 | 2023-01-05 13:15 | 2023-01-10 17:00 | 2023-01-09 10:15 | 2023-01-10 17:00 | 2023-01-09 11:50
MSA-DCA | WA5133885 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Dress Circle - Dress Circle Bar - The tap in the Dress Circle bar is broken | Plumbing & Drainage | Materials | 477.045 | Pass | Pass | 0 | 0 | 1.5833 | 2022-02-15 16:39 | 2022-02-18 17:00 | 2022-02-17 10:20 | 2022-02-18 17:00 | 2022-02-17 11:55 |  |  | Replaced damaged mixer
MSA-DCA | WA5289411 | 1 | GPS Plumbing & Gas Services PtyLtd | Main Building - First floor - rest rooms - hotwater system is faulty - not providing hot water | Plumbing & Drainage | HWS/Units Electric & Gas | 320.9325 | Pass | Pass | 0 | 0 | 1.5833 | 2022-03-24 09:06 | 2022-03-25 17:00 | 2022-03-24 10:35 | 2022-03-25 17:00 | 2022-03-24 12:10 |  |  | Inspected circulating pump. Air lock in the system causing the pump not to work efficiently. Run all the hot taps for several minutes in the adjacent toilets. Everything in good working order
MSA-DTAG | WA5303626 | 1 | GPS Plumbing & Gas Services PtyLtd | Custody area - Staff Male Toilet – Toilet not functioning – the cistern does not fill with water | Plumbing & Drainage | Toilets/Cisterns | 370.555 | Pass | Pass | 0 | 0 | 1.5833 | 2022-04-04 11:26 | 2022-04-05 17:00 | 2022-04-05 13:05 | 2022-04-05 17:00 | 2022-04-05 14:40 |  |  | On my arrival the plastic parts of the buttons were sitting at the bottom of the cistern, hence cistern not operating as it should.Installed new outlet valve and washer
MSA-MRWA | WA6292426 | 1 | GPS Plumbing & Gas Services PtyLtd | Right hand side urinal is constantly running | Plumbing & Drainage | Toilets/Cisterns | 261.7275 | Pass | Pass | 0 | 0 | 1.5833 | 2022-11-29 10:16 | 2022-11-30 17:00 | 2022-11-29 13:20 | 2022-11-30 17:00 | 2022-11-29 14:55 |  |  | Replaced outlet washer and flushed cistern
MSA-DTWD | WA6294323 | 1 | AHS Services WA Pty Ltd (Anchor) | A block - Level 3 - A353B - Leaking male toilet pan onto floor (OHS issue) | Plumbing & Drainage | Toilets/Cisterns | 254.2825 | Pass | Pass | 0 | 0 | 1.5833 | 2022-11-30 14:38 | 2022-12-01 17:00 | 2022-12-01 07:50 | 2022-12-01 17:00 | 2022-12-01 09:25 |  |  | Completed
MSA-DCA | WA6518028 | 3 | GPS Plumbing & Gas Services PtyLtd | Loose tap in lady's toilet in the courtyard | Plumbing & Drainage | Water | 266.7275 | Pass | Pass | -1 | -1 | 1.5833 | 2023-01-24 15:48 | 2023-02-01 17:00 | 2023-01-25 12:35 | 2023-02-01 17:00 | 2023-01-25 14:10
MSA-DTWD | WA6675769 | 1 | Casa Security Pty Ltd | Whole campus-Allocate new PIN's to new Security Contractor-see notes | Security | Security Management System | 275 | Pass | Pass | 0 | 0 | 1.5833 | 2023-02-28 09:08 | 2023-03-01 17:00 | 2023-03-01 12:05 | 2023-03-01 17:00 | 2023-03-01 13:40
MSA-DCA | WA5017148 | 0 | GPS Plumbing & Gas Services PtyLtd | Ground water leak | Plumbing & Drainage | Water | 237.755 | Pass | Pass | 0 | 0 | 1.5833 | 2022-01-13 10:54 | 2022-01-13 12:54 | 2022-01-13 11:15 | 2022-01-13 14:54 | 2022-01-13 12:50 |  |  | Investigated water leak. Retic leaking. Reese advised. Trench backfilled.
MSA-DTAG | WA5413295 | 2 | Water2water Pty Ltd | Registrar’s Kitchen - Level 1 - Instant hot water tap not working | Plumbing & Drainage | HWS/Units Electric & Gas | 461.6925 | Pass | Pass | 0 | 0 | 1.5833 | 2022-05-12 10:01 | 2022-05-17 17:00 | 2022-05-17 09:00 | 2022-05-17 17:00 | 2022-05-17 10:35 |  |  | No hot water on arrival. Faulty hot pump. Replaced hot pump and inlet solenoid. Waited for tanks to fill and get to temp. Ran water through. Normal operation
MSA-DTAG | WA5495054 | 1 | Water2water Pty Ltd | JSO Staff Kitchen - Billi unit displaying “level sensors wrong” - intermittent fault. | Plumbing & Drainage | HWS/Units Electric & Gas | 452.9125 | Pass | Pass | 0 | 0 | 1.5833 | 2022-06-08 09:15 | 2022-06-09 17:00 | 2022-06-08 13:45 | 2022-06-09 17:00 | 2022-06-08 15:20 |  |  | Machine showing level sensor wrong. Replaced level sensor and loom and also replaced inlet solenoid. Waited for tanks to fill and heat and get cold to temp. Normal operation
MSA-DTWD | WA5672824 | 3 | Water2water Pty Ltd | G 102 staff kitchen - Chilled water unit not working | Plumbing & Drainage | Water | 873.265 | Pass | Pass | -1 | -1 | 1.5833 | 2022-07-20 09:55 | 2022-07-27 17:00 | 2022-07-21 10:55 | 2022-07-27 17:00 | 2022-07-21 12:30 |  |  | Replaced Wilson tap due to internal electrical failure checked and tested all okay
MSA-DTWD | WA5697961 | 2 | Water2water Pty Ltd | Ground Floor staff lunchroom - Zip tap stops working | Plumbing & Drainage | Water | 653.945 | Pass | Pass | 0 | 0 | 1.5833 | 2022-08-09 13:15 | 2022-08-12 17:00 | 2022-08-10 13:45 | 2022-08-12 17:00 | 2022-08-10 15:20 |  |  | System in fault on arrival. Really poor incoming water, and blocked filter. Replaced zip filter and flushed and reset counters. Also replaced safety solenoid and JG fitting and tube. Also replaced stirrer pump. Ran to temp. Normal operation
MSA-DCA | WA5839778 | 1 | TK Elevator Australia Pty Ltd | Main Passenger Lift is stuck on level 1 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5833 | 2022-09-09 15:53 | 2022-09-12 17:00 | 2022-09-09 17:13 | 2022-09-12 17:00 | 2022-09-09 18:48 |  |  | Suspect door motor to be faulty and stalling. Switched off due to possibility of future trappings. Further investigation needed
MSA-MRWA | WA5853472 | 1 | GPS Plumbing & Gas Services PtyLtd | right hand side toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 288.915 | Pass | Pass | 0 | 0 | 1.5833 | 2022-09-12 09:03 | 2022-09-13 17:00 | 2022-09-12 15:15 | 2022-09-13 17:00 | 2022-09-12 16:50 |  |  | Repaired faukty cistern
MSA-MRWA | WA5976725 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - cleaners cupboard - leaking tap | Plumbing & Drainage | Water | 313.7275 | Pass | Pass | 0 | 0 | 1.5833 | 2022-09-27 10:58 | 2022-09-28 17:00 | 2022-09-27 14:40 | 2022-09-28 17:00 | 2022-09-27 16:15 |  |  | Replaced lekaing and faulty taps in the cleaners as agreed with Danica
MSA-MRWA | WA6357197 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Male Bathroom RHS Urinal - L1 Male RHS Urinal constantly running - See Notes | Plumbing & Drainage | Toilets/Cisterns | 345.7275 | Pass | Pass | 0 | 0 | 1.5833 | 2022-12-05 11:42 | 2022-12-08 17:00 | 2022-12-06 15:45 | 2022-12-08 17:00 | 2022-12-06 17:20 |  |  | Replaced outlet valve
MSA-DFES | WA6675107 | 2 | Dom's Total Grounds Maintenance | Front Verge - Reticulation sprinklers broken | Plumbing & Drainage | Water | 279 | Fail | Fail | 0 | 0 | 1.5833 | 2023-02-27 15:27 | 2023-03-02 17:00 | 2023-03-04 12:45 | 2023-03-02 17:00 | 2023-03-04 14:20
MSA-DCA | WA4991646 | 2 | GPS Plumbing & Gas Services PtyLtd | Male Public Toilet - 2nd cubicle has slow leak to pan. Supply has been isolated | Plumbing & Drainage | Toilets/Cisterns | 279.285 | Pass | Pass | -1 | -1 | 1.5667 | 2022-01-05 10:20 | 2022-01-10 17:00 | 2022-01-06 13:41 | 2022-01-10 17:00 | 2022-01-06 15:15 |  |  | Replaced outlet washer and inlet, flexi
MSA-DCA | WA5989197 | 1 | Techworks Electrical | Ground Floor - Discovery Lounge Male Toilet - Hand dryer coming off wall - See notes below | Electrical | General Electrical | 191.765 | Pass | Pass | 0 | 0 | 1.5667 | 2022-10-04 12:44 | 2022-10-05 17:00 | 2022-10-04 14:00 | 2022-10-05 17:00 | 2022-10-04 15:34 |  |  | Removed fixings from loose hand dryer and installed new fixings. Hand dryer now fixed back to the wall
MSA-DFES | WA6642371 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Building-First Floor-ComCen Female Toilet - toilet not flushing properly | Plumbing & Drainage | Toilets/Cisterns | 344.775 | Pass | Pass | 0 | 0 | 1.5667 | 2023-02-19 12:25 | 2023-02-22 17:00 | 2023-02-20 15:59 | 2023-02-22 17:00 | 2023-02-20 17:33
MSA-MRWA | WA5216954 | 3 | GPS Plumbing & Gas Services PtyLtd | Drinking Water Fountain - Blocked drain under Water Fountain unit | Plumbing & Drainage | Drainage | 138.235 | Pass | Pass | 0 | 0 | 1.5667 | 2022-03-11 14:24 | 2022-03-18 17:00 | 2022-03-16 12:06 | 2022-03-18 17:00 | 2022-03-16 13:40 |  |  | Unblocked water fountain drain
MSA-DTWD | WA5478479 | 2 | Precise Air Group | Ground Level - Loading Dock - has two under bench friges broken needs de-gas and removing | Refrigeration | Refrigerators | 266.88 | Pass | Pass | -1 | -1 | 1.5667 | 2022-05-26 11:56 | 2022-05-31 17:00 | 2022-05-27 13:00 | 2022-05-31 17:00 | 2022-05-27 14:34 |  |  | Attended suppliers and collected bullet piercing valve. Attended site and completed pre start paperwork and signed in. Acessed loading bay and located 2x fridges and completed decommission. Removed doors and reclaimed gas. Disposed of old fridges into skip bin as directed. Cleaned work area and packed up work equipment. Completed paperwork.
MSA-DTAG | WA5834407 | 1 | Schindler Lifts Australia | Level 2a - Lift 2 - lift faulty - please see notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.55 | 2022-09-06 16:41 | 2022-09-07 17:00 | 2022-09-06 17:07 | 2022-09-07 17:00 | 2022-09-06 18:40 |  |  | Tested lift for 20 mins and did not fault No errors Lift left in service
MSA-MRWA | WA5534557 | 2 | Water2water Pty Ltd | ***See PFM for location***- Fountain continual dripping | Building | General Building | 324.7825 | Pass | Pass | -1 | -1 | 1.55 | 2022-06-16 11:51 | 2022-06-21 17:00 | 2022-06-16 15:01 | 2022-06-21 17:00 | 2022-06-16 16:34 |  |  | Replaced faucet
MSA-MRWA | WA5318208 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 7 - Female Toilet – LHS - Broken Toilet Seat | Plumbing & Drainage | Toilets/Cisterns | 626.385 | Pass | Pass | -1 | -1 | 1.55 | 2022-04-12 09:23 | 2022-04-19 17:00 | 2022-04-13 09:07 | 2022-04-19 17:00 | 2022-04-13 10:40 |  |  | Replaced damaged toilet seat
MSA-DTWD | WA4991965 | 3 | SCAVENGER SUPPLIES PTY LTD | Unit 1 - Customer Service - Main fire panel faulty | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Fail | Fail | 0 | 0 | 1.55 | 2022-01-05 14:54 | 2022-01-12 17:00 | 2022-01-13 11:57 | 2022-01-12 17:00 | 2022-01-13 13:30 |  |  | COMPLETEDSEE Report Description:WA4991965
MSA-DCA | WA5126885 | 3 | GPS Plumbing & Gas Services PtyLtd | Diesel pump house - Next to diesel pump house - Tap leaking | Plumbing & Drainage | Water | 232.6475 | Pass | Pass | -1 | -1 | 1.55 | 2022-02-14 10:11 | 2022-02-21 17:00 | 2022-02-16 10:57 | 2022-02-21 17:00 | 2022-02-16 12:30 |  |  | Replaced antivandal hosetap and installed vaccime breaker
MSA-DTAG | WA5513473 | 3 | Water2water Pty Ltd | Level 7 - Court 72 - Water Fountain - water pressure is very low | Plumbing & Drainage | Water | 522.805 | Pass | Pass | -1 | -1 | 1.55 | 2022-06-14 10:49 | 2022-06-21 17:00 | 2022-06-17 08:55 | 2022-06-21 17:00 | 2022-06-17 10:28 |  |  | Replaced bubbler
MSA-DCA | WA5827736 | 0 | TK Elevator Australia Pty Ltd | Lift Foyer - lift in fault | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.55 | 2022-09-01 12:43 | 2022-09-01 14:43 | 2022-09-01 14:19 | 2022-09-01 16:43 | 2022-09-01 15:52 |  |  | Upon arrival I found the lift ooo at the ground floor, i reset the cpu and investigated the pencil switchon the car to and found the guids worn causing the switch to touch the magnet i adjusted the guide as much as possible for clearance
MSA-DCA | WA5974832 | 0 | GPS Plumbing & Gas Services PtyLtd | Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 416.775 | Pass | Pass | 0 | 0 | 1.55 | 2022-09-24 08:16 | 2022-09-24 10:16 | 2022-09-24 10:00 | 2022-09-24 12:16 | 2022-09-24 11:33 |  |  | Replaced close coupled seal foam and fixing cistern kit to female public ground floor toilet
MSA-DCA | WA6518564 | 2 | GPS Plumbing & Gas Services PtyLtd | Upper Circle - Men's toilets - Auto flush is not working | Plumbing & Drainage | Toilets/Cisterns | 221.7275 | Pass | Pass | -1 | -1 | 1.55 | 2023-01-25 09:26 | 2023-01-31 17:00 | 2023-01-25 10:57 | 2023-01-31 17:00 | 2023-01-25 12:30
MSA-DFES | WA5437372 | 1 | Australian HVAC Services Pty. Ltd. | Power outage - running on generator at the moment - please check systems | Air Conditioning | Building HVAC Maintenance (Major Plant) | 179.76 | Pass | Pass | 0 | 0 | 1.5433 | 2022-05-16 07:29 | 2022-05-16 17:00 | 2022-05-16 08:26 | 2022-05-16 17:00 | 2022-05-16 09:59 |  |  | Attended site and inspected plant operation after power outage. Reset faults and confirmed correct operation of plant.
MSA-DTWD | WA5105435 | 3 | Boilertronics | A Block - Level 5 - Boiler Plant Room - Boiler is faulting shorlty after stratup procedure | Mechanical Services | Boilers | 280.5 | Pass | Pass | 0 | 0 | 1.5333 | 2022-02-04 10:32 | 2022-02-11 17:00 | 2022-02-09 08:10 | 2022-02-11 17:00 | 2022-02-09 09:42 |  |  | Travel to site. Contact Gareth and Meet with him to see what faults have been coming up on the LFL. Looks to be faulting just before the ‘2’ on the first line when the main gas valves switch on. Make way up to boiler but no heat call. Able to manual the heating water pump but unable to enable the boiler, speak with gareth and there doesn’t seem to be a way we can get the boiler to run. We may need to reopen this job when weather starts getting cooler in a couple months time and there is a heating call to the boiler but for now not able to run or test it.
MSA-MRWA | WA5395496 | 3 | GPS Plumbing & Gas Services PtyLtd | Basement - Male Toilets - Leaking showers | Plumbing & Drainage | Water | 222.29 | Pass | Pass | 0 | 0 | 1.5333 | 2022-05-05 13:33 | 2022-05-12 17:00 | 2022-05-09 08:38 | 2022-05-12 17:00 | 2022-05-09 10:10 |  |  | Rewashed lhs shower
MSA-DCA | WA5735247 | 3 | Techworks Electrical | Male Toilets Stalls ceiling light is out and not functioning - See notes | Electrical | Lighting, Internal | 210.15 | Pass | Pass | -1 | -1 | 1.5333 | 2022-08-16 12:04 | 2022-08-23 17:00 | 2022-08-16 13:30 | 2022-08-23 17:00 | 2022-08-16 15:02 |  |  | Attended site. Sourced tall ladder to reach light. Found globe to be loose. Tightened globe into light and globe came on and stayed on
MSA-MRWA | WA6107194 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 2 - UAT - Cistern button full flush button broken - see images in email | Plumbing & Drainage | Toilets/Cisterns | 299.7275 | Pass | Pass | -1 | -1 | 1.5333 | 2022-10-20 08:41 | 2022-10-27 17:00 | 2022-10-21 12:18 | 2022-10-27 17:00 | 2022-10-21 13:50 |  |  | Replaced damaged butto
MSA-DTAG | WA6370669 | 3 | Gilmour & Jooste Electrical | Internet input clip damaged - see notes | Electrical | General Electrical | 279.08 | Pass | Pass | 0 | 0 | 1.5333 | 2022-12-14 10:06 | 2022-12-21 17:00 | 2022-12-20 06:00 | 2022-12-21 17:00 | 2022-12-20 07:32 |  |  | Repaired data outlet.
MSA-DCA | WA6373541 | 1 | GPS Plumbing & Gas Services PtyLtd | pump room-Sewer smell in pump room and spreading to rest of basement area. | Plumbing & Drainage | Sewer Drains & Septic Systems | 221.7275 | Pass | Pass | 0 | 0 | 1.5333 | 2022-12-14 15:00 | 2022-12-15 17:00 | 2022-12-15 14:25 | 2022-12-15 17:00 | 2022-12-15 15:57 |  | WACCES | Have taped up lid to prevent smells from leaking out, spoke with Denise and will be issuing quote to replace lid under new work order
MSA-DCA | WA6390661 | 1 | Techworks Electrical | Phase 3 outlets-on bottom of floodlight poles need to be turned off. -see notes | Electrical | Lighting, External | 132.36 | Pass | Pass | 0 | 0 | 1.5333 | 2022-12-22 11:27 | 2022-12-23 17:00 | 2022-12-23 07:00 | 2022-12-23 17:00 | 2022-12-23 08:32 |  |  | Attended site and met with Kevininspected outlets to be isolatedisolated outlets and marked for identificationgot signoff from Kevinlet site, job complete
MSA-DTWD | WA6680385 | 1 | Dormakaba Australia Pty Ltd | Auto door not working and electronic lock not working | Building | Automatic Doors | 306.95 | Pass | Pass | 0 | 0 | 1.5333 | 2023-03-01 10:43 | 2023-03-02 17:00 | 2023-03-01 11:37 | 2023-03-02 17:00 | 2023-03-01 13:09
MSA-MRWA | WA6650974 | 3 | GPS Plumbing & Gas Services PtyLtd | Neither flush button working | Plumbing & Drainage | Toilets/Cisterns | 367.29 | Pass | Pass | -1 | -1 | 1.5167 | 2023-02-20 15:26 | 2023-02-27 17:00 | 2023-02-22 13:46 | 2023-02-27 17:00 | 2023-02-22 15:17
MSA-DTWD | WA5286257 | 1 | AHS Services WA Pty Ltd (Anchor) | A-Block - A039 - blocked sink | Plumbing & Drainage | Drainage | 522.105 | Pass | Pass | 0 | 0 | 1.5167 | 2022-03-21 14:00 | 2022-03-22 17:00 | 2022-03-21 14:29 | 2022-03-22 17:00 | 2022-03-21 16:00 |  |  | Completed
MSA-DTWD | WA5734606 | 1 | Dormakaba Australia Pty Ltd | nth west auto door-not securing at night | Building | Automatic Doors | 389.5 | Pass | Pass | 0 | 0 | 1.5167 | 2022-08-16 08:15 | 2022-08-17 17:00 | 2022-08-16 08:36 | 2022-08-17 17:00 | 2022-08-16 10:07 |  |  | 1091698. Call to site. Attend to auto door. Check and reset controller unit. Replace lock board causing mode errors. Restart and fully test - all okay now. Recommend unit is upgraded to ES200 locking platform due to age of unit. New sensors required, but existing keyswitches and buttons can be re-used.
MSA-DTWD | WA6020125 | 2 | AWB Co. | Replace the fluorescent tubes in the H002 staff lunch room | Electrical | Lighting, Internal | 194.275 | Pass | Pass | 0 | 0 | 1.5167 | 2022-10-13 10:56 | 2022-10-18 17:00 | 2022-10-18 10:44 | 2022-10-18 17:00 | 2022-10-18 12:15 |  |  | Attended site and signed in, completed JSA, spoke with fm about job, located room h002 , got parts from store room, replaced all tubes and starters in room, replaced 1x ballast, lights now working as intended, completed paperwork,packed up, cleaned up, signed out **job completed**
MSA-DFES | WA5482207 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level -Toilet (adjacent to Dining Room)- water from cistern is not draining from basin | Plumbing & Drainage | Toilets/Cisterns | 736.91 | Pass | Pass | 0 | 0 | 1.5167 | 2022-05-31 09:51 | 2022-06-01 17:00 | 2022-05-31 13:29 | 2022-06-01 17:00 | 2022-05-31 15:00 |  |  | Arrived to site and unblocked the urinal
MSA-DCA | WA6165833 | 0 | Automatic Fire Protection (ARA) | Multiple Fire Panels in Fault | Fire Protection Services | Fire Protection - Monitor System | 309.52 | Pass | Pass | 0 | 0 | 1.5167 | 2022-11-11 09:56 | 2022-11-11 11:56 | 2022-11-11 10:29 | 2022-11-11 13:56 | 2022-11-11 12:00 |  |  | Attended site Zones 11 duct probe, vesda alert zone 7 and vesda zone 8 activated at 440am this morning. Contractors working on installing new air conditioning unit system caused alarm, when attended site fip had been reset by DFES.Left normal on departure
MSA-DTWD | WA5053238 | 3 | AWB Co. | Block 3 - Ground - Male toilet - Broken light fitting | Electrical | Lighting, Internal | 180.54 | Pass | Pass | -1 | -1 | 1.5167 | 2022-01-18 14:22 | 2022-01-25 17:00 | 2022-01-20 13:59 | 2022-01-25 17:00 | 2022-01-20 15:30 |  |  | Attended site, signed in, completed jsa, spoke with fm about job, fm supplied 2x led battons as replacement, set up work area, isolated lighting circuit, removed old battens , installed new battens , re energised lighting circuit, tested lights and all working as intended , cleaned up, packed up, completed paperwork , signed out **job completed**
MSA-DCA | WA5207669 | 2 | Techworks Plumbing | Hackett Hall - G Floor- Male Toilets - Unblock hand basin wastes | Plumbing & Drainage | Water | 341.19 | Pass | Pass | 0 | 0 | 1.5167 | 2022-03-08 15:26 | 2022-03-11 17:00 | 2022-03-09 06:29 | 2022-03-11 17:00 | 2022-03-09 08:00 |  |  | Travel to site, sign in and access bathroom, located basin, cleaned out bottle trap and reassembled, tested, cleaned up work area and completed paperwork
MSA-DCA | WA6255407 | 0 | Techworks Plumbing | Francis St - Multiple toilet faults - see notes for locations | Plumbing & Drainage | Toilets/Cisterns | 135.14 | Pass | Pass | 0 | 0 | 1.5167 | 2022-11-23 10:29 | 2022-11-23 12:29 | 2022-11-23 12:29 | 2022-11-23 14:29 | 2022-11-23 14:00 |  |  | Joshua Salmon (23/11/2022) - Work NoteAttended for 2 flush plate issues. Both flush plates broken and were replaced using parts from storage onsite. Pneumatic flush plate had a broken locking clip at the base and had to be replaced.mechanical flush plate half flush button had cracked on the rear of the plate causing it to twist when flushed. Removed and replaced with new
MSA-DCA | WA4788998 | 3 | Techworks Electrical | Emergency Light Out - Arrow (Ref.E1) - see note below | Electrical | Emergency & Exit Lighting | 209.32 | Pass | Pass | 0 | -19 | 1.5 | 2021-11-10 07:26 | 2021-11-16 17:00 | 2021-11-15 11:00 | 2022-03-31 17:00 | 2021-11-15 12:30 |  | WACCES | Assessed and tested fault HA exit sign - sourced alternative part and provided option to client to replace
MSA-DFES | WA4985869 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Hallway to Gym - Exit sign from hallway into gym is not illuminating | Electrical | Lighting, Internal | 374.28 | Pass | Pass | 0 | 0 | 1.5 | 2021-12-30 13:25 | 2022-01-07 17:00 | 2022-01-06 12:45 | 2022-01-07 17:00 | 2022-01-06 14:15 |  |  | Attended site to investigate Exit sign from hallway into gym is not illuminating. Located light and tested, found light fitting was faulty. Went to wholesaler to collect gear. Returned to site and replaced fitting, tested and all is okay. Notified staff and left site.
MSA-DCA | WA4990840 | 1 | EQUANS Mechanical Services (WA) Pty Limited | plant room - boiler 2 - fire fault | Mechanical Services | Boilers | 1361.965 | Fail | Fail | 1 | 1 | 1.5 | 2022-01-04 12:18 | 2022-01-05 17:00 | 2022-01-11 08:00 | 2022-01-05 17:00 | 2022-01-11 09:30 |  |  | Boiler tronics attended site, and found loose wiring on boiler 1. Wiring has now been repaired and is up and running, further parts are required.
MSA-DTAG | WA4991828 | 2 | Schindler Lifts Australia | Ground Floor - Lift 2 - elevator second to the left has the 11th floor button pushed all the way in | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1.5 | 2022-01-05 12:38 | 2022-01-10 17:00 | 2022-01-06 08:45 | 2022-01-10 17:00 | 2022-01-06 10:15 |  |  | to be closed out at $0 cost
MSA-DCA | WA4991981 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Plant Room - Level 4 - chiller 4 not operational is failing | Refrigeration | Chiller | 1191.855 | Fail | Fail | 1 | 1 | 1.5 | 2022-01-05 15:39 | 2022-01-06 17:00 | 2022-01-10 08:00 | 2022-01-06 17:00 | 2022-01-10 09:30 |  |  | Attended site with airvision to investigate chiller 4 fault. Airvision have recommended a condenser water tube clean to be carried out on chiller 4 as a process of elimination to rectify further faults.
MSA-DTWD | WA4992616 | 3 | AWB Co. | E block - room E105 - damaged Wifi units - detaching from ceilings | Building | Ceiling | 264.78 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-06 14:27 | 2022-01-13 17:00 | 2022-01-13 09:30 | 2022-01-13 17:00 | 2022-01-13 11:00 |  |  | Attended site and signed in. Completed jsa. Met with IT guy on site and located wifi units and discussed where he wanted them, and what one was allocated to eat port on roof. Secured brackets to roof and connected cable from wifi box to port on roof. Took after pictures. Completed paperwork. Signed out.Job completed
MSA-DFES | WA4992627 | 3 | AWB Co. | S/O Dorm 1 - Refix fire door retaining magnet to wall, Fixings coming out of wall | Building | General Building | 298.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-06 14:37 | 2022-01-13 17:00 | 2022-01-12 07:00 | 2022-01-13 17:00 | 2022-01-12 08:30 |  |  | Retaining magnet removed to reveal plugs coming out of wall, wall anchors purchased from bunnings and fitted
MSA-DCA | WA4993608 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 4-Plant Room- Steam boiler alarm | Building | Materials | 225.0025 | Fail | Fail | 1 | 1 | 1.5 | 2022-01-08 12:32 | 2022-01-09 12:32 | 2022-01-13 09:30 | 2022-01-09 12:32 | 2022-01-13 11:00 |  | WACCES | Attended site with Boiler tronics. Boiler 1 faulty flame mechanism was removed and repaired. Unit tested and is now operational.
MSA-DTWD | WA4994843 | 3 | Falcetta Plumbing and Gas | B1 - Level 1 - Corridor - Water seaping from outlet and has low rate of flow | Plumbing & Drainage | Drainage | 342.55 | Fail | Fail | 0 | 0 | 1.5 | 2022-01-10 08:09 | 2022-01-17 17:00 | 2022-01-20 15:00 | 2022-01-17 17:00 | 2022-01-20 16:30 |  |  | replaced filter, inlet valve, flex hose, repaired faucet
MSA-DTWD | WA4995657 | 2 | PEEL LOCK SERVICES PTY LTD | Ground - AT106 - Entrance door barrel damaged to heavy vehicle workshop key won’t open | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.5 | 2022-01-10 14:44 | 2022-01-13 17:00 | 2022-01-13 10:35 | 2022-01-13 17:00 | 2022-01-13 12:05 |  |  | Job completed - replaced lock
MSA-DTWD | WA5001616 | 1 | Equans Mechanical Services Australia | B2417 – Fashion Office - air con is not cooling | Air Conditioning | Room Air Conditioners | 162.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-11 13:45 | 2022-01-12 17:00 | 2022-01-12 14:30 | 2022-01-12 17:00 | 2022-01-12 16:00 |  |  | Travelled to site. Logged on to site. Gained access to site. Checked and found office area AC unit operating as normal and office to be cool. Was informed that unit wasn't cooling on previous days and that maintenance had reset unit at MSSB. Gained access to roof and inspected AC unit. Found no active faults and nothing in history as unit was reset. Informed maintenance of outcomes. Completed paperwork and logged off site.
MSA-DTWD | WA5001622 | 1 | Equans Mechanical Services Australia | Main Plant Room - Air con 4 not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 162.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-11 13:53 | 2022-01-12 17:00 | 2022-01-12 12:30 | 2022-01-12 17:00 | 2022-01-12 14:00 |  |  | POWER TO UNIT IS LOW ON WHITE PHASE AND CAUSING OVERLOAD ON COMPRESSOR 1 STOPPING WHOLE UNIT. 2 X GPOS INSTALLED FOR TEMP SPOT COOLERS COULD BE THE ISSUE. ELECTRICAL REQUIRED ON-SITE AND RETURN VISIT REQUIRED TO CHECK AC OPERATION.Electrician attended site several times but appear to have fixed issue. Unit operating as normal
MSA-DTAG | WA5009994 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Public Toilet - Male Toilet - seat is broken toilet opposite caffisimo | Plumbing & Drainage | Toilets/Cisterns | 177.915 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-12 09:05 | 2022-01-13 17:00 | 2022-01-12 09:30 | 2022-01-13 17:00 | 2022-01-12 11:00 |  |  | Picked up and replaced damaged male toilet seat on the grid floor
MSA-DTWD | WA5017249 | 3 | AWB Co. | A123 - light requires replacing | Electrical | Lighting, Internal | 353.205 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-13 11:59 | 2022-01-20 17:00 | 2022-01-19 07:00 | 2022-01-20 17:00 | 2022-01-19 08:30 |  | WACCES | Attended site, signed in, completed jsa,picked up ordered parts from wholesaler, isolated lighting circui5, removed old light , found that cut out was too big to screw light onto gyprock, got a piece of timber and cut it in half , pre drilled holes to suit light base, put timber’s in roof space and mounted base of light to them , light was solid, put on cover , re energised circuit and all working as intended , took photos, packed up , cleaned up, completed paperwork , signed out ***job complete***
MSA-DCA | WA5018088 | 1 | Techworks Electrical | plant room - no electrics to hot water system | Electrical | General Electrical | 165.925 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 08:41 | 2022-01-17 17:00 | 2022-01-14 10:30 | 2022-01-17 17:00 | 2022-01-14 12:00 |  |  | Investigated faulty hwu power to find a tripped rcd,dosconnected circuit and tested to ensure correct test results with all passes.reconnected circuit and powered on with all HWU working.
MSA-DFES | WA5018115 | 3 | AWB Co. | gymnasium - damaged skirting board requiring repairs | Building | Internal Walls | 216.75 | Pass | Pass | -1 | -1 | 1.5 | 2022-01-14 08:54 | 2022-01-21 17:00 | 2022-01-17 07:00 | 2022-01-21 17:00 | 2022-01-17 08:30 |  |  | Attended site and installed new skirting , gapped and ?lled
MSA-DTWD | WA5018277 | 2 | AWB Co. | Light fitting has come loose & is hanging precariously. | Electrical | Lighting, Internal | 193.04 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 10:38 | 2022-01-19 17:00 | 2022-01-18 08:30 | 2022-01-19 17:00 | 2022-01-18 10:00 |  |  | Attended site, signed in, completed jsa, spoke with fm about work to be done, located room with lighting hanging down, set up work area, removed diffuser , cover and tubes from fitting, removed old screw and plug , wiped down surfaces between light and ceiling , put in new plug and ran a bead of silicon along ceiling then fixed light back up, re fitted cover , tubes and diffuser , went to all other light fittings in room to check they were secure as per fm request , all lights were secure, tested lights and they are working as intended , cleaned up, packed up , completed paperwork , signed out ***job completed***
MSA-DTAG | WA5018409 | 2 | Water2water Pty Ltd | level 14 - staff kitchen - billi tap not hot or cold | Plumbing & Drainage | Water | 435.93 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 11:24 | 2022-01-19 17:00 | 2022-01-17 15:00 | 2022-01-19 17:00 | 2022-01-17 16:30 |  |  | Replaced faulty tap loom
MSA-DTWD | WA5018415 | 2 | LIGHTHOUSE LOCKSMITHS | Exterior gate the press button security gate lock is broken | Security | Locksmith | 460 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 11:25 | 2022-01-19 17:00 | 2022-01-18 14:15 | 2022-01-19 17:00 | 2022-01-18 15:45 |  |  | replaced broken mortice lock on gate
MSA-DCA | WA5018567 | 2 | Techworks Electrical | Francis Street, Main Entry Building -Faulty light switch, located inside store to the left of door. | Electrical | Lighting, Internal | 190.095 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 13:00 | 2022-01-19 17:00 | 2022-01-19 06:00 | 2022-01-19 17:00 | 2022-01-19 07:30 |  |  | Swapped faulty mech with new
MSA-DTWD | WA5018680 | 3 | Equans Mechanical Services Australia | Creche - Room 3 - Water damage | Air Conditioning | Room Air Conditioners | 162.21 | Pass | Pass | -1 | -1 | 1.5 | 2022-01-14 14:35 | 2022-01-21 17:00 | 2022-01-17 08:30 | 2022-01-21 17:00 | 2022-01-17 10:00 |  |  | Attended site,signed in and accessed building B1 creche room 3. Found no water in affected area at the time of inspection. Turned on sink tap behind wall of affected area, checked the drain line, water supply line and all areas around the sink for and water residue. Found no water. Spoke with the lady on site who spotted the water week's ago and asked her to monitor certain areas for any dampness. Asked creche staff to notify me as soon as water returns.
MSA-DTWD | WA5018699 | 2 | Equans Mechanical Services Australia | Level 3 - Plant Room - 133N - Air con not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 162.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 15:04 | 2022-01-19 17:00 | 2022-01-17 08:00 | 2022-01-19 17:00 | 2022-01-17 09:30 |  |  | Attended site, signed in and accessed the chiller compound. Checked the chiller status and found a fault (75) - inadequate chilled water flow. Reset the fault and monitored chiller start up and running conditions. Further investigation is required into flow fault. Will investigate and monitor during hvac maintenance.
MSA-DTAG | WA5018701 | 2 | Bullant Security Pty Ltd | Courtside - Admin - Women's toilets - Shower door has internally locked & cannot open | Security | Locksmith | 408.64 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 15:24 | 2022-01-19 17:00 | 2022-01-17 11:15 | 2022-01-19 17:00 | 2022-01-17 12:45 |  |  | Attended site, gained entry to women's toilet/shower room and replaced faulty mortice lock and set function as requested. Date on site: 17/01/2022 Time on site: 11:15 - 12:45
MSA-DFES | WA5018732 | 2 | Protek 24/7 Building & Maintenance | Door between DOSS office to comcen door will not close | Building | Doors | 177.55 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-14 16:09 | 2022-01-19 17:00 | 2022-01-18 13:30 | 2022-01-19 17:00 | 2022-01-18 15:00 |  |  | repair door
MSA-DTAG | WA5038154 | 1 | Elec Power Technologies | Level 8 - UPs Room - fault in the ups on level 8 causing an alarm to go off | Security | Security Management System |  | Fail | Fail | 1 | 1 | 1.5 | 2022-01-17 10:41 | 2022-01-18 17:00 | 2022-01-24 11:00 | 2022-01-18 17:00 | 2022-01-24 12:30 |  |  | Site attendance for Call Out & Fault Finding on Level 8 UPS 2: Smoke is coming from UPS2.
MSA-DTWD | WA5069102 | 2 | Techworks Electrical | Austco system has a comms fault | Electrical | General Electrical | 171.535 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-19 14:56 | 2022-01-24 17:00 | 2022-01-24 13:00 | 2022-01-24 17:00 | 2022-01-24 14:30 |  |  | found Austco system to be in fail safe mode in the data rack, could not identify what caused the system to go into fail safe mode, after resetting power and cycling through the outputs to turn it all on again system is working correctly, went through each ward and activated the alarm for every bed and system cycles through beds on the screen.
MSA-DTWD | WA5069154 | 2 | Techworks Plumbing | Toilets full flush button not working | Plumbing & Drainage | Toilets/Cisterns | 304.24 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-19 15:33 | 2022-01-24 17:00 | 2022-01-21 09:00 | 2022-01-24 17:00 | 2022-01-21 10:30 |  |  | Attended site to see why full flush was not working, Found to be just the button being sticky applied some grease to it and was working fine, found the inlet valve was spraying water over the side of the cistern when filling due to no having a cover we ,a aged to find the cover in the wall cavity and put back on to rectify, also found the back plate on the wall was flapping everyone they opened the toilet door, so I secured it to the was properly
MSA-DTWD | WA5069178 | 3 | Falcetta Plumbing and Gas | Flick mixer not working properly | Plumbing & Drainage | Water | 286.79 | Pass | Pass | -1 | -1 | 1.5 | 2022-01-19 16:07 | 2022-01-27 17:00 | 2022-01-20 13:45 | 2022-01-27 17:00 | 2022-01-20 15:15 |  |  | repaired piping and installed filter faucet
MSA-DCA | WA5070493 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Gallery 14 lvl 1 - BMS alarm - Room temp - value 25.8552 | Air Conditioning | Room Air Conditioners | 188.375 | Fail | Fail | 1 | 1 | 1.5 | 2022-01-19 19:21 | 2022-01-19 21:21 | 2022-01-27 11:00 | 2022-01-19 23:21 | 2022-01-27 12:30 |  |  | Attended site, signed accessed the bms and located areas with temperature complaints. Checked the ahu servicing the area and found chwv fully open but not reaching set point. stroked the chilled water valve and monitored temperatures slowly lowering.
MSA-DTWD | WA5081104 | 2 | AWB Co. | V Block - V06- V07 -V08 -toilets- Faulty exhaust fans | Electrical | General Electrical | 301.06 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-20 11:07 | 2022-01-25 17:00 | 2022-01-25 07:00 | 2022-01-25 17:00 | 2022-01-25 08:30 |  |  | Attended site and signed in. Completed JSA. Located mssb, fans in toilet area and store room, tested for voltage and one contactor wasn’t pulled in, fault light on fan b was on , turned off RCDs and switched them back on, reset both thermal overloads and contactor pulled in, reset RCDs again and both contractors pulled in, recommended to fm that he gets the exhaust fans serviced as they were working but not too strong , packed up , cleaned up, completed paperwork , signed out , **job completed**
MSA-DTWD | WA5081482 | 2 | Techworks Plumbing | G Block - Ground - G6 - Ladies toilet - see details below | Plumbing & Drainage | Toilets/Cisterns | 304.24 | Pass | Pass | -1 | -1 | 1.5 | 2022-01-20 14:24 | 2022-01-25 17:00 | 2022-01-21 12:00 | 2022-01-25 17:00 | 2022-01-21 13:30 |  |  | Attended site signed in at reception met with Dennis who showed us the 2 ladies toilet that kept running after they were flushed, inspected and found that the inlet valve was set to high and water was going in the over flow pipe, we reset the inlet valve to below the over pipe and tested after, toilets are working properly now
MSA-DTWD | WA5081574 | 3 | AWB Co. | E Block - Ground - E628 - Smashed outlet Surface Grinder 46 | Electrical | General Electrical | 510.53 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-20 16:21 | 2022-01-28 17:00 | 2022-01-28 13:30 | 2022-01-28 17:00 | 2022-01-28 15:00 |  |  | Attended site and signed in. Complete jsa. Located faulty outlets on machine. Supply and replace with new outlet and covers. Unable to test due to being locked out by staff on site and they had left. All okay on site. Signed out, job complete
MSA-DTWD | WA5085889 | 3 | AWB Co. | A Block Exterior - 1 Richmond Street - Exterior Stairs - see details | Building | General Building | 257.3 | Pass | Pass | -1 | -1 | 1.5 | 2022-01-21 10:02 | 2022-01-31 17:00 | 2022-01-27 07:00 | 2022-01-31 17:00 | 2022-01-27 08:30 |  |  | Hand rail fitted to wall, job complete**Holiday Works - slip not signed**
MSA-DTWD | WA5087903 | 3 | AWB Co. | level 1 - B/block - 6 classroom has no lighting | Electrical | General Electrical | 180.54 | Pass | Pass | -1 | -1 | 1.5 | 2022-01-24 14:17 | 2022-02-01 17:00 | 2022-01-24 15:00 | 2022-02-01 17:00 | 2022-01-24 16:30 |  |  | Repaired faulty lighting in B block and repaired broken sensor**JSA not required due no work undertaken, only site inspection and parts ordered**
MSA-DTWD | WA5088723 | 2 | AWB Co. | Faulty Emergency light fitting | Electrical | Lighting, Internal | 280.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-24 18:53 | 2022-01-28 17:00 | 2022-01-27 11:30 | 2022-01-28 17:00 | 2022-01-27 13:00 |  |  | Attached site and signed in. Located room E62. Found light. Isolated power and tested. Removed and replaced faulty light. Retested all now working. Informed site.
MSA-DTWD | WA5090049 | 3 | AWB Co. | E block - South East car park - Small sink hole in the bitumen driveway | Paving & Roadworks | Asphalt | 210 | Fail | Fail | 1 | 1 | 1.5 | 2022-01-25 08:58 | 2022-02-02 17:00 | 2022-02-11 13:00 | 2022-02-02 17:00 | 2022-02-11 14:30 |  |  | Sink hole - repair and make good
MSA-DTAG | WA5090507 | 2 | Midolo Building Services | Level 4 - ALS reception counter - A metal strip has come off the ALS Reception Counter | Building | Internal Walls | 240.38 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-25 12:56 | 2022-01-31 17:00 | 2022-01-31 09:15 | 2022-01-31 17:00 | 2022-01-31 10:45 |  |  | secured strip back to glass
MSA-DCA | WA5090697 | 1 | Techworks Electrical | Power is out for half of the building | Electrical | General Electrical | 190.385 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-25 15:20 | 2022-01-27 17:00 | 2022-01-27 09:00 | 2022-01-27 17:00 | 2022-01-27 10:30 |  |  | Water spilled onto PowerPoint cleaned and dried and circuit tested and reset
MSA-DTWD | WA5092652 | 2 | AHS Services WA Pty Ltd (Anchor) | A Block - Level 1 - A154 - Cistern running continuously | Plumbing & Drainage | Toilets/Cisterns | 148.785 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-28 08:49 | 2022-02-02 17:00 | 2022-01-31 08:00 | 2022-02-02 17:00 | 2022-01-31 09:30 |  |  | Replaced worn flush rubber
MSA-DTWD | WA5093354 | 2 | M Construction (WA) | E Block - Ground - Deli - internal door to Deli not closing properly | Building | General Building | 180 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-28 13:43 | 2022-02-02 17:00 | 2022-01-31 07:00 | 2022-02-02 17:00 | 2022-01-31 08:30 |  |  | Fix set of double doors that were not locking.
MSA-DTWD | WA5094313 | 1 | AWB Co. | Block 7 - Ground - Canteen kitchen - Wall fans not working | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-31 10:08 | 2022-02-01 17:00 | 2022-01-31 11:15 | 2022-02-01 17:00 | 2022-01-31 12:45 |  |  | Attended site and signed in. Completed JSA. Located canteen area fans. Found to be on circuit R10. Tested for power at outlets and nothing. Tested for power at circuit breaker and all okay. Investigated to see if related to new works in canteen but not related. Looked through kitchen to find a 2 gang switch that controls the fans. Switch works staff didn’t know about the fans as they use the pull cords. All is good. Signed out. Job complete
MSA-DCA | WA5094920 | 1 | Techworks Electrical | Mezzanine Level - Dressing Room - Reinstall/replace emergency exit light disconnected due to water. | Electrical | General Electrical | 170.07 | Pass | Pass | 0 | 0 | 1.5 | 2022-01-31 15:58 | 2022-02-01 17:00 | 2022-02-01 08:00 | 2022-02-01 17:00 | 2022-02-01 09:30 |  |  | Reinstalled em light
MSA-DFES | WA5098409 | 1 | Critical Fire Protection & Training | Main Entrance - FIP - 2 x sensors in fault - see notes below | Fire Protection Services | Fire Protection - Monitor System | 513.51 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-01 09:07 | 2022-02-02 17:00 | 2022-02-01 10:45 | 2022-02-02 17:00 | 2022-02-01 12:15 |  |  | Upon arrival, found detectors L1 37 & 45. 37 were dirty with gyprock dust and required replacement. 45 had a damaged address card. Fixed card. Performed loop test. System normal. 1x xp 95 optical. 1x xp 95 heat supplied.
MSA-MRWA | WA5098790 | 2 | LYNX INTEGRATED SYSTEMS | Open Office Area – West End - Section of lights out in open area at west end of level 3 | Electrical | Lighting, Internal | 240 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-01 11:28 | 2022-02-04 17:00 | 2022-02-01 13:00 | 2022-02-04 17:00 | 2022-02-01 14:30 |  |  | Lights were off upon arrival. Upon investigation found the sensor in area appears to have stopped sending commands. Swapped sensor 1.7.8 and sensor 1.7.69 as master and slave and simulated the enabling and disabling of commands. Could see commands being sent without issue. Tested the presence detection of the new master at 10 seconds with success and could also see the slave commands from 1.7.69 without issue. Client to monitor and advise if issue reoccurs.
MSA-DTWD | WA5100459 | 3 | Falcetta Plumbing and Gas | Sink is leaking | Plumbing & Drainage | Water | 196.98 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-02 13:57 | 2022-02-09 17:00 | 2022-02-08 14:00 | 2022-02-09 17:00 | 2022-02-08 15:30 |  |  | Repaired leaking waste and sealed at slab
MSA-DTWD | WA5101613 | 1 | AWB Co. | Emergency Exit bar on door is not engaging locking mechanism. | Building | Doors | 188.25 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-03 13:18 | 2022-02-04 17:00 | 2022-02-04 14:30 | 2022-02-04 17:00 | 2022-02-04 16:00 |  |  | Arrived on site signed in at facility services then was shown the door lock with the issue proceeded to pull the door lock to bits to investigate issue found that the pin driving from the internal side was disengaged I reengaged and replaced door handle screws which were bent and not quite long enough to hold external handle tightly clean site
MSA-DTWD | WA5101616 | 1 | GRAFFITI FORCE PTY LTD | Whole of campus - Removal of graffiti on front of campus entry sign also within campus area | Cleaning | Graffiti | 244.92 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-03 13:18 | 2022-02-04 17:00 | 2022-02-04 07:30 | 2022-02-04 17:00 | 2022-02-04 09:00 |  |  | REMOVAL OF GRAFFITI FROM FRONT SIGN OF CAMPUS
MSA-DCA | WA5101798 | 1 | Techworks Plumbing | Ground - Male Toilet - Install Geberit flush plate in the male toilets - see details below | Plumbing & Drainage | Toilets/Cisterns | 180.87 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-03 14:57 | 2022-02-04 17:00 | 2022-02-03 15:00 | 2022-02-04 17:00 | 2022-02-03 16:30 |  |  | Replace new cistern button
MSA-DFES | WA5101865 | 1 | Go Doors | rear engine room door - not working - will not open or close, lights are on but not action | Building | Automatic Doors | 722.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-03 15:54 | 2022-02-04 17:00 | 2022-02-04 08:00 | 2022-02-04 17:00 | 2022-02-04 09:30 |  |  | Completed works. See attachments.
MSA-DTAG | WA5105342 | 1 | Sapio Pty Ltd | Court Complex - all areas - Alarm to Building would not set – required manual over | Security | Security Management System | 190 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-04 09:42 | 2022-02-07 17:00 | 2022-02-04 16:00 | 2022-02-07 17:00 | 2022-02-04 17:30 |  | WACCES | Found duress for court 1 judicial entry door isolated and then I de isolated, tested and confirmed working all okay. Also resecured button as it was lose when attempting to twist reset. All okay and arming with no issues. Reporting to monitoring as well.
MSA-DTWD | WA5105713 | 2 | AWB Co. | Block 3 - 3B6 - 4 x faulty GPO’s | Electrical | General Electrical | 369.93 | Fail | Fail | 1 | 1 | 1.5 | 2022-02-04 13:13 | 2022-02-09 17:00 | 2022-02-14 15:00 | 2022-02-09 17:00 | 2022-02-14 16:30 |  |  | Attended site as requested by site due to class being in use and signed in. Completed jsa. Liaised with fm about works. Located room. Supplied and replaced 5x single GPOs with 5x new Double GPOs. Notified of works completed. **job complete**
MSA-DCA | WA5106995 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main building - Level 1 - High temp in HLT auditorium – 24.4, reading at stage door is 21.5 | Air Conditioning | Room Air Conditioners | 188.375 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-07 13:28 | 2022-02-08 17:00 | 2022-02-08 14:30 | 2022-02-08 17:00 | 2022-02-08 16:00 |  |  | Attended site. Investigated temp complaints in HLT. Found complaints were raised Saturday when the outdoor temperature reached 42c. As unit brings in fresh air this would result in a higher supply air temp. Checked temperatures and sensors reading true. All ok. Completed paperwork.
MSA-DTWD | WA5108058 | 1 | AWB Co. | B Block - Ground - B37 – Electrical Workshop 2 - see details below | Electrical | General Electrical | 272.43 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-08 11:17 | 2022-02-09 17:00 | 2022-02-08 14:00 | 2022-02-09 17:00 | 2022-02-08 15:30 |  |  | Attended site and signed in. Completed JSA. Liaised with tech about works. Reinstated light switches at damaged wall. Left tied up near window. Lights now working. **job complete**
MSA-DTWD | WA5108154 | 3 | AWB Co. | Re install white board falling off wall | Building | Internal Walls | 184.7 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-08 12:00 | 2022-02-15 17:00 | 2022-02-11 07:00 | 2022-02-15 17:00 | 2022-02-11 08:30 |  |  | Removed existing pin board and installed new whiteboard
MSA-DCA | WA5108215 | 3 | Techworks Electrical | Lift Foyer - Hallway light switches on Mezzanine level just outside lift under the clock, are faulty | Electrical | General Electrical | 336.91 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-08 12:31 | 2022-02-15 17:00 | 2022-02-11 09:30 | 2022-02-15 17:00 | 2022-02-11 11:00 |  |  | Replaced switches
MSA-DCA | WA5108498 | 2 | Techworks Plumbing | Hackett Hall - ground - female toilet - Check & repair blockage to Female WC basin - see notes | Plumbing & Drainage | Water | 277.83 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-08 14:43 | 2022-02-11 17:00 | 2022-02-09 07:00 | 2022-02-11 17:00 | 2022-02-09 08:30 |  |  | Bathroom basin trap full of hair and gunk, removed and cleaned to allow drainage
MSA-DTWD | WA5109446 | 2 | Lane's Plumbing | BLD 822A - Bathroom -Faulty water drains | Plumbing & Drainage | Drainage |  | Pass | Pass | -1 | -1 | 1.5 | 2022-02-09 09:47 | 2022-02-14 17:00 | 2022-02-09 15:00 | 2022-02-14 17:00 | 2022-02-09 16:30 |  |  | job completed - check & cleared Drain
MSA-DTWD | WA5109843 | 1 | BJ SYSTEMS | Security controller system is offline.. | Security | Security Management System | 207.5 | Fail | Fail | 1 | 1 | 1.5 | 2022-02-09 13:42 | 2022-02-10 17:00 | 2022-02-17 12:45 | 2022-02-10 17:00 | 2022-02-17 14:15 |  |  | Attend site for F Block controller offline. Located panel in room F25, restarted controller, now back online and working correctly
MSA-DCA | WA5111865 | 1 | Techworks Electrical | Ground - dressing room 4 - Broken light/fan switch in the bathrooms of Dressing Room 4 | Electrical | General Electrical | 635.26 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-10 11:37 | 2022-02-11 17:00 | 2022-02-11 08:00 | 2022-02-11 17:00 | 2022-02-11 09:30 |  |  | Replaced faulty switch mechs for new iconic range, replaced switch from work order and a few others also in need of replacing soon as preventative maintenance
MSA-DTWD | WA5115728 | 2 | ECO PLUMBING AND GAS PTY LTD | Disabled toilet - will not flush | Plumbing & Drainage | Toilets/Cisterns | 290.98 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-11 08:56 | 2022-02-16 17:00 | 2022-02-14 13:00 | 2022-02-16 17:00 | 2022-02-14 14:30 |  |  | Repaired cistern
MSA-DTWD | WA5115876 | 2 | AWB Co. | F Block courtyard adjacent to room F16 - Courtyard light pole not working | Electrical | Lighting, External | 316.79 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-11 09:54 | 2022-02-16 17:00 | 2022-02-16 11:00 | 2022-02-16 17:00 | 2022-02-16 12:30 |  |  | Attended site and signed in. Completed JSA. Located faulty light fitting in court yard of F block. Supply and replaced lamp where required, and wired to suit new lamp. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5116304 | 3 | AWB Co. | A Block - Level 3 - A308 - Replace GROWLUX light tubes in plant incubation cabinet | Electrical | General Electrical | 360.93 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-11 13:28 | 2022-02-18 17:00 | 2022-02-16 13:00 | 2022-02-18 17:00 | 2022-02-16 14:30 |  |  | attended site and signed in. Located FM on site and found room with faultyTubes and starters so replaced 4x s10 starters and 4x growlux 36w tubes as sourced from supplier. Have left 6 extra tubes in room on site for future use. Notified technician of extra tubes. Tested ok **job completed**
MSA-DCA | WA5116489 | 3 | MARSHALL BEATTIE AUTOMATION | Jubilee - Reflections Gallery - Main door will not close - hydraulic auto fire door | Building | Automatic Doors | 203.48 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-11 16:08 | 2022-02-18 17:00 | 2022-02-14 12:30 | 2022-02-18 17:00 | 2022-02-14 14:00
MSA-DFES | WA5126356 | 3 | Australian HVAC Services Pty. Ltd. | Kitchen - DAI KIN Inverter Air Con in kitchen has water leaking from RH side as you look at unit. | Air Conditioning | Room Air Conditioners | 179.76 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-14 07:49 | 2022-02-18 17:00 | 2022-02-16 08:00 | 2022-02-18 17:00 | 2022-02-16 09:30 |  |  | Arrived on site and spoke to site representative about the issue with the AC unit. Gained access to the AC and found that the condensate drain was blocked. Dismantled the unit and carried out unblocking the drain. Tested drain with water and found that the drain was operating correctly. Wash the facia and filters. Reassemble the unit and tested operation. Packed up and left site.
MSA-DTWD | WA5126880 | 3 | AWB Co. | Level 3 - room A303 staff room - blown flurors | Electrical | Lighting, Internal | 431.17 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-14 10:24 | 2022-02-21 17:00 | 2022-02-17 10:00 | 2022-02-21 17:00 | 2022-02-17 11:30 |  |  | Attended site signed in contacted FM about job location. Replaced various lamps in level 3 office area. Also replaced x 2 mh lamps and x 1 halogen 20w downlight Inspected lights in room 252 all lights were operational light switch was hidden behind boxes.** Job complete **
MSA-DFES | WA5127340 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Dorm 6 shower - Shower mixer tap has lost the locking screw and falls off the mixer | Plumbing & Drainage | Materials | 194.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-14 12:35 | 2022-02-21 17:00 | 2022-02-21 14:00 | 2022-02-21 17:00 | 2022-02-21 15:30 |  |  | Attended site for dorm six shower mixer tap has lost grub screw and falls off the mixer I have replaced the grub screw and tightened so the mixer handle is now secure everything is working correctly cleaned up packed up
MSA-DTAG | WA5127713 | 3 | Australian HVAC Services Pty. Ltd. | Courtside - Level 1 - staff kitchen - Air Conditioner in Staff kitchen appears to be leaking | Air Conditioning | Room Air Conditioners | 266.1 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-14 13:51 | 2022-02-21 17:00 | 2022-02-15 14:00 | 2022-02-21 17:00 | 2022-02-15 15:30 |  |  | Service call water leaking in kitchen acLocated unit and then found drain. Drain was slightly blocked unblocked drain cleaned drip tray and poured 3l of water to test and flush system.All working well packed up and left site.
MSA-DTWD | WA5127882 | 1 | Equans Mechanical Services Australia | BMS Aircon - Rooms 205,215,216,219,229,229 - aircon not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 162.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-14 14:33 | 2022-02-15 17:00 | 2022-02-15 14:30 | 2022-02-15 17:00 | 2022-02-15 16:00 |  |  | Found the VRV that services the warm rooms is the on that Daikin is repairing. Will chase up the status of this job .
MSA-DTWD | WA5128018 | 3 | Falcetta Plumbing and Gas | Level 2 - Room B200 - Leaking water hoses - further notes below | Plumbing & Drainage | Water | 206.98 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-14 15:21 | 2022-02-21 17:00 | 2022-02-17 16:30 | 2022-02-21 17:00 | 2022-02-17 18:00 |  |  | installed new connection for dishwasher drain hose and inspected all
MSA-DTAG | WA5128157 | 3 | AHS Services WA Pty Ltd (Anchor) | G Floor - Ladies & Mens staff toilet - Flush buttons not working, further notes below | Plumbing & Drainage | Toilets/Cisterns | 247.555 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-14 16:09 | 2022-02-21 17:00 | 2022-02-21 07:30 | 2022-02-21 17:00 | 2022-02-21 09:00 |  |  | Replaced split bellows to female toilets on ground floor.Checked male toilets found to be all good.
MSA-DTWD | WA5133297 | 1 | Milners Tree Solutions Pty Ltd | Block 7 - Ground - Driveway to skip bin bay - Large tree branch blocking access way | Landscaping & Gardening | General Tree Works | 1000 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-15 09:20 | 2022-02-16 17:00 | 2022-02-15 10:10 | 2022-02-16 17:00 | 2022-02-15 11:40 |  |  | FALLEN LIMB REMOVED
MSA-DFES | WA5133838 | 2 | Australian HVAC Services Pty. Ltd. | Meeting Room - Meeting Room – Split System Airconditioning, Runs for approx. 10 minutes then stops | Air Conditioning | Room Air Conditioners | 179.76 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-15 14:56 | 2022-02-18 17:00 | 2022-02-17 08:00 | 2022-02-18 17:00 | 2022-02-17 09:30 |  |  | Dave Mayers (17/02/2022) - Work Note - Travelled to site, spoke with on-site representatives regarding access to the Armadale Volunteer fire services building, gained access, located Daikin wall split system serving the meeting room, found AC unit not working, further investigation found that the air-conditioning system had been switched off & fitted with an Out of Service tag.Gas leak repairs required, quote submitted.
MSA-DTWD | WA5133854 | 1 | Precise Air Group | U Block - U008 and U009 - Evap air con consantly leaking water while its on | Air Conditioning | Room Air Conditioners | 266.88 | Fail | Fail | 0 | 0 | 1.5 | 2022-02-15 15:23 | 2022-02-16 17:00 | 2022-02-17 14:00 | 2022-02-16 17:00 | 2022-02-17 15:30 |  |  | Attended site signed in and gained access to reported area. Checked all units in the area and adjusted all bleed valves and float valves as needed. Issue resolved
MSA-DFES | WA5133871 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Engine Room - Power point to vehicle chargers not working on northern wall of engine room | Electrical | General Electrical | 274.08 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-15 16:08 | 2022-02-18 17:00 | 2022-02-18 13:30 | 2022-02-18 17:00 | 2022-02-18 15:00 |  |  | Attended site to investigate power points not working in truck charging room. Found multiple PowerPoints with no voltage. Found RCD controlling those points has tripped. Reset RCD and plugged in chargers. Tested rcd trip time and conducted a load test on a circuit. Unable to recreate the fault. Suspect a faulty appliance was plugged in at some stage. Notified staff and signed out
MSA-DCA | WA5141260 | 1 | Precise Air Group | plant room - level 4 - WA opera offices air con issue | Air Conditioning | Room Air Conditioners | 188.385 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-16 08:48 | 2022-02-17 17:00 | 2022-02-16 09:30 | 2022-02-17 17:00 | 2022-02-16 11:00 |  |  | Attended site, gained access spoke with site contact regarding issues, gained access into BMS, made minor adjustments, left equipment in auto
MSA-DTWD | WA5141405 | 1 | Precise Air Group | B block - Chiller not running due to Chilled water pump fault | Air Conditioning | Room Air Conditioners | 188.385 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-16 09:57 | 2022-02-17 17:00 | 2022-02-16 12:00 | 2022-02-17 17:00 | 2022-02-16 13:30 |  |  | Attended site and completed pre start paperwork and signed in. Fm reported that b block chiller is not running. Inspected and found no chilled water flow. Found pump circuit breaker tripped. Reset and test ran with vsd. Found motor to start and run with out fault. Monitored for a while and left running. Fm to monitor.
MSA-DFES | WA5151532 | 0 | Go Doors | Gate is not working - auto gate | Building | Doors | 418.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-17 13:29 | 2022-02-17 15:29 | 2022-02-17 14:30 | 2022-02-17 17:29 | 2022-02-17 16:00 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5151644 | 2 | AHS Services WA Pty Ltd (Anchor) | A block - A145 - 1st toilet on the right- Cistern running continuously | Plumbing & Drainage | Toilets/Cisterns | 185.415 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-17 15:16 | 2022-02-22 17:00 | 2022-02-18 14:00 | 2022-02-22 17:00 | 2022-02-18 15:30 |  |  | Replaced faulty inlet valve to female toilet next to the prayer room
MSA-DTWD | WA5163607 | 2 | WESTERN IRRIGATION PTY LTD | P-Block -grass area - broken gear sprinkler again, repair and place concrete protect around sprinkle | Landscaping & Gardening | Grounds Maintenance | 369.12 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-18 10:16 | 2022-02-23 17:00 | 2022-02-23 08:00 | 2022-02-23 17:00 | 2022-02-23 09:30 |  |  | Liaised with site contact, moved and replaced sprinkler contentiously being damaged by vehicles, fitted concrete surround to protect the sprinkler.
MSA-DTWD | WA5163691 | 2 | SCAVENGER SUPPLIES PTY LTD | Existing Fire Extinguishers need to be mounted on the wall. | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 134.6 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-18 11:10 | 2022-02-23 17:00 | 2022-02-23 13:45 | 2022-02-23 17:00 | 2022-02-23 15:15 |  |  | COMPLETED 23/2/20223 x remounted extinguishers2 x Fire extinguisher location signs2 x AFFF ID signs1 x ABE ID sign
MSA-DTWD | WA5175695 | 3 | Falcetta Plumbing and Gas | Kitchen - Hot water system in garden bed has water gushing out | Plumbing & Drainage | HWS/Units Electric & Gas | 883.06 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-21 12:55 | 2022-02-28 17:00 | 2022-02-22 17:00 | 2022-02-28 17:00 | 2022-02-22 18:30 |  |  | replaced 50L hwu
MSA-DTWD | WA5186567 | 3 | Falcetta Plumbing and Gas | 6F Painting and Decorating - Ground - Wash room - Tap handle missing from chilled water unit | Plumbing & Drainage | Materials | 241.98 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-22 08:38 | 2022-03-01 17:00 | 2022-03-01 10:00 | 2022-03-01 17:00 | 2022-03-01 11:30 |  |  | replaced bottle filler
MSA-DFES | WA5187191 | 2 | Protek 24/7 Building & Maintenance | Heritage Shed - Ground - Sliding Shed Door - see details below | Building | General Building | 272.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-22 11:54 | 2022-02-25 17:00 | 2022-02-24 09:45 | 2022-02-25 17:00 | 2022-02-24 11:15 |  |  | Repair sliding shed door
MSA-DTWD | WA5187867 | 2 | AWB Co. | Faulty Power points | Electrical | General Electrical | 219.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-22 15:35 | 2022-02-25 17:00 | 2022-02-23 14:00 | 2022-02-25 17:00 | 2022-02-23 15:30 |  |  | Attended site signed in completed jsa. Spoke to john and showed me where the fault was. investigated and due to two faulty GPO’s there was no power coming out of them. Replaced with new double gpo’s, tested and working fine now.*** job completed***
MSA-DTWD | WA5188765 | 3 | AWB Co. | light tubes are faulty | Electrical | Lighting, Internal | 264.78 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-23 11:25 | 2022-03-02 17:00 | 2022-02-28 07:00 | 2022-03-02 17:00 | 2022-02-28 08:30 |  |  | Attended site , signed in , completed jsa, spoke to fm about job, went up to level 3 and located store rooms with lights out, replaced tubes and starters, tested lights and all working as intended , cleaned up , packed up, disposed of tubes in allocated boxes locate$ in level 1 store room , completed paperwork , signed out, Job completed
MSA-DTWD | WA5190030 | 2 | SENTINEL LOCK SERVICE PTY LTD | Lock not working - Keys not unlocking door | Security | Locksmith | 859.45 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-24 10:07 | 2022-03-01 17:00 | 2022-03-01 13:00 | 2022-03-01 17:00 | 2022-03-01 14:30 |  |  | E block - ET04A Lock not working.Lock replaced.
MSA-DTWD | WA5190159 | 0 | Equans Mechanical Services Australia | BMS for rooms AT248 250 & 253 - not working | Air Conditioning | Room Air Conditioners | 162.21 | Fail | Fail | 0 | 0 | 1.5 | 2022-02-24 11:27 | 2022-02-24 13:27 | 2022-02-24 14:00 | 2022-02-24 15:27 | 2022-02-24 15:30 |  |  | Attened P0 call out. Grained access to site and spoke with staff. Shown to main mssb in lower level plant room. On inspection evap cooler enable switches Auto/Off/Manual were in the off position preventing signal to local room controllers. Moved back to auto position and tested EC units. Operation returned. Note all eaf switches were I. The manual position. These have all been placed back into auto. On speaking with stores staff member Betty had placed switches into the off position earlier this morning and forgotten to put them back into auto. Site have been advised to leave all switches in the auto position as BMS program will manage equipment operation. Work area left tidy. EC units operational.
MSA-DTWD | WA5190294 | 2 | Techworks Electrical | north west corner has a wall mounted loud speaker come off its brackets | Electrical | General Electrical | 189.15 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-24 12:24 | 2022-03-01 17:00 | 2022-02-25 07:00 | 2022-03-01 17:00 | 2022-02-25 08:30 |  |  | Re assembled and re secured speaking into existing mount on wall
MSA-DTAG | WA5190830 | 2 | Bullant Security Pty Ltd | Level 3 - Staff Toilet outside meeting room 3.4 - see notes below | Security | Locksmith | 281.36 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-24 15:03 | 2022-03-01 17:00 | 2022-03-01 08:30 | 2022-03-01 17:00 | 2022-03-01 10:00 |  |  | Attended site to replace faulty electric lock that was supplied by customer. Re-coded the lock to work previous code 115599. Serviced the lock and adjusted the strike.Date on site: 01/03/2022Time on site: 08:30am - 10:00am
MSA-DTWD | WA5191573 | 3 | Falcetta Plumbing and Gas | Level 3 - Staff toilet - Cistern overflowing | Plumbing & Drainage | Toilets/Cisterns | 236.98 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-25 07:30 | 2022-03-03 17:00 | 2022-03-03 13:00 | 2022-03-03 17:00 | 2022-03-03 14:30 |  |  | repaired flush pipe in duct and rear of pan
MSA-DTWD | WA5193655 | 3 | AWB Co. | C block carpark Sth - near Eddie Barron Dve - see details below | Building | General Building | 168.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-25 12:52 | 2022-03-04 17:00 | 2022-03-01 07:00 | 2022-03-04 17:00 | 2022-03-01 08:30 |  |  | Re-installed muster point sign
MSA-DTWD | WA5193690 | 2 | Techworks Electrical | D-Block room D240 and A west G/ Floor male toilets has a flickering lights | Electrical | General Electrical | 276 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-25 13:04 | 2022-03-02 17:00 | 2022-02-25 13:30 | 2022-03-02 17:00 | 2022-02-25 15:00 |  |  | Rectified flashing light in D240 and installed new led batten in Ablock male toilet
MSA-DTWD | WA5193929 | 3 | AWB Co. | Grinding bay 1 sensor light no coming on | Electrical | General Electrical | 375.64 | Pass | Pass | -1 | -1 | 1.5 | 2022-02-25 16:16 | 2022-03-04 17:00 | 2022-02-28 11:30 | 2022-03-04 17:00 | 2022-02-28 13:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty light fitting in the outside welding bay. Took light fittin apart and tested for voltage. 240v was present at light fitting. Discovered that electronic ballast was faulty and not the sensor. Went to wholesaler to pick up parts. Returned to site. Turned off breaker feeding light fitting and out lockout on it. Took down old fitting and replaced with new LED WP batten. Put fitting together. Re energised circuit and tested. Light fitting is working as intended. Packed and cleaned up. Took pictures before and after. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5193930 | 1 | Falcetta Plumbing and Gas | Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 166.98 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-25 16:20 | 2022-02-28 17:00 | 2022-02-28 14:00 | 2022-02-28 17:00 | 2022-02-28 15:30 |  |  | unblocked toilet pan
MSA-DCA | WA5193981 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Building has lights in offices but no lights working in the gallery. | Electrical | Lighting, Internal | 306.12 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-26 07:16 | 2022-02-26 09:16 | 2022-02-26 07:30 | 2022-02-26 11:16 | 2022-02-26 09:00 |  |  | Attended site and signed in, investigated lighting fault in lighting control room. Found the lighting control computer had shut down and was not restarting. Unplugged computer from power and fully rebooted computer. Logged into computer and turn all lights on. All working correctly. Informed staff of job completion.
MSA-DTWD | WA5195103 | 2 | AWB Co. | 9F3 - staff room - multiple lights are out - Lights are not accessible with my step ladder. | Electrical | Lighting, Internal | 302.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-02-28 10:44 | 2022-03-03 17:00 | 2022-02-28 11:30 | 2022-03-03 17:00 | 2022-02-28 13:00 |  |  | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Located room. Replaced various tubes which were out. Packed up. Notified fm of works completed. **job complete**
MSA-DTWD | WA5195593 | 3 | Equans Mechanical Services Australia | Room E324 - No airflow - VAV 100% open | Air Conditioning | Room Air Conditioners | 162.21 | Fail | Fail | 0 | 0 | 1.5 | 2022-02-28 13:15 | 2022-03-08 17:00 | 2022-03-11 10:30 | 2022-03-08 17:00 | 2022-03-11 12:00 |  |  | Attened site gained access located equipment and carried out inspection of VAV. BMS showing VAV SE-E3-06 at 100% open. Checked vav secure on damper drive shaft. Manual opened and colded vav with over ride button. Reset power to vav and equipment returned to fully closed position. Site will need to get there BMS company to investigate further. This has been confirmed with David Gaff. Work area left tidy. VAV manually left at 100% open position to allow air flow to class room. BMS tech required
MSA-DFES | WA5199827 | 3 | AWB Co. | Engine Room – entry to tunic room - Timber pelmet above sliding door is broken - further notes below | Building | Doors | 176.91 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-01 12:15 | 2022-03-09 17:00 | 2022-03-01 14:00 | 2022-03-09 17:00 | 2022-03-01 15:30 |  |  | attended site, supplied and installed new door stop
MSA-DTWD | WA5200202 | 3 | Precise Air Group | No air flow in this room either (apart from us opening the windows) | Air Conditioning | Room Air Conditioners | 188.385 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-01 15:43 | 2022-03-09 17:00 | 2022-03-02 09:30 | 2022-03-09 17:00 | 2022-03-02 11:00 |  |  | Attended site and completed pre start paperwork and signed in. Acessed bms and inspected c block operation. Acessed room and found air flow from the 2 outlets. Was unable to get chiller to engage as no demand for cooling. C block chiller is awating repairs and b block I believe is running on one system. Once chillers are running we can make sure room is getting the appropriate cooling. Room dose have air flow.
MSA-DCA | WA5201291 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Main - Basement - Sever room - HVAC system is making loud bussing noise - please inspect | Air Conditioning | Room Air Conditioners | 188.375 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-02 12:50 | 2022-03-03 17:00 | 2022-03-02 13:00 | 2022-03-03 17:00 | 2022-03-02 14:30 |  |  | Attended site, signed and accessed the server room. Investigated CRC.01.05 and no alarms/ faults visible in the log history. System is working correctly and further investigation into the noise will be looked at on the next maintenance visit.
MSA-MRWA | WA5201402 | 3 | EQUANS Mechanical Services (WA) Pty Limited | plant room - boiler 2 - F5 fault | Mechanical Services | Boilers | 1503.35 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-02 14:36 | 2022-03-10 17:00 | 2022-03-08 13:30 | 2022-03-10 17:00 | 2022-03-08 15:00 |  |  | Travelled to site and signed in. Assisted subcontractor Boilertronics with the investigation into the F5 fault on the Meridian boiler number 2.
MSA-DTWD | WA5203010 | 2 | AWB Co. | Electric vehicle used to carry goods around campus has lost power. | Electrical | General Electrical | 350.75 | Fail | Fail | 1 | 1 | 1.5 | 2022-03-03 09:57 | 2022-03-09 17:00 | 2022-03-15 12:30 | 2022-03-09 17:00 | 2022-03-15 14:00 |  | WCAPPR | attended site and completed works
MSA-DTWD | WA5204224 | 1 | AWB Co. | Damaged light switch that needs repairing | Electrical | General Electrical | 267.84 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-04 08:57 | 2022-03-08 17:00 | 2022-03-08 07:00 | 2022-03-08 17:00 | 2022-03-08 08:30 |  |  | Attended site and signed in. Completed JSA. Located faulty light switch. Called cleaner to open up building so we could access board to isolate. Took switch off wall and found switch mech in wall box. Condition of light switch and switch mech were both good. Popped mech back into position. Working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-MRWA | WA5207251 | 2 | AWB Co. | admin North Easter corner - damaged ethernet port - see notes | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-08 11:51 | 2022-03-11 17:00 | 2022-03-09 09:00 | 2022-03-11 17:00 | 2022-03-09 10:30 |  |  | Attended site and signed in. Completed JSA. Located data points 51 and 52. Found to be pushed through the wall and other not working. Removed wall plate from wall and re attached both mechs back into wall plate. Resecured to wall. Tested Ethernet cables on site and found 1 to be broken and not able to be used. Used other leads and patched in computer from wall. Tested all okay. Site advised the other port doesn’t work and they want to use it for a computer. Wen to server room and found port 52. Found to be not is use. Ran patch cable for hub to port. Tested at wall plate in office and all is okay and ready to be used for networking. Notified lady in office. Signed out. Job complete
MSA-DCA | WA5207675 | 2 | Techworks Plumbing | Hackett Hall - Mezzanine Level- Male Toilets - Unblock hand basin wastes | Plumbing & Drainage | Water | 275.68 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-08 15:33 | 2022-03-11 17:00 | 2022-03-09 08:00 | 2022-03-11 17:00 | 2022-03-09 09:30 |  |  | Travel to site, sign in and access bathroom, located basin, cleaned out bottle trap and reassembled, tested, cleaned up work area and completed paperwork
MSA-DTAG | WA5208567 | 1 | Seme Solutions Pty Ltd | Alarm system not self activating at 9pm and alarms going off throughout the day. | Security | Monitoring | 195 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-09 09:25 | 2022-03-10 17:00 | 2022-03-09 11:00 | 2022-03-10 17:00 | 2022-03-09 12:30 |  |  | Check system for configuration issues, all seems ok. Contacted Sapio Monitoring to change auto alarm time to 2200 hrs.
MSA-DTWD | WA5208693 | 2 | M Construction (WA) | Block S - Step pavers - loose step pavers from S-block to class rooms | Paving & Roadworks | Paving | 187.95 | Fail | Fail | 0 | 0 | 1.5 | 2022-03-09 10:16 | 2022-03-14 17:00 | 2022-03-15 13:00 | 2022-03-14 17:00 | 2022-03-15 14:30 |  |  | Attend and inspect loose pavers, clean and install pavers.
MSA-DFES | WA5209094 | 3 | Protek 24/7 Building & Maintenance | Ground - Gym - see details below | Building | General Building | 295.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-09 13:24 | 2022-03-16 17:00 | 2022-03-14 11:30 | 2022-03-16 17:00 | 2022-03-14 13:00 |  |  | Replace rollers on sliding door
MSA-DTWD | WA5216239 | 1 | Precise Air Group | Kendrew- E-Block E74 Barista room aircon ( E - Vap ) not working | Air Conditioning | Room Air Conditioners | 340.14 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-11 08:52 | 2022-03-14 17:00 | 2022-03-11 12:00 | 2022-03-14 17:00 | 2022-03-11 13:30 |  |  | Attended site and completed pre start paperwork and signed in. Completed working at heights permit and acessed unit on roof. Found water flow into unit to be poor and no water flowing over pads. Removed solenoid and dismantled. Found rubber bladder to have got stuck blocking flow. Repaired and test ran system. Monitored. Left system operating in good working order. No further works required. Left all ok
MSA-DTWD | WA5216254 | 1 | Techworks Electrical | Kendrew- A- Block room A237 power point on skirting board has come adrift | Electrical | General Electrical | 177.57 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-11 08:56 | 2022-03-14 17:00 | 2022-03-11 13:00 | 2022-03-14 17:00 | 2022-03-11 14:30 |  |  | Re fixed data point back to skirting in A block.
MSA-DTWD | WA5216834 | 3 | AWB Co. | room C50 - AC technician reported 393volts supply to AC plant room that should be reading 415volts | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-11 13:17 | 2022-03-18 17:00 | 2022-03-15 07:45 | 2022-03-18 17:00 | 2022-03-15 09:15 |  |  | Attended site and signed in, completed jsa, spoke to fm about job,located plant room, called precise air about job, technician said he was getting 390v on load side of the contactor, tested load side of contactor and found I was getting 403v which voltage at all blocks on campus , closed up all boards, completed paperwork,packed up, Job completed
MSA-DTWD | WA5217076 | 2 | Equans Mechanical Services Australia | Student common room - Evap. on roof leaking water - see notes | Air Conditioning | Evaporative Coolers | 366.81 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-11 16:06 | 2022-03-16 17:00 | 2022-03-14 13:30 | 2022-03-16 17:00 | 2022-03-14 15:00 |  |  | Found water hose to unit had failed and split. Replaced hose and all ok. Also found evaporative cooler for canteen near repaired unit has no water on pads but pump running. Found failed water solenoid transformer. Replaced transformer from van stock. Checked operation and all ok. Client approved with second repair on same job.
MSA-DTWD | WA5226417 | 2 | AWB Co. | Double GPO remaining on when switched off needs rewiring | Electrical | General Electrical | 193.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-14 08:49 | 2022-03-17 17:00 | 2022-03-16 07:00 | 2022-03-17 17:00 | 2022-03-16 08:30 |  |  | Attended site and signed in. Completed JSA. Located T102 and got access with swipe card. Found double gpo to have a faulty switch on 1 side. Supply and replace with new double gpo. Found server gpo to be off. Reset and tested the circuit to be okay and ran server from the gpo it’s intended to run from. Showed facilities one site. Signed out. Job complete
MSA-DTWD | WA5226889 | 2 | AHS Services WA Pty Ltd (Anchor) | Kendrew- C-Block 2nd floor female toilets two broken toilet seats Cubicles 2 and 4 | Plumbing & Drainage | Toilets/Cisterns | 443.925 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-14 14:37 | 2022-03-17 17:00 | 2022-03-15 08:15 | 2022-03-17 17:00 | 2022-03-15 09:45 |  |  | Completed
MSA-DCA | WA5230713 | 0 | Techworks Electrical | Both street bollards not operational | Electrical | General Electrical | 196.23 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-15 07:05 | 2022-03-15 09:05 | 2022-03-15 07:30 | 2022-03-15 11:05 | 2022-03-15 09:00 |  |  | Came to site and began investigating both sets of bollards, reset both systems and put through a series of dropping them and letting them rise up, both sets are working as normal.
MSA-DTWD | WA5231324 | 2 | AHS Services WA Pty Ltd (Anchor) | A-Block West male toilets , two leaking basin taps | Plumbing & Drainage | Water | 453.655 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-15 10:17 | 2022-03-18 17:00 | 2022-03-18 07:00 | 2022-03-18 17:00 | 2022-03-18 08:30 |  |  | Completed
MSA-DFES | WA5252892 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Exterior Administration Bld - Ground - Exterior Conference Room - see details | Plumbing & Drainage | Water | 183.85 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-17 08:52 | 2022-03-24 17:00 | 2022-03-21 13:00 | 2022-03-24 17:00 | 2022-03-21 14:30 |  |  | HAD DIG up a valve and workout which part it isolated I, it was the main kitchen.
MSA-DFES | WA5286357 | 2 | Australian HVAC Services Pty. Ltd. | Ground - Station Officer Twin Dorm - Aircon unit in dorm leaking water, most likely blocked drain. | Air Conditioning | Room Air Conditioners | 229.26 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-21 15:08 | 2022-03-24 17:00 | 2022-03-22 14:00 | 2022-03-24 17:00 | 2022-03-22 15:30 |  |  | Arrived on-site, signed in & spoke with on-site representative who directed me to leaking A/C unit. Isolated power & began dismantling evaporator unit fascia panelling, disconnected drain and drained excess water into a bucket, found drain to be on incorrect angle as indoor unit had been knocked off holding bracket causing water to flood back, refitted evaporator to bracket, used nitrogen to blow out any blockages in drain, reassembled unit and poured 5 litres of warm water through drain work, found there to no longer be any leaks on unit, informed client of findings/repairs & left site.
MSA-DTWD | WA5287088 | 2 | AWB Co. | 326 - Fault in UX exposure unit | Electrical | General Electrical | 267.84 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-22 10:07 | 2022-03-25 17:00 | 2022-03-25 10:15 | 2022-03-25 17:00 | 2022-03-25 11:45 |  |  | Attended site and signed in, completed jsa,called fm and discussed job and issue with u.v machine, was told to speak to technician, found technician and spoke to him about issue, he said a student had experienced a very mild shock (he suspected it was from static) , technician had tagged out because he wanted to be sure, pulled off cover and inspected internal wiring, everything looked in good condition, tested earth continuity and it was a pass, I.r tested machine and it passed, turn machine on and tested for voltage on the frame at multiple spots, got 0v on all metal parts, found no faults with the machine , spoke to fm and explained this , packed up, cleaned up, completed paperwork , signed out Job completed
MSA-DTWD | WA5288883 | 1 | AHS Services WA Pty Ltd (Anchor) | A block - Level 2 - A 254 Male toilet - Urinal blocked | Plumbing & Drainage | Water | 219.135 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-23 15:12 | 2022-03-24 17:00 | 2022-03-24 08:00 | 2022-03-24 17:00 | 2022-03-24 09:30 |  |  | Urinal was blocked on level 2 A block, unblocked the urinal and used a bottle of mo flo
MSA-DTWD | WA5289463 | 2 | GRAFFITI FORCE PTY LTD | D-Block - 1st Floor Library Male toilets has Graffiti on cubicle wall and toilet seat | Cleaning | Graffiti | 244.92 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-24 09:40 | 2022-03-29 17:00 | 2022-03-29 11:05 | 2022-03-29 17:00 | 2022-03-29 12:35 |  |  | REMOVAL OF GRAFFITI FROM LIBRARY MALE TOILETS
MSA-DTWD | WA5290427 | 1 | Swan Pest Control | E-Block - External of building - ant problem around building | Pest Control | General Pest | 442.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-25 08:59 | 2022-03-28 17:00 | 2022-03-28 10:45 | 2022-03-28 17:00 | 2022-03-28 12:15 |  |  | Sprayed external perimeter, gardens and paved areas and sprayed internal kitchen and storerooms with Firponil
MSA-DCA | WA5290865 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Male toilet - Minimal amount of water constantly running from tap | Plumbing & Drainage | Water | 516.1375 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-25 12:26 | 2022-03-30 17:00 | 2022-03-28 10:19 | 2022-03-30 17:00 | 2022-03-28 11:49 |  |  | Replaced push tap that was badly corroded. In male public first floor male RHS basin
MSA-DTAG | WA5290873 | 1 | Schindler Lifts Australia | Level 1 - Lift 1 - is broken - faulty error message | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5 | 2022-03-25 12:33 | 2022-03-28 17:00 | 2022-03-25 13:00 | 2022-03-28 17:00 | 2022-03-25 14:30 |  |  | to be closed out at $0 cost
MSA-DCA | WA5291054 | 2 | Techworks Electrical | Main Building - Basement 1- Stairwell 1 landing (outside pool plant room) - see details below | Electrical | General Electrical | 374.94 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-25 14:15 | 2022-03-30 17:00 | 2022-03-29 10:30 | 2022-03-30 17:00 | 2022-03-29 12:00 |  |  | Replaced light with an LED oyster in stairwell next to pool plant room. All working well.
MSA-DTAG | WA5293226 | 2 | AWB Co. | Ground Floor - Caffissimo - power not working behind counter of cafe | Electrical | General Electrical | 267.84 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-28 09:49 | 2022-03-31 17:00 | 2022-03-28 11:30 | 2022-03-31 17:00 | 2022-03-28 13:00 |  |  | Attended site and signed in , completed jsa, called pfm and discussed job, located cafe and spoke with workers there about the electrical issue, cafe power was working on Friday afternoon and had tripped sometime over the weekend (possibly cleaners appliances caused power to trip) , identified circuit and went to switchboard to reset, reset rcd and went back to cafe to turn everything on , everything working as intended , located gpo on same circuit to the right of the male toilets , completed paperwork, packed up, signed out , Job completed
MSA-DTWD | WA5294116 | 2 | Falcetta Plumbing and Gas | Wash Area - Auto stop wash trough taps sticking/staying on | Plumbing & Drainage | Water | 166.98 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-28 13:00 | 2022-03-31 17:00 | 2022-03-30 15:30 | 2022-03-31 17:00 | 2022-03-30 17:00 |  |  | Replaced faulty tap
MSA-DTWD | WA5294134 | 2 | AWB Co. | External Staff car park lights - Staff car park northwest lights remaining on during daylight | Electrical | Lighting, External | 361.77 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-28 13:15 | 2022-03-31 17:00 | 2022-03-30 07:00 | 2022-03-31 17:00 | 2022-03-30 08:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located board where lights are fed from. Removed escutcheons from board. Tested all control gear. Found to be contactor was seized and wasn’t operating correctly. Removed and replaced with new contactor. Tested for correct operation. All working correctly. Placed everything back to original state. **job complete**
MSA-DTAG | WA5294304 | 1 | Sapio Pty Ltd | Level 3 - camera is not working (C323 - L3 Patch room) | Security | CCTV Surveillance | 190 | Fail | Fail | 0 | 0 | 1.5 | 2022-03-28 16:15 | 2022-03-29 17:00 | 2022-03-30 09:30 | 2022-03-29 17:00 | 2022-03-30 11:00 |  |  | Reset camera and checked on milestone
MSA-DTWD | WA5295479 | 2 | AHS Services WA Pty Ltd (Anchor) | D-Block - 1st Floor Library Male toilets replace broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 665.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-29 14:00 | 2022-04-01 17:00 | 2022-03-30 11:45 | 2022-04-01 17:00 | 2022-03-30 13:15 |  |  | Completed
MSA-DTAG | WA5296347 | 2 | AHS Services WA Pty Ltd (Anchor) | Perth Magistrates Court - Level 4 - Male and Female Toilets - toilets blocked | Plumbing & Drainage | Toilets/Cisterns | 177.915 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-30 11:33 | 2022-04-04 17:00 | 2022-03-31 11:30 | 2022-04-04 17:00 | 2022-03-31 13:00 |  |  | Used plunger and rod's to clear local paper blockage flushed through all good
MSA-DTWD | WA5296500 | 2 | Lane's Plumbing | BLD 822 - Flat D - Bathroom - Leaking vanity | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 1.5 | 2022-03-30 12:36 | 2022-04-04 17:00 | 2022-04-01 10:00 | 2022-04-04 17:00 | 2022-04-01 11:30 |  |  | job completed - REPAIR LEAKING VANITY PIPES BLD82 FLAT D
MSA-DTWD | WA5296675 | 1 | Critical Fire Protection & Training | BLD 822 - Fire panel is faulty | Fire Protection Services | Fire Protection - Monitor System | 258.88 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-30 13:05 | 2022-03-31 17:00 | 2022-03-31 10:50 | 2022-03-31 17:00 | 2022-03-31 12:20 |  |  | .
MSA-DTWD | WA5296679 | 1 | Critical Fire Protection & Training | BLD 820 - Fire panel is faulty | Fire Protection Services | Fire Protection - Monitor System | 258.88 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-30 13:31 | 2022-03-31 17:00 | 2022-03-31 10:50 | 2022-03-31 17:00 | 2022-03-31 12:20 |  |  | .
MSA-DTWD | WA5296680 | 1 | Critical Fire Protection & Training | BLD 821 - Fire panel is faulty | Fire Protection Services | Fire Protection - Monitor System | 258.88 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-30 13:31 | 2022-03-31 17:00 | 2022-03-31 10:50 | 2022-03-31 17:00 | 2022-03-31 12:20 |  |  | .
MSA-DTWD | WA5296741 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block E-Vap RPZ valve leaking on roof | Plumbing & Drainage | Drainage | 414.735 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-30 15:18 | 2022-04-04 17:00 | 2022-03-31 11:15 | 2022-04-04 17:00 | 2022-03-31 12:45 |  |  | Completed
MSA-DTAG | WA5297572 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Staff Female toilets - toilet bowl not draining | Plumbing & Drainage | Water | 154.3675 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-31 11:24 | 2022-04-01 17:00 | 2022-03-31 13:30 | 2022-04-01 17:00 | 2022-03-31 15:00 |  |  | Investigated used rod's to clear blockage from cell area flushed through all flowing well
MSA-DTAG | WA5297658 | 3 | Midolo Building Services | Level 1 - Female Staff Toilets - Air freshener has fallen off the wall | Building | General Building | 188.62 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-31 11:52 | 2022-04-07 17:00 | 2022-04-01 12:00 | 2022-04-07 17:00 | 2022-04-01 13:30 |  |  | fixed air freshener to wall
MSA-DCA | WA5297914 | 2 | Protek 24/7 Building & Maintenance | Please see details below: | Building | General Building | 272.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-03-31 14:23 | 2022-04-05 17:00 | 2022-04-05 07:30 | 2022-04-05 17:00 | 2022-04-05 09:00 |  |  | Repair Internal door
MSA-DTWD | WA5298186 | 3 | Falcetta Plumbing and Gas | Library staff kitchen - Water leak from tap spindle that supplies dishwasher | Plumbing & Drainage | Water | 196.98 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-31 15:52 | 2022-04-07 17:00 | 2022-04-01 16:30 | 2022-04-07 17:00 | 2022-04-01 18:00 |  |  | replaced supply tap for dishwasher
MSA-DTWD | WA5298219 | 2 | AWB Co. | All lights in the room are not working. Breakers in distribution board are on. | Electrical | Lighting, Internal | 180.54 | Pass | Pass | -1 | -1 | 1.5 | 2022-03-31 16:45 | 2022-04-05 17:00 | 2022-04-01 09:45 | 2022-04-05 17:00 | 2022-04-01 11:15 |  |  | Attended site and signed in. Completed JSA. Located D block and met with facilities to locate what room wasn’t working. Found to be a store room behind the roller door. Found no power to switch. Checked out area and found all new electrical works been done through workshop. Looked into switchboard and found circuits tagged redundant. Found R1 isolated and safe to reinstate. R1 feeds the store room. All lights in store working again. Advised site that this was parts of the works don’t by other contractor. Signed out. Job complete
MSA-DTWD | WA5303477 | 3 | Equans Mechanical Services Australia | Level 8 - Plant Room - Return air fan not working (blown fuse) | Air Conditioning | Room Air Conditioners | 166.96 | Pass | Pass | -1 | -1 | 1.5 | 2022-04-04 10:24 | 2022-04-11 17:00 | 2022-04-05 12:00 | 2022-04-11 17:00 | 2022-04-05 13:30 |  |  | ATTENDED SITE, SIGNED AND ACCESSED BUILDING B1 MECHANICAL PLANTROOM. LOCATED MECHANICAL SWITCH BOARD AND FOUND THE RETURN AIR FAN HAD TRIPPED THE BREAKER AND FAULT LIGHT PRESENT.ISOLATED SWITCHBOARD, REMOVED PANELS AND CHECKED THE FUSE. FOUND THE FUSE HAD BLOWN, REPLACED THE FUSE, TESTED AND RAN THE FAN. CHECKED THE VOLTAGES AND RECORDED AMP DRAWS - ALL WITH IN RANGE. WILL MONITOR AND CHECK FAN DURING THE ROUTINE MAINTENANCE
MSA-DTWD | WA5303538 | 3 | Equans Mechanical Services Australia | Level 8 - Plant room - AHU supply fan not working (blown fuse) | Air Conditioning | Room Air Conditioners | 125.58 | Pass | Pass | -1 | -1 | 1.5 | 2022-04-04 10:51 | 2022-04-11 17:00 | 2022-04-05 13:30 | 2022-04-11 17:00 | 2022-04-05 15:00 |  |  | ATTENDED SITE, SIGNED AND ACCESSED BUILDING B1 MECHANICAL PLANTROOM.LOCATED MECHANICAL SWITCH BOARD AND FOUND THE SUPPLY AIR FAN HAD TRIPPED THEBREAKER AND FAULT LIGHT PRESENT.ISOLATED SWITCHBOARD, REMOVED PANELS AND CHECKED THE FUSE. FOUND THE FUSE HADBLOWN, REPLACED THE FUSE, TESTED AND RAN THE FAN. CHECKED THE VOLTAGES ANDRECORDED AMP DRAWS - ALL WITH IN RANGE. WILL MONITOR AND CHECK FAN DURING THEROUTINE MAINTENANCE.
MSA-DFES | WA5303668 | 2 | Complete Pest Management Services | Whole Station - Ant infestation throughout the Station | Pest Control | General Pest | 337.16 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-04 11:48 | 2022-04-07 17:00 | 2022-04-07 08:00 | 2022-04-07 17:00 | 2022-04-07 09:30 |  |  | External perimeter spray of the whole fire station.Treated curb line, fencelines, garden beds and external of garden shed.Injected chemical directly into multiple ant nests front and back of fire station for ant control.
MSA-DCA | WA5303732 | 2 | Techworks Plumbing | Geology Building - Ground Level - Male Toilet - see notes below | Plumbing & Drainage | Toilets/Cisterns | 495.65 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-04 12:17 | 2022-04-07 17:00 | 2022-04-05 07:00 | 2022-04-07 17:00 | 2022-04-05 08:30 |  |  | Changed button assemblyAttended site and signed in at security office, went to geology building and found no running toilets so found one of the lady’s that worked at the museum and she informed us that the toilet that was running had already been fixed but the right hand side toilet would not full flush.We inspected it and pulled it apart to find that the button kept getting stuck down and that’s what kept it from not flushing. We went to security and got a new button assembly from the stock we have at the museum and just changed it over and the toilet flushes fine now. Cleaned up and got a signature slip then completed paperwork .
MSA-DCA | WA5303919 | 2 | Protek 24/7 Building & Maintenance | Ground – external - James Street Amphitheatre - see notes below | Carpentry | Timber (all types) | 289.66 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-04 13:09 | 2022-04-07 17:00 | 2022-04-05 10:00 | 2022-04-07 17:00 | 2022-04-05 11:30 |  |  | Repair 2 planter boxes
MSA-DTWD | WA5304116 | 2 | AWB Co. | Block 7 - Ground - Male toilet - Broken light | Electrical | General Electrical | 371.43 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-04 14:53 | 2022-04-07 17:00 | 2022-04-05 10:00 | 2022-04-07 17:00 | 2022-04-05 11:30 |  |  | attended site signed in completed jsa. Found faulty light as reported by site FM. Located toilet block. Replaced with new 4ft led fluro. Tested ok*** job completed ***
MSA-DTWD | WA5304138 | 1 | Complete Pest Management Services | Block 1 - Ground - 1G1 and 1G19 - Infestation of little flying bugs | Pest Control | General Pest | 234.91 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-04 15:01 | 2022-04-05 17:00 | 2022-04-05 10:15 | 2022-04-05 17:00 | 2022-04-05 11:45 |  |  | Longicorn Beetles founds throughout soil beds and pot plants.Recommend surface spraying of soil beds where beetles found in leaf matter.Recommend ULV misting of vegetation to kill remaining mosquitoes.Recommend ULV surface spraying of building to repel beetles and mosquitoes.
MSA-DTWD | WA5305815 | 2 | AHS Services WA Pty Ltd (Anchor) | A105 - toilet is in the last cubicle - Cistern leaking | Plumbing & Drainage | Toilets/Cisterns | 163.785 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-06 07:51 | 2022-04-08 17:00 | 2022-04-06 14:00 | 2022-04-08 17:00 | 2022-04-06 15:30 |  |  | Replaced leaking pan cone to last female toilet A105
MSA-DTAG | WA5306219 | 1 | Complete Pest Management Services | Court Front and trees - Aggressive Bees need to be removed from main entrance, emergency exit court | Pest Control | General Pest | 289.46 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-06 11:03 | 2022-04-07 17:00 | 2022-04-07 07:00 | 2022-04-07 17:00 | 2022-04-07 08:30 |  |  | Removed 2 feral bee hives's from tree out front of court house
MSA-DTWD | WA5307150 | 2 | Equans Mechanical Services Australia | Compressor/Dryer room - Receiver dryer not working | Equipment | Compressors, Generators | 162.21 | Pass | Pass | -1 | -1 | 1.5 | 2022-04-07 10:35 | 2022-04-12 17:00 | 2022-04-08 14:10 | 2022-04-12 17:00 | 2022-04-08 15:40 |  |  | MONITORED UNIT AND APPEARS OK
MSA-DTAG | WA5308127 | 1 | Sapio Pty Ltd | L3-L4,L6-L9 all in-session buttons are not working. | Security | Security Management System | 190 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-08 09:03 | 2022-04-11 17:00 | 2022-04-08 09:30 | 2022-04-11 17:00 | 2022-04-08 11:00 |  |  | Work performed by Ken Moore (08/04/2022)Attended site. Reset macro controllers, tested, OK.
MSA-DCA | WA5308173 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Cooling tower - Top floor - water leaking | Air Conditioning | Cooling Tower | 345.35 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-08 09:29 | 2022-04-08 11:29 | 2022-04-08 10:00 | 2022-04-08 13:29 | 2022-04-08 11:30 |  |  | Investigation found no fault on site, site technician will continue to monitor.
MSA-DCA | WA5308660 | 2 | Techworks Electrical | Museum Plaza – Beaufort St end - see details below | Electrical | General Electrical | 214.55 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-08 14:23 | 2022-04-13 17:00 | 2022-04-12 09:00 | 2022-04-13 17:00 | 2022-04-12 10:30 |  |  | The covers for the manual bollards have been heavily bent back, most likely from a car driving over them at some stage when the bollards were taken out and the covers left back and not closed up, there are fractures in the metal from being bent back so much. I am unable to bend these back to the correct angle at all. These are not a serviceable item and cannot be replaced so the bollard that’s missing the cover is unable to have a replacement put on, we would need to change the whole bollard sleeve in the ground too. They’re bent so far back the other way that they now sit flush with the ground, this is fine for cars to drive over as they can’t get bent back anymore than they’re are now. To fix these properly we will need to replace all 3 bollard sleeves in the ground.
MSA-DCA | WA5311692 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Level 5 - Plant Room - Cooling tower - faulty again this morning - | Air Conditioning | Room Air Conditioners | 319.195 | Fail | Fail | 0 | 0 | 1.5 | 2022-04-11 08:33 | 2022-04-11 10:33 | 2022-04-11 11:30 | 2022-04-11 12:33 | 2022-04-11 13:00 |  |  | Attended site, signed in and accessed the cooling tower compound Checked the cooling tower 4 over flowing, there is butterfly valves on the return lines which need to be set up as throttling valves to allow even water distribution to the headers. I have set them in the correct position. Will put some information tags on these valves to notify contractors for future works.
MSA-DTWD | WA5318034 | 3 | AWB Co. | D Block -Replace metal cover that is loose to stairs | Building | General Building | 308.1 | Pass | Pass | -1 | -1 | 1.5 | 2022-04-12 07:43 | 2022-04-20 17:00 | 2022-04-13 08:00 | 2022-04-20 17:00 | 2022-04-13 09:30 |  |  | Metal plate adhesive scraped back, new adhesive purchased, plate re glued in position
MSA-DTWD | WA5319387 | 1 | BJ SYSTEMS | Ground -Gallagher security system - Card reader beeping and auto door not opening to swipe card | Security | Keys & Access | 207.5 | Fail | Fail | 0 | 0 | 1.5 | 2022-04-12 15:27 | 2022-04-13 17:00 | 2022-04-14 14:00 | 2022-04-13 17:00 | 2022-04-14 15:30 |  |  | T block added access east auto door to access group. Reader beeping in U block classroom. Replaced magnet missing in door all tested ok
MSA-DTWD | WA5377813 | 2 | AWB Co. | Room J127 - Magnabend Machine not operating | Electrical | High Voltage | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-20 09:17 | 2022-04-26 17:00 | 2022-04-26 11:15 | 2022-04-26 17:00 | 2022-04-26 12:45 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located Magna bend machine in j block, plugged machine in and tested , machine was not operational, tested gpo for voltage and all readings were good, I.r tested machine and it passed, tried resetting trip switch a number of times with no success, cover to machine was held on with a mixture of screws and pop rivets, spoke with fm and he advised me that company that supplied the unit will be contacted , packed up, completed paperwork, signed outJob completed
MSA-DTWD | WA5377858 | 3 | AWB Co. | Room A05 - Flickering Fluoro in Facilities Office | Electrical | Lighting, Internal | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-20 09:37 | 2022-04-28 17:00 | 2022-04-26 07:00 | 2022-04-28 17:00 | 2022-04-26 08:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located lighting,isolated lighting,removed old tombstones and replaced with new, put in new starters and tubes , re energised lighting, lights now working as intended , packed up, disposed of tubes in allocated boxes, completed paperwork , signed outJob completed
MSA-DFES | WA5377987 | 1 | SONTEC WA PTY LTD | Exit gate - Yard - gate is working intermittently and faulty | Building | Security Doors | 530.25 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-20 10:41 | 2022-04-21 17:00 | 2022-04-20 13:00 | 2022-04-21 17:00 | 2022-04-20 14:30 |  |  | 20/4/22 - Dylan Parslow, Joshua ParkRewired signal from Intercom to exit gate and tested.All working.
MSA-DTWD | WA5378291 | 1 | BJ SYSTEMS | Kendrew- E-Block - alarm panel faulty, sending random alarms to ed sec | Security | Monitoring | 207.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-20 13:03 | 2022-04-21 17:00 | 2022-04-20 14:30 | 2022-04-21 17:00 | 2022-04-20 16:00 |  |  | E Block intruder alarm sending random alarms to ED Sec on ID. Removed unwanted alarms from hospitality intruder alarm zone. Tested all other alarms. Central stores doors EBG is open causing door to stay open. Staff had left, had no access to Gallagher to sort out this issue
MSA-DTWD | WA5378300 | 2 | BAKE-QUIP PTY LTD | D3 Pastry Lab - Rotel oven Element & Lever issue – Middle deck | Equipment | Catering Equipment | 300 | Pass | Pass | -1 | -1 | 1.5 | 2022-04-20 13:08 | 2022-04-26 17:00 | 2022-04-21 12:30 | 2022-04-26 17:00 | 2022-04-21 14:00 |  |  | REFER TO SERVICE REPORT.
MSA-DCA | WA5378479 | 2 | Earth & Water Pty Ltd | Broken retic - zone 13 | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | -1 | -1 | 1.5 | 2022-04-20 14:37 | 2022-04-26 17:00 | 2022-04-21 07:30 | 2022-04-26 17:00 | 2022-04-21 09:00 |  |  | -Arrived on site-Met with Kevin-Found broken retic in front of pretzel stand-Head and body both broken. Needs replaced#Return with extra tall 12" Hunter pop up-Exposed around sprinkler body-Replaced internals-Flushed-Left area clean and tidy
MSA-DFES | WA5379712 | 0 | Anvil Doors | Engine Room door 1 - faulting | Building | Doors | 575 | Fail | Fail | 0 | 0 | 1.5 | 2022-04-21 13:42 | 2022-04-21 15:42 | 2022-04-21 17:30 | 2022-04-21 17:42 | 2022-04-21 19:00 |  | WACCES | Attached a relay to the junction and set timing for 4minutes and door close after movement which will be more efficient and easier for the station employees to use.
MSA-DTWD | WA5380641 | 2 | AWB Co. | West Block - W105 - door wont close properly | Building | Doors | 168.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-22 14:28 | 2022-04-28 17:00 | 2022-04-26 08:00 | 2022-04-28 17:00 | 2022-04-26 09:30 |  |  | Ed Lankester (26/04/2022) - Work NoteArrived on site signed in and shown the job, completed a JSA. Modified the door lock latch to enable the door to closes and latched. Signed out and left site
MSA-DTWD | WA5381455 | 3 | AWB Co. | Room E628 - Faulty GPO East wall | Electrical | General Electrical | 182.34 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-26 09:10 | 2022-05-03 17:00 | 2022-05-02 08:30 | 2022-05-03 17:00 | 2022-05-02 10:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located gpos/grinders, isolated circuits, disconnected from wall, put out of service tags on cables, tested for dead, cleaned up, packed up,completed paperwork,signed out ,Job completed
MSA-DTWD | WA5382935 | 0 | Techworks Plumbing | All toilets are blocking up | Plumbing & Drainage | Toilets/Cisterns | 311.67 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-27 10:15 | 2022-04-27 12:15 | 2022-04-27 11:30 | 2022-04-27 14:15 | 2022-04-27 13:00 |  |  | Attended site signed in at office and spoke to Dennis Went to childcare centre where the lady there told me that the water was backing up and toilets were not flushingWe inspected and found all the gullets to be blocked up also We found and inspection opening outside and used drain rods to unblock the drain it looked like it was just a toilet paper build up,After we had unblocked the drain we flushed the toilets and ran the taps to make sure they would not block up again,Cleaned up and left site Completed paperwork
MSA-MRWA | WA5384100 | 1 | AWB Co. | Level 9 - lighting - lights not working (majority) - not sure fof amount | Electrical | General Electrical | 295.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-28 09:52 | 2022-04-29 17:00 | 2022-04-29 06:00 | 2022-04-29 17:00 | 2022-04-29 07:30 |  |  | Attended site and signed in. Completed JSA. Located level 9 lights. Found corridor lights not to turning on. Found power to light fittings. Supply and replace dead lamp tubes to fittings. Tested all okay. 1 light fitting isolated due to ballast faulty. Signed out. Job complete
MSA-DTWD | WA5384137 | 1 | Protek 24/7 Building & Maintenance | G200 - Plant room - Roof Leak | Building | General Building | 298.9 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-28 10:07 | 2022-04-29 17:00 | 2022-04-28 12:30 | 2022-04-29 17:00 | 2022-04-28 14:00 |  |  | Repair Roof leak
MSA-DTWD | WA5384364 | 1 | Damian Rak Electrical Pty Ltd | Faulty RCD circuit | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1.5 | 2022-04-28 12:12 | 2022-04-29 17:00 | 2022-04-28 12:30 | 2022-04-29 17:00 | 2022-04-28 14:00 |  |  | job completed -
MSA-DFES | WA5384710 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main Admin Building - Lights not working in various locations - See notes | Electrical | Lighting, Internal | 281.43 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-28 15:23 | 2022-05-05 17:00 | 2022-05-05 14:45 | 2022-05-05 17:00 | 2022-05-05 16:15 |  |  | Continued on from last job at same site at 1445. Checked all lights in DRM office and found multiple lights not working. Replaced fluros and starters in marks office x 4, kitchen x 1 and admin office x 4 and tested. Notified staff and left site at 1615
MSA-DTWD | WA5385238 | 2 | Techworks Electrical | T108 broken cable to electric bed circuit B18 | Electrical | General Electrical | 386.64 | Pass | Pass | 0 | 0 | 1.5 | 2022-04-29 08:34 | 2022-05-04 17:00 | 2022-05-03 09:30 | 2022-05-04 17:00 | 2022-05-03 11:00 |  |  | Replaced damaged lead and plug top to electric bed in T block
MSA-DTWD | WA5385569 | 2 | ECO PLUMBING AND GAS PTY LTD | U011 - Blocked drain at wash trough | Plumbing & Drainage | Drainage | 190.99 | Fail | Fail | 0 | 0 | 1.5 | 2022-04-29 10:47 | 2022-05-04 17:00 | 2022-05-05 13:00 | 2022-05-04 17:00 | 2022-05-05 14:30 |  |  | cleared blockage
MSA-DTWD | WA5389861 | 0 | AWB Co. | B130.2 - power is tripping | Electrical | General Electrical | 217.41 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-02 08:26 | 2022-05-02 10:26 | 2022-05-02 09:00 | 2022-05-02 12:26 | 2022-05-02 10:30 |  |  | Attended site and signed in. Completed JSA. Signed out keys for site. Located work area in room B310.2. Found w3 to be tripping. Began testing to find fault on circuit and found all cabling to be okay. Reset RCD and tripped again. Supply and replace faulty RCD. Reconnect and reinstate power. Tested all okay. Students began turning on PCs. No problems occurring. Signed out. Job complete
MSA-DTWD | WA5392221 | 2 | Protek 24/7 Building & Maintenance | Room ET09 - Window at high level won’t stay shut - May require roof access | Building | Windows | 300 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-03 08:38 | 2022-05-06 17:00 | 2022-05-04 06:30 | 2022-05-06 17:00 | 2022-05-04 08:00 |  |  | Repairs to window- not shutting
MSA-DCA | WA5392675 | 2 | FCT SURFACE CLEANING | James St entrance & corner Roe/William - Various areas of Graffiti - See notes | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.5 | 2022-05-03 11:26 | 2022-05-06 17:00 | 2022-05-05 13:00 | 2022-05-06 17:00 | 2022-05-05 14:30 |  |  | job completed - removed graffiti
MSA-DCA | WA5395048 | 2 | Techworks Electrical | Main Switch Room - Noisy fluro light in main switch room, fitting needs to be repalced | Electrical | General Electrical | 425.85 | Pass | Pass | -1 | -1 | 1.5 | 2022-05-05 10:29 | 2022-05-10 17:00 | 2022-05-05 13:30 | 2022-05-10 17:00 | 2022-05-05 15:00 |  |  | Replaced fluro light for new led batten
MSA-DTWD | WA5396806 | 1 | Milners Tree Solutions Pty Ltd | B Block External – East End of Campus - Tree removal along driveway near B Block carpark | Landscaping & Gardening | General Tree Works | 810 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-06 11:28 | 2022-05-09 17:00 | 2022-05-07 12:30 | 2022-05-09 17:00 | 2022-05-07 14:00 |  |  | tree/bushes removed
MSA-DCA | WA5397023 | 2 | Protek 24/7 Building & Maintenance | Ground Level - BOH Stage Area - 2 x magentic windows not operating - See notes below | Building | Windows | 157.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-06 12:51 | 2022-05-11 17:00 | 2022-05-10 09:00 | 2022-05-11 17:00 | 2022-05-10 10:30 |  |  | Job Closed as per Denise McCartney
MSA-DCA | WA5397568 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Roe st humidity alarm in gallery 3,4 & 9 | Building | Materials | 486.65 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-07 06:42 | 2022-05-07 08:42 | 2022-05-07 07:30 | 2022-05-07 10:42 | 2022-05-07 09:00 |  |  | See work logs
MSA-DFES | WA5398457 | 2 | Australian HVAC Services Pty. Ltd. | Outside - Rear -air con is making loud noises | Air Conditioning | Room Air Conditioners | 266.1 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-09 10:27 | 2022-05-12 17:00 | 2022-05-11 08:00 | 2022-05-12 17:00 | 2022-05-11 09:30 |  |  | Normal operation noises no issues could be found.
MSA-DFES | WA5400710 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | L1 Hall / passage Light hanging from ceiling outside SO dorm. | Electrical | Lighting, Internal | 195.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-10 12:21 | 2022-05-13 17:00 | 2022-05-11 08:00 | 2022-05-13 17:00 | 2022-05-11 09:30 |  |  | Arrived on site at 0800. Waited for staff to arrive on site to be granted access. Investigated hanging light in station hallway. Discovered 2 x battens parted from ceiling. Reinstated both light fittings and reenergised circuit. Left site at 0930.
MSA-DTWD | WA5406893 | 3 | Falcetta Plumbing and Gas | Toilet cistern dribbling | Plumbing & Drainage | Toilets/Cisterns | 1153.62 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-11 07:27 | 2022-05-17 17:00 | 2022-05-16 17:00 | 2022-05-17 17:00 | 2022-05-16 18:30 |  |  | Replaced old cistern with dual flush invisi
MSA-DTWD | WA5413142 | 2 | Protek 24/7 Building & Maintenance | Courtyard next to CG13 - Water coming through in several areas - See notes below | Roofing | Metal Roofing | 322 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-12 09:15 | 2022-05-17 17:00 | 2022-05-17 09:30 | 2022-05-17 17:00 | 2022-05-17 11:00 |  |  | Repair Roof leaks
MSA-DTWD | WA5413432 | 1 | Damian Rak Electrical Pty Ltd | BLd 833 - Faulty smoke alarm | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1.5 | 2022-05-12 11:07 | 2022-05-13 17:00 | 2022-05-12 12:20 | 2022-05-13 17:00 | 2022-05-12 13:50 |  |  | job completed - Faulty smoke alarm repaired
MSA-DTWD | WA5413479 | 2 | Protek 24/7 Building & Maintenance | Room F47 - Roof Leak | Roofing | Metal Roofing | 272.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-05-12 11:29 | 2022-05-17 17:00 | 2022-05-13 10:00 | 2022-05-17 17:00 | 2022-05-13 11:30 |  |  | Repair Roof leak - Room F47
MSA-DFES | WA5414076 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | External Ground Floor - Rear Carport Area - see details below | Electrical | General Electrical | 212.06 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-12 16:33 | 2022-05-17 17:00 | 2022-05-17 09:15 | 2022-05-17 17:00 | 2022-05-17 10:45 |  |  | Arrived on site at 0915 to investigate faulty external switch in rear carport of station. Discovered lights not switching correctly and identified damaged mechs within switch. Left site at at 0945 to wholesaler. Returned to site at 1015 and replaced/reenergised faulty switch. All lights now switching correctly. Left site at 1045.
MSA-DFES | WA5417698 | 3 | Australian HVAC Services Pty. Ltd. | Main Administration - Ceiling - Director Training Development office - see details below | Air Conditioning | Room Air Conditioners | 179.76 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-13 15:24 | 2022-05-20 17:00 | 2022-05-17 11:00 | 2022-05-20 17:00 | 2022-05-17 12:30 |  |  | Arrived on-site, spoke with on-site representative who directed me to office where staff member had said it is getting too hot, began investigation and found separate office is run off FCU that supply's main office area, no sensor in private office in question, no zone controls at all, found excessive airflow from grill outlet, adjusted airflow from ducting to office, this will allow room to better heat as same rate as main office and stop overheating in private office, informed client of adjustments made & left site.
MSA-DTWD | WA5417737 | 2 | Lane's Plumbing | BATHROOM B - Tap are faulty ---- loose | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 1.5 | 2022-05-13 16:30 | 2022-05-18 17:00 | 2022-05-17 16:00 | 2022-05-18 17:00 | 2022-05-17 17:30 |  |  | Repairs to faulty taps
MSA-MRWA | WA5437355 | 1 | AWB Co. | Maintenance Control Room - power points are not working | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-16 07:39 | 2022-05-16 17:00 | 2022-05-16 14:30 | 2022-05-16 17:00 | 2022-05-16 16:00 |  |  | Attended site and signed in. Completed JSA. Called PFM to locate area. Was told to speak with lady at desks in the entry on the right. Lady was on the phone for 20 minutes. Got shown the training room that was not working. Investigated all gpos and power to be on and working. Called PFM to advise it could be an AV issue and found that to be a different previous job. Was advised to go find another person and they were not on site. Began asking around to find where the power was not working. Found south east room to be the reported room and found the gpos pointed out not working to all work. Checked switchboard and all circuits on and working correctly. No faults on site. Advised staff to try again tomorrow morning and find out if someone’s accessing the switchboard and turning things on and off. Signed out. Job complete
MSA-DTWD | WA5438085 | 2 | Complete Pest Management Services | Ground Level - Room F39 - Strong rodent smell - please investigate | Pest Control | General Pest | 289.45 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-16 12:26 | 2022-05-19 17:00 | 2022-05-18 07:00 | 2022-05-19 17:00 | 2022-05-18 08:30 |  |  | Inspected rooms for dead rodent smell, removed slats to inspect roof void could not find dead rodent, rodent has fallen down cavity wall and cannotremove , place odour eater bag for cease of smell
MSA-DTAG | WA5438525 | 3 | Midolo Building Services | Level 4 - Male Public Toilets' - Toilet Cubicle door not locking - Latch & hinges require attention | Security | Locksmith | 207.52 | Pass | Pass | -1 | -1 | 1.5 | 2022-05-16 15:00 | 2022-05-23 17:00 | 2022-05-17 13:15 | 2022-05-23 17:00 | 2022-05-17 14:45 |  |  | repaired door & hardware
MSA-DTAG | WA5438537 | 2 | O'Brien Glass With Care | Level 5 - Window in waiting area, opposite court 56 - top of window is broken | Glazing | Window Glass |  | Fail | Fail | 1 | 1 | 1.5 | 2022-05-16 15:05 | 2022-05-19 17:00 | 2022-05-28 06:45 | 2022-05-19 17:00 | 2022-05-28 08:15 |  |  | reglazed window
MSA-DTWD | WA5451228 | 2 | AHS Services WA Pty Ltd (Anchor) | B209 - Tap in staff kicthen, spout stuck in one position B209 | Plumbing & Drainage | Materials | 203.985 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-17 07:46 | 2022-05-19 17:00 | 2022-05-17 08:00 | 2022-05-19 17:00 | 2022-05-17 09:30 |  |  | Inspected attempted multiple times to remove spout, completely siezed, collected parts cutaway installed new all good
MSA-DTWD | WA5454734 | 1 | AWB Co. | First Floor - Disabled Toilet - when fan is operating it smells like something is burning | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-17 13:46 | 2022-05-18 17:00 | 2022-05-18 07:00 | 2022-05-18 17:00 | 2022-05-18 08:30 |  |  | Attended site and signed in. Completed JSA. Awaited access to building. Located disabled toilet and turned on fan. Ran for numerous minutes and checked for smell and heats and burning. Nothing out of the ordinary. All is good. Fan is a fresh air fan not exhaust fan. Checked on roof and nothing in the area could create that sort of smell. Burn off could have been the cause. All seems to be safe and working correctly. Signed out. Job complete
MSA-DTWD | WA5454837 | 2 | AHS Services WA Pty Ltd (Anchor) | A Block - Second Floor - Female - Toilet Cubicle - Not flushing properly | Plumbing & Drainage | Toilets/Cisterns | 177.915 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-17 15:06 | 2022-05-20 17:00 | 2022-05-20 08:00 | 2022-05-20 17:00 | 2022-05-20 09:30 |  |  | Cleaned bithxisterns and adjusted to maximum flush all working well
MSA-DTAG | WA5460325 | 2 | Midolo Building Services | Level 12 - Door near bins and emergency exit stairwell - Door slams very loudly | Building | Doors | 713.39 | Fail | Fail | 1 | 1 | 1.5 | 2022-05-18 12:56 | 2022-05-23 17:00 | 2022-05-27 13:30 | 2022-05-23 17:00 | 2022-05-27 15:00 |  |  | new door closer installed
MSA-DTWD | WA5462033 | 2 | Techworks Plumbing | H Block - Toilet leaking water onto floor | Plumbing & Drainage | Toilets/Cisterns | 170.07 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-19 10:45 | 2022-05-24 17:00 | 2022-05-24 14:00 | 2022-05-24 17:00 | 2022-05-24 15:30 |  |  | Arrived on site Signed inDrove around to H block Found toiletCouldn't see anything wrong with it.Wasn't leaking at all May of been from the rainSigned out
MSA-DTWD | WA5470662 | 0 | AWB Co. | Q Block - Water damage - getting into the building via door ways | Cleaning | Cleaning | 265 | Fail | Fail | 0 | 0 | 1.5 | 2022-05-23 11:33 | 2022-05-23 13:33 | 2022-05-23 16:00 | 2022-05-23 15:33 | 2022-05-23 17:30 |  |  | Description of Workorder: Q Block - Water damage - getting into the building via door waysAdditional Notes: Water damage on carpets and foyerno one on site to sign
MSA-MRWA | WA5471437 | 1 | Automatic Fire Protection (ARA) | East Basement carpark - Server room - secondary fire panel not functional - showing random symbols | Fire Protection Services | Fire Protection - Monitor System | 193.51 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-23 12:53 | 2022-05-24 17:00 | 2022-05-24 08:30 | 2022-05-24 17:00 | 2022-05-24 10:00 |  |  | LCD display on server room Gas SIP faulty.Parts now obsolete for IFS-2600 panels, therefore, unable to replace LCD component.To rectify issue, new FIP will be required, ARA to provide quote. Details for quote are as follows;-Notifier Conventional FIP-8 way relay card-Gas expansion module-Fire suppression control modulePhotos attached for further reference by supplier.Note: LCD will not impede functionality of fire system.
MSA-DTWD | WA5471643 | 3 | AWB Co. | B326 - Fashion - Rain water leak from roof above | Building | General Building | 347.09 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-23 13:03 | 2022-05-30 17:00 | 2022-05-30 08:00 | 2022-05-30 17:00 | 2022-05-30 09:30 |  |  | Attended sealed downpipe over flow, sealed wall flashing, conduit and rusted sheets. Job complete
MSA-DTWD | WA5472097 | 2 | AWB Co. | Faulty Light switch | Electrical | Lighting, Internal | 284.78 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-23 14:05 | 2022-05-26 17:00 | 2022-05-25 07:00 | 2022-05-26 17:00 | 2022-05-25 08:30 |  |  | Attended site and signed in. Completed jsa. Located faulty light switch. Isolated power. Changed over switch mech. Took pic. Working as intended. Completed paperwork. Signed out.Job complete
MSA-DFES | WA5472158 | 2 | Protek 24/7 Building & Maintenance | Numerous leaks and water downpipe overflows in outdoor area and under patio. | Roofing | Metal Roofing | 278 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-23 14:51 | 2022-05-26 17:00 | 2022-05-26 08:15 | 2022-05-26 17:00 | 2022-05-26 09:45 |  |  | Cleaned gutters
MSA-DCA | WA5472208 | 1 | Protek 24/7 Building & Maintenance | Scene Dock - Water leak in Scene Dock | Building | General Building | 215.125 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-23 15:41 | 2022-05-24 17:00 | 2022-05-24 13:00 | 2022-05-24 17:00 | 2022-05-24 14:30 |  |  | Repair Water leak in Scene Dock
MSA-DTWD | WA5472464 | 3 | AWB Co. | Centre Block - Room C712 - Rain water leaks coming from ceiling | Roofing | Metal Roofing | 326.47 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 07:58 | 2022-05-30 17:00 | 2022-05-30 06:30 | 2022-05-30 17:00 | 2022-05-30 08:00 |  |  | Vinyl from floor area on rooftop coming apart around drainage outlet. Fixed down joins with butyl tape and sealed around outlet with silicone. If issue continues would suggest engaging a special contractor to assess the membrane.
MSA-DTWD | WA5472517 | 2 | Protek 24/7 Building & Maintenance | Roof leak in room A006 | Roofing | Metal Roofing | 303.3 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 08:22 | 2022-05-27 17:00 | 2022-05-25 13:45 | 2022-05-27 17:00 | 2022-05-25 15:15 |  |  | Repair Roof leak in room A006
MSA-DCA | WA5472702 | 1 | Protek 24/7 Building & Maintenance | Tiptoe Alley Storeroom - see notes below | Roofing | Metal Roofing | 303.3 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 09:31 | 2022-05-25 17:00 | 2022-05-24 12:15 | 2022-05-25 17:00 | 2022-05-24 13:45 |  |  | Repair leak to storeroom
MSA-DCA | WA5472825 | 1 | TK Elevator Australia Pty Ltd | Main Building - Ground - Lift - Light in lift not working - venues only access to upstairs | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 10:53 | 2022-05-25 17:00 | 2022-05-24 13:45 | 2022-05-25 17:00 | 2022-05-24 15:15 |  |  | Lift1 Blue-Hydraulic :Lift car lights (2x 2 foot fluorescent tubes and 2x S2 starters) faulty, replaced both fluro tubes and starters. Tested car light and power RCD. Tested phone line unit. Lift in service.
MSA-DTWD | WA5472919 | 3 | AWB Co. | Rain water Leak | Roofing | Metal Roofing | 347.09 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 11:36 | 2022-05-31 17:00 | 2022-05-30 10:30 | 2022-05-31 17:00 | 2022-05-30 12:00 |  |  | Attended and sealed box gutter sumo, sealed dektites as were split, found rust spots on roof sheets, sealed, sealed ridgecappings and flashing. Job Complete
MSA-DTWD | WA5472959 | 2 | Techworks Electrical | Q-Block 1st Floor hall way has flickering lights | Electrical | Lighting, Internal | 363.11 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 11:56 | 2022-05-27 17:00 | 2022-05-27 12:00 | 2022-05-27 17:00 | 2022-05-27 13:30 |  |  | Replaced fluro tubes and starters in Q block level 1 lobby
MSA-DTWD | WA5473006 | 2 | AWB Co. | light fitting missing cover | Electrical | Lighting, Internal | 66.72 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 12:16 | 2022-05-27 17:00 | 2022-05-27 15:00 | 2022-05-27 17:00 | 2022-05-27 16:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, found replacement cover on site and fitted it, light now good, packed up, completed paperwork,signed out, ***job completed***
MSA-DTWD | WA5473201 | 3 | AWB Co. | Industrial Wall fan not working above Linisher station | Electrical | General Electrical | 374.145 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-24 12:43 | 2022-05-31 17:00 | 2022-05-30 08:15 | 2022-05-31 17:00 | 2022-05-30 09:45 |  |  | Attended site and signed in. Completed JSA. Located room with faulty fan. Left site to go pic, up required parts for job. Returned to site. Removed old fan and installed new 750mm industrial fan. Tested to see if all working correctly. Notified relevant personal of works done. **job complete**
MSA-DTWD | WA5476123 | 2 | AWB Co. | Roof leak south west corner | Roofing | Metal Roofing | 309 | Fail | Fail | 2 | 2 | 1.5 | 2022-05-25 11:03 | 2022-05-30 17:00 | 2022-06-16 07:00 | 2022-05-30 17:00 | 2022-06-16 08:30 |  |  | Attended and located leak, required return. Sealed completely around base flashing to A/C and repaired rusted sump. May need replacement if issue persist.
MSA-DCA | WA5477616 | 1 | Techworks Electrical | Chicho Gelato shop - Water ingress into spotlights of gelato shop. Please inspect to make safe | Electrical | General Electrical | 321.69 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-25 15:30 | 2022-05-26 17:00 | 2022-05-26 10:30 | 2022-05-26 17:00 | 2022-05-26 12:00 |  |  | Water entering light. Sealed cable entries and exterior of light with silicone
MSA-DTWD | WA5478079 | 1 | AWB Co. | No power M002 - faulty GPO's | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-26 08:40 | 2022-05-27 17:00 | 2022-05-27 10:15 | 2022-05-27 17:00 | 2022-05-27 11:45 |  |  | Attended site and signed in, completed jsa,spoke with fm about the job, located room that had lost power, went to all surrounding switchboards and checked if there were breakers off, no breakers were off, ran finger over all breakers and found one to switch off , reset breaker and tested power in room , all power now back on and working, completed Paperwork, packed up , **job completed ***
MSA-DFES | WA5478212 | 3 | Protek 24/7 Building & Maintenance | Main Administration - Ground - Lecture room 1 - see details below | Building | General Building | 322 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-26 10:08 | 2022-06-02 17:00 | 2022-06-02 13:00 | 2022-06-02 17:00 | 2022-06-02 14:30 |  |  | Repair ceiling panel - Ground - Lecture room 1
MSA-DTWD | WA5478433 | 2 | AWB Co. | Multiple Faulty Fluro's Lights | Electrical | Lighting, Internal | 212.44 | Pass | Pass | -1 | -1 | 1.5 | 2022-05-26 11:41 | 2022-05-31 17:00 | 2022-05-27 11:45 | 2022-05-31 17:00 | 2022-05-27 13:15 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located lighting, replaced various tubes and starters, re mounted light fitting to beam, cleaned up, tested all light and working as intended, completed paperwork, signed out , **job completed***
MSA-DTAG | WA5478777 | 3 | AWB Co. | Level 10 - Various - Counter area and Banksia room - lights are out | Electrical | General Electrical | 185.905 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-26 13:38 | 2022-06-02 17:00 | 2022-06-02 15:00 | 2022-06-02 17:00 | 2022-06-02 16:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located various lights that need replacing. Left site to pick up parts. Returned and repaired lights as per site request. Packed up site. Completed paperwork. **job complete**
MSA-DTWD | WA5479424 | 0 | Protek 24/7 Building & Maintenance | Window Above Office A10 - window has dropped out - need roof access | Building | Windows | 287.9 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-27 09:29 | 2022-05-27 11:29 | 2022-05-27 10:45 | 2022-05-27 13:29 | 2022-05-27 12:15 |  |  | Repair window above Office A10
MSA-DTWD | WA5479500 | 2 | Techworks Electrical | Metaks section - Workshops Metals section faulty 3 phase plug to cold saw | Electrical | General Electrical | 303.51 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-27 09:55 | 2022-06-01 17:00 | 2022-05-31 11:00 | 2022-06-01 17:00 | 2022-05-31 12:30 |  |  | Replaced plug to machine
MSA-DTWD | WA5481090 | 3 | Critical Fire Protection & Training | Level 2 - Entry Foyer - Fault on Fire Panel | Fire Protection Services | Fire Protection - Monitor System | 341.21 | Pass | Pass | -1 | -1 | 1.5 | 2022-05-30 10:47 | 2022-06-07 17:00 | 2022-05-31 10:30 | 2022-06-07 17:00 | 2022-05-31 12:00 |  |  | Attended site to investigate fault to fire panel. On arrival found loop 2, detector 62, zone 2 in maintenance fault. Replaced smoke detector head with new XP95 smoke detector and fault cleared after detector replacement. No further action required
MSA-DTWD | WA5481238 | 3 | AWB Co. | Room D04 - Flickering Fluoro - Broken Tombstones | Electrical | Lighting, Internal | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-30 11:39 | 2022-06-07 17:00 | 2022-06-07 15:00 | 2022-06-07 17:00 | 2022-06-07 16:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located lighting in d block, isolated lighting circuits in dB, got parts from store on site and repaired all tombstones that were broken, replaced tubes and starters , re fitted covers and energised lights, all lights working as intended , all parts supplied by site, completed paperwork,packed up. ***job completed **
MSA-DCA | WA5481603 | 1 | Protek 24/7 Building & Maintenance | Ground Floor - Fault on emergency push bar door | Building | General Building | 157.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-30 14:30 | 2022-05-31 17:00 | 2022-05-31 09:30 | 2022-05-31 17:00 | 2022-05-31 11:00 |  |  | Assess Fault on emergency door push Bar
MSA-DTWD | WA5481889 | 1 | BJ SYSTEMS | Main Auto Door - the door isnt locking | Security | Access Control | 207.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-31 07:40 | 2022-05-31 17:00 | 2022-05-31 10:45 | 2022-05-31 17:00 | 2022-05-31 12:15 |  |  | Main auto door not locking. Attend site and override the door to secure mode and door locked, gained entry with card and exited with press to exit. Tried multiple times, was locking and unlocking, no issues with auto door now
MSA-DCA | WA5482563 | 0 | Techworks Plumbing | Ground Floor - Hackett Hall - Male Toilets' - blocked urinal | Plumbing & Drainage | Toilets/Cisterns | 292.7 | Pass | Pass | 0 | 0 | 1.5 | 2022-05-31 13:10 | 2022-05-31 15:10 | 2022-05-31 13:30 | 2022-05-31 17:10 | 2022-05-31 15:00 |  |  | While there was no visible cause evident for this blockage I would say the cause was Uric acid build up creating a crust. I used an acidic cleaner to soften crust and plunged through the blockage. I removed the ceramic plug to ensure the ceramic trap was clear and flowing
MSA-DFES | WA5486428 | 0 | MALCOLM THOMPSON PUMPS PTY LTD | Bottom Damp - Applied Training - Pump is faulty | Mechanical Services | Pumps |  | Fail | Fail | 6 | 6 | 1.5 | 2022-06-01 08:40 | 2022-06-01 10:40 | 2022-07-13 15:00 | 2022-06-01 12:40 | 2022-07-13 16:30 |  |  | Repairs to pumps
MSA-DCA | WA5486769 | 2 | Protek 24/7 Building & Maintenance | Roof - Gutter - Gutter needs new clips | Roofing | Guttering | 272.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-01 10:15 | 2022-06-07 17:00 | 2022-06-03 12:00 | 2022-06-07 17:00 | 2022-06-03 13:30 |  |  | Replaced Gutter Clips
MSA-DTWD | WA5486784 | 3 | ECO PLUMBING AND GAS PTY LTD | Male Toilets - L05 - Running tap | Plumbing & Drainage | Water | 208.99 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-01 10:23 | 2022-06-09 17:00 | 2022-06-07 15:00 | 2022-06-09 17:00 | 2022-06-07 16:30 |  |  | Reseated and serviced hot tap
MSA-DTWD | WA5487344 | 3 | SENTINEL LOCK SERVICE PTY LTD | Room 8G13 - Fly wire door has a faulty door lock | Security | Locksmith | 157.64 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-01 14:20 | 2022-06-09 17:00 | 2022-06-03 11:15 | 2022-06-09 17:00 | 2022-06-03 12:45 |  |  | 8g13 - FLYSCREEN DOOR LOCK IS FAULTY.Lock removed by request.Custom plates installed to cover.
MSA-DTWD | WA5487443 | 3 | ACTION GLASS & ALUMINIUM | N59 - Cracked internal window pane in hallway | Glazing | Window Glass | 328.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-01 15:21 | 2022-06-09 17:00 | 2022-06-02 11:30 | 2022-06-09 17:00 | 2022-06-02 13:00 |  |  | ATTENDED SITE, REGLAZED WINDOW CLIENT DID NOT WANT FROST FILM
MSA-DCA | WA5487974 | 2 | Techworks Plumbing | Level 1 - Geology Bld - Female Toilets - 2 x toilets seats faulty - see notes below | Plumbing & Drainage | Toilets/Cisterns | 222.71 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-02 09:39 | 2022-06-08 17:00 | 2022-06-08 10:30 | 2022-06-08 17:00 | 2022-06-08 12:00 |  |  | Replaced 2 broken toilet seats
MSA-DTAG | WA5487990 | 3 | Midolo Building Services | Level 2A - Middle of ceiling in main office - Water stains on ceiling | Building | Ceiling | 231.38 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-02 09:45 | 2022-06-10 17:00 | 2022-06-07 13:00 | 2022-06-10 17:00 | 2022-06-07 14:30 |  |  | DAMAGED CEILING TILES REPLACED
MSA-DCA | WA5488100 | 2 | Techworks Electrical | Hackett Hall - Level 3 - Cleaners storeroom - light switch faulty | Electrical | General Electrical | 188.37 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-02 10:30 | 2022-06-08 17:00 | 2022-06-03 14:00 | 2022-06-08 17:00 | 2022-06-03 15:30 |  |  | Replqced fauly switch mech with new
MSA-DTWD | WA5488574 | 3 | AHS Services WA Pty Ltd (Anchor) | Urinal blocked when flushed D Block level 2 | Plumbing & Drainage | Toilets/Cisterns | 141.285 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-02 13:54 | 2022-06-10 17:00 | 2022-06-07 11:30 | 2022-06-10 17:00 | 2022-06-07 13:00 |  |  | Cleared blocked urinal
MSA-DTAG | WA5488592 | 1 | Total Security Systems Pty Ltd | Camera [029] B1 West Entry External showing “attempting to reconnect” and “failed to recover”. | Security | CCTV Surveillance | 348 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-02 14:03 | 2022-06-03 17:00 | 2022-06-03 14:00 | 2022-06-03 17:00 | 2022-06-03 15:30 |  |  | 3/6/2022 - Comtec Data KarrathaAttended site and power cycled and ping tested the camera, it came back on line and all working.
MSA-DTAG | WA5493864 | 2 | AAA Ability Locksmiths | Ground Level - Courtroom 3 - The handle on door is broken | Security | Locksmith | 441.57 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-07 10:48 | 2022-06-10 17:00 | 2022-06-10 07:30 | 2022-06-10 17:00 | 2022-06-10 09:00 |  |  | Attend Site, replace lock parts and set same function as corresponding court room door.
MSA-DTWD | WA5493943 | 3 | AWB Co. | Level 3 - East Block - Lift Lobby (Exit door to roof) - Door closer pulled off door frame | Building | Doors | 168.75 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-07 11:30 | 2022-06-14 17:00 | 2022-06-10 08:30 | 2022-06-14 17:00 | 2022-06-10 10:00 |  |  | Refit door closer onto frame
MSA-DCA | WA5494359 | 2 | Techworks Electrical | Admin F/F - Passage - Emergency lighting switch in distribution Board - no3 is humming very loud | Electrical | Distribution Board | 347.1 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-07 14:26 | 2022-06-10 17:00 | 2022-06-08 13:00 | 2022-06-10 17:00 | 2022-06-08 14:30 |  |  | Found contactor ever so slightly humming. Cleaned contacts and all working well again.
MSA-DTWD | WA5494484 | 3 | AWB Co. | 2 x orange GPO not working on test benches | Electrical | General Electrical | 207.74 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-07 15:58 | 2022-06-14 17:00 | 2022-06-10 10:30 | 2022-06-14 17:00 | 2022-06-10 12:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job and determined which GPOs needed replacing, isolated circuits and removed damaged GPOs, replaced with new, labelled GPOs, re energised circuits and tested gpos, everything working as intended,packed up, completed paperwork, signed out ** job completed**
MSA-DFES | WA5495811 | 3 | Australian HVAC Services Pty. Ltd. | Ground Level - Dorms 3&5 - Issues with air conditioning - See notes below | Air Conditioning | Room Air Conditioners | 179.76 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-08 16:01 | 2022-06-15 17:00 | 2022-06-09 14:30 | 2022-06-15 17:00 | 2022-06-09 16:00 |  |  | Attended service call, tested ac 6.1 & 6.2 on heating and cooling. Operation was normal. Yested system for faults ,none found. The system will not run on heating on one head unit & cooling on the other. Advised staff
MSA-DTWD | WA5496290 | 2 | Techworks Electrical | Restaurant entrance area - light not working | Electrical | Lighting, Internal | 793.71 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-09 08:58 | 2022-06-14 17:00 | 2022-06-14 07:00 | 2022-06-14 17:00 | 2022-06-14 08:30 |  |  | Replaced lights out in walkway
MSA-DCA | WA5496320 | 1 | Techworks Plumbing | Ground Level - Hackett Hall - Male Toilets - WHB Water spout has fault - See notes below | Plumbing & Drainage | Water | 178.23 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-09 09:12 | 2022-06-10 17:00 | 2022-06-10 10:00 | 2022-06-10 17:00 | 2022-06-10 11:30 |  |  | Unblocked sinkTighten sink outlet
MSA-DTWD | WA5496582 | 3 | AWB Co. | A48A -Light out (Tombstone) | Electrical | Lighting, Internal | 267.84 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-09 11:29 | 2022-06-16 17:00 | 2022-06-13 07:00 | 2022-06-16 17:00 | 2022-06-13 08:30 |  |  | Attended site and signed in. Completed JSA. Located 2x faulty light fittings. Replaced tubes, starters and tombstones in both fittings. Lights are now working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5496888 | 0 | Techworks Electrical | Level 3 open area - emergency exit lights are flashing on multiple levels | Electrical | General Electrical | 196.23 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-09 13:03 | 2022-06-09 15:03 | 2022-06-09 13:30 | 2022-06-09 17:03 | 2022-06-09 15:00 |  |  | Arrived onsite and Found no EMs flashing, talked to one of the techs at stage door and he said they flashed at 10am for 2min and hadn’t done it for the rest of the day.
MSA-DTAG | WA5497230 | 2 | Sapio Pty Ltd | Ground Level - Custody - Custody Intercom – not working from Police door - See notes below | Security | Monitoring | 215.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-09 16:00 | 2022-06-14 17:00 | 2022-06-10 11:00 | 2022-06-14 17:00 | 2022-06-10 12:30 |  |  | Attended site. Checked reported fault. Found faulty power supply for standalone video intercom. Supplied and installednew power supply. Tested operation. Ok.Note.Video intercom is having black and white distorted picture. Upgrade is recommended.
MSA-DTWD | WA5499432 | 2 | Techworks Plumbing | D18 - Leaking wash trough taps | Plumbing & Drainage | Materials | 197.81 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-10 13:07 | 2022-06-15 17:00 | 2022-06-14 07:30 | 2022-06-15 17:00 | 2022-06-14 09:00 |  |  | Attend site for tap servicing. This trough area has 6 sets of taps 12 spindles total. All spindles removed and serviced with new tap washers, red fibre washers, re seat tapsets lubricate and re install then test
MSA-DTWD | WA5499488 | 2 | Techworks Plumbing | D25 - Leaking wash trough taps | Plumbing & Drainage | Materials | 191.62 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-10 13:10 | 2022-06-15 17:00 | 2022-06-14 09:00 | 2022-06-15 17:00 | 2022-06-14 10:30 |  |  | This trough area contain 5 sets of taps. 10 spindles total. All spindles removed and serviced, new tap, washers red fibre washers, re seat all wall sets lubricant spindles and re install. Test
MSA-DTWD | WA5499874 | 0 | Protek 24/7 Building & Maintenance | Room F52 - Roof Leak- Will need water soaker & Blower - May be caused by blocked gutters | Roofing | Metal Roofing | 1000 | Fail | Fail | 0 | 0 | 1.5 | 2022-06-10 14:58 | 2022-06-10 16:58 | 2022-06-10 20:00 | 2022-06-10 18:58 | 2022-06-10 21:30 |  |  | Clean gutters and inspected rooms Recommendation to site made that RM frequency be increased to avoid issue recurring
MSA-DTWD | WA5511785 | 2 | AHS Services WA Pty Ltd (Anchor) | Basin tap leaking A Block level 3 West Female | Plumbing & Drainage | Water | 200.965 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-13 09:02 | 2022-06-16 17:00 | 2022-06-14 12:00 | 2022-06-16 17:00 | 2022-06-14 13:30 |  |  | serviced basin taps in demale bathroom
MSA-DTAG | WA5511866 | 3 | PPM Project Painting & Maintenance | External - Sally port - Graffiti on wall of sally port | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 1.5 | 2022-06-13 10:18 | 2022-06-20 17:00 | 2022-06-14 12:00 | 2022-06-20 17:00 | 2022-06-14 13:30 |  |  | Removal of graffiti
MSA-DCA | WA5511880 | 2 | Techworks Electrical | Level 1 - Kitchen - Power Point near sink not currently working | Electrical | General Electrical | 301.88 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-13 10:34 | 2022-06-16 17:00 | 2022-06-13 12:30 | 2022-06-16 17:00 | 2022-06-13 14:00 |  |  | Tasks completed 1. Arrived onsite and met with Elena who’s showed us to the outlet in question. 2. plugged tester in and found no power. 3. Elena opened switch board for us and found a tripped breaker. Reset breaker and tested again. Gpo then had power.
MSA-DCA | WA5513323 | 1 | Protek 24/7 Building & Maintenance | M Block - M Block Windown - Window cover has come away - Needs to be reattached | Building | Windows | 185.25 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-14 09:36 | 2022-06-15 17:00 | 2022-06-15 08:30 | 2022-06-15 17:00 | 2022-06-15 10:00 |  |  | Refitted loose window covers
MSA-DCA | WA5513331 | 1 | Protek 24/7 Building & Maintenance | Ripped Banners needing removal - See notes below | Building | External Walls | 196.25 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-14 09:41 | 2022-06-15 17:00 | 2022-06-15 07:00 | 2022-06-15 17:00 | 2022-06-15 08:30 |  |  | Remove Ripped Banners
MSA-DTWD | WA5513361 | 1 | Lane's Plumbing | kitchen Faulty dish washer | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1.5 | 2022-06-14 09:53 | 2022-06-15 17:00 | 2022-06-14 10:30 | 2022-06-15 17:00 | 2022-06-14 12:00 |  |  | job completed - REPAIRS TO LEAKING DISHWASHER AT HOMESTEAD
MSA-DTWD | WA5513613 | 2 | Lane's Plumbing | kitchen, Faulty pipework under sink | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 1.5 | 2022-06-14 11:46 | 2022-06-17 17:00 | 2022-06-14 13:00 | 2022-06-17 17:00 | 2022-06-14 14:30 |  |  | job completed - replace leaking pipework under sink
MSA-DCA | WA5513861 | 3 | Techworks Electrical | Library and Salvadore’s Office in warehouse - 3 Fluorescent light fittings faulty - See notes below | Electrical | Lighting, Internal | 227.05 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-14 13:49 | 2022-06-21 17:00 | 2022-06-16 13:00 | 2022-06-21 17:00 | 2022-06-16 14:30 |  |  | Completed replacement of lights in library and salvodores office.
MSA-DCA | WA5513884 | 2 | Techworks Electrical | Level 1 - HLT Stairwell 2 - Bottom of stairwell - Level 1a near green room - Exit light out | Electrical | Emergency & Exit Lighting | 257.81 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-14 14:01 | 2022-06-17 17:00 | 2022-06-16 09:00 | 2022-06-17 17:00 | 2022-06-16 10:30 |  |  | Replaced exit sign with new. All working well.
MSA-DCA | WA5522306 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - HBRC - Leaking pipe in the potable water filter unit | Plumbing & Drainage | Water | 182.29 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-15 14:10 | 2022-06-20 17:00 | 2022-06-20 08:15 | 2022-06-20 17:00 | 2022-06-20 09:45 |  |  | Leak on system. Could not pinpoint where leak was exactly coming from. SPOKEN TO DENISE FROM programmed. Sent her photos to phone on manufacturing model and service agent. She to follow up completion of job. Not much more gps can do at this stage
MSA-DCA | WA5534366 | 3 | Techworks Electrical | Main Building - Puccini Room - Lights have been flickering - see notes below | Electrical | Lighting, Internal | 515.9 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-16 09:33 | 2022-06-23 17:00 | 2022-06-17 08:00 | 2022-06-23 17:00 | 2022-06-17 09:30 |  |  | Rectified faulty lighting within Puccini room
MSA-DCA | WA5534915 | 1 | Techworks Electrical | Roof - external - GPOs on roof are not safe, water ingress. Please make safe. | Electrical | General Electrical | 320.38 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-16 15:44 | 2022-06-17 17:00 | 2022-06-17 09:30 | 2022-06-17 17:00 | 2022-06-17 11:00 |  |  | Installed gpos on a bracket made from some aluminium from the HLT workshop.
MSA-DTWD | WA5548744 | 3 | AWB Co. | E47- Faulty Main Switch on EVAP main Switchboard | Electrical | General Electrical | 138.94 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-17 09:11 | 2022-06-24 17:00 | 2022-06-22 11:30 | 2022-06-24 17:00 | 2022-06-22 13:00 |  |  | Attended site signed in jsa completed. Spoke to theo about job. Needed evaps disconnected from plant room boards as no longer in use and need powered off so roof leak job can proceed. all disconnected and put out of service tag.*** job completed***
MSA-DTAG | WA5548753 | 3 | AHS Services WA Pty Ltd (Anchor) | Male staff toilet -Cistern flush button broken | Plumbing & Drainage | Toilets/Cisterns | 205.615 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-17 09:20 | 2022-06-24 17:00 | 2022-06-23 07:30 | 2022-06-24 17:00 | 2022-06-23 09:00 |  |  | Picked up and replaced broken cistern button-male staff
MSA-DTWD | WA5548797 | 2 | ECO PLUMBING AND GAS PTY LTD | Left hand toilet is not flushing - Cistern is faulty | Plumbing & Drainage | Toilets/Cisterns | 190.99 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-17 09:52 | 2022-06-22 17:00 | 2022-06-22 13:00 | 2022-06-22 17:00 | 2022-06-22 14:30 |  |  | Flushed through inlet valces
MSA-DTWD | WA5548830 | 3 | AWB Co. | E410 - E47 Faulty Main Switch on EVAP main Switchboard | Electrical | General Electrical | 186.04 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-17 10:01 | 2022-06-24 17:00 | 2022-06-22 10:00 | 2022-06-24 17:00 | 2022-06-22 11:30 |  |  | Attended site signed in jsa completed. Spoke to theo about job. Needed evaps disconnected from plant room boards as no longer in use and need powered off so roof leak job can proceed. all disconnected and put out of service tag.*** job completed***
MSA-DCA | WA5563450 | 3 | Techworks Electrical | Ground Floor - CRC Between Collection Box 1 and Collection Box 2 - | Electrical | General Electrical | 349.97 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-20 14:50 | 2022-06-27 17:00 | 2022-06-22 08:00 | 2022-06-27 17:00 | 2022-06-22 09:30 |  |  | Completed repair.
MSA-DTWD | WA5565180 | 3 | AWB Co. | W206 and W206a - Replace light tubes not working | Electrical | General Electrical | 279.36 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-21 14:28 | 2022-06-28 17:00 | 2022-06-23 09:45 | 2022-06-28 17:00 | 2022-06-23 11:15 |  |  | Attended site and signed in. Completed jsa. Located faulty light fittings. Replaced all tubes and starters. Working as intended. Took pictures, completed paperwork. Signed out.Job complete
MSA-DTWD | WA5565606 | 3 | AWB Co. | hanging GPO's tripping | Electrical | General Electrical | 404.04 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-22 09:23 | 2022-06-29 17:00 | 2022-06-24 08:00 | 2022-06-29 17:00 | 2022-06-24 09:30 |  |  | Attended site and signed in. Completed JSA. Located outside area at N block. Found 3 pendants not working and 2 pole gpos not working. Supply and replace faulty and full of water pendant gpo. Supply and replace 2 x switched socket outlets on pillars. Tested all okay. Signed out. Job complete
MSA-DCA | WA5565900 | 2 | Techworks Electrical | BOH Stage area - Ground Level - Power outlet is tripping | Electrical | General Electrical | 464.73 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-22 12:24 | 2022-06-27 17:00 | 2022-06-27 07:30 | 2022-06-27 17:00 | 2022-06-27 09:00 |  |  | Replaced damaged 3phase switched outlet in back of stage area for motor control cable
MSA-DTAG | WA5567011 | 3 | AHS Services WA Pty Ltd (Anchor) | Ground - Interview room 3 (Victim Support Room) - please see details below | Plumbing & Drainage | Water | 195.415 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-23 13:40 | 2022-06-30 17:00 | 2022-06-29 08:00 | 2022-06-30 17:00 | 2022-06-29 09:30 |  |  | Inspected roof , gutter all clear, found seals around window perished causing water to leak in sealed with silicone.
MSA-DTWD | WA5567073 | 3 | Critical Fire Protection & Training | Entry Foyer - Fire panel fault | Fire Protection Services | Fire Protection - Monitor System | 341.21 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-23 14:30 | 2022-06-30 17:00 | 2022-06-27 07:40 | 2022-06-30 17:00 | 2022-06-27 09:10 |  |  | Start time: 7:40amFinish time: 9:10amAttended site to investigate fault reported on fire panel. On arrival panel operating with all systems normal and no faults present. Used panel history log to identify recent faults and found re-occurring intermittent fault originating from loop 2/sensor 67 in zone 2 (lithography room). Replaced faulty detector with new XP95 addressable smoke to eliminate further intermittent faults. Panel operating with all systems normal on departure.
MSA-DTAG | WA5567379 | 0 | Sapio Pty Ltd | Level 10 -Swipe card entry to office doors has failed | Security | Access Control | 370 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-24 08:29 | 2022-06-24 10:29 | 2022-06-24 09:30 | 2022-06-24 12:29 | 2022-06-24 11:00 |  |  | Clock satellite lock lost and failed to find NTP satellite. Fault restored after relocation of time sync antennas. Solid lockand all time GPS & synced to correct times. All restored.
MSA-DTWD | WA5567396 | 2 | Techworks Electrical | Classroom 1- has a broken power point/ socket | Electrical | General Electrical | 359.57 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-24 08:43 | 2022-06-29 17:00 | 2022-06-28 09:00 | 2022-06-29 17:00 | 2022-06-28 10:30 |  |  | Replaced damaged 15a gpo with new 15a gpo and installed additional double gpo next to it
MSA-DTAG | WA5567420 | 1 | Gilmour & Jooste Electrical | Ground -Court of Appeal Registry - Light flickering | Electrical | General Electrical | 64.84 | Pass | Pass | 0 | 0 | 1.5 | 2022-06-24 08:50 | 2022-06-27 17:00 | 2022-06-27 06:00 | 2022-06-27 17:00 | 2022-06-27 07:30 |  |  | Replaced multiple flickering tubes and starters
MSA-DTWD | WA5567435 | 2 | AHS Services WA Pty Ltd (Anchor) | U-Block disabled toilet has a broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 177.915 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-24 09:03 | 2022-06-29 17:00 | 2022-06-24 12:00 | 2022-06-29 17:00 | 2022-06-24 13:30 |  |  | Toilet seat was lose replaced clips and refixed seat
MSA-DTWD | WA5567569 | 2 | Lane's Plumbing | Outside farm shed BLD 844 - Standpipe out side - Leaking stand pipe valve | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 1.5 | 2022-06-24 10:31 | 2022-06-29 17:00 | 2022-06-27 10:00 | 2022-06-29 17:00 | 2022-06-27 11:30 |  |  | repairs to leaks
MSA-DFES | WA5567948 | 3 | AWB Co. | Kitchen - Drawer runners have failed -please see details below | Building | General Building | 173.75 | Pass | Pass | -1 | -1 | 1.5 | 2022-06-24 13:54 | 2022-07-01 17:00 | 2022-06-27 13:30 | 2022-07-01 17:00 | 2022-06-27 15:00 |  |  | Removed draw completely and repositioned draw runners and refitted draw.
MSA-DTWD | WA5568899 | 2 | PEEL LOCK SERVICES PTY LTD | B57A - Lock on door will not secure | Security | Locksmith |  | Fail | Fail | 2 | 2 | 1.5 | 2022-06-27 09:59 | 2022-06-30 17:00 | 2022-07-12 12:15 | 2022-06-30 17:00 | 2022-07-12 13:45 |  |  | Repairs to lock
MSA-DCA | WA5570351 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Lift no. 2 (Kitchen Lift) - Kitchen car lift is not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5 | 2022-06-28 09:53 | 2022-06-29 17:00 | 2022-06-28 14:15 | 2022-06-29 17:00 | 2022-06-28 15:45 |  |  | Lift 2 Art-Kitchen-Geared :Lift stopped on level 1 with doors half open, found UCM module tripped with 11 flash sequence, rope brake ok, moved lift and further investigation found locks not making on level 1, adjusted and tested, all ok. Returned to service.
MSA-DCA | WA5571671 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Prep Lab - too high of air pressure | Air Conditioning | Building HVAC Maintenance (Major Plant) | 240.7 | Fail | Fail | 0 | 0 | 1.5 | 2022-06-29 11:13 | 2022-06-29 13:13 | 2022-06-29 15:00 | 2022-06-29 15:13 | 2022-06-29 16:30 |  |  | See work logs
MSA-DTAG | WA5571781 | 2 | O'Brien Glass With Care | Level 2 - Unit/Block 1987 - Ladies & Gents Toilets - Install of small window in (see notes below) | Glazing | Door Glass |  | Fail | Fail | 1 | 1 | 1.5 | 2022-06-29 12:16 | 2022-07-04 17:00 | 2022-07-14 11:00 | 2022-07-04 17:00 | 2022-07-14 12:30 |  |  | Install viewing panels in toilet entry doors
MSA-DFES | WA5583189 | 3 | GRAFFITI FORCE PTY LTD | Ground Floor - External Perimeter South -Graffiti needing removal - See notes below | Cleaning | Graffiti | 307 | Fail | Fail | 1 | 1 | 1.5 | 2022-07-04 10:49 | 2022-07-11 17:00 | 2022-07-15 07:30 | 2022-07-11 17:00 | 2022-07-15 09:00
MSA-DTAG | WA5583258 | 3 | Midolo Building Services | Basement - Custody - Ceiling recess brackets in Cell 4 are loose | Building | Ceiling | 612.45 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-04 11:23 | 2022-07-11 17:00 | 2022-07-06 07:00 | 2022-07-11 17:00 | 2022-07-06 08:30 |  |  | Completed
MSA-DTWD | WA5584757 | 3 | GRAFFITI FORCE PTY LTD | Building perimeter-Graffiti tagging at various locations | Cleaning | Graffiti | 333 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-05 10:11 | 2022-07-12 17:00 | 2022-07-06 11:30 | 2022-07-12 17:00 | 2022-07-06 13:00 |  |  | REMOVAL OF GRAFFITI FROM PERIMETER OF BUILDING
MSA-DFES | WA5585352 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room - Middle fluro light on RHS of engine room is out. Requires new starter. - see notes | Electrical | Lighting, External | 473.895 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-05 15:18 | 2022-07-12 17:00 | 2022-07-12 06:30 | 2022-07-12 17:00 | 2022-07-12 08:00 |  |  | Picked up scissor lift from wholesaler. Attended site and signed in, located faulty fluro light in engine bay room. Used scissor lift to replace tubes and starters. Light now working correctly.Informed staff of job completion.
MSA-DCA | WA5585405 | 2 | GPS Plumbing & Gas Services PtyLtd | Accessible unisex toilet in theatre foyer - Toilet seat broken and falling off | Plumbing & Drainage | Toilets/Cisterns | 303.935 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-05 16:17 | 2022-07-08 17:00 | 2022-07-07 14:55 | 2022-07-08 17:00 | 2022-07-07 16:25 |  |  | Replaced toilet seat in diabled toilet foyer
MSA-DCA | WA5585698 | 0 | Critical Fire Protection & Training | zone 18 coming up with a fire fault | Fire Protection Services | Fire Protection - Monitor System | 287.65 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-06 07:31 | 2022-07-06 09:31 | 2022-07-06 09:20 | 2022-07-06 11:31 | 2022-07-06 10:50 |  |  | Start time: 9:20amFinish time: 10:50amOn arrival found zone 18 in isolated condition. After removing isolate all systems returned to normal operation and zone did not re-enter fault condition. Unable to conduct any further investigations into zone fault as is a conventional system. Zone 18 is high level roof and will require EWP use to reach detectors. Noted detectors heads have red indicator sticker on them and are potentially over 10 years old if they haven’t been replaced since system installation.1x tyco style detector in zone would also recommend replacing with series 65 Ampac detector. 13 detectors in total. Contacted FAMS and notes fault occurred at 03:22 and isolated at 06:04 between isolate time and arrival time fault had cleared itself.
MSA-DTWD | WA5587457 | 3 | AWB Co. | 4F16 - Numerous lights not working - Ceiling is higher than standard. Extra high ladder required | Electrical | Lighting, Internal | 219.795 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-07 08:14 | 2022-07-14 17:00 | 2022-07-13 07:00 | 2022-07-14 17:00 | 2022-07-13 08:30 |  |  | Attended site signed in jsa completed.john showed me what the job was to replace tubes + starters in classroom. all working and tested finejob completed
MSA-DFES | WA5587803 | 2 | AWB Co. | Level 1 - Room 36 - Gym courtyard door stop broken | Building | Doors | 210.105 | Fail | Fail | 1 | 1 | 1.5 | 2022-07-07 10:52 | 2022-07-12 17:00 | 2022-07-20 14:00 | 2022-07-12 17:00 | 2022-07-20 15:30 |  |  | Gate hinges needed adjusting to allow door to shut. Then attached chain from door frame to door to stop door opening to farand bending hinges. Filed out striker plate for latch to lock easily on and lubricated hinges. Cleaned up work area.
MSA-DTAG | WA5587916 | 1 | Australian HVAC Services Pty. Ltd. | Ground Floor - Admin - Heating failure throughout the building | Air Conditioning | Building HVAC Maintenance (Major Plant) | 193.43 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-07 11:43 | 2022-07-08 17:00 | 2022-07-07 14:30 | 2022-07-08 17:00 | 2022-07-07 16:00 |  |  | Attended service call, met with manager who informed me of admin ac 1 temperature issue.& adjustments made on bms. Accessed plantroom & confirmed correct control settings. Tested ac1 & found no fault.
MSA-DTWD | WA5588994 | 3 | Australian Airconditioning Services Pty Ltd | Coil clean on large ice machine | Refrigeration | Ice machine | 309.435 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-08 09:05 | 2022-07-15 17:00 | 2022-07-11 10:00 | 2022-07-15 17:00 | 2022-07-11 11:30 |  |  | complete
MSA-DTWD | WA5589118 | 3 | AWB Co. | Exterior - Drain cover plate needs to be secured | Building | Steel Work | 196.525 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-08 09:49 | 2022-07-15 17:00 | 2022-07-12 07:00 | 2022-07-15 17:00 | 2022-07-12 08:30 |  |  | Secured metal drain cover onto drain. Job complete
MSA-DTWD | WA5589166 | 1 | Damian Rak Electrical Pty Ltd | Level 1 - Hallway - Faulty Light | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1.5 | 2022-07-08 10:21 | 2022-07-11 17:00 | 2022-07-08 13:30 | 2022-07-11 17:00 | 2022-07-08 15:00 |  |  | Repairs to lights
MSA-DTWD | WA5589309 | 2 | AWB Co. | D07-faulty fluro fitting | Electrical | Lighting, Internal | 180.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-08 11:51 | 2022-07-13 17:00 | 2022-07-11 12:00 | 2022-07-13 17:00 | 2022-07-11 13:30 |  |  | Attended site and signed in. Completed JSA. Located D block. Spoke to staff and could not locate room 7. Found a light broken in room 8. Used sites materials to repair light fitting. Put light fitting back together and tested all okay. Signed out. Job complete
MSA-DFES | WA5589503 | 0 | Australian HVAC Services Pty. Ltd. | Ground Floor - SO B/Room 2nd left along hallway - Aircon vent found cracked/ damaged during service | Air Conditioning | Room Air Conditioners | 263.3 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-08 13:32 | 2022-07-08 15:32 | 2022-07-08 15:00 | 2022-07-08 17:32 | 2022-07-08 16:30 |  |  | Oscar Holil (08/07/2022) - Work NoteArrived on site and spoke to site representative about the issue with the AC unit. Was able to order a replacement fan barrel from Daikin. Picked up the fan barrel and returned to site. Isolated the unit and dismantled the unit. Replaced fan barrel and reassemble the unit. Tested operation and found it to be operating correctly. Packed up and left site
MSA-DTWD | WA5597107 | 0 | AWB Co. | Bifold Doors is not opening - Electrical door - See notes below | Equipment | Electrical Equipment | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-11 12:01 | 2022-07-11 14:01 | 2022-07-11 13:00 | 2022-07-11 16:01 | 2022-07-11 14:30 |  |  | Attended site signed in jsa completed. Tested from board to isolator and found power 426v across the board. e stops functioning correctly which was a previous job. upon inspection of motor removed case for emergency stop chain and found it had pulled a limit switch in. This was done on the weekend works by concrete grinder company who had pulled on it to open as they were not aware of electric motor. Un spooled chain and reset correctly now roller door goes up and down no problems. Educated staff of this and Dennis campus manager. job is completed
MSA-DCA | WA5597458 | 3 | FCT SURFACE CLEANING | External Ground - Urban Orchard - Graffiti in urban orchard area | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.5 | 2022-07-11 13:22 | 2022-07-18 17:00 | 2022-07-18 11:45 | 2022-07-18 17:00 | 2022-07-18 13:15 |  |  | Removed graffiti from urban orchard area.
MSA-DTAG | WA5603420 | 2 | Sapio Pty Ltd | Level 14 - Room 14.05 - issues with swipe reader - not working | Security | Access Control | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-12 10:30 | 2022-07-15 17:00 | 2022-07-13 08:30 | 2022-07-15 17:00 | 2022-07-13 10:00 |  | WACCES | Reterminated card reader and connection, tested, all OK.
MSA-DTWD | WA5603949 | 3 | AWB Co. | Replace Fluro tubes | Electrical | Lighting, Internal | 226.175 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-12 14:26 | 2022-07-19 17:00 | 2022-07-18 09:30 | 2022-07-19 17:00 | 2022-07-18 11:00 |  |  | Attended site and signed in. Completed JSA. Located faulty lights. Supply and replace tubes and starters to all lights out in room. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5604012 | 3 | AWB Co. | Lights not working in passageway - Ceiling is a lot higher than standard. Extra high ladder required | Electrical | Lighting, Internal | 216.605 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-12 14:58 | 2022-07-19 17:00 | 2022-07-13 08:30 | 2022-07-19 17:00 | 2022-07-13 10:00 |  |  | Attended site signed in jsa completed.john showed me what the job was to replace tubes + starters in office . all working and tested finejob completed
MSA-DTWD | WA5608338 | 3 | AWB Co. | LED Light now working - Ceiling light is waterproof baton | Electrical | Lighting, Internal | 194.275 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-13 08:04 | 2022-07-20 17:00 | 2022-07-13 10:00 | 2022-07-20 17:00 | 2022-07-13 11:30 |  |  | Attended site signed in jsa completed. Found led light not working. Took it apart and found cable out of terminal. Pushed back in and tested operation and it worked. job completed
MSA-DTWD | WA5608348 | 2 | Techworks Electrical | Planning and Evaluating office - Flickering Light | Electrical | Lighting, Internal | 252.055 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-13 08:09 | 2022-07-18 17:00 | 2022-07-13 14:00 | 2022-07-18 17:00 | 2022-07-13 15:30 |  |  | Replaced faulty lighting throughout, replaced 8x 36w tubes in various lights
MSA-DTWD | WA5612521 | 2 | Protek 24/7 Building & Maintenance | Water leak from ceiling, water running down the back of the wall in several areas | Roofing | Metal Roofing | 339.46 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-14 11:50 | 2022-07-19 17:00 | 2022-07-19 07:30 | 2022-07-19 17:00 | 2022-07-19 09:00 |  |  | Repaired roof leak
MSA-DTAG | WA5627909 | 3 | Midolo Building Services | Coroners court registry - Cupboard door off railings | Building | Doors | 216.49 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-15 09:08 | 2022-07-22 17:00 | 2022-07-18 07:30 | 2022-07-22 17:00 | 2022-07-18 09:00 |  |  | repairs made to door/re secured/new fixings
MSA-DTAG | WA5628123 | 2 | Water2water Pty Ltd | Reception - Bill filtration unit system no hot water | Plumbing & Drainage | HWS/Units Electric & Gas | 435.58 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-15 11:16 | 2022-07-20 17:00 | 2022-07-19 14:05 | 2022-07-20 17:00 | 2022-07-19 15:35 |  |  | Replaced failed hot pump to restore hot water flow
MSA-DTWD | WA5656030 | 3 | AWB Co. | 2 x GPO's hanging off skirting | Electrical | General Electrical | 396.72 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-18 11:24 | 2022-07-25 17:00 | 2022-07-22 07:30 | 2022-07-25 17:00 | 2022-07-22 09:00 |  |  | Attended site and signed in, completed jsa, located GPOs in e227 , went to wholesaler to pick up materials , returned to site, isolated power circuit, removed damaged GPOs and replaced with new, re energised circuit , tested gpos and working as intended , cleaned up, packed up, completed paperwork, signed out, ***job completed***
MSA-DTWD | WA5656599 | 3 | PEEL LOCK SERVICES PTY LTD | Faulty Lock needs replacing | Security | Locksmith |  | Pass | Pass | -1 | -1 | 1.5 | 2022-07-18 15:12 | 2022-07-25 17:00 | 2022-07-20 12:00 | 2022-07-25 17:00 | 2022-07-20 13:30 |  |  | Job completed - replaced 2x locks
MSA-DCA | WA5660403 | 3 | FCT SURFACE CLEANING | Ground External - graffiti on external side of Fiji room door. Cleaners cannot remove | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 1.5 | 2022-07-19 09:33 | 2022-07-26 17:00 | 2022-07-19 14:00 | 2022-07-26 17:00 | 2022-07-19 15:30 |  |  | Job completed - Removed blue graffiti from external side of Fiji room door.
MSA-DCA | WA5660509 | 2 | Techworks Plumbing | Geologist building - Ground Floor - Male Toilet - Toilet cistern constantly running | Plumbing & Drainage | Toilets/Cisterns | 334.74 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-19 10:14 | 2022-07-22 17:00 | 2022-07-22 09:00 | 2022-07-22 17:00 | 2022-07-22 10:30 |  |  | attended site and signed in at security officewent to the geology building male toilets and inspected the toilet issue.we found that the flush was not working and when you hold the button down the cistern would let water seep through into the toilet bowl making the cistern constantly runso we removed the push button assembly and fixed the flush by reattaching the plastic pulley that pulls the flush valve open because it had somehow come loose once we had done this we put the push button assembly back on and tested the flush it is now flushing how it should and the cistern is not running we left site and got a signature slipcompleted paperwork
MSA-DTWD | WA5660579 | 2 | AWB Co. | AC unit has no power unable to find power supply | Electrical | General Electrical | 288.22 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-19 10:49 | 2022-07-22 17:00 | 2022-07-21 10:00 | 2022-07-22 17:00 | 2022-07-21 11:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, tried to located circuit in switch board, couldn’t find in main switch board, went out and looked at outdoor unit and checked if isolator was on , followed cables back to board in plant room, board had been isolated, re energised circuit for ac and tested, everything working as intended, completed paperwork, packed up, signed out **job completed**
MSA-DFES | WA5672939 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - End cubicle toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 345.64 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-20 10:45 | 2022-07-27 17:00 | 2022-07-27 08:45 | 2022-07-27 17:00 | 2022-07-27 10:15 |  |  | Serviced toilet cistern
MSA-DTWD | WA5673117 | 3 | Falcetta Plumbing and Gas | Female Student Toilet - Toilet out of order | Plumbing & Drainage | Toilets/Cisterns | 266.925 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-20 12:19 | 2022-07-27 17:00 | 2022-07-20 17:00 | 2022-07-27 17:00 | 2022-07-20 18:30 |  |  | repaired in-wall invisi cistern
MSA-DTWD | WA5673125 | 2 | AWB Co. | Between F & H Blocks - Adjust Motion Light sensor to stay on | Electrical | General Electrical | 194.275 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-20 12:24 | 2022-07-25 17:00 | 2022-07-21 09:30 | 2022-07-25 17:00 | 2022-07-21 11:00 |  |  | Attended site signed in jsa completed. Office staff complaining about motion sensor in office keeps turning lights off. Bypassed sensor to a switch only. Works fine now with no interuptions.Job completed
MSA-DTWD | WA5673261 | 3 | BAKE-QUIP PTY LTD | Combi Oven not working | Electrical | General Electrical | 731.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-20 13:28 | 2022-07-27 17:00 | 2022-07-20 13:30 | 2022-07-27 17:00 | 2022-07-20 15:00 |  |  | Refer to service report
MSA-DTWD | WA5674227 | 2 | Techworks Electrical | Pan room-room lights not working | Electrical | Lighting, Internal | 406.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-21 09:43 | 2022-07-26 17:00 | 2022-07-25 09:00 | 2022-07-26 17:00 | 2022-07-25 10:30 |  |  | Replaced 4 x T5 28w tubes and 1 electronic ballast. In Mclarty pan room
MSA-DTWD | WA5674311 | 2 | Protek 24/7 Building & Maintenance | Roof leak in centre of room over guillotine- Possible skylight roof sheet deterioration | Roofing | Metal Roofing | 317.46 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-21 10:34 | 2022-07-26 17:00 | 2022-07-25 13:30 | 2022-07-26 17:00 | 2022-07-25 15:00 |  |  | Replaced rubbers on poly carb screws with new - Re torque loose screws - Re fix down ridge flashing
MSA-MRWA | WA5674762 | 1 | AWB Co. | Lights out in office | Electrical | Lighting, Internal | 288.22 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-21 13:46 | 2022-07-22 17:00 | 2022-07-22 06:00 | 2022-07-22 17:00 | 2022-07-22 07:30 |  |  | Attended site and signed in. Completed JSA. Located faulty lighting on level 2. Took down 2 lights that weren’t working in office. Took down 2 lights in corridor to swap over to make sure it wasn’t a programming issue. Replaced drivers in 2x fittings. Installed 2 working lights into office. 2 other light wouldn’t work, this is a programming issue. They have been put in the corridor. Called Danika to explain the issue and that she has to get a programmer out. Took pics. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5674856 | 1 | AWB Co. | Power point keeps sparking needs to be checked. | Electrical | General Electrical | 312.01 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-21 14:45 | 2022-07-22 17:00 | 2022-07-22 13:00 | 2022-07-22 17:00 | 2022-07-22 14:30 |  |  | Attended site and signed in. Completed JSA. Located faulty plug top on coffee machine. Been recently tagged but not sure how. Plug is poorly installed. Supply and replaced with proper plug top and correct connections. Located faulty gpo sparking with microwave. Found to be broken inside. Supply and replace with new double D all okay. Signed out. Job complete
MSA-DTWD | WA5676362 | 2 | Techworks Electrical | Q Block - Pan Room - room lights not working | Electrical | Lighting, Internal | 389.71 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-25 08:01 | 2022-07-28 17:00 | 2022-07-25 13:30 | 2022-07-28 17:00 | 2022-07-25 15:00 |  |  | Replaced 8x fluro tubes and starters in Pan room kendrew campus.
MSA-DFES | WA5676552 | 2 | AWB Co. | Engine Room Roof - Leak in roof - See notes below | Roofing | Metal Roofing | 366.56 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-25 09:18 | 2022-07-28 17:00 | 2022-07-26 14:20 | 2022-07-28 17:00 | 2022-07-26 15:50 |  |  | Investigated leak above damage.found issues around apron flashing silicone and fixings.found issue with cable fixings over area.carried out repairs
MSA-DTWD | WA5676768 | 3 | Protek 24/7 Building & Maintenance | Ladies toilet near B244 - Lino from floor to lower wall peeling away | Flooring | Vinyl | 344.96 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-25 10:23 | 2022-08-01 17:00 | 2022-07-29 11:30 | 2022-08-01 17:00 | 2022-07-29 13:00 |  |  | Repaired peeling Lino
MSA-DTWD | WA5676804 | 1 | Protek 24/7 Building & Maintenance | F1 - Roof - Roof Leak -See notes below | Roofing | Metal Roofing | 321.88 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-25 10:47 | 2022-07-26 17:00 | 2022-07-25 13:45 | 2022-07-26 17:00 | 2022-07-25 15:15 |  |  | Sealed ridge vent joints
MSA-DTWD | WA5677074 | 1 | Techworks Plumbing | External service compound front elevation - Water escaping from top of electric Rheem storage heater | Plumbing & Drainage | Water | 183 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-25 12:24 | 2022-07-26 17:00 | 2022-07-25 13:30 | 2022-07-26 17:00 | 2022-07-25 15:00 |  |  | attended site and signed in at front desk, they showed me where the hot water units were the first hot water unit when the valve is turned on water run out of the top of it as shown in the photos, I have isolated the valves and turned off the power, there is an out of order tag on it.unit will have to be replaced the second one by the looks of it is also not far off doing the same thing would also be good to change it over while we are doing the other one and redo the pipe work to suit so it is all new. signed out and left site completed paperwork
MSA-DFES | WA5677874 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Firefighter changeroom - 2x faulty Fluro Lights - See notes below | Electrical | Lighting, Internal | 477.33 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-26 08:11 | 2022-08-02 17:00 | 2022-08-02 09:45 | 2022-08-02 17:00 | 2022-08-02 11:15 |  |  | Arrived on site at 945. Located faulty lights. Left site to collect new lights. Arrived back on site and replaced faulty lights with new. Left site at 1115
MSA-DTWD | WA5677961 | 3 | AWB Co. | A51 - Light with broken tombstone | Electrical | Lighting, Internal | 194.275 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-26 08:42 | 2022-08-02 17:00 | 2022-07-26 13:00 | 2022-08-02 17:00 | 2022-07-26 14:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, got materials from h block and located faulty lighting, replaced tombstones, tubes and starters , all lights working as intended, completed paperwork, signed out**job completed **
MSA-DTAG | WA5679041 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground floor registry - 3x female staff toilets blocked - See notes below | Plumbing & Drainage | Toilets/Cisterns | 191.445 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-26 10:13 | 2022-07-27 17:00 | 2022-07-26 12:00 | 2022-07-27 17:00 | 2022-07-26 13:30 |  |  | cleared blockage in female toilets
MSA-DFES | WA5679500 | 2 | AWB Co. | ground dorm 3 bathroom-water leaking through vent above sink in dorm 3 bathroom when raining | Roofing | Metal Roofing | 314.73 | Fail | Fail | 1 | 1 | 1.5 | 2022-07-26 14:23 | 2022-07-29 17:00 | 2022-08-02 13:45 | 2022-07-29 17:00 | 2022-08-02 15:15 |  |  | Investigated area above leak. Found the ends of roof sheets were not weathered properly. Carried out works turneddown sheets. found no other issues
MSA-DTAG | WA5680367 | 3 | Midolo Building Services | Level 1 kitchen cupboard coming away from wall | Building | Doors | 205.05 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-27 11:37 | 2022-08-03 17:00 | 2022-07-29 12:15 | 2022-08-03 17:00 | 2022-07-29 13:45 |  |  | KITCHEN CUPBOARD RESECURED TO WALL
MSA-DTWD | WA5681139 | 3 | AWB Co. | Replace light not working | Electrical | Lighting, Internal | 305.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-28 09:25 | 2022-08-04 17:00 | 2022-08-02 11:45 | 2022-08-04 17:00 | 2022-08-02 13:15 |  |  | Attended site and signed in. Completed JSA. Located faulty lighting. Replaced tubes and starters in room225. Took pictures. Everything working as intended. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5681313 | 2 | AWB Co. | Replace light not working A256 | Electrical | Lighting, Internal | 207.035 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-28 11:11 | 2022-08-02 17:00 | 2022-07-29 09:00 | 2022-08-02 17:00 | 2022-07-29 10:30 |  |  | Attended site and signed in. Completed JSA. Located A 256 staff room. Found lights out in the office. Supply and replaced lamps and starters as required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5681320 | 2 | AWB Co. | Lights not working in N227 | Electrical | Lighting, Internal | 302.94 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-28 11:13 | 2022-08-02 17:00 | 2022-07-29 07:15 | 2022-08-02 17:00 | 2022-07-29 08:45 |  |  | Attended site and signed in. Completed JSA. located all faulty lighting . Replaced all tubes and starters. Took pics.completed paperwork. Signed out.Job complete
MSA-DTWD | WA5681411 | 2 | AWB Co. | Light in Female Toilet A Block Level 2 near library needs replacing | Electrical | Lighting, Internal | 209.195 | Pass | Pass | -1 | -1 | 1.5 | 2022-07-28 11:47 | 2022-08-02 17:00 | 2022-07-29 07:30 | 2022-08-02 17:00 | 2022-07-29 09:00 |  |  | Attended site and signed in. Completed JSA. Located female toilets as described on job and found lights to be working. Supply and replaced lamps. Checked out job notes as no facilities on site and spoke with cleaners and they advised female toilets at the other end of the A block are flashing. Went over there and found lights out. Supply and replace lamps to those toilets. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5681450 | 1 | AWB Co. | Student dinning room - Power point / USB charging point broken | Electrical | General Electrical | 205.975 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-28 12:00 | 2022-07-29 17:00 | 2022-07-29 07:00 | 2022-07-29 17:00 | 2022-07-29 08:30 |  |  | Attended site signed in jsa completed.found broken gpo as john had showed me in diner. Blanked off as requested by john and put B30 label. job completed
MSA-DTWD | WA5682241 | 1 | AWB Co. | bad roof leak | Roofing | Metal Roofing | 314.73 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-29 07:41 | 2022-07-29 17:00 | 2022-07-29 08:00 | 2022-07-29 17:00 | 2022-07-29 09:30 |  |  | Attended as per signature slip and un clogged outlets, site to monitor, if leak continued further investigation may berequired.
MSA-DTWD | WA5682611 | 2 | AWB Co. | South east corner - roof leak | Building | Ceiling | 340.73 | Pass | Pass | 0 | 0 | 1.5 | 2022-07-29 10:13 | 2022-08-03 17:00 | 2022-08-03 11:45 | 2022-08-03 17:00 | 2022-08-03 13:15 |  |  | Investigated roof leak found loose screws. Lifted multiple sheets found little damp patches nothing major may be a buildup issue .Site to monitor
MSA-DCA | WA5683073 | 2 | FCT SURFACE CLEANING | ground-Electrical substation, by Francis St footpath-graffiti tags x2 | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.5 | 2022-07-29 15:48 | 2022-08-03 17:00 | 2022-08-02 10:00 | 2022-08-03 17:00 | 2022-08-02 11:30 |  |  | Removed graffiti from State Library of WA Electrical substation, by Francis St footpath.
MSA-DTWD | WA5686709 | 2 | Equans Mechanical Services Australia | F30 - Air Con, on/off wall switch not working | Air Conditioning | Room Air Conditioners | 174.555 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-01 10:22 | 2022-08-04 17:00 | 2022-08-01 12:30 | 2022-08-04 17:00 | 2022-08-01 14:00 |  |  | FAULT CAUSED BY WATER - REMOVED COVER AND CLEANED, DRIED AND RESEALED - OK
MSA-DFES | WA5686795 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Circuit 12 On electrical board continuously tripping out | Electrical | Distribution Board | 342.64 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-01 10:37 | 2022-08-04 17:00 | 2022-08-02 13:30 | 2022-08-04 17:00 | 2022-08-02 15:00 |  |  | Arrived on site at 13:30 to investigate power tripping on circuit R12. Found gpo mounted externally to have water damage. Replaced gpo and tested all ok. Informed staff of works and left site at 1500.
MSA-DTWD | WA5686799 | 2 | Protek 24/7 Building & Maintenance | Bistro entrance - Fault description Roof leak in front of Cake Display Fridge at Bistro Counter-note | Roofing | Metal Roofing | 266.3 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-01 10:49 | 2022-08-04 17:00 | 2022-08-02 10:30 | 2022-08-04 17:00 | 2022-08-02 12:00 |  |  | Repaired roof leak
MSA-DTWD | WA5687091 | 2 | Protek 24/7 Building & Maintenance | Roof leak – dripping through skylight | Roofing | Metal Roofing | 309.83 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-01 13:01 | 2022-08-04 17:00 | 2022-08-02 13:30 | 2022-08-04 17:00 | 2022-08-02 15:00 |  |  | Re sealed cracked silicon
MSA-DFES | WA5687167 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Tap in FF toilet sink is leaking. | Plumbing & Drainage | Water | 210.78 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-01 13:50 | 2022-08-08 17:00 | 2022-08-05 13:30 | 2022-08-08 17:00 | 2022-08-05 15:00 |  |  | attended site to investigate leaking tap in toilet at fire station. found leaking tap isolated water under vanity, serviced hot and cold taps on basin all tested all ok
MSA-DFES | WA5689933 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | ground main foyer-cover on light broken - see notes | Electrical | Lighting, Internal | 278.95 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-02 15:21 | 2022-08-05 17:00 | 2022-08-05 11:45 | 2022-08-05 17:00 | 2022-08-05 13:15 |  |  | Arrived on site at 1145 to investigate ground main foyer-cover on light broken. Obtained keys for vols shed and located damaged light. Signed out and left to wholesaler at 1215. Returned to site at 1245 and replaced/reenergised light. Informed staff of completed works and left site at 1315.
MSA-DFES | WA5692022 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Fluros need replacing - See notes below | Electrical | Lighting, Internal | 253.95 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-03 09:43 | 2022-08-08 17:00 | 2022-08-05 11:30 | 2022-08-08 17:00 | 2022-08-05 13:00 |  |  | Arrived on site at 11:30. Replaced 2 x blown tubes in country operations and replaced 2 x blown tubes in the doss office. Left site at 13:00
MSA-DCA | WA5692267 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Old Gaol - General operations admin areas - FCU OG.05 unit is out of service | Air Conditioning | Building HVAC Maintenance (Major Plant) | 202.705 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-03 11:40 | 2022-08-08 17:00 | 2022-08-03 14:30 | 2022-08-08 17:00 | 2022-08-03 16:00 |  |  | Attended site. Unit labelled incorrectly, troubled unit is actually fcu OG-06. Investigated unit not operating. Found controller settings had been adjusted, which blanked the screen and gave limited functions. Reprogrammed controller and tested. Found unit had no control. Adjusted bms settings to occupied for both time schedule and plant mode. Unit now operates with the time schedule and temp controlled locally through the controller on the unit. All ok. Completed paperwork.
MSA-DCA | WA5693290 | 0 | Techworks Electrical | Anthropology & History Office - Lights in area are not working | Electrical | Lighting, Internal | 426.65 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-04 11:09 | 2022-08-04 13:09 | 2022-08-04 12:00 | 2022-08-04 15:09 | 2022-08-04 13:30 |  |  | Replaced switch mechs and altered wiring in switch so two way switching works properly
MSA-DTWD | WA5693332 | 2 | AWB Co. | Flickering Fluoros - Up high | Electrical | Lighting, Internal | 256.775 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-04 11:30 | 2022-08-09 17:00 | 2022-08-09 11:00 | 2022-08-09 17:00 | 2022-08-09 12:30 |  |  | Attended site and signed in. Completed JSA. Located faulty lights and replaced with site supplied tubes and starters to fluros down the back of hair dressing. Supplied and replace downlight in foyer with new led fitting. Tested all okay. Signed out. Job complete
MSA-DFES | WA5693809 | 3 | AWB Co. | Radio Comms various Offices-stains on ceiling - see notes | Building | Ceiling | 181.575 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-04 15:31 | 2022-08-11 17:00 | 2022-08-10 11:30 | 2022-08-11 17:00 | 2022-08-10 13:00 |  |  | repair ceiling tiles
MSA-DFES | WA5693810 | 3 | AWB Co. | Plant Room door has warped and does not close properly | Building | Doors | 133.155 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-04 15:31 | 2022-08-11 17:00 | 2022-08-10 11:30 | 2022-08-11 17:00 | 2022-08-10 13:00 |  |  | Planed and adjusted door
MSA-DTAG | WA5694399 | 3 | Midolo Building Services | Level 4 -Adult Community Corrections wall leading into Kitchen- skirting board damaged - See notes | Building | Internal Walls | 311.72 | Fail | Fail | 1 | 1 | 1.5 | 2022-08-05 09:47 | 2022-08-12 17:00 | 2022-08-19 12:30 | 2022-08-12 17:00 | 2022-08-19 14:00 |  |  | WALL REPAIRED & SKIRTING RE-ATTACHED
MSA-DCA | WA5694579 | 1 | EQUANS Mechanical Services (WA) Pty Limited | RETROPSECTIVE WORK ORDER - Exhaust Fan Fault | Electrical | General Electrical | 202.705 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-05 11:35 | 2022-08-08 17:00 | 2022-08-05 12:00 | 2022-08-08 17:00 | 2022-08-05 13:30 |  |  | Investigated fault with EF B1-01 holding out gas to stove top. Found emergency stop button had been pressed, released and cleared fault from bms. Tested operation of fan, all ok. Stovetop isolation valve opened and operating in series with fan. Completed paperwork.
MSA-DCA | WA5694895 | 1 | Techworks Plumbing | Level 3 - Male Toilet - Repair/replace broken toilet flush button/mechanism | Plumbing & Drainage | Toilets/Cisterns | 191.16 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-05 14:26 | 2022-08-08 17:00 | 2022-08-05 14:30 | 2022-08-08 17:00 | 2022-08-05 16:00 |  |  | Arrived on site and signed in at security desk.Located the broken toilet flush button and removed.Once removed I could see that the spring had been snapped off.I then went back down to security to get them to open up our locker with spare parts. Found the correct toilet flush button.Went back to the toilet that needed the button and re installed a new one. Tested multiple times to make sure it flushed properly.Returned to security and signed out.
MSA-DTWD | WA5696138 | 3 | AWB Co. | ground - 7G14 Kitchen wash area - Faulty double PowerPoint | Electrical | General Electrical | 296.35 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-08 09:58 | 2022-08-15 17:00 | 2022-08-09 13:00 | 2022-08-15 17:00 | 2022-08-09 14:30 |  |  | attended site signed in jsa completed.found broken gpo in dishwashing bay. removed gpo and found broken terminal behind. Replaced with new and tested operation.Job completed
MSA-DTWD | WA5696401 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 303.58 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-08 11:23 | 2022-08-09 17:00 | 2022-08-08 13:30 | 2022-08-09 17:00 | 2022-08-08 15:00 |  |  | cleaned Gutters and pipes Advised by the site to close job out as first fix as gutters are unblocked they do not want us to do a tree prune
MSA-DTWD | WA5696561 | 3 | AWB Co. | Entry area near N423 - Water leak -Entry area near RM N423. | Roofing | Metal Roofing | 353.23 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-08 12:48 | 2022-08-15 17:00 | 2022-08-15 10:00 | 2022-08-15 17:00 | 2022-08-15 11:30 |  |  | Sourced leaks cracked membrane all along stepOver sealed all cracks and splits on membrane . As was shown by staff
MSA-DTWD | WA5696593 | 3 | GRAFFITI FORCE PTY LTD | Graffiti Leadlight Lane Gate | Cleaning | Graffiti | 359 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-08 13:07 | 2022-08-15 17:00 | 2022-08-11 09:30 | 2022-08-15 17:00 | 2022-08-11 11:00 |  |  | REMOVAL OF GRAFFITI FROM LEAD LIGHT LANE GATE
MSA-DTWD | WA5696822 | 2 | AWB Co. | E200 steel store-roof leaks above band saw | Roofing | Metal Roofing | 358.06 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-08 15:00 | 2022-08-11 17:00 | 2022-08-11 11:30 | 2022-08-11 17:00 | 2022-08-11 13:00 |  |  | Cleaned and re-sealed apron flashing seals and decktites
MSA-DFES | WA5696873 | 1 | Australian HVAC Services Pty. Ltd. | COMs office - Server room -Air con faulty - See notes below | Air Conditioning | Room Air Conditioners | 139.94 | Fail | Fail | 0 | 0 | 1.5 | 2022-08-08 16:09 | 2022-08-09 17:00 | 2022-08-10 11:30 | 2022-08-09 17:00 | 2022-08-10 13:00 |  |  | Rhys Hall (10/08/2022) - Work NoteUnit has a fault, unable to work on the ac due to it being installed by another company 2 months ago and still being under warranty.
MSA-DTWD | WA5697329 | 2 | AWB Co. | ground-Fault description External passageway lights not working | Electrical | General Electrical | 224.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-09 08:42 | 2022-08-12 17:00 | 2022-08-11 14:00 | 2022-08-12 17:00 | 2022-08-11 15:30 |  |  | Attended site and signed in. Completed JSA. Located lights not coming on at night outside the A block, turned on all overrides and found those lights not coming. Located the feed and found to be off. Reset and replaced all faulty lamps in the walkway. Tested all okay. Signed out. Job complete
MSA-DCA | WA5698021 | 2 | Techworks Electrical | First Floor - Electrical Cupboard -Constant Beeping coming from cabinet inside cupboard | Electrical | General Electrical | 183.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-09 13:47 | 2022-08-12 17:00 | 2022-08-11 15:00 | 2022-08-12 17:00 | 2022-08-11 16:30 |  | WACCES | Investigated beeping in cupboard. Found to be the UPS. Spoke to the company service department and advised me the batteries needed replacing. Sourced new batteries will need to take apart ups on return as the old batteries have swollen and will not come out
MSA-DTWD | WA5698159 | 2 | Protek 24/7 Building & Maintenance | ground 3B library - Water leak at entrance | Building | Ceiling | 338.26 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-09 15:05 | 2022-08-12 17:00 | 2022-08-10 07:00 | 2022-08-12 17:00 | 2022-08-10 08:30 |  |  | Installed temp flashing to stop/ slow water, will order newBRAF Declined
MSA-DCA | WA5699154 | 0 | EQUANS Mechanical Services (WA) Pty Limited | boiler in fault | Mechanical Services | Boilers | 371.62 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-10 07:26 | 2022-08-10 09:26 | 2022-08-10 08:00 | 2022-08-10 11:26 | 2022-08-10 09:30 |  |  | Attended site. Investigated temperature complaints in the admin building. Found boiler had faulted on no flame fault. Reset and tested operation. Checked over bms for space temps and operation of heating valve actuators, all ok. Checked boilers in collections. Both operational. Completed paperwork.
MSA-DTWD | WA5699519 | 2 | Lane's Plumbing | Faulty taps | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 1.5 | 2022-08-10 09:59 | 2022-08-15 17:00 | 2022-08-11 09:30 | 2022-08-15 17:00 | 2022-08-11 11:00 |  |  | repairs to taps
MSA-DTWD | WA5699904 | 2 | AWB Co. | There is a roof leak in O007 | Roofing | Metal Roofing | 335.73 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-10 12:57 | 2022-08-15 17:00 | 2022-08-15 09:30 | 2022-08-15 17:00 | 2022-08-15 11:00 |  |  | Investigated area above leak.only issue we could see is the window seals completely worn out with moss growing out of them.scraped all moss off and sealed windows
MSA-DTWD | WA5700000 | 2 | AWB Co. | External walkway - next to lift - Fluro light not working,see notes | Electrical | Lighting, External | 239.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-10 14:04 | 2022-08-15 17:00 | 2022-08-15 13:30 | 2022-08-15 17:00 | 2022-08-15 15:00 |  |  | Attended site and signed in. Completed JSA. Located lift area and found pe cell for the lights. Covered and nothing came on. Checked power from switchboard and found all to be okay. Removed pe cell and found to be blown and broken. Supply and replaced with new pe cell. Tested light under walkway working. Light at lift not working. Supply and replaced lamp at the lift. Tested all lights working. Notified site of works. Signed out. Job complete
MSA-DFES | WA5700063 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Secure electrical wiring in complaint conduit as reported | Electrical | General Electrical | 406.26 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-10 14:43 | 2022-08-15 17:00 | 2022-08-12 12:45 | 2022-08-15 17:00 | 2022-08-12 14:15 |  |  | complete
MSA-DTWD | WA5706102 | 3 | Protek 24/7 Building & Maintenance | Water leak next to switchboard | Roofing | Metal Roofing | 330.73 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-11 08:45 | 2022-08-18 17:00 | 2022-08-17 11:00 | 2022-08-18 17:00 | 2022-08-17 12:30 |  |  | Valley tray and gutter join has separatedClean, resecure and reseal join
MSA-DTWD | WA5706367 | 2 | Protek 24/7 Building & Maintenance | East exit door frame uneven making it hard to open near control room | Building | Doors | 169.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-11 10:51 | 2022-08-16 17:00 | 2022-08-16 07:30 | 2022-08-16 17:00 | 2022-08-16 09:00 |  |  | Assess issue with door on call out Braf Declined
MSA-DCA | WA5706759 | 0 | EQUANS Mechanical Services (WA) Pty Limited | L1-Air con not turning on have tried resetting system | Air Conditioning | Room Air Conditioners | 202.705 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-11 13:46 | 2022-08-11 15:46 | 2022-08-11 14:00 | 2022-08-11 17:46 | 2022-08-11 15:30 |  |  | Attended site. Investigated 4x ahu not running. Found stagedoor had tried to reschedule on global schedules and didn't clear alarms. Cleared alarms and checked status. All switched to occupied and started operation. Adjusted temps and confirmed operation, all ok. Completed paperwork.Will get a job raised for Honeywell to investigate scheduling issues further. Will monitor on maintenance. Unsure if it’s operator error or bacnet is failing.
MSA-DFES | WA5706783 | 1 | Go Doors | Ground Floor - Pump Room - Issues with Roller Door - See notes below | Building | Roller Shutters | 372.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-11 13:56 | 2022-08-12 17:00 | 2022-08-12 13:45 | 2022-08-12 17:00 | 2022-08-12 15:15 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5714742 | 3 | Go Doors | side gate closes after only 5 seconds - see notes | Building | Steel Fencing & Gates | 372.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-12 08:09 | 2022-08-19 17:00 | 2022-08-15 12:30 | 2022-08-19 17:00 | 2022-08-15 14:00 |  |  | Completed works. Please see attachments.
MSA-DTAG | WA5714950 | 1 | Sapio Pty Ltd | Level 2 - Basement Entry Door - Door closing incorrectly causing alarm activation in security system | Building | Security Doors | 204.44 | Fail | Fail | 0 | 0 | 1.5 | 2022-08-12 09:39 | 2022-08-15 17:00 | 2022-08-16 08:30 | 2022-08-15 17:00 | 2022-08-16 10:00 |  |  | Found Car Park door not closing properly. Adjusted door closer and tightened mortise lock. Door closing properly now.Job completed.
MSA-DTWD | WA5715383 | 2 | AHS Services WA Pty Ltd (Anchor) | Water leak under sink in S210 | Plumbing & Drainage | Water | 177.915 | Fail | Fail | 0 | 0 | 1.5 | 2022-08-12 14:37 | 2022-08-17 17:00 | 2022-08-19 10:10 | 2022-08-17 17:00 | 2022-08-19 11:40 |  |  | Completed
MSA-DTWD | WA5734870 | 3 | Water2water Pty Ltd | Water fountain leaking | Plumbing & Drainage | Water | 4519.67 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-16 10:04 | 2022-08-23 17:00 | 2022-08-18 09:00 | 2022-08-23 17:00 | 2022-08-18 10:30 |  |  | Unit needs replacing. Leaking water tank and compressor failure
MSA-DTWD | WA5734953 | 1 | Total Security Systems Pty Ltd | H3 old canteen - Deactivate panic button 0945 Zone 8 / activated today | Security | Security Management System | 315 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-16 10:27 | 2022-08-17 17:00 | 2022-08-16 14:30 | 2022-08-17 17:00 | 2022-08-16 16:00 |  |  | 16/8/2022 - Michael Higginbotham - 2.30pm to 4pmLocated intruder alarm panel in f block next to switchboard not on Gallagher system.Disconnected panic button in field and disconnected inside panel and bridged out zone with resistor.Updated setup with monitoring company.
MSA-DTWD | WA5735668 | 2 | AWB Co. | faulty 3 phase 5 pin gpo | Electrical | General Electrical | 288.22 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-16 14:23 | 2022-08-19 17:00 | 2022-08-18 09:45 | 2022-08-19 17:00 | 2022-08-18 11:15 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Went to work area and spoke to lecturer about job. He explained that 3 phase outlet had dropped a phase and there was a faulty GPO at front of classroom. Pulled cover off and tested for voltage. Found that blue phase connection was loose. Reterminate and Tighten everything up. Re tested. Tested as intended. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5749391 | 2 | Critical Fire Protection & Training | Southern Hall , Hughes Hall and Southern Hall - Foyers - Faulty Panels | Fire Protection Services | Fire Protection - Monitor System | 151.95 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-17 08:39 | 2022-08-22 17:00 | 2022-08-22 12:30 | 2022-08-22 17:00 | 2022-08-22 14:00 |  |  | Attended site to investigate faulty fire panels. On arrival noted neither panels in both Hughes and southern hall buildings in fault. Conducted operational test on system to confirm correct cause and effect triggers from fire panels to EWIS panel in both building. Hughes building fire alarm trigger operates EWIS as intended and when following instructions to place EWIS into manual to silence tones all systems operate as intended.Southern hall building fire alarm trigger operates EWIS as intended and when following panel instructions to place EWIS in manual to silence all tones all systems operating as intended. Recommend replacing panels on site due to age and intermittent faults occurring.
MSA-MRWA | WA5749961 | 1 | Water2water Pty Ltd | kitchenette HWU has stopped working | Plumbing & Drainage | Water | 220.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-17 09:12 | 2022-08-18 17:00 | 2022-08-17 14:00 | 2022-08-18 17:00 | 2022-08-17 15:30 |  |  | System has no power on arrival. Drained system and removed tap. Re connected all wiring looms on system. Seems to be the main power connection on the rear pcb board. Re calibrated unit and waited to fill. Normal operation
MSA-DFES | WA5750598 | 3 | AHS Services WA Pty Ltd (Anchor) | Trough near washing machine has a leaking tap | Plumbing & Drainage | Water | 345.615 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-17 10:05 | 2022-08-24 17:00 | 2022-08-19 08:15 | 2022-08-24 17:00 | 2022-08-19 09:45 |  |  | Completed
MSA-DTWD | WA5753126 | 1 | Dormakaba Australia Pty Ltd | Ground Floor - Entry - Secure gate motor not working | Building | Automatic Doors | 307.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-17 14:03 | 2022-08-18 17:00 | 2022-08-18 08:02 | 2022-08-18 17:00 | 2022-08-18 09:32 |  |  | Gate motor had been dismounted by customer due to gate being stuck closed. Repositioned motor tested and inspected operation multiple times all ok, tested ups, ok, customer says there have been many previous issues with motor and mag lock which may have caused motor to fault. Since then mag lock has been temporarily disabled. Customer says ups is meant to open the gate during power outage but only allows normal operation. have left manual release on motor unlocked as per customer request due to them not having a VIRO key. Customer may want motor to be removed and have hydraulic or spring closer installed. Or VIRO keyQuote will be forwarded through as per customer request
MSA-DTWD | WA5761778 | 3 | AWB Co. | When ceiling lights are switched on, half of the lights turn off after a few seconds. | Electrical | Lighting, Internal | 344.605 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-18 11:47 | 2022-08-25 17:00 | 2022-08-19 08:30 | 2022-08-25 17:00 | 2022-08-19 10:00 |  |  | Attended site and signed in. Completed JSA. Liaised with DM about works going ahead. Located v block staff room. Found to be 4x lights not working. Supplied and replaced tubes in faulty fittings. Tested and All working now. Packed up.**job complete**
MSA-DTAG | WA5770020 | 2 | Midolo Building Services | Level 6 - Male Toilet - Grill has fallen out of door. | Building | Doors | 194.43 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-18 16:11 | 2022-08-23 17:00 | 2022-08-23 10:00 | 2022-08-23 17:00 | 2022-08-23 11:30 |  |  | DOOR REPAIRED & GRILL RE-INSTALLED
MSA-DTWD | WA5780502 | 1 | AWB Co. | Class room 1, Classroom 2 and hall way have no lights. RCD keeps tripping. | Electrical | Lighting, Internal | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-19 11:07 | 2022-08-22 17:00 | 2022-08-19 14:00 | 2022-08-22 17:00 | 2022-08-19 15:30 |  |  | Attended site and signed in. Completed JSA. Located jobs and skills area with no lights. Investigated to find all switches are off. Checked out switchboard 2 on site. Found all rcds to be on. Located switchboard 1 and found 2 x light circuit rcds off. Tested circuit and no faults found. Reset and checked all lights to be operating. Spoke with site about the issue they haven't had any recent works or roof leaks. Unsure why this has happened. Close job and return if it happens again. Job complete
MSA-DTWD | WA5781081 | 2 | Lane's Plumbing | BLD 822 - Foyer - Faulty filter housing on water fountain | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.5 | 2022-08-19 12:42 | 2022-08-24 17:00 | 2022-08-22 12:15 | 2022-08-24 17:00 | 2022-08-22 13:45 |  |  | Job is completed - Faulty filter housing on water fountain was replaced
MSA-DTWD | WA5781304 | 3 | AHS Services WA Pty Ltd (Anchor) | Broken tap please replace/repair | Plumbing & Drainage | Water | 206.945 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-19 14:55 | 2022-08-26 17:00 | 2022-08-22 07:30 | 2022-08-26 17:00 | 2022-08-22 09:00 |  |  | Tap handle has been broken off, repaired tap handle to tap
MSA-DTWD | WA5781330 | 2 | AWB Co. | FT01 – Corridor-faulty light fitting | Electrical | Lighting, Internal | 236.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-19 15:47 | 2022-08-24 17:00 | 2022-08-23 10:00 | 2022-08-24 17:00 | 2022-08-23 11:30 |  | WACCES | Attended site and signed in, completed jsa, spoke with fm about job, located lighting in corridor, isolated circuit and removed old tubes, replaced all tombstones, replaced tubes and starters(site supplied), re energised circuit, tested light and working as intended, packed up, completed paperwork, signed out **job completed**
MSA-DTWD | WA5781332 | 3 | Protek 24/7 Building & Maintenance | B01 - 4 x stair edge tread are loose on 2nd flight of stairs | Flooring | Concrete | 193.5 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-19 15:45 | 2022-08-26 17:00 | 2022-08-22 13:00 | 2022-08-26 17:00 | 2022-08-22 14:30 |  |  | Removed damaged/ missing fixings , renewed, re secure rubber nosing strips
MSA-DFES | WA5790268 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Dorm 2 Light Flickering | Electrical | General Electrical | 282.85 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-22 09:33 | 2022-08-29 17:00 | 2022-08-23 10:15 | 2022-08-29 17:00 | 2022-08-23 11:45 |  |  | Arrived on site at 10:15, was shown by so flickering led oyster fitting in dorm room 2. Found that led strip to be faulty, left site to collect new fitting from wholesaler. Replaced fitting and tested all okay. Left site at 11:45.
MSA-DTWD | WA5791581 | 2 | Damian Rak Electrical Pty Ltd | BLD 834 Facilities office - Vacumn lead faulty | Equipment | Electrical Equipment |  | Fail | Fail | 1 | 1 | 1.5 | 2022-08-23 08:34 | 2022-08-26 17:00 | 2022-09-03 17:00 | 2022-08-26 17:00 | 2022-09-03 18:30 |  |  | repairs to lead
MSA-DTWD | WA5791634 | 2 | AWB Co. | Faulty Light Switch - Light switch marked A &TSI | Electrical | General Electrical | 419.3 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-23 08:51 | 2022-08-26 17:00 | 2022-08-24 09:30 | 2022-08-26 17:00 | 2022-08-24 11:00 |  |  | Attended site and signed in. Completed jsa. Located faulty switches in Library. Counted up what we needed. Went to wholesaler to pick up 3x 15a switch mechs and 1x 10a switch mech. Returned to site. Isolated circuits. Replaced switch mechs. Tested. Working as intended. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTAG | WA5792156 | 2 | Midolo Building Services | Level 2 - Basement door to underground carpark - Door is not closing completely | Building | Doors | 763.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-23 11:54 | 2022-08-26 17:00 | 2022-08-26 09:30 | 2022-08-26 17:00 | 2022-08-26 11:00 |  |  | NEW DOOR CLOSER INSTALLED & REPAIRED
MSA-DTWD | WA5793684 | 2 | Damian Rak Electrical Pty Ltd | Exhaust Fan faulty | Equipment | Electrical Equipment |  | Pass | Pass | 0 | 0 | 1.5 | 2022-08-24 09:27 | 2022-08-29 17:00 | 2022-08-26 11:30 | 2022-08-29 17:00 | 2022-08-26 13:00 |  |  | Completed
MSA-DTWD | WA5793870 | 2 | AWB Co. | Welding Bay 19-faulty 3 phase power socket | Electrical | General Electrical | 301.405 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-24 10:40 | 2022-08-29 17:00 | 2022-08-29 12:30 | 2022-08-29 17:00 | 2022-08-29 14:00 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Drove around to F block and located welding bay 19. Tested power outlet and no power at outlet. Investigated fuse box above gpo. Upon investigation found to be 3x blown 50A fuses. Went to other blocks and found 3x new 50a fuses. Installed new fuses. Tested GPO. All working. Tested welder. no faults were apparent on welder. Plugged welder in and turned on. Welder blew fuses again. Found to be welder is faulty. Located more fuses and swapped welder for a different one. Repeated process and now all is working correctly. Packed up site. Notified relevant personnel of works completed. Completed paperwork. **job complete**
MSA-DCA | WA5793913 | 1 | GPS Plumbing & Gas Services PtyLtd | Male Toilets (behind rehearsal room) - Leaking pipe outlet above LH Male Toilet | Plumbing & Drainage | Water | 321.025 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-24 11:02 | 2022-08-25 17:00 | 2022-08-24 12:15 | 2022-08-25 17:00 | 2022-08-24 13:45 |  |  | New invisi inlet
MSA-DFES | WA5793964 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Ladies Toilet & Male Toilet - No hot water | Plumbing & Drainage | Water | 205.28 | Pass | Pass | -1 | -1 | 1.5 | 2022-08-24 11:22 | 2022-08-29 17:00 | 2022-08-25 08:30 | 2022-08-29 17:00 | 2022-08-25 10:00 |  |  | Attend site to check out no hot water to make and female toilets hand basins checked temp valves below bench tops in each bathroom. Adjusted temperature to 48.7 at all hand basins in male andfemale toilets. All working correctly.
MSA-DTWD | WA5794038 | 2 | Protek 24/7 Building & Maintenance | Ground - Front door - Door closer faulty | Building | Doors | 163.66 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-24 11:47 | 2022-08-29 17:00 | 2022-08-26 13:30 | 2022-08-29 17:00 | 2022-08-26 15:00 |  |  | Adjusted door closer to latch
MSA-DTWD | WA5795223 | 1 | AWB Co. | 4F15 - Light switch dislodged from wall plate | Electrical | General Electrical | 208.485 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-25 10:17 | 2022-08-26 17:00 | 2022-08-26 07:00 | 2022-08-26 17:00 | 2022-08-26 08:30 |  |  | Attended site and signed in. Completed JSA. Awaited staff to give me the keys for the classroom. Got into the room and found 2 gang light switch all kinds of broken. Supply and replaced with new 2 gang switch and plate. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5795390 | 2 | ACTION GLASS & ALUMINIUM | Impact hole in window on r/h side | Glazing | Window Glass | 335.61 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-25 11:48 | 2022-08-30 17:00 | 2022-08-29 13:00 | 2022-08-30 17:00 | 2022-08-29 14:30 |  |  | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-660 X 6753 L/M OF RUBBER REPLACED
MSA-DTWD | WA5797568 | 2 | Techworks Electrical | the hot servery unit warming lights not working | Equipment | Electrical Equipment | 401.41 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-29 09:13 | 2022-09-01 17:00 | 2022-08-30 13:00 | 2022-09-01 17:00 | 2022-08-30 14:30 |  |  | Replaced heating lamps
MSA-DTWD | WA5797602 | 1 | M Construction (WA) | Ground floor - Hallway - Walkway loose floor covering causing a trip hazard | Flooring | Vinyl | 195.42 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-29 09:18 | 2022-08-30 17:00 | 2022-08-30 13:30 | 2022-08-30 17:00 | 2022-08-30 15:00 |  |  | Cleared and tapped floor joints with industrial strengths tape to solve trip hazard.
MSA-DTAG | WA5798100 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 10 (Coroners Court) - Male toilets - Water is filling up high and not receding down | Plumbing & Drainage | Toilets/Cisterns | 171.175 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-29 12:16 | 2022-08-30 17:00 | 2022-08-30 07:30 | 2022-08-30 17:00 | 2022-08-30 09:00 |  |  | Unlocked toilets used bottle of mo flo
MSA-DCA | WA5798179 | 3 | Techworks Electrical | Level 3 - Cleaners Store Room - 3 x faulty fluoro lights - See notes below | Electrical | Lighting, Internal | 326.61 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-29 12:32 | 2022-09-05 17:00 | 2022-09-02 06:00 | 2022-09-05 17:00 | 2022-09-02 07:30 |  |  | Replaced 4x tubes and starters
MSA-DTWD | WA5799430 | 0 | AWB Co. | Switch board- white 19 breaker tripped out, when trying to set sparks coming out | Electrical | General Electrical | 368.905 | Fail | Fail | 0 | 0 | 1.5 | 2022-08-30 11:54 | 2022-08-30 13:54 | 2022-08-31 10:45 | 2022-08-30 15:54 | 2022-08-31 12:15 |  | WCAPPR | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located D block and board with Rcd tripping. Investigated classroom duct. Upon investigation found that ducting lid had squished cable and come into contact with active conductor causing Rcd to trip. Repaired cable. Tested cable. Energised circuit, circuit now staying on. Placed duct lid back on making sure no cables were getting squished. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5801179 | 1 | AWB Co. | Door Broken | Building | Doors | 378.42 | Pass | Pass | 0 | 0 | 1.5 | 2022-08-31 14:31 | 2022-09-01 17:00 | 2022-08-31 16:00 | 2022-09-01 17:00 | 2022-08-31 17:30 |  |  | fixed broken hinge coming off frme
MSA-DCA | WA5827333 | 1 | Protek 24/7 Building & Maintenance | staff male toilet - Disabled Cubicle - Broken lock | Building | Doors | 201 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-01 09:31 | 2022-09-02 17:00 | 2022-09-01 11:30 | 2022-09-02 17:00 | 2022-09-01 13:00 |  |  | Removed damaged missing pop rivets , install flush head screws to track and overhead support structure, removedLock assembly, lubricated, reinstated lock assembly, check and test operation , all ok
MSA-DFES | WA5827338 | 3 | GRAFFITI FORCE PTY LTD | Ground Floor - Car Park - Graffiti on car park wall near the tunnel | Cleaning | Graffiti | 333 | Fail | Fail | 1 | 1 | 1.5 | 2022-09-01 09:45 | 2022-09-08 17:00 | 2022-09-13 09:40 | 2022-09-08 17:00 | 2022-09-13 11:10 |  |  | REMOVAL OF GRAFFITI FROM CARPARK WALLS NEAR TUNNEL
MSA-DTAG | WA5827476 | 1 | Sapio Pty Ltd | Custody - Receiver 6 alarm fault | Security | Security Management System | 214.53 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-01 10:34 | 2022-09-02 17:00 | 2022-09-01 11:00 | 2022-09-02 17:00 | 2022-09-01 12:30 |  |  | replaced low battery
MSA-DCA | WA5827504 | 2 | Techworks Electrical | Accessible toilet - Faulty extractor fan - is linked to aircon | Electrical | General Electrical | 183.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-01 10:47 | 2022-09-06 17:00 | 2022-09-06 09:00 | 2022-09-06 17:00 | 2022-09-06 10:30 |  |  | Attended site found that exhaust fans were not working in 5he bathroom on level 1Found that starter motor control box was tripped and also found Air-conditioning switch for fan control was offReset motor control box and reset fan control back into auto Tested fans all working
MSA-DTAG | WA5829467 | 2 | AHS Services WA Pty Ltd (Anchor) | Male public toilet urinal blocked | Plumbing & Drainage | Drainage | 191.445 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-02 13:45 | 2022-09-07 17:00 | 2022-09-05 08:30 | 2022-09-07 17:00 | 2022-09-05 10:00 |  |  | .
MSA-DTWD | WA5831886 | 1 | AWB Co. | Faulty door handle | Building | Doors | 181.575 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 09:19 | 2022-09-06 17:00 | 2022-09-06 09:30 | 2022-09-06 17:00 | 2022-09-06 11:00 |  |  | fixed handle cock
MSA-DTWD | WA5832049 | 2 | AWB Co. | Steel store -3x roof leaks | Roofing | Tiled Roofing | 385.27 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 10:37 | 2022-09-08 17:00 | 2022-09-07 12:00 | 2022-09-08 17:00 | 2022-09-07 13:30 |  |  | Found rusted out sheets made repairs. Found blocked sumps unblocked all sumps. Job complete
MSA-DTWD | WA5832104 | 2 | AWB Co. | Water Leak above machine numbers 33 & 23 | Roofing | Metal Roofing | 360.3 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 11:07 | 2022-09-08 17:00 | 2022-09-07 10:30 | 2022-09-08 17:00 | 2022-09-07 12:00 |  |  | Refixed apron flashing back in place and sealed. Re sealed joints to vent. Job complete
MSA-DCA | WA5832531 | 1 | Ballantyne Plumbing Gas & Electrical | Basement - Sewer pump room - Sewer Pump controller in alarm | Plumbing & Drainage | Sewer Drains & Septic Systems |  | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 13:55 | 2022-09-06 17:00 | 2022-09-05 14:15 | 2022-09-06 17:00 | 2022-09-05 15:45 |  |  | Possibly issue related to power surge or PCB is faultyIf continues to fault will require new PCB and or surge protection equipment
MSA-DTWD | WA5832659 | 3 | COMMERCIAL PLUMBING AND GAS | Student Urinal Blocked | Plumbing & Drainage | Toilets/Cisterns | 568.925 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 14:44 | 2022-09-12 17:00 | 2022-09-09 11:30 | 2022-09-12 17:00 | 2022-09-09 13:00 |  |  | unblock urinal with sani snake, Drainsflush scour downstream with larger machine
MSA-DTWD | WA5832669 | 3 | COMMERCIAL PLUMBING AND GAS | Level 4 - Men's Student Toilet - Student urinal blocked | Plumbing & Drainage | Drainage | 526.195 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 14:51 | 2022-09-12 17:00 | 2022-09-09 15:30 | 2022-09-12 17:00 | 2022-09-09 17:00 |  |  | unblocked urinal and replaced service kits
MSA-DTWD | WA5832673 | 3 | COMMERCIAL PLUMBING AND GAS | Level 3 - Men's Student Toilet - Student urinal blocked | Plumbing & Drainage | Drainage | 526.195 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-05 14:53 | 2022-09-12 17:00 | 2022-09-09 14:00 | 2022-09-12 17:00 | 2022-09-09 15:30 |  |  | unblocked urinal and replaced service kits
MSA-DCA | WA5833505 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Power outage cut supply to BMS system | Air Conditioning | Building HVAC Maintenance (Major Plant) | 202.705 | Fail | Fail | 0 | 0 | 1.5 | 2022-09-06 10:20 | 2022-09-06 12:20 | 2022-09-06 13:00 | 2022-09-06 14:20 | 2022-09-06 14:30 |  |  | ATTENDED SITE, SIGNED IN AND ACCESSED ALL THE CENTRAL PLANT EQUIPMENT AFTER POWEROUTAGE AND CHECKED FOR CORRECT OPERATION. RESET VARIOUS VARIABLE SPEED DRIVES,CHILLERS AND EQUIPMENT THAT HAD NOT RESUMED BACK TO NORMAL OPERATION.LOGGED INTO THE BMS AND RESET ALL ALARMS. MONITORED THE CENTRAL PLANT EQUIPMENTAND ALARMS.
MSA-DTWD | WA5833976 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 299.8 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-06 12:57 | 2022-09-07 17:00 | 2022-09-07 13:00 | 2022-09-07 17:00 | 2022-09-07 14:30 |  |  | Sealed over top of dektit
MSA-DTWD | WA5834036 | 3 | AWB Co. | Sculpture Room main power breaker not resetting | Electrical | General Electrical | 288.22 | Pass | Pass | -1 | -1 | 1.5 | 2022-09-06 13:21 | 2022-09-13 17:00 | 2022-09-08 06:30 | 2022-09-13 17:00 | 2022-09-08 08:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Located main isolator in board that wouldn’t reset. Found out which e stops were part of that circuit. Reset all e stops. Went back to board and reset breaker. Everything all good. Took pics. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5836018 | 2 | Techworks Electrical | light not working | Electrical | Lighting, Internal | 676.23 | Pass | Pass | -1 | -1 | 1.5 | 2022-09-07 09:44 | 2022-09-12 17:00 | 2022-09-08 14:00 | 2022-09-12 17:00 | 2022-09-08 15:30 |  |  | Investigate faulty light fitting, working at time of inspection. Search surrounding area for any faulty fittings, none found.
MSA-DFES | WA5838303 | 3 | AWB Co. | Roof-secure loose roof flashing - see notes | Roofing | Guttering | 339.67 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-08 12:07 | 2022-09-15 17:00 | 2022-09-12 13:00 | 2022-09-15 17:00 | 2022-09-12 14:30 |  |  | Re fixed flashing into place and secured - Job complete
MSA-DFES | WA5839231 | 2 | Protek 24/7 Building & Maintenance | Tunic Room - Faulty door - not opening and closing properly | Building | Doors | 318.23 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-09 10:37 | 2022-09-14 17:00 | 2022-09-13 07:45 | 2022-09-14 17:00 | 2022-09-13 09:15 |  |  | Re tighten existing fixings and added more fixings to hold weight of door Adjusted door stopper and tightened handle
MSA-DFES | WA5839578 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Isolate power after water leak | Electrical | General Electrical | 303.33 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-09 13:41 | 2022-09-09 15:41 | 2022-09-09 14:30 | 2022-09-09 17:41 | 2022-09-09 16:00 |  |  | complete
MSA-DTAG | WA5839621 | 3 | Midolo Building Services | multiple chairs broken/loose - see notes below | Furniture | Indoor Furniture | 211.04 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-09 14:05 | 2022-09-16 17:00 | 2022-09-14 07:45 | 2022-09-16 17:00 | 2022-09-14 09:15 |  |  | replaced 1 broken chair & re secured the rest with new fixings
MSA-DTWD | WA5853730 | 2 | Water2water Pty Ltd | EG15 Corridor - West end entrance - Faulty faucet on water cooler | Plumbing & Drainage | Water | 318.58 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-12 10:33 | 2022-09-15 17:00 | 2022-09-12 15:30 | 2022-09-15 17:00 | 2022-09-12 17:00 |  |  | Replaced failed faucet and cleared drain to stop overflowing/flooding
MSA-DTWD | WA5853769 | 3 | GRAFFITI FORCE PTY LTD | Ground Floor - Leadlight Lane Gate - Large Graffiti Tag on Gate | Cleaning | Graffiti | 385 | Fail | Fail | 1 | 1 | 1.5 | 2022-09-12 10:53 | 2022-09-19 17:00 | 2022-09-27 14:00 | 2022-09-19 17:00 | 2022-09-27 15:30 |  |  | REMOVAL OF GRAFFITI ROM LEADLIGHT LANE GATE
MSA-DTWD | WA5861384 | 1 | AWB Co. | lights not working - RCD tripped | Electrical | Lighting, Internal | 235.8575 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-13 09:15 | 2022-09-14 17:00 | 2022-09-13 14:30 | 2022-09-14 17:00 | 2022-09-13 16:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Went to E003. Pulled off board cover. Tested for voltages. Found blue phase had no power. Located main db that sub board was fed from. Found out that blue phase fuse was blown. Replaced fuse. Everything working as intended now. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5861707 | 1 | AHS Services WA Pty Ltd (Anchor) | Unisex toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 319.2 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-13 10:50 | 2022-09-14 17:00 | 2022-09-14 11:00 | 2022-09-14 17:00 | 2022-09-14 12:30 |  |  | Unlocked toiletUsed bottle of moflo
MSA-DTAG | WA5861883 | 2 | Water2water Pty Ltd | Sheriffs office - Billi Tap – Cold Water not working – Far end of kitchen | Plumbing & Drainage | HWS/Units Electric & Gas | 415.58 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-13 11:58 | 2022-09-16 17:00 | 2022-09-14 13:15 | 2022-09-16 17:00 | 2022-09-14 14:45 |  |  | Replaced inlet and dual solenoid to restore flow of water back to the unit. Tested and checked, all ok
MSA-DTWD | WA5866050 | 0 | AWB Co. | power outage | Electrical | General Electrical | 301.405 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-14 08:27 | 2022-09-14 10:27 | 2022-09-14 08:30 | 2022-09-14 12:27 | 2022-09-14 10:00 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Investigated power out after power shut down yesterday. Located board with power out. Found to be power isolator had not been reset properly. Reset isolator. Made sure power was reinstated back to rooms. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5867820 | 2 | AWB Co. | Block Z - Belt Splicing - Faulty 3 Phase Plug on a battery charger | Electrical | Materials | 593.9 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-14 10:15 | 2022-09-19 17:00 | 2022-09-16 14:00 | 2022-09-19 17:00 | 2022-09-16 15:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Spoke to lecturer. They needed a male and female end fitting on either side of cable for forklift. Went to wholesaler and picked up parts for job. Fit off both ends. Test and tagged. Plugged in. Working as intended. Packed up. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5869457 | 1 | Midolo Building Services | Level 13 - Judicial Floor - Outside of meeting room - Ceiling panel is loose | Building | Ceiling | 178.15 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-14 13:53 | 2022-09-15 17:00 | 2022-09-15 09:30 | 2022-09-15 17:00 | 2022-09-15 11:00 |  |  | repaired/secured ceiling panel
MSA-DTWD | WA5879918 | 1 | AWB Co. | K Block - Kitchen - Faulty GPO | Electrical | General Electrical | 328.12 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-15 10:10 | 2022-09-16 17:00 | 2022-09-16 12:30 | 2022-09-16 17:00 | 2022-09-16 14:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Located faulty gpo. Fm said he wanted another one adding next to it. Isolated power circuit. Installed new WP gpo next to it. Re energised. Tested. Working as intended. Cleaned and packed up. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5887598 | 2 | Water2water Pty Ltd | the wall mounted hot water zip urn not working | Plumbing & Drainage | HWS/Units Electric & Gas | 220.75 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-16 08:51 | 2022-09-21 17:00 | 2022-09-20 11:50 | 2022-09-21 17:00 | 2022-09-20 13:20 |  |  | Reset tripped thermal overload, checked and tested unit and worked ok.
MSA-DTWD | WA5887612 | 2 | Techworks Electrical | Room E46 - Light not working | Electrical | Lighting, Internal | 368.7 | Pass | Pass | -1 | -1 | 1.5 | 2022-09-16 08:53 | 2022-09-21 17:00 | 2022-09-16 11:00 | 2022-09-21 17:00 | 2022-09-16 12:30 |  |  | Replaced failed light with new LED batten
MSA-DCA | WA5887746 | 2 | Techworks Plumbing | Faulty Zip tap - Hackett Hall Learning Studio 1 - kitchen | Plumbing & Drainage | Water | 748.58 | Fail | Fail | 4 | 4 | 1.5 | 2022-09-16 09:43 | 2022-09-21 17:00 | 2022-10-20 07:00 | 2022-09-21 17:00 | 2022-10-20 08:30 |  | WCAPPR | Attended site and signed in at the security office then we made our way to hacket hall to fix the faulty zip unit, the cupboard was locked so we couldn’t get into it to work on the unit we called and waited for someone to come and open it up for us.We saw that the filter needed changing so we went to reece and grabbed a new filter for the unit then once back on site we installed and flushed the filter then tested the zip unit zip unit is working correctly again Cleaned up and leftcompleted paperwork
MSA-DTWD | WA5888195 | 2 | Lane's Plumbing | faulty cistern | Plumbing & Drainage | Toilets/Cisterns |  | Fail | Fail | 0 | 0 | 1.5 | 2022-09-16 13:35 | 2022-09-21 17:00 | 2022-09-23 12:00 | 2022-09-21 17:00 | 2022-09-23 13:30 |  |  | Repairs to cistern
MSA-DTWD | WA5888320 | 3 | Techworks Electrical | Main Admin Building - 4 non functional lights in staff area need replacing | Electrical | Lighting, Internal | 240.775 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-16 15:39 | 2022-09-23 17:00 | 2022-09-23 07:30 | 2022-09-23 17:00 | 2022-09-23 09:00 |  |  | Attended site found 4 lights out in office area, replaced lights all working.
MSA-DTWD | WA5970863 | 3 | Australian HVAC Services Pty. Ltd. | Whole Block - no aircon working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 638.93 | Pass | Pass | -1 | -1 | 1.5 | 2022-09-20 09:53 | 2022-09-28 17:00 | 2022-09-23 09:00 | 2022-09-28 17:00 | 2022-09-23 10:30 |  |  | Attended site to check on comms issue with BMS. Found that comms had been lost with Tower Block controllers after the IT contractor had changed out all the network switches with new ones. This caused the port used by the BMS from tower block to admin to be blocked. Determined with patch point was being used on Level 2 IT rack (G19) and which port on which new switch it was connected to (Port 25 on top switch). Dept of Training IT liaised with contractor to open port again and BMS now working ok. Checked operation of BMS and all working ok. 2. Also updated public holidays due to recent events (Queens death). Also completed backup of BMS (Main Controller – JACE Only).
MSA-DTWD | WA5970897 | 2 | Damian Rak Electrical Pty Ltd | Faulty exit light | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 1.5 | 2022-09-20 10:03 | 2022-09-23 17:00 | 2022-09-29 13:00 | 2022-09-23 17:00 | 2022-09-29 14:30 |  |  | Repairs to light
MSA-DCA | WA5973678 | 2 | Protek 24/7 Building & Maintenance | C+K Kitchen - Kitchen Door Handle Falling Apart - see notes below | Building | Doors | 161.54 | Fail | Fail | 0 | 0 | 1.5 | 2022-09-21 17:03 | 2022-09-27 17:00 | 2022-09-28 10:30 | 2022-09-27 17:00 | 2022-09-28 12:00 |  |  | Pull lock apart, service and reinstate
MSA-DCA | WA5974848 | 0 | TK Elevator Australia Pty Ltd | PICA-Main Building-Level 1-Lift Foyer - lilft not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5 | 2022-09-24 09:27 | 2022-09-24 11:27 | 2022-09-24 10:30 | 2022-09-24 13:27 | 2022-09-24 12:00 |  |  | Lift1 PICA-Elevator > MRL > Gearless :On arrival lift 200mm below top floor.No faults on controller board .Fault on drive codef31 - pulse generator fault.Lift will drive for approximately 4 seconds on inspection then drive faults.Suspect shaft information board on car top fitted to floating tape,possibly guides as light TC goes off and on as you touch board.Lift switched off for further investigation.
MSA-DTWD | WA5976728 | 2 | Techworks Electrical | Kitchen area - kitchenette area light not working | Electrical | Lighting, Internal | 482.34 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-27 10:58 | 2022-09-30 17:00 | 2022-09-28 10:30 | 2022-09-30 17:00 | 2022-09-28 12:00 |  |  | Replaced tubes in kitchen area Materials used 8x 36W 840 tubes 8x S10 starters
MSA-DTWD | WA5976853 | 3 | Protek 24/7 Building & Maintenance | Unit 3 - ground - Mechanical compound gate behind 3B36 - gate has broken slats | Building | Steel Fencing & Gates | 244.01 | Pass | Pass | -1 | -1 | 1.5 | 2022-09-27 11:43 | 2022-10-04 17:00 | 2022-09-28 10:30 | 2022-10-04 17:00 | 2022-09-28 12:00 |  |  | Screwed the timbers back to frame work
MSA-DCA | WA5977225 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Geology building - mezzanine - Comms room 5 - aircon SCU 0301 not working | Air Conditioning | Room Air Conditioners | 202.705 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-27 14:47 | 2022-09-28 17:00 | 2022-09-27 15:30 | 2022-09-28 17:00 | 2022-09-27 17:00 |  |  | Attended site. Signed in and gained access. Investigated cassette unit in comms room. Accessed bms and found unit running but no cooling. Drove actuator to 100% open, cooling works. Checked over trends and found unit loss comms and didn't return to normal. Isolated power to unit and comms. Restored power and relinquished controls to actuator. Unit operating as required. Completed paperwork.
MSA-DCA | WA5978556 | 3 | FCT SURFACE CLEANING | Admin Building - Ground Floor Exterior - Outside Window Lintel - Graffit on window - See notes below | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.5 | 2022-09-28 11:32 | 2022-10-05 17:00 | 2022-10-04 13:00 | 2022-10-05 17:00 | 2022-10-04 14:30 |  |  | Removal of graffiti
MSA-DTAG | WA5978587 | 0 | Seme Solutions Pty Ltd | Entry Door to courtroom 2 - Electronic controlled door is not working - door is not opening | Building | Automatic Doors | 209.82 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-28 11:38 | 2022-09-28 13:38 | 2022-09-28 13:15 | 2022-09-28 15:38 | 2022-09-28 14:45 |  |  | Checked court 2 door the people on sote were saying the mag lock was not releasing, after doing my own testing couldn't find an issue with the door. Restarted the controller and checked transaction logs
MSA-DCA | WA5979098 | 2 | Protek 24/7 Building & Maintenance | Old Gaol - Roof Level - External Area (outside kitchen) - Blocked downpipe - See notes | Roofing | Guttering | 278.96 | Pass | Pass | -1 | -1 | 1.5 | 2022-09-28 15:59 | 2022-10-03 17:00 | 2022-09-29 13:15 | 2022-10-03 17:00 | 2022-09-29 14:45 |  |  | BRAF Declined
MSA-DTWD | WA5980066 | 1 | Equans Mechanical Services Australia | RETROSPECTIVE WORK ORDER for attendance ref WA5479940 | Air Conditioning | Room Air Conditioners | 259.42 | Fail | Fail | 2 | 2 | 1.5 | 2022-09-27 07:00 | 2022-09-27 17:00 | 2022-10-10 09:00 | 2022-09-27 17:00 | 2022-10-10 10:30 | 1 |  | Found timer to be faultyThornlie TAFE to organise repairs
MSA-MRWA | WA5981652 | 3 | Automatic Fire Protection (ARA) | Level 1 - Outside of bitumen lab - Leaking fire hose | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 208.23 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-30 08:02 | 2022-10-07 17:00 | 2022-10-06 13:00 | 2022-10-07 17:00 | 2022-10-06 14:30 |  |  | Investigated leaking hose reel. Found hose reel leaking from packing gland of the swing arm, unable to replace packing gland so hose reel isunserviceable. Recommend replacing with new swing arm hose reel
MSA-DTAG | WA5982654 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - 1987 Wing Cleaners room - Tap leaking | Plumbing & Drainage | Water | 236.165 | Pass | Pass | 0 | 0 | 1.5 | 2022-09-30 13:11 | 2022-10-05 17:00 | 2022-10-03 07:30 | 2022-10-05 17:00 | 2022-10-03 09:00 |  |  | Service leak cold tap in cleaners
MSA-DTAG | WA5987111 | 1 | Midolo Building Services | Room/Office - Secure waiting area Hay St (Shuttle Conferencing Room)-damp roof tiles-see notes | Roofing | Tiled Roofing | 145.26 | Fail | Fail | 0 | 0 | 1.5 | 2022-10-03 08:00 | 2022-10-03 17:00 | 2022-10-04 09:00 | 2022-10-03 17:00 | 2022-10-04 10:30 |  |  | ROOF TILES REPLACED
MSA-DFES | WA5987330 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | L1 nth west corner near stair well- various power points not working along wall | Electrical | General Electrical | 187.95 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-03 10:46 | 2022-10-04 17:00 | 2022-10-03 11:15 | 2022-10-04 17:00 | 2022-10-03 12:45 |  |  | complete
MSA-DTWD | WA5988615 | 2 | Techworks Plumbing | Left side male toilet constant leaking | Plumbing & Drainage | Toilets/Cisterns | 311.79 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-04 10:11 | 2022-10-07 17:00 | 2022-10-05 14:30 | 2022-10-07 17:00 | 2022-10-05 16:00 |  |  | Removed and replaced existing flush and inlet valves for g block cistern
MSA-DTAG | WA5988732 | 1 | Sapio Pty Ltd | ground-main custody control-Duress alarm – 18 Sally port ‘Open circuit tampered’ | Security | Security Management System | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-04 10:50 | 2022-10-05 17:00 | 2022-10-04 13:00 | 2022-10-05 17:00 | 2022-10-04 14:30 |  |  | Checked reported issue. Traced fault to loose connection on expander 6, input 2. Rectified fault and tested. Ok.
MSA-DTWD | WA5992723 | 1 | High Tech Pest Control | Behind Block C - Bin Compound - bees | Pest Control | General Pest | 171.48 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-04 16:33 | 2022-10-05 17:00 | 2022-10-05 10:30 | 2022-10-05 17:00 | 2022-10-05 12:00 |  |  | weep holes dusted
MSA-DCA | WA5993297 | 3 | FCT SURFACE CLEANING | Graffiti outside old church close to playground. see notes | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1.5 | 2022-10-05 09:39 | 2022-10-12 17:00 | 2022-10-10 10:30 | 2022-10-12 17:00 | 2022-10-10 12:00 |  |  | Removal of graffiti
MSA-DCA | WA5993332 | 3 | Protek 24/7 Building & Maintenance | Gardens near Iris Avenue entrance-Bollard missing-photo to follow in email | Building | Columns | 177.72 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-05 09:50 | 2022-10-12 17:00 | 2022-10-10 07:30 | 2022-10-12 17:00 | 2022-10-10 09:00 |  |  | One bollard was completely out, was installed poorly had no screws in bottom of post and only half a bag of concrete.Fixings in bottom of post so concrete will grab, two bags of concrete to post
MSA-DFES | WA5995739 | 2 | Anvil Doors | Engine Room Door 6 - Roller Guide at the bottom of door 6 broken | Building | Automatic Doors | 452.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-06 15:47 | 2022-10-11 17:00 | 2022-10-10 15:00 | 2022-10-11 17:00 | 2022-10-10 16:30 |  |  | Please see attached signature slip and service reports
MSA-DCA | WA5997778 | 1 | Techworks Plumbing | Jubilee Building admin - Level G -2 x UATs Beaufort St (Epoch Cafe ) Tap | Plumbing & Drainage | Materials | 446.06 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-07 09:36 | 2022-10-10 17:00 | 2022-10-07 10:30 | 2022-10-10 17:00 | 2022-10-07 12:00 |  |  | signed in at security & spoke with a man who showed us the issues with the toilets & the issue with the tap at epoch cafe. -Jubilee toilets these toilets are the same ones which are always having issues being blocked. Opened cleanouts in plant room to find the drains full. Grabbed the drain rods and after a while managed to clear the drain. Ran all fixtures and toilets for a good amount of time to make sure & issue seems to be resolved for now. -epoch cafe male toilets loose spout tap & aerator missing. Someone on site already had the aerator for us to chuck in no dramas. Tightened spout tap to prevent it from coming off.
MSA-DTWD | WA5998084 | 2 | AWB Co. | 15 amp GPO and plug top for Salamander Grill have burnt out | Electrical | General Electrical | 368.355 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-07 11:51 | 2022-10-12 17:00 | 2022-10-10 12:30 | 2022-10-12 17:00 | 2022-10-10 14:00 |  |  | Attended site signed in jsa completed. Found burnt 15a socket and plug on wall as shown by glenn. Also replaced an additional failed plug 10a. Tested and tagged.Job completed
MSA-DTWD | WA5998378 | 2 | AWB Co. | A202 - Ladies Toilet - Door besides A202 - Step/Flooring loose when stepping into duct area | Building | General Building | 181.575 | Fail | Fail | 3 | 3 | 1.5 | 2022-10-07 15:08 | 2022-10-12 17:00 | 2022-11-03 07:30 | 2022-10-12 17:00 | 2022-11-03 09:00 |  |  | Arrived on site.Inspected areaSet up bollards to cordon off area Attached the wooden floor panels firmly to the wooden supports
MSA-MRWA | WA6000638 | 2 | LYNX INTEGRATED SYSTEMS | Level 2 - Programming required for 3 light locations on level 2 - See notes below | Electrical | Lighting, Internal | 317.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-10 09:22 | 2022-10-13 17:00 | 2022-10-10 14:30 | 2022-10-13 17:00 | 2022-10-10 16:00 |  |  | 1. West fitting in room 201 had no issue.2. West fitting outside room 201 has a broken globe and needs to be replaced by an electrician3. Found 1 x fitting on the West side perimeter which was bringing down the whole DALI line. I have unplugged this fitting which needs to be replaced by an electrician.4. East fitting has a broken globe and needs to be replaced by an electrician.
MSA-DTWD | WA6000694 | 2 | AWB Co. | Classroom C67 - Lights tripping | Electrical | Lighting, Internal | 301.405 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-10 09:47 | 2022-10-13 17:00 | 2022-10-13 11:00 | 2022-10-13 17:00 | 2022-10-13 12:30 |  |  | Attended site signed in jsa completed. Found rcd w1 and w6 w1 power also tripping when room c67 was turned on. Found black bms control box inside faulty in one light. Removed and bypassed and now working fine. Job completed
MSA-DTAG | WA6001150 | 2 | Automatic Fire Protection (ARA) | 1903 - FIP indicates zone 15 detector fault | Fire Protection Services | Fire Protection - Monitor System | 517.355 | Fail | Fail | 0 | 0 | 1.5 | 2022-10-10 12:46 | 2022-10-13 17:00 | 2022-10-14 10:00 | 2022-10-13 17:00 | 2022-10-14 11:30 |  |  | Attended site and found device 2117 Az 15 Ground lift lobby in missing fault.Device went missing in 19/9 at 12:51Checked area and found device missing see pic in docsLooks like removed due to water damageFitted new detector and base and left system normal.Materials1 x XP95 smoke detector1 x XP95 base
MSA-DTAG | WA6007554 | 3 | Midolo Building Services | Custody - Cupboard ceiling access hatch frame is damaged | Building | Ceiling | 252.56 | Pass | Pass | -1 | -1 | 1.5 | 2022-10-11 08:52 | 2022-10-18 17:00 | 2022-10-11 11:45 | 2022-10-18 17:00 | 2022-10-11 13:15 |  |  | MANHOLE REPLACED
MSA-DFES | WA6008421 | 2 | Protek 24/7 Building & Maintenance | Ground - Rear patio area - Gate to rear of station has fallen off hinges. | Building | Steel Fencing & Gates | 186.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-11 14:25 | 2022-10-14 17:00 | 2022-10-13 07:00 | 2022-10-14 17:00 | 2022-10-13 08:30 |  |  | Re hung gate using appropriate fixingsAdjusted self closing hinge tension.
MSA-DCA | WA6014707 | 0 | Techworks Electrical | Pump Room underneath Courtyard pond - Water is leaking into room onto electronics - Please make safe | Electrical | General Electrical | 339.78 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-12 11:19 | 2022-10-12 11:49 | 2022-10-12 11:30 | 2022-10-12 13:19 | 2022-10-12 13:00 |  |  | Arrived on site and spoke to technician who showed us the GPO’s being effected, 4x GPO’s sitting a level down below pond, water is leaking through wall and down to GPO’s face plate, we have disconnected each GPO and left the cable in a safe manner behind the gpo, preventing any chance of someone getting a shock from the wet surface plate, we have tagged out each GPO, Once the pond has been drained completely we can return to re connect the GPO’s.
MSA-DCA | WA6014992 | 1 | Techworks Electrical | Electrical assist - Heat Reclaim Pump not working | Electrical | General Electrical | 306.63 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-12 13:31 | 2022-10-13 17:00 | 2022-10-12 13:31 | 2022-10-13 17:00 | 2022-10-12 15:01 |  |  | Arrived on site and spoke to Equans worker jordan, who informed us that he could not get a motor running and they he had no power at it, we opened and investigated the MSSB controller for the circuit, checked for voltage, checked fuses, checked over the contactors for any thermal overloading, everything looked good and in good working order. Put back together MSSB controller and turned it all on to override, voltage was at the motor but the motor was not working at all - faulty motor, jordan from equans is going to go through the necessary steps to rectify the faulty motor
MSA-DTAG | WA6015123 | 3 | Sapio Pty Ltd | Managers workstation unable to override front door in an emergency | Security | Access Control | 333.56 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-12 15:21 | 2022-10-19 17:00 | 2022-10-18 08:00 | 2022-10-19 17:00 | 2022-10-18 09:30 |  |  | Set up main front auto door overrides and demo public holidays to manager.
MSA-DTWD | WA6022933 | 1 | COMMERCIAL PLUMBING AND GAS | Ground female toilet-Fault description Foul water coming up the drain in one of the toilets blocked | Plumbing & Drainage | Toilets/Cisterns | 683.925 | Fail | Fail | 0 | 0 | 1.5 | 2022-10-14 13:31 | 2022-10-17 17:00 | 2022-10-18 15:30 | 2022-10-17 17:00 | 2022-10-18 17:00 |  |  | unblocked drain w/ drainsflush
MSA-DCA | WA6022949 | 3 | Techworks Electrical | Epoch Café - ground - Stove top RCD has tripped and will not reset. -see notes | Electrical | General Electrical | 406.97 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-14 13:42 | 2022-10-21 17:00 | 2022-10-19 07:00 | 2022-10-21 17:00 | 2022-10-19 08:30 |  |  | Rotary switch was damaged due to short circuit, found replacement switch and installed onto stove, stove is back working as normal.
MSA-DTWD | WA6023031 | 2 | Lane's Plumbing | ground-Tenant reports fast consumption of gas bottles - see notes | Plumbing & Drainage | Gas |  | Pass | Pass | 0 | 0 | 1.5 | 2022-10-14 14:47 | 2022-10-19 17:00 | 2022-10-17 14:30 | 2022-10-19 17:00 | 2022-10-17 16:00 |  |  | REPLACE LEAKING GAS REGULATOR AT 0.00 GSTBOTTLES HOUSE 11
MSA-DTWD | WA6050662 | 1 | Australian Airconditioning Services Pty Ltd | Skope under bench fridge sitting at -3.5 degrees – ‘LA’ showing on display | Refrigeration | Refrigerators | 358.56 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-17 15:30 | 2022-10-18 17:00 | 2022-10-18 08:00 | 2022-10-18 17:00 | 2022-10-18 09:30 |  |  | complete
MSA-DTWD | WA6081947 | 2 | AWB Co. | Metal Fabrication 2 - Faulty single phase drop pendant | Electrical | Lighting, Internal | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-18 15:02 | 2022-10-21 17:00 | 2022-10-20 07:00 | 2022-10-21 17:00 | 2022-10-20 08:30 |  |  | Attended site signed in jsa completed. Found drop pendant that is out of serviced. Tested trip 0-180 and 180-0 and passed 0.30. tested fault loop 0.28. Found nothing wrong inside gpo. Removed tag and good for useJob completed
MSA-DFES | WA6088870 | 2 | Australian HVAC Services Pty. Ltd. | Mechanical vent on engine room roof needs repair | Air Conditioning | Building HVAC Maintenance (Major Plant) | 286.34 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-19 11:17 | 2022-10-24 17:00 | 2022-10-21 09:30 | 2022-10-24 17:00 | 2022-10-21 11:00 |  |  | Attended service call, spoke with staff & accessed roof. Found engine room roof vents in good condition , sealed ef1 rear flashing plate as possible cause of water leak into ceiling space
MSA-DCA | WA6090763 | 1 | Techworks Plumbing | Jubilee - Ground - UAT toilets - Sewerage smell - see notes below | Plumbing & Drainage | Toilets/Cisterns | 392.5 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-19 13:37 | 2022-10-20 17:00 | 2022-10-20 08:30 | 2022-10-20 17:00 | 2022-10-20 10:00 |  |  | Attended site and signed in at the security office, then we called Neil and met him at the jubilee building, the residents had been complaining about a bad smell coming from the toilets so we had a look and ran the basins, toilets and showers, we found that the smell was coming from the shower drains probably due to the previous blockages that they have been having in those particular toilets, a few times the blockage has overflowed out of the shower drains and because no one uses those showers we think it ended up causing the smell to linger so we ran a decent amount of water down the shower drains which seemed to make a big difference we also put disinfectant down the shower drains for a better smell.due to the drain not having much fall the toilets will sometimes get partially blocked and take a while to drain so this may keep occurring until they figure out what they want to do with the drains we made sure everything was draining well before we left then we signed out and left s
MSA-DFES | WA6090942 | 3 | MR POTHOLE | Front of boatshed - Ground - Asphalt is cracked and has some potholes | Paving & Roadworks | Asphalt |  | Fail | Fail | 3 | 3 | 1.5 | 2022-10-19 15:38 | 2022-10-26 17:00 | 2022-11-16 13:00 | 2022-10-26 17:00 | 2022-11-16 14:30 |  |  | Works completed as per Tania Cook
MSA-DTWD | WA6105961 | 2 | AWB Co. | Replace the fluorescent tubes in the R017 class room | Electrical | Lighting, Internal | 217.07 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-20 07:39 | 2022-10-24 17:00 | 2022-10-21 07:00 | 2022-10-24 17:00 | 2022-10-21 08:30 |  |  | Attended site and signed in, completed JSA, spoke with fm about works,located room r017, found that switch on wall was also damaged, isolated lighting circuit, replaced tubes and starters, replaced switch on wall, re energised circuit, tested lights and switch and all working as intended, packed up, completed paperwork,signed out **job complete**
MSA-DTWD | WA6107854 | 2 | Lane's Plumbing | House 14 - Bathroom - Blocked shower cubicle drain | Plumbing & Drainage | Drainage |  | Pass | Pass | -1 | -1 | 1.5 | 2022-10-20 09:18 | 2022-10-25 17:00 | 2022-10-20 12:00 | 2022-10-25 17:00 | 2022-10-20 13:30 |  |  | Completed
MSA-MRWA | WA6113097 | 3 | AWB Co. | Ground - eastern stairwell - faulty stairwell light | Electrical | Lighting, Internal | 341.97 | Pass | Pass | -1 | -1 | 1.5 | 2022-10-24 09:00 | 2022-10-31 17:00 | 2022-10-27 06:00 | 2022-10-31 17:00 | 2022-10-27 07:30 |  |  | Attended site and signed in, completed JSA, located light in stairwell, went to wholesaler to pick up parts, returned to site and set up work area, isolated lighting circuit, removed old light, replaced with new, re energised circuit, tested light and working as intended, packed up, cleaned up, completed paperwork, signed out **job complete**
MSA-DTAG | WA6113295 | 0 | Sapio Pty Ltd | L1 comms room door not accessable issues with key pad | Security | Access Control | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-24 10:14 | 2022-10-24 12:14 | 2022-10-24 12:00 | 2022-10-24 14:14 | 2022-10-24 13:30 |  |  | Re terminated lock connections behind the lock.
MSA-DTWD | WA6113588 | 2 | Lane's Plumbing | Faulty gas regulator | Plumbing & Drainage | HWS/Units Electric & Gas |  | Pass | Pass | 0 | 0 | 1.5 | 2022-10-24 12:56 | 2022-10-27 17:00 | 2022-10-27 10:00 | 2022-10-27 17:00 | 2022-10-27 11:30 |  |  | REPLACE FAULTY REGULATOR TO HOUSE 12
MSA-DTWD | WA6125814 | 2 | AWB Co. | The flashing around the ventilation duct is leaking | Building | Ceiling | 335.36 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-25 08:26 | 2022-10-28 17:00 | 2022-10-27 11:30 | 2022-10-28 17:00 | 2022-10-27 13:00 |  |  | Works completed
MSA-DTWD | WA6126178 | 2 | Techworks Electrical | Lights in Female Public toilets outside the restaurant are not working | Electrical | Lighting, Internal | 238.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-25 10:43 | 2022-10-28 17:00 | 2022-10-27 14:00 | 2022-10-28 17:00 | 2022-10-27 15:30 |  |  | Attended site found 2 light in female toilets not workingReplaced lights with LED downlightsMaterials used 2x LED Downlight
MSA-DCA | WA6127789 | 1 | SCAVENGER SUPPLIES PTY LTD | RETROSPECTIVE - Do not attend - Fire alarm incident - 13/10/2022 | Fire Protection Services | Fire Protection - Monitor System | 151.95 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-13 07:00 | 2022-10-13 17:00 | 2022-10-13 08:45 | 2022-10-13 17:00 | 2022-10-13 10:15 | 1 |  | COMPLETED 13/10/2022WORK WAS CONDUCTED AT TIME AND DATE OF RN WORK ON REQUEST OF MUSEUM STAFF***UNAUTHROISED SIG SLIP ATTACHED-UNSIGNED SIG SLIP SENT TO NEIL DUCHAN TO SIGN 27/10/22**PLEASE UPLOAD AUTHORISED SS AND SUBMIT CLAIM ASAP
MSA-DTWD | WA6129385 | 1 | Protek 24/7 Building & Maintenance | Main entrance - Door bolt not engaging on front door. | Building | Doors | 297.65 | Pass | Pass | 0 | 0 | 1.5 | 2022-10-27 14:24 | 2022-10-28 17:00 | 2022-10-28 07:30 | 2022-10-28 17:00 | 2022-10-28 09:00 |  |  | Screws are missing from the bracket and general build up of debris in the holeReplaced all the screws in the brackets and cleaned out the hole
MSA-DFES | WA6132479 | 3 | MR POTHOLE | Workshop- Concrete in workshop floor has deteriorated and is now a trip hazard | Paving & Roadworks | Concreting |  | Fail | Fail | 1 | 1 | 1.5 | 2022-10-31 14:17 | 2022-11-07 17:00 | 2022-11-14 13:00 | 2022-11-07 17:00 | 2022-11-14 14:30 |  |  | Completed
MSA-DTWD | WA6143718 | 2 | AHS Services WA Pty Ltd (Anchor) | Vanity tap is leaking water | Plumbing & Drainage | Water | 240.975 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-01 14:04 | 2022-11-04 17:00 | 2022-11-02 07:30 | 2022-11-04 17:00 | 2022-11-02 09:00 |  |  | nil
MSA-DTAG | WA6144751 | 1 | Sapio Pty Ltd | Custody Area - Basement - Control Room - faulty monitors and cameras - see notes below | Security | CCTV Surveillance | 299.14 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-02 08:53 | 2022-11-03 17:00 | 2022-11-02 10:30 | 2022-11-03 17:00 | 2022-11-02 12:00 |  |  | Rectified viewing issues on Indigo Custody CCTV workstation. All restored and setup okay.
MSA-DTAG | WA6145106 | 0 | Sapio Pty Ltd | Level 2 - SAT Building - secure door to judges area - card reader does not work | Security | Security Management System | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-02 11:08 | 2022-11-02 13:08 | 2022-11-02 13:00 | 2022-11-02 15:08 | 2022-11-02 14:30 |  |  | Found that the L2 lobby door to staff area was not working. Door controller had locked up. Reset board and tested.
MSA-MRWA | WA6145450 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - Administation - Investigate failed UPS 0700 04/11/2022 | Electrical | General Electrical | 303.315 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-02 12:01 | 2022-11-09 17:00 | 2022-11-04 07:00 | 2022-11-09 17:00 | 2022-11-04 08:30 |  |  | On-site to investigate faulty UPS system causing RCBO to trip. Will need to return to investigate as discussed on-site.
MSA-DTWD | WA6145690 | 2 | M Construction (WA) | K004 - Faulty sliding aluminum sliding door - Sliding door coming off track- See notes | Building | Doors | 226.68 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-02 13:59 | 2022-11-07 17:00 | 2022-11-04 08:00 | 2022-11-07 17:00 | 2022-11-04 09:30 |  |  | 1. Cleaned out debris2. Lubed rollers3. Installed packers to prevent door coming off track4. Installed mulion
MSA-DTWD | WA6147345 | 2 | AWB Co. | Lights over reception not working | Electrical | Lighting, Internal | 312.22 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-03 06:35 | 2022-11-07 17:00 | 2022-11-07 13:00 | 2022-11-07 17:00 | 2022-11-07 14:30 |  |  | Attended site and signed in,completed jsa ,spoke with admin staff and they showed us which lights they wanted working, took it old lamps and went to wholesaler to pick up replacements, returned to site, replaced lights and working as intended , cleaned up, packed up, completed paperwork, signed out**job completed**
MSA-DTWD | WA6147955 | 2 | AWB Co. | A Block - Client Services Back Office - Light flickering and switching on and off | Electrical | Lighting, Internal | 250.525 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-03 11:16 | 2022-11-08 17:00 | 2022-11-07 10:00 | 2022-11-08 17:00 | 2022-11-07 11:30 |  |  | Attended site signed in jsa completed. Found faulty flickering light reported by staff. Replaced with led panel.Job completed
MSA-DTAG | WA6148283 | 1 | Australian HVAC Services Pty. Ltd. | Level 2 - Sheriff’s Office - Air conditioning not cooling. Office is very hot | Air Conditioning | Room Air Conditioners | 427.92 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-03 13:50 | 2022-11-04 17:00 | 2022-11-03 14:00 | 2022-11-04 17:00 | 2022-11-03 15:30 |  |  | Attend site. Access Sherriffs office and check AC. Found office area to be warm. Further investigation found other contractors having issues with the portable chiller not working correctly. Speak with contractors and the said it would be back on soon. Access Sherriffs office and explain the situation. Found chiller to come back on and office has become to cool down.
MSA-DTWD | WA6148379 | 1 | Australian Airconditioning Services Pty Ltd | AC not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 333.56 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-03 16:29 | 2022-11-04 17:00 | 2022-11-04 10:30 | 2022-11-04 17:00 | 2022-11-04 12:00 |  |  | Found LP switch tripped and holding out compressor. Reset switch and tested and monitored system. System fully operational.
MSA-DCA | WA6148724 | 1 | Techworks Electrical | Lollipop light to the left of sculpture (Perth station side) is loose and needs securing-see notes | Electrical | Lighting, External | 143.595 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-04 08:30 | 2022-11-07 17:00 | 2022-11-04 09:00 | 2022-11-07 17:00 | 2022-11-04 10:30 |  |  | Found light was one that I had already fixed on the 4am routine maintenace.
MSA-DFES | WA6148857 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Unisex ambulant toilet-fan is making loud noises - see notes | Electrical | General Electrical | 427.93 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-04 09:43 | 2022-11-11 17:00 | 2022-11-07 08:25 | 2022-11-11 17:00 | 2022-11-07 09:55 |  |  | Matthew Kenney (07/11/2022) - Work NoteArrived onsite at 8:25 to investigate noisy fan in unisex toilet, found a noisy wall exhaust with a loose bearing and is beyond repair, collected replacement fan from wholesaler, returned to site and replaced faulty fan with new one, tested ok, advised staff of works and left site at 9:55.
MSA-DTAG | WA6149014 | 1 | AWB Co. | Upstairs - Kitchen - No power in kitchen - See notes below | Electrical | General Electrical | 288.22 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-04 11:17 | 2022-11-07 17:00 | 2022-11-04 12:30 | 2022-11-07 17:00 | 2022-11-04 14:00 |  |  | Attended site and signed in, completed jsa, spoke with security about job and got keys, located kitchen upstairs, located circuit, unplugged all appliances and reset circuit, plugged appliances in 1 by 1 and found the kettle tripped the circuit, tested the kettle and was a dead short, re energised circuit and ran all appliances, everything working as intended, disposed of kettle, went to reception to give back keys and she said printer PowerPoint was faulty. Went back up there to check it out. There was a breaker tripped in board, reset. All good now. completed paperwork, signed out **job completed**
MSA-DTWD | WA6151668 | 1 | ACTION GLASS & ALUMINIUM | A block - A106 - Broken glass window to a106 - see notes | Glazing | Window Glass | 950.61 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-07 08:09 | 2022-11-08 17:00 | 2022-11-07 15:30 | 2022-11-08 17:00 | 2022-11-07 17:00 |  |  | ATTENDED SITEPATCHED TO SECURE & MAKE SAFE ONLY BROKEN WINDOW AS REQUESTED6.38 CLEAR LAMINATED SAFETY GLASS1-1300 X 10001-950 X 1000PLUS 5 L/M OF DOUBLE SIDED TAPE, 3 SQM OF SAFETY FILM AND 2 TUBES OF SILICONE USED
MSA-DCA | WA6151706 | 1 | Techworks Electrical | Stage door - No 3 phase power to BMS system. | Electrical | Distribution Board | 183.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-07 08:22 | 2022-11-08 17:00 | 2022-11-07 10:00 | 2022-11-08 17:00 | 2022-11-07 11:30 |  |  | Tasks completed 1. arrived and met with the HVAC guys. Went downstairs and found the board had no power. Found that it was a tripped main breaker at the other underground board. Reset. Tested and all working well. The HVAC guys where running tests and checking all of their stuff before they took off.
MSA-DTWD | WA6154492 | 3 | AHS Services WA Pty Ltd (Anchor) | N115 - Leaking tap in N115a | Plumbing & Drainage | Water | 146.27 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-07 13:04 | 2022-11-14 17:00 | 2022-11-08 12:15 | 2022-11-14 17:00 | 2022-11-08 13:45 |  |  | Removed and serviced tap
MSA-DTWD | WA6154664 | 1 | Equans Mechanical Services Australia | Air conditioning cooling mode not working intermittently | Air Conditioning | Room Air Conditioners | 174.555 | Fail | Fail | 0 | 0 | 1.5 | 2022-11-07 15:08 | 2022-11-08 17:00 | 2022-11-09 08:00 | 2022-11-08 17:00 | 2022-11-09 09:30 |  |  | Attended site, to classroom AT238.i tested EC, checked water pump, Fan belts, all OK. Check everything and found everything to be working.
MSA-DCA | WA6155929 | 3 | Techworks Electrical | Level 2 - Male Front of House Toilet Sign - Sign needs new bulb - See notes | Electrical | General Electrical | 316.63 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-08 15:09 | 2022-11-15 17:00 | 2022-11-11 09:00 | 2022-11-15 17:00 | 2022-11-11 10:30 |  |  | Work has been carried out to scope. rectified faulty lighting to male sign toilet on level 2, used 2x new light bulbs from HMT stock
MSA-DCA | WA6155959 | 3 | Techworks Electrical | Ground Floor - Bottom of spiral staircase - No power to phase 3 outlet. Please reinstate | Electrical | General Electrical | 306.63 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-08 15:48 | 2022-11-15 17:00 | 2022-11-14 08:30 | 2022-11-15 17:00 | 2022-11-14 10:00 |  |  | Spoke with Hayden about the job as he investigated the issue to begin with, carrying on from his investigation I also had a look where the cable goes up into the slab and gets lost, where he lost the cable under the floorboards I knew of a little back room that also has cabling coming through it. I lifted up the floorboards in the little room and there was a 3ø cable with plug top on the end of it, we belled out the cable and sure enough it was the cable feeding the external GPO. There is an isolator in this room that is used to plug in the lead and by doing so energising the external GPO next to the stairwell. no material used
MSA-DTWD | WA6156397 | 2 | AWB Co. | Various lights faulty | Electrical | Lighting, Internal | 333.805 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-09 07:47 | 2022-11-11 17:00 | 2022-11-11 11:00 | 2022-11-11 17:00 | 2022-11-11 12:30 |  |  | Attended site signed in jsa completed. Found 3 lights not working replaced tubes with new 28w tubes.Tested operational.Job completed
MSA-DCA | WA6156464 | 2 | Techworks Plumbing | Basement - Security control room - Zip tap is not working | Plumbing & Drainage | Water | 416.38 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-09 08:11 | 2022-11-14 17:00 | 2022-11-09 12:00 | 2022-11-14 17:00 | 2022-11-09 13:30 |  |  | Lam Nguyen (09/11/2022) - Technician Note- arrived at perth museum and signed in- inspected zip tap in security room- filter needed changing - went to get a new filter required - arrived back at the museum - changed the filter for the zip tap- flushed the new filter - cleaned up area - signed out
MSA-DTAG | WA6156760 | 0 | Sapio Pty Ltd | Ground floor - lobby - access passes in staff turnstile not working | Security | Access Control | 204.44 | Fail | Fail | 0 | 0 | 1.5 | 2022-11-09 10:12 | 2022-11-09 12:12 | 2022-11-09 13:00 | 2022-11-09 14:12 | 2022-11-09 14:30 |  |  | Attended site, held up by Fire Drill in DMJC trying to sign in. Checked over reported issue. All working correctly. Job completed.
MSA-DTWD | WA6159269 | 3 | AWB Co. | Welding Workshop - 3G5 - Broken light fitting above bay 15 and protective guard missing | Electrical | Lighting, Internal | 368.905 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-10 13:39 | 2022-11-17 17:00 | 2022-11-14 11:30 | 2022-11-17 17:00 | 2022-11-14 13:00 |  |  | Attended site signed in jsa completed. Found light faulty and also no diffuser. Replaced with new WP led fitting.Job completed
MSA-DTAG | WA6165955 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 4 - Male Public Toilet - Public male toilet is blocked. At risk of flooding. | Plumbing & Drainage | Toilets/Cisterns | 188.655 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-11 10:56 | 2022-11-14 17:00 | 2022-11-11 12:00 | 2022-11-14 17:00 | 2022-11-11 13:30 |  |  | Used plunger and sprit of salts to clear stubborn urinal blockage
MSA-DTAG | WA6165990 | 2 | AWB Co. | Level 10 - Banksia Marriage room and Heath’s Office - Light needing replacement | Electrical | Lighting, Internal | 458.025 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-11 11:22 | 2022-11-16 17:00 | 2022-11-15 12:15 | 2022-11-16 17:00 | 2022-11-15 13:45 |  |  | Job complete
MSA-DTAG | WA6166468 | 2 | Schindler Lifts Australia | Lift not working - no power | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5 | 2022-11-11 16:14 | 2022-11-16 17:00 | 2022-11-15 11:20 | 2022-11-16 17:00 | 2022-11-15 12:50 |  |  | Works completed - close out at $0
MSA-DTWD | WA6190889 | 2 | AWB Co. | E" Block (Electrical Section) - Bay 1 - Dangerous three phase outlet | Electrical | General Electrical | 251.755 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-16 11:14 | 2022-11-21 17:00 | 2022-11-21 07:00 | 2022-11-21 17:00 | 2022-11-21 08:30 |  |  | Attended ute and signed in. Completed JSA. Liaised with site about works going ahead. Located E block gpo loose. Isolated power. Removed gpo. Resecured gpo with thicker screws. Made sure it was secure. Notified lecturer that was in use of room. Notified fm of works completed. **job complete**
MSA-DTAG | WA6191258 | 1 | Seme Solutions Pty Ltd | SEME CCTV and Access Control equipment needs reconnecting in court custody | Security | CCTV Surveillance | 209.82 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-16 14:34 | 2022-11-17 17:00 | 2022-11-16 15:00 | 2022-11-17 17:00 | 2022-11-16 16:30 |  |  | Attended custody control room, reconnected and tidied security equipment cabling/hardware after recent renovations and confirmed all devices operational.
MSA-DTWD | WA6206215 | 1 | AWB Co. | B313 Light switch broken and not working. No functioning lighting for classroom. | Electrical | Lighting, Internal | 300.5125 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-17 10:34 | 2022-11-18 17:00 | 2022-11-18 07:00 | 2022-11-18 17:00 | 2022-11-18 08:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located faulty light switch. Went to wholesaler for parts. Returned. Replaced with new 20a switch. Took pics. Completed paperwork. Signed out.Job complete
MSA-DFES | WA6206531 | 2 | Australian HVAC Services Pty. Ltd. | Wellness Office - Continuous whirring coming from HVAC ducting - see notes | Air Conditioning | Building HVAC Maintenance (Major Plant) | 193.43 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-17 10:51 | 2022-11-22 17:00 | 2022-11-18 09:00 | 2022-11-22 17:00 | 2022-11-18 10:30 |  |  | Attend site. Access level 2 wellness off and check noise comming from ceiling. Access ceiling and remove ceiling tile. Check for noise and found to be coming from around buildings external cladding. Noise appears to be cause by air on outside of building. Found no noise coming from Airconditioning systems. Require builder to further investigate. There has been some previous works carried out in the area to repair a water leak.
MSA-DTWD | WA6208289 | 1 | Protek 24/7 Building & Maintenance | AT105-Leak through window - photo's to follow in email | Roofing | Metal Roofing | 278.9 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-17 16:06 | 2022-11-18 17:00 | 2022-11-18 10:30 | 2022-11-18 17:00 | 2022-11-18 12:00 |  |  | BRAF Declined
MSA-DTWD | WA6249270 | 1 | Lane's Plumbing | House 809 - Water meter faulty | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.5 | 2022-11-21 10:59 | 2022-11-22 17:00 | 2022-11-21 13:00 | 2022-11-22 17:00 | 2022-11-21 14:30 |  |  | Completed
MSA-DFES | WA6249714 | 1 | AWB Co. | Tunic Room Door - internal hallway - electronic button isnt working - See Notes | Building | General Building | 365.895 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-21 14:01 | 2022-11-22 17:00 | 2022-11-22 07:30 | 2022-11-22 17:00 | 2022-11-22 09:00 |  |  | Attended site and completed JSA. Liaised with sites about works going ahead. Located faulty automatic door. Investigated door not operating correctly. Upon investigation found to be, faulty push button switch in hallway to change room. Picked up parts. Supplied and replaced with new Green push button. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6249744 | 2 | Equans Mechanical Services Australia | B28 - Low aircon speed even when set to high. | Air Conditioning | Room Air Conditioners | 782.1675 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-21 14:19 | 2022-11-24 17:00 | 2022-11-22 14:30 | 2022-11-24 17:00 | 2022-11-22 16:00 |  |  | Attended call, advised insufficient airflow on high speed. Checked low/ high speed on unit -ok. Checked airflow- no air flow. Checked direction of fan - found fan going in wrong direction. Checked wiring noted that wiring had been modified to accommodate overall greenhouse system control. Arranged with office to send electrician to rectify.
MSA-DCA | WA6250529 | 1 | Techworks Electrical | External Ground - Rear of PICA - Light coming off the wall | Electrical | Lighting, External | 193.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-22 08:59 | 2022-11-23 17:00 | 2022-11-22 15:00 | 2022-11-23 17:00 | 2022-11-22 16:30 |  |  | Re attached light fitting to wall.
MSA-DCA | WA6255397 | 0 | Techworks Plumbing | Hackett Hall - Multiple toilets faulty - see notes for locations | Plumbing & Drainage | Toilets/Cisterns | 183 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-23 10:24 | 2022-11-23 12:24 | 2022-11-23 11:00 | 2022-11-23 14:24 | 2022-11-23 12:30 |  |  | Flush plate issue was a broken spring loaded clip. I used the clip from another plate that was damaged at the museum to repair and replace. Running cistern, I removed the locking clip and blanking plate from the internal of the cistern to allow for full movement as it got stuck on flush. Tested multiple times with no issuesBlocked basin issues- baffle in floorwaste was not set in and had twisted causing the drain to be slow.- I removed the bottle trap and cleared hair from the base, there are no grates in the basin wastes due to the design the bottle trap had caught everything. toilet seat loose was due to a missing locking clip. Parts sourced from storage onsite and fixed
MSA-DFES | WA6255556 | 2 | Protek 24/7 Building & Maintenance | Double gate, side entrance station front - holes for drop bolts do not line up correctly - see notes | Building | Steel Fencing & Gates | 332.61 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-23 11:30 | 2022-11-28 17:00 | 2022-11-28 13:00 | 2022-11-28 17:00 | 2022-11-28 14:30 |  |  | Install chem set bolts and brackets
MSA-DTWD | WA6255825 | 2 | Techworks Plumbing | G05 - Dripping tap over basin | Plumbing & Drainage | Water | 330.61 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-23 14:19 | 2022-11-28 17:00 | 2022-11-24 10:30 | 2022-11-28 17:00 | 2022-11-24 12:00 |  |  | Kyle Pace (24/11/2022) - Work NoteArrived on sight signed in at office met Lam the facility manager he showed me the leaking tap, pulledt tap set apart and performed tap service reseated and replaced washer applied some spindal lube and put tap back together to commission with no leaks
MSA-DTWD | WA6255869 | 1 | AWB Co. | Northern end of workshops - Colourbond flashing has come loose - see notes | Roofing | Metal Roofing | 314.73 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-23 14:54 | 2022-11-24 17:00 | 2022-11-24 07:00 | 2022-11-24 17:00 | 2022-11-24 08:30 |  |  | attended site and completed jsa, we had a inspection with a staff member then set up our ladder safely. We then removed the temporary tape and installed multiple metal screws to secure the flashings to the structural steel of the builing. Cleaned up.Job completed
MSA-DTWD | WA6258068 | 1 | AWB Co. | Toilets and staff room lights not working. | Electrical | Lighting, Internal | 174.77 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-25 10:17 | 2022-11-28 17:00 | 2022-11-25 14:00 | 2022-11-28 17:00 | 2022-11-25 15:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located k block staff room. Found to be lights tripping when trying to turn on. Isolated circuit. Removed one panel. Energised. Found to be faulty ballast. Supplied and replaced ballast. Put panel back into slot. Energised. All working correctly. Notified of works. **job complete**
MSA-DCA | WA6258081 | 2 | Protek 24/7 Building & Maintenance | White picket fence near Padbury Court requires repair | Building | Steel Fencing & Gates | 161.54 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-25 10:33 | 2022-11-30 17:00 | 2022-11-30 07:00 | 2022-11-30 17:00 | 2022-11-30 08:30 |  |  | Fence needs replacing, not a security issue as it’s just a decorative fence. Measure to replace
MSA-MRWA | WA6290963 | 3 | AWB Co. | near desk 240 - Failed LED light | Electrical | Lighting, Internal | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 11:06 | 2022-12-05 17:00 | 2022-12-05 06:30 | 2022-12-05 17:00 | 2022-12-05 08:00 |  |  | Attended site and signed in, completed jsa, located faulty lighting on level 2, got new drivers from level 9, returned to level 2 and set up work area, removed light and replaced with working light from other location to check programming, replaced driver in faulty fitting, put faulty fitting back up, found 2x light that will need to be programmed as drivers have been replaced , told site, packed up, completed paperwork, signed out , job complete
MSA-DCA | WA6290989 | 2 | Techworks Electrical | Ground - Amphitheatre - 4 x Lollipop lights not working - see notes below | Electrical | Lighting, External | 471.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 11:21 | 2022-12-01 17:00 | 2022-11-30 13:30 | 2022-12-01 17:00 | 2022-11-30 15:00 |  |  | Completed replacement of three globes. Unable to see if they are working due to day time light. Will check on the 4am walkaround on Friday (2/12/22)
MSA-DCA | WA6291091 | 2 | Techworks Electrical | Conservation Lab, old darkroom - Disconnected GPO to be reinstated and made safe. | Electrical | General Electrical | 170.45 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 12:06 | 2022-12-01 17:00 | 2022-11-30 15:00 | 2022-12-01 17:00 | 2022-11-30 16:30 |  |  | Tasks completed 1. re fed GPO in level 3 with a new feed as the feed it had, had a fault from the switchboard upgrade two years ago and was tagged out. 2. tested and all working well.
MSA-DCA | WA6291152 | 2 | Protek 24/7 Building & Maintenance | G Block - Ground - Splashback around female toilet sink required re-fixing | Building | Internal Walls | 202.94 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 12:36 | 2022-12-01 17:00 | 2022-11-30 08:30 | 2022-12-01 17:00 | 2022-11-30 10:00 |  |  | Used construction adhesive to hold all panels back together
MSA-DCA | WA6291274 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 in fault | Refrigeration | Chiller | 304.065 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 13:28 | 2022-11-29 17:00 | 2022-11-28 17:00 | 2022-11-29 17:00 | 2022-11-28 18:30 |  |  | Attended site. Signed in and gained access. Checked over bms and found chiller 1 in fault. Reset on bms and tested operation. Fault cleared. Accessed external plantroom and checked over chiller interface. Found no alarms on either chiller and history shows, fault on 26/11 but chiller auto reset. Plant operating as required. Confirmed with schneider tech. Recommend installing ventilation to external plantroom to remove heat load. Completed paperwork.
MSA-DTWD | WA6291344 | 1 | High Tech Pest Control | Ground - E74 External (East End) - Large Bee population present | Pest Control | General Pest | 425.27 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 14:04 | 2022-11-29 17:00 | 2022-11-29 06:50 | 2022-11-29 17:00 | 2022-11-29 08:20 |  |  | applied dust to entry points and into void of brick wall. 2 tech spotter/working at heights
MSA-DTWD | WA6291385 | 1 | Techworks Plumbing | Male toilet area - Ground floor adjacent to Cafe - Male toilet (student) urinal is blocked | Plumbing & Drainage | Toilets/Cisterns | 248.92 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-28 14:29 | 2022-11-29 17:00 | 2022-11-29 07:00 | 2022-11-29 17:00 | 2022-11-29 08:30 |  |  | Joshua Salmon (29/11/2022) - Work NoteAttended Murdoch and signed in.Located bathroom with blocked urinal.Drain was completely blocked on arrival, I removed the purple mate and used Bowl guard and plunger to clear blockage.Managed to get the drain moving, I then removed the locking clip in the trap which was covered in hair and uric acid build up. finished with more bowl guard and a plunge to completely clear trap. test and replace parts removed
MSA-DTAG | WA6293004 | 3 | PPM Project Painting & Maintenance | CLC - level 6 balcony - Graffiti stating “pengu” on two edges. | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 1.5 | 2022-11-29 15:55 | 2022-12-06 17:00 | 2022-12-01 12:00 | 2022-12-06 17:00 | 2022-12-01 13:30 |  |  | Removal of graffiti
MSA-MRWA | WA6293007 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | MD bathroom - sensor light is failing - see notes | Electrical | General Electrical | 394.315 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-29 15:58 | 2022-11-30 17:00 | 2022-11-30 10:30 | 2022-11-30 17:00 | 2022-11-30 12:00 |  |  | Cameron Vasey (30/11/2022) - Work NoteReplaced sensor in bathroom with 360 degree surface mount. Set to 30 min incase they have shower. Tested and cleaned up
MSA-DTAG | WA6294316 | 3 | AWB Co. | President’s Chambers - dimmer light switch faulty | Electrical | Lighting, Internal | 307.275 | Pass | Pass | -1 | -1 | 1.5 | 2022-11-30 14:39 | 2022-12-07 17:00 | 2022-12-02 12:30 | 2022-12-07 17:00 | 2022-12-02 14:00 |  |  | Job complete
MSA-DTWD | WA6294449 | 2 | Australian Airconditioning Services Pty Ltd | Ceiling cassette split AC unit leaking water | Air Conditioning | Ducted Split System | 289.38 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-30 16:52 | 2022-12-05 17:00 | 2022-12-05 11:00 | 2022-12-05 17:00 | 2022-12-05 12:30 |  |  | complete
MSA-DTWD | WA6294452 | 2 | Australian Airconditioning Services Pty Ltd | Wall split AC unit leaking water | Air Conditioning | Ducted Split System | 378.56 | Pass | Pass | 0 | 0 | 1.5 | 2022-11-30 16:55 | 2022-12-05 17:00 | 2022-12-05 09:30 | 2022-12-05 17:00 | 2022-12-05 11:00 |  |  | complete
MSA-DTAG | WA6298230 | 3 | Midolo Building Services | Level 4 - Female public toilet Hay Street side - Towel Dispenser (see notes) | Building | General Building | 198.7 | Pass | Pass | -1 | -1 | 1.5 | 2022-12-01 08:25 | 2022-12-08 17:00 | 2022-12-02 11:15 | 2022-12-08 17:00 | 2022-12-02 12:45 |  |  | repairs made to bin cover - now operational
MSA-DTWD | WA6298346 | 0 | ACTION GLASS & ALUMINIUM | B Block - Level 0-1 - West exit door - Broken Glass door panel | Glazing | Door Glass | 218.95 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-01 09:19 | 2022-12-01 11:19 | 2022-12-01 11:15 | 2022-12-01 13:19 | 2022-12-01 12:45 |  |  | ATTENDED SITEREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-690 X 745
MSA-DTWD | WA6300429 | 2 | CONNECT SECURITY SYSTEMS | CCTV System not functioning properly - see notes | Security | CCTV Surveillance | 247.21 | Fail | Fail | 0 | 0 | 1.5 | 2022-12-02 10:37 | 2022-12-07 17:00 | 2022-12-09 10:50 | 2022-12-07 17:00 | 2022-12-09 12:20 |  |  | Completed 9/12/2022
MSA-DCA | WA6336785 | 0 | Critical Fire Protection & Training | Reset fire panel after isolation | Fire Protection Services | Fire Protection - Monitor System | 393.925 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-03 21:24 | 2022-12-03 23:24 | 2022-12-03 21:30 | 2022-12-04 01:24 | 2022-12-03 23:00 |  |  | Received call out and left immediately.When we were in Subiaco, Critical Fire received a call advising the call out was no longer required and to stand down.
MSA-DCA | WA6357319 | 0 | Techworks Plumbing | Jubilee Admin - Ground Level - UAT 1&2 - Toilets are not flushing | Plumbing & Drainage | Toilets/Cisterns | 334.74 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-05 12:24 | 2022-12-05 14:24 | 2022-12-05 12:30 | 2022-12-05 16:24 | 2022-12-05 14:00 |  |  | Attended site and signed in at the security officewent to jubilee building to see why the toilets weren’t flushing the lady at reception had said that they were blocked upwe flushed all the toilets and found they had a slight blockagewe plunged the toilets we ran all appliances and flushed toilets paper down the drain to make sure they did not block up againCleaned up and left sitecompleted paperwork
MSA-DTWD | WA6358207 | 3 | COMMERCIAL PLUMBING AND GAS | Leaking tap in hand basin | Plumbing & Drainage | Water | 729.855 | Fail | Fail | 0 | 0 | 1.5 | 2022-12-06 08:20 | 2022-12-13 17:00 | 2022-12-15 17:00 | 2022-12-13 17:00 | 2022-12-15 18:30 |  |  | replaced 4 taps and repaired cistern
MSA-DTWD | WA6358761 | 3 | GRAFFITI FORCE PTY LTD | North West Corner - External Graffiti | Building | External Walls | 307 | Pass | Pass | -1 | -1 | 1.5 | 2022-12-06 09:55 | 2022-12-13 17:00 | 2022-12-09 07:00 | 2022-12-13 17:00 | 2022-12-09 08:30 |  |  | REMOVAL OF GRAFFITI FROM NORTH WEST CORNER OF B2
MSA-DTAG | WA6359374 | 1 | AWB Co. | Registry Hallway - Flickering light in registry office | Electrical | Lighting, Internal | 217.965 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-06 15:11 | 2022-12-07 17:00 | 2022-12-07 10:30 | 2022-12-07 17:00 | 2022-12-07 12:00 |  |  | Attended site signed in jsa completed. Found two lights flickering in office area. Removed and replaced new tubes and new starters. Tested operational.Job completed
MSA-DTAG | WA6361746 | 3 | Midolo Building Services | Sallyport - door closer has failed - unit leaking | Building | Doors | 735.92 | Pass | Pass | -1 | -1 | 1.5 | 2022-12-08 12:40 | 2022-12-15 17:00 | 2022-12-09 09:45 | 2022-12-15 17:00 | 2022-12-09 11:15 |  |  | new door closer installed
MSA-DTWD | WA6362276 | 1 | COMMERCIAL PLUMBING AND GAS | Oil separator will not turn off when set to automatic | Plumbing & Drainage | HWS/Units Electric & Gas | 213.925 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-09 09:18 | 2022-12-12 17:00 | 2022-12-09 14:30 | 2022-12-12 17:00 | 2022-12-09 16:00 |  |  | repaired float, installed new bracket
MSA-DFES | WA6363462 | 0 | Critical Fire Protection & Training | fire panel issue says charger fault | Fire Protection Services | Fire Protection - Monitor System | 393.925 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-11 09:20 | 2022-12-11 11:20 | 2022-12-11 10:45 | 2022-12-11 13:20 | 2022-12-11 12:15 |  |  | Upon arrival, the charger fail LED on the EWIS was in fault.There were no faults present on fire detection system.System fault on the code red, switched the EWIS to manual and reset the EWIS which got rid of the charger fail LED and also cleared the system fault on the code red.Since resetting, the charger fail hasn’t come back which indicates that there may have been a mains issue momentarily as it was also noted by staff at DFES that the back up generator was kicked in before their arrival.All systems normal with no faults upon departure.
MSA-DTAG | WA6364752 | 1 | AWB Co. | Custody stairs-Flickering light over custody stairs | Electrical | Lighting, Internal | 204.505 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-12 14:30 | 2022-12-13 17:00 | 2022-12-13 07:00 | 2022-12-13 17:00 | 2022-12-13 08:30 |  |  | Attended site signed in jsa completed. At first site didnt know where light was took time to find. Found light and replaced with tube had to source as special kind.Tested operationalJob completed
MSA-DCA | WA6364798 | 0 | Techworks Electrical | James St Bollards - Bollards are slow to lower - see notes below | Electrical | General Electrical | 183.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-12 15:12 | 2022-12-12 17:12 | 2022-12-12 15:30 | 2022-12-12 19:12 | 2022-12-12 17:00 |  |  | Reset the bollards and they where up and working and confirmed with the site contact as well.
MSA-MRWA | WA6365589 | 1 | Schindler Lifts Australia | Lift 3 - stuck on level 4 - doors open | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.5 | 2022-12-13 11:02 | 2022-12-14 17:00 | 2022-12-13 13:15 | 2022-12-14 17:00 | 2022-12-13 14:45 |  |  | to be closed out at $0 cost
MSA-DCA | WA6365766 | 0 | Techworks Electrical | Ground floor - Office -elctrical switch gone into wall | Electrical | General Electrical | 202.295 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-13 12:20 | 2022-12-13 14:20 | 2022-12-13 13:30 | 2022-12-13 16:20 | 2022-12-13 15:00 |  |  | Replaced 1x light switch and mech in crc offices.isolated from DB5re labelled plate with W8 pin.tested light switch for operation.cleaned up work area and signed out
MSA-DCA | WA6369735 | 2 | Techworks Electrical | 3x lights not working. | Electrical | Lighting, External | 183.015 | Pass | Pass | -1 | -1 | 1.5 | 2022-12-14 08:58 | 2022-12-19 17:00 | 2022-12-15 09:00 | 2022-12-19 17:00 | 2022-12-15 10:30 |  |  | Found lighting working it’s just not PCC lighting it’s STC lighting so they have the control over them.
MSA-DTAG | WA6370958 | 1 | Sapio Pty Ltd | L6-court room 607-insetion button broken and cannot unlock judicial door | Security | Access Control | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-14 10:29 | 2022-12-15 17:00 | 2022-12-14 14:00 | 2022-12-15 17:00 | 2022-12-14 15:30 |  |  | Attended site. Performed full initialisation on Controller. Tested In-Session button, tested OK.
MSA-DCA | WA6372221 | 1 | GPS Plumbing & Gas Services PtyLtd | Black swan office-sewerage smell & it’s very strong coming from Air con | Plumbing & Drainage | Sewage Treatment Plant | 196.165 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-14 11:47 | 2022-12-15 17:00 | 2022-12-14 13:00 | 2022-12-15 17:00 | 2022-12-14 14:30 |  |  | Investigated the strong smell that was coming from the aircon. We found out that people are using space behind the office as a toilet so the smell is just finding its way into the building
MSA-MRWA | WA6373522 | 3 | Automatic Fire Protection (ARA) | Fire panel Southern entrance - Investigate Fire Panel fault Z1 ST:COV FLT SENSOR FAULT 1:1 | Fire Protection Services | Fire Protection - Monitor System | 564.53 | Pass | Pass | -1 | -1 | 1.5 | 2022-12-14 14:48 | 2022-12-21 17:00 | 2022-12-16 09:30 | 2022-12-21 17:00 | 2022-12-16 11:00 |  |  | Intermittent FIP fault caused by faulty MCP on front of panel. Resistor also failed. Replaced resistor and flush mount conventional MCP. Faultcleared, tested okay
MSA-DTAG | WA6376471 | 3 | Midolo Building Services | Level 3 - Staff toilet behind Court 31 - Soap dispenser & toilet roll holder faulty- see notes | Building | Internal Walls | 325.76 | Fail | Fail | 7 | 7 | 1.5 | 2022-12-15 15:50 | 2022-12-22 17:00 | 2023-02-09 08:00 | 2022-12-22 17:00 | 2023-02-09 09:30 |  |  | SOAP DISPENSER ISECURED & MISSING TOILET ROLL HOLDERS REPLACED
MSA-DFES | WA6379023 | 1 | AWB Co. | SO PPC Store - sliding door is faulty | Building | Doors | 200.825 | Fail | Fail | 0 | 0 | 1.5 | 2022-12-19 08:48 | 2022-12-20 17:00 | 2022-12-21 10:30 | 2022-12-20 17:00 | 2022-12-21 12:00 |  |  | Reattached roller door to roller and service door. Cleaned up work area. Job Complete
MSA-DTWD | WA6381840 | 3 | GRAFFITI FORCE PTY LTD | Level B4-graffiti tagging external walls | Cleaning | Graffiti | 359 | Pass | Pass | -1 | -1 | 1.5 | 2022-12-19 15:13 | 2022-12-28 17:00 | 2022-12-21 06:00 | 2022-12-28 17:00 | 2022-12-21 07:30 |  |  | REMOVAL OF GRAFFITI FROM EXTERNAL WALLS OF B5
MSA-DTWD | WA6383605 | 3 | AWB Co. | 4 cracked electrical GPO on wall | Electrical | General Electrical | 284.92 | Fail | Fail | 1 | 1 | 1.5 | 2022-12-20 11:46 | 2022-12-29 17:00 | 2023-01-03 10:30 | 2022-12-29 17:00 | 2023-01-03 12:00 |  |  | Attended site signed in jsa completed. Found faulty gpos and isolated removed from wall also renovation happening to wall getting patched up and no longer needed. Removed cabling also.Job completed
MSA-DCA | WA6383720 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Old Jail - Volunteers Hub - Aircon unit is working | Air Conditioning | Room Air Conditioners | 259.01 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-20 12:50 | 2022-12-21 17:00 | 2022-12-20 15:00 | 2022-12-21 17:00 | 2022-12-20 16:30 |  |  | Attended site. Investigated ac not working in the old gaol. Found FCU OG-07 in heating mode and not switching to cooling. Checked over other units and confirmed all units were running cooling as units are linked. Power cycled unit to reset controls. Tested operation of units, all running cooling 22.5°c. There's still commissioning works required by Mitsubishi
MSA-DCA | WA6390708 | 1 | Techworks Electrical | Geology Building - Level 1 - Female Toilets - sensor light isnt working | Electrical | General Electrical | 183.015 | Pass | Pass | 0 | 0 | 1.5 | 2022-12-22 12:00 | 2022-12-23 17:00 | 2022-12-23 14:00 | 2022-12-23 17:00 | 2022-12-23 15:30 |  |  | Cycled switch to turn sensor on and off, no fault evident, cycled another 2 x times and could not get the fault to appear again. have let lighting control RM Contractor know to look out on the next RM test and report.
MSA-DTAG | WA6393798 | 3 | Midolo Building Services | Levels 7, 8 & 9 - Missing toilet roll holders that need to be replaced (see notes) | Plumbing & Drainage | Toilets/Cisterns | 499.66 | Fail | Fail | 1 | 1 | 1.5 | 2022-12-29 10:11 | 2023-01-06 17:00 | 2023-01-10 07:45 | 2023-01-06 17:00 | 2023-01-10 09:15
MSA-DTAG | WA6394429 | 3 | Sapio Pty Ltd | Basement - interview room 2 - security camera lens was scratched - see notes | Security | CCTV Surveillance | 1764.42 | Fail | Fail | 0 | 0 | 1.5 | 2022-12-30 15:42 | 2023-01-09 17:00 | 2023-01-10 07:15 | 2023-01-09 17:00 | 2023-01-10 08:45
MSA-DFES | WA6400026 | 0 | Australian HVAC Services Pty. Ltd. | BMS - is faulty - please see Blake | Air Conditioning | Building HVAC Maintenance (Major Plant) | 193.43 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-03 09:01 | 2023-01-03 11:01 | 2023-01-03 09:30 | 2023-01-03 13:01 | 2023-01-03 11:00
MSA-DTWD | WA6400109 | 1 | Securex Security Systems & Services | A Block - A48 - Alarm panels indicating alarms in the system | Security | Monitoring | 388.75 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-03 09:07 | 2023-01-04 17:00 | 2023-01-03 13:15 | 2023-01-04 17:00 | 2023-01-03 14:45
MSA-DTWD | WA6400543 | 3 | AWB Co. | Switch for H/W unit broken and stuck in “on” position | Electrical | General Electrical | 300.55 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-03 14:09 | 2023-01-10 17:00 | 2023-01-10 09:30 | 2023-01-10 17:00 | 2023-01-10 11:00
MSA-DFES | WA6400607 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Bathroom 4 - Tap has corroded and wont secure | Plumbing & Drainage | Water | 397.095 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-03 15:40 | 2023-01-10 17:00 | 2023-01-04 12:40 | 2023-01-10 17:00 | 2023-01-04 14:10
MSA-DTAG | WA6402221 | 1 | Gilmour & Jooste Electrical | Custody Lower - Cell 4 & surrounding - Police corridor water leaking through light fixture-see notes | Electrical | Lighting, Internal | 209.31 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-05 09:01 | 2023-01-06 17:00 | 2023-01-06 07:00 | 2023-01-06 17:00 | 2023-01-06 08:30
MSA-DTWD | WA6404860 | 1 | AWB Co. | Garden area - External GPO adjacent to water tank - Faulty external GPO | Electrical | Distribution Board | 328.12 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-09 09:44 | 2023-01-10 17:00 | 2023-01-10 07:00 | 2023-01-10 17:00 | 2023-01-10 08:30
MSA-DCA | WA6405504 | 2 | Techworks Plumbing | GEO / Francis St - Level 1 - Various plumbing works (see notes) | Plumbing & Drainage | Toilets/Cisterns | 326.58 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-09 14:46 | 2023-01-12 17:00 | 2023-01-11 08:00 | 2023-01-12 17:00 | 2023-01-11 09:30
MSA-DCA | WA6405509 | 2 | Techworks Plumbing | HH / Francis St - Various toilet works | Plumbing & Drainage | Toilets/Cisterns | 326.58 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-09 14:51 | 2023-01-12 17:00 | 2023-01-11 09:30 | 2023-01-12 17:00 | 2023-01-11 11:00
MSA-DTWD | WA6405525 | 2 | AWB Co. | faulty lighting in the disabled toilet | Electrical | General Electrical | 368.12 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-09 15:07 | 2023-01-12 17:00 | 2023-01-11 11:30 | 2023-01-12 17:00 | 2023-01-11 13:00
MSA-DFES | WA6407618 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | One flickering light in multiple rooms - See Notes Below | Electrical | General Electrical | 272.63 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-10 10:10 | 2023-01-17 17:00 | 2023-01-11 08:45 | 2023-01-17 17:00 | 2023-01-11 10:15
MSA-DTAG | WA6407807 | 3 | Midolo Building Services | Level 11 - Chambers - Whiteboard fixings have dislodged from cavity wall | Building | General Building | 217.7 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-10 11:49 | 2023-01-17 17:00 | 2023-01-11 11:00 | 2023-01-17 17:00 | 2023-01-11 12:30
MSA-DTWD | WA6407981 | 2 | AWB Co. | W204 - Magnetic Door latch broken | Building | Doors | 235.075 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-10 13:14 | 2023-01-13 17:00 | 2023-01-11 12:30 | 2023-01-13 17:00 | 2023-01-11 14:00
MSA-DTWD | WA6414848 | 2 | AWB Co. | First Floor - A54 - Repair replace x2 fluro lights - Tombstone/globe holders broken | Electrical | Lighting, Internal | 284.92 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-11 10:27 | 2023-01-16 17:00 | 2023-01-16 13:30 | 2023-01-16 17:00 | 2023-01-16 15:00
MSA-DFES | WA6425663 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Dorm 3 Bed - Reading light is broken | Electrical | Lighting, Internal | 262.67 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-12 10:29 | 2023-01-19 17:00 | 2023-01-13 13:30 | 2023-01-19 17:00 | 2023-01-13 15:00
MSA-DTAG | WA6425816 | 3 | SCAVENGER SUPPLIES PTY LTD | Level 1 - FIP - EWIS system needs to be reset - See Notes Below | Fire Protection Services | Fire Protection - Monitor System | 208.23 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-12 11:59 | 2023-01-19 17:00 | 2023-01-18 08:30 | 2023-01-19 17:00 | 2023-01-18 10:00
MSA-DTWD | WA6426171 | 3 | GRAFFITI FORCE PTY LTD | External area - Multiple graffiti tags - large one also in lane way | Cleaning | Graffiti | 359 | Fail | Fail | 2 | 2 | 1.5 | 2023-01-12 15:30 | 2023-01-19 17:00 | 2023-01-31 10:45 | 2023-01-19 17:00 | 2023-01-31 12:15
MSA-DFES | WA6431008 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Change room 5 Drying Room & Lecture room 5 - Lights not working (see notes) | Electrical | Lighting, Internal | 428.45 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-13 11:14 | 2023-01-20 17:00 | 2023-01-16 10:45 | 2023-01-20 17:00 | 2023-01-16 12:15
MSA-DTWD | WA6431074 | 2 | AWB Co. | Museum St courtyard- pavers are lifted and causing trip | Paving & Roadworks | Paving | 181.575 | Fail | Fail | 0 | 0 | 1.5 | 2023-01-13 11:50 | 2023-01-18 17:00 | 2023-01-20 14:00 | 2023-01-18 17:00 | 2023-01-20 15:30
MSA-DTWD | WA6431486 | 1 | Precise Air Group | H Block East A/C is not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 441.25 | Fail | Fail | 0 | 0 | 1.5 | 2023-01-13 15:49 | 2023-01-16 17:00 | 2023-01-17 08:00 | 2023-01-16 17:00 | 2023-01-17 09:30
MSA-DCA | WA6450205 | 1 | Automatic Fire Protection (ARA) | Faulty Smoke Detector: L4S14 & L4S31 | Fire Protection Services | Smoke and Heat Detection | 422.08 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-16 09:50 | 2023-01-17 17:00 | 2023-01-16 11:30 | 2023-01-17 17:00 | 2023-01-16 13:00
MSA-DTAG | WA6467176 | 1 | AFD Contracting | Ground - Front gate not latching properly | Building | Steel Fencing & Gates | 311.52 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-17 14:24 | 2023-01-18 17:00 | 2023-01-18 11:15 | 2023-01-18 17:00 | 2023-01-18 12:45
MSA-DCA | WA6482082 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Faulty light fitting | Electrical | Lighting, Internal | 350.835 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-18 07:02 | 2023-01-24 17:00 | 2023-01-20 10:45 | 2023-01-24 17:00 | 2023-01-20 12:15
MSA-DTWD | WA6482532 | 3 | AWB Co. | S225- 5 x lights not working | Electrical | Lighting, Internal | 274.275 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-18 11:10 | 2023-01-25 17:00 | 2023-01-24 13:30 | 2023-01-25 17:00 | 2023-01-24 15:00
MSA-DTWD | WA6489948 | 2 | Milners Tree Solutions Pty Ltd | Driveway- Tree requires pruning | Landscaping & Gardening | General Tree Works | 832.5 | Fail | Fail | 0 | 0 | 1.5 | 2023-01-18 14:42 | 2023-01-23 17:00 | 2023-01-25 06:30 | 2023-01-23 17:00 | 2023-01-25 08:00
MSA-DTWD | WA6504381 | 2 | AWB Co. | x 7 lights not working see notes | Electrical | Lighting, External | 378.67 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-19 15:14 | 2023-01-24 17:00 | 2023-01-24 09:30 | 2023-01-24 17:00 | 2023-01-24 11:00
MSA-DTWD | WA6509204 | 3 | AWB Co. | Faulty power point on south wall | Electrical | General Electrical | 294.265 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-20 08:29 | 2023-01-30 17:00 | 2023-01-25 07:00 | 2023-01-30 17:00 | 2023-01-25 08:30
MSA-DTWD | WA6509372 | 2 | AHS Services WA Pty Ltd (Anchor) | spout has disconnected from base | Plumbing & Drainage | Water | 191.155 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-20 10:04 | 2023-01-25 17:00 | 2023-01-23 13:00 | 2023-01-25 17:00 | 2023-01-23 14:30
MSA-DTWD | WA6509377 | 2 | Techworks Electrical | x2 broken GPO's behind cooking equipment | Electrical | General Electrical | 400.61 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-20 10:10 | 2023-01-25 17:00 | 2023-01-23 13:30 | 2023-01-25 17:00 | 2023-01-23 15:00
MSA-DTWD | WA6509739 | 2 | AWB Co. | Pavers lifting - Creche side of courtyard | Building | General Building | 314.73 | Fail | Fail | 2 | 2 | 1.5 | 2023-01-20 14:35 | 2023-01-25 17:00 | 2023-02-07 14:00 | 2023-01-25 17:00 | 2023-02-07 15:30
MSA-DFES | WA6509787 | 3 | Critical Fire Protection & Training | Front Entry - Fire Indicator Panel Fault - Low battery warning | Fire Protection Services | Fire Protection - Monitor System | 151.95 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-20 15:30 | 2023-01-30 17:00 | 2023-01-23 12:30 | 2023-01-30 17:00 | 2023-01-23 14:00
MSA-DFES | WA6516253 | 2 | Water2water Pty Ltd | Room 37 - Kitchen - Zip boil - Leaking and not working | Plumbing & Drainage | Water | 485.4 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-23 10:17 | 2023-01-27 17:00 | 2023-01-25 08:00 | 2023-01-27 17:00 | 2023-01-25 09:30
MSA-DFES | WA6517246 | 1 | Australian HVAC Services Pty. Ltd. | Location 1 - First Floor - AC unit is un-serviceable | Air Conditioning | Package | 286.34 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-24 08:30 | 2023-01-25 17:00 | 2023-01-24 10:30 | 2023-01-25 17:00 | 2023-01-24 12:00
MSA-DTWD | WA6517422 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, Internal | 354.46 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-24 09:41 | 2023-01-30 17:00 | 2023-01-24 12:00 | 2023-01-30 17:00 | 2023-01-24 13:30
MSA-DTAG | WA6517947 | 1 | Australian HVAC Services Pty. Ltd. | RETROSPECTIVE - ATT 23/1-A/C split unit leaking | Air Conditioning | Room Air Conditioners | 641.08 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-23 19:00 | 2023-01-24 17:00 | 2023-01-23 20:00 | 2023-01-24 17:00 | 2023-01-23 21:30 | 1
MSA-DTWD | WA6519228 | 2 | COMMERCIAL PLUMBING AND GAS | Leaking mixer tap- may need replacing | Plumbing & Drainage | Water | 362.295 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-25 14:08 | 2023-01-31 17:00 | 2023-01-31 14:00 | 2023-01-31 17:00 | 2023-01-31 15:30
MSA-DTWD | WA6520498 | 2 | AHS Services WA Pty Ltd (Anchor) | Wall and Floor Tiling Area - Blocked Floor Drain closest to the Wall and floor tiling area | Plumbing & Drainage | Drainage | 188.655 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-27 15:21 | 2023-02-01 17:00 | 2023-01-30 11:30 | 2023-02-01 17:00 | 2023-01-30 13:00
MSA-DTWD | WA6521216 | 1 | Precise Air Group | Ice machine not working | Refrigeration | Ice machine |  | Pass | Pass | 0 | 0 | 1.5 | 2023-01-30 09:15 | 2023-01-31 17:00 | 2023-01-30 10:00 | 2023-01-31 17:00 | 2023-01-30 11:30
MSA-DCA | WA6521296 | 1 | EQUANS Mechanical Services (WA) Pty Limited | SLWA - Level 5 - Plant Room - Heating Hot Water Boiler 3 Unit in Fault | Plumbing & Drainage | HWS/Units Electric & Gas | 259.01 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-30 09:50 | 2023-01-31 17:00 | 2023-01-30 12:30 | 2023-01-31 17:00 | 2023-01-30 14:00
MSA-DTWD | WA6521804 | 0 | SENTINEL LOCK SERVICE PTY LTD | Front door handle has come off the door | Security | Locksmith | 383.13 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-30 13:14 | 2023-01-31 17:00 | 2023-01-30 14:50 | 2023-01-31 17:00 | 2023-01-30 16:20
MSA-DTWD | WA6521938 | 2 | Techworks Electrical | light not working | Electrical | Lighting, Internal | 306.43 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-30 14:47 | 2023-02-02 17:00 | 2023-02-02 08:30 | 2023-02-02 17:00 | 2023-02-02 10:00
MSA-DCA | WA6521966 | 2 | Techworks Electrical | Light Switch in the Meeting room is faulty | Electrical | Lighting, Internal | 314.55 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-30 15:10 | 2023-02-02 17:00 | 2023-01-31 06:00 | 2023-02-02 17:00 | 2023-01-31 07:30
MSA-DTWD | WA6522897 | 3 | AWB Co. | C707 - White board has come off wall | Building | Internal Walls | 181.575 | Pass | Pass | -1 | -1 | 1.5 | 2023-01-31 10:13 | 2023-02-07 17:00 | 2023-02-03 14:00 | 2023-02-07 17:00 | 2023-02-03 15:30
MSA-DTWD | WA6522913 | 2 | AWB Co. | lights flickering | Electrical | Lighting, Internal | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2023-01-31 11:02 | 2023-02-03 17:00 | 2023-02-01 10:45 | 2023-02-03 17:00 | 2023-02-01 12:15
MSA-DTAG | WA6526634 | 0 | Sapio Pty Ltd | Control room - Security camera faulty | Security | CCTV Surveillance | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-01 09:32 | 2023-02-01 11:32 | 2023-02-01 11:00 | 2023-02-01 13:32 | 2023-02-01 12:30
MSA-DTAG | WA6527029 | 3 | AWB Co. | Magistrates Chambers 2 - Middle light not working | Electrical | Lighting, Internal | 224.235 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-01 12:58 | 2023-02-08 17:00 | 2023-02-06 07:00 | 2023-02-08 17:00 | 2023-02-06 08:30
MSA-DCA | WA6527037 | 2 | Techworks Electrical | Light switch has gone into the panel | Electrical | Lighting, Internal | 202.015 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-01 12:48 | 2023-02-06 17:00 | 2023-02-06 09:00 | 2023-02-06 17:00 | 2023-02-06 10:30
MSA-DTWD | WA6531622 | 2 | Equans Mechanical Services Australia | Air conditioner - Split system not working | Air Conditioning | Ducted Split System | 174.555 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-03 13:25 | 2023-02-08 17:00 | 2023-02-06 13:00 | 2023-02-08 17:00 | 2023-02-06 14:30
MSA-DTWD | WA6534241 | 2 | Techworks Plumbing | Level 1 - Tap dripping & hard to turn off - Please ring before attending | Plumbing & Drainage | Water | 189.19 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-06 10:39 | 2023-02-09 17:00 | 2023-02-09 07:00 | 2023-02-09 17:00 | 2023-02-09 08:30
MSA-DTWD | WA6534276 | 2 | AWB Co. | entrance-Faulty light switch causing RCD to trip - see notes | Electrical | Lighting, Internal | 237.415 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-06 11:03 | 2023-02-09 17:00 | 2023-02-07 10:30 | 2023-02-09 17:00 | 2023-02-07 12:00
MSA-DTWD | WA6534443 | 2 | PEEL LOCK SERVICES PTY LTD | Room G15 - Faulty lock - replace | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.5 | 2023-02-06 12:28 | 2023-02-09 17:00 | 2023-02-08 14:00 | 2023-02-09 17:00 | 2023-02-08 15:30
MSA-MRWA | WA6535170 | 3 | AWB Co. | Failed light 18W | Electrical | Lighting, Internal | 388.31 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-06 15:01 | 2023-02-13 17:00 | 2023-02-09 06:00 | 2023-02-13 17:00 | 2023-02-09 07:30
MSA-DTWD | WA6535241 | 2 | AWB Co. | Repair or replace defective hanging GPO | Electrical | Lighting, Internal | 292.935 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-06 16:24 | 2023-02-09 17:00 | 2023-02-08 08:15 | 2023-02-09 17:00 | 2023-02-08 09:45
MSA-DTWD | WA6537698 | 1 | Precise Air Group | Canteen - Freezer not working - Icing up - temp fix needed. see notes | Refrigeration | Freezers | 202.705 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-07 11:04 | 2023-02-08 17:00 | 2023-02-07 14:30 | 2023-02-08 17:00 | 2023-02-07 16:00
MSA-DTWD | WA6538156 | 1 | COMMERCIAL PLUMBING AND GAS | Faulty Tap on Kitchen sink | Plumbing & Drainage | Water | 213.925 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-07 15:26 | 2023-02-08 17:00 | 2023-02-07 15:30 | 2023-02-08 17:00 | 2023-02-07 17:00
MSA-DTWD | WA6539266 | 1 | Precise Air Group | Aircon not working - | Air Conditioning | Room Air Conditioners | 411.68 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-08 11:34 | 2023-02-09 17:00 | 2023-02-09 13:30 | 2023-02-09 17:00 | 2023-02-09 15:00
MSA-DCA | WA6539354 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Performing lines office - RDC CU17 - Has tripped / Damaged | Electrical | General Electrical | 441.805 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-08 12:35 | 2023-02-08 14:35 | 2023-02-08 13:00 | 2023-02-08 16:35 | 2023-02-08 14:30
MSA-DFES | WA6539666 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - Ladies Changeroom - Lights out in ladies toilet cubicle | Electrical | Lighting, Internal | 232.83 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-08 15:34 | 2023-02-13 17:00 | 2023-02-10 07:00 | 2023-02-13 17:00 | 2023-02-10 08:30
MSA-DCA | WA6540549 | 2 | Protek 24/7 Building & Maintenance | Winch house - 2 planks have been removed | Building | General Building | 174.04 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-09 11:47 | 2023-02-14 17:00 | 2023-02-10 10:00 | 2023-02-14 17:00 | 2023-02-10 11:30
MSA-DTWD | WA6540556 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 485.075 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-09 11:48 | 2023-02-14 17:00 | 2023-02-10 08:30 | 2023-02-14 17:00 | 2023-02-10 10:00
MSA-DTWD | WA6540617 | 2 | AWB Co. | rectify faulty network connection on electrical floor box | Electrical | General Electrical | 385.32 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-09 12:11 | 2023-02-14 17:00 | 2023-02-09 13:30 | 2023-02-14 17:00 | 2023-02-09 15:00
MSA-DTWD | WA6540640 | 2 | AWB Co. | repair or replace 32 amp 5 pin socket | Electrical | General Electrical | 614.52 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-09 12:26 | 2023-02-14 17:00 | 2023-02-14 09:15 | 2023-02-14 17:00 | 2023-02-14 10:45
MSA-DTWD | WA6543916 | 2 | AWB Co. | work table earthing - faulty | Electrical | General Electrical | 284.92 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-10 09:09 | 2023-02-15 17:00 | 2023-02-10 10:30 | 2023-02-15 17:00 | 2023-02-10 12:00
MSA-DCA | WA6544510 | 2 | Techworks Electrical | Anthropology workshop - Flickering light | Electrical | Lighting, Internal | 389.775 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-10 13:27 | 2023-02-15 17:00 | 2023-02-15 08:30 | 2023-02-15 17:00 | 2023-02-15 10:00
MSA-DTWD | WA6560450 | 1 | Techworks Electrical | Car Park - Lights - Hager light timer - replace | Electrical | Lighting, External | 480.61 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-13 10:18 | 2023-02-14 17:00 | 2023-02-14 12:30 | 2023-02-14 17:00 | 2023-02-14 14:00
MSA-DTWD | WA6573046 | 3 | AWB Co. | 13 (Demountable) - Emergency stop button - tripping RCD | Electrical | General Electrical | 202.575 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-14 10:34 | 2023-02-21 17:00 | 2023-02-15 11:30 | 2023-02-21 17:00 | 2023-02-15 13:00
MSA-DFES | WA6573101 | 2 | Protek 24/7 Building & Maintenance | kitchen-draws failing to work getting stuck when opeining-see notes | Carpentry | Timber (all types) | 196.42 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-14 10:59 | 2023-02-17 17:00 | 2023-02-15 13:45 | 2023-02-17 17:00 | 2023-02-15 15:15 |  | WCAPPR
MSA-DCA | WA6573110 | 3 | Techworks Electrical | Rehearsal Room 1 - Fuse is being tripped when lights are turned off and emergency lighting is active | Electrical | Lighting, Internal | 326.61 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-14 10:57 | 2023-02-21 17:00 | 2023-02-17 08:30 | 2023-02-21 17:00 | 2023-02-17 10:00
MSA-DFES | WA6573335 | 2 | Complete Pest Management Services | Information Resources work area - Cockroaches - Mice | Pest Control | General Pest | 455.35 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-14 12:34 | 2023-02-17 17:00 | 2023-02-15 10:30 | 2023-02-17 17:00 | 2023-02-15 12:00
MSA-DTWD | WA6573386 | 2 | PEEL LOCK SERVICES PTY LTD | Room B1 - door lock will not open / key B13 - B1 37 239 | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.5 | 2023-02-14 12:29 | 2023-02-17 17:00 | 2023-02-16 14:00 | 2023-02-17 17:00 | 2023-02-16 15:30
MSA-DTWD | WA6585362 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground Floor - A Block East - Male toilet - Leak above ceiling in cubicle | Plumbing & Drainage | Toilets/Cisterns | 196.945 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-16 07:05 | 2023-02-16 17:00 | 2023-02-16 12:30 | 2023-02-16 17:00 | 2023-02-16 14:00
MSA-DTWD | WA6585584 | 2 | M Construction (WA) | Toilet door - lock/ latch faulty | Building | Doors | 195.06 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-16 09:02 | 2023-02-21 17:00 | 2023-02-20 09:00 | 2023-02-21 17:00 | 2023-02-20 10:30
MSA-DTWD | WA6585736 | 0 | PEEL LOCK SERVICES PTY LTD | Door handle/lock falling apart | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.5 | 2023-02-16 10:32 | 2023-02-16 12:32 | 2023-02-16 12:30 | 2023-02-16 14:32 | 2023-02-16 14:00
MSA-DTWD | WA6598701 | 2 | Techworks Electrical | Data point 21 1 13 not working | Electrical | Distribution Board | 199.955 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-17 07:25 | 2023-02-21 17:00 | 2023-02-21 14:00 | 2023-02-21 17:00 | 2023-02-21 15:30
MSA-DTWD | WA6604059 | 2 | AWB Co. | 1-27 Engineering Lab - One of our volumetric benches is tripping the circuit breaker (see notes) | Electrical | General Electrical | 284.92 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-17 15:22 | 2023-02-22 17:00 | 2023-02-22 08:15 | 2023-02-22 17:00 | 2023-02-22 09:45
MSA-DTAG | WA6650226 | 0 | Sapio Pty Ltd | Access system not working - | Security | Access Control | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 10:06 | 2023-02-20 12:06 | 2023-02-20 11:00 | 2023-02-20 14:06 | 2023-02-20 12:30
MSA-DTAG | WA6650369 | 1 | AWB Co. | Level 2 - Registry Document Production - Power board on Supervisors desk is sparking when turned off | Electrical | Distribution Board | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 10:34 | 2023-02-21 17:00 | 2023-02-21 07:00 | 2023-02-21 17:00 | 2023-02-21 08:30
MSA-DTWD | WA6650443 | 2 | Techworks Electrical | Lights are not working | Electrical | General Electrical | 191.635 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 11:27 | 2023-02-23 17:00 | 2023-02-20 12:30 | 2023-02-23 17:00 | 2023-02-20 14:00
MSA-DTWD | WA6650934 | 2 | SENTINEL LOCK SERVICE PTY LTD | External Security door - damaged handle/lock set | Security | Locksmith | 203.47 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 14:49 | 2023-02-23 17:00 | 2023-02-23 09:20 | 2023-02-23 17:00 | 2023-02-23 10:50
MSA-DTWD | WA6650935 | 2 | Protek 24/7 Building & Maintenance | Water leak over projector screen south wall | Building | General Building | 278.9 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 14:43 | 2023-02-23 17:00 | 2023-02-22 08:00 | 2023-02-23 17:00 | 2023-02-22 09:30
MSA-DTWD | WA6650964 | 3 | AWB Co. | Disconnect fault spot welder | Electrical | General Electrical | 197.235 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 15:11 | 2023-02-27 17:00 | 2023-02-24 10:00 | 2023-02-27 17:00 | 2023-02-24 11:30
MSA-DTWD | WA6650968 | 3 | AWB Co. | Replace defective GPO | Electrical | General Electrical | 207.875 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 15:17 | 2023-02-27 17:00 | 2023-02-24 11:30 | 2023-02-27 17:00 | 2023-02-24 13:00
MSA-DTWD | WA6650973 | 2 | SENTINEL LOCK SERVICE PTY LTD | Campus entry gate - hayman road - security gate at campus entry has faulty padlock | Security | Locksmith | 209.77 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-20 15:26 | 2023-02-23 17:00 | 2023-02-23 09:20 | 2023-02-23 17:00 | 2023-02-23 10:50
MSA-DTAG | WA6653827 | 1 | Sapio Pty Ltd | L7-30 Mediation DUR IN 7.2 - Duress Alarm Not Working-see notes | Security | Security Management System | 209.25 | Fail | Fail | 0 | 0 | 1.5 | 2023-02-21 07:17 | 2023-02-21 17:00 | 2023-02-22 10:30 | 2023-02-21 17:00 | 2023-02-22 12:00
MSA-DTWD | WA6653989 | 2 | M Construction (WA) | Playgroup area - has a sand pit where the retaining timber side wall has come apart | Building | General Building | 200.28 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-21 08:46 | 2023-02-24 17:00 | 2023-02-22 07:45 | 2023-02-24 17:00 | 2023-02-22 09:15
MSA-DTWD | WA6654873 | 2 | Techworks Plumbing | Ladies’ toilets near Library - Toilet Buttons get stuck – problems flushing (see notes) | Plumbing & Drainage | Toilets/Cisterns | 326.58 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-21 10:10 | 2023-02-24 17:00 | 2023-02-22 12:30 | 2023-02-24 17:00 | 2023-02-22 14:00
MSA-DCA | WA6657248 | 0 | Critical Fire Protection & Training | Fire relay 2 in fault | Fire Protection Services | Fire Protection - Monitor System | 443.57 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-21 11:16 | 2023-02-21 13:16 | 2023-02-21 11:30 | 2023-02-21 15:16 | 2023-02-21 13:00
MSA-DTWD | WA6668949 | 1 | COMMERCIAL PLUMBING AND GAS | Eye wash station unit broken and associated drain blocked | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.5 | 2023-02-22 12:48 | 2023-02-23 17:00 | 2023-02-22 15:30 | 2023-02-23 17:00 | 2023-02-22 17:00
MSA-DTWD | WA6668998 | 2 | AWB Co. | Circuit breaker tripping - left hand side (RWB 3 on Q08 DB in room) 3 phase outlets. | Electrical | General Electrical | 284.92 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-22 13:06 | 2023-02-27 17:00 | 2023-02-23 07:00 | 2023-02-27 17:00 | 2023-02-23 08:30
MSA-DTWD | WA6669196 | 1 | AWB Co. | D Block - Needs isolating at the switch board | Electrical | General Electrical | 196.755 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-22 15:14 | 2023-02-23 17:00 | 2023-02-22 16:15 | 2023-02-23 17:00 | 2023-02-22 17:45
MSA-DTWD | WA6671430 | 3 | AWB Co. | 2 fluorescent lights out in room AF24 &1 fluorescent light out in room AF26 - ring before attending | Electrical | Lighting, Internal | 241.075 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-23 07:37 | 2023-03-01 17:00 | 2023-02-24 13:00 | 2023-03-01 17:00 | 2023-02-24 14:30
MSA-DFES | WA6671561 | 2 | AWB Co. | Ground - Kitchen - Door loose - sercure to brick wall | Building | Doors | 208.475 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-23 08:29 | 2023-02-28 17:00 | 2023-02-28 09:00 | 2023-02-28 17:00 | 2023-02-28 10:30
MSA-DTWD | WA6672303 | 2 | AHS Services WA Pty Ltd (Anchor) | A110c-Leaking cistern into bowl | Plumbing & Drainage | Toilets/Cisterns | 224.015 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-23 14:40 | 2023-02-28 17:00 | 2023-02-27 13:00 | 2023-02-28 17:00 | 2023-02-27 14:30
MSA-DTWD | WA6673173 | 1 | AWB Co. | Circuit trip - RCD test - See notes | Electrical | General Electrical | 284.92 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-24 11:29 | 2023-02-27 17:00 | 2023-02-27 07:00 | 2023-02-27 17:00 | 2023-02-27 08:30
MSA-DTWD | WA6674159 | 2 | AWB Co. | Room A113 & 114 - Store lights not working - Tubes or starters to be replaced, use 845 tubes | Electrical | Lighting, Internal | 302.085 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-27 08:21 | 2023-03-02 17:00 | 2023-03-01 11:15 | 2023-03-02 17:00 | 2023-03-01 12:45
MSA-DTWD | WA6674616 | 2 | Australian Airconditioning Services Pty Ltd | AC not working great and the air pushing through stinks - Filters/Coils may need to be cleaned | Air Conditioning | Ducted Split System | 334.93 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-27 11:04 | 2023-03-02 17:00 | 2023-02-28 09:30 | 2023-03-02 17:00 | 2023-02-28 11:00
MSA-DTWD | WA6675043 | 3 | AWB Co. | The exhaust fan in the disabled toilet is not working - see notes | Electrical | General Electrical | 194.275 | Pass | Pass | -1 | -1 | 1.5 | 2023-02-27 14:34 | 2023-03-07 17:00 | 2023-03-02 07:00 | 2023-03-07 17:00 | 2023-03-02 08:30
MSA-DTAG | WA6675087 | 1 | AHS Services WA Pty Ltd (Anchor) | Male Toilets opposite Aboriginal Legal Services – 4 Lift side - Blocked urinal | Plumbing & Drainage | Toilets/Cisterns | 233.945 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-27 15:08 | 2023-02-28 17:00 | 2023-02-28 13:30 | 2023-02-28 17:00 | 2023-02-28 15:00
MSA-DCA | WA6675145 | 1 | Protek 24/7 Building & Maintenance | Groud Level - Front of house - Windows can be opened from the outside – Presents a security issue | Building | Windows | 161.54 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-27 16:00 | 2023-02-28 17:00 | 2023-02-28 09:30 | 2023-02-28 17:00 | 2023-02-28 11:00
MSA-DTWD | WA6675797 | 1 | AWB Co. | Dust extraction fan M028 tile cutting room faulty (see notes) | Electrical | General Electrical | 284.92 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-28 09:24 | 2023-03-01 17:00 | 2023-02-28 13:00 | 2023-03-01 17:00 | 2023-02-28 14:30
MSA-DTWD | WA6675811 | 2 | AWB Co. | Room F37 - Damaged/faulty extension lead to computer desk. Tagged out. (see notes) | Electrical | General Electrical | 330.57 | Pass | Pass | 0 | 0 | 1.5 | 2023-02-28 09:33 | 2023-03-03 17:00 | 2023-02-28 12:00 | 2023-03-03 17:00 | 2023-02-28 13:30
MSA-DCA | WA6676452 | 0 | Techworks Electrical | Exterior Lights - Timer is Faulty | Electrical | Lighting, External |  | Pass | Pass | 0 | 0 | 1.5 | 2023-02-28 14:14 | 2023-02-28 16:14 | 2023-02-28 16:00 | 2023-02-28 18:14 | 2023-02-28 17:30
MSA-DTWD | WA6680254 | 1 | AWB Co. | Heavy plant Reception 2G6 - Light fitting hanging Light fitting hanging down | Electrical | Lighting, Internal | 194.275 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-01 09:39 | 2023-03-02 17:00 | 2023-03-01 13:30 | 2023-03-02 17:00 | 2023-03-01 15:00
MSA-DTWD | WA6681631 | 2 | Techworks Electrical | Outside cool room / Demo Kitchen - Broken switches (see notes) | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1.5 | 2023-03-02 10:28 | 2023-03-08 17:00 | 2023-03-08 12:30 | 2023-03-08 17:00 | 2023-03-08 14:00
MSA-DTWD | WA6681906 | 1 | Australian Airconditioning Services Pty Ltd | AC blowing hot air | Air Conditioning | Ducted Split System | 236.72 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-02 12:51 | 2023-03-03 17:00 | 2023-03-03 08:00 | 2023-03-03 17:00 | 2023-03-03 09:30
MSA-DTWD | WA6683277 | 1 | Techworks Plumbing | Disable toilet - Water running – doesn’t flush – cannot turn off tap | Plumbing & Drainage | Toilets/Cisterns |  | Fail | Fail | 1 | 1 | 1.5 | 2023-03-03 07:07 | 2023-03-03 17:00 | 2023-03-09 07:00 | 2023-03-03 17:00 | 2023-03-09 08:30
MSA-DTAG | WA6683933 | 2 | Water2water Pty Ltd | Adult Community Corrections Central Breach Unit - Indicators on Hot/cold Tap broken | Plumbing & Drainage | HWS/Units Electric & Gas | 485.45 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-03 13:54 | 2023-03-09 17:00 | 2023-03-09 14:00 | 2023-03-09 17:00 | 2023-03-09 15:30
MSA-DTAG | WA6688039 | 0 | Sapio Pty Ltd | Security door - Fault - See notes | Security | Access Control | 204.44 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-07 11:12 | 2023-03-07 13:12 | 2023-03-07 12:00 | 2023-03-07 15:12 | 2023-03-07 13:30
MSA-DTWD | WA6688175 | 2 | COMMERCIAL PLUMBING AND GAS | Male toilets - hand basin slow to drain (see notes) | Plumbing & Drainage | Drainage | 203.925 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-07 12:25 | 2023-03-10 17:00 | 2023-03-08 17:00 | 2023-03-10 17:00 | 2023-03-08 18:30
MSA-DTWD | WA6688952 | 2 | AWB Co. | hts are not working | Electrical | Lighting, Internal | 194.275 | Pass | Pass | -1 | -1 | 1.5 | 2023-03-08 08:10 | 2023-03-13 17:00 | 2023-03-09 07:00 | 2023-03-13 17:00 | 2023-03-09 08:30
MSA-DTWD | WA6688968 | 2 | AWB Co. | Repair faulty light fitting | Electrical | Lighting, Internal | 284.92 | Pass | Pass | -1 | -1 | 1.5 | 2023-03-08 08:19 | 2023-03-13 17:00 | 2023-03-08 12:30 | 2023-03-13 17:00 | 2023-03-08 14:00
MSA-DTWD | WA6689200 | 2 | AWB Co. | Faulty Lights - Hallway near kitchen | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1.5 | 2023-03-08 10:06 | 2023-03-13 17:00 | 2023-03-13 10:30 | 2023-03-13 17:00 | 2023-03-13 12:00
MSA-DFES | WA6689206 | 1 | Protek 24/7 Building & Maintenance | Eastern End door has broken hinge. | Building | Doors | 180.29 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-08 10:19 | 2023-03-09 17:00 | 2023-03-08 11:00 | 2023-03-09 17:00 | 2023-03-08 12:30
MSA-DTAG | WA6689607 | 1 | Seme Solutions Pty Ltd | Sally port door in court custody - Sally port door no longer use control - see notes | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 1.5 | 2023-03-08 13:36 | 2023-03-09 17:00 | 2023-03-08 15:00 | 2023-03-09 17:00 | 2023-03-08 16:30
MSA-DCA | WA6726935 | 1 | GPS Plumbing & Gas Services PtyLtd | Shipwrights Office - Toilet seat fixings is broken | Plumbing & Drainage | Toilets/Cisterns | 196.165 | Pass | Pass | 0 | 0 | 1.5 | 2023-03-15 09:14 | 2023-03-16 17:00 | 2023-03-15 11:30 | 2023-03-16 17:00 | 2023-03-15 13:00
MSA-DFES | WA5208386 | 0 | Australian HVAC Services Pty. Ltd. | Whole building - air con is not working throughout the building | Air Conditioning | Room Air Conditioners | 640.1 | Pass | Pass | 0 | 0 | 1.4872 | 2022-03-09 08:25 | 2022-03-09 10:25 | 2022-03-09 09:28 | 2022-03-09 12:25 | 2022-03-09 10:58 |  |  | Received call and attended site. Found bms controllers offline. Engaged bms subcontractor to remote in and inspect. Reset faulty controllers and restored bms operations. Confirmed plant operating correctly. Bms contractor carried out further tests. Found system operating correctly.
MSA-DTWD | WA5100623 | 2 | Falcetta Plumbing and Gas | Level 1 - Female Toilet - Toilet is Leaking from the cystern | Plumbing & Drainage | Toilets/Cisterns | 868.74 | Pass | Pass | 0 | 0 | 1.4833 | 2022-02-02 16:27 | 2022-02-07 17:00 | 2022-02-07 15:30 | 2022-02-07 17:00 | 2022-02-07 16:59 |  |  | replaced 1x cistern, repaired 1x cistern
MSA-DTWD | WA5175564 | 1 | Falcetta Plumbing and Gas | First floor - female toilets - Staff cubical cistern leaking | Plumbing & Drainage | Water | 544.64 | Pass | Pass | 0 | 0 | 1.4833 | 2022-02-21 12:26 | 2022-02-22 17:00 | 2022-02-22 15:30 | 2022-02-22 17:00 | 2022-02-22 16:59 |  |  | replaced invisi in duct cistern
MSA-DTWD | WA5305082 | 2 | Falcetta Plumbing and Gas | Level 6 - Kitchen - Hot water tap leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 344.85 | Pass | Pass | 0 | 0 | 1.4833 | 2022-04-05 11:57 | 2022-04-08 17:00 | 2022-04-08 15:30 | 2022-04-08 17:00 | 2022-04-08 16:59 |  |  | sourced and replaced outlet tap
MSA-DTWD | WA5319205 | 1 | Falcetta Plumbing and Gas | E58 Large Scale Kitchen - Cleaners tap leaking | Plumbing & Drainage | Drainage | 181.98 | Pass | Pass | 0 | 0 | 1.4833 | 2022-04-12 13:09 | 2022-04-13 17:00 | 2022-04-13 15:30 | 2022-04-13 17:00 | 2022-04-13 16:59 |  |  | isolated water, replaced hose tap
MSA-DTWD | WA5368824 | 0 | AHS Services WA Pty Ltd (Anchor) | A Block - Level 3 - East end - water fountain | Plumbing & Drainage | Water | 183.745 | Pass | Pass | 0 | 0 | 1.4833 | 2022-04-19 13:17 | 2022-04-19 15:17 | 2022-04-19 14:00 | 2022-04-19 17:17 | 2022-04-19 15:29 |  |  | Replaced cracked fitting at the back of the water fountain
MSA-DCA | WA5795380 | 0 | TK Elevator Australia Pty Ltd | lift 2 - kitchen lift - stuck between ground and level 2 - person stuck | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.4833 | 2022-08-25 11:47 | 2022-08-25 13:47 | 2022-08-25 12:18 | 2022-08-25 15:47 | 2022-08-25 13:47 |  |  | Lift 2 Art-Kitchen-Elevator > MR > Geared :Passenger stuck at bottom floor, doors 10mm open, doors jammed, released doors, passenger escaped, inspected hallway doormech and door clutch, inspected door sills, ran lift to every floor for 30 mins, lift running fine. Lift left in service.
MSA-DTWD | WA6539702 | 1 | COMMERCIAL PLUMBING AND GAS | Leaking ground floor ladies toilet | Plumbing & Drainage | Toilets/Cisterns | 138.835 | Pass | Pass | 0 | 0 | 1.4833 | 2023-02-08 16:22 | 2023-02-09 17:00 | 2023-02-09 15:30 | 2023-02-09 17:00 | 2023-02-09 16:59 |  | WCAPPR
MSA-DCA | WA5105908 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant room - Alarm P0 AC 1 Effecting Galleries 1 and 6 | Air Conditioning | Cooling Tower | 507.58 | Pass | Pass | 0 | 0 | 1.4833 | 2022-02-04 22:07 | 2022-02-05 00:07 | 2022-02-04 22:30 | 2022-02-05 02:07 | 2022-02-04 23:59 |  |  | Call out completed, system is running as required.
MSA-DFES | WA5323541 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Front Garden - burst water pipe | Plumbing & Drainage | Water | 338 | Pass | Pass | 0 | 0 | 1.4833 | 2022-04-13 09:08 | 2022-04-14 17:00 | 2022-04-13 12:00 | 2022-04-14 17:00 | 2022-04-13 13:29 |  |  | Repaired a 32mm burst pipe in front garden
MSA-DCA | WA5493791 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - First floor - Public ladies bathroom - see details below | Plumbing & Drainage | Drainage | 182.29 | Pass | Pass | 0 | 0 | 1.4833 | 2022-06-07 10:22 | 2022-06-10 17:00 | 2022-06-08 10:40 | 2022-06-10 17:00 | 2022-06-08 12:09 |  |  | Replace cracked/split nut that was leaking with new chrome Nut and compression fitting.
MSA-DTWD | WA6383842 | 2 | CONNECT SECURITY SYSTEMS | NTU not communicating properly with computers - see notes below | Security | Monitoring | 247.23 | Pass | Pass | 0 | 0 | 1.4833 | 2022-12-20 14:08 | 2022-12-23 17:00 | 2022-12-21 10:06 | 2022-12-23 17:00 | 2022-12-21 11:35 |  |  | Completed 21/12/2022
MSA-DFES | WA4992686 | 1 | Water2water Pty Ltd | Second floor - kitchen - zip hotwater unit not working | Plumbing & Drainage | HWS/Units Electric & Gas | 389.415 | Pass | Pass | 0 | 0 | 1.4833 | 2022-01-06 15:31 | 2022-01-07 17:00 | 2022-01-07 11:59 | 2022-01-07 17:00 | 2022-01-07 13:28 |  |  | Replaced fault lcd
MSA-DTWD | WA5127259 | 1 | Kone Elevators Pty Ltd | Q Block - Ground - Lift - Q-Block lift telephone not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.4833 | 2022-02-14 12:00 | 2022-02-15 17:00 | 2022-02-15 13:07 | 2022-02-15 17:00 | 2022-02-15 14:36 |  |  | Equipment running, back to normal operation4 REPORTED ISSUES WITH PHONE SINCE 24 7 20. GSM IS A SCHINDLER CUDE, IT STATES THAT THERE IS NO AVAILABLE SIGNAL. MOVED ANTENNA INTO LIFT HALLWAY, NO SIG. COMPANY OPTUS PHONE HAS HALF A BAR. SUGGEST ANOTHER GSM, ANTENNA AND TELSTRA SIM CARD.
MSA-DTAG | WA5394244 | 1 | FSA (WA) Pty Ltd | Fire Panel - Ground - Courtroom building - please see details below | Fire Protection Services | Fire Protection - Monitor System | 193.51 | Pass | Pass | 0 | 0 | 1.4833 | 2022-05-04 14:16 | 2022-05-05 17:00 | 2022-05-04 14:30 | 2022-05-05 17:00 | 2022-05-04 15:59 |  |  | Arrived for false alarm in zone 13. When arrived the fire panel had zone 13 isolated but it was all normal. Spoke with Managaer and was told firies came and couldn’t find detector and they isolated the zone. Unable to look for detector that went off as there is no alarm present and someone must have reset the alarm. There are roof workers above zone 13 changing out flashings on the roof and it is possible when using the blowtorch they have set off a roof space detector. I have put the system back online and all is ok.
MSA-DCA | WA5381730 | 1 | TK Elevator Australia Pty Ltd | Main Building - Basement 2 - Lift 7 - not leaving B2 level unless called from another level | Lifts | Lifts | 420.98 | Pass | Pass | 0 | 0 | 1.4667 | 2022-04-26 11:08 | 2022-04-27 17:00 | 2022-04-27 08:33 | 2022-04-27 17:00 | 2022-04-27 10:01 |  |  | Lift hallway button and landing board on B2 damaged due to water. Water damaged evident.
MSA-DFES | WA5385613 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Hallway before duty room - faulty light switch - see notes below | Electrical | Lighting, Internal | 113.295 | Pass | Pass | 0 | 0 | 1.4667 | 2022-04-29 11:07 | 2022-05-02 17:00 | 2022-04-29 13:30 | 2022-05-02 17:00 | 2022-04-29 14:58 |  |  | Arrived onsite at 13:30 to investigate light switch pushed in located near duty room. Found 1 x light switched had been pushed into recess box due to damaged grid plate holding the mechanism in. Replaced 1 x 2 gang grid plate and resecured to wall. Left site at 14:15
MSA-DTWD | WA6526798 | 2 | AHS Services WA Pty Ltd (Anchor) | Sink is constantly running and wasting water | Plumbing & Drainage | Water | 194.155 | Pass | Pass | -1 | -1 | 1.4667 | 2023-02-01 10:58 | 2023-02-06 17:00 | 2023-02-01 13:15 | 2023-02-06 17:00 | 2023-02-01 14:43
MSA-DTAG | WA6726910 | 0 | GPS Plumbing & Gas Services PtyLtd | Detention - Cell 3 & 4 - Toilets and fountain have no water | Plumbing & Drainage | Toilets/Cisterns | 259.335 | Pass | Pass | 0 | 0 | 1.4667 | 2023-03-15 09:12 | 2023-03-15 11:12 | 2023-03-15 11:02 | 2023-03-15 13:12 | 2023-03-15 12:30
MSA-DTAG | WA6654086 | 3 | Gilmour & Jooste Electrical | Laneway - Underground carpark - Strobe light - Damaged | Electrical | Lighting, External | 679.54 | Pass | Pass | 0 | 0 | 1.45 | 2023-02-21 09:35 | 2023-02-28 17:00 | 2023-02-28 06:00 | 2023-02-28 17:00 | 2023-02-28 07:27
MSA-DFES | WA5377702 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Level - Hose room - Taps on sink are blocked or broken - Nil waterflow when taps are open | Plumbing & Drainage | Water | 184.13 | Pass | Pass | 0 | 0 | 1.45 | 2022-04-20 08:37 | 2022-04-28 17:00 | 2022-04-26 08:48 | 2022-04-28 17:00 | 2022-04-26 10:15 |  |  | Isolated the water to the station to remove 3 bib taps they are blocked up found that the taps are full off sand so cleared out put back together tested and working correctly now.
MSA-DCA | WA5437567 | 0 | TK Elevator Australia Pty Ltd | Ground Level - Kitchen Lift -out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.45 | 2022-05-16 09:40 | 2022-05-16 11:40 | 2022-05-16 10:18 | 2022-05-16 13:40 | 2022-05-16 11:45 |  |  | Eleven flashes from LED, reset rope brake monitor. Pumped rope brake to reset pads.to be closed out at $0 cost
MSA-DTAG | WA5081215 | 1 | AHS Services WA Pty Ltd (Anchor) | All areas - Administration - prominent sewage smell at the front security check point - blocked pipe | Plumbing & Drainage | Drainage | 260.515 | Pass | Pass | 0 | 0 | 1.4333 | 2022-01-20 12:01 | 2022-01-21 17:00 | 2022-01-21 07:24 | 2022-01-21 17:00 | 2022-01-21 08:50 |  |  | Completed
MSA-DFES | WA5307764 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Station officers bathroom - plumbing issues - see notes below | Plumbing & Drainage | Water | 459.91 | Pass | Pass | 0 | 0 | 1.4333 | 2022-04-07 16:08 | 2022-04-12 17:00 | 2022-04-12 09:01 | 2022-04-12 17:00 | 2022-04-12 10:27 |  |  | Changed a shower mixer 40mm
MSA-DCA | WA5494380 | 2 | GPS Plumbing & Gas Services PtyLtd | Food & Beverage Kitchen Office - Toilet leaking a sewerage smell - See notes below | Plumbing & Drainage | Toilets/Cisterns | 182.29 | Pass | Pass | 0 | 0 | 1.4333 | 2022-06-07 14:39 | 2022-06-10 17:00 | 2022-06-08 12:30 | 2022-06-10 17:00 | 2022-06-08 13:56 |  |  | Inspect smell in office near stage door entrance. No smell evident while I was there. Check all drains and toilets near by. No evidence around. Aircon vent in office looks like it is coming in from outside. Maybe smell is coming from there somehow? But no immediate reason while there would be a smell there. But once again, no smell was there whilst I was present
MSA-DTAG | WA5682778 | 3 | GPS Plumbing & Gas Services PtyLtd | Staff Ladies Toilet - 2 x toilet seats in deteriorated state and unhygienic | Plumbing & Drainage | Toilets/Cisterns | 323.75 | Pass | Pass | -1 | -1 | 1.4333 | 2022-07-29 11:49 | 2022-08-05 17:00 | 2022-08-01 14:14 | 2022-08-05 17:00 | 2022-08-01 15:40 |  |  | Replaced 2x toilet seats in female staff toilets
MSA-DCA | WA5207667 | 1 | Allpest WA | Level 2 - Main bar - pigeons in the ceiling and air conditioning | Pest Control | General Pest | 161.82 | Fail | Fail | 1 | 1 | 1.4333 | 2022-03-08 15:25 | 2022-03-09 17:00 | 2022-03-14 11:05 | 2022-03-09 17:00 | 2022-03-14 12:31 |  |  | Allpest completed works 14.03.2022
MSA-DCA | WA5697881 | 0 | Techworks Plumbing | ground Hackett Hall-water spout on wash hand basin has come off | Plumbing & Drainage | Water | 326.58 | Pass | Pass | 0 | 0 | 1.4333 | 2022-08-09 12:33 | 2022-08-09 14:33 | 2022-08-09 12:34 | 2022-08-09 16:33 | 2022-08-09 14:00 |  |  | attended site and signed in at security office, they directed us to where the tap spout had come off when we got there someone had already put the spout back on so we had a look at why it come off sometimes it’s just hold on by a o ring and a grub screw so we tightened the crib screw up really tight it should be fine now we also tightened the Airator because it was loosewe informed the reception that it was allgood and signed out completed paperwork
MSA-MRWA | WA6361329 | 3 | EQUANS Mechanical Services (WA) Pty Limited | Soils Lab-Replace failed fume cupboard battery | Air Conditioning | Evaporative Coolers | 323.705 | Pass | Pass | -1 | -1 | 1.4333 | 2022-12-08 09:05 | 2022-12-15 17:00 | 2022-12-08 14:04 | 2022-12-15 17:00 | 2022-12-08 15:30 |  |  | Obtained battery and delivered to DAC
MSA-DTWD | WA5018104 | 2 | AHS Services WA Pty Ltd (Anchor) | V Block - male toilets - end cubicle - toilet seat broken | Plumbing & Drainage | Toilets/Cisterns | 421.465 | Pass | Pass | 0 | 0 | 1.4167 | 2022-01-14 08:47 | 2022-01-19 17:00 | 2022-01-17 07:15 | 2022-01-19 17:00 | 2022-01-17 08:40 |  |  | Completed
MSA-DFES | WA5093653 | 1 | Anvil Doors | Engine room-Area 21-Engine Door has been struck by Vehicle and door cant be closed | Building | General Building | 550 | Pass | Pass | 0 | 0 | 1.4167 | 2022-01-29 11:54 | 2022-01-30 11:54 | 2022-01-29 12:45 | 2022-01-30 11:54 | 2022-01-29 14:10 |  |  | Attended Wangara Fire Station. Technician reset error code on motor. Technician straightened bottom door panel and fixed some trim back on the door panel. Door is fit for service and is working as it should. Bottom panel may need replacing-- Panel size 580 x 3570.Please see attached service report and signature slip.
MSA-DTWD | WA5291905 | 1 | CONNECT SECURITY SYSTEMS | Power went off on Saturday and the alarm went off in C block now we unable to arm or disarm it | Security | Security Management System | 439.77 | Pass | Pass | 0 | 0 | 1.4167 | 2022-03-28 07:47 | 2022-03-28 17:00 | 2022-03-28 10:15 | 2022-03-28 17:00 | 2022-03-28 11:40 |  |  | reset alarms and replaced 2 x motion sensors
MSA-DTWD | WA5294700 | 1 | ECO PLUMBING AND GAS PTY LTD | C block - walkway out side customer service (C21) - External garden tap leaking | Plumbing & Drainage | Water | 205.99 | Pass | Pass | 0 | 0 | 1.4167 | 2022-03-29 08:37 | 2022-03-30 17:00 | 2022-03-29 13:50 | 2022-03-30 17:00 | 2022-03-29 15:15 |  |  | Replaced leaking hose tap
MSA-DFES | WA5384387 | 2 | SONTEC WA PTY LTD | Court Yard & Foyer - Camera Issues - See Notes | Security | CCTV Surveillance | 390 | Pass | Pass | 0 | 0 | 1.4167 | 2022-04-28 12:26 | 2022-05-03 17:00 | 2022-05-02 09:20 | 2022-05-03 17:00 | 2022-05-02 10:45 |  |  | 2/5/22 - Dylan ParslowReset power alarm on keysafe.Found powered housing for courtyard camera faulty. Rewired to camera directly.All working correctly.
MSA-DTWD | WA5691792 | 1 | Milners Tree Solutions Pty Ltd | Large fallen tree requiring cutting and removal - See notes below | Landscaping & Gardening | Tree Lopping | 2200 | Fail | Fail | 1 | 1 | 1.4167 | 2022-08-03 08:05 | 2022-08-04 17:00 | 2022-08-08 06:20 | 2022-08-04 17:00 | 2022-08-08 07:45 |  |  | FALLEN STEM REMOVED. REPORT ON CONDITION OF TREE FORWARDED
MSA-DTWD | WA5862196 | 1 | AWB Co. | No power to half the workshop | Electrical | General Electrical | 216.4225 | Pass | Pass | 0 | 0 | 1.4167 | 2022-09-13 14:34 | 2022-09-14 17:00 | 2022-09-13 14:35 | 2022-09-14 17:00 | 2022-09-13 16:00 |  |  | Attended site. Signed in. Completed jsa. Spoke to fm. He said half workshop had no power. Went to workshop and located DB. found that e stop isolator had tripped causing no power to half of workshop. Went around workshop and made sure all e stops weren’t pushed in. Found one that was pushed in. Reset e stop. Reset e stop isolator in board. Working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5973249 | 3 | Dormakaba Australia Pty Ltd | West entrance gallery -Automatic sliding door opening only up to three quarters of door frame | Building | Automatic Doors | 240 | Pass | Pass | -1 | -1 | 1.4167 | 2022-09-21 11:51 | 2022-09-29 17:00 | 2022-09-21 14:17 | 2022-09-29 17:00 | 2022-09-21 15:42 |  |  | 1091699. Call to site. Access and attend to auto door. Inspect circuitry. Re-instate door stopper to correct position to comply with AS5007 and complete fresh learn cycle. Tested operational and safety features - all okay. Check adjacent door as requested by Michael.
MSA-DCA | WA5988767 | 2 | GPS Plumbing & Gas Services PtyLtd | Full Flush Button does not flush and button keeps sticking | Plumbing & Drainage | Toilets/Cisterns | 292.665 | Pass | Pass | 0 | 0 | 1.4167 | 2022-10-04 10:56 | 2022-10-07 17:00 | 2022-10-05 10:15 | 2022-10-07 17:00 | 2022-10-05 11:40 |  |  | Replaced button washers and added extra grease.
MSA-DCA | WA6126667 | 3 | GPS Plumbing & Gas Services PtyLtd | DR5 & Ladies on Mezzanine, Ladies far left cubicle in Upper Circle-toilets running | Plumbing & Drainage | Toilets/Cisterns | 324.75 | Pass | Pass | -1 | -1 | 1.4167 | 2022-10-25 12:53 | 2022-11-01 17:00 | 2022-10-27 12:30 | 2022-11-01 17:00 | 2022-10-27 13:55 |  |  | Replaced 2 inlet valves and 2 outlet washers, the other toilet mezzanine level far left change room toilet, no issues
MSA-DFES | WA6143797 | 0 | Anvil Doors | Engine Room - Front SET entry door is stuck open and is security | Building | Automatic Doors | 452.5 | Pass | Pass | 0 | 0 | 1.4167 | 2022-11-01 15:16 | 2022-11-01 17:16 | 2022-11-01 16:50 | 2022-11-01 19:16 | 2022-11-01 18:15 |  |  | Please see attached attendance report for Osbourne Park Fire Station. Our technician has recommended that the transforms are replaced/ upgraded to 3 of the doors (he did one yesterday evening) and 4 x additional power supplies are installed for each of the 4 traffic lights.If you need any further information or assistance,
MSA-DTAG | WA6365513 | 3 | Water2water Pty Ltd | Magistrates Hot Water Urn - not working | Plumbing & Drainage | HWS/Units Electric & Gas | 405.26 | Fail | Fail | 0 | 0 | 1.4167 | 2022-12-13 10:16 | 2022-12-20 17:00 | 2022-12-23 12:05 | 2022-12-20 17:00 | 2022-12-23 13:30 |  |  | Replaced faulty element- Also replaced Blown Board
MSA-DTWD | WA6528670 | 2 | Securex Security Systems & Services | Level 1 - Check security system - alarms are being activated every 2 to 3 days | Security | Security Management System | 280 | Pass | Pass | 0 | 0 | 1.4167 | 2023-02-02 11:40 | 2023-02-07 17:00 | 2023-02-07 12:45 | 2023-02-07 17:00 | 2023-02-07 14:10
MSA-DCA | WA6531032 | 1 | GPS Plumbing & Gas Services PtyLtd | Second sink, u-bend under sink leaking after water goes down drain | Plumbing & Drainage | Water | 204.165 | Pass | Pass | 0 | 0 | 1.4167 | 2023-02-03 08:34 | 2023-02-06 17:00 | 2023-02-03 12:20 | 2023-02-06 17:00 | 2023-02-03 13:45
MSA-DFES | WA6540184 | 3 | Dom's Total Grounds Maintenance | Outside lawn area - Water leak - see notes | Plumbing & Drainage | Water | 303 | Pass | Pass | -1 | -1 | 1.4167 | 2023-02-09 09:06 | 2023-02-16 17:00 | 2023-02-11 16:50 | 2023-02-16 17:00 | 2023-02-11 18:15
MSA-DTWD | WA6672334 | 2 | CONNECT SECURITY SYSTEMS | Allocate new PIN's to new Security Contractor, ( see notes ) | Security | Security Management System | 234.03 | Pass | Pass | 0 | 0 | 1.4167 | 2023-02-23 15:12 | 2023-02-28 17:00 | 2023-02-28 09:30 | 2023-02-28 17:00 | 2023-02-28 10:55
MSA-DTWD | WA5287764 | 2 | SENTINEL LOCK SERVICE PTY LTD | Faulty Padlock on pool table | Security | Locksmith | 287.93 | Fail | Fail | 1 | 1 | 1.4167 | 2022-03-22 15:39 | 2022-03-25 17:00 | 2022-03-31 12:25 | 2022-03-25 17:00 | 2022-03-31 13:50 |  | WACCES | Block C - Cafe area - padlock to pool table faulty.Faulty padlock removed and replaced with new padlock.
MSA-DTAG | WA5698141 | 3 | Water2water Pty Ltd | Kitchen - Hot water urn tap is leaking | Plumbing & Drainage | HWS/Units Electric & Gas | 481.49 | Pass | Pass | 0 | 0 | 1.4167 | 2022-08-09 14:56 | 2022-08-16 17:00 | 2022-08-15 11:25 | 2022-08-16 17:00 | 2022-08-15 12:50 |  |  | Leaking tap on arrival. Opened system. Solenoid and level sensors in bad shape due to age. Replaced tap, hot tank level sensors and solenoid. Checked under pressure. Ran system to temp. Normal operation
MSA-DFES | WA5459676 | 1 | SONTEC WA PTY LTD | Exit Boom Gate - not opening and closing properly - manually open it | Security | Access Control | 390 | Pass | Pass | 0 | 0 | 1.4167 | 2022-05-18 08:03 | 2022-05-19 17:00 | 2022-05-18 15:15 | 2022-05-19 17:00 | 2022-05-18 16:40 |  |  | 18/5/22 - Dylan ParslowTested operation of boom gate.Boom gate sometimes not responding to open signal.No fault with security contact.
MSA-MRWA | WA5976716 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Male bathroom - right side cubicle leaking from wall | Plumbing & Drainage | Water | 391.125 | Pass | Pass | 0 | 0 | 1.4167 | 2022-09-27 10:56 | 2022-09-28 17:00 | 2022-09-27 16:00 | 2022-09-28 17:00 | 2022-09-27 17:25 |  |  | Replaced leaking rubbers. Pan must not be used for at least 24h.
MSA-DTWD | WA5995227 | 2 | BAKE-QUIP PTY LTD | Canteen kitchen the Combo therm oven does not heat anymore | Equipment | Catering Equipment | 262.5 | Pass | Pass | 0 | 0 | 1.4167 | 2022-10-06 11:30 | 2022-10-11 17:00 | 2022-10-11 10:00 | 2022-10-11 17:00 | 2022-10-11 11:25 |  |  | PARTS CANNOT BE SOURCED - SUGGEST OVEN IS REPLACED.
MSA-DTWD | WA6156842 | 0 | SCAVENGER SUPPLIES PTY LTD | admin - fire hose leaking and fire alarm going off | Fire Protection Services | Fire Protection - Monitor System | 369.52 | Pass | Pass | 0 | 0 | 1.4167 | 2022-11-09 11:03 | 2022-11-09 13:03 | 2022-11-09 11:50 | 2022-11-09 15:03 | 2022-11-09 13:15 |  |  | COMPLETED 09/11/2022NO FURTHER WORK REQUIRED BUT REQUEST FOR QUOTATION OF MCP MULTIKIT STOPPER WITH SOUNDER FOR ALL MCP TO PREVENT VANDALISM
MSA-DTWD | WA6688087 | 1 | ACTION GLASS & ALUMINIUM | Main Entrance - External - Glass wall panel loose (potential hazard if falls) | Glazing | Glass wall | 262.61 | Pass | Pass | 0 | 0 | 1.4167 | 2023-03-07 11:41 | 2023-03-08 17:00 | 2023-03-07 13:20 | 2023-03-08 17:00 | 2023-03-07 14:45
MSA-DTAG | WA5308717 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Custody Area - Cell 3 - Bio clean - toilet water and spitting | Cleaning | Cleaning | 300 | Fail | Fail | 0 | 0 | 1.4 | 2022-04-08 15:07 | 2022-04-11 17:00 | 2022-04-14 01:06 | 2022-04-11 17:00 | 2022-04-14 02:30 |  |  | As per work order no# WA5308717
MSA-DTAG | WA5379411 | 3 | AHS Services WA Pty Ltd (Anchor) | Ground Level - Male Custody Staff Toilets - Toilet is slowly leaking - ( male Ventia staff toilet) | Plumbing & Drainage | Toilets/Cisterns | 183.415 | Pass | Pass | -1 | -1 | 1.4 | 2022-04-21 10:58 | 2022-04-29 17:00 | 2022-04-22 13:22 | 2022-04-29 17:00 | 2022-04-22 14:46 |  |  | Completed
MSA-DTWD | WA5206903 | 1 | CONNECT SECURITY SYSTEMS | Security alarm panel in T/Block has communication issues with the monitoring company - Education Sec | Security | Security Management System | 458.11 | Pass | Pass | 0 | 0 | 1.4 | 2022-03-08 10:10 | 2022-03-09 17:00 | 2022-03-08 10:11 | 2022-03-09 17:00 | 2022-03-08 11:35 |  |  | Replaced blown transformer in B Block. Closed window in T Block causing issues
MSA-DCA | WA5270425 | 1 | Earth & Water Pty Ltd | Retic - leak high flow alert zone 10 | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.4 | 2022-03-18 07:52 | 2022-03-18 17:00 | 2022-03-18 08:21 | 2022-03-18 17:00 | 2022-03-18 09:45 |  |  | job completed - -Arrived on site and ran zone 10.-Located leak at base of sprinkler. Leak had caused lawn pimple.-Exposed area around leak and found snapped 15mm poly nipple-Replaced nipple. Could not get old nipple out of Rainbird sprinkler body so replaced the body as well.-Tested and flushed system. Leak fixed.-Old Mp rotator head had become blocked by sediment which had got in through cracked fitting. Replaced.-Flow tested system. 7200Iph-Left area clean and tidy-Photos added to client diary
MSA-MRWA | WA5488364 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - Female bathroom - leaking toilet | Plumbing & Drainage | Toilets/Cisterns | 158.235 | Pass | Pass | 0 | 0 | 1.4 | 2022-06-02 12:16 | 2022-06-03 17:00 | 2022-06-03 10:36 | 2022-06-03 17:00 | 2022-06-03 12:00 |  |  | Replaced cone rubber
MSA-DCA | WA5585930 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground floor - men's toilet - broken toilet lid | Plumbing & Drainage | Water | 303.935 | Pass | Pass | -1 | -1 | 1.4 | 2022-07-06 09:22 | 2022-07-13 17:00 | 2022-07-08 09:17 | 2022-07-13 17:00 | 2022-07-08 10:41 |  |  | Replaced toilet seat to ground floor male toilets
MSA-MRWA | WA6166446 | 3 | GPS Plumbing & Gas Services PtyLtd | Sink drainage pipe is leaking | Plumbing & Drainage | Drainage | 225.165 | Pass | Pass | 0 | 0 | 1.4 | 2022-11-11 15:25 | 2022-11-18 17:00 | 2022-11-15 08:26 | 2022-11-18 17:00 | 2022-11-15 09:50 |  |  | Replaced leaking trap under sink in asphalt lab
MSA-MRWA | WA5454890 | 0 | GPS Plumbing & Gas Services PtyLtd | Level 9 - Plant room - Domestic Hot water unit is flashing as fault | Plumbing & Drainage | HWS/Units Electric & Gas | 258.42 | Pass | Pass | 0 | 0 | 1.3833 | 2022-05-17 15:55 | 2022-05-17 17:55 | 2022-05-17 16:52 | 2022-05-17 19:55 | 2022-05-17 18:15 |  |  | On my arrivale the water temperature was on 57 degrees. It did raise to 60. Checked and cleaned strainers(pump strainer pretty full). No faults dound. Both continuous hot water system working. Hot water in all 4 storage tanks. Turn hot tap on on several floor-hot water coming out with the right temperature.
MSA-DTAG | WA5569268 | 2 | Dormakaba Australia Pty Ltd | Staff car park exit door – electronic door -pedestrian gate attached to the car park is not locking | Building | Steel Fencing & Gates | 715.45 | Pass | Pass | 0 | 0 | 1.3833 | 2022-06-27 13:06 | 2022-06-30 17:00 | 2022-06-28 12:18 | 2022-06-30 17:00 | 2022-06-28 13:41 |  |  | Inspected gate and found an intermittent fault with the closing cycle of the door closer (closing too quickly) replaced door closer as necessary with new ts83 closer and adjusted speeds etc. I’ve also noticed that if a complete cycle isn’t carried out once the gate is unlocked that the electric lock doesn’t re-engage, advised to site that the only way over this is to get a mag lock fitted instead by access control techs.
MSA-MRWA | WA6112172 | 2 | Automatic Fire Protection (ARA) | Smoke sensor in fault L3S20 Storage shed | Fire Protection Services | Fire Protection - Monitor System | 563.9 | Pass | Pass | 0 | 0 | 1.3833 | 2022-10-21 13:20 | 2022-10-26 17:00 | 2022-10-25 10:37 | 2022-10-26 17:00 | 2022-10-25 12:00 |  |  | Attended site and found device 3020 Az 17 Smoke detector in maintenance fault checked Av found to be 40.Located device and fitted new reset and left normal.
MSA-DCA | WA6431324 | 0 | Dormakaba Australia Pty Ltd | Main Entrance - Sliding Doors - not closing properly | Building | Automatic Doors | 436.95 | Pass | Pass | 0 | 0 | 1.3833 | 2023-01-13 12:59 | 2023-01-13 14:59 | 2023-01-13 14:02 | 2023-01-13 16:59 | 2023-01-13 15:25
MSA-DCA | WA6651018 | 1 | Dormakaba Australia Pty Ltd | Jubilee is wrong location - Fault is at Frasers Street side auto door - See Attached Photo | Building | Automatic Doors | 290 | Pass | Pass | 0 | 0 | 1.3833 | 2023-02-20 16:39 | 2023-02-21 17:00 | 2023-02-21 09:27 | 2023-02-21 17:00 | 2023-02-21 10:50
MSA-DCA | WA5660504 | 2 | Dormakaba Australia Pty Ltd | Ground Level - Loading Bay - Service and repair auto sliding doors to either side | Building | Doors | 430 | Pass | Pass | 0 | 0 | 1.3833 | 2022-07-19 10:10 | 2022-07-22 17:00 | 2022-07-19 13:20 | 2022-07-22 17:00 | 2022-07-19 14:43 |  |  | 2 techs - Arrived to door, to discover rubbing on top and bottom capping of doors, adjusted door gap, and re tightened, door is now aligned straight. Cosmetic damage has been done to end caps, approx 1.8 meters longThis will require a glass fabricator to replace.
MSA-MRWA | WA6544677 | 1 | GPS Plumbing & Gas Services PtyLtd | male toilet - constant running cisten | Plumbing & Drainage | Toilets/Cisterns | 196.165 | Pass | Pass | 0 | 0 | 1.3833 | 2023-02-10 15:53 | 2023-02-13 17:00 | 2023-02-13 07:47 | 2023-02-13 17:00 | 2023-02-13 09:10
MSA-DTAG | WA6519966 | 1 | Automatic Fire Protection (ARA) | Near Custody – Main Fire Panel - Fault displaying on fire panel (see notes) | Fire Protection Services | Fire Protection - Monitor System | 400.7 | Pass | Pass | 0 | 0 | 1.3667 | 2023-01-27 09:24 | 2023-01-30 17:00 | 2023-01-27 10:08 | 2023-01-30 17:00 | 2023-01-27 11:30
MSA-DTWD | WA5038104 | 1 | CONNECT SECURITY SYSTEMS | Block 1 - Ground - Cleaners room - Alarm panel for block 1 faulting | Security | Monitoring | 300.45 | Pass | Pass | 0 | 0 | 1.3667 | 2022-01-17 10:21 | 2022-01-18 17:00 | 2022-01-17 11:48 | 2022-01-18 17:00 | 2022-01-17 13:10 |  |  | Replaced 1 x PIR, and indidiually fused remaining zones 2 & 4 shorting out power supply.
MSA-DCA | WA5306590 | 2 | GPS Plumbing & Gas Services PtyLtd | Main Museum - Ground - Men’s toilets - Water is running constantly in two of the three urinals | Plumbing & Drainage | Toilets/Cisterns | 778.345 | Pass | Pass | 0 | 0 | 1.3667 | 2022-04-06 15:00 | 2022-04-11 17:00 | 2022-04-08 08:50 | 2022-04-11 17:00 | 2022-04-08 10:12 |  | WACCES | Replaced urinal flushing valve/solenoid.
MSA-DCA | WA6535233 | 2 | GPS Plumbing & Gas Services PtyLtd | History Department-Seal between cistern pipe and toilet base. Seal is badly eroded and leaking-notes | Plumbing & Drainage | Toilets/Cisterns | 301.165 | Pass | Pass | 0 | 0 | 1.3667 | 2023-02-06 16:04 | 2023-02-09 17:00 | 2023-02-08 10:07 | 2023-02-09 17:00 | 2023-02-08 11:29
MSA-DCA | WA5295213 | 3 | GPS Plumbing & Gas Services PtyLtd | Men’s bathrooms - BOH Opera - Level 3 - see details below | Plumbing & Drainage | Materials | 138.235 | Pass | Pass | -1 | -1 | 1.3667 | 2022-03-29 11:49 | 2022-04-05 17:00 | 2022-04-01 08:30 | 2022-04-05 17:00 | 2022-04-01 09:52 |  |  | Tightened loose nuts under basin RHS
MSA-DCA | WA5675260 | 0 | TK Elevator Australia Pty Ltd | Lift is stuck below ground level | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.3667 | 2022-07-22 09:11 | 2022-07-22 11:11 | 2022-07-22 10:43 | 2022-07-22 13:11 | 2022-07-22 12:05 |  |  | Lift1 PICA-Gearless :Found lift below sill on level B.Moved lift on inspection. Reset processor.Cheked iputs from shaft inductors for UP and Down travel and terminal slow down.Ran lift top to bottom , V1 relay does not come ON to input medium speed . As per prints the VVF does not get medium speed commands from processor. Checked voltageon ouput U08 on PLC.Checked in inspection mode, V1 remains OFF . Checked VIM board (Drive interface board) DL1 dip switch setting does not match prints. Tested lift . Put back in service.
MSA-DTWD | WA5400313 | 2 | AHS Services WA Pty Ltd (Anchor) | Barista room has a leaking tap behind coffee machine | Plumbing & Drainage | Water | 215.415 | Pass | Pass | 0 | 0 | 1.35 | 2022-05-10 09:20 | 2022-05-13 17:00 | 2022-05-10 12:09 | 2022-05-13 17:00 | 2022-05-10 13:30 |  |  | work complete
MSA-DCA | WA5573124 | 1 | GPS Plumbing & Gas Services PtyLtd | Exterior behind PICA building - Drains appear to be blocked with toilet paper | Plumbing & Drainage | Drainage | 231.165 | Pass | Pass | 0 | 0 | 1.35 | 2022-06-30 13:32 | 2022-07-01 17:00 | 2022-07-01 11:09 | 2022-07-01 17:00 | 2022-07-01 12:30 |  |  | Cleaned sewage at the back of pica building.Installed new grate to gully.
MSA-DTWD | WA5980235 | 2 | Techworks Plumbing | AT221 Male Toilet -Toilet in 1st cubicle, the flush pipe is leaking. | Plumbing & Drainage | Toilets/Cisterns | 599.92 | Pass | Pass | 0 | 0 | 1.35 | 2022-09-29 13:41 | 2022-10-04 17:00 | 2022-10-03 07:45 | 2022-10-04 17:00 | 2022-10-03 09:06 |  |  | Assessed toilet in first male cubicle, found leaking flush pipe and keeseal, and loose toilet panReplaced flush pipe and 50mm keesealReinstated and resealed toilet pan to floor
MSA-DCA | WA6394234 | 0 | TK Elevator Australia Pty Ltd | Ground - main lift - fault message: emergency phone line not working | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 1.35 | 2022-12-30 09:53 | 2022-12-30 11:53 | 2022-12-30 10:53 | 2022-12-30 13:53 | 2022-12-30 12:14 |  |  | Upon arrival I found the lift running however the 3g gsm unit located on the lift car top is not connecting to the new 4/5 g system a new gsm unit is required the staff on site has been advised a quote to follow for a new gsm unit
MSA-DTAG | WA6404762 | 1 | Water2water Pty Ltd | Level 1 - Staff Kitchen - water not being dispensed from hot water unit - see notes below | Plumbing & Drainage | Water | 537.49 | Pass | Pass | 0 | 0 | 1.35 | 2023-01-09 09:02 | 2023-01-10 17:00 | 2023-01-09 10:40 | 2023-01-10 17:00 | 2023-01-09 12:01
MSA-DTWD | WA6516369 | 0 | Equans Mechanical Services Australia | IT Office 240 - No air conditioning in building | Air Conditioning | Package | 219.6 | Pass | Pass | 0 | 0 | 1.35 | 2023-01-23 11:08 | 2023-01-23 13:08 | 2023-01-23 11:09 | 2023-01-23 15:08 | 2023-01-23 12:30
MSA-DCA | WA5380297 | 3 | GPS Plumbing & Gas Services PtyLtd | First floor - Ladies public bathroom - Tap in disabled cubicle loose | Plumbing & Drainage | Materials | 214.29 | Pass | Pass | -1 | -1 | 1.3333 | 2022-04-22 10:23 | 2022-05-02 17:00 | 2022-04-22 14:20 | 2022-05-02 17:00 | 2022-04-22 15:40 |  |  | Replaced broken lock nut and installed ministop to make future maintenance easier
MSA-DTWD | WA6603164 | 2 | Water2water Pty Ltd | Ground floor & First floor - T block court yard, Canteen, Gym and 1st Floor x3 (see notes) | Plumbing & Drainage | Water | 368.41 | Pass | Pass | 0 | 0 | 1.3333 | 2023-02-17 11:54 | 2023-02-22 17:00 | 2023-02-22 12:05 | 2023-02-22 17:00 | 2023-02-22 13:25
MSA-DTWD | WA5053019 | 1 | AHS Services WA Pty Ltd (Anchor) | E Block - Ground - Staff Male Toilet - the urinal is leaking from the wall | Plumbing & Drainage | Toilets/Cisterns | 177.915 | Pass | Pass | 0 | 0 | 1.3333 | 2022-01-18 12:01 | 2022-01-19 17:00 | 2022-01-18 13:15 | 2022-01-19 17:00 | 2022-01-18 14:35 |  |  | Completed
MSA-DTWD | WA5175025 | 1 | ECO PLUMBING AND GAS PTY LTD | K02 - Bain Marie leaking onto Kitchen Floor | Plumbing & Drainage | Water | 195.99 | Pass | Pass | 0 | 0 | 1.3333 | 2022-02-21 09:20 | 2022-02-22 17:00 | 2022-02-22 15:10 | 2022-02-22 17:00 | 2022-02-22 16:30 |  |  | Serviced tap on baine marie.
MSA-DTWD | WA5239697 | 1 | AWB Co. | U015 - Glazing workshop - damaged pendant power point | Electrical | General Electrical | 180.54 | Pass | Pass | 0 | 0 | 1.3333 | 2022-03-16 14:36 | 2022-03-17 17:00 | 2022-03-16 14:40 | 2022-03-17 17:00 | 2022-03-16 16:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located pendant gpo, gpo had been ripped of by fork lift , isolated circuit and reconnected pendant, re energised and tested , everything working as intended, cable tied GPOs up high as per fm request as they aren’t used, completed paperwork, packed up, signed out Job completed
MSA-DCA | WA5303221 | 2 | Earth & Water Pty Ltd | James Street Amphitheatre - Ground – external - zone 13 - Broken sprinklers | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 1.3333 | 2022-04-04 08:29 | 2022-04-07 17:00 | 2022-04-04 10:40 | 2022-04-07 17:00 | 2022-04-04 12:00 |  |  | job completed - Arrived on site, ran zone 13 and identified the 2 broken sprinkler. Exposed around the sprinklers and removed the damaged ones.Replaced with 2 new sprinklers and fitted the old heads as they were still serviceable. Backfilled sprinklers and readjusted
MSA-DTWD | WA5304623 | 1 | LIGHTHOUSE LOCKSMITHS | Admin Building office next to Board Room - the door lock does not unlock | Security | Locksmith | 593.48 | Pass | Pass | 0 | 0 | 1.3333 | 2022-04-05 08:42 | 2022-04-06 17:00 | 2022-04-05 09:25 | 2022-04-06 17:00 | 2022-04-05 10:45 |  |  | Replaced damaged mortice lock and turn adaptor on office door next to board room in admin
MSA-DTAG | WA5305374 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Lower - Custody - Lower Custody Cell 2 Special clean - Person held within cell 2 had scabies | Cleaning | Hazardous Materials | 500 | Fail | Fail | 1 | 1 | 1.3333 | 2022-04-05 14:55 | 2022-04-06 17:00 | 2022-04-14 01:15 | 2022-04-06 17:00 | 2022-04-14 02:35 |  |  | As per work order
MSA-DCA | WA5398746 | 3 | Earth & Water Pty Ltd | Various Locations - Retic (Trip Hazard) Rectification - see notes below | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | -1 | -1 | 1.3333 | 2022-05-09 12:10 | 2022-05-16 17:00 | 2022-05-09 12:55 | 2022-05-16 17:00 | 2022-05-09 14:15 |  |  | -Raised 4x sprinklers-Packed around sprinkler with washed sand-Levelled off-Tested zone-Left area clean and tidy
MSA-DTAG | WA5462177 | 2 | Water2water Pty Ltd | Level 2 - Sherriffs Office - Kitchen - First Billi tap is not working | Plumbing & Drainage | HWS/Units Electric & Gas | 474.985 | Pass | Pass | 0 | 0 | 1.3333 | 2022-05-19 12:20 | 2022-05-24 17:00 | 2022-05-23 13:30 | 2022-05-24 17:00 | 2022-05-23 14:50 |  |  | replaced pump and level sensor loom on Billi Quadra A402011524
MSA-DCA | WA5472076 | 1 | GPS Plumbing & Gas Services PtyLtd | Blocked drain in walkway between AGWA and Urban Orchard. Water pooling and cause safety issue | Plumbing & Drainage | Drainage | 182.29 | Pass | Pass | 0 | 0 | 1.3333 | 2022-05-23 13:54 | 2022-05-24 17:00 | 2022-05-23 16:30 | 2022-05-24 17:00 | 2022-05-23 17:50 |  |  | On my arrival the drain was not blocked. Inspetthe area to find where a soakwell might be. Unable to find it. Run water into grate for approx 30mins. Water draining away good.
MSA-DCA | WA5565798 | 1 | TK Elevator Australia Pty Ltd | Lift 7 - broken down again - displaying Out of Order. | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.3333 | 2022-06-22 11:25 | 2022-06-23 17:00 | 2022-06-22 14:40 | 2022-06-23 17:00 | 2022-06-22 16:00 |  |  | On arrival lift at 3rd landing “STElap” fault, run timer exceeded. Also found hoist door fault due to faulty unlocking device on top landing. Checked run times - UP=33sec, DN=46sec empty car with final run timer set to 45sec. Adjusted run timer to 60sec. Test unit multiple times and OK on departure.to be closed out at $0 cost
MSA-DTWD | WA5566608 | 3 | Water2water Pty Ltd | First Level - Staff Room - Boiling Billy went bang and tripped RCD. | Plumbing & Drainage | HWS/Units Electric & Gas | 486.895 | Pass | Pass | -1 | -1 | 1.3333 | 2022-06-23 10:02 | 2022-06-30 17:00 | 2022-06-24 10:40 | 2022-06-30 17:00 | 2022-06-24 12:00 |  |  | Replaced fault float and element. Tested and calibrated. All now ok.
MSA-DCA | WA5613704 | 1 | ACTION GLASS & ALUMINIUM | Level 1 - Small dressing room - Broken window - See notes below | Glazing | Window Glass | 337.4 | Pass | Pass | 0 | 0 | 1.3333 | 2022-07-14 15:32 | 2022-07-15 17:00 | 2022-07-15 10:40 | 2022-07-15 17:00 | 2022-07-15 12:00 |  |  | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 TRANSLUCENT LAMINATED SAFETY GLASS1-1082 X 318PLUS SILICONE AND 8 SCREWS
MSA-DTWD | WA5674918 | 2 | Swan Pest Control | T Block - All Levels - Small Ants seen on all levels of T Block | Pest Control | General Pest | 490.5 | Pass | Pass | 0 | 0 | 1.3333 | 2022-07-21 15:56 | 2022-07-26 17:00 | 2022-07-26 11:40 | 2022-07-26 17:00 | 2022-07-26 13:00 |  |  | Sprayed external east end of building. Gelled window sills east end level 2. Gelled and sprayed west end ground level kitchenette.
MSA-DTAG | WA5761520 | 1 | Water2water Pty Ltd | L13 staff kitchen-Fault description Hot water system not working, water is not hot | Plumbing & Drainage | Water | 435.58 | Pass | Pass | 0 | 0 | 1.3333 | 2022-08-18 09:53 | 2022-08-19 17:00 | 2022-08-18 11:00 | 2022-08-19 17:00 | 2022-08-18 12:20 |  |  | Replaced hot pump and tested
MSA-DTWD | WA5976727 | 2 | AHS Services WA Pty Ltd (Anchor) | Staff Kitchenette-the sink drain is blocked | Plumbing & Drainage | Drainage | 211.655 | Pass | Pass | 0 | 0 | 1.3333 | 2022-09-27 11:01 | 2022-09-30 17:00 | 2022-09-28 14:00 | 2022-09-30 17:00 | 2022-09-28 15:20 |  |  | Completed
MSA-DCA | WA5988589 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Public area - Men's bathroom - Urinal blocked/not draining - see notes | Plumbing & Drainage | Drainage | 279.875 | Pass | Pass | 0 | 0 | 1.3333 | 2022-10-04 09:56 | 2022-10-07 17:00 | 2022-10-05 13:30 | 2022-10-07 17:00 | 2022-10-05 14:50 |  |  | Unblocked urinal, replaced grate
MSA-DCA | WA6001305 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 & 2 are alarming and chiller pump number 1 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 281.53 | Pass | Pass | 0 | 0 | 1.3333 | 2022-10-10 15:08 | 2022-10-10 17:08 | 2022-10-10 15:10 | 2022-10-10 19:08 | 2022-10-10 16:30 |  |  | Travelled to site and reset chiller 1 and 2 and chilled water pump 2 vsd all on alarm due to power failure. Accessed roof to ensure all equipment working again. Accessed bms to ensure no further alarms.
MSA-DCA | WA6159113 | 0 | TK Elevator Australia Pty Ltd | Lift is out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.3333 | 2022-11-10 11:45 | 2022-11-10 13:45 | 2022-11-10 12:45 | 2022-11-10 15:45 | 2022-11-10 14:05 |  |  | Lift1 PICA-Elevator > MRL > Gearless :Lift drove down into bottom final limits, reset lift, inspected and adjusted floor magnets on bottom floor, inspected IF relay givingabnormal readings-ordered new relay, No error log. Lift back in service.
MSA-DTWD | WA6159144 | 3 | Water2water Pty Ltd | A Block - Level 3 - Corridor - Cold Water Drinking Unit - No flow | Plumbing & Drainage | Water | 835.8 | Pass | Pass | 0 | 0 | 1.3333 | 2022-11-10 12:10 | 2022-11-17 17:00 | 2022-11-15 08:40 | 2022-11-17 17:00 | 2022-11-15 10:00 |  |  | Damaged/worn bottle filler faucet causing water block to trip. Replaced bottle filler faucet, tested and checked, all ok.
MSA-DTWD | WA6208085 | 2 | WESTERN IRRIGATION PTY LTD | External area of D15 Bakery Shop - Retic break under paving | Plumbing & Drainage | Water | 297.42 | Pass | Pass | 0 | 0 | 1.3333 | 2022-11-17 12:50 | 2022-11-22 17:00 | 2022-11-22 09:10 | 2022-11-22 17:00 | 2022-11-22 10:30 |  |  | Repaired broken pipework
MSA-DCA | WA6298836 | 0 | GPS Plumbing & Gas Services PtyLtd | boiler is leaking - GPS on site | Mechanical Services | Boilers | 230.285 | Pass | Pass | 0 | 0 | 1.3333 | 2022-12-01 13:59 | 2022-12-01 15:59 | 2022-12-01 14:00 | 2022-12-01 17:59 | 2022-12-01 15:20 |  |  | Cleared blocked drain in the plant room
MSA-DTWD | WA6385506 | 1 | SCAVENGER SUPPLIES PTY LTD | T126 cleaners store - Alarm activated overnight - Sensors need checking - See Notes | Fire Protection Services | Fire Protection - Monitor System | 353.699 | Pass | Pass | 0 | 0 | 1.3333 | 2022-12-21 09:48 | 2022-12-22 17:00 | 2022-12-21 12:00 | 2022-12-22 17:00 | 2022-12-21 13:20 |  |  | Arrived at site at 12 pm to a call out and alarm activation overnight. Detector 12 of zone 208 Was inalarm this morning and I had also come across another alarm being detector 61 of zone 134. Bothdetectors were taken out and checked with one detector having mild dust and the other a build up ofbugs and dust, this detector was replaced. Both detectors have be reinstated and the FIP back tonormal. A contractor of recent was doing renovations in a toilet block and has caused quite a lot ofdust. Monitor the area as this could bring more activations.Left site at 1.20pm- Completed 21/12/2022
MSA-DTWD | WA6425999 | 2 | AHS Services WA Pty Ltd (Anchor) | Through in hallway - Tap | Plumbing & Drainage | Water | 188.655 | Pass | Pass | 0 | 0 | 1.3333 | 2023-01-12 13:14 | 2023-01-17 17:00 | 2023-01-16 08:40 | 2023-01-17 17:00 | 2023-01-16 10:00
MSA-DCA | WA6488047 | 3 | GPS Plumbing & Gas Services PtyLtd | Cracked caroma button | Plumbing & Drainage | Toilets/Cisterns | 407.025 | Pass | Pass | 0 | 0 | 1.3333 | 2023-01-18 14:07 | 2023-01-25 17:00 | 2023-01-23 09:00 | 2023-01-25 17:00 | 2023-01-23 10:20
MSA-DTWD | WA6650956 | 2 | Water2water Pty Ltd | Zippy hot water system not working one in near east sink (please ring before attending) | Plumbing & Drainage | HWS/Units Electric & Gas | 239.62 | Pass | Pass | 0 | 0 | 1.3333 | 2023-02-20 15:01 | 2023-02-23 17:00 | 2023-02-23 10:30 | 2023-02-23 17:00 | 2023-02-23 11:50
MSA-DCA | WA5493773 | 3 | ADVANCED LOCK & KEY | Level 1 - Sensorium (next to Regional Arts) - please see details below | Security | Locksmith | 413.5 | Pass | Pass | -1 | -1 | 1.3333 | 2022-06-07 10:06 | 2022-06-14 17:00 | 2022-06-10 12:20 | 2022-06-14 17:00 | 2022-06-10 13:40 |  |  | Rekey 1.7.1 to work with only the xx and 1.7.1 keys on office and cut 4 keys 2 xx and 2 1.7.1 1x mk oval cyl 4x ot status 6 keys
MSA-DCA | WA5836300 | 0 | GPS Plumbing & Gas Services PtyLtd | sewerage pipe seal broken, leaking sewerage | Plumbing & Drainage | Sewer Drains & Septic Systems | 230.285 | Pass | Pass | 0 | 0 | 1.3333 | 2022-09-07 11:11 | 2022-09-07 13:11 | 2022-09-07 11:50 | 2022-09-07 15:11 | 2022-09-07 13:10 |  |  | No leaking sewer pipes found. Bad smell coming out from exhaust box/pipe located on the scene dock. Ken and I were unable to determin where the galvinsed spiral pipes come from. Different contractor needed. Denise advised
MSA-DTAG | WA5985900 | 1 | GPS Plumbing & Gas Services PtyLtd | Water leak in the Plant Room Level 3 | Plumbing & Drainage | Drainage | 349.48 | Pass | Pass | 0 | 0 | 1.3333 | 2022-10-01 16:52 | 2022-10-02 16:52 | 2022-10-02 10:50 | 2022-10-02 16:52 | 2022-10-02 12:10 |  |  | Inspected thoroughly plant room for water leaks. Found plastic tap on pvc pipe leaking(dripping). No other issues found. Moped the floor. No other actions taken. Let security know that different contractor has to be contacted to fix the leaking tap. Not an urgent job in my opinion.
MSA-DTAG | WA5998327 | 1 | GPS Plumbing & Gas Services PtyLtd | Detention-cell 3-Fault description Damage to the toilet button & steel plate surrounding the toilet | Plumbing & Drainage | Toilets/Cisterns | 226.165 | Pass | Pass | 0 | 0 | 1.3333 | 2022-10-07 14:07 | 2022-10-10 17:00 | 2022-10-10 13:50 | 2022-10-10 17:00 | 2022-10-10 15:10 |  |  | Screwed back the steel plate that was coming off the wall and fixed the bottom
MSA-MRWA | WA6393356 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 6 - Male Bathroom - RHS toilet constantly running | Plumbing & Drainage | Toilets/Cisterns | 391.165 | Pass | Pass | 0 | 0 | 1.3333 | 2022-12-28 12:55 | 2023-01-03 17:00 | 2023-01-03 09:20 | 2023-01-03 17:00 | 2023-01-03 10:40
MSA-DFES | WA6462454 | 1 | SONTEC WA PTY LTD | First Floor - Sock Entrance - Sock entrance door is not working - Auto door - egress button | Building | Automatic Doors | 486.73 | Pass | Pass | 0 | 0 | 1.3333 | 2023-01-17 09:07 | 2023-01-18 17:00 | 2023-01-17 13:50 | 2023-01-18 17:00 | 2023-01-17 15:10
MSA-DTWD | WA5109483 | 1 | CONNECT SECURITY SYSTEMS | AG21 Library Toilet Block Foyer - Alarm Panels in audible alarm and can’t be muted | Security | Security Management System | 425.47 | Pass | Pass | 0 | 0 | 1.3333 | 2022-02-09 09:47 | 2022-02-10 17:00 | 2022-02-09 10:00 | 2022-02-10 17:00 | 2022-02-09 11:20 |  |  | Replaced 6 x backup batteries
MSA-DCA | WA5112127 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Ground - Theatre Foyer - male public toilet - see below | Plumbing & Drainage | Toilets/Cisterns | 234.235 | Pass | Pass | 0 | 0 | 1.3333 | 2022-02-10 13:36 | 2022-02-15 17:00 | 2022-02-15 14:30 | 2022-02-15 17:00 | 2022-02-15 15:50 |  |  | Replaced toilet seat
MSA-DTAG | WA5735289 | 3 | Gilmour & Jooste Electrical | Court Waiting Area - 2 x down lights need fixing | Electrical | Lighting, Internal | 593.21 | Pass | Pass | 0 | 0 | 1.3333 | 2022-08-16 12:14 | 2022-08-23 17:00 | 2022-08-22 08:17 | 2022-08-23 17:00 | 2022-08-22 09:37 |  |  | Replaced 2x downlights to LED on dimmers above reception desk. Lights tested and working.
MSA-DTAG | WA6074748 | 1 | GPS Plumbing & Gas Services PtyLtd | Detention - Cell 1 - The button on the toilet is broken - May need to be replaced | Plumbing & Drainage | Toilets/Cisterns | 339.535 | Pass | Pass | 0 | 0 | 1.3333 | 2022-10-18 09:52 | 2022-10-19 17:00 | 2022-10-19 07:00 | 2022-10-19 17:00 | 2022-10-19 08:20 |  |  | Replaced damaged toilet button
MSA-DTWD | WA6128098 | 2 | Water2water Pty Ltd | Sandpit area - The water cooler near sand pit area is broken | Plumbing & Drainage | Water | 246.22 | Pass | Pass | -1 | -1 | 1.3333 | 2022-10-26 12:20 | 2022-10-31 17:00 | 2022-10-26 12:40 | 2022-10-31 17:00 | 2022-10-26 14:00 |  |  | Performed repairs to drain and internal tubings that was leaking.
MSA-MRWA | WA6449882 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 4 - Male toilets - Cistern constantly running | Plumbing & Drainage | Toilets/Cisterns | 430.165 | Pass | Pass | 0 | 0 | 1.3333 | 2023-01-16 08:08 | 2023-01-17 17:00 | 2023-01-16 11:23 | 2023-01-17 17:00 | 2023-01-16 12:43
MSA-DFES | WA6531211 | 2 | Water2water Pty Ltd | Cold water dispenser adjacent to the mezzanine floor leaking (see notes) | Plumbing & Drainage | HWS/Units Electric & Gas | 308.75 | Pass | Pass | 0 | 0 | 1.3333 | 2023-02-03 10:11 | 2023-02-08 17:00 | 2023-02-07 10:00 | 2023-02-08 17:00 | 2023-02-07 11:20
MSA-DTWD | WA6722049 | 1 | SCAVENGER SUPPLIES PTY LTD | Room - F009 - EWIS system in F Block not working - please investigate | Fire Protection Services | Fire Protection - Monitor System | 405.2 | Pass | Pass | 0 | 0 | 1.3333 | 2023-03-14 14:40 | 2023-03-15 17:00 | 2023-03-15 10:00 | 2023-03-15 17:00 | 2023-03-15 11:20
MSA-DFES | WA6364396 | 2 | Australian HVAC Services Pty. Ltd. | Ground floor - BMS is in fault. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 286.34 | Pass | Pass | 0 | 0 | 1.3275 | 2022-12-12 11:28 | 2022-12-13 17:00 | 2022-12-12 14:20 | 2022-12-13 17:00 | 2022-12-12 15:40 |  |  | Attended site and inspected hvac plant after power shut-down over weekend. Found chiller 2 on fault. Reset chiller and confirmed operation. Reset crac unit water flow faults.Confirmed all other plant operating correctly.
MSA-DCA | WA5694440 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 4 - Blocked floor drain | Plumbing & Drainage | Drainage | 196.165 | Pass | Pass | -1 | -1 | 1.3167 | 2022-08-05 10:10 | 2022-08-10 17:00 | 2022-08-05 12:10 | 2022-08-10 17:00 | 2022-08-05 13:29 |  |  | Inspected floor drains in plant room. Emptied few buckets of water in them. Drains draining ok. Closest water tap ~60m away.
MSA-DCA | WA5142306 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Ground Level - HBRC - Intermittent Fault in Walk in freezer HBRC | Refrigeration | Freezers | 293.025 | Pass | Pass | 0 | 0 | 1.3167 | 2022-02-16 14:17 | 2022-02-17 17:00 | 2022-02-17 15:38 | 2022-02-17 17:00 | 2022-02-17 16:57 |  |  | Attended site gained access and carried out inspection of walk in cool room and freezer due to reported temp fault. Freezer was at -19degCool room 2.0degConfirmed equipment operation and control settings. Checked BMS equipment temp logs and found no major temperature spikes. Equipment running to set point and cycling correctly to maintain set point. No fault could be identified. Work area has been left tidy.
MSA-DFES | WA5324255 | 1 | SONTEC WA PTY LTD | Reception - Access Door - Swipe Door - not working | Security | Monitoring | 981.13 | Pass | Pass | 0 | 0 | 1.3167 | 2022-04-13 13:28 | 2022-04-14 17:00 | 2022-04-14 14:11 | 2022-04-14 17:00 | 2022-04-14 15:30 |  |  | 14/4/22 - Dean SimpsonTested system and found fault with 2 Door Controller.Replaced controller and tested, all working ok.
MSA-DTWD | WA5519272 | 1 | Schindler Lifts Australia | Block A - Level 1 - Lift making unusual movement activity/noise - See notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.3167 | 2022-06-15 09:01 | 2022-06-16 17:00 | 2022-06-15 10:41 | 2022-06-16 17:00 | 2022-06-15 12:00 |  |  | Lift running on arrival All errors, 38 - unknown floor Cleaned SALSIS tape, checked SALSIS unit, returned lift to service andmonitored. Governor making knocking noise, visually checked governor, could not identify any issues
MSA-DTWD | WA5570185 | 3 | AHS Services WA Pty Ltd (Anchor) | Block A - Level 3 - A311 - pipes under sink leaking | Plumbing & Drainage | Water | 166.1075 | Fail | Fail | 11 | 11 | 1.3167 | 2022-06-28 08:07 | 2022-07-05 17:00 | 2022-09-23 10:00 | 2022-07-05 17:00 | 2022-09-23 11:19 |  |  | Arrived at mt Lawley and advised jobs at Leederville tafe.Arrived and then advised by Steve the jobs at East Perth but already completed
MSA-DCA | WA5689367 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 3 - Conservation Lab - Slow water leak from ceiling space | Plumbing & Drainage | Water | 349.54 | Pass | Pass | 0 | 0 | 1.3167 | 2022-08-02 12:22 | 2022-08-03 17:00 | 2022-08-02 13:16 | 2022-08-03 17:00 | 2022-08-02 14:35 |  |  | Investigate water leak coming through ceiling.Condesation around the hot water pipe in the ceiling causing a few drops on the floor.Advised to to leave pipe as is.No leak found but pipe is a bit rusty.
MSA-DTAG | WA5887779 | 2 | Dormakaba Australia Pty Ltd | Front revolving door - Hay St entrance - Slow, sluggish and loose panel above door | Building | Automatic Doors | 271.25 | Pass | Pass | -1 | -1 | 1.3167 | 2022-09-16 09:56 | 2022-09-21 17:00 | 2022-09-16 11:24 | 2022-09-21 17:00 | 2022-09-16 12:43 |  |  | 1002977, arrived onsite and turned revolver back to auto, found to be running slow and found problem to be the the push to slow button stuck. Repaired button and tested operation all ok, further inspection found the O rings for the encoder in bad state, had one secondhand in van and replaced it.
MSA-DCA | WA6426144 | 1 | GPS Plumbing & Gas Services PtyLtd | Exterior rear - Water coming from drain | Plumbing & Drainage | Water | 196.165 | Pass | Pass | 0 | 0 | 1.3167 | 2023-01-12 15:08 | 2023-01-13 17:00 | 2023-01-13 11:11 | 2023-01-13 17:00 | 2023-01-13 12:30
MSA-DTAG | WA6129118 | 1 | Schindler Lifts Australia | ground-Lift 4 – Next to Mazza JA chambers-lift not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.3 | 2022-10-27 11:07 | 2022-10-28 17:00 | 2022-10-27 12:50 | 2022-10-28 17:00 | 2022-10-27 14:08 |  |  | Works completed - close out at $0
MSA-DFES | WA4983978 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | The isolation tap behind change room 1 is stuck and cant be turned on/off. | Plumbing & Drainage | Water | 157 | Pass | Pass | -2 | -2 | 1.3 | 2021-12-23 15:54 | 2022-01-04 17:00 | 2021-12-24 08:42 | 2022-01-04 17:00 | 2021-12-24 10:00 |  |  | Inspected valves and isolation areas
MSA-DTAG | WA5291188 | 1 | GPS Plumbing & Gas Services PtyLtd | Male staff toilet in custody continues to re-fill and overflow | Plumbing & Drainage | Toilets/Cisterns | 230.29 | Pass | Pass | 0 | 0 | 1.3 | 2022-03-25 16:51 | 2022-03-28 17:00 | 2022-03-28 15:25 | 2022-03-28 17:00 | 2022-03-28 16:43 |  |  | Replaced faulty inlet valve
MSA-DCA | WA6559626 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Stream Generator 2 / Boiler 2 - Fail PRG and Fail Alarm | Plumbing & Drainage | Water | 447.64 | Pass | Pass | 0 | 0 | 1.3 | 2023-02-13 03:47 | 2023-02-13 17:00 | 2023-02-13 04:30 | 2023-02-13 17:00 | 2023-02-13 05:48
MSA-DCA | WA5692319 | 1 | Dormakaba Australia Pty Ltd | Office area - external roller doors -Doors are not secure and blowing in wind. Could easily be damag | Building | Automatic Doors | 351.95 | Pass | Pass | 0 | 0 | 1.3 | 2022-08-03 11:53 | 2022-08-04 17:00 | 2022-08-03 13:29 | 2022-08-04 17:00 | 2022-08-03 14:47 |  |  | Requires quote to Remanufacture guides and end stops, have advised to keep using sand bags to prevent doors from swinging in the wind until doors are repaired. See attached images.
MSA-MRWA | WA5128417 | 0 | GPS Plumbing & Gas Services PtyLtd | Female toilets lvl 1 - water dripping through light fitting in ceiling | Plumbing & Drainage | Water | 317.12 | Pass | Pass | 0 | 0 | 1.2833 | 2022-02-14 19:11 | 2022-02-14 21:11 | 2022-02-14 19:40 | 2022-02-14 23:11 | 2022-02-14 20:57 |  |  | Found leak was from leak in plant room above toilets from aircon. Checked what water feed pipes I could and all looked good. Leak seemed to be coming from inside the air con unit
MSA-MRWA | WA6088463 | 2 | Dormakaba Australia Pty Ltd | Interior double glass doors in the Tuart Room lunchroom are not opening-see notes | Building | Automatic Doors | 351.95 | Pass | Pass | -1 | -1 | 1.2833 | 2022-10-19 08:52 | 2022-10-24 17:00 | 2022-10-19 10:24 | 2022-10-24 17:00 | 2022-10-19 11:41 |  |  | Located door which had a old Dormakaba serial number 68752, inspected door and found the power supply failed. The operator is a G-U type and recommend to replace.
MSA-DCA | WA5239829 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Plant has gone into local mode and temperature issues. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 256.3975 | Pass | Pass | 0 | 0 | 1.2833 | 2022-03-16 19:37 | 2022-03-16 21:37 | 2022-03-16 20:30 | 2022-03-16 23:37 | 2022-03-16 21:47 |  |  | Recieved AH call. EQUANS manager dialed into State library to check chiller plant operation and found fire alarm had been active leading onto the temperature issue. AH call Attended Signed in and carried out inspection. Temp alarms had cleared on arrival to site. Note as plant is serving 3 large buildings it will take time for alarms to clear. Steam Gen 1 was found in alarm. Reset and confirmed operation. Confirmed no active faults on site. Confirmed chilled water supply temp currently at 7deg.
MSA-DFES | WA5367959 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Dorm 1 Bathroom - toilet cistern and stop tap all leaking and corroded | Plumbing & Drainage | Toilets/Cisterns | 197.12 | Fail | Fail | 1 | 1 | 1.2833 | 2022-04-19 10:41 | 2022-04-22 17:00 | 2022-04-26 11:17 | 2022-04-22 17:00 | 2022-04-26 12:34 |  |  | Serviced toilet cistern.
MSA-DTWD | WA5438121 | 2 | AHS Services WA Pty Ltd (Anchor) | Gym Female toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 324.515 | Pass | Pass | 0 | 0 | 1.2833 | 2022-05-16 12:38 | 2022-05-19 17:00 | 2022-05-18 10:05 | 2022-05-19 17:00 | 2022-05-18 11:22 |  |  | Completed
MSA-DCA | WA5586121 | 1 | Techworks Plumbing | Jubliee ground floor - UAT toilets - blocked | Plumbing & Drainage | Toilets/Cisterns | 239.02 | Pass | Pass | 0 | 0 | 1.2833 | 2022-07-06 10:32 | 2022-07-07 17:00 | 2022-07-06 14:30 | 2022-07-07 17:00 | 2022-07-06 15:47 |  |  | Drain blocked behind ground floor toilets in plant room. Backing up in the right hand toilet. Used drain rods to clear and then flush through with bucket loads of water.
MSA-DCA | WA5689769 | 1 | Techworks Electrical | Chicho Gelato - Ground Exterior - Left hand side door spotlight is not working - see notes below | Electrical | Lighting, External | 203.125 | Pass | Pass | 0 | 0 | 1.2833 | 2022-08-02 13:33 | 2022-08-03 17:00 | 2022-08-02 15:13 | 2022-08-03 17:00 | 2022-08-02 16:30 |  | WCAPPR | Attended site found that downright outside gelato lefthandside door was flickering Found water dripping into fitting Disconnected fitting made safe Refer to photo for light fitting details
MSA-DTAG | WA5988957 | 2 | Water2water Pty Ltd | Staff kitchen - hot/cold tap not working intermittently - see notes below | Plumbing & Drainage | HWS/Units Electric & Gas | 472.575 | Pass | Pass | 0 | 0 | 1.2833 | 2022-10-04 12:35 | 2022-10-07 17:00 | 2022-10-06 13:35 | 2022-10-07 17:00 | 2022-10-06 14:52 |  |  | Replaced tap heads and loom to solve intermittent problems.
MSA-DFES | WA6155476 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Toilet Rm# 15 - Toilet slow leak from cistern | Plumbing & Drainage | Toilets/Cisterns | 210.02 | Pass | Pass | 0 | 0 | 1.2833 | 2022-11-08 10:54 | 2022-11-11 17:00 | 2022-11-11 13:28 | 2022-11-11 17:00 | 2022-11-11 14:45 |  |  | Arrived on site and singed in went to room 15 looked at slow leaking cistern and had to replaces headseal and a Geberit outlet valve
MSA-DTWD | WA5127229 | 1 | AHS Services WA Pty Ltd (Anchor) | Kendrew- E-Block Restaurant kitchen the tap on the Pot Wash Sink has snapped off | Plumbing & Drainage | Water | 257.31 | Pass | Pass | 0 | 0 | 1.2667 | 2022-02-14 11:53 | 2022-02-15 17:00 | 2022-02-14 12:31 | 2022-02-15 17:00 | 2022-02-14 13:47 |  |  | Picked up and replaced broken sink mixer in main kitchen E block
MSA-DTWD | WA6482435 | 2 | Dormakaba Australia Pty Ltd | West entry auto door - Auto Door only opening half way | Building | Automatic Doors | 479.08 | Pass | Pass | -1 | -1 | 1.2667 | 2023-01-18 10:23 | 2023-01-23 17:00 | 2023-01-19 14:09 | 2023-01-23 17:00 | 2023-01-19 15:25
MSA-DTAG | WA5101606 | 1 | Sapio Pty Ltd | Level 9 - Court 902 - In Session Button to court is not functioning correctly - see notes below | Security | Monitoring | 370 | Pass | Pass | 0 | 0 | 1.2667 | 2022-02-03 13:14 | 2022-02-04 17:00 | 2022-02-03 13:14 | 2022-02-04 17:00 | 2022-02-03 14:30 |  |  | Attended site. Programmed macros and event triggers. Tested, all OK.
MSA-DFES | WA5563047 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Disabled toilet by SO Office - Broken mixer tap on disabled toilet sink | Plumbing & Drainage | Materials | 377.04 | Pass | Pass | 0 | 0 | 1.2667 | 2022-06-20 11:35 | 2022-06-23 17:00 | 2022-06-22 11:29 | 2022-06-23 17:00 | 2022-06-22 12:45 |  |  | Attend site to check out broken basin mixer in disable toilet near co office. Found mixer handle has broken off due to old age. This was not repairable. Supply and installed new mixer tap and long reChhandle to meet plumbing standards for disabled bathroom.
MSA-DTWD | WA5563349 | 1 | OTIS ELEVATOR COMPANY PTY LTD | Block 9 - Ground - Lift 1 - Lift not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.2667 | 2022-06-20 14:08 | 2022-06-21 17:00 | 2022-06-20 16:08 | 2022-06-21 17:00 | 2022-06-20 17:24 |  |  | DOORS/ENTRANCES - CLOSER WEIGHT/SPIRATOR - STRIPPED,CLEANED,ADJUSTED
MSA-DTWD | WA5570338 | 2 | Water2water Pty Ltd | Water cooler requires attention - caps leaking | Plumbing & Drainage | Water | 459.985 | Pass | Pass | 0 | 0 | 1.2667 | 2022-06-28 09:45 | 2022-07-01 17:00 | 2022-06-29 09:30 | 2022-07-01 17:00 | 2022-06-29 10:46 |  |  | Completed full service and sanitisation of water coolerReplaced filter and headReplaced both taps due to corrosion
MSA-DCA | WA6375668 | 1 | GPS Plumbing & Gas Services PtyLtd | Blocked sink in female bathroom, second from right, stinks of sewerage | Plumbing & Drainage | Drainage | 247.29 | Pass | Pass | 0 | 0 | 1.2667 | 2022-12-15 09:42 | 2022-12-16 17:00 | 2022-12-15 11:00 | 2022-12-16 17:00 | 2022-12-15 12:16 |  |  | Cleaned out blocked sink in female bathroom second from the right both myself and maintenance couldnt smell or see sewerage but sink was full of foreign matter not sure what as photo
MSA-DFES | WA6394018 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Gym/Laundry - Washing machine outlet spigot broken off - Requires new fitting | Electrical | General Electrical | 208.55 | Pass | Pass | 0 | 0 | 1.2667 | 2022-12-29 16:25 | 2023-01-06 17:00 | 2023-01-03 09:14 | 2023-01-06 17:00 | 2023-01-03 10:30
MSA-DTWD | WA5080891 | 1 | Dormakaba Australia Pty Ltd | E Block - Ground - Canteen main auto door - Door will not secure with key or handle | Building | Automatic Doors | 225 | Pass | Pass | 0 | 0 | 1.2667 | 2022-01-20 09:27 | 2022-01-21 17:00 | 2022-01-20 11:50 | 2022-01-21 17:00 | 2022-01-20 13:06 |  |  | 1046529. Call to site. Attend to auto door. Diagnose lock receptacle damaged at fixings. Repair as best possible. Advise long term that a locksmith is required to move lock and receptacle to undamaged part of door.
MSA-DFES | WA6257876 | 1 | Australian HVAC Services Pty. Ltd. | Plant Room - Level 3 - Power went out - Please investigate | Air Conditioning | Building HVAC Maintenance (Major Plant) | 201.88 | Pass | Pass | 0 | 0 | 1.2544 | 2022-11-25 08:33 | 2022-11-28 17:00 | 2022-11-25 12:23 | 2022-11-28 17:00 | 2022-11-25 13:38 |  |  | Attended site and signed in. Accessed bms and inspected plant after power outage. Reset faults on bms. Accessed plantroom and reset faults. Confirmed all operating correctly.
MSA-DTWD | WA4990864 | 2 | PEEL LOCK SERVICES PTY LTD | Room F6 - Damaged lock needs repair | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.25 | 2022-01-04 12:34 | 2022-01-07 17:00 | 2022-01-06 15:30 | 2022-01-07 17:00 | 2022-01-06 16:45 |  |  | job completed - repaired and replace lock
MSA-DTWD | WA4995550 | 3 | AWB Co. | A Block - AF14 Front Reception - Light switches faulty and crackling - see details below | Electrical | General Electrical | 176.1 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-10 13:49 | 2022-01-17 17:00 | 2022-01-17 09:30 | 2022-01-17 17:00 | 2022-01-17 10:45 |  |  | Attended site and signed in. Completed JSA. Located AF14 and found faulty switches on wall with a dimmer controller. Supply and replaced switches to lights. Refitted to wall. Tested all okay. Signed out, job complete
MSA-DTWD | WA5038017 | 1 | Equans Mechanical Services Australia | T Block - Level 2 (west end) - open space - High pitched whistling noise from ceiling air vent | Air Conditioning | Materials | 245.93 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-17 09:21 | 2022-01-18 17:00 | 2022-01-17 13:15 | 2022-01-18 17:00 | 2022-01-17 14:30 |  |  | Found noise to be caused but out of adjustment fresh air damper. Reset and adjusted. Checked and noise no longer present.
MSA-DTWD | WA5052423 | 3 | AWB Co. | A300 Door closer broken on Male toilet entry door | Building | Doors | 204.935 | Pass | Pass | -1 | -1 | 1.25 | 2022-01-18 08:06 | 2022-01-25 17:00 | 2022-01-21 14:00 | 2022-01-25 17:00 | 2022-01-21 15:15 |  |  | Arrived on site meet with client, he showed the to the door. I replaced the the old closer with a new one, cleaned up and left site. job complete
MSA-DTWD | WA5098749 | 2 | Water2water Pty Ltd | Wall mounted hot water urn - faulty | Plumbing & Drainage | Water | 324.4875 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-01 11:04 | 2022-02-04 17:00 | 2022-02-03 08:45 | 2022-02-04 17:00 | 2022-02-03 10:00 |  |  | Cleared internal blockage behind float valve. Replaced degraded tap.
MSA-MRWA | WA5106722 | 2 | AWB Co. | Level 2 - Room 250 - LED light in room very dim | Electrical | General Electrical | 234.875 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-07 10:53 | 2022-02-10 17:00 | 2022-02-10 08:00 | 2022-02-10 17:00 | 2022-02-10 09:15 |  |  | Attended site and signed in. Completed JSA. Located room 250. Found to be light being dull. Inspected light fitting, plug and sensor all seems to be operating fine. Will have to get programmer out to investigate further. Notified FM **job complete**
MSA-DTWD | WA5126810 | 2 | AWB Co. | Level 2 - A203a - Gallery Store - Light fitting hanging from slab | Electrical | General Electrical | 235.295 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-14 10:06 | 2022-02-17 17:00 | 2022-02-17 14:00 | 2022-02-17 17:00 | 2022-02-17 15:15 |  |  | Attended site signed in. Contacted fm about job location. X2 Lights found hanging on by cables. Isolated circuits and tagged out. Took lights apart and re fixed to concrete ceiling. Turned circuits on and tested. **job complete**
MSA-DTWD | WA5133790 | 2 | Protek 24/7 Building & Maintenance | A11 southern side of block - Window winder is seized up and windows cannot be opened | Building | Windows | 234.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-15 14:12 | 2022-02-18 17:00 | 2022-02-18 14:00 | 2022-02-18 17:00 | 2022-02-18 15:15 |  |  | Scope works & report -
MSA-DTWD | WA5187298 | 0 | AWB Co. | north block - no power | Electrical | General Electrical | 231.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-22 12:36 | 2022-02-22 14:36 | 2022-02-22 13:15 | 2022-02-22 16:36 | 2022-02-22 14:30 |  |  | Attended site and signed in. Completed JSA. Very minimal information was on job. Asked security if they knew anything about power out in north block, they didn’t know. Spoke to receptionist and he got into contact with facilities, room N202 is where the issue has been reported from. Spoke to lecturer in room N202 and she had no idea and didn’t report anything. Rang Steve and explained to him what had happened, Steve said he would make some phone calls and ring back, Steve called back ,old Steve that we will go through switchboards in N block just to make sure nothing had tripped. Checked all switchboards upstairs and downstairs, All switchboards were working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5187866 | 2 | AWB Co. | Band saw has no power | Electrical | General Electrical | 231.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-22 15:30 | 2022-02-25 17:00 | 2022-02-23 11:00 | 2022-02-25 17:00 | 2022-02-23 12:15 |  |  | Attended site and signed in. Completed JSA. Spoke to Jeffrey about the job. Went over to U block - U018. Located band saw and isolator. Found that isolator had been locked out. Went around and found lecturer. Spoke to lecturer and he said it was him that put lockout on isolator. He said it was because band saw was not working / tripped. Got lecturer to take lock off isolator. Left isolator off. Opened up contactor box on band saw. Found that thermal overload had tripped. Reset thermal overload and machine was now working. Put machine under load and there was no issues. Found lecturer again and told him the issue. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5187889 | 3 | K2 Audiovisual Pty Ltd | Lunchroom TV’s not picking up TV channels | ICT/Audiovisual | General AV works | 500 | Fail | Fail | 4 | 4 | 1.25 | 2022-02-22 15:59 | 2022-03-01 17:00 | 2022-04-01 14:00 | 2022-03-01 17:00 | 2022-04-01 15:15 |  | WCAPPR | as attached
MSA-DTWD | WA5187890 | 3 | K2 Audiovisual Pty Ltd | Lunchroom TV’s not picking up TV channels | ICT/Audiovisual | General AV works | 500 | Fail | Fail | 1 | 1 | 1.25 | 2022-02-22 16:05 | 2022-03-01 17:00 | 2022-03-10 14:00 | 2022-03-01 17:00 | 2022-03-10 15:15 |  | WCAPPR | See work updates
MSA-DFES | WA5188793 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | BAT Building - Multiple faulty lights - see notes below | Electrical | Lighting, Internal | 225.96 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-23 11:39 | 2022-03-02 17:00 | 2022-03-01 13:15 | 2022-03-02 17:00 | 2022-03-01 14:30 |  |  | Arrived on site at 1315 to replace faulty light fittings around building. Discovered and replaced 3 sets of light fitting tubes. Investigated the rest off the building for any other defected lights and did not identify any more. Completed works at 1430 and left site.
MSA-DFES | WA5190865 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Reception and stairwell - faulty lights - see notes below | Electrical | Lighting, Internal | 229.725 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-24 15:50 | 2022-03-03 17:00 | 2022-03-01 13:15 | 2022-03-03 17:00 | 2022-03-01 14:30 |  |  | Arrived on site at 1315 to replace faulty light fittings around building. Discovered and replaced 3 sets of light fitting tubes. Investigated the rest of the building for any other defected lights and did not identify any more. Completed works at 1430 and left site.
MSA-DFES | WA5202976 | 2 | Protek 24/7 Building & Maintenance | Main Administration - External Door - Western Admin - see details below | Building | General Building | 238.16 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-03 09:44 | 2022-03-09 17:00 | 2022-03-09 07:15 | 2022-03-09 17:00 | 2022-03-09 08:30 |  |  | Replace fixings
MSA-DCA | WA5209239 | 1 | Protek 24/7 Building & Maintenance | Block -roof sheet came of need replacement | Roofing | Metal Roofing | 283.75 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-09 15:48 | 2022-03-10 17:00 | 2022-03-10 11:00 | 2022-03-10 17:00 | 2022-03-10 12:15 |  |  | Reinstalled roof sheet
MSA-DTWD | WA5217080 | 2 | High Tech Pest Control | Campus Entry - Lawn Area (Assembly Area 2) - Large Bee population in & around underground pit | Pest Control | General Pest | 403.95 | Fail | Fail | 2 | 2 | 1.25 | 2022-03-11 16:17 | 2022-03-16 17:00 | 2022-03-29 11:45 | 2022-03-16 17:00 | 2022-03-29 13:00 |  |  | Bee removed from retic box by hand, transferred to another box and relocated. Job finished.
MSA-DTWD | WA5226871 | 1 | Protek 24/7 Building & Maintenance | 45 Commerce Ave - Ground - Front door - Door closer broken. Door hard to open and close. | Building | General Building | 256.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-14 14:16 | 2022-03-15 17:00 | 2022-03-15 09:30 | 2022-03-15 17:00 | 2022-03-15 10:45 |  |  | Repair door closer
MSA-DTWD | WA5231426 | 2 | AWB Co. | 145 Jull St - Ground - Jobs and Skills foyer - Flashing light | Electrical | General Electrical | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-15 11:24 | 2022-03-18 17:00 | 2022-03-16 08:45 | 2022-03-18 17:00 | 2022-03-16 10:00 |  |  | Attended site signed in completed jsa. Found flickering fluro. Removed one tube as per sites instructions and left it out. ***job completed***
MSA-DFES | WA5238515 | 2 | Protek 24/7 Building & Maintenance | Ground - BTS Store - store door out of align, requires realignment | Building | Doors | 250.75 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-16 07:15 | 2022-03-18 17:00 | 2022-03-17 11:00 | 2022-03-18 17:00 | 2022-03-17 12:15 |  |  | Adjust & repair door closer
MSA-DTWD | WA5239733 | 2 | AWB Co. | B116 - Cord operated light switch jammed | Electrical | General Electrical | 231.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-16 15:17 | 2022-03-21 17:00 | 2022-03-21 13:15 | 2022-03-21 17:00 | 2022-03-21 14:30 |  |  | Attended site and signed in. Completed jsa. Located faulty corded light switch. Spoke to fm and lecturer in area and he said that light switch had been previously bypassed. Got 12ft ladder in room and Flicked ceiling rose to always on so lights can be controlled from light switch. Tied up cords as they wanted room to have only switches for now . Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DCA | WA5257103 | 2 | Protek 24/7 Building & Maintenance | Level 4 - Great Southern Room - Door is stuck in closed position - see notes | Building | Doors | 160.625 | Pass | Pass | -1 | -1 | 1.25 | 2022-03-17 11:35 | 2022-03-22 17:00 | 2022-03-18 09:30 | 2022-03-22 17:00 | 2022-03-18 10:45 |  |  | Re secured aluminium door frame that was causing door to jam, removed door handle assembly, lubricated door striker , and handles
MSA-DTWD | WA5295223 | 3 | Milners Tree Solutions Pty Ltd | Carpark 1 - Ground - Visitors parking area - see details | Landscaping & Gardening | Tree Lopping | 1000 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-29 11:53 | 2022-04-05 17:00 | 2022-04-02 06:30 | 2022-04-05 17:00 | 2022-04-02 07:45 |  |  | removed tree and stump grinding
MSA-MRWA | WA5296606 | 2 | AWB Co. | Asphalt Lab - Wireless Access Point - No power - please investigate | Electrical | General Electrical | 158.3 | Pass | Pass | -1 | -1 | 1.25 | 2022-03-30 13:43 | 2022-04-04 17:00 | 2022-03-31 09:30 | 2022-04-04 17:00 | 2022-03-31 10:45 |  |  | Attended site and signed in, completed jsa, located wifi unit not working , set up work area and removed wifi unit from ceiling , cat 6 cable is only cable used on this device, went upstairs to office and test area and checked that all wifi routers were powered by just the cat 6 , pulled down router and tested it in other ports around site, router still didn’t work , port number on roof is 195 , called fm and he said that IT can now rectify issue as it isn’t a power issue, packed up, completed paperwork , signed out Job completed
MSA-DTWD | WA5306587 | 3 | AWB Co. | Block B - Level 2 - room B205 - Remove data cabling on floor B205 from patch panel. see notes | Electrical | General Electrical | 231.05 | Pass | Pass | -1 | -1 | 1.25 | 2022-04-06 14:55 | 2022-04-13 17:00 | 2022-04-07 10:15 | 2022-04-13 17:00 | 2022-04-07 11:30 |  |  | Attended site and signed in. Completed jsa. Located room b205. Set up ladder and pulled up all cabling. Coiled up all cables neatly and stored in roof space. Took picture. Completed paperwork. Signed out. *** Job complete ***
MSA-DTAG | WA5307455 | 0 | AWB Co. | Multiple Floors - Power outage (level 2, 3, 4 and 5) | Electrical | General Electrical | 231.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-07 13:47 | 2022-04-07 15:47 | 2022-04-07 15:30 | 2022-04-07 17:47 | 2022-04-07 16:45 |  |  | Attended site and signed in. Completed JSA. Went to blocks that had reported power out and noted down which areas of each floor were affected. Spoke to Michael and he told us what the issue was. Tested all boards for voltage on each floor. Went to basement main board room and found there was a tripped main switch (QN19). Turned main switch back on and there was no issues. Went up to every floor to check if all areas now had power. Everything now working as intended. Rang Michael and told him that we had resolved the issue and he was happy with that. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTAG | WA5308338 | 3 | Go Doors | Adjustment to Secured Doors - please see details below | Building | Security Doors | 262.5 | Pass | Pass | -1 | -1 | 1.25 | 2022-04-08 10:48 | 2022-04-19 17:00 | 2022-04-12 08:00 | 2022-04-19 17:00 | 2022-04-12 09:15 |  |  | Completed works. Please see attachments.
MSA-DTAG | WA5308571 | 1 | Midolo Building Services | Court 1 - Leak in roof above step to the witness box | Roofing | Tiled Roofing | 244.4 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-08 13:23 | 2022-04-11 17:00 | 2022-04-11 08:00 | 2022-04-11 17:00 | 2022-04-11 09:15 |  |  | repaired suspect areas - siliconed windows
MSA-DTWD | WA5311926 | 1 | Securex Security Systems & Services | J Block - Keypad not accepting code number | Security | Access Control | 250 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-11 09:56 | 2022-04-12 17:00 | 2022-04-12 08:45 | 2022-04-12 17:00 | 2022-04-12 10:00 |  |  | Removed old codes and added new codes for all tecom and ademco systems.
MSA-DTAG | WA5318309 | 3 | Midolo Building Services | Court 4 - 3 x Damaged wall panels falling off frames | Building | Internal Walls | 177.43 | Pass | Pass | -1 | -1 | 1.25 | 2022-04-12 10:12 | 2022-04-21 17:00 | 2022-04-14 08:00 | 2022-04-21 17:00 | 2022-04-14 09:15 |  |  | re attached panels
MSA-DTWD | WA5319144 | 3 | AWB Co. | Room A133- Office Door wont close properly | Building | Doors | 148.125 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-12 12:38 | 2022-04-21 17:00 | 2022-04-21 12:30 | 2022-04-21 17:00 | 2022-04-21 13:45 |  |  | arrived on site and Adjusted door
MSA-DTWD | WA5383887 | 3 | Equans Mechanical Services Australia | Room - B127 - Dust extraction fan not starting | Equipment | Building Equipment | 141.28 | Pass | Pass | -1 | -1 | 1.25 | 2022-04-28 08:05 | 2022-05-05 17:00 | 2022-04-28 14:00 | 2022-05-05 17:00 | 2022-04-28 15:15 |  |  | Found the motor over load had tripped, reset and checked the operation all OK
MSA-DTWD | WA5392865 | 3 | ECO PLUMBING AND GAS PTY LTD | E114A - Unable to turn off water to obsolete Evap system ( valve Frozen ) | Plumbing & Drainage | Drainage | 173.135 | Pass | Pass | -1 | -1 | 1.25 | 2022-05-03 13:02 | 2022-05-10 17:00 | 2022-05-05 11:00 | 2022-05-10 17:00 | 2022-05-05 12:15 |  |  | Capped off water to obsolete evap unit
MSA-DTWD | WA5395617 | 3 | Milners Tree Solutions Pty Ltd | Carpark STH - Tree branch Hanging dangerously over access road | Landscaping & Gardening | Tree Lopping | 940 | Pass | Pass | -1 | -1 | 1.25 | 2022-05-05 14:24 | 2022-05-12 17:00 | 2022-05-07 06:30 | 2022-05-12 17:00 | 2022-05-07 07:45 |  |  | large branch removed
MSA-DTWD | WA5399174 | 3 | AWB Co. | Light fails after 5 minutes | Electrical | Lighting, Internal | 163.7 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-09 16:43 | 2022-05-16 17:00 | 2022-05-16 10:15 | 2022-05-16 17:00 | 2022-05-16 11:30 |  |  | Attended site and signed in. Located w132. Found light above the lecturer desk to be faulty. Supply and replace lamp to fitting. Tested and awaited to ensure light fitting wouldn’t fail in 15 minutes again. All okay. Signed out. Job complete
MSA-DTAG | WA5460280 | 1 | Midolo Building Services | Front Foyer - Hole in ceiling - Leaking into the foyer | Roofing | Metal Roofing | 211.29 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-18 12:25 | 2022-05-19 17:00 | 2022-05-18 13:15 | 2022-05-19 17:00 | 2022-05-18 14:30 |  | WACCES | potential leak spots sealed/cleaned/repaired
MSA-DTAG | WA5460495 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 5 - Disabled Toilets opposite court 54 - Toilet Blocked | Plumbing & Drainage | Toilets/Cisterns | 154.3675 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-18 14:37 | 2022-05-23 17:00 | 2022-05-20 09:30 | 2022-05-23 17:00 | 2022-05-20 10:45 |  |  | Investigated used rod's and plunger to clear blockage all flowing well
MSA-DTWD | WA5472929 | 2 | AWB Co. | room C117 has a flickering light | Electrical | Lighting, Internal | 177.44 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-24 11:45 | 2022-05-27 17:00 | 2022-05-27 08:45 | 2022-05-27 17:00 | 2022-05-27 10:00 |  |  | Attended site and signed in, completed jsa,loacated room c117, found a few tubes that needed replacing , grabbed ladder and changed tubes, took photos, completed paperwork,signed out ***job completed**
MSA-DTAG | WA5476048 | 2 | Midolo Building Services | Cell 1 – there is a small hole in the corner of the ceiling which drips when it rains | Roofing | Metal Roofing | 186.65 | Fail | Fail | 0 | 0 | 1.25 | 2022-05-25 10:24 | 2022-05-30 17:00 | 2022-05-31 10:15 | 2022-05-30 17:00 | 2022-05-31 11:30 |  |  | resealed flashing & patched roof
MSA-DFES | WA5477624 | 2 | AWB Co. | Admin building Lecture Room 8 ceiling water leak from air con | Roofing | Metal Roofing | 271.88 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-25 15:30 | 2022-05-30 17:00 | 2022-05-30 07:15 | 2022-05-30 17:00 | 2022-05-30 08:30 |  |  | Attended and sealed around pipe work to AC unit from outside unit. Job complete
MSA-MRWA | WA5478916 | 3 | AWB Co. | Bitumen Spray shed External rear - Pump won’t remain on possible wall switch fault - see notes below | Electrical | General Electrical | 241.2625 | Pass | Pass | -1 | -1 | 1.25 | 2022-05-26 14:48 | 2022-06-02 17:00 | 2022-05-27 09:30 | 2022-06-02 17:00 | 2022-05-27 10:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located controls for oil pump at bitumen shed. Removed cover and tested all seemed to be tested. Upon further investigation found to be controlled by limit switch. Located limit switch and found to be stuck in on position due to float being stuck around brackets. Unhooked and rectified. Tested to make sure all working correctly. **job complete**
MSA-DTWD | WA5487401 | 3 | AWB Co. | ground N45 2 lights not working Priority 3 | Electrical | Lighting, Internal | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-01 14:50 | 2022-06-09 17:00 | 2022-06-08 14:45 | 2022-06-09 17:00 | 2022-06-08 16:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located room and removed all faulty tubes and starters , replaced with new, tested lights and all working as intended, put old tubes in disposal bins on site, cleaned up, packed up, completed paperwork, signed out ,all materials supplied by site ***job completed***
MSA-DTWD | WA5499837 | 2 | AHS Services WA Pty Ltd (Anchor) | A111 - client services - female toilet - broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 196.9975 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-10 14:34 | 2022-06-15 17:00 | 2022-06-14 10:15 | 2022-06-15 17:00 | 2022-06-14 11:30 |  |  | Replaced broken toilet seat, trip to supplier required
MSA-DTWD | WA5511793 | 2 | Protek 24/7 Building & Maintenance | Room G23B - Roof leak over desk to left of Sally Hackett | Roofing | Metal Roofing | 256.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-13 09:08 | 2022-06-16 17:00 | 2022-06-13 11:45 | 2022-06-16 17:00 | 2022-06-13 13:00 |  |  | Repair roof leak over Room G23B
MSA-DTWD | WA5512185 | 3 | CAPS AUSTRALIA PTY LTD | ground G09 Air compressor moisture trap solenoid is stuck open | Equipment Hire | Compressors, Generators | 1312.35 | Fail | Fail | 1 | 1 | 1.25 | 2022-06-13 12:27 | 2022-06-20 17:00 | 2022-06-29 11:00 | 2022-06-20 17:00 | 2022-06-29 12:15 |  |  | Replaced Electronic Drain. Topped Up Oil
MSA-DCA | WA5512191 | 1 | Protek 24/7 Building & Maintenance | Level 4 - Great Southern Room - Door is stuck in closed position. Urgent as emergency exit pathway | Building | Doors | 234.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-13 14:46 | 2022-06-14 17:00 | 2022-06-14 09:30 | 2022-06-14 17:00 | 2022-06-14 10:45 |  |  | Free up Bifold doors
MSA-DTWD | WA5513365 | 3 | PEEL LOCK SERVICES PTY LTD | New lock required for door to suit purple key | Security | Locksmith |  | Pass | Pass | -1 | -1 | 1.25 | 2022-06-14 09:53 | 2022-06-21 17:00 | 2022-06-15 12:30 | 2022-06-21 17:00 | 2022-06-15 13:45 |  |  | Repairs to lock
MSA-DTWD | WA5518327 | 3 | Critical Fire Protection & Training | Level 2 - Entry Foyer - Fault/Alarm on EWIS/Fire Panel | Fire Protection Services | Fire Protection - Monitor System | 117.675 | Pass | Pass | -1 | -1 | 1.25 | 2022-06-15 07:05 | 2022-06-21 17:00 | 2022-06-17 12:30 | 2022-06-21 17:00 | 2022-06-17 13:45 |  |  | Start time: 12:30pmFinish time: 1:45pmOn arrival found fire panel operating as all systems normal however audio line fault is being displayed on EWIS zone 3 upper ground. Walked throughout entire zone and found no apparent physical damage to any speakers on system. Unable to locate any as-wired diagrams for assistance to further investigate. Reset EWIS panel and fault cleared and system remained fault free before departure. If fault returns and persists potential requirement for 2 man investigate with sound production required to assist for search of line fault.
MSA-DTAG | WA5520645 | 2 | Sapio Pty Ltd | Ground Level - Court 2 - Entry door is having issues - Time lock entry mechanism not working | Security | Locksmith | 205 | Pass | Pass | -1 | -1 | 1.25 | 2022-06-15 10:01 | 2022-06-20 17:00 | 2022-06-16 06:30 | 2022-06-20 17:00 | 2022-06-16 07:45 |  |  | Replaced resistors in button, secured, all restored and working ok
MSA-DFES | WA5563168 | 3 | AWB Co. | Kitchen - Vinyl skirting in kitchen area is lifting / bubbling off | Flooring | Vinyl | 148.125 | Pass | Pass | -1 | -1 | 1.25 | 2022-06-20 12:21 | 2022-06-27 17:00 | 2022-06-22 13:15 | 2022-06-27 17:00 | 2022-06-22 14:30 |  |  | Realign skirting under sink and re-glue vinyl skirting.
MSA-DFES | WA5563484 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Recreation room / front room of the station - lighting issue - see notes below | Electrical | General Electrical | 176.325 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-20 15:08 | 2022-06-23 17:00 | 2022-06-22 11:45 | 2022-06-23 17:00 | 2022-06-22 13:00 |  |  | Arrived onsite at 11:45 to investigate light not working located crib room. Found difficulty getting into station as station is unmanned , staff arrived shortly after my arrival and let me in. Found like was not working due to faulty parts and replaced and tested. Left site at 13:00
MSA-DTWD | WA5566492 | 3 | Water2water Pty Ltd | 207 - Billi unit not working | Plumbing & Drainage | Water | 333.1675 | Pass | Pass | -1 | -1 | 1.25 | 2022-06-23 08:55 | 2022-06-30 17:00 | 2022-06-24 14:45 | 2022-06-30 17:00 | 2022-06-24 16:00 |  |  | TECH REPLACED BILLI FILTER, RETHREADED MINI-STOP & CLEARED HOT TUBE. ALL OKAY ON DEPARTURE
MSA-DCA | WA5568192 | 1 | TK Elevator Australia Pty Ltd | Lift 7 broken down again last night - displaying Out of Order, Recurring issue. | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.25 | 2022-06-25 11:02 | 2022-06-27 17:00 | 2022-06-25 11:45 | 2022-06-27 17:00 | 2022-06-25 13:00 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped on top landing. On arrival dound park key active inside car. Controller shows STElap error. Start time exceeded . Checked and found parameter for start time to be adjusted. Accel/Decel to be adjusted. Reset and switch PLC to normal . Seitched car lights and tested operation. Put unit in service.
MSA-DCA | WA5569362 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | First Floor - Katies Office - GPO fault | Electrical | General Electrical | 149.805 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-27 13:55 | 2022-06-28 17:00 | 2022-06-27 14:45 | 2022-06-28 17:00 | 2022-06-27 16:00 |  |  | Arrived onsite at 14:45 to investigate GPO not working located upstairs office. Found 1 x GPO wired completely wrong and couldn't have possibly worked. There was a working GPO back to back with it on the same wall. Wired new feed from existing GPO to get working. Tested GPO all good. Continued onsite at 16:00
MSA-DFES | WA5569522 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilet - Dripping hand basin tap | Plumbing & Drainage | Water | 168 | Pass | Pass | -1 | -1 | 1.25 | 2022-06-27 15:21 | 2022-07-04 17:00 | 2022-06-30 10:15 | 2022-07-04 17:00 | 2022-06-30 11:30 |  |  | Attended site for a leaking tap in the men’s staff toilets I have serviced the leaking tap after I have tested everything is working correctly cleaned up packed up
MSA-DTWD | WA5570183 | 2 | AWB Co. | Replace tubes not working N113, outside N206 - See notes | Electrical | General Electrical | 285.1625 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-28 08:04 | 2022-07-01 17:00 | 2022-06-30 13:15 | 2022-07-01 17:00 | 2022-06-30 14:30 |  |  | Attended site and signed in. Completed JSA. Liaised with technician about which lights need replacing. Supplied and replaced multiple fluros. Tested for corrrect operation. Packed up site. **job complete**
MSA-DCA | WA5578456 | 0 | Assa Abloy Entrance Systems Aust P/L-WA | Roller Door - is stuck open | Building | Automatic Doors | 446.99 | Fail | Fail | 0 | 0 | 1.25 | 2022-07-01 11:58 | 2022-07-01 13:58 | 2022-07-01 14:45 | 2022-07-01 15:58 | 2022-07-01 16:00 |  |  | Attended site and inspected roller door. Noted door jammed open and ballooned. Required to Un jam door and lubed guides. Ran door for a fewoperations and tested operations all OK.
MSA-DTWD | WA5679994 | 1 | Protek 24/7 Building & Maintenance | Window/roof leak on SW side of classroom | Roofing | Metal Roofing | 282.87 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-27 08:59 | 2022-07-28 17:00 | 2022-07-28 11:45 | 2022-07-28 17:00 | 2022-07-28 13:00 |  |  | Seal up windows
MSA-DTWD | WA5682300 | 2 | Protek 24/7 Building & Maintenance | BG25-Water leak above new metal folding machines | Roofing | Metal Roofing | 239.77 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-29 08:13 | 2022-08-03 17:00 | 2022-08-01 09:30 | 2022-08-03 17:00 | 2022-08-01 10:45 |  |  | Took measurements and photosBRAF Declined
MSA-DTAG | WA5687283 | 1 | Midolo Building Services | Chris Steytler Library - Leak above the window, next to the doors to the verandah | Building | Windows | 211.69 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-01 15:05 | 2022-08-02 17:00 | 2022-08-02 10:15 | 2022-08-02 17:00 | 2022-08-02 11:30 |  |  | sealed potential leak spots in gutter
MSA-DFES | WA5688176 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 – All Toilets - All toilet on Level 2 are blocked | Plumbing & Drainage | Toilets/Cisterns | 168.94 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-02 10:18 | 2022-08-02 12:18 | 2022-08-02 11:00 | 2022-08-02 14:18 | 2022-08-02 12:15 |  |  | Arrived on site and singed in went to toilets located on level 2 went to female toilets first every toilet was blocked gave it a plunge blockage disappeared went to male toilets there were no water in the traps. Flushed every toilet 6 in the female and 6 in the male toilets with paper everything was fine re Flushed and ran every basin, every was fine spoke to Deborah and suggested if happens again need to investigate with camera.
MSA-DFES | WA5689877 | 0 | AWB Co. | secure car park-light pole that is imbedded in garden bed going to fall over | Electrical | General Electrical | 266.0725 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-02 14:33 | 2022-08-02 16:33 | 2022-08-02 15:30 | 2022-08-02 18:33 | 2022-08-02 16:45 |  |  | Attended site and signed in. Completed JSA. Located pole in carpark to be wobbly. Dug out ground to check the pole bolts. And found a heap of play in the base plate to the bolts. Re tightened all bolts down onto the base plate to hold it tight. Checked and wobbled pole and all good. Showed facilities works completed. Pole is safe and not a issue anymore. Signed out. Job complete
MSA-DCA | WA5694890 | 2 | Protek 24/7 Building & Maintenance | Level 1 - Reflections Gallery - Refix loose cladding panel | Building | General Building | 274.57 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-05 14:23 | 2022-08-10 17:00 | 2022-08-08 11:45 | 2022-08-10 17:00 | 2022-08-08 13:00 |  |  | Re-fixed cladding panel
MSA-DTWD | WA5696790 | 2 | AWB Co. | Check the power supply to the foam cutting machine in L Block | Electrical | General Electrical | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-08 14:38 | 2022-08-11 17:00 | 2022-08-10 15:30 | 2022-08-11 17:00 | 2022-08-10 16:45 |  |  | NA
MSA-DTWD | WA5696818 | 2 | AWB Co. | E200-roof leaks one above machine 33 | Roofing | Metal Roofing | 262.675 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-08 14:57 | 2022-08-11 17:00 | 2022-08-11 10:15 | 2022-08-11 17:00 | 2022-08-11 11:30 |  |  | Lifted roof sheets and cleaned laps, replaced roof screws and rivets where missing and sealed sections where needed
MSA-DTWD | WA5735186 | 2 | PEEL LOCK SERVICES PTY LTD | Lock on entry door faulty | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.25 | 2022-08-16 11:36 | 2022-08-19 17:00 | 2022-08-17 10:15 | 2022-08-19 17:00 | 2022-08-17 11:30 |  |  | Job completed - Faulty Locks replaced
MSA-DCA | WA5790605 | 1 | Automatic Fire Protection (ARA) | Admin building - Level 2 - Female Toilet - Smoke detector in fault (& Isolated) – L8S18l | Fire Protection Services | Smoke and Heat Detection | 592.03 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-22 11:29 | 2022-08-23 17:00 | 2022-08-23 11:00 | 2022-08-23 17:00 | 2022-08-23 12:15 |  |  | 23/8/22 KS and DSAttend site found thermal detector isolated in staff wc. Replaced thermal. Left as normal.
MSA-DTWD | WA5790994 | 3 | AHS Services WA Pty Ltd (Anchor) | Male Toilet East End - Urinal Ground Floor A Block East is leaking all the time | Plumbing & Drainage | Toilets/Cisterns | 323.3775 | Pass | Pass | -1 | -1 | 1.25 | 2022-08-22 13:56 | 2022-08-29 17:00 | 2022-08-25 08:00 | 2022-08-29 17:00 | 2022-08-25 09:15 |  |  | .
MSA-DTWD | WA5791035 | 1 | AWB Co. | Kitchen - near reception - RCD faulty switch | Electrical | General Electrical | 183.9425 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-22 14:20 | 2022-08-23 17:00 | 2022-08-23 13:15 | 2022-08-23 17:00 | 2022-08-23 14:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, fm said that switch on gpo was arcing when sandwich press was being turned off, gpo looked old so replaced gpo, switch still arcing due to load , arcing much smaller now , showed fm and explained why it was happening, packed up, cleaned up, completed paperwork, signed out**job completed**
MSA-DCA | WA5793757 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground - C&K Bar - Leaking tap closest to the glass washer | Plumbing & Drainage | Water | 227.6025 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-24 09:52 | 2022-08-25 17:00 | 2022-08-24 11:00 | 2022-08-25 17:00 | 2022-08-24 12:15 |  |  | Ks mixer cartridge
MSA-DTAG | WA5793892 | 1 | Water2water Pty Ltd | Public Area - Drinking fountain drain is clogged - See notes below | Plumbing & Drainage | Drainage | 197.285 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-24 10:49 | 2022-08-25 17:00 | 2022-08-24 13:15 | 2022-08-25 17:00 | 2022-08-24 14:30 |  |  | Unblocked blockage from drain tubing.
MSA-DTAG | WA5836393 | 2 | AWB Co. | Coroners Court - faulty wall plug - see notes below | Electrical | General Electrical | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-07 11:47 | 2022-09-12 17:00 | 2022-09-09 12:30 | 2022-09-12 17:00 | 2022-09-09 13:45 |  |  | No data port available
MSA-DTAG | WA5971618 | 3 | Midolo Building Services | Qasi Judicial Office - Edge coming away from 2 x desks | Furniture | Office Furniture | 187.94 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-20 15:32 | 2022-09-28 17:00 | 2022-09-27 09:30 | 2022-09-28 17:00 | 2022-09-27 10:45 |  |  | DESK EDGES RE GLUED
MSA-DTAG | WA5973158 | 3 | Total Security Systems Pty Ltd | NVR has an error message “RAID degraded” please investigate - see notes below | Security | Security Management System | 315 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-21 11:08 | 2022-09-29 17:00 | 2022-09-29 10:15 | 2022-09-29 17:00 | 2022-09-29 11:30 |  |  | 29/9/2022 - Michael Higginbotham - time on site 10.15am to 11.30am - no travel time, already on site.Inspected NVR, all hard drives are healthy no failed raid alarms or faulty hard drives.
MSA-DTWD | WA5973510 | 3 | AWB Co. | T102 - Switches not operating correctly - photo followed in email | Electrical | General Electrical | 243.3725 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-21 13:54 | 2022-09-29 17:00 | 2022-09-23 12:30 | 2022-09-29 17:00 | 2022-09-23 13:45 |  |  | Attended site and signed in. Completed JSA. Located T102 and found faulty light switch faulty gpo and faulty 15a gpo. Supply and replaced with new parts. Tested all okay. Signed out. Job complete
MSA-DCA | WA5987166 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Back Carpark - External Plant room - Cooling tower GPO not working | Electrical | General Electrical | 161.205 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-03 08:46 | 2022-10-03 10:46 | 2022-10-03 09:30 | 2022-10-03 12:46 | 2022-10-03 10:45 |  |  | Arrived on site at 09:30. Went to cooling tower plant room and located effected gpos, reset and tested circuit all okay. Other contractors on site have isolated the hydro chem controller plugged into circuit as faulty solenoid has been found. No action needed as part being replaced and isolated till replaced. Left site at 10:45
MSA-DTWD | WA5987747 | 1 | Complete Pest Management Services | Child Care access driveway - Bees swarming and making a hive in small tree creating a safety hazard | Pest Control | General Pest | 247.34 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-03 14:04 | 2022-10-04 17:00 | 2022-10-04 14:00 | 2022-10-04 17:00 | 2022-10-04 15:15 |  |  | Inspected tree for feral bees found feral bees and treated.Some of the bees were trying to enter the building applied spray to stop entry.
MSA-DFES | WA5994350 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Room 30 (Engine Room) - Recharging Cable has exposing wires - See notes | Electrical | General Electrical | 594.89 | Fail | Fail | 0 | 0 | 1.25 | 2022-10-05 15:29 | 2022-10-10 17:00 | 2022-10-11 10:15 | 2022-10-10 17:00 | 2022-10-11 11:30 |  |  | Arrived on site 1015. The crew on site are from another station and did not know a about the job. The faulty plug was not left in a easy to find spot but they found the plug. Fixed up the wiring so it was correct. When looking for the faulty cable I also found another faulty plug top. Replaced the faulty plug top with new. Left site at 1130.
MSA-DFES | WA5995756 | 3 | AWB Co. | Radio Comms - Ground - Boat Shed - faulty door see notes below | Building | Doors | 171.8825 | Pass | Pass | -1 | -1 | 1.25 | 2022-10-06 16:16 | 2022-10-13 17:00 | 2022-10-07 12:30 | 2022-10-13 17:00 | 2022-10-07 13:45 |  |  | Shed entry door repairs
MSA-DTWD | WA6014580 | 1 | AWB Co. | Second Floor West Side - noisy light fitting | Electrical | Lighting, Internal | 348.5925 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-12 10:16 | 2022-10-13 17:00 | 2022-10-13 09:30 | 2022-10-13 17:00 | 2022-10-13 10:45 |  |  | Job complete
MSA-DFES | WA6050989 | 1 | Australian HVAC Services Pty. Ltd. | Level 1 - Dorm 6 - Air conditioner not working | Air Conditioning | Room Air Conditioners | 133.725 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-17 15:26 | 2022-10-18 17:00 | 2022-10-18 08:00 | 2022-10-18 17:00 | 2022-10-18 09:15 |  |  | Rhys Hall (18/10/2022) - Work NoteArrived on site signed in.On the fire station building plan dorm 6 is our simpro (dorm7 a40144154c) And fire station building plan dorm 4 is our simpro (dorm 6 a40091807l) And fire station building plan dorm 1 is our simpro (dorm 4 a40095450g) So, a bit of confusion and the firemen didn't know about the call.I ran all 3 units up on full heating and full cooling for 20-30mins each and ran tests.After getting all the temperatures and everything running fine, I didn't see any problems with the units.I believe the firemen must have had a shift change as no one knew anything about any problems.I let them know I ran tests and couldn't see any issues and if anything happens with the units to give us a call.All seemed to be working well.A40095450g Heating supply - 41°c - return 19°cCooling supply - 10.2°c - return 20°c A40091807lHeating supply - 47°c - return 28°c Cooling supply - 8.2°c- return 19°cA40144154cHeating su
MSA-DTWD | WA6127004 | 3 | Haz-Ed Services | Fault with ladder secure point below access point | Roofing | Roof Safety Systems | 300 | Fail | Fail | 0 | 0 | 1.25 | 2022-10-25 16:04 | 2022-11-01 17:00 | 2022-11-03 08:45 | 2022-11-01 17:00 | 2022-11-03 10:00 |  |  | Works completed 03/11/22
MSA-DTAG | WA6128180 | 2 | GPS Plumbing & Gas Services PtyLtd | Upstairs -1 - Male toilets - The flusher button on the wall is broken, its now on the floor | Plumbing & Drainage | Toilets/Cisterns | 176.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-26 12:52 | 2022-10-31 17:00 | 2022-10-31 14:20 | 2022-10-31 17:00 | 2022-10-31 15:35 |  |  | Reattached toilet button back, replaced inlet valve and outlet washer
MSA-DFES | WA6148028 | 2 | Dom's Total Grounds Maintenance | Ground - Visitor Car Park - Leaking retic adjacent to visitor bays 162 and 163 | Landscaping & Gardening | Grounds Maintenance | 230.5 | Fail | Fail | 0 | 0 | 1.25 | 2022-11-03 11:48 | 2022-11-08 17:00 | 2022-11-10 09:05 | 2022-11-08 17:00 | 2022-11-10 10:20 |  |  | Works completed 10/11/22
MSA-DTWD | WA6148103 | 3 | AWB Co. | J100 work shop - faulty ceiling fan switch | Electrical | General Electrical | 313.24 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-03 12:18 | 2022-11-10 17:00 | 2022-11-09 06:30 | 2022-11-10 17:00 | 2022-11-09 07:45 |  |  | Attended site and signed in. Completed JSA. Located faulty light switch for fan. Went to wholesaler for part. Returned to site. Isolated circuit. Installed new light switch and dimmer. Re energised. Tested. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DFES | WA6148763 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | ground - Radio Comms Male Toilet-urinal will not stop flushing | Plumbing & Drainage | Toilets/Cisterns | 240.87 | Pass | Pass | -1 | -1 | 1.25 | 2022-11-04 08:57 | 2022-11-09 17:00 | 2022-11-04 10:15 | 2022-11-09 17:00 | 2022-11-04 11:30 |  |  | Cistern no longer leaking.
MSA-DTWD | WA6155890 | 3 | AWB Co. | Passage / Landing - Evacuation sign light damaged - see note | Electrical | Emergency & Exit Lighting | 259.6175 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-08 14:42 | 2022-11-15 17:00 | 2022-11-14 10:15 | 2022-11-15 17:00 | 2022-11-14 11:30 |  |  | Attended site signed in jsa completed. Found exit with no blade detached. Drilled two new pin holes and attached back to exit. Plugged in and operationalJob completed
MSA-DTWD | WA6184785 | 2 | AWB Co. | Freight entry roller door - Roller door switch to be repaired | Electrical | General Electrical | 248.63 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-15 16:01 | 2022-11-18 17:00 | 2022-11-18 08:45 | 2022-11-18 17:00 | 2022-11-18 10:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Went to u block and asked lecturer to show us what issue was with roller door. Active cable was hanging out the side of the control box. De energised roller door control box. Put active cable back in box and tightened up all 4 screws. Took pics. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6190635 | 0 | ACTION GLASS & ALUMINIUM | west side of building from down steps-window smashed | Glazing | Window Glass | 329.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-16 09:28 | 2022-11-16 11:28 | 2022-11-16 11:25 | 2022-11-16 13:28 | 2022-11-16 12:40 |  |  | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-392 X 655PLUS SILICONE & 2.1 L/M OF PUTTY USED
MSA-DTWD | WA6298739 | 2 | AWB Co. | Faulty Power point in B107 | Electrical | General Electrical | 183.9425 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-01 12:45 | 2022-12-06 17:00 | 2022-12-05 08:00 | 2022-12-06 17:00 | 2022-12-05 09:15 |  |  | Spoke with technician in room and he identified faulty gpo, switch was damaged, isolated circuit, removed old gpo and replaced with new, re energised circuit, tested gpo and working as intended, labelled gpo accordingly. Job complete
MSA-DCA | WA6300143 | 0 | TK Elevator Australia Pty Ltd | lift is stuck on ground floor | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1.25 | 2022-12-02 09:11 | 2022-12-02 11:11 | 2022-12-02 12:30 | 2022-12-02 13:11 | 2022-12-02 13:45 |  |  | Lift1 PICA-Elevator > MRL > Gearless :Lift below floor level, tripped bottom limit.Drove lift up, checked wires on main board for floor level, checked battery voltage and checked floor level indicator. Person on site informed me that they found the lift like thatin the morning.Tested operation of lift multiple times couldn't reproduce fault. Returned unit to service.To be closed out at $0 cost
MSA-DTAG | WA6361459 | 2 | Midolo Building Services | Ground - Court 1 Custody - Air lock door into court hinges are damaged - see notes | Building | Doors | 188.32 | Pass | Pass | -1 | -1 | 1.25 | 2022-12-08 10:05 | 2022-12-13 17:00 | 2022-12-09 07:15 | 2022-12-13 17:00 | 2022-12-09 08:30 |  |  | HINGE REPAIRS & DOOR ADJUSTMENT COMPLETED
MSA-DTAG | WA6365857 | 2 | GPS Plumbing & Gas Services PtyLtd | 1987-Sheriff's office-Urinal in men’s toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 298.415 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-13 12:54 | 2022-12-16 17:00 | 2022-12-15 12:30 | 2022-12-16 17:00 | 2022-12-15 13:45 |  |  | Unblocked urinal to male toilet in sheriff's office
MSA-DTWD | WA6366013 | 1 | AWB Co. | Wall lights to expo are flashing | Electrical | Lighting, Internal | 271.38 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-13 14:03 | 2022-12-14 17:00 | 2022-12-13 14:45 | 2022-12-14 17:00 | 2022-12-13 16:00 |  |  | Arrived on site, signed in, completed jsa, located faulty light, removed old light for reference when buying new light. Went to pro lamp to buy 2 new lamps as lamps were non standard , returned to site, installed new lights, tested and all working, signed out, completed paper work. ***job complete***
MSA-DTWD | WA6373502 | 2 | Protek 24/7 Building & Maintenance | Room 3E - 10 store room - Hinges damaged on door. | Building | Doors | 160.695 | Pass | Pass | -1 | -1 | 1.25 | 2022-12-14 14:37 | 2022-12-19 17:00 | 2022-12-15 13:15 | 2022-12-19 17:00 | 2022-12-15 14:30 |  |  | Re aligned top hinge and placed timber shims in the screw holes to help the screws stay in place.
MSA-DTAG | WA6377224 | 3 | Midolo Building Services | Ground - Mens toilet - 2nd cubicle missing toilet roll holder | Building | Internal Walls | 298.69 | Fail | Fail | 7 | 7 | 1.25 | 2022-12-16 12:02 | 2022-12-23 17:00 | 2023-02-13 08:45 | 2022-12-23 17:00 | 2023-02-13 10:00 |  |  | new toilet roll holders installed
MSA-MRWA | WA6394195 | 2 | Schindler Lifts Australia | Level 9 - Lift 3 - not operating | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1.25 | 2022-12-30 09:07 | 2023-01-05 17:00 | 2022-12-30 12:30 | 2023-01-05 17:00 | 2022-12-30 13:45
MSA-DCA | WA6402383 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Main Theatre - 3 x GPO have come away from the wall - see notes below | Electrical | General Electrical | 262.8425 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-05 10:33 | 2023-01-10 17:00 | 2023-01-09 08:00 | 2023-01-10 17:00 | 2023-01-09 09:15
MSA-DFES | WA6403758 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Dorm 1 - Toilet in dorm 1 is running non stop | Plumbing & Drainage | Toilets/Cisterns | 282.69 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-06 15:09 | 2023-01-11 17:00 | 2023-01-10 13:15 | 2023-01-11 17:00 | 2023-01-10 14:30
MSA-DTAG | WA6414959 | 2 | Midolo Building Services | Ground - Court of Appeal Office - Loose Fittings | Building | General Building | 160.6 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-11 11:11 | 2023-01-16 17:00 | 2023-01-13 11:00 | 2023-01-16 17:00 | 2023-01-13 12:15
MSA-DCA | WA6467813 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Exterior Ramp - Two ramp lights faulty | Electrical | Lighting, External | 299.1425 | Pass | Pass | -1 | -1 | 1.25 | 2023-01-17 16:35 | 2023-01-24 17:00 | 2023-01-20 08:45 | 2023-01-24 17:00 | 2023-01-20 10:00
MSA-DCA | WA6482391 | 3 | Protek 24/7 Building & Maintenance | Office 2- Blind has fallen down see notes | Building | Curtains & Blinds | 239.82 | Pass | Pass | -1 | -1 | 1.25 | 2023-01-18 09:49 | 2023-01-25 17:00 | 2023-01-19 11:45 | 2023-01-25 17:00 | 2023-01-19 13:00
MSA-DFES | WA6517932 | 1 | Protek 24/7 Building & Maintenance | commissioners door second floor-not locking after it closes could be the lock | Building | Doors | 166.97 | Fail | Fail | 1 | 1 | 1.25 | 2023-01-24 14:30 | 2023-01-25 17:00 | 2023-01-30 10:15 | 2023-01-25 17:00 | 2023-01-30 11:30
MSA-DFES | WA6518642 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Charger for 1st LT pulled out of roof. Will require a scissor lift. | Electrical | Distribution Board | 297.445 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-25 10:14 | 2023-01-25 12:14 | 2023-01-25 11:45 | 2023-01-25 14:14 | 2023-01-25 13:00
MSA-DTAG | WA6518933 | 3 | AWB Co. | ground - listings area-Fault description Emergency Light 102 Replace driver (missing) | Electrical | Lighting, Internal | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-25 11:40 | 2023-02-02 17:00 | 2023-02-02 11:45 | 2023-02-02 17:00 | 2023-02-02 13:00
MSA-DTWD | WA6521434 | 2 | AWB Co. | Carpet tile lifting near first row of chairs RH side when entering room | Flooring | Carpet | 198.075 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-30 10:52 | 2023-02-02 17:00 | 2023-02-02 12:30 | 2023-02-02 17:00 | 2023-02-02 13:45
MSA-DTWD | WA6528939 | 3 | AWB Co. | Aberdeen St Driveway to Garage - "No Parking" lines faded and unreadable on drive way to Garage | Signage | General Signage | 756.82 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-02 13:05 | 2023-02-09 17:00 | 2023-02-06 10:15 | 2023-02-09 17:00 | 2023-02-06 11:30
MSA-DTWD | WA6531728 | 1 | AWB Co. | Disabled unisex toilet, light switch button pushed through base plate | Electrical | General Electrical | 279.68 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-03 15:17 | 2023-02-06 17:00 | 2023-02-06 09:30 | 2023-02-06 17:00 | 2023-02-06 10:45
MSA-DTWD | WA6539106 | 2 | M Construction (WA) | door broken - top hinge has broken | Building | Doors | 169.47 | Fail | Fail | 0 | 0 | 1.25 | 2023-02-08 10:35 | 2023-02-13 17:00 | 2023-02-15 11:45 | 2023-02-13 17:00 | 2023-02-15 13:00
MSA-DTWD | WA6578526 | 2 | AWB Co. | Router Plug - Faulty | Electrical | General Electrical | 245.88 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-15 10:14 | 2023-02-20 17:00 | 2023-02-17 09:30 | 2023-02-20 17:00 | 2023-02-17 10:45
MSA-DTWD | WA6655042 | 2 | Equans Mechanical Services Australia | Creche - toddlers room -not getting cold water, CW valve 100% open but passing 27 degrees | Air Conditioning | Ducted Split System | 152.0325 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-21 10:13 | 2023-02-24 17:00 | 2023-02-22 10:15 | 2023-02-24 17:00 | 2023-02-22 11:30
MSA-MRWA | WA6681405 | 1 | Automatic Fire Protection (ARA) | server room - vesda panel in alarm-please reset and investigate | Fire Protection Services | Fire Protection - Monitor System | 305.55 | Pass | Pass | 0 | 0 | 1.25 | 2023-03-02 08:33 | 2023-03-03 17:00 | 2023-03-02 11:45 | 2023-03-03 17:00 | 2023-03-02 13:00
MSA-DCA | WA6688514 | 3 | GPS Plumbing & Gas Services PtyLtd | Cistern running constantly & toilet seat loose | Plumbing & Drainage | Toilets/Cisterns | 303.9025 | Pass | Pass | -1 | -1 | 1.25 | 2023-03-07 15:54 | 2023-03-14 17:00 | 2023-03-08 14:00 | 2023-03-14 17:00 | 2023-03-08 15:15
MSA-DFES | WA6707914 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | FF Toilet - Drain in vanity leaking- swelling and mould growing | Plumbing & Drainage | Water | 186.32 | Pass | Pass | 0 | 0 | 1.25 | 2023-03-13 10:16 | 2023-03-16 17:00 | 2023-03-14 14:00 | 2023-03-16 17:00 | 2023-03-14 15:15
MSA-DFES | WA5487764 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen - sink - blocked | Plumbing & Drainage | Drainage | 351.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-02 08:29 | 2022-06-03 17:00 | 2022-06-02 09:46 | 2022-06-03 17:00 | 2022-06-02 11:01 |  |  | Plunge sink, use mo flow. Did more investigating and noticed that new airrmittens valve had to be replaced. Had to go Reece and pick up
MSA-DFES | WA4983411 | 3 | AWB Co. | Outside rear of engine room - hose drums faulty | Building | Materials | 148.125 | Pass | Pass | 0 | 0 | 1.25 | 2021-12-23 09:22 | 2022-01-04 17:00 | 2022-01-04 12:45 | 2022-01-04 17:00 | 2022-01-04 14:00 |  |  | Inspect damaged hose reel**BRAF submitted, declined**
MSA-DCA | WA4986169 | 2 | Automatic Fire Protection (ARA) | Fire Speaker fallen down | Fire Protection Services | Fire Protection - Monitor System | 169.975 | Pass | Pass | 0 | 0 | 1.25 | 2021-12-31 10:48 | 2022-01-06 17:00 | 2022-01-04 12:15 | 2022-01-06 17:00 | 2022-01-04 13:30 |  |  | On arrival, speaker cover had fallen off and speaker was hanging down. Put speaker back in ceiling above cover and reaffixed cover to ceiling.
MSA-DTWD | WA4990858 | 2 | PEEL LOCK SERVICES PTY LTD | Room F1 - Damaged lock needs repair | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1.25 | 2022-01-04 12:29 | 2022-01-07 17:00 | 2022-01-07 08:15 | 2022-01-07 17:00 | 2022-01-07 09:30 |  |  | Job completed - replaced lock
MSA-DFES | WA4990947 | 3 | AWB Co. | Investigate a possible water leak in the gymnasium, rectify & repair the dam | Building | Internal Walls | 280.29 | Pass | Pass | -1 | -1 | 1.25 | 2022-01-04 13:30 | 2022-01-11 17:00 | 2022-01-06 06:45 | 2022-01-11 17:00 | 2022-01-06 08:00 |  |  | Sealed sliding door bottom track
MSA-DTWD | WA4992222 | 2 | ECO PLUMBING AND GAS PTY LTD | The Whole Block - water leaking from pipe at the back - eastern side of block S - see notes below | Plumbing & Drainage | Water | 176.135 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-06 08:40 | 2022-01-11 17:00 | 2022-01-10 10:30 | 2022-01-11 17:00 | 2022-01-10 11:45 |  |  | Completed job on day ProMAP was down so unable to fill out paperwork Isolated pipework in S Block that led to a hose tap as instructed but Tafe maintenance man
MSA-DTWD | WA4993480 | 3 | AHS Services WA Pty Ltd (Anchor) | Repair button cubicle One Male B Block Ground Floor | Plumbing & Drainage | Water | 177.915 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-07 14:55 | 2022-01-14 17:00 | 2022-01-12 14:30 | 2022-01-14 17:00 | 2022-01-12 15:45 |  |  | Found cistern turned off at the wall.Turned back on and tested multiple times
MSA-DTAG | WA5018345 | 2 | High Tech Pest Control | Ground level - registry/reception area - infestation of mosquitos | Pest Control | General Pest | 282.26 | Fail | Fail | 4 | 4 | 1.25 | 2022-01-14 11:09 | 2022-01-19 17:00 | 2022-02-16 12:00 | 2022-01-19 17:00 | 2022-02-16 13:15 |  |  | Installed Mosquito Traps x 5 Completed
MSA-DTWD | WA5038160 | 1 | Equans Mechanical Services Australia | T - Block - Cafe - Air con water ponding outside the café area again on the floor | Air Conditioning | Room Air Conditioners | 245.93 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-17 10:43 | 2022-01-18 17:00 | 2022-01-17 14:30 | 2022-01-18 17:00 | 2022-01-17 15:45 |  |  | Re adjusted drain pan and lowered drain pan condensate pump for better water flow
MSA-DCA | WA5038352 | 2 | Protek 24/7 Building & Maintenance | Front door not closing or locking properly | Building | Doors | 146.605 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-17 12:30 | 2022-01-20 17:00 | 2022-01-18 09:00 | 2022-01-20 17:00 | 2022-01-18 10:15 |  |  | Serviced door latch
MSA-DTWD | WA5052987 | 3 | AWB Co. | Block 3 - Ground - heavy plant workshop - Power point on west wall (number 37) broken and won’t turn | Electrical | General Electrical | 216.8 | Pass | Pass | -1 | -1 | 1.25 | 2022-01-18 11:45 | 2022-01-25 17:00 | 2022-01-20 12:45 | 2022-01-25 17:00 | 2022-01-20 14:00 |  |  | Attended site, signed in, completed jsa, spoke to fm about job, located gpo and found that it had a faulty switch, fm asked if we could change it to a quad gpo, left site and went to wholesaler to pick up materials, returned to site, set up work area, isolated power circuit, removed old gpo and replaced it with new , re energised circuit and tested gpo, all working as intended, put label on gpo, cleaned up , packed up, completed paperwork, signed out ***job completed***
MSA-DTAG | WA5069131 | 2 | Midolo Building Services | Level 11 - Chambers 11.7 - Chambers door closer needs adjusting | Building | Doors | 180.92 | Pass | Pass | -1 | -1 | 1.25 | 2022-01-19 15:25 | 2022-01-24 17:00 | 2022-01-20 13:00 | 2022-01-24 17:00 | 2022-01-20 14:15 |  |  | door closer repaired & adjustments made
MSA-DTWD | WA5080607 | 3 | AWB Co. | Light out not working | Electrical | Lighting, Internal | 231.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-20 07:58 | 2022-01-27 17:00 | 2022-01-27 09:00 | 2022-01-27 17:00 | 2022-01-27 10:15 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B52 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box located in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DTAG | WA5085550 | 1 | Sapio Pty Ltd | Ground - Security - see details below | Security | CCTV Surveillance | 190 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-21 08:38 | 2022-01-24 17:00 | 2022-01-21 13:30 | 2022-01-24 17:00 | 2022-01-21 14:45 |  |  | Found that the keyswitch logic blocks and doors hD dropped offline. Tested them now they are back online and all are working.
MSA-DCA | WA5087099 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | please attend and check the power for the museum after the water leak | Electrical | General Electrical | 149.805 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-23 18:49 | 2022-01-24 17:00 | 2022-01-24 07:00 | 2022-01-24 17:00 | 2022-01-24 08:15 |  |  | Arrived on site 0700, located Socket outlets that had tripped due to water coming in contact with leads connected, were protected by a RCD inbuilt Socket outlet on the first floor. Reset the RCD and power was restored to the outlets. Check DB1 and DB2 for tripped RCDs in case we had missed any but all was okay. Left site at 0815.
MSA-DTWD | WA5087642 | 2 | AWB Co. | Reaffix whteboards loose in S105 | Building | Internal Walls | 157.125 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-24 11:29 | 2022-01-28 17:00 | 2022-01-27 09:45 | 2022-01-28 17:00 | 2022-01-27 11:00 |  |  | Attended site, filled out JSA, drove to Bunnings to pick up white caps for screws.Attended back to site and installed whiteboard.
MSA-DTWD | WA5087646 | 2 | AWB Co. | Reaffix whteboards loose in S107 | Building | Internal Walls | 162.585 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-24 11:34 | 2022-01-28 17:00 | 2022-01-27 08:30 | 2022-01-28 17:00 | 2022-01-27 09:45 |  |  | Attended site, filled out JSA, met Steve on site and carried whiteboards from C block to S block and discussed the location he wanted both boards installed on the wall.
MSA-DTAG | WA5090406 | 1 | Midolo Building Services | Doors - Leading to Court 1 - sticking and not closing properly | Building | Doors | 185.02 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-25 11:48 | 2022-01-27 17:00 | 2022-01-27 07:00 | 2022-01-27 17:00 | 2022-01-27 08:15 |  | WCAPPR | ADJUSTMENTS MADE TO DOORS & REPAIRS MADE
MSA-DTAG | WA5093477 | 0 | AWB Co. | Family Voilience room - CCTV room - water leak , please check to make | Electrical | General Electrical | 159.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-28 15:07 | 2022-01-28 17:07 | 2022-01-28 16:45 | 2022-01-28 19:07 | 2022-01-28 18:00 |  |  | Attended site, signed in, completed jsa, spoke to manager about issue and located gpo and water leak, tested gpo and it was dead, located distribution board, found that r5 on the essential power was tripped and powered that circuit, circuit would have tripped due to water causing short circuit, tested circuit to see if there was a fault, no fault found , reisolated circuit and placed out of service tag on breaker to make safe until leak is rectified , gpo was the only power close to the leak , re assured manager that all circuits in area are on rcd and will trip if water gets to them (have deemed site safe), also mentioned that hvac technician should be able to re energised circuit once the leak is rectified , completed paperwork , signed out **job completed**
MSA-DFES | WA5094531 | 3 | Seme Solutions Pty Ltd | CAMERA 1 - BLANK ON SECURITY MONITOR SCREEN | Security | CCTV Surveillance | 162.5 | Pass | Pass | -1 | -1 | 1.25 | 2022-01-31 11:53 | 2022-02-07 17:00 | 2022-02-03 13:30 | 2022-02-07 17:00 | 2022-02-03 14:45 |  |  | Camera 1 was offline, after investigation found PoE switch where camera is connect to on equipment room, rest the switch and camera came back online. All tests ok. Had to also reset workstations around the premises to have it back online.
MSA-DTWD | WA5094933 | 2 | AWB Co. | E Block - Ground - E612 - Hand towel dispenser broken in Ladies toilet , needs to be replaced | Building | General Building | 148.125 | Pass | Pass | 0 | 0 | 1.25 | 2022-01-31 16:39 | 2022-02-03 17:00 | 2022-02-03 07:00 | 2022-02-03 17:00 | 2022-02-03 08:15 |  |  | Remove old hand towel dispenser and install new dispenser supplied by site
MSA-DTWD | WA5098267 | 2 | AWB Co. | S block - Level 1 - Corridor - reset power to water cooler S block corridor | Electrical | General Electrical | 234.875 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-01 08:06 | 2022-02-04 17:00 | 2022-02-04 14:30 | 2022-02-04 17:00 | 2022-02-04 15:45 |  |  | Attended the site and sighed in. Located faulty powerpoint. Searched electrical switchboard for the trip circuit. Found a RCD switched GPO that has tripped reset and tested all now working. Informed site.
MSA-DFES | WA5098891 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | First floor - ICT Kitchen - lost power to the entire kitchen | Electrical | General Electrical | 281.88 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-01 12:17 | 2022-02-02 17:00 | 2022-02-01 12:45 | 2022-02-02 17:00 | 2022-02-01 14:00 |  |  | Arrived onsite at 12:45 to investigate GPOS not working located ICT kitchen. Identified circuit as W10 and found tripped RCD.Returned to kitchen and smelt burning smell coming from fridge, unplugged fridge as suspected faulty and reenergised circuit. Circuit held on as faulty appliance was removed. Found fridge element was submerged in water due to leak and caused RCD to trip. Fridge has been tagged out and recommended to replace. Explained to site maintenance coordinator what happened and left site at 14:00
MSA-DTWD | WA5100087 | 1 | Nessco Pressure Systems | Workshop - Compressed air line blown | Equipment | Compressors, Generators |  | Fail | Fail | 1 | 1 | 1.25 | 2022-02-02 10:12 | 2022-02-03 17:00 | 2022-02-09 10:00 | 2022-02-03 17:00 | 2022-02-09 11:15 |  |  | repair air leaks replaced faulty parts
MSA-DTWD | WA5100177 | 1 | Water2water Pty Ltd | Newly installed water bottle filler leaks onto floor causing slip hazard | Plumbing & Drainage | Water | 258.3475 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-02 11:28 | 2022-02-03 17:00 | 2022-02-03 10:30 | 2022-02-03 17:00 | 2022-02-03 11:45 |  |  | replaced old style faulty faucet.This was not one of the newly installed bottle fillers it was a different system SN A40323089I located Block E 210 Mechanical Fitters.
MSA-DCA | WA5105505 | 2 | SCAVENGER SUPPLIES PTY LTD | Francis street - Level - Ground - Service Lift Loading bay - see details | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 99.37 | Fail | Fail | 4 | 4 | 1.25 | 2022-02-04 11:24 | 2022-02-09 17:00 | 2022-03-09 10:45 | 2022-02-09 17:00 | 2022-03-09 12:00 |  |  | COMPLETED 09/03/2022
MSA-DFES | WA5105939 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Leaking hot water tap. Unable to turn off. | Plumbing & Drainage | Water | 473.12 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-05 08:48 | 2022-02-07 17:00 | 2022-02-05 09:15 | 2022-02-07 17:00 | 2022-02-05 10:30 |  |  | Arrived on site and singed in went to Cleaners room and had to replaces a 2 tap washer in Cleaners sink every is running fine
MSA-DTWD | WA5107107 | 3 | AWB Co. | C Block - Ground - C48 - 7 x Lights out. | Electrical | General Electrical | 250.83 | Pass | Pass | -1 | -1 | 1.25 | 2022-02-07 14:26 | 2022-02-14 17:00 | 2022-02-10 11:30 | 2022-02-14 17:00 | 2022-02-10 12:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Spoke to receptionist in C Block and she showed us what she wanted doing in salon 2. Turned all lights on to see what needed replacing. Replaced all faulty tubes and starters. Took before and after pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTAG | WA5107615 | 2 | Dom's Total Grounds Maintenance | Garden -Irrigation pipe leaking | Landscaping & Gardening | Grounds Maintenance | 207 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-08 08:06 | 2022-02-11 17:00 | 2022-02-10 06:15 | 2022-02-11 17:00 | 2022-02-10 07:30 |  |  | Retic Pipe Split
MSA-DTWD | WA5108482 | 2 | AWB Co. | 7 x lights for attention | Electrical | Lighting, Internal | 260.4 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-08 14:28 | 2022-02-11 17:00 | 2022-02-10 12:45 | 2022-02-11 17:00 | 2022-02-10 14:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located E103. Turned on lights to see which needed replacing. Set up work area. Replaced faulty tubes and starters. Found last light wasn’t working after tubes and starters were changed. De energised light. Took off cover and figured that light had been disconnected. Reconnected light. Re energised. Light is now working as intended. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DTWD | WA5110027 | 3 | Falcetta Plumbing and Gas | Block 10 - level 1 - female toilets - Cistern running continually | Air Conditioning | Room Air Conditioners | 146.05 | Pass | Pass | -1 | -1 | 1.25 | 2022-02-09 15:13 | 2022-02-16 17:00 | 2022-02-09 15:15 | 2022-02-16 17:00 | 2022-02-09 16:30 |  |  | disassembled and repaired cistern
MSA-DTWD | WA5116015 | 3 | AHS Services WA Pty Ltd (Anchor) | S210A - pump unit in this lab for drainage - blocked sink in A10a | Mechanical Services | Pumps | 154.3675 | Pass | Pass | -1 | -1 | 1.25 | 2022-02-11 10:44 | 2022-02-18 17:00 | 2022-02-14 12:00 | 2022-02-18 17:00 | 2022-02-14 13:15 |  |  | cleaned waste pump impeller.
MSA-DTWD | WA5127179 | 1 | Equans Mechanical Services Australia | FG31 - Fiberglass is blowing through the evaporative AC supply ductwork. | Air Conditioning | Evaporative Coolers | 834.58 | Fail | Fail | 1 | 1 | 1.25 | 2022-02-14 11:41 | 2022-02-15 17:00 | 2022-02-23 12:45 | 2022-02-15 17:00 | 2022-02-23 14:00 |  | WCAPPR | Temporary filter material fitted over vent to stop insulation blowing out. Works approved to repair insulation in ducting. To be carried out on next break for safe access.
MSA-DTWD | WA5127246 | 0 | BJ SYSTEMS | Ground - Block T - Controller damaged - needs new controller | Security | Keys & Access | 1405.16 | Fail | Fail | 0 | 0 | 1.25 | 2022-02-14 12:03 | 2022-02-14 14:03 | 2022-02-14 15:15 | 2022-02-14 16:03 | 2022-02-14 16:30 |  |  | Attend site as T Block had HBus module not responding. Replaced 6000 controller and reprogrammed. All tested ok
MSA-DTWD | WA5127726 | 1 | AWB Co. | Carpark (outside of A Block) - Carpark lights not working | Electrical | General Electrical | 234.875 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-14 13:52 | 2022-02-15 17:00 | 2022-02-15 07:30 | 2022-02-15 17:00 | 2022-02-15 08:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located switchboard with controls for car park lighting. Found to be nothing had tripped. Found PE cell and tested for correct operation. PE cell working correctly. Upon further investigation in board found to be timer out of sync with PE cell. Reset and tested timer. Both now working correctly. Notified relevant personal of works. **job completed**
MSA-DTAG | WA5141326 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground - Custody - Staff female toilet - leak through walls - see notes of possible location | Plumbing & Drainage | Water | 333.545 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-16 09:21 | 2022-02-17 17:00 | 2022-02-16 12:25 | 2022-02-17 17:00 | 2022-02-16 13:40 |  |  | Replaced leaking temperature pressure relief and expansion control valve to hot water unit in cleaners cupboard.
MSA-DTWD | WA5142026 | 2 | Equans Mechanical Services Australia | Damaged evap ceiling vents x 2 | Air Conditioning | Room Air Conditioners | 338.28 | Fail | Fail | 6 | 6 | 1.25 | 2022-02-16 12:57 | 2022-02-21 17:00 | 2022-04-06 14:30 | 2022-02-21 17:00 | 2022-04-06 15:45 |  |  | Picked up 2 new vent assemblies from workshop stock. Returned to site. Gained access to site. Fitted and secured 2 x new vents in ceiling. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5151141 | 0 | BJ SYSTEMS | Half the campus - Gallagher securitty system is not communicating with education security | Security | Monitoring | 118.75 | Fail | Fail | 0 | 0 | 1.25 | 2022-02-17 11:09 | 2022-02-17 13:09 | 2022-02-17 14:15 | 2022-02-17 15:09 | 2022-02-17 15:30 |  |  | Gallagher alarm zones not sending alarms to monitoring. Reset Gallagher panel and IRIS unit. All reported alarm zones are going through to Education Security
MSA-DCA | WA5163879 | 2 | Protek 24/7 Building & Maintenance | Buskers platform near AGWA – train station walkway - Loose screws - see notes | Building | Foundations | 283.75 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-18 12:50 | 2022-02-23 17:00 | 2022-02-21 10:30 | 2022-02-23 17:00 | 2022-02-21 11:45 |  |  | Screwed down all screws
MSA-DCA | WA5163907 | 0 | GPS Plumbing & Gas Services PtyLtd | Whole in the wall Cafe - pipes leaking (next to coffee machine )plumbing issue -Behind boxoffice | Plumbing & Drainage | Water | 272.3075 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-18 13:26 | 2022-02-18 15:26 | 2022-02-18 14:05 | 2022-02-18 17:26 | 2022-02-18 15:20 |  |  | Unblocked and cleared coffee machine drain line
MSA-DTWD | WA5189162 | 1 | AWB Co. | Student received minor shock from equipment connected to W19 GPO | Electrical | General Electrical | 234.875 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-23 14:58 | 2022-02-24 17:00 | 2022-02-24 14:30 | 2022-02-24 17:00 | 2022-02-24 15:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about suspected electrical shock. Located GPO in Asian kitchen. Located W19 which caused the suspected electric shock. Found 2x mixes which had been tagged out. Visual inspected cables and controls, Megger the cables and test for continuity of earth. All tested correctly. Inspected gpo visually, megger the whole of W19 circuit, tested RCD operation, fault looped the circuit all test passed. Have reported to western power. Informed FM of works done. Packed up. **job complete**Western power Ref 90445Y
MSA-DTAG | WA5190057 | 0 | Sapio Pty Ltd | Custody - 'Receiver 3 Alarm' that is active on our systems - see notes below | Security | Security Management System | 180 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-24 10:24 | 2022-02-24 12:24 | 2022-02-24 10:30 | 2022-02-24 14:24 | 2022-02-24 11:45 |  |  | Found input 1 on receiver 3 in tamper. Restored tamper and receiver 3 alarm restored.Job completed.
MSA-DFES | WA5190110 | 1 | Water2water Pty Ltd | First Floor - Zip tap unit is faulty | Plumbing & Drainage | Water | 510.4875 | Pass | Pass | 0 | 0 | 1.25 | 2022-02-24 10:56 | 2022-02-25 17:00 | 2022-02-24 14:46 | 2022-02-25 17:00 | 2022-02-24 16:01 |  |  | Replaced faulty power pcb
MSA-DTAG | WA5194948 | 3 | Midolo Building Services | Level 13 - staff corridor - Skirting corner has detached from wall | Building | Internal Walls | 217.96 | Pass | Pass | -1 | -1 | 1.25 | 2022-02-28 09:49 | 2022-03-08 17:00 | 2022-03-01 07:45 | 2022-03-08 17:00 | 2022-03-01 09:00 |  |  | skirting corner mould has been replaced
MSA-DTWD | WA5200803 | 2 | Equans Mechanical Services Australia | faulty indoor fan motor | Air Conditioning | Room Air Conditioners | 1362.83 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-02 09:15 | 2022-03-08 17:00 | 2022-03-08 14:30 | 2022-03-08 17:00 | 2022-03-08 15:45 |  |  | Found fan motor seized. Ordered and picked up new motor and blades. Returned to site and replaced failed parts. Checked operation. All ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA5201345 | 2 | SENTINEL LOCK SERVICE PTY LTD | Entry - Faulty lock to sliding auto entry door needs to be replaced. | Security | Locksmith | 465.03 | Fail | Fail | 5 | 5 | 1.25 | 2022-03-02 13:59 | 2022-03-08 17:00 | 2022-04-13 10:45 | 2022-03-08 17:00 | 2022-04-13 12:00 |  | WACCES | E BLock - Entry- locks to sliding auto entry door faulty.Locks repaired.
MSA-DFES | WA5206121 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Bathroom - Basin tap wont turn off | Plumbing & Drainage | Water | 557.31 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-07 12:34 | 2022-03-08 12:34 | 2022-03-07 13:45 | 2022-03-08 12:34 | 2022-03-07 15:00 |  |  | Attend site to check out basin tap that won’t turn off, located first bathroom down hall way on left, two basin right hand basin tap not shutting off. Isolated water to building and removed tap to find 1/4 taprubber has failed. Remove complete basin set and supply and in stall new basin set with new mini stops and flea I hoses. Tested and checked all, working correctly.
MSA-DTWD | WA5209252 | 3 | SENTINEL LOCK SERVICE PTY LTD | Faulty lock on storeroom door | Security | Locksmith | 290.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-09 16:55 | 2022-03-16 17:00 | 2022-03-16 11:50 | 2022-03-16 17:00 | 2022-03-16 13:05 |  |  | Block 14 - 3G1 - Faulty lock on storeroom - Metals Finishing Room.Lock replaced.
MSA-DTWD | WA5215591 | 2 | Protek 24/7 Building & Maintenance | Ground - Cleaners store - Sliding door hard to open and close | Building | General Building | 652.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-10 13:57 | 2022-03-15 17:00 | 2022-03-15 01:30 | 2022-03-15 17:00 | 2022-03-15 02:45 |  | WACCES | Supply & fit new sliding door wheels
MSA-DFES | WA5226395 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | RCD tripping - short circuit -(no lights ect) | Electrical | General Electrical | 192.305 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-14 08:31 | 2022-03-15 17:00 | 2022-03-14 11:15 | 2022-03-15 17:00 | 2022-03-14 12:30 |  |  | Arrived on site at 11:15. Located tripped lighting circuit L2 in db1, fault found circuit and located exhaust fan in kitchen seized from age. Replaced exhaust fan with new 250mm airflow and tested all okay. Left site at 12:30
MSA-DFES | WA5226981 | 1 | Go Doors | Engine Room - Rear door on Bay 1 is not working. | Building | Automatic Doors | 566.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-14 19:05 | 2022-03-15 17:00 | 2022-03-15 12:45 | 2022-03-15 17:00 | 2022-03-15 14:00 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5239652 | 2 | AWB Co. | Metal Fab wash room - light switch broken | Electrical | General Electrical | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-16 13:58 | 2022-03-21 17:00 | 2022-03-18 13:00 | 2022-03-21 17:00 | 2022-03-18 14:15 |  |  | Attended site signed in completed jsa. Found switch pushed in. Pushed back in and works and holds fine.***job completed***
MSA-DTWD | WA5278433 | 2 | AWB Co. | ET03 - Faulty light switch which needs to be repaired | Electrical | General Electrical | 246.575 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-18 14:48 | 2022-03-23 17:00 | 2022-03-21 09:15 | 2022-03-23 17:00 | 2022-03-21 10:30 |  |  | Attended site signed in completed jsa. Found faulty switch in et03 for lights, replaced with new one and works correctly now. ***job completed****
MSA-DFES | WA5286033 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Second floor - male toilet - last cubicle - toilets blocked | Plumbing & Drainage | Toilets/Cisterns | 163.6 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-21 11:59 | 2022-03-22 17:00 | 2022-03-21 14:30 | 2022-03-22 17:00 | 2022-03-21 15:45 |  |  | Had to unblock male toilet on second floor with a plunger and while I was there l had to look at the female toilets on the ground that where blocked, the blockage had passed did paper test everything is fine
MSA-DCA | WA5286264 | 2 | Protek 24/7 Building & Maintenance | External metal door - the internal side of door, bottom strip is coming away from door. Has been tem | Building | General Building | 149.625 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-21 14:04 | 2022-03-24 17:00 | 2022-03-23 07:30 | 2022-03-24 17:00 | 2022-03-23 08:45 |  |  | Re secure weather strips
MSA-DFES | WA5286820 | 0 | Anvil Doors | Front Engine Room door - pump side - not working in auto mode - will work on manual | Building | Fire Door | 527.5 | Fail | Fail | 0 | 0 | 1.25 | 2022-03-22 08:27 | 2022-03-22 10:27 | 2022-03-22 13:00 | 2022-03-22 12:27 | 2022-03-22 14:15 |  |  | Attended Osborne Park Fire Station and carried out repair to front engine room door (pump side) door was not operating in Logic mode. Carried out repair to CB6 limit switched. P{lease see attached signature slip and service reports.Thank you
MSA-DTAG | WA5288348 | 3 | Midolo Building Services | Level 3 - Admin office - 5 x PC holders to be attached to remaing court rooms | Building | General Building | 198.57 | Fail | Fail | 1 | 1 | 1.25 | 2022-03-23 10:12 | 2022-03-30 17:00 | 2022-04-04 07:30 | 2022-03-30 17:00 | 2022-04-04 08:45 |  |  | reattached pc holders
MSA-DFES | WA5288919 | 3 | Protek 24/7 Building & Maintenance | Engine Room - Change room #2 Male - door to male change room #2 is slamming shut | Building | Doors | 234.25 | Pass | Pass | -1 | -1 | 1.25 | 2022-03-23 15:44 | 2022-03-30 17:00 | 2022-03-24 10:30 | 2022-03-30 17:00 | 2022-03-24 11:45 |  |  | Adjust door closer
MSA-DFES | WA5289856 | 0 | SONTEC WA PTY LTD | Security Door - leading to court yard - not closing not working | Security | Access Control | 981.13 | Fail | Fail | 0 | 0 | 1.25 | 2022-03-24 13:17 | 2022-03-24 15:17 | 2022-03-25 09:00 | 2022-03-24 17:17 | 2022-03-25 10:15 |  |  | 25/3/22 - Dean SimpsonReplaced Pacom 2 Door controller.Tested, all working correctly.
MSA-DTAG | WA5294095 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Ground & Level 1 - see notes for locations - BIO-HAZARD DEEP CLEAN - Covid close contact | Cleaning | Cleaning | 300 | Fail | Fail | 2 | 2 | 1.25 | 2022-03-28 12:51 | 2022-03-29 17:00 | 2022-04-15 18:00 | 2022-03-29 17:00 | 2022-04-15 19:15 |  |  | Please this not this is resubmission
MSA-DCA | WA5294177 | 2 | Protek 24/7 Building & Maintenance | Ground floor - Ladies toilet - door is binding on floor - very hard to open | Building | Doors | 247.45 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-28 13:39 | 2022-03-31 17:00 | 2022-03-31 13:30 | 2022-03-31 17:00 | 2022-03-31 14:45 |  |  | Repair Ladies Toilet Door
MSA-DTAG | WA5297563 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Staff toilet - Female staff toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 154.3675 | Fail | Fail | 6 | 6 | 1.25 | 2022-03-31 11:19 | 2022-04-01 17:00 | 2022-05-10 15:00 | 2022-04-01 17:00 | 2022-05-10 16:15 |  |  | Adjusted flush buttons in toilet
MSA-MRWA | WA5297580 | 1 | Dormakaba Australia Pty Ltd | Garage Door - Garage Door not responding to remote - | Building | General Building | 499.75 | Pass | Pass | 0 | 0 | 1.25 | 2022-03-31 11:29 | 2022-04-01 17:00 | 2022-03-31 12:34 | 2022-04-01 17:00 | 2022-03-31 13:49 |  |  | Tested door found the safety beam not working. Replaced beam and tested. All good.
MSA-DTWD | WA5304126 | 2 | AWB Co. | Block 9 - Ground Floor - Ladies toilet - Broken light | Electrical | General Electrical | 333.875 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-04 14:57 | 2022-04-07 17:00 | 2022-04-05 11:30 | 2022-04-07 17:00 | 2022-04-05 12:45 |  |  | attended site signed in completed jsa. Found faulty light as reported by site FM. Located toilet block. Replaced with new 4ft led fluro. Tested ok*** job completed ***
MSA-DFES | WA5308387 | 3 | Protek 24/7 Building & Maintenance | Applied Training Ground - Briefing Room Transportable - Door is sticking badly and difficult to ope | Building | General Building | 138.625 | Pass | Pass | -2 | -2 | 1.25 | 2022-04-08 11:18 | 2022-04-19 17:00 | 2022-04-08 13:30 | 2022-04-19 17:00 | 2022-04-08 14:45 |  |  | Repair Sticking Door
MSA-DTWD | WA5318137 | 3 | AWB Co. | Room E203 - Lights not working | Electrical | Lighting, Internal | 258.57 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-12 08:42 | 2022-04-21 17:00 | 2022-04-21 07:00 | 2022-04-21 17:00 | 2022-04-21 08:15 |  |  | Attended site and signed in, completed jsa,spoke with security and got keys, located room with faulty lights , set up work area, removed old tubes and starters , replaced with new, disposed of tubes and starters in allocated bin, wiped down diffusers , tested lights and working as intended , cleaned up , packed up, completed paperwork, signed out ***job completed**
MSA-DTWD | WA5323506 | 1 | AWB Co. | A263 - Disabled toilet - Lights not working | Electrical | General Electrical | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-13 08:43 | 2022-04-14 17:00 | 2022-04-14 15:00 | 2022-04-14 17:00 | 2022-04-14 16:15 |  |  | Attended site and signed in, completed jsa, got keys from student services, located toilet with faulty light , turned all switches on , went to all surrounding switch boards and found breaker tripped , reset breaker and lights now working , took photos , completed paperwork, returned keys to student services, signed out, Job completed
MSA-DTWD | WA5323714 | 3 | AWB Co. | CF11 - Lights not working - see details below | Building | General Building | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-13 10:29 | 2022-04-22 17:00 | 2022-04-20 10:00 | 2022-04-22 17:00 | 2022-04-20 11:15 |  |  | Attended site signed in completed jsa. Spoke with Nick site fm about job. 4 faulty tubes in two lights. Replaced with tubes from site. Covers were stuck as salt in room. Removed covers to make easy for next time and put back up. *** job completed ***
MSA-DTWD | WA5379752 | 3 | AHS Services WA Pty Ltd (Anchor) | Hot water Tap opposite A304 A Block needs repairing - Female Toilet | Plumbing & Drainage | Water | 156.8675 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-21 14:07 | 2022-04-29 17:00 | 2022-04-28 14:15 | 2022-04-29 17:00 | 2022-04-28 15:30 |  |  | Replaced hot and cold tap washers to right hand side basin
MSA-DTWD | WA5380658 | 3 | AWB Co. | D04 - Light requires tombstone and light switch that controls the light is faulty | Electrical | General Electrical | 196.62 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-22 14:42 | 2022-05-02 17:00 | 2022-05-02 10:00 | 2022-05-02 17:00 | 2022-05-02 11:15 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located light switch and light needing repair, isolated circuits, removed old switch and replaced with new, replaced tombstones ,tubes and starters, re energised circuit, tested lights and all working as intended, cleaned up, packed up, completed paperwork, signed out Job completed
MSA-DTAG | WA5383002 | 3 | AWB Co. | Magistrate Hogan’s Chambers - has faulty on/off button, RHS wall powerpoint opposite his desk | Electrical | General Electrical | 184.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-27 10:48 | 2022-05-04 17:00 | 2022-05-03 07:00 | 2022-05-04 17:00 | 2022-05-03 08:15 |  |  | Attended site and signed in, completed jsa, spoke with security about job,located PowerPoint with faulty switch , identified and isolated circuit, removed old gpo, replaced with new, re energised circuit and tested, gpo working as intended , packed up, cleaned up, completed paperwork, signed out***job completed***
MSA-DTWD | WA5384286 | 2 | AWB Co. | A-Block room A217 has a water leak above lecturers window | Plumbing & Drainage | Water | 251.25 | Pass | Pass | -1 | -1 | 1.25 | 2022-04-28 11:31 | 2022-05-03 17:00 | 2022-04-29 11:30 | 2022-05-03 17:00 | 2022-04-29 12:45 |  |  | Investigate roof leak.cant access as solar panels in the way .will need braf to remove panels
MSA-DTWD | WA5386107 | 2 | AWB Co. | Light Switches are crackling - see notes below | Electrical | General Electrical | 273.195 | Pass | Pass | 0 | 0 | 1.25 | 2022-04-29 16:39 | 2022-05-04 17:00 | 2022-05-03 11:30 | 2022-05-04 17:00 | 2022-05-03 12:45 |  |  | Attended site signed in jsa completed. Found faulty switch crackling in room, isolated power and replaced. Works well now*** job completed ***
MSA-DTAG | WA5393174 | 2 | AWB Co. | Level 3 - JSO Male Toilets - Faulty light - see notes | Electrical | Lighting, Internal | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-03 15:36 | 2022-05-06 17:00 | 2022-05-05 07:00 | 2022-05-06 17:00 | 2022-05-05 08:15 |  |  | Attended site and signed in, completed jsa,spoke with fm and he showed me the problem, grabbed tubes and starters from level 6, replaced tube and starter, test light and working as intended, packed up, completed paperwork, signed out Job completed
MSA-DTWD | WA5412976 | 3 | AWB Co. | Water Leak - E Block Light Fab - Just in front of linisher which is located outside of welding bays | Roofing | Concrete Roof Construction | 307.28 | Pass | Pass | -1 | -1 | 1.25 | 2022-05-12 08:10 | 2022-05-19 17:00 | 2022-05-12 11:30 | 2022-05-19 17:00 | 2022-05-12 12:45 |  |  | E500 roof leak in middle of workshop, found to be roof screws washers fully perished and roof sheet laps over 4 sheets in poor condition with seal. Replaced and re-sealed.
MSA-DTWD | WA5413513 | 3 | AWB Co. | A03 - Flickering Light in Client Services Midland ( Light requires tombstone ) | Electrical | General Electrical | 231.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-12 11:38 | 2022-05-19 17:00 | 2022-05-17 09:15 | 2022-05-19 17:00 | 2022-05-17 10:30 |  |  | Attended site signed in completed jsa. Located light fitting with faulty tombstone. Replaced faulty tombstones tubes and starters. Light is now working as intended. Took pictures.Job complete
MSA-DFES | WA5438792 | 3 | AWB Co. | L1 gym courtyard Paving sunk at rear of station - further information | Paving & Roadworks | Paving | 148.125 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-16 16:56 | 2022-05-23 17:00 | 2022-05-20 07:00 | 2022-05-23 17:00 | 2022-05-20 08:15 |  |  | Attended site completed jsaRemoved pavers in area packed with sand and reinstalledCleaned area Job complete
MSA-DTWD | WA5453809 | 2 | AWB Co. | J.108 - 4 x lights out | Electrical | General Electrical | 308.715 | Fail | Fail | 0 | 0 | 1.25 | 2022-05-17 10:08 | 2022-05-20 17:00 | 2022-05-23 11:30 | 2022-05-20 17:00 | 2022-05-23 12:45 |  | WCAPPR | Attended site and signed in. Completed JSA. Located area with faulty lighting. Replaced all faulty tubes and starters. Completed paperwork. Signed out. *** Job complete ***
MSA-DFES | WA5454875 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Server Room - CCTV Has a blank screen - Faulty Power box - - see notes below | Electrical | General Electrical | 149.805 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-17 15:33 | 2022-05-24 17:00 | 2022-05-23 09:00 | 2022-05-24 17:00 | 2022-05-23 10:15 |  |  | Arrived onsite at 9:00am to investigate CCTV not working located in comms room, found PSU was faulty. Circuit supplying PSU tested fine, transformer supplying alarm panel PSU was faulty. PSU is serviced by sontec and is tied in with the acess control. Sontec will need to be contacted to repair unit. Issue has been identified as transformer inside PSU. Notified staff of outcome of works and left site at 10:15
MSA-DTAG | WA5460291 | 2 | Midolo Building Services | Level 8 - Secure area/ judicial corridor - Grey discolouration around air vents – possibly mould | Equipment | Building Equipment | 112.5 | Fail | Fail | 1 | 1 | 1.25 | 2022-05-18 12:39 | 2022-05-23 17:00 | 2022-05-27 09:15 | 2022-05-23 17:00 | 2022-05-27 10:30 |  |  | dust cleaned off around air vents - not mould
MSA-DCA | WA5468422 | 2 | Earth & Water Pty Ltd | Retic leak in zone 13, please investigate | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | -1 | -1 | 1.25 | 2022-05-20 09:36 | 2022-05-25 17:00 | 2022-05-20 14:15 | 2022-05-25 17:00 | 2022-05-20 15:30 |  |  | tightened sprinkler and sprinkler head until leak stopped
MSA-DTWD | WA5469113 | 1 | Equans Mechanical Services Australia | Room D3 - Ceiling mount split system leaking water - see notes below | Air Conditioning | Ducted Split System | 184.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-20 16:15 | 2022-05-23 17:00 | 2022-05-23 08:30 | 2022-05-23 17:00 | 2022-05-23 09:45 |  |  | Found pump float switch seized due to dirt. Cleaned out part and reassembled. Checked operation and all ok.
MSA-DTWD | WA5473210 | 3 | AWB Co. | Light above sink not working | Electrical | Lighting, Internal | 302.5125 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-24 12:49 | 2022-05-31 17:00 | 2022-05-30 07:00 | 2022-05-31 17:00 | 2022-05-30 08:15 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Removed old lights fitting. Supplied and replaced with new LED 4ft batten. Tested for correct operation. All working properly. **job complete**
MSA-DTWD | WA5478217 | 1 | Falcetta Plumbing and Gas | A Block - Between A40 & A41 - Gas wall heater keeps going out | Plumbing & Drainage | Gas | 136.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-26 10:11 | 2022-05-27 17:00 | 2022-05-27 14:30 | 2022-05-27 17:00 | 2022-05-27 15:45 |  |  | restored power to gpo
MSA-DTWD | WA5479942 | 1 | AWB Co. | Room 6E - Power tripping in the area | Electrical | General Electrical | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-27 13:26 | 2022-05-30 17:00 | 2022-05-30 12:15 | 2022-05-30 17:00 | 2022-05-30 13:30 |  |  | Attended site and signed in. Completed JSA. Located area where the power was tripping. Spoke with site regarding the issue. Found power to be reset this morning by site. Tested circuit and all okay. Investigated other areas and checked all okay. Spoke with techs about why it wouldn’t reset and they were not informed that the RCD needs to go off before it goes back on. No problems found on site. Signed out. Job complete
MSA-DFES | WA5481947 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Kitchen - LED Batton light - not working | Electrical | General Electrical | 225.195 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-31 08:07 | 2022-06-01 17:00 | 2022-05-31 14:15 | 2022-06-01 17:00 | 2022-05-31 15:30 |  |  | Arrived on site located faulty light. Left site to get a new light. Replaced faulty light with new.
MSA-DTWD | WA5482000 | 2 | AWB Co. | GG01 - Power tripping out in one half of room. Reset, but needs to be checked | Electrical | General Electrical | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-31 08:19 | 2022-06-03 17:00 | 2022-06-02 07:00 | 2022-06-03 17:00 | 2022-06-02 08:15 |  |  | Attended site and signed in. Completed JSA. Located G block switchboard and Room with the power fault. Investigated r9 to be the main circuit to office. Drawing 10amps, checked out further appliances running in area. Found that the room has 2 x kettles, 1 x fridge, 2 x sandwich press, 1 x urn, 4 x computers all on the same circuit. Advised site that this is not a kitchen it’s a office and all these appliances will cause issues. Site will tell the office staff that they need to be aware what that are using and I advised that we can install a separate circuit to split some load if they are wanting too down the track. Signed out. Job complete
MSA-DTWD | WA5482645 | 2 | Milners Tree Solutions Pty Ltd | In Vicinity of I & M Blocks - Assembly Area 1 Lawn Area - Tree limb has split - failure imminent | Landscaping & Gardening | Tree Lopping | 1000 | Fail | Fail | 0 | 0 | 1.25 | 2022-05-31 13:46 | 2022-06-03 17:00 | 2022-06-04 12:00 | 2022-06-03 17:00 | 2022-06-04 13:15 |  |  | TREE LIMB REMOVED
MSA-DTWD | WA5482667 | 3 | AWB Co. | Room S213 - towel dispenser fallen off wall | Building | General Building | 148.125 | Pass | Pass | 0 | 0 | 1.25 | 2022-05-31 13:59 | 2022-06-08 17:00 | 2022-06-08 12:00 | 2022-06-08 17:00 | 2022-06-08 13:15 |  |  | Attended site and completed works 08/06/2022Installed towel dispenserCompleted job.
MSA-DTWD | WA5487328 | 1 | SENTINEL LOCK SERVICE PTY LTD | Key pad wont un lock | Security | Locksmith | 150.96 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-01 14:13 | 2022-06-02 17:00 | 2022-06-01 14:40 | 2022-06-02 17:00 | 2022-06-01 15:55 |  |  | First aid room - key pad will not unlock.Lock repaired.
MSA-DTWD | WA5487845 | 3 | AWB Co. | N26 - 3 x lights out | Electrical | General Electrical | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-02 08:54 | 2022-06-10 17:00 | 2022-06-08 13:45 | 2022-06-10 17:00 | 2022-06-08 15:00 |  |  | Milan Barjaktar (08/06/2022) - Work NoteAttended site signed in jsa completed. Located faulty lights in n26. Fair few are faulty and burnt out tips. Will need to replace most as per sites request.need man lift for job also.Need x1 manliftx75 36w 865w tubesx75 starters s10Need two people as spotter requiredBRAF NEEDED**BRAF DECLINED** Invoice costs to date
MSA-DTAG | WA5488398 | 1 | Midolo Building Services | Children's Court + Registry to Garage - Cross over door not closing properly | Building | Doors | 187.19 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-02 12:31 | 2022-06-03 17:00 | 2022-06-03 10:30 | 2022-06-03 17:00 | 2022-06-03 11:45 |  |  | NEW FIXINGS & DOOR EASED
MSA-DTWD | WA5496177 | 2 | AWB Co. | P22 - A GPO in the student’s desk has a broken switch on it. 3rd table om the left as you enter | Electrical | General Electrical | 244.05 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-09 08:10 | 2022-06-14 17:00 | 2022-06-13 08:30 | 2022-06-14 17:00 | 2022-06-13 09:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty gpo. Replaced gpo. Tested. Working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5496496 | 0 | Critical Fire Protection & Training | Plant room detector - faulty and setting off alarm | Fire Protection Services | Fire Protection - Monitor System | 349.975 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-09 10:35 | 2022-06-09 12:35 | 2022-06-09 12:20 | 2022-06-09 14:35 | 2022-06-09 13:35 |  |  | Start time: 12:20pmFinish time: 1:35pmLocated activated detector in zone 5 in ground floor plant room in front of supply duct vent. Detector head extremely dusty and required replacing. New detector head installed and recommended to Pey-Sui to have air supply grill cleaned and dust removed as build-up is most likely cause for false alarm. Panel returned to all systems normal with zone 5 de-isolated.
MSA-DTWD | WA5497037 | 3 | AWB Co. | West Block - Level 2 - Corridor - Emergency lighting still active following RM visit | Electrical | Emergency & Exit Lighting | 158.3 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-09 13:56 | 2022-06-16 17:00 | 2022-06-14 09:15 | 2022-06-16 17:00 | 2022-06-14 10:30 |  |  | Attended site and signed in. Completed JSA. Located west wing on level 2. Found emergency lights to be operating on battery power. Reinstated fuse to circuit. And retested all on mains now. Signed out. Job complete
MSA-DTAG | WA5499292 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 13 - Ladies staff toilet - toilet seat cover has a crack - second toilet | Plumbing & Drainage | Toilets/Cisterns | 181.2075 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-10 12:19 | 2022-06-17 17:00 | 2022-06-14 15:15 | 2022-06-17 17:00 | 2022-06-14 16:30 |  |  | Replaced broken toilet seat, trip to supplier required.
MSA-DTWD | WA5499891 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 234.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-10 15:02 | 2022-06-13 17:00 | 2022-06-13 14:15 | 2022-06-13 17:00 | 2022-06-13 15:30 |  |  | ROOF LEAK REPAIRED
MSA-DFES | WA5511726 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | ground FF Bathroom and SO Bathroom Exhaust fan not working intermittently - see notes | Electrical | General Electrical | 327.555 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-13 08:04 | 2022-06-16 17:00 | 2022-06-16 14:30 | 2022-06-16 17:00 | 2022-06-16 15:45 |  |  | Located faulty exhaust fans. Found two noisy/faulty exhaust fan. Left site to get new fans. Replaced faulty exhaust fans with new.
MSA-DTWD | WA5511776 | 2 | Protek 24/7 Building & Maintenance | A11 - Roof leak over desk to left on entering room | Roofing | Metal Roofing | 333.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-13 08:53 | 2022-06-16 17:00 | 2022-06-13 13:00 | 2022-06-16 17:00 | 2022-06-13 14:15 |  |  | Repair roof leak - A11
MSA-DTWD | WA5512170 | 3 | AWB Co. | C101 - 4 x lights out | Electrical | Lighting, Internal | 231.05 | Pass | Pass | -1 | -1 | 1.25 | 2022-06-13 14:34 | 2022-06-20 17:00 | 2022-06-16 07:00 | 2022-06-20 17:00 | 2022-06-16 08:15 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located faulty light fittings, removed old tubs and replaced with new, replaced ballast , all lights working as intended ,put old tubes in allocated boxes on site , packed up, completed paperwork, signed out** job completed**
MSA-DTWD | WA5549103 | 2 | AWB Co. | GPO next to roller door needs replacement | Electrical | General Electrical | 171.9 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-17 12:55 | 2022-06-22 17:00 | 2022-06-22 10:30 | 2022-06-22 17:00 | 2022-06-22 11:45 |  |  | Attended site and signed in. Completed JSA. Located gpo in shed next to roller door. Supply and replace gpo. Tested all okay. Signed out. Job complete
MSA-MRWA | WA5549205 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Male Toilets - Leaking toilet | Plumbing & Drainage | Toilets/Cisterns | 229.8 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-17 14:31 | 2022-06-22 17:00 | 2022-06-21 09:40 | 2022-06-22 17:00 | 2022-06-21 10:55 |  |  | Repaired leaking pipe in plumbing duct L2
MSA-DCA | WA5562693 | 1 | Protek 24/7 Building & Maintenance | Ground Floor - External - Sign has come off fixings, requires new rivets to reattach | Building | General Building | 248.43 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-20 09:05 | 2022-06-21 17:00 | 2022-06-20 13:00 | 2022-06-21 17:00 | 2022-06-20 14:15 |  |  | Refix External Sign
MSA-DFES | WA5562998 | 2 | Water2water Pty Ltd | Administration Building - Ground - BRM Kitchen - please see details below | Plumbing & Drainage | Water | 618.5075 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-20 11:23 | 2022-06-23 17:00 | 2022-06-21 13:45 | 2022-06-23 17:00 | 2022-06-21 15:00 |  |  | replaced PCB board & re-calibrated. All okay on departure,
MSA-DCA | WA5563073 | 1 | Protek 24/7 Building & Maintenance | 1 off office Door fragile and wood is broken. | Building | Doors | 256.13 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-20 11:42 | 2022-06-21 17:00 | 2022-06-20 14:15 | 2022-06-21 17:00 | 2022-06-20 15:30 |  |  | Repair office door
MSA-DCA | WA5565988 | 2 | Critical Fire Protection & Training | Level 2 - Studio 1 – WAB Studio (near entrance) - Smoke detector hanging from ceiling | Fire Protection Services | Fire Protection - Monitor System | 117.675 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-22 13:21 | 2022-06-27 17:00 | 2022-06-24 13:00 | 2022-06-27 17:00 | 2022-06-24 14:15 |  |  | Start time: 1pmFinish time: 2:15pmOn arrival located reported “detector” hanging from ceiling. After locating hanging device found emergency light- spitfire hanging from roof. Re-installed EM light back into ceiling.
MSA-DTAG | WA5566165 | 1 | SONTEC WA PTY LTD | Custody to office - Door to custody control centre not closing property on its own | Building | Doors | 350 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-22 16:41 | 2022-06-23 17:00 | 2022-06-23 12:15 | 2022-06-23 17:00 | 2022-06-23 13:30 |  |  | 23/6/22 - Joshua Park, Dylan ParslowRefitted mortice lock into door and tested, all working.
MSA-DFES | WA5568269 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Light indicator - monitored mechanical and electrical faut | Electrical | Materials | 149.805 | Pass | Pass | 0 | 0 | 1.25 | 2022-06-26 10:06 | 2022-06-27 17:00 | 2022-06-27 10:45 | 2022-06-27 17:00 | 2022-06-27 12:00 |  |  | Arrived on site at 10:45 to investigate fault light indicating on monitored mechanical system. Found indicator light to be 24v wired into mechanical system. Checked both electrical and mechanical switchboards and power all okay. Advised staff to bring in mechanical contractor to check as fault light wired to their system. Left site at 12:00
MSA-DTWD | WA5585904 | 1 | BJ SYSTEMS | A-Block - room A009 - the door handle does not engage when door pad is swiped to open | Security | Security Management System | 197.72 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-06 09:12 | 2022-07-07 17:00 | 2022-07-07 09:15 | 2022-07-07 17:00 | 2022-07-07 10:30 |  |  | Attend site, signed in. Checked door, found the cam shaft for the handle on the secure side had come out of the lock, but was not damaged, adjusted the spring so it will sit securely in the shaft hole, checked lock operation, all working ok. Optimised door open programming to work better, all working ok
MSA-DFES | WA5585956 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Workshop - Male Toilets - blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 157 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-06 09:35 | 2022-07-07 17:00 | 2022-07-06 14:30 | 2022-07-07 17:00 | 2022-07-06 15:45 |  |  | Arrived on site and signed in went to male toilet and plunge the last toilet tested with paper everything is fine
MSA-DFES | WA5586098 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room ground-exhaust fan not working does not turn off | Electrical | General Electrical | 780.405 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-06 10:35 | 2022-07-11 17:00 | 2022-07-08 06:00 | 2022-07-11 17:00 | 2022-07-08 07:15 |  |  | Arrived on site at 0600 to investigate engine room exhaust not operating. Found enclosure/contactor for circuit full of water and discovered water coming from conduit of relative circuit. Contactor appeared corroded & damaged. Will need to return to site with parts AND 12FT LADDER to carry out investigation and locate source of water exposure. Left site at 0715.Mechanical door company needs to be contacted, issue is not electrical
MSA-DTWD | WA5587545 | 1 | Securex Security Systems & Services | E Block - Security Alarm panel fault - See notes below | Security | Monitoring | 280.26 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-07 09:02 | 2022-07-08 17:00 | 2022-07-07 12:45 | 2022-07-08 17:00 | 2022-07-07 14:00 |  |  | 07/07/2022, 1245-1400Reterminated zone 166 motion sensor and reset tamper.Replaced blown plug pack on DGP in Records Section.
MSA-DTWD | WA5587821 | 2 | SENTINEL LOCK SERVICE PTY LTD | Faulty door lock – the barrel of the lock is loose & keys keep getting stuck in the lock | Security | Locksmith | 230.59 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-07 10:59 | 2022-07-12 17:00 | 2022-07-12 13:10 | 2022-07-12 17:00 | 2022-07-12 14:25 |  |  | EG01 - door locks faulty.Locks repaired.
MSA-DTWD | WA5589007 | 3 | AHS Services WA Pty Ltd (Anchor) | Ground-West end Male toilets end cubicle flush button not working | Plumbing & Drainage | Toilets/Cisterns | 293.6275 | Pass | Pass | -1 | -1 | 1.25 | 2022-07-08 09:10 | 2022-07-15 17:00 | 2022-07-08 14:30 | 2022-07-15 17:00 | 2022-07-08 15:45 |  |  | Completed
MSA-DFES | WA5655982 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Cable for the valt charger is damaged | Electrical | General Electrical | 166.705 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-18 11:18 | 2022-07-21 17:00 | 2022-07-20 07:30 | 2022-07-21 17:00 | 2022-07-20 08:45 |  |  | Fixed the charger cable
MSA-DTWD | WA5670930 | 0 | BJ SYSTEMS | U & V block auto doors not working - jammed open currently - Secuirty issue | Building | Automatic Doors | 197.72 | Fail | Fail | 0 | 0 | 1.25 | 2022-07-20 08:25 | 2022-07-20 10:25 | 2022-07-20 13:45 | 2022-07-20 12:25 | 2022-07-20 15:00 |  |  | Attend site and assessed system regarding doors being stuck. System programming (Schedules) required modi?cation as doors were scheduled to be in secure mode rather than free access between 7am - 16:00. Modifications made, system has been tested and is functioning as intended
MSA-DTWD | WA5674432 | 2 | Protek 24/7 Building & Maintenance | Roof leak in center of room near air con vent | Roofing | Metal Roofing | 314.8 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-21 11:49 | 2022-07-26 17:00 | 2022-07-25 09:15 | 2022-07-26 17:00 | 2022-07-25 10:30 |  |  | Repaired and resealed pipes
MSA-DTAG | WA5676518 | 1 | AWB Co. | L1 - Roof leak shows water pooling in light fittings – disconnect light units. | Electrical | Lighting, Internal | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-25 09:08 | 2022-07-26 17:00 | 2022-07-26 09:00 | 2022-07-26 17:00 | 2022-07-26 10:15 |  |  | Attended site and signed in, completed jsa, spoke with manager of level 1 about lights with water, found room with ceiling damage and disconnected lights accordingly, disconnected light in joining office, 3 lights disconnected in total , called Ian to confirm but no answer, walked around and couldn’t see any others with water pooled, packed up, completed paperwork, signed out**job completed**
MSA-DFES | WA5676960 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | whole carpark soak wells need to be emptied and pumped | Plumbing & Drainage | Drainage | 244.96 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-25 11:39 | 2022-07-28 17:00 | 2022-07-28 10:00 | 2022-07-28 17:00 | 2022-07-28 11:15 |  |  | Arrived On site and singed in went to soakwall in car park could see damage that new soakwall have caused. Went to old existing soakwall next to damage one that needed to be suck out after inspecting soakwall all l can do is suck 200mm of water and the rest of th wall is solid sand. Spoke to one of the fire guy and he explain to me in this area where the green shed is that's where the builder left all of the rubble and sand, as you can see this is a issue where building supplies have been put and why the soakwall is full of sand, need to know if we have to clean it out or the builder.
MSA-DFES | WA5678937 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | ground floor-Lights not working Yih Pyng Lee in Intelligence Systems | Electrical | Lighting, Internal | 421.855 | Pass | Pass | -1 | -1 | 1.25 | 2022-07-26 09:37 | 2022-08-02 17:00 | 2022-07-29 11:15 | 2022-08-02 17:00 | 2022-07-29 12:30 |  |  | Arrived onsite at 11:15 to change fluoro tubes. Changed tubes and lights working, replaced 3x 14w t5 840 & 10 x 28w t5 840. Left site at 12:30
MSA-DFES | WA5680329 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Second floor - all toilets female and male - blocked/ draining issues - coming back up. | Plumbing & Drainage | Drainage | 179.94 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-27 11:26 | 2022-07-27 13:26 | 2022-07-27 12:00 | 2022-07-27 15:26 | 2022-07-27 13:15 |  |  | Inspecting the blocked toilets in male and female toilets on 2nd floor. Kept flushing them all at the same time until it didn’t clear. Tested, all drains good. Possible cause of blockage could be unflushablepapers or tampons. Have found a plastic wrap, presuming from tampon, in the toilet pan.
MSA-DTWD | WA5680693 | 3 | AWB Co. | reattached Blood Pressure Gauges fallen off wall | Building | Internal Walls | 170.3825 | Pass | Pass | -1 | -1 | 1.25 | 2022-07-27 14:39 | 2022-08-03 17:00 | 2022-07-28 09:00 | 2022-08-03 17:00 | 2022-07-28 10:15 |  |  | Reattach blood pressure gauges to wall.
MSA-DFES | WA5681436 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Air Compressor Room-exhaust fan is not able to be operated after hours | Electrical | General Electrical | 257.355 | Pass | Pass | 0 | 0 | 1.25 | 2022-07-28 11:42 | 2022-08-02 17:00 | 2022-08-02 08:15 | 2022-08-02 17:00 | 2022-08-02 09:30 |  |  | Arrived on site at 815. Located faulty exhaust fan room and switch. The override switch I was shown does not control the exhaust fan in the compressor room. I found the exhaust fan is plugged into a gpo and power to the gpo is controlled from a timer above the gpo. Showed Josh how to manually override the timer so the exhaust fan can turn on after hours. Left site at 930.
MSA-DTAG | WA5687022 | 0 | AWB Co. | Level 1 - Youth Justice - Water in light fittings near Judys desk - Please isolate and make safe | Electrical | Lighting, Internal | 259.6175 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-01 12:41 | 2022-08-01 14:41 | 2022-08-01 13:30 | 2022-08-01 16:41 | 2022-08-01 14:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. located various lights with leaks. Isolated lights and made safe for works. Notified relevant personnel. **job complete**
MSA-DTAG | WA5687325 | 1 | Midolo Building Services | Level 2 - Room 219 - Small leak coming from ceiling | Building | Ceiling | 238.59 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-01 15:55 | 2022-08-02 17:00 | 2022-08-02 09:00 | 2022-08-02 17:00 | 2022-08-02 10:15 |  |  | sealed potential leak spots to ridge capping
MSA-DTWD | WA5688133 | 2 | AWB Co. | Level 2 - Finance area -2 x ceiling Florence lights not working | Electrical | Lighting, Internal | 349.6975 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-02 10:02 | 2022-08-05 17:00 | 2022-08-03 09:00 | 2022-08-05 17:00 | 2022-08-03 10:15 |  |  | Attended site signed in jsa completed. walked around with susan to show us which lights not working. Replaced 8 tubes in T block.all working and testedJob completed
MSA-DTWD | WA5693545 | 3 | AWB Co. | Currently 5 buckets catching rain water | Roofing | Metal Roofing | 286.845 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-04 13:12 | 2022-08-11 17:00 | 2022-08-09 13:00 | 2022-08-11 17:00 | 2022-08-09 14:15 |  |  | Sourced leaks wire brushed rusted areas sealed up holes in sheets
MSA-DTAG | WA5694532 | 3 | AHS Services WA Pty Ltd (Anchor) | Female public toilets, Irwin/hay street side - toilet seat cover broken, hinge catches clothes | Plumbing & Drainage | Toilets/Cisterns | 210.9375 | Pass | Pass | -1 | -1 | 1.25 | 2022-08-05 11:13 | 2022-08-12 17:00 | 2022-08-08 12:45 | 2022-08-12 17:00 | 2022-08-08 14:00 |  |  | Replaced toilet seat.
MSA-MRWA | WA5695999 | 1 | Schindler Lifts Australia | Lift stuck on level 7 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.25 | 2022-08-08 09:03 | 2022-08-09 17:00 | 2022-08-08 11:05 | 2022-08-09 17:00 | 2022-08-08 12:20 |  |  | Works completed - close out at $0
MSA-DFES | WA5696759 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Front Gate - Soak wells need to be cleared - causing moderate to severe flooding - See notes below | Plumbing & Drainage | Water | 168.94 | Fail | Fail | 2 | 2 | 1.25 | 2022-08-08 14:18 | 2022-08-11 17:00 | 2022-08-22 12:00 | 2022-08-11 17:00 | 2022-08-22 13:15 |  |  | attend site to check out block storm drain in drive way been in contact with site contact and he has explained which tank is the problem. Check over drive way drain and found 1200x1200 tank ring with not bottom to tank. In the event of hevey this tank will soak into ground and once ground is soaked it can’t go anywhere else. Sand that is in bottom is ground sand.
MSA-DTAG | WA5697567 | 1 | Midolo Building Services | Ground - court 3 - leak from ceiling | Building | Ceiling | 238.59 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-09 10:26 | 2022-08-10 17:00 | 2022-08-10 07:30 | 2022-08-10 17:00 | 2022-08-10 08:45 |  |  | clean roof & seal potential leak spots - ridge capping
MSA-DTAG | WA5697652 | 2 | Midolo Building Services | L7-Staff kitchen (Judicial Officers)-Panel of skirting board has come away from the wall | Flooring | Timber | 266.09 | Fail | Fail | 1 | 1 | 1.25 | 2022-08-09 11:05 | 2022-08-12 17:00 | 2022-08-16 13:00 | 2022-08-12 17:00 | 2022-08-16 14:15 |  |  | SKIRTING REFIXED TO WALL
MSA-DTWD | WA5697910 | 1 | Australian Airconditioning Services Pty Ltd | 6A1 -Exhaust system for Oxy Acetylene booths not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 192.5 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-09 12:48 | 2022-08-12 17:00 | 2022-08-10 07:30 | 2022-08-12 17:00 | 2022-08-10 08:45 |  |  | Found VSD in fault 3381 (motor circuit fault due to missing motor connection). Found isolator off outside preventing motor from running. Turned isolator on, reset fault and test ran unit. All ok
MSA-MRWA | WA5699363 | 3 | AWB Co. | Power lost to air-con - see notes below | Electrical | General Electrical | 238.025 | Pass | Pass | -1 | -1 | 1.25 | 2022-08-10 09:14 | 2022-08-17 17:00 | 2022-08-10 09:15 | 2022-08-17 17:00 | 2022-08-10 10:30 |  |  | Attended site and signed in. Completed JSA. Located power to transportable and found now blue phase to the units. Investigated to find the main circuit breaker not switching on blue phase. Supply and replaced with new circuit breaker to yard DB. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5699916 | 2 | AWB Co. | Could we please have a flickering light in Balga room E003 faulty | Electrical | Lighting, Internal | 203.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-10 13:26 | 2022-08-15 17:00 | 2022-08-15 08:15 | 2022-08-15 17:00 | 2022-08-15 09:30 |  |  | Job complete
MSA-DFES | WA5706496 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Radio Comms & North Metro Office - Emergency Lights not functional - See notes | Electrical | Emergency & Exit Lighting | 446.355 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-11 11:47 | 2022-08-18 17:00 | 2022-08-18 14:15 | 2022-08-18 17:00 | 2022-08-18 15:30 |  |  | Onsite 1415 replaced two emergency lights and 3 fluro globes. Completed and Signed out. At 1530
MSA-DTWD | WA5714961 | 3 | AWB Co. | Lighting sensor/timer fault | Electrical | Lighting, Internal | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-12 09:50 | 2022-08-19 17:00 | 2022-08-16 14:15 | 2022-08-19 17:00 | 2022-08-16 15:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,went to level 7 and located conference room, found sensor and joined cables , tested lights and now working as intended, cleaned up, packed up, completed paperwork,signed out **job completed**
MSA-DTAG | WA5715141 | 1 | AWB Co. | Court Room 2 - Flickering light in court room 2 - see notes below | Electrical | Lighting, Internal | 207.1425 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-12 11:39 | 2022-08-15 17:00 | 2022-08-15 07:00 | 2022-08-15 17:00 | 2022-08-15 08:15 |  |  | Attended site and signed in. Completed JSA. Escorted by security to court 2. Found no lights flickering. Found a few lights out. Supply and replace with new tubes and starters. Tested all okay. Signed out. Job complete
MSA-DTAG | WA5727308 | 1 | Midolo Building Services | Detention - Cell 6 - a loose security screw, It is loose on a ceiling fixture - see notes | Building | Ceiling | 213.27 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-15 08:36 | 2022-08-16 17:00 | 2022-08-16 07:30 | 2022-08-16 17:00 | 2022-08-16 08:45 |  |  | FIRE ALARM COVER RE-SECURED
MSA-DFES | WA5735730 | 2 | Protek 24/7 Building & Maintenance | Ground floor - Rooftop plant Room - Door to roof top plant room keeps catching - see notes | Building | Doors | 149.17 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-16 14:56 | 2022-08-19 17:00 | 2022-08-17 09:00 | 2022-08-19 17:00 | 2022-08-17 10:15 |  |  | Clean paint and residue of door hardware Adjust door closer
MSA-DFES | WA5780393 | 1 | Go Doors | Entry Gate - South Entrance - Auto Entry Gate - Controller no longer working | Building | Automatic Doors | 341.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-19 10:00 | 2022-08-22 17:00 | 2022-08-19 15:15 | 2022-08-22 17:00 | 2022-08-19 16:30 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5793977 | 1 | Protek 24/7 Building & Maintenance | Ground Floor - Disabled Toilet - Door to disabled toilet does not close fully - See notes below | Building | Doors | 174.17 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-24 11:28 | 2022-08-25 17:00 | 2022-08-24 13:30 | 2022-08-25 17:00 | 2022-08-24 14:45 |  |  | Cut back the bottom of the door to allow the door to close properly without touching the floor, lubricated all door furniture and closer mechanism
MSA-DFES | WA5794992 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Lights are not working | Electrical | Lighting, Internal | 274.365 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-25 09:08 | 2022-08-26 17:00 | 2022-08-25 13:45 | 2022-08-26 17:00 | 2022-08-25 15:00 |  |  | Replace faulty light switch
MSA-DTWD | WA5796814 | 3 | AWB Co. | Room A001 Foyer - 8 fluorescent tubes aren’t working | Electrical | Lighting, Internal | 237.475 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-26 13:50 | 2022-09-02 17:00 | 2022-08-30 07:00 | 2022-09-02 17:00 | 2022-08-30 08:15 |  |  | Attended site and signed in. Completed JSA. Located lights faulty in foyer area. Supply and replace lamps as required. Tested all okay. Whilst on site noticed that the downlights throughout the foyer are only half working. 25x not working. 111mm CDM r111 930. Removed the lights and got details to source parts if available or swap with LED. lamps not locally available so will put price together and send when we hear back. Signed out. Job complete
MSA-DFES | WA5797297 | 1 | Water2water Pty Ltd | Kitchen - Billi unit - drinking unit faulty, intermittently stopping and breaking down | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.25 | 2022-08-29 07:05 | 2022-08-29 17:00 | 2022-08-29 12:45 | 2022-08-29 17:00 | 2022-08-29 14:00 |  |  | REPLACED SOLENOID ALL WORKING OKAY ON DEPARTURE
MSA-DTWD | WA5801404 | 2 | AWB Co. | Room V008 - light is faulty | Electrical | Lighting, Internal | 194.93 | Pass | Pass | 0 | 0 | 1.25 | 2022-08-31 16:35 | 2022-09-05 17:00 | 2022-09-05 11:30 | 2022-09-05 17:00 | 2022-09-05 12:45 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works going ahead. Located disabled toilet at V block. Set up work area. Isolated circuit requiring work. Supplied and replaced faulty globe. Energised and tested. Packed up. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5831807 | 2 | AWB Co. | Water leak coming from roof | Roofing | Metal Roofing | 270.345 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-05 08:49 | 2022-09-08 17:00 | 2022-09-07 13:00 | 2022-09-08 17:00 | 2022-09-07 14:15 |  |  | Cleaned back tiles that were blocking water gates. Job complete
MSA-DCA | WA5831857 | 0 | Automatic Fire Protection (ARA) | Fire panel - making a very high pitch/ whistling sound | Fire Protection Services | Fire Protection - Monitor System | 396.755 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-05 09:07 | 2022-09-05 11:07 | 2022-09-05 10:00 | 2022-09-05 13:07 | 2022-09-05 11:15 |  |  | L1 S41 in maint fault on arrival. Replaced with new XP95 smoke. Cleared fault and reset.
MSA-DTWD | WA5833121 | 3 | AWB Co. | W204 - Student Services kitchenette - Broken GPO Switch | Electrical | Lighting, Internal | 261.63 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-06 08:04 | 2022-09-13 17:00 | 2022-09-07 10:30 | 2022-09-13 17:00 | 2022-09-07 11:45 |  |  | Attended site and signed in. Completed jsa. Located faulty PowerPoint. Replaced. Working as intended, completed paperwork. Signed out.Job complete
MSA-DFES | WA5834045 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Bin Store Door - Door closer for Bin store is broken | Building | Doors | 252.07 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-06 13:26 | 2022-09-13 17:00 | 2022-09-08 07:00 | 2022-09-13 17:00 | 2022-09-08 08:15 |  |  | Reconnect closer and test
MSA-DTWD | WA5837959 | 3 | AWB Co. | Batten light in office is faulty. Please replace with LED | Electrical | Lighting, Internal | 309.88 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-08 09:48 | 2022-09-15 17:00 | 2022-09-09 10:45 | 2022-09-15 17:00 | 2022-09-09 12:00 |  |  | Attended site and signed in, completed JSA,spoke with fm about job,located lighting in a10, went to wholesaler to pick up materials,returned to site, isolated lighting, removed old light fitting and replaced with new , re energised circuit and tested light, working as intended, completed paperwork,packed up,signed out,*job completed*
MSA-DFES | WA5839839 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Contractor to connect power to remove flat key and disconnect the power again | Electrical | Materials | 161.205 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-09 17:40 | 2022-09-10 17:40 | 2022-09-09 18:00 | 2022-09-10 17:40 | 2022-09-09 19:15 |  |  | Key retrieved
MSA-DTWD | WA5853473 | 3 | AWB Co. | Faulty Light switch | Electrical | Lighting, Internal | 261.63 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-12 09:03 | 2022-09-19 17:00 | 2022-09-13 08:15 | 2022-09-19 17:00 | 2022-09-13 09:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located faulty switch mech. De energised circuit. Replaced switch mech. Re energised circuit. Working as intended. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5854261 | 2 | AHS Services WA Pty Ltd (Anchor) | Staff female toilets - first stall is leaking and not flushing correctly | Plumbing & Drainage | Toilets/Cisterns | 191.6075 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-12 15:08 | 2022-09-15 17:00 | 2022-09-14 13:00 | 2022-09-15 17:00 | 2022-09-14 14:15 |  |  | Completed
MSA-DFES | WA5861906 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Female toilets - Faulty water pressure to basin - slow and not much water coming out. | Plumbing & Drainage | Water | 174.44 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-13 12:16 | 2022-09-20 17:00 | 2022-09-19 12:00 | 2022-09-20 17:00 | 2022-09-19 13:15 |  |  | Attend site to check out low water pressure in basins sinks in female toilets lvl2 on arrival checked over all basins and all working correctly, check back with person who,reported it and she advised me it was it was intermittent. Checked over all hand basin in male and female toilets and found low pressure in male toilets lvl1. Found isolation ball valve under bench that had been turned off. Turned back on and checked all levels and found on other turn back on. If any more issues arise further investigate needed.
MSA-DTWD | WA5970712 | 2 | BAKE-QUIP PTY LTD | Combi oven door handle is faulty | Equipment | Catering Equipment | 879.4 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-20 08:54 | 2022-09-23 17:00 | 2022-09-23 08:15 | 2022-09-23 17:00 | 2022-09-23 09:30 |  |  | Refer to service report
MSA-DFES | WA5971486 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | ground-There is a leak under the hydrant-see notes | Plumbing & Drainage | Water | 168.94 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-20 14:26 | 2022-09-23 17:00 | 2022-09-23 07:45 | 2022-09-23 17:00 | 2022-09-23 09:00 |  |  | Arrived on site and singed in went to hydrant leaking in ground north side of the Bat building you can see where the sand is coming up out of bitumen and part of the road has sunk. Need to get job raised to big up bitumen and repair pipe work in ground
MSA-DTWD | WA5973170 | 2 | Protek 24/7 Building & Maintenance | Water leak from internal rain head above south wall welding bay 7 | Building | General Building | 329.42 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-21 11:12 | 2022-09-27 17:00 | 2022-09-21 15:00 | 2022-09-27 17:00 | 2022-09-21 16:15 |  |  | Cleaned out 2 sumps in area
MSA-DCA | WA5974898 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Main Building-Staff Tea Room - Lost Power to the HW machine and the fridge | Electrical | Materials | 161.205 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-24 15:14 | 2022-09-25 15:14 | 2022-09-25 08:30 | 2022-09-25 15:14 | 2022-09-25 09:45 |  |  | Arrived on site at 08:00 to investigate tripped circuit in staff kitchen area, told by staff recent problems with instant boil hot water system. Reset circuit and tested all okay. Checked each appliance plugged into circuit and tested all okay. Inspected hot water unit and tested through draining all water and re-boil all okay. Left site at 09:45
MSA-DFES | WA5976919 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - BA Cleaning room - Fluoro light not working | Electrical | Lighting, Internal | 245.205 | Pass | Pass | 0 | 0 | 1.25 | 2022-09-27 12:20 | 2022-09-30 17:00 | 2022-09-28 13:45 | 2022-09-30 17:00 | 2022-09-28 15:00 |  |  | Arrived onsite at 13:45 to investigate light not working located BA store. Found light was faulty beyond repair and collected new LED batten from nearest wholesaler. Returned to site and installed and tested new light. Informed staff of works completed whilst onsite and left site at 15:00
MSA-DFES | WA5981422 | 2 | Anvil Doors | Front Gate - security gate stays in the open position periodically | Building | Steel Fencing & Gates | 377 | Pass | Pass | -1 | -1 | 1.25 | 2022-09-29 16:26 | 2022-10-04 17:00 | 2022-09-30 16:00 | 2022-10-04 17:00 | 2022-09-30 17:15 |  |  | Technician attended and checked gate operation. Technician notice al noise coming from the gate motor. Technician lubricated the gate motor but the noise persisted. Technician recommends full replacement of gate motor, plastics drive cogs and safety beams. Technician left gate in operable condition.Works to be quoted as an option to replace the gate motor.Thank you
MSA-DTWD | WA5990092 | 3 | Protek 24/7 Building & Maintenance | Wooden Boat works building - Large wooden sliding door jamming - See notes | Building | Doors | 141.945 | Pass | Pass | -1 | -1 | 1.25 | 2022-10-04 13:05 | 2022-10-11 17:00 | 2022-10-05 10:30 | 2022-10-11 17:00 | 2022-10-05 11:45 |  |  | BRAF Declined Scope out works Photo areas of concern and problems are
MSA-DTAG | WA5993320 | 2 | AWB Co. | Ground - Waiting room hallway - Flickering light | Electrical | Lighting, Internal | 287.3775 | Pass | Pass | -1 | -1 | 1.25 | 2022-10-05 09:48 | 2022-10-10 17:00 | 2022-10-06 07:00 | 2022-10-10 17:00 | 2022-10-06 08:15 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works. Went through and replaced various globes and tubes. Notified of works done. **job complete**
MSA-DTWD | WA5993443 | 3 | GRAFFITI FORCE PTY LTD | east south-Graffiti tagging Aberdeen and Beaufort St, Pink container, and near gates | Cleaning | Graffiti | 264.5 | Fail | Fail | 0 | 0 | 1.25 | 2022-10-05 10:19 | 2022-10-12 17:00 | 2022-10-13 19:00 | 2022-10-12 17:00 | 2022-10-13 20:15 |  |  | removal of graffiti from sea container and entry to 14 aberdeen street
MSA-DFES | WA5993501 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | main admin-ground-Lecture room 6-Numerous floor and walls power points are not working-see notes | Electrical | Lighting, Internal | 257.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-05 10:46 | 2022-10-12 17:00 | 2022-10-10 10:45 | 2022-10-12 17:00 | 2022-10-10 12:00 |  |  | Arrived onsite at 10:45 to investigate no power located lecture room 6. Found GPOs on circuit R6 had no power due to tripped RCD. Located switchboard supplying circuit and reset RCD. Found power had been reenergised to R6 GPOs and satisfied with circuit not tripping so fault has been cleared. Tested all GPOs inside room to ensure no areas inside room 6 are without power. Notified staff of works completed whilst onsite and continued onsite at 12:00
MSA-DFES | WA5997828 | 0 | ADVANCED LOCK & KEY | External Door - Stairwell Front of Building - door not closing properly not latching | Security | Locksmith | 250 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-07 10:02 | 2022-10-07 12:02 | 2022-10-07 10:55 | 2022-10-07 14:02 | 2022-10-07 12:10 |  |  | adjusted electric strike as tabs were wrong way around & when the right way the dead latching triggered was hitting on electric stike so filed a rounded edge on strike & it fixed the issue.
MSA-DFES | WA6000442 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Various locations- faulty lights - see notes | Electrical | Lighting, Internal | 311.125 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-10 07:49 | 2022-10-12 17:00 | 2022-10-11 09:00 | 2022-10-12 17:00 | 2022-10-11 10:15 |  |  | Arrived on site at 09:00 to investigate lights not working. Found 4 x lights with blown tubes, tunic room, dorm 1, dorm 2 and bathroom. Replaced both tubes and starters in each and tested all okay. Left site at 10:15
MSA-DTWD | WA6007348 | 3 | AHS Services WA Pty Ltd (Anchor) | Male Student Toilet pan not flushing | Plumbing & Drainage | Toilets/Cisterns | 335.615 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-11 07:28 | 2022-10-17 17:00 | 2022-10-14 10:45 | 2022-10-17 17:00 | 2022-10-14 12:00 |  |  | Replaced bellows and serviced buttons on left hand side male cistern
MSA-DTWD | WA6015100 | 2 | AHS Services WA Pty Ltd (Anchor) | Submersible pump not pumping water out of Sullage Chamber - See notes below ` | Plumbing & Drainage | Water | 166.1075 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-12 14:58 | 2022-10-17 17:00 | 2022-10-14 13:45 | 2022-10-17 17:00 | 2022-10-14 15:00 |  |  | Cleaned out tank checked non-return valve.Tested multiple times-all good
MSA-DCA | WA6020142 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Security control room basement-fire alarm has caused auto doors to open - see notes | Security | Access Control | 550.79 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-13 11:07 | 2022-10-14 17:00 | 2022-10-13 16:45 | 2022-10-14 17:00 | 2022-10-13 18:00 |  |  | Honeywell attended site and checked the issue with the fire curtains and that escape door. They appear to be entirely controlled by the fire panel. Noted there was an input / output isolation on the panel which may be related. Fire contractors are required to check that isolation and resolve the curtain issue.
MSA-DTWD | WA6021444 | 2 | SENTINEL LOCK SERVICE PTY LTD | Digital Keypad Lock not working | Security | Locksmith | 428.6 | Fail | Fail | 5 | 5 | 1.25 | 2022-10-14 08:03 | 2022-10-19 17:00 | 2022-11-24 11:55 | 2022-10-19 17:00 | 2022-11-24 13:10 |  | WACCES | Digital Lock to AG 23A not working.Pad and lock replaced.
MSA-DCA | WA6021531 | 0 | TK Elevator Australia Pty Ltd | Linkway Lift - something hanging from the lift, possibly electrical | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.25 | 2022-10-14 08:45 | 2022-10-14 10:45 | 2022-10-14 09:45 | 2022-10-14 12:45 | 2022-10-14 11:00 |  |  | Lift 4 Centenary-Elevator > MR > Hydraulic :Lift 3 top landing door closer aircord broken, replaced aircord and tested. Left in service. (Onsite at0930)To be closed out at $0 cost
MSA-DFES | WA6051379 | 1 | Australian HVAC Services Pty. Ltd. | Level 1 - Dorm 4 - Air conditioner not working | Air Conditioning | Room Air Conditioners | 166.685 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-17 15:59 | 2022-10-18 17:00 | 2022-10-18 09:15 | 2022-10-18 17:00 | 2022-10-18 10:30 |  |  | Rhys Hall (18/10/2022) - Work NoteArrived on site signed in.On the fire station building plan dorm 6 is our simpro (dorm7 a40144154c) And fire station building plan dorm 4 is our simpro (dorm 6 a40091807l) And fire station building plan dorm 1 is our simpro (dorm 4 a40095450g) So, a bit of confusion and the firemen didn't know about the call.I ran all 3 units up on full heating and full cooling for 20-30mins each and ran tests.After getting all the temperatures and everything running fine, I didn't see any problems with the units.I believe the firemen must of had a shift change as no one knew anything about any problems.I let them know I ran tests and couldn't see any issues and if anything happens with the units to give us a call.All seem to be working well.
MSA-DTWD | WA6079451 | 3 | AWB Co. | repair GPO on wall of entry to N115 corridor | Electrical | General Electrical | 181.5925 | Pass | Pass | -1 | -1 | 1.25 | 2022-10-18 12:51 | 2022-10-25 17:00 | 2022-10-20 13:00 | 2022-10-25 17:00 | 2022-10-20 14:15 |  |  | Job complete
MSA-DFES | WA6088749 | 2 | Protek 24/7 Building & Maintenance | Ground/external area - Yard/ side gate from academy - Gate support post has sunk - see notes | Building | Steel Fencing & Gates | 240.25 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-19 10:20 | 2022-10-24 17:00 | 2022-10-24 07:00 | 2022-10-24 17:00 | 2022-10-24 08:15 |  |  | Adjusted gate height , re located bottom hinge below gate rail
MSA-DTWD | WA6112199 | 3 | AHS Services WA Pty Ltd (Anchor) | The vanity tap is leaking and requires a new washer | Plumbing & Drainage | Water | 171.6075 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-21 13:47 | 2022-10-28 17:00 | 2022-10-27 12:15 | 2022-10-28 17:00 | 2022-10-27 13:30 |  |  | Serviced tap
MSA-DTAG | WA6113880 | 2 | AHS Services WA Pty Ltd (Anchor) | L3-Female Public Toilet (Hay St Side) running constantly - see notes | Plumbing & Drainage | Toilets/Cisterns | 166.1075 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-24 16:27 | 2022-10-27 17:00 | 2022-10-27 10:30 | 2022-10-27 17:00 | 2022-10-27 11:45 |  |  | Picked up and replaced worn outlet washer on female toilet
MSA-DTWD | WA6130546 | 2 | AWB Co. | Faulty Fluoro unit - turning off after a few seconds/flickering | Electrical | Lighting, Internal | 265.4775 | Pass | Pass | 0 | 0 | 1.25 | 2022-10-28 12:53 | 2022-11-02 17:00 | 2022-11-02 10:45 | 2022-11-02 17:00 | 2022-11-02 12:00 |  |  | Attended site signed in jsa completed. Found hazardeous area fitting in store not working. Isolated fitting and replaced two tubes in light. Job completed
MSA-DTAG | WA6145830 | 1 | Australian HVAC Services Pty. Ltd. | Courtroom 1 - aircon isnt working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 166.685 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-02 15:47 | 2022-11-03 17:00 | 2022-11-02 16:00 | 2022-11-03 17:00 | 2022-11-02 17:15 |  |  | Fixed
MSA-DTAG | WA6147523 | 3 | Midolo Building Services | Level 1 - Registry - Access hatch frame near staff kitchen is loose | Building | Ceiling | 180.84 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-03 08:05 | 2022-11-10 17:00 | 2022-11-07 07:30 | 2022-11-10 17:00 | 2022-11-07 08:45 |  |  | access hatch frame re secured
MSA-DTWD | WA6149299 | 1 | Lane's Plumbing | Leaking pipe in front of building 820 - Burst water pipe | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 1.25 | 2022-11-04 13:55 | 2022-11-07 17:00 | 2022-11-04 14:15 | 2022-11-07 17:00 | 2022-11-04 15:30 |  |  | Repairs to burst water pipe
MSA-DTAG | WA6154683 | 2 | AHS Services WA Pty Ltd (Anchor) | Ground Floor - Male Staff Toilets - Both toilets blocked - See notes | Plumbing & Drainage | Toilets/Cisterns | 166.1075 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-07 15:30 | 2022-11-10 17:00 | 2022-11-09 07:30 | 2022-11-10 17:00 | 2022-11-09 08:45 |  |  | Used internal plunger to clear blocked toilets
MSA-DTWD | WA6155466 | 2 | AWB Co. | J Block - North Compound - Faulty lighting | Electrical | Lighting, Internal | 248.63 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-08 10:45 | 2022-11-11 17:00 | 2022-11-09 08:15 | 2022-11-11 17:00 | 2022-11-09 09:30 |  |  | Attended site and signed in. Completed paperwork. Located cables that needed to be made safe. Put connectors and tape on. Placed out of service tags. Double checked for dead. Took pics, completed paperwork, signed out.Job complete
MSA-DTWD | WA6158797 | 3 | Equans Mechanical Services Australia | D Block Air con system – change from heating to cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 197.0775 | Pass | Pass | -1 | -1 | 1.25 | 2022-11-10 09:12 | 2022-11-17 17:00 | 2022-11-11 09:15 | 2022-11-17 17:00 | 2022-11-11 10:30 |  |  | GAINED ACCESS TO BMS AND FOUND SETPOINT TO BE SLIGHTLY LOW. ADJUSTED SETPOINT TO 22.5 DEG
MSA-DCA | WA6159322 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Guards |  | Pass | Pass | 0 | 0 | 1.25 | 2022-11-06 15:15 | 2022-11-07 17:00 | 2022-11-06 15:15 | 2022-11-07 17:00 | 2022-11-06 16:30 | 1 |  | Completed
MSA-DFES | WA6165749 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - Grounds Floor - charging cable hanging from roof - needs to be re fit | Electrical | General Electrical | 270.355 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-11 09:19 | 2022-11-14 17:00 | 2022-11-11 12:45 | 2022-11-14 17:00 | 2022-11-11 14:00 |  |  | Investigated charging cable hanging from roof in engine bay. Cable and ceiling rose has been torn out of the roof and disconnected from supply. Relocated light and reconnected to power supply. Tested all working, notified staff of outcome and left site.
MSA-DCA | WA6166135 | 3 | Protek 24/7 Building & Maintenance | Doors to DB 1A, in level one staff workroom - Doors hard to open and close - See notes | Building | Doors | 160.72 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-11 12:26 | 2022-11-18 17:00 | 2022-11-15 13:30 | 2022-11-18 17:00 | 2022-11-15 14:45 |  |  | Bent back metal and fixed in all areas that swelling, showed site rep Ben if he was happy with fix and he was.
MSA-DFES | WA6206811 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Workshop Maintenance office - Lights sensor in maintenance office to be disabled - See Notes | Electrical | Lighting, Internal | 185.205 | Pass | Pass | -1 | -1 | 1.25 | 2022-11-17 11:11 | 2022-11-22 17:00 | 2022-11-17 13:00 | 2022-11-22 17:00 | 2022-11-17 14:15 |  |  | Sebastian Pino (17/11/2022) - Work NoteArrived on site at 1300 to attend faulty sensors in main office. When arrived, staff strictly requested 2 x sensors were to be disconnected as this fault has been tended to multiple times in the past and still not rectified. Located room/identified equipment and disconnected both sensors in the room leaving existing 2 way switches in the room as primary source of operation. Completed at 1415 and continued other works on site.
MSA-DTAG | WA6231224 | 2 | AWB Co. | Corridor, Mail table, Avon room -Light replacement required in corridor, mail table and Avon room | Electrical | Lighting, Internal | 285.1375 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-18 15:17 | 2022-11-23 17:00 | 2022-11-22 12:00 | 2022-11-23 17:00 | 2022-11-22 13:15 |  |  | Attended site and signed in. Completed JSA. Spoke to site regarding lights not working. Checked out lights needing repair and what’s required. Supply and replace lamps and starters as required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA6231242 | 2 | AWB Co. | Main Plant Room - Power point not working | Electrical | General Electrical | 259.6175 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-18 15:52 | 2022-11-23 17:00 | 2022-11-22 14:15 | 2022-11-23 17:00 | 2022-11-22 15:30 |  |  | Attended site and signed in. Liaised with site about works going ahead. Located plant room. Upon investigation found to be cable had been isolated within board. No tag was on cable. Terminated cable back into RCD. Went and tested PowerPoint. Power now at gpo. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6256750 | 2 | AWB Co. | B103 - Light switch is stuck on. | Electrical | Lighting, Internal | 273.8275 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-24 08:36 | 2022-11-29 17:00 | 2022-11-28 09:15 | 2022-11-29 17:00 | 2022-11-28 10:30 |  |  | Attended site and signed in. Completed JSA. Located room B103. Found to be faulty switch and won’t switch off. Isolated supply. Removed old 2gang switch, supplied and installed 2gang switch plate and mechs to suit. Energised and tested. All working correctly. **job complete**
MSA-DTAG | WA6292620 | 1 | Go Doors | Custody Sally Port -Sally Port Garage Door needs repairing - See Notes Below | Building | Automatic Doors | 262.5 | Pass | Pass | 0 | 0 | 1.25 | 2022-11-29 11:44 | 2022-11-30 17:00 | 2022-11-30 07:30 | 2022-11-30 17:00 | 2022-11-30 08:45 |  |  | Completed works. Please see attachments.
MSA-DTAG | WA6356788 | 3 | Midolo Building Services | Office & Kitchen - Fix Pinboard and paper towel dispenser to wall - see notes | Building | Internal Walls | 180.84 | Pass | Pass | -1 | -1 | 1.25 | 2022-12-05 09:21 | 2022-12-12 17:00 | 2022-12-06 13:00 | 2022-12-12 17:00 | 2022-12-06 14:15 |  |  | pin board & towel dispenser installed
MSA-DTWD | WA6358696 | 2 | BJ SYSTEMS | Gallagher system down | ICT/Audiovisual | Software / Licences | 225 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-06 09:26 | 2022-12-09 17:00 | 2022-12-07 09:15 | 2022-12-09 17:00 | 2022-12-07 10:30 |  |  | Attend site and signed in, adjusted schedules as requested. Gave customer training on how to use and edit schedules on Gallagher. Added access to a cardholder as requested, all ok. Signed out and left site
MSA-DTAG | WA6360407 | 1 | Seme Solutions Pty Ltd | SEME - Court 2 secure delay door not working. | Security | Access Control | 174.85 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-07 11:07 | 2022-12-08 17:00 | 2022-12-07 12:45 | 2022-12-08 17:00 | 2022-12-07 14:00 |  |  | Attended and test the door function multiple times,check status from the access control system. Job completed.
MSA-MRWA | WA6360550 | 3 | AWB Co. | External rear Metrology Lab-Failed external LED light | Electrical | Lighting, Internal | 139.955 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-07 12:03 | 2022-12-14 17:00 | 2022-12-14 07:00 | 2022-12-14 17:00 | 2022-12-14 08:15 |  |  | Attended site and signed in. Completed JSA. Liased with site about works going ahead. Located exterior light on meteorology lab. Located switchboard which light was fed from. Flicked override on. Checked light for power. Light was working correctly. Went back to board and found that time clock was locked on manual off. Set time clock correctly should now operate at “6:00pm”-“6:00am”. Notified relevant personnel. **job complete**
MSA-DCA | WA6361673 | 0 | Earth & Water Pty Ltd | Plantrs orchid bed - Retic not working when turned on. | Plumbing & Drainage | Water |  | Fail | Fail | 0 | 0 | 1.25 | 2022-12-08 11:51 | 2022-12-08 13:51 | 2022-12-08 16:45 | 2022-12-08 15:51 | 2022-12-08 18:00 |  |  | repairs to retic
MSA-DTWD | WA6362212 | 1 | AHS Services WA Pty Ltd (Anchor) | Isolation tap needs to have a washer changed unable to use to isolate water | Plumbing & Drainage | Water | 248.9325 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-09 08:44 | 2022-12-12 17:00 | 2022-12-09 10:30 | 2022-12-12 17:00 | 2022-12-09 11:45 |  |  | Completed
MSA-DTWD | WA6373590 | 0 | AWB Co. | Electrical Roller Door - isnt coming down - no power coming to the door | Electrical | General Electrical | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-14 16:27 | 2022-12-14 18:27 | 2022-12-14 16:30 | 2022-12-14 20:27 | 2022-12-14 17:45 |  |  | Attended site and signed in,completed jsa , spoke with fm about job , found there to be no power in stonemason work area, went to db and found no power at board, went to next board and reset breaker to db , power now working, put roller door down, completed paperwork, signed out**job completed**
MSA-DTAG | WA6376440 | 3 | Midolo Building Services | Court 41 - 1x public chair broken | Furniture | Office Furniture | 153.94 | Fail | Fail | 3 | 3 | 1.25 | 2022-12-15 15:18 | 2022-12-22 17:00 | 2023-01-09 13:00 | 2022-12-22 17:00 | 2023-01-09 14:15 |  |  | Broken chair replaced
MSA-DTAG | WA6379063 | 1 | Seme Solutions Pty Ltd | Alarm System - It would appear that the building is being Armed but not showing as Armed with monito | Security | Security Management System | 174.85 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-19 09:04 | 2022-12-20 17:00 | 2022-12-19 11:30 | 2022-12-20 17:00 | 2022-12-19 12:45 |  |  | Attended to Admin, Anne-Marie informed she couldn't arm the Alarm last Saturday, after investigation found she haven't bypassed open areas on the alarm when tried to arm it, she said she would try it again tonight and call back in case it doesn't work.
MSA-DTWD | WA6381842 | 1 | BJ SYSTEMS | Gallagher security software-Fault Description Locking up building at Rockingham Campus turns on alar | Security | Security Management System | 225 | Pass | Pass | 0 | 0 | 1.25 | 2022-12-19 15:17 | 2022-12-20 17:00 | 2022-12-20 13:45 | 2022-12-20 17:00 | 2022-12-20 15:00 |  |  | Attend site and meet with Dennis. Change the lecturers access group to lockdown over the holiday period
MSA-DTAG | WA6388350 | 2 | AHS Services WA Pty Ltd (Anchor) | Ground - Custody Area - Cell 2 - Toilet is constantly running - See Notes | Plumbing & Drainage | Toilets/Cisterns | 210.2175 | Pass | Pass | -1 | -1 | 1.25 | 2022-12-21 12:21 | 2022-12-28 17:00 | 2022-12-22 08:15 | 2022-12-28 17:00 | 2022-12-22 09:30 |  |  | Completed
MSA-DTAG | WA6392181 | 1 | SCAVENGER SUPPLIES PTY LTD | Basement-fire panel-fault showing on panel- see notes | Fire Protection Services | Fire Protection - Monitor System | 929.53 | Pass | Pass | -1 | -1 | 1.25 | 2022-12-23 10:39 | 2022-12-28 17:00 | 2022-12-23 12:00 | 2022-12-28 17:00 | 2022-12-23 13:15 |  |  | 23/12/22 - 2 x technicians on site to install new batteries (75AH). BRAF will be submitted as completion is above PO value assigned. 23/12/22 - BRAF Submitted to wasc for works completed today. Copy attached. 9/1/23 - Followed up approval of BRAF. note: Field completed after receiving approval for BRAF 9/1/23 hence delay in lodging claim.
MSA-DTAG | WA6401455 | 3 | Midolo Building Services | L4-Adult Community Corrections - Kitchen-Door closer leading from corridor to kitchen is leaking | Building | Doors | 148.09 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-04 11:58 | 2023-01-11 17:00 | 2023-01-10 10:30 | 2023-01-11 17:00 | 2023-01-10 11:45
MSA-DTWD | WA6403237 | 3 | AWB Co. | Jobs and Skills Room 3 - tubes not working in light | Electrical | Lighting, Internal | 171.855 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-06 09:20 | 2023-01-13 17:00 | 2023-01-11 09:00 | 2023-01-13 17:00 | 2023-01-11 10:15
MSA-DFES | WA6404987 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Duty Room - failure of the 1st light | Electrical | General Electrical | 234.705 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-09 10:51 | 2023-01-12 17:00 | 2023-01-09 13:45 | 2023-01-12 17:00 | 2023-01-09 15:00
MSA-DTWD | WA6405069 | 2 | BAKE-QUIP PTY LTD | SK2 oven keeps tripping RCD when turned on | Electrical | General Electrical | 325.55 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-09 11:20 | 2023-01-12 17:00 | 2023-01-11 08:30 | 2023-01-12 17:00 | 2023-01-11 09:45
MSA-DTWD | WA6482423 | 3 | Protek 24/7 Building & Maintenance | Outside wall Cygnet - 4 x Gutter / down pipe brackets broken and down pipe dropped - See Notes | Roofing | Guttering | 271.07 | Pass | Pass | -1 | -1 | 1.25 | 2023-01-18 10:19 | 2023-01-25 17:00 | 2023-01-20 12:00 | 2023-01-25 17:00 | 2023-01-20 13:15
MSA-DTWD | WA6504029 | 2 | AWB Co. | Two GPO's aren't working | Electrical | General Electrical | 170.3425 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-19 12:57 | 2023-01-24 17:00 | 2023-01-24 12:00 | 2023-01-24 17:00 | 2023-01-24 13:15
MSA-DTWD | WA6509468 | 1 | Critical Fire Protection & Training | fire alarm activation - room C208 in ceiling - see notes | Fire Protection Services | Fire Protection - Monitor System | 473.53 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-20 10:58 | 2023-01-23 17:00 | 2023-01-20 14:30 | 2023-01-23 17:00 | 2023-01-20 15:45
MSA-DFES | WA6517589 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | engine room - Fluro light hanging by electrical cable | Electrical | Lighting, Internal | 242.405 | Pass | Pass | -1 | -1 | 1.25 | 2023-01-24 11:09 | 2023-01-30 17:00 | 2023-01-25 15:00 | 2023-01-30 17:00 | 2023-01-25 16:15
MSA-DTWD | WA6519197 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground Level - Block E - E108 - Staff Retreat - Water is leaking through cupboard (see notes) | Plumbing & Drainage | Drainage | 168.8175 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-25 13:46 | 2023-01-27 17:00 | 2023-01-25 15:15 | 2023-01-27 17:00 | 2023-01-25 16:30
MSA-DTWD | WA6519982 | 2 | Lane's Plumbing | Ground Floor - House 14 - Leaking shower head (see notes) | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 1.25 | 2023-01-27 09:29 | 2023-02-01 17:00 | 2023-01-30 10:00 | 2023-02-01 17:00 | 2023-01-30 11:15
MSA-DTWD | WA6521568 | 1 | PEEL LOCK SERVICES PTY LTD | Ladies toilets - Near Gym - Ladies toilet door - Keys not opening main door lock | Security | Keys & Access |  | Pass | Pass | 0 | 0 | 1.25 | 2023-01-30 11:41 | 2023-01-31 17:00 | 2023-01-31 12:00 | 2023-01-31 17:00 | 2023-01-31 13:15
MSA-DTWD | WA6521901 | 1 | AHS Services WA Pty Ltd (Anchor) | Water constantly running | Plumbing & Drainage | Toilets/Cisterns | 148.1875 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-30 14:10 | 2023-01-31 17:00 | 2023-01-31 07:30 | 2023-01-31 17:00 | 2023-01-31 08:45
MSA-DCA | WA6522859 | 3 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Ground Level - Ladies Staff bathroom - toilet constantly running | Plumbing & Drainage | Toilets/Cisterns | 167.8125 | Pass | Pass | -1 | -1 | 1.25 | 2023-01-31 10:41 | 2023-02-07 17:00 | 2023-01-31 15:45 | 2023-02-07 17:00 | 2023-01-31 17:00
MSA-DTWD | WA6523271 | 2 | AWB Co. | the ceiling fan switch is broken | Electrical | General Electrical | 189.8425 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-31 13:57 | 2023-02-03 17:00 | 2023-02-02 10:45 | 2023-02-03 17:00 | 2023-02-02 12:00
MSA-DTWD | WA6523308 | 1 | AHS Services WA Pty Ltd (Anchor) | Male toilets has a tap continuously running | Plumbing & Drainage | Toilets/Cisterns | 171.6075 | Pass | Pass | 0 | 0 | 1.25 | 2023-01-31 14:23 | 2023-02-01 17:00 | 2023-02-01 12:00 | 2023-02-01 17:00 | 2023-02-01 13:15
MSA-DTWD | WA6526675 | 2 | SENTINEL LOCK SERVICE PTY LTD | Faulty Door Lock/Cylinder | Security | Locksmith | 311.34 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-01 09:51 | 2023-02-06 17:00 | 2023-02-03 13:05 | 2023-02-06 17:00 | 2023-02-03 14:20
MSA-DTWD | WA6527995 | 2 | AHS Services WA Pty Ltd (Anchor) | C129 - Male toilets - First cubicle toilet constantly running | Plumbing & Drainage | Drainage | 187.6075 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-02 08:12 | 2023-02-07 17:00 | 2023-02-06 09:45 | 2023-02-07 17:00 | 2023-02-06 11:00
MSA-DTWD | WA6538224 | 2 | Dormakaba Australia Pty Ltd | Limit switch broken on roller door | Building | Automatic Doors |  | Fail | Fail | 2 | 2 | 1.25 | 2023-02-07 16:27 | 2023-02-10 17:00 | 2023-02-22 09:00 | 2023-02-10 17:00 | 2023-02-22 10:15
MSA-DTWD | WA6544384 | 1 | AHS Services WA Pty Ltd (Anchor) | Welding bay has a broken tap that cant be turned off | Plumbing & Drainage | Drainage | 196.6075 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-10 12:24 | 2023-02-13 17:00 | 2023-02-10 14:15 | 2023-02-13 17:00 | 2023-02-10 15:30
MSA-DFES | WA6573764 | 1 | Go Doors | engine room door No1-door is not coming down automatically-see notes | Building | Automatic Doors | 333.56 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-14 16:21 | 2023-02-15 17:00 | 2023-02-15 07:30 | 2023-02-15 17:00 | 2023-02-15 08:45
MSA-DTWD | WA6578713 | 1 | AWB Co. | Library computer Booth 2 - Faulty double GPO | Electrical | General Electrical | 264.38 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-15 11:35 | 2023-02-16 17:00 | 2023-02-16 06:00 | 2023-02-16 17:00 | 2023-02-16 07:15
MSA-DTWD | WA6578917 | 1 | BJ SYSTEMS | Access code to electronic keypad needs changing | Security | Access Control | 225 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-15 13:05 | 2023-02-16 17:00 | 2023-02-16 10:30 | 2023-02-16 17:00 | 2023-02-16 11:45
MSA-DFES | WA6650993 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Admin Block - Fluro light flickering - workstation | Electrical | Lighting, Internal | 295.3425 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-20 15:45 | 2023-02-23 17:00 | 2023-02-22 08:15 | 2023-02-23 17:00 | 2023-02-22 09:30
MSA-DTWD | WA6656971 | 2 | Assa Abloy Entrance Systems Aust P/L-WA | Roller door is catching on the way down. Chain operated, may need re-tensioning | Building | Automatic Doors | 429.5 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-21 10:52 | 2023-02-24 17:00 | 2023-02-22 08:15 | 2023-02-24 17:00 | 2023-02-22 09:30
MSA-DTAG | WA6667895 | 1 | AWB Co. | Ground floor - Power board sparking when items plugged in | Electrical | General Electrical | 247.08 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-21 16:43 | 2023-02-22 17:00 | 2023-02-22 07:00 | 2023-02-22 17:00 | 2023-02-22 08:15
MSA-DTWD | WA6672074 | 1 | AWB Co. | 3Phase power point loose | Electrical | General Electrical | 180.0125 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-23 12:32 | 2023-02-24 17:00 | 2023-02-23 16:00 | 2023-02-24 17:00 | 2023-02-23 17:15
MSA-DTWD | WA6673247 | 2 | AHS Services WA Pty Ltd (Anchor) | Ladies toilet -Toilet seat broken - Seat to be replaced | Plumbing & Drainage | Toilets/Cisterns | 630.8175 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-24 11:59 | 2023-03-01 17:00 | 2023-03-01 09:00 | 2023-03-01 17:00 | 2023-03-01 10:15
MSA-DFES | WA6673703 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ensuite 5 - Leaking tap under neath the basin. where the hose was connected | Plumbing & Drainage | Materials | 139.49 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-25 17:42 | 2023-03-01 17:00 | 2023-03-01 11:30 | 2023-03-01 17:00 | 2023-03-01 12:45
MSA-DFES | WA6674885 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen - Tap is leaking - washers have been changed and has not fixed it | Plumbing & Drainage | Drainage | 247.7525 | Pass | Pass | 0 | 0 | 1.25 | 2023-02-27 12:55 | 2023-03-02 17:00 | 2023-03-02 14:15 | 2023-03-02 17:00 | 2023-03-02 15:30
MSA-DTWD | WA6680319 | 3 | LD TOTAL | Garden near the pond - Broken pipe | Plumbing & Drainage | Water | 144.35 | Pass | Pass | -1 | -1 | 1.25 | 2023-03-01 10:10 | 2023-03-09 17:00 | 2023-03-01 12:00 | 2023-03-09 17:00 | 2023-03-01 13:15
MSA-DFES | WA6683856 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Male Locker Room Westend-Light is flashing about locker 115. | Electrical | Lighting, Internal | 281.075 | Pass | Pass | 0 | 0 | 1.25 | 2023-03-03 12:54 | 2023-03-09 17:00 | 2023-03-08 14:15 | 2023-03-09 17:00 | 2023-03-08 15:30
MSA-DFES | WA6683992 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Front driveway - Broken power box on right pole - exposed wires | Electrical | General Electrical | 255.845 | Pass | Pass | -1 | -1 | 1.25 | 2023-03-03 15:05 | 2023-03-07 17:00 | 2023-03-03 15:45 | 2023-03-07 17:00 | 2023-03-03 17:00
MSA-DFES | WA5674713 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Male and female showers - Shower heads in male and female leaking | Plumbing & Drainage | Water | 212.22 | Pass | Pass | 0 | 0 | 1.2383 | 2022-07-21 13:32 | 2022-07-28 17:00 | 2022-07-28 07:31 | 2022-07-28 17:00 | 2022-07-28 08:45 |  |  | Attend site check out leaking showers. On arrival found both shower not leaking but once the water is turned on water spray she and leaks from the shower rose and arm., removed old shower heads and replace with new like for like.
MSA-DTAG | WA5016833 | 0 | Gilmour & Jooste Electrical | Whole courthouse - No power to the whole building | Electrical | General Electrical | 162.0875 | Pass | Pass | 0 | 0 | 1.2333 | 2022-01-13 08:01 | 2022-01-13 10:00 | 2022-01-13 09:00 | 2022-01-13 12:00 | 2022-01-13 10:14 |  |  | Inspected faulty power to courthouse. Found main switch for courthouse to be off. Tested cables and reset main switch. Now in working order.
MSA-DTWD | WA5091914 | 3 | Falcetta Plumbing and Gas | Level 4 - 428 - sink damaged and requires replacement | Plumbing & Drainage | Water | 166.05 | Pass | Pass | 0 | 0 | 1.2333 | 2022-01-27 12:17 | 2022-02-03 17:00 | 2022-02-03 15:45 | 2022-02-03 17:00 | 2022-02-03 16:59 |  |  | removed basin and installed mini stop
MSA-DTWD | WA5393939 | 1 | Techworks Electrical | C- Block - Car Park - lights not working | Electrical | General Electrical | 299.99 | Pass | Pass | 0 | 0 | 1.2333 | 2022-05-04 11:29 | 2022-05-05 17:00 | 2022-05-04 14:00 | 2022-05-05 17:00 | 2022-05-04 15:14 |  |  | Investigated carpark lights not working. Found light not working to have cable attached which has a fault. Disconnected cable from fuse and does not effect any of the lights. Faulty cable possibly in a pit some where on site
MSA-MRWA | WA5493537 | 0 | TK Elevator Australia Pty Ltd | Lift number 1 & 4 - not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.2333 | 2022-06-07 08:59 | 2022-06-07 10:59 | 2022-06-07 09:24 | 2022-06-07 12:59 | 2022-06-07 10:38 |  |  | Lift1 DAC-Geared :Call was for lift 2and 4 . Both lifts had bode board tripped. LED blink 10 times. Tighten connection on bode boards, relays and terminals. Tested lift, running ok with no fault recorded. Put lifts back on service.to be closed out at $0 cost
MSA-DTWD | WA5831856 | 3 | Water2water Pty Ltd | A56 kitchen - filtered water spout leaking | Plumbing & Drainage | Water | 505.395 | Pass | Pass | -1 | -1 | 1.2333 | 2022-09-05 09:05 | 2022-09-12 17:00 | 2022-09-06 10:41 | 2022-09-12 17:00 | 2022-09-06 11:55 |  |  | Removed old system due to leaks and installed new maxiflow system. All tested and flushed
MSA-MRWA | WA5200989 | 1 | GPS Plumbing & Gas Services PtyLtd | toilet constantly running slush button broken | Plumbing & Drainage | Toilets/Cisterns | 314.535 | Pass | Pass | 0 | 0 | 1.2333 | 2022-03-02 10:47 | 2022-03-03 17:00 | 2022-03-02 12:51 | 2022-03-03 17:00 | 2022-03-02 14:05 |  |  | Replaced flushing valve platforms and outlet washer to unisex toilet.
MSA-DTAG | WA5472202 | 2 | Water2water Pty Ltd | Level 11 - Kitchen - Cold-water filter tap on our level is running very slow | Plumbing & Drainage | Water | 286.9 | Pass | Pass | 0 | 0 | 1.2333 | 2022-05-23 15:34 | 2022-05-26 17:00 | 2022-05-24 13:45 | 2022-05-26 17:00 | 2022-05-24 14:59 |  |  | REPLACED INLET AND COLD SOLIENOID TO BILLI TO SMALL CORRECTION OF MACHINE. INLET WATER REQUIRES PLUMBERS ATTENDANCE.
MSA-DTAG | WA5682366 | 0 | Gilmour & Jooste Electrical | whole of building- major flood needs to be made safe | Electrical | General Electrical | 205.46 | Pass | Pass | 0 | 0 | 1.2333 | 2022-07-29 08:43 | 2022-07-29 10:43 | 2022-07-29 10:00 | 2022-07-29 12:43 | 2022-07-29 11:14 |  |  | Investigated flooding to courthouse. Found victim support area to be affected. No water damage to power circuits found. Disconnected and removed water damaged light fittings to let ceiling dry. Made area safe. New light will need to be installed once ceiling is fixed/dried out.
MSA-DCA | WA6520161 | 0 | TK Elevator Australia Pty Ltd | Ground Floor - Lift 7 - Stuck on ground floor | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 1.2333 | 2023-01-27 11:25 | 2023-01-27 13:25 | 2023-01-27 14:04 | 2023-01-27 15:25 | 2023-01-27 15:18
MSA-DFES | WA5497148 | 1 | Australian HVAC Services Pty. Ltd. | Plant Room - Running on generator - Inspect to make sure power is all good | Air Conditioning | Building HVAC Maintenance (Major Plant) | 130.05 | Pass | Pass | 0 | 0 | 1.2239 | 2022-06-09 14:43 | 2022-06-10 17:00 | 2022-06-09 14:55 | 2022-06-10 17:00 | 2022-06-09 16:09 |  |  | Attended site and found generator running. Found building operating correctly. Power restored while onsite. Checked crac units and cleared faults. Found chiller 1 faulting repeatedly. Checked system and reset unit. Found fault cleared. All system restored and faults cleared.
MSA-DTWD | WA5018560 | 1 | Dormakaba Australia Pty Ltd | Main Entrance - sliding door not closing | Building | Security Doors | 200 | Pass | Pass | 0 | 0 | 1.2167 | 2022-01-14 12:49 | 2022-01-17 17:00 | 2022-01-14 13:46 | 2022-01-17 17:00 | 2022-01-14 14:59 |  |  | 1069559 Find After hours activated replace terminal block on after hour connection.Tested ok.1069558 Fire alarm activated disconnect cable put a bridge across the terminals. They will call fire company on Monday.
MSA-DCA | WA5628055 | 0 | Techworks Electrical | King Of Gem Stones - Shop - Murray St Entrance - Water coming in from light fitting - Please isolate | Electrical | General Electrical | 230.845 | Pass | Pass | 0 | 0 | 1.2167 | 2022-07-15 10:41 | 2022-07-15 12:41 | 2022-07-15 11:00 | 2022-07-15 14:41 | 2022-07-15 12:13 |  |  | Inspected lights. Found water to be dripping onto light but not inside light due to the light being installed on a join. Siliconed up join and a seal all the way round the light to prevent water dripping onto light. Found some slight moisture on middle light which appeared to be due to the conduit entree. Siliconed around cable entree
MSA-DTAG | WA6178106 | 3 | Midolo Building Services | L3-public corridor-Public bench seat attached to the floor outside admin services is broken | Furniture | Commercial Furniture | 153.94 | Pass | Pass | -1 | -1 | 1.2167 | 2022-11-14 09:31 | 2022-11-21 17:00 | 2022-11-14 09:32 | 2022-11-21 17:00 | 2022-11-14 10:45 |  |  | replaced broken chair & secured @ 0930
MSA-DCA | WA6560307 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander Library - Level 1 - male public toilets | Plumbing & Drainage | Toilets/Cisterns | 278.9025 | Pass | Pass | 0 | 0 | 1.2167 | 2023-02-13 09:12 | 2023-02-16 17:00 | 2023-02-15 09:50 | 2023-02-16 17:00 | 2023-02-15 11:03
MSA-DCA | WA5018469 | 2 | TK Elevator Australia Pty Ltd | lift 6 - Button on HLT dock end of the lift has fallen into the recess behind panel. | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1.2167 | 2022-01-14 11:50 | 2022-01-19 17:00 | 2022-01-14 12:29 | 2022-01-19 17:00 | 2022-01-14 13:42 |  |  | Studio car call button retaining plate clips broken and button in pieces, located replacemnet button in LMR and replaced.
MSA-DTAG | WA5111808 | 2 | Gilmour & Jooste Electrical | Lower level - custody - Custody Staff Area Fluro light flickering will not stay on | Electrical | Lighting, Internal | 135.85 | Pass | Pass | -1 | -1 | 1.2167 | 2022-02-10 11:09 | 2022-02-15 17:00 | 2022-02-10 12:00 | 2022-02-15 17:00 | 2022-02-10 13:13 |  |  | Replaced blown lamp and starter to toilet fluoro in lower custody.
MSA-DFES | WA5480059 | 2 | Seme Solutions Pty Ltd | Please see details below - | Security | Access Control | 162.5 | Pass | Pass | 0 | 0 | 1.2167 | 2022-05-27 15:07 | 2022-06-01 17:00 | 2022-05-30 09:15 | 2022-06-01 17:00 | 2022-05-30 10:28 |  |  | Programmed Door 29 into system to allow access.
MSA-DCA | WA5494051 | 0 | TK Elevator Australia Pty Ltd | Ground Floor - Lift not working - stuck | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 1.2167 | 2022-06-07 12:18 | 2022-06-07 14:18 | 2022-06-07 14:32 | 2022-06-07 16:18 | 2022-06-07 15:45 |  |  | Lift through the bottom level, ongoing intermittent fault. Recorded event log. Rechecked shaft positioning circuits and equipment. Follow up raised to replace the tape head reader board. Returned the lift to service.to be closed out at $0 cost
MSA-MRWA | WA5683180 | 0 | Dormakaba Australia Pty Ltd | Eastern car park auto shutter gate not working | Building | Roller Shutters | 360 | Pass | Pass | 0 | 0 | 1.2167 | 2022-07-30 10:28 | 2022-07-30 12:28 | 2022-07-30 11:42 | 2022-07-30 14:28 | 2022-07-30 12:55 |  |  | Bottom slats had moved and got caught on top of guide on left hand side. Realigned slats and replaced slat clips. Lubricated in between slats and both guides. Tested and inspected operation multiple times. Door is safe to use.
MSA-DTWD | WA5715420 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 1 male toilet in library seat broken | Plumbing & Drainage | Toilets/Cisterns | 306.3375 | Pass | Pass | 0 | 0 | 1.2167 | 2022-08-12 15:11 | 2022-08-19 17:00 | 2022-08-16 07:27 | 2022-08-19 17:00 | 2022-08-16 08:40 |  |  | Completed
MSA-DCA | WA5791948 | 2 | GPS Plumbing & Gas Services PtyLtd | Administration - Ground - Gents Toilet - Leaking tap on basin | Plumbing & Drainage | Water | 286.6025 | Pass | Pass | 0 | 0 | 1.2167 | 2022-08-23 10:37 | 2022-08-26 17:00 | 2022-08-25 09:42 | 2022-08-26 17:00 | 2022-08-25 10:55 |  |  | Replaced hand basin taps set to male toilet that was leaking and damaged when they tried to replace themselves
MSA-DTAG | WA5995266 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Sheriffs Office - Tap in cleaners utility room broken | Plumbing & Drainage | Water | 195.8125 | Pass | Pass | -1 | -1 | 1.2167 | 2022-10-06 11:42 | 2022-10-11 17:00 | 2022-10-07 13:00 | 2022-10-11 17:00 | 2022-10-07 14:13 |  |  | Replace broken spout with new
MSA-DTAG | WA6509472 | 2 | High Tech Pest Control | Whole building - Pest control required – rat droppings evident | Pest Control | General Pest | 344.57 | Pass | Pass | 0 | 0 | 1.2167 | 2023-01-20 11:02 | 2023-01-25 17:00 | 2023-01-25 12:20 | 2023-01-25 17:00 | 2023-01-25 13:33
MSA-DTWD | WA6690410 | 2 | AHS Services WA Pty Ltd (Anchor) | ladies facilities in D Block is currently locked. The toilet is blocked and not flushing | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | -1 | -1 | 1.2167 | 2023-03-09 09:25 | 2023-03-14 17:00 | 2023-03-10 10:45 | 2023-03-14 17:00 | 2023-03-10 11:58
MSA-DTAG | WA5187481 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 7 - Staff Kitchen - sink taps have low water pressure both hot and cold | Plumbing & Drainage | Water | 154.3675 | Pass | Pass | 0 | 0 | 1.2 | 2022-02-22 13:18 | 2022-02-25 17:00 | 2022-02-25 12:45 | 2022-02-25 17:00 | 2022-02-25 13:57 |  |  | Checked all valves all good.Removed and cleared out aerator. Tested all working fine
MSA-DFES | WA5307252 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Bunker - Ground - Female toilet - toilet in the female toilet has an issue runs when flushed | Plumbing & Drainage | Toilets/Cisterns | 321.85 | Pass | Pass | 0 | 0 | 1.2 | 2022-04-07 11:38 | 2022-04-12 17:00 | 2022-04-11 14:50 | 2022-04-12 17:00 | 2022-04-11 16:02 |  |  | Had to clean the out let rubber it had rubbish onit
MSA-DCA | WA5392509 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Ground Level - Male Toilet 2nd Cubicle - Full Flush not working | Plumbing & Drainage | Toilets/Cisterns | 212.275 | Pass | Pass | 0 | 0 | 1.2 | 2022-05-03 10:22 | 2022-05-06 17:00 | 2022-05-04 14:48 | 2022-05-06 17:00 | 2022-05-04 16:00 |  |  | Use repair kit to fix faulty rubbers
MSA-DTWD | WA5660319 | 1 | Water2water Pty Ltd | student kitchenette zippy boil leaking water | Plumbing & Drainage | Water | 508.15 | Pass | Pass | 0 | 0 | 1.2 | 2022-07-19 08:50 | 2022-07-20 17:00 | 2022-07-19 15:43 | 2022-07-20 17:00 | 2022-07-19 16:55 |  |  | Replaced leaking tubing. Also replaced solenoid as was stuck open meaning unit could isolate once it detected leak. Also changed PLV as was almost completely restricting the flow. All now ok.
MSA-DTAG | WA5305430 | 1 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Cell 1, custody area - bio clean - PIC in cell had been spitting on walls and floor | Cleaning | Emergency Cleans | 300 | Fail | Fail | 1 | 1 | 1.2 | 2022-04-05 16:15 | 2022-04-06 17:00 | 2022-04-14 01:21 | 2022-04-06 17:00 | 2022-04-14 02:33 |  |  | As per work order
MSA-DTWD | WA5596996 | 2 | Dormakaba Australia Pty Ltd | Kendrew- D-Block G/Floor disabled toilet auto door not working | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 1.2 | 2022-07-11 11:47 | 2022-07-14 17:00 | 2022-07-11 15:04 | 2022-07-14 17:00 | 2022-07-11 16:16 |  |  | Note incorrect door given should be 1086530 ED100. Programmed asset number A40442182E. Arrived onsite and signed in, located door and found the screw for the arm had come out and lost. Fitted new screw and found no power to unit , located switchboard and breaker is set, further investigation found an isolator above outside unit, switched on and tested operation all correct.
MSA-DTWD | WA5980035 | 3 | CONNECT SECURITY SYSTEMS | Room - I1 - Issues with alarm sensors | Security | Security Management System | 328.57 | Pass | Pass | -1 | -1 | 1.2 | 2022-09-29 11:54 | 2022-10-06 17:00 | 2022-09-30 14:16 | 2022-10-06 17:00 | 2022-09-30 15:28 |  |  | replaced faulty shock sensor to window of Room I1
MSA-DFES | WA6008088 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | L1 male toilets 1st cubical-is blocked-door is locked key from security | Plumbing & Drainage | Toilets/Cisterns | 168.94 | Pass | Pass | 0 | 0 | 1.1833 | 2022-10-11 12:44 | 2022-10-12 17:00 | 2022-10-11 14:18 | 2022-10-12 17:00 | 2022-10-11 15:29 |  |  | Arrived on site and singed in went to level 1 male toilets 1st cubicle gave it a plunge everything was fine, as l flash the toilet it was taking along time to fill up pulled out the inlet valve and cleaned out a lot of rubbish. Put it all back together and tested it and everything was fine.
MSA-DFES | WA5974741 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Bathroom in Dorm 2 - Shower head has snapped off. Wall outlet thread is undamaged. | Plumbing & Drainage | Water | 193.33 | Pass | Pass | -1 | -1 | 1.1833 | 2022-09-23 16:07 | 2022-10-03 17:00 | 2022-09-28 10:04 | 2022-10-03 17:00 | 2022-09-28 11:15 |  |  | Replaced broken shower head.
MSA-MRWA | WA6672806 | 2 | GPS Plumbing & Gas Services PtyLtd | Admin male toilet - Left sink leaking pipe very loose | Plumbing & Drainage | Drainage | 241.165 | Pass | Pass | -1 | -1 | 1.1833 | 2023-02-24 08:39 | 2023-03-01 17:00 | 2023-02-24 08:40 | 2023-03-01 17:00 | 2023-02-24 09:51
MSA-DTWD | WA5831899 | 2 | Techworks Plumbing | urinal not flushing | Plumbing & Drainage | Drainage | 775.38 | Pass | Pass | 0 | 0 | 1.1833 | 2022-09-05 09:17 | 2022-09-08 17:00 | 2022-09-05 14:19 | 2022-09-08 17:00 | 2022-09-05 15:30 |  |  | Opened up access panel and noticed there was no GPO for each urinal in an accessible location. Bought a double adaptor from Bunnings and plugged both power leads in and tested.
MSA-MRWA | WA5832134 | 1 | GPS Plumbing & Gas Services PtyLtd | both cubicle full flush not working | Plumbing & Drainage | Toilets/Cisterns | 322.09 | Pass | Pass | 0 | 0 | 1.1833 | 2022-09-05 11:23 | 2022-09-06 17:00 | 2022-09-06 07:59 | 2022-09-06 17:00 | 2022-09-06 09:10 |  |  | Replaced both bellows for both cisterns, flushed multiple times with no issues after replacing bellows.
MSA-MRWA | WA6578564 | 2 | GPS Plumbing & Gas Services PtyLtd | Middle and RHS toilet - Not flushing | Plumbing & Drainage | Toilets/Cisterns | 226.59 | Pass | Pass | -1 | -1 | 1.1833 | 2023-02-15 10:26 | 2023-02-20 17:00 | 2023-02-15 10:59 | 2023-02-20 17:00 | 2023-02-15 12:10
MSA-DFES | WA5790227 | 1 | Australian HVAC Services Pty. Ltd. | BMS-needs to be reset due to fault over the weekend | Air Conditioning | Room Air Conditioners | 139.94 | Pass | Pass | 0 | 0 | 1.1808 | 2022-08-22 09:24 | 2022-08-23 17:00 | 2022-08-22 12:26 | 2022-08-23 17:00 | 2022-08-22 13:37 |  |  | Attended site and inspected bms fault that occured over weekend. Found power fault appears to have occured and multiple controllers appeared offline. Reset controllers and found all plant operating and fault cleared. Suspect cause was works carried out by other contractor over weekend.
MSA-DCA | WA5318273 | 2 | ACTION GLASS & ALUMINIUM | Main Auditorium- Level 1 - Broken Window onto street - see notes | Glazing | Window Glass | 283.72 | Pass | Pass | -1 | -1 | 1.1667 | 2022-04-12 09:44 | 2022-04-19 17:00 | 2022-04-14 12:28 | 2022-04-19 17:00 | 2022-04-14 13:38 |  |  | ATTENDED SITE REGLAZED BROKEN WINDOW5.38 CLEAR LAMINATED SAFETY GLASS1-503 X 438SUPPLIED & FIT NEW TIMBER BEAD 1-440mmPLUS SILICONE & 10 NAILS USED
MSA-DTAG | WA5093402 | 1 | GPS Plumbing & Gas Services PtyLtd | ground - Male public toilet - Last cubical toilet blocked | Plumbing & Drainage | Water | 158.535 | Pass | Pass | 0 | 0 | 1.1667 | 2022-01-28 14:14 | 2022-01-31 17:00 | 2022-01-31 06:55 | 2022-01-31 17:00 | 2022-01-31 08:05 |  |  | Unblocked badly blocked cubicle full of tissues.
MSA-DTWD | WA5475994 | 2 | ACTION GLASS & ALUMINIUM | D006 - Broken window winder openers handle x 6 | Building | Windows | 351.25 | Pass | Pass | -1 | -1 | 1.1667 | 2022-05-25 09:51 | 2022-05-30 17:00 | 2022-05-26 13:40 | 2022-05-30 17:00 | 2022-05-26 14:50 |  |  | ATTENDED SITESUPPLIED & FIT 4 NEW WINDERS TO AWNING WINDOWS
MSA-DCA | WA6204010 | 1 | GPS Plumbing & Gas Services PtyLtd | Urinal is blocked - see notes | Plumbing & Drainage | Toilets/Cisterns | 131.09 | Pass | Pass | 0 | 0 | 1.1667 | 2022-11-17 08:38 | 2022-11-18 17:00 | 2022-11-17 13:40 | 2022-11-18 17:00 | 2022-11-17 14:50 |  |  | Unblocked level 1 urinals lhs and rhs both blocked.
MSA-DTAG | WA6461695 | 1 | SCAVENGER SUPPLIES PTY LTD | Level 1 - FIP panel displays 'communication failure' | Fire Protection Services | Fire Protection - Monitor System | 173.788 | Pass | Pass | 0 | 0 | 1.1667 | 2023-01-17 08:02 | 2023-01-18 17:00 | 2023-01-17 09:10 | 2023-01-18 17:00 | 2023-01-17 10:20
MSA-DTWD | WA6521660 | 2 | Water2water Pty Ltd | ZIP water filter not working - see notes | Plumbing & Drainage | Water | 444.275 | Pass | Pass | 0 | 0 | 1.1667 | 2023-01-30 12:18 | 2023-02-02 17:00 | 2023-02-02 15:10 | 2023-02-02 17:00 | 2023-02-02 16:20
MSA-DCA | WA4991183 | 2 | GPS Plumbing & Gas Services PtyLtd | Level one public male toilet – second basin tap is loose. | Plumbing & Drainage | Water | 190.04 | Fail | Fail | 1 | 1 | 1.1667 | 2022-01-04 16:20 | 2022-01-07 17:00 | 2022-01-13 07:50 | 2022-01-07 17:00 | 2022-01-13 09:00 |  |  | Replaced pan and adjusted pipework to suit new pan
MSA-DTWD | WA5018468 | 2 | Water2water Pty Ltd | External - D Block - water cooler faulty | Plumbing & Drainage | Water | 183.3475 | Pass | Pass | 0 | 0 | 1.1667 | 2022-01-14 11:51 | 2022-01-19 17:00 | 2022-01-18 07:50 | 2022-01-19 17:00 | 2022-01-18 09:00 |  |  | Fountain is working okay. Investigated installing bottle fillers to all the fountains on site. Quote to follow.
MSA-DFES | WA5030119 | 2 | Water2water Pty Ltd | Kitchen -Water filter in the kitchen is leaking- right hand sink | Building | Materials | 601.0775 | Pass | Pass | 0 | 0 | 1.1667 | 2022-01-16 13:35 | 2022-01-19 17:00 | 2022-01-18 12:00 | 2022-01-19 17:00 | 2022-01-18 13:10 |  |  | System leaking from different parts on arrival. Replaced complete system. Some parts are really old. Replaced system, parts and tubing. Connected system. Checked under pressure and flushed. Normal operation
MSA-DTWD | WA5094625 | 1 | Complete Pest Management Services | G Block - Ground - Workshop - Possum Urinating and dropping faeces | Pest Control | General Pest | 203.23 | Pass | Pass | 0 | 0 | 1.1667 | 2022-01-31 12:34 | 2022-02-01 17:00 | 2022-02-01 12:20 | 2022-02-01 17:00 | 2022-02-01 13:30 |  |  | Possums have been entering G Block for the past 4 years.Possum numbers appear to have been increasing over time.Possum faeces and urine is spread throughout G Block each day.Cleaners are unable to clean up the large quantities of faeces and urine each day leading to staff and students beingexposed and in contact with urine and faeces.A strong odour is present throughout G Block.Staff have expressed health concerns.Possums are climbing walls and gaining entry into workshops in multiple locations.Possums are entering roof voids and causing damage and mess.Urine stains are visible on ceiling tiles and stairway.Urine can be seen running down walls.Faeces is scattered across many floor surfaces.Attempting to possum proof affected areas may be an unrealistic undertaking.It is advised that an application be made to trap and relocate the possum population to a distance which will ensurethey do not return.
MSA-DTWD | WA5109327 | 3 | Water2water Pty Ltd | B6 - Level 3 - Fashion Corridor - Water filter needs changing | Plumbing & Drainage | Water | 438.3575 | Pass | Pass | -1 | -1 | 1.1667 | 2022-02-09 08:51 | 2022-02-16 17:00 | 2022-02-10 14:00 | 2022-02-16 17:00 | 2022-02-10 15:10 |  |  | Water fountain had no filter so installed new filter System Maxiflow Filter System A40142014S to resolve taste issues
MSA-DFES | WA5126262 | 2 | Water2water Pty Ltd | Kitchen - Hot water urn showing error and not operating as it should | Plumbing & Drainage | Water | 360.345 | Pass | Pass | 0 | 0 | 1.1667 | 2022-02-14 07:13 | 2022-02-16 17:00 | 2022-02-14 15:30 | 2022-02-16 17:00 | 2022-02-14 16:40 |  |  | Replaced inlet solenoid and level sensors
MSA-DTWD | WA5126692 | 0 | Securex Security Systems & Services | T Block - Ground -Security system not opening doors according to schedule - Doors do not open | Building | Automatic Doors | 336.98 | Pass | Pass | 0 | 0 | 1.1667 | 2022-02-14 09:33 | 2022-02-14 11:33 | 2022-02-14 10:50 | 2022-02-14 13:33 | 2022-02-14 12:00 |  |  | Ian Fouche (14/02/2022, 1050-1200) - Work NoteRoc FTC t block plugin module not responding. And software configuration issue when trying to do push configuration. Tried rebooting. I can ping it ok. The expander i/o expanders are working but everything on the controller. Bjs came earlier in the month and redownloaded software to system as lost software. They getting BJ systems out today as they have a controller onboard
MSA-DCA | WA5133798 | 2 | GPS Plumbing & Gas Services PtyLtd | Garden – Livingstone’s café - External garden tap not working and is worn out | Plumbing & Drainage | Water | 320.44 | Fail | Fail | 0 | 0 | 1.1667 | 2022-02-15 14:21 | 2022-02-18 17:00 | 2022-02-18 17:30 | 2022-02-18 17:00 | 2022-02-18 18:40 |  |  | Service and rewasher outside tap to Livingstone cafe.Had to turn the water supply to main area off.
MSA-DTWD | WA5297718 | 2 | Water2water Pty Ltd | A block - A 261 - Corridor outside A 261 - Drink fountain leaking | Plumbing & Drainage | Water | 183.3475 | Pass | Pass | 0 | 0 | 1.1667 | 2022-03-31 12:22 | 2022-04-05 17:00 | 2022-04-04 13:30 | 2022-04-05 17:00 | 2022-04-04 14:40 |  |  | FOUNTAIN IS LEAKING REALLY BADLY FROM MULTIPLE PLACES, COMPLETELY RUSTED UNDERNEATH. NEW FOUNTAIN REQUIRED TO BE INSTALLED.
MSA-DCA | WA5304088 | 2 | GPS Plumbing & Gas Services PtyLtd | Urban Orchard - Ground – external - Drink fountain between Urban Orchard and AGWA - see details | Plumbing & Drainage | Water | 158.535 | Pass | Pass | 0 | 0 | 1.1667 | 2022-04-04 14:32 | 2022-04-07 17:00 | 2022-04-05 11:50 | 2022-04-07 17:00 | 2022-04-05 13:00 |  |  | Cleaned areator and filter. Let the water run for few minutes to clear water from sand and other debris
MSA-DFES | WA5381028 | 0 | Go Doors | Roller Door dropped on top of the truck and stuck need to be fix ASAP so the truck can move | Electrical | General Electrical | 1080 | Pass | Pass | 0 | 0 | 1.1667 | 2022-04-25 18:09 | 2022-04-25 20:09 | 2022-04-25 19:20 | 2022-04-25 22:09 | 2022-04-25 20:30 |  |  | Completed
MSA-DTWD | WA5384028 | 0 | TK Elevator Australia Pty Ltd | Lift 2 - Lift is faulty | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.1667 | 2022-04-28 09:17 | 2022-04-28 11:17 | 2022-04-28 09:48 | 2022-04-28 13:17 | 2022-04-28 10:58 |  |  | Error codes: 2504, 4800, 0931.Lift on level 3 with doors open, lift cop buttons working but lop's wouldnt operate. Power cycled controller. Lift tested. Lift back in operation.work order to be closed out at $0 cost
MSA-DTWD | WA5400111 | 2 | LIGHTHOUSE LOCKSMITHS | Staff and Student Female toilets - 3 x locks on cubicles broken | Security | Locksmith | 212.2 | Pass | Pass | 0 | 0 | 1.1667 | 2022-05-10 07:43 | 2022-05-12 17:00 | 2022-05-10 09:50 | 2022-05-12 17:00 | 2022-05-10 11:00 |  |  | Replaced broken cubicle lock in student toilet and refit 2 other, all in E block
MSA-DCA | WA5473026 | 3 | GPS Plumbing & Gas Services PtyLtd | Mens Toilets - Men’s toilet, first floor, middle urinal. Water is continually running | Plumbing & Drainage | Toilets/Cisterns | 717.8775 | Pass | Pass | -1 | -1 | 1.1667 | 2022-05-24 12:24 | 2022-05-31 17:00 | 2022-05-27 09:11 | 2022-05-31 17:00 | 2022-05-27 10:21 |  |  | Replaced leaking latching valve to urinal level 1
MSA-DTWD | WA5477282 | 2 | ECO PLUMBING AND GAS PTY LTD | Grass area behind E-Block - There is a copper pipe sticking out of the ground with water slowly leak | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.1667 | 2022-05-25 12:39 | 2022-05-30 17:00 | 2022-05-27 13:20 | 2022-05-30 17:00 | 2022-05-27 14:30 |  |  | Capped off leaking pipe
MSA-DTWD | WA5499259 | 2 | Milners Tree Solutions Pty Ltd | G200 external - Large tree limb has fallen | Landscaping & Gardening | General Tree Works | 840 | Pass | Pass | 0 | 0 | 1.1667 | 2022-06-10 12:00 | 2022-06-15 17:00 | 2022-06-13 09:30 | 2022-06-15 17:00 | 2022-06-13 10:40 |  |  | FALLEN LIMB REMOVED
MSA-DTWD | WA5586670 | 2 | Dormakaba Australia Pty Ltd | Auto door will not closer shut-photo to follow in email | Building | Automatic Doors | 180 | Pass | Pass | -1 | -1 | 1.1667 | 2022-07-06 09:21 | 2022-07-11 17:00 | 2022-07-07 08:00 | 2022-07-11 17:00 | 2022-07-07 09:10 |  |  | Note new IP number 1153245, FAAC 415 swing gate bike store T Block. Programmed asset number A401301716.Arrived onsite and signed in, inspected gate and found motor torque weak which can stop the gate from closing, increased torque but not enough to crush when closing as there is no safety beam.
MSA-DTAG | WA5613632 | 2 | Gilmour & Jooste Electrical | Ground Level - Magistrates Chambers 2 -Phone port fault – Phone connection faulty -See notes below | Electrical | General Electrical | 194.505 | Pass | Pass | 0 | 0 | 1.1667 | 2022-07-14 14:18 | 2022-07-19 17:00 | 2022-07-19 07:00 | 2022-07-19 17:00 | 2022-07-19 08:10 |  |  | Fault found to be data outlet not patched in. Confirmed and tested wiring to ports #39 and #40. All in good working order.Repaired security light whilst on-site also.
MSA-DTWD | WA5673411 | 1 | CLEVELAND COMPRESSED AIR SERVICES | FT15 - Compressor blow back is causing water to blow out of P-Trap & run down the wall | Equipment | Compressors, Generators | 251.6 | Pass | Pass | 0 | 0 | 1.1667 | 2022-07-20 14:52 | 2022-07-21 17:00 | 2022-07-21 07:30 | 2022-07-21 17:00 | 2022-07-21 08:40 |  |  | The ball valve for the timed auto drain was fully open, causing the water to blow back up through the water trap. Closed the ball valve so it’s open a quarter of a turn. Water isn’t blowing back. The customer is going to extend the water trap
MSA-DFES | WA5681418 | 1 | SONTEC WA PTY LTD | Yard - Gate D007 (Gate#2) - Gate is inoperative - See notes below | Security | Access Control | 350 | Pass | Pass | 0 | 0 | 1.1667 | 2022-07-28 11:50 | 2022-07-29 17:00 | 2022-07-28 13:20 | 2022-07-29 17:00 | 2022-07-28 14:30 |  |  | 28/7/22 - Dylan ParslowInvestigated issues with vehicle gate not opening.No fault found with access control equipment.Found gate motor not operating on signal.Gate contractor required. Advised site.
MSA-DFES | WA5694013 | 1 | Water2water Pty Ltd | kitchen-instant HW system-Billi quadra this has been the 5 request no HW | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.1667 | 2022-08-05 07:22 | 2022-08-05 17:00 | 2022-08-05 15:15 | 2022-08-05 17:00 | 2022-08-05 16:25 |  |  | Re adjusted settings. Replace dispenser loom.
MSA-DFES | WA5696868 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - Upstairs Northern Firefighters Bathroom -The hot water coming from the taps are warm | Plumbing & Drainage | HWS/Units Electric & Gas | 194.28 | Pass | Pass | 0 | 0 | 1.1667 | 2022-08-08 16:00 | 2022-08-09 17:00 | 2022-08-09 07:20 | 2022-08-09 17:00 | 2022-08-09 08:30 |  |  | Arrived on site and singed in went to bathroom tested basin hot tap in room 35.5 degree but l noticed the pipe coming from the roof was not hot at all. Spoke to Sharon and explain to her what was going on they are going to organise an electrician to come out.
MSA-DTWD | WA5801387 | 2 | LIGHTHOUSE LOCKSMITHS | Repair lock to the elect switchboard and 6x replacement MKMM Keys | Security | Keys & Access | 612.2 | Pass | Pass | 0 | 0 | 1.1667 | 2022-08-31 16:09 | 2022-09-05 17:00 | 2022-09-02 09:30 | 2022-09-05 17:00 | 2022-09-02 10:40 |  |  | OPENED ELECTRICAL CUPBOARD IN R BLOCK AS 201 LOCK JAMMED, REPLACED KEYS ONSITE AS REQUIRED
MSA-DCA | WA5831360 | 1 | TK Elevator Australia Pty Ltd | Lift is not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.1667 | 2022-09-03 14:09 | 2022-09-05 17:00 | 2022-09-04 10:34 | 2022-09-05 17:00 | 2022-09-04 11:44 |  |  | Arrived on site and lift stopped on G floor, status - DTO ST although earliest event was an SE fault, tape head guides worn and on orderaswell as DO relay. Checked locks, all ok. Took details of SE circuit contacrors, U UX and L. Photos sent to TK. Cleared errors tightened all terminals on main contactors andreturned to service. Called away to SWP
MSA-DTWD | WA5838529 | 2 | Water2water Pty Ltd | Water Fountain - leaking water | Plumbing & Drainage | Water | 197.285 | Pass | Pass | 0 | 0 | 1.1667 | 2022-09-08 14:24 | 2022-09-13 17:00 | 2022-09-12 09:00 | 2022-09-13 17:00 | 2022-09-12 10:10 |  |  | Fixed issue with wasteline
MSA-DTWD | WA5976958 | 2 | Securex Security Systems & Services | Remove Broken Panic Alarm button | Security | Security Management System | 250 | Pass | Pass | 0 | 0 | 1.1667 | 2022-09-27 12:37 | 2022-09-30 17:00 | 2022-09-28 09:50 | 2022-09-30 17:00 | 2022-09-28 11:00 |  |  | 28/09/2022, 950-1100Removed duress button from system. Relocated keypad at clients request.
MSA-DTWD | WA5987072 | 2 | SENTINEL LOCK SERVICE PTY LTD | Room/Office G4 – X Ray Room-Door Lock Broken | Security | Locksmith | 455.37 | Pass | Pass | 0 | 0 | 1.1667 | 2022-10-03 07:24 | 2022-10-05 17:00 | 2022-10-04 11:30 | 2022-10-05 17:00 | 2022-10-04 12:40 |  |  | Room/office G4 - x ray room lock broken.Lock repaired - handles replaced.
MSA-DCA | WA6112577 | 0 | ACTION GLASS & ALUMINIUM | Big window broken need be boarded up - 2.4,mwide 4 m high | Glazing | Window Glass | 457.07 | Fail | Fail | 0 | 0 | 1.1667 | 2022-10-23 11:30 | 2022-10-23 13:30 | 2022-10-23 15:00 | 2022-10-23 15:30 | 2022-10-23 16:10 |  |  | ATTENDED SITE AFTER HOURSMEASURED & MADE SAFE BROKEN WINDOW4 SQM OF SAFETY FILM USED****spoke with Reese - he has advised to close this off for works done to date and we will send quote through for replacement***
MSA-DTWD | WA6125764 | 2 | Water2water Pty Ltd | D308 - Boiler unit fault in kitchen | Plumbing & Drainage | HWS/Units Electric & Gas | 197.285 | Pass | Pass | 0 | 0 | 1.1667 | 2022-10-25 08:14 | 2022-10-28 17:00 | 2022-10-28 13:20 | 2022-10-28 17:00 | 2022-10-28 14:30 |  |  | Unit working perfectly on site. Steve happy to monitor unit
MSA-DTWD | WA6144693 | 3 | Water2water Pty Ltd | Block K- outer workshop - Water drinking fountain inoperative | Plumbing & Drainage | Water | 250.745 | Pass | Pass | -1 | -1 | 1.1667 | 2022-11-02 08:38 | 2022-11-09 17:00 | 2022-11-02 15:50 | 2022-11-09 17:00 | 2022-11-02 17:00 |  |  | Replaced filter, fully sanitised as been inactive for long period. All now ok.
MSA-DTWD | WA6151738 | 0 | ACTION GLASS & ALUMINIUM | L102 - Broken window | Glazing | Window Glass | 409.145 | Pass | Pass | 0 | 0 | 1.1667 | 2022-11-07 08:38 | 2022-11-07 10:38 | 2022-11-07 09:20 | 2022-11-07 12:38 | 2022-11-07 10:30 |  |  | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-896 X 9554 L/M OF RUBBER REPLACED
MSA-DFES | WA6356883 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 8 Bathroom - Ground - Leaking toilet (see notes) | Plumbing & Drainage | Toilets/Cisterns | 229.5525 | Pass | Pass | 0 | 0 | 1.1667 | 2022-12-05 09:47 | 2022-12-08 17:00 | 2022-12-05 14:45 | 2022-12-08 17:00 | 2022-12-05 15:55 |  |  | Arrived on site and singed in went to Dorm 8 could see toilet was leaking out off back pan removed pan a replaced a 50mm kee seal and a cone pan rubber flushed toilet 5 times no water to be seen sillcone pan back cleaned up and everything is running fine
MSA-DCA | WA6358673 | 0 | ACTION GLASS & ALUMINIUM | Broken window | Building | Windows | 303.75 | Pass | Pass | 0 | 0 | 1.1667 | 2022-12-06 09:14 | 2022-12-06 11:14 | 2022-12-06 10:50 | 2022-12-06 13:14 | 2022-12-06 12:00 |  |  | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-413 X 2841.4 L/M OF PUTTY USED
MSA-DFES | WA6369813 | 2 | Dom's Total Grounds Maintenance | Entry Driveway garden bed along fence - Reticulation faulty - see notes below | Landscaping & Gardening | Grounds Maintenance | 260.5 | Pass | Pass | 0 | 0 | 1.1667 | 2022-12-14 09:11 | 2022-12-19 17:00 | 2022-12-19 09:35 | 2022-12-19 17:00 | 2022-12-19 10:45 |  |  | Call Out, Labour & Parts
MSA-MRWA | WA6404970 | 2 | Water2water Pty Ltd | Kitchenette - hot water urn is leaking | Plumbing & Drainage | Water | 351.705 | Pass | Pass | 0 | 0 | 1.1667 | 2023-01-09 10:39 | 2023-01-12 17:00 | 2023-01-11 11:05 | 2023-01-12 17:00 | 2023-01-11 12:15
MSA-DCA | WA6516590 | 1 | Critical Fire Protection & Training | Ground Floor - Vault exterior - Attend to faulty FM200 cylinder on fire protection system -see notes | Fire Protection Services | Fire Protection - Monitor System | 292.309 | Pass | Pass | 0 | 0 | 1.1667 | 2023-01-23 12:57 | 2023-01-24 17:00 | 2023-01-24 08:30 | 2023-01-24 17:00 | 2023-01-24 09:40
MSA-DFES | WA6522828 | 2 | Go Doors | Front Gate not closing properly - see notes | Security | Security Management System | 367.18 | Pass | Pass | 0 | 0 | 1.1667 | 2023-01-31 10:31 | 2023-02-03 17:00 | 2023-02-02 09:20 | 2023-02-03 17:00 | 2023-02-02 10:30
MSA-DCA | WA6540590 | 3 | GPS Plumbing & Gas Services PtyLtd | Laneway - Downpipe has been damaged. see notes | Plumbing & Drainage | Drainage | 343.9025 | Pass | Pass | 0 | 0 | 1.1667 | 2023-02-09 11:58 | 2023-02-16 17:00 | 2023-02-16 08:30 | 2023-02-16 17:00 | 2023-02-16 09:40
MSA-MRWA | WA6668635 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground floor - Ladies bathroom - Right cubicle - Toilet isnt flushing | Plumbing & Drainage | Toilets/Cisterns | 170.6025 | Pass | Pass | 0 | 0 | 1.1667 | 2023-02-22 10:47 | 2023-02-23 17:00 | 2023-02-22 12:05 | 2023-02-23 17:00 | 2023-02-22 13:15
MSA-DCA | WA4991664 | 2 | EQUANS Mechanical Services (WA) Pty Limited | HBRC - Terrestrial Invertebrates - Down flow pipes not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 554.65 | Pass | Pass | 0 | 0 | 1.1667 | 2022-01-05 10:51 | 2022-01-10 17:00 | 2022-01-07 16:25 | 2022-01-10 17:00 | 2022-01-07 17:35 |  |  | Attened site and carried out inspection of down flow works tables. Site FM Sue showed which ones were having issues on North side lads. EAF 5 was found to be showing operation but fan motor was not running. Carried out reset of VSD and confirmed fan operation restarted as normal. Issue is believed to be comms between VSD and run request input. Monitored equipment. All OK. Normal function resumed no further action required.
MSA-MRWA | WA5126639 | 1 | ADVANCED LOCK & KEY | Amenities- Ground -Kitchen - Door lock broken - unable to acces | Security | Locksmith | 330.08 | Pass | Pass | 0 | 0 | 1.1667 | 2022-02-14 09:15 | 2022-02-15 17:00 | 2022-02-14 13:55 | 2022-02-15 17:00 | 2022-02-14 15:05 |  |  | Sp3540-lssc Open and Replaced broken 590 strike with new SP3540-LSSC on kitchen door
MSA-DTAG | WA5151375 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Cleaning Utility Room - HWS not working as no hot water and both taps hard to turn off | Plumbing & Drainage | Water | 318.535 | Pass | Pass | -1 | -1 | 1.1667 | 2022-02-17 12:41 | 2022-02-22 17:00 | 2022-02-17 14:10 | 2022-02-22 17:00 | 2022-02-17 15:20 |  |  | Replaced leaking taps
MSA-DTWD | WA5291114 | 3 | AHS Services WA Pty Ltd (Anchor) | Tap to basin Disabled Toilet b Block runing | Plumbing & Drainage | Water | 135.01 | Pass | Pass | -1 | -1 | 1.1667 | 2022-03-25 15:17 | 2022-04-01 17:00 | 2022-03-28 07:57 | 2022-04-01 17:00 | 2022-03-28 09:07 |  |  | Replaced washer to disabled toilet taps on the ground floor b block
MSA-DTWD | WA5438111 | 2 | AHS Services WA Pty Ltd (Anchor) | Block West Male toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 286.1025 | Pass | Pass | 0 | 0 | 1.1667 | 2022-05-16 12:33 | 2022-05-19 17:00 | 2022-05-18 08:55 | 2022-05-19 17:00 | 2022-05-18 10:05 |  |  | Completed
MSA-DCA | WA5479550 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground Level - Staff Ladies toilet - Water leaking from cistern into toilet bowl – 1st cubicle as yo | Plumbing & Drainage | Toilets/Cisterns | 198.535 | Pass | Pass | 0 | 0 | 1.1667 | 2022-05-27 10:11 | 2022-06-03 17:00 | 2022-05-31 14:10 | 2022-06-03 17:00 | 2022-05-31 15:20 |  |  | Replaced outlet wahser abd lubricated mechanism
MSA-DCA | WA5513633 | 1 | ADVANCED LOCK & KEY | Level 3 - Gallery 7 - Grill lock needs repair | Security | Locksmith | 517.5 | Pass | Pass | 0 | 0 | 1.1667 | 2022-06-14 12:05 | 2022-06-15 17:00 | 2022-06-14 14:40 | 2022-06-15 17:00 | 2022-06-14 15:50 |  |  | Cut keys
MSA-DTAG | WA5800560 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Male Toilets - Cubicle 1 wont flush | Plumbing & Drainage | Toilets/Cisterns | 175.8125 | Pass | Pass | 0 | 0 | 1.1667 | 2022-08-31 10:56 | 2022-09-01 17:00 | 2022-08-31 11:40 | 2022-09-01 17:00 | 2022-08-31 12:50 |  |  | Replaced inlet valve to male toilet
MSA-DTAG | WA5833352 | 3 | Dormakaba Australia Pty Ltd | Ground floor - Main entrance - Draught excluder strip on auto entry doors detached from door frame | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 1.1667 | 2022-09-06 09:26 | 2022-09-13 17:00 | 2022-09-13 06:59 | 2022-09-13 17:00 | 2022-09-13 08:09 |  |  | Attended site and installed 2 x length of H track to bottoms of doors as per quote. Tested all fine. Left area clean and tidy
MSA-DCA | WA5976982 | 2 | GPS Plumbing & Gas Services PtyLtd | Backstage-Toilet cistern needs replacing as is not shutting off. -see notes | Plumbing & Drainage | Toilets/Cisterns | 222.6025 | Pass | Pass | 0 | 0 | 1.1667 | 2022-09-27 12:48 | 2022-09-30 17:00 | 2022-09-28 12:40 | 2022-09-30 17:00 | 2022-09-28 13:50 |  |  | Replaced faulty inlet valve and ministop
MSA-MRWA | WA6148899 | 2 | Water2water Pty Ltd | Kitchenette-Hot Water unit leaking | Plumbing & Drainage | Water | 126.89 | Pass | Pass | 0 | 0 | 1.1667 | 2022-11-04 10:12 | 2022-11-09 17:00 | 2022-11-08 11:10 | 2022-11-09 17:00 | 2022-11-08 12:20 |  | WACCES | TECH CLEANED AND REPAIRED SYSTEM TANK TEMPERATURE PROBE GASKET/SEAL. SITE TO MONITOR.
MSA-DTAG | WA6407654 | 2 | Water2water Pty Ltd | Level 10 - Coroners Court Kitchen - Hot water function on zip not working - See Notes | Plumbing & Drainage | Water | 418.785 | Pass | Pass | 0 | 0 | 1.1667 | 2023-01-10 10:31 | 2023-01-13 17:00 | 2023-01-11 12:40 | 2023-01-13 17:00 | 2023-01-11 13:50
MSA-DTWD | WA6529103 | 1 | De.mem-Capic Pty Ltd | Investigate water loss from water treatment cooling tower | Air Conditioning | Room Air Conditioners | 114.333 | Pass | Pass | 0 | 0 | 1.1667 | 2023-02-02 14:36 | 2023-02-03 17:00 | 2023-02-02 14:40 | 2023-02-03 17:00 | 2023-02-02 15:50
MSA-DCA | WA4991179 | 2 | GPS Plumbing & Gas Services PtyLtd | Level one public male toilet – disabled cubicle cistern faulty. | Plumbing & Drainage | Water | 246.535 | Pass | Pass | 0 | 0 | 1.15 | 2022-01-04 16:09 | 2022-01-07 17:00 | 2022-01-06 09:31 | 2022-01-07 17:00 | 2022-01-06 10:40 |  |  | Replaced inlet valve and fixed broken mechanism
MSA-DTWD | WA5695992 | 1 | Dormakaba Australia Pty Ltd | B/block disable toilets auto door not working | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 1.15 | 2022-08-08 08:54 | 2022-08-09 17:00 | 2022-08-08 10:20 | 2022-08-09 17:00 | 2022-08-08 11:29 |  |  | Arrived on site on found UAT swing door mag lock was hanging loose. The bracket on the under side was also loose as it was only secured with one screw so I took mag lock off so I could secure the bracket with another fixing. Plate on the door face was not engaging so I had to add another washer for the pin to able to pull in. (Photos attached). Door left in operation with mag lock engaging.
MSA-DTWD | WA5570806 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block SK2 R/H sink 1 leaking | Plumbing & Drainage | Water | 126.49 | Pass | Pass | 0 | 0 | 1.15 | 2022-06-28 15:06 | 2022-07-01 17:00 | 2022-06-29 08:21 | 2022-07-01 17:00 | 2022-06-29 09:30 |  |  | Job completed
MSA-DCA | WA5727698 | 1 | Dormakaba Australia Pty Ltd | Stalls Foyer Accessible Toilet - Door is not responding - see notes below | Building | Automatic Doors | 351.95 | Pass | Pass | 0 | 0 | 1.15 | 2022-08-15 11:23 | 2022-08-16 17:00 | 2022-08-15 13:11 | 2022-08-16 17:00 | 2022-08-15 14:20 |  |  | On inspection, found unit in no mode due to multiple faults. Cleared all faults, adjusted safety sensor and reset unit. Tested unit, all ok.
MSA-DTWD | WA5835982 | 3 | Dormakaba Australia Pty Ltd | Francis St entry - Faulty auto door - door guide broken | Building | Automatic Doors | 206.95 | Pass | Pass | -1 | -1 | 1.15 | 2022-09-07 09:31 | 2022-09-14 17:00 | 2022-09-07 13:47 | 2022-09-14 17:00 | 2022-09-07 14:56 |  |  | Found that the part that had dislodged was a door stop attached to the beam. Reattached the stop, tested and all working fine now. Left area clean and tidy.
MSA-DCA | WA5838527 | 3 | GPS Plumbing & Gas Services PtyLtd | Third floor staff kitchenette (by toilets) - basin tap dripping | Plumbing & Drainage | Water | 143.3 | Pass | Pass | 0 | 0 | 1.15 | 2022-09-08 14:22 | 2022-09-15 17:00 | 2022-09-13 10:47 | 2022-09-15 17:00 | 2022-09-13 11:56 |  |  | Replaced 2 tap washers hot and cold and replaced arerator
MSA-DTWD | WA6430848 | 2 | AHS Services WA Pty Ltd (Anchor) | East Ladies toilets - Tap Handles seized see notes | Plumbing & Drainage | Water | 168.8175 | Pass | Pass | 0 | 0 | 1.15 | 2023-01-13 09:32 | 2023-01-18 17:00 | 2023-01-16 07:25 | 2023-01-18 17:00 | 2023-01-16 08:34
MSA-DCA | WA6537524 | 1 | GPS Plumbing & Gas Services PtyLtd | Star Dressing Room - Tap for filling toilet cistern does not work | Plumbing & Drainage | Toilets/Cisterns | 242.6025 | Pass | Pass | 0 | 0 | 1.15 | 2023-02-07 09:47 | 2023-02-08 17:00 | 2023-02-08 08:30 | 2023-02-08 17:00 | 2023-02-08 09:39
MSA-DTWD | WA5297725 | 2 | AHS Services WA Pty Ltd (Anchor) | A-Block 1st Floor East Ladies toilets , toilet leaking at floor | Plumbing & Drainage | Toilets/Cisterns | 133.2375 | Pass | Pass | 0 | 0 | 1.1333 | 2022-03-31 12:27 | 2022-04-05 17:00 | 2022-04-04 14:07 | 2022-04-05 17:00 | 2022-04-04 15:15 |  |  | Completed
MSA-DTWD | WA5407480 | 2 | Dormakaba Australia Pty Ltd | T Block - 2nd Floor - West end of Passage - Glass auto door Beeps every 30 mins | Building | Automatic Doors | 304.1 | Pass | Pass | -1 | -1 | 1.1333 | 2022-05-11 12:03 | 2022-05-16 17:00 | 2022-05-11 14:54 | 2022-05-16 17:00 | 2022-05-11 16:02 |  |  | 11/5/22 - Door was beeping due to low batteries. Replaced batteries and tested. All good.13/5/22 - 1091058. Call to site. On arrival battery alarm was active. Check mains and battery backup (all okay). Complete fresh learn cycle and test run for 30mins - unit alarmed again. Please provide quotation to revisit and install a new controller to resolve battery alarm fault. De-energise unit as requested by Sue
MSA-DTAG | WA6107932 | 2 | Water2water Pty Ltd | Basement - Security Kitchen - Water being dispensed from the HWU has a strange taste - See notes | Plumbing & Drainage | Water | 494.795 | Pass | Pass | -1 | -1 | 1.1333 | 2022-10-20 09:21 | 2022-10-25 17:00 | 2022-10-20 10:15 | 2022-10-25 17:00 | 2022-10-20 11:23 |  |  | Installed new maxiflow system scale to rheem unit and flushed system.
MSA-DTWD | WA5596672 | 1 | Dormakaba Australia Pty Ltd | Ground Floor - Entry east corridor - Auto door will not operate on any level - See notes below | Building | Automatic Doors | 449.63 | Pass | Pass | 0 | 0 | 1.1333 | 2022-07-11 09:46 | 2022-07-12 17:00 | 2022-07-11 16:06 | 2022-07-12 17:00 | 2022-07-11 17:14 |  |  | Assert tag for this door is 1064275. Attended site and found door was in mode switch error. On testing found lock board to be faulty, replaced board, tested and all working fine now left area clean and tidy.
MSA-DCA | WA4991834 | 0 | GPS Plumbing & Gas Services PtyLtd | Seating area opposite Q block - water fountain jammed on constantly | Plumbing & Drainage | Water | 190.245 | Pass | Pass | 0 | 0 | 1.1333 | 2022-01-05 12:47 | 2022-01-05 14:47 | 2022-01-05 14:22 | 2022-01-05 16:47 | 2022-01-05 15:30 |  |  | Service drink fountain bubbler
MSA-MRWA | WA5094182 | 2 | Water2water Pty Ltd | Alfresco area - Ice machine not working correctly | Plumbing & Drainage | Water | 277.8975 | Pass | Pass | 0 | 0 | 1.1333 | 2022-01-31 09:04 | 2022-02-03 17:00 | 2022-02-02 07:52 | 2022-02-03 17:00 | 2022-02-02 09:00 |  |  | replaced blocked filter on maxiflow system - checked ice machine reactivated ok
MSA-DTAG | WA5838101 | 1 | Schindler Lifts Australia | Lift 2 is not responding to carriage buttons | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.1333 | 2022-09-08 10:55 | 2022-09-09 17:00 | 2022-09-08 14:05 | 2022-09-09 17:00 | 2022-09-08 15:13 |  |  | Button on 2 a replaced Lift requires two tech to fix lock issue Will return with second tech to complete
MSA-DFES | WA6676566 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Toilet sytem are blocked | Plumbing & Drainage | Toilets/Cisterns | 194.28 | Pass | Pass | 0 | 0 | 1.1333 | 2023-02-28 14:58 | 2023-02-28 16:58 | 2023-02-28 15:52 | 2023-02-28 18:58 | 2023-02-28 17:00
MSA-DTWD | WA4992563 | 2 | MR POTHOLE | B16 Staff Room external road /path access -Uneven trip hazard in a section of road Bitumen/ concret | Paving & Roadworks | Concreting |  | Fail | Fail | 2 | 2 | 1.1167 | 2022-01-06 13:26 | 2022-01-11 17:00 | 2022-01-25 11:20 | 2022-01-11 17:00 | 2022-01-25 12:27 |  |  | job completed - Site inspected and works completed by Mr Pothole crew on 25/01/2022
MSA-DTAG | WA5089799 | 3 | Sapio Pty Ltd | Custody - Issue with the upper custody staircase duress - see notes below | Security | Monitoring | 130 | Pass | Pass | -1 | -1 | 1.1167 | 2022-01-25 06:35 | 2022-02-01 17:00 | 2022-01-27 08:25 | 2022-02-01 17:00 | 2022-01-27 09:32
MSA-DTAG | WA5304639 | 0 | Gilmour & Jooste Electrical | Courtside - Ground - Court 2 - Lights completely out in Court 2 | Electrical | Lighting, Internal | 129.67 | Pass | Pass | 0 | 0 | 1.1167 | 2022-04-05 08:51 | 2022-04-05 10:51 | 2022-04-05 09:45 | 2022-04-05 12:51 | 2022-04-05 10:52 |  |  | Reset tripped us today for lights in court room two. Tested lights all in working order
MSA-MRWA | WA5518697 | 1 | TK Elevator Australia Pty Ltd | Level 5 - Elevator 3 & 4 - Completely stuck on level 5 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.1167 | 2022-06-15 08:23 | 2022-06-16 17:00 | 2022-06-15 09:12 | 2022-06-16 17:00 | 2022-06-15 10:19 |  |  | Lift3 DAC-Geared :Trace for fault, found rope brake bode board yellow led blinking 2 times. There is no air in compressor tank. Found compressor circuit breaker in off position. Turned on circuit breaker , compressor starts to run. Lift 3 & 4 starts to run also. Monitor lifts running ok. Put lift back on service.to be closed out at $0 cost
MSA-DFES | WA5835741 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Workshop - Mens Toilet - urinal constantly running | Plumbing & Drainage | Toilets/Cisterns | 437.18 | Pass | Pass | 0 | 0 | 1.1167 | 2022-09-07 09:31 | 2022-09-08 17:00 | 2022-09-08 07:53 | 2022-09-08 17:00 | 2022-09-08 09:00 |  |  | Arrived on site and singed in went to Staff toilets and replaced a urinal cistern in toilets in workshop had to go to Reece and pick up
MSA-DTWD | WA6184762 | 2 | AHS Services WA Pty Ltd (Anchor) | S209 - Leaking Basin Tap | Plumbing & Drainage | Water | 146.088 | Pass | Pass | 0 | 0 | 1.1167 | 2022-11-15 15:30 | 2022-11-18 17:00 | 2022-11-18 09:39 | 2022-11-18 17:00 | 2022-11-18 10:46 |  |  | Checked basin wasn’t leaking rang Brett from facilities and asked if info was correct it was and he was happy that I’d called to check
MSA-DTWD | WA6526963 | 2 | AHS Services WA Pty Ltd (Anchor) | Male toilets - A126 - Urinal not flushing | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | -1 | -1 | 1.1167 | 2023-02-01 12:19 | 2023-02-06 17:00 | 2023-02-02 09:30 | 2023-02-06 17:00 | 2023-02-02 10:37
MSA-DTAG | WA6671701 | 1 | GPS Plumbing & Gas Services PtyLtd | Plant room 7 (near court 8) - Water leaking due to blocked drain | Plumbing & Drainage | Drainage | 258.9025 | Pass | Pass | 0 | 0 | 1.1167 | 2023-02-23 10:00 | 2023-02-24 17:00 | 2023-02-24 08:10 | 2023-02-24 17:00 | 2023-02-24 09:17
MSA-DCA | WA5087973 | 1 | GPS Plumbing & Gas Services PtyLtd | Last Cubicle - water leaking into the cubicle | Plumbing & Drainage | Water | 240.5975 | Pass | Pass | 0 | 0 | 1.1167 | 2022-01-24 16:03 | 2022-01-25 17:00 | 2022-01-25 11:03 | 2022-01-25 17:00 | 2022-01-25 12:10 |  |  | Checked leak into level 1 female toilet.Found 2nd cubicle female toilet level 2 China cistern is cracked and leaking onto the floor.Isolated and made safe. Advised to close off work order as new one will be raised under LVM
MSA-MRWA | WA5462086 | 2 | TK Elevator Australia Pty Ltd | Lift 1- Level 4- Up light remains luminated | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1.1 | 2022-05-19 11:08 | 2022-05-24 17:00 | 2022-05-19 12:41 | 2022-05-24 17:00 | 2022-05-19 13:47 |  |  | Lift 1 level 4 up direction always on. Found landing relay driver board faulty. Disconnected up direction output so lamp does not light. Informed building management of this and that a replacement board will be ordered.To be closed out at $0 cost
MSA-DTAG | WA5676514 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 -Youth Justice- Water penetrations above ceiling space | Plumbing & Drainage | Water | 170.6025 | Pass | Pass | 0 | 0 | 1.1 | 2022-07-25 09:05 | 2022-07-28 17:00 | 2022-07-25 12:32 | 2022-07-28 17:00 | 2022-07-25 13:38 |  |  | Inspected ceiling. No water pipes located in the cdiling space. Roof sheet isolation completely soaked. Different contractor required. Ian advised
MSA-DCA | WA5789590 | 0 | TK Elevator Australia Pty Ltd | public lift stuck on level 1 not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.1 | 2022-08-21 13:23 | 2022-08-21 15:23 | 2022-08-21 14:56 | 2022-08-21 17:23 | 2022-08-21 16:02 |  |  | On arrival lift at top floor with doors closed.Found tank slightly hot,Faults. Op mode dtc,op mode dcp ,Suspect doors trying to close and couldnt.Check top floor doors, car doors and operator.Ran lift and left in service.
MSA-DTAG | WA5795409 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Ladies Toilet - Cubicle 1 the flush button is broken | Plumbing & Drainage | Toilets/Cisterns | 156.09 | Pass | Pass | 0 | 0 | 1.1 | 2022-08-25 12:02 | 2022-08-26 17:00 | 2022-08-26 07:49 | 2022-08-26 17:00 | 2022-08-26 08:55 |  |  | Lubricated red ring washer, replaced spring mechanism, and reattached button back to the plate
MSA-DTAG | WA6379260 | 1 | Australian HVAC Services Pty. Ltd. | Ground - Courtroom 6 - Airconditioning is too hot | Air Conditioning | Room Air Conditioners | 407.39 | Pass | Pass | 0 | 0 | 1.1 | 2022-12-19 10:23 | 2022-12-20 17:00 | 2022-12-19 10:24 | 2022-12-20 17:00 | 2022-12-19 11:30 |  |  | Attend site. Check operation of AC serving courts. Found whole building warm. Found 3 chillers running and working as normal. Found all Fan Coil unit to be calling for 100% chilled water valve. Due to the warm weekend there was a high heat load in the building. Adjust schedule for plant to start 3am Monday morning. Monitor operation and found temp to slowly drop throughout the courts. Lower chiller chilled water supply srtpoint to 7 degrees. Adjust weekly schedules to combat hot week. All plant working as normal.
MSA-DTAG | WA5513846 | 1 | Gilmour & Jooste Electrical | Jury Services Room – Kitchen (room 216) - Fridge and Microwave not working -PowerPoint/circuit issue | Electrical | General Electrical | 162.1 | Pass | Pass | 0 | 0 | 1.1 | 2022-06-14 13:44 | 2022-06-15 17:00 | 2022-06-15 08:51 | 2022-06-15 17:00 | 2022-06-15 09:57 |  |  | Inspected faulty power. Found faulty urn. Removed appliance. Reset RCD. All in good working order.
MSA-DTAG | WA6359387 | 2 | AHS Services WA Pty Ltd (Anchor) | Registry Kitchen - Tap leaking from under tap body | Plumbing & Drainage | Water | 172.07 | Fail | Fail | 1 | 1 | 1.1 | 2022-12-06 15:18 | 2022-12-09 17:00 | 2022-12-14 15:00 | 2022-12-09 17:00 | 2022-12-14 16:06 |  |  | Picked up and replaced faucet in kitchen
MSA-DCA | WA6403498 | 1 | TK Elevator Australia Pty Ltd | Loud noise with accompanying vibrations coming from lift motor room (see notes) | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 1.1 | 2023-01-06 10:59 | 2023-01-09 17:00 | 2023-01-06 12:51 | 2023-01-09 17:00 | 2023-01-06 13:57
MSA-DCA | WA6408121 | 2 | GPS Plumbing & Gas Services PtyLtd | BOH Men’s Toilets Cubicle 1 - Flush button not working - See Notes Below | Plumbing & Drainage | Toilets/Cisterns | 170.6025 | Pass | Pass | 0 | 0 | 1.1 | 2023-01-10 14:54 | 2023-01-13 17:00 | 2023-01-11 09:24 | 2023-01-13 17:00 | 2023-01-11 10:30
MSA-DCA | WA6414813 | 2 | GPS Plumbing & Gas Services PtyLtd | Bathroom with all cubicles - Toilet leaking | Plumbing & Drainage | Toilets/Cisterns | 218.6025 | Pass | Pass | -1 | -1 | 1.1 | 2023-01-11 10:08 | 2023-01-16 17:00 | 2023-01-12 15:20 | 2023-01-16 17:00 | 2023-01-12 16:26
MSA-DCA | WA6522612 | 3 | SCAVENGER SUPPLIES PTY LTD | Ground floor - FIP - Fire Alarm Fault - Fire Zone 32 - See notes | Fire Protection Services | Fire Protection - Monitor System | 187.97 | Pass | Pass | -1 | -1 | 1.1 | 2023-01-31 09:03 | 2023-02-07 17:00 | 2023-02-01 07:10 | 2023-02-07 17:00 | 2023-02-01 08:16
MSA-DTAG | WA6674508 | 1 | GPS Plumbing & Gas Services PtyLtd | Detention - Cell 4 - Toilet flushing button not working (please attend early tomorrow at 6:30am) | Plumbing & Drainage | Toilets/Cisterns | 352.6025 | Pass | Pass | 0 | 0 | 1.1 | 2023-02-27 10:28 | 2023-02-28 17:00 | 2023-02-28 06:22 | 2023-02-28 17:00 | 2023-02-28 07:28
MSA-DTWD | WA5295427 | 2 | Water2water Pty Ltd | B Block - B16 - No water from the chiller unit under sink | Plumbing & Drainage | Water | 336.7075 | Pass | Pass | 0 | 0 | 1.1 | 2022-03-29 13:26 | 2022-04-01 17:00 | 2022-03-31 14:55 | 2022-04-01 17:00 | 2022-03-31 16:01 |  |  | Reset leak detector. Replaced filter as wasn’t sealing to the head correctly causing a leak.
MSA-DTAG | WA6154695 | 2 | GPS Plumbing & Gas Services PtyLtd | Upstairs – 1 - Male Toilet - Male toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 482.89 | Pass | Pass | 0 | 0 | 1.1 | 2022-11-07 15:46 | 2022-11-10 17:00 | 2022-11-09 13:14 | 2022-11-10 17:00 | 2022-11-09 14:20 |  |  | Replaced flush button, cleaned inlet valve
MSA-DFES | WA5522450 | 3 | Dom's Total Grounds Maintenance | Lower Car Park - Epsom Av Fence - trees have broken in the wind | Landscaping & Gardening | General Tree Works | 357.5 | Pass | Pass | 0 | 0 | 1.0833 | 2022-06-15 16:19 | 2022-06-22 17:00 | 2022-06-19 12:50 | 2022-06-22 17:00 | 2022-06-19 13:55 |  |  | Call Out, Labour & Large Greenwaste Removal
MSA-DTAG | WA5692256 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - Public Ladies Toilet - The push button in the first cubical is stuck- See notes | Plumbing & Drainage | Water | 266.1025 | Pass | Pass | -1 | -1 | 1.0833 | 2022-08-03 11:32 | 2022-08-10 17:00 | 2022-08-05 07:35 | 2022-08-10 17:00 | 2022-08-05 08:40 |  |  | Replaced faulty bellows
MSA-DCA | WA5796695 | 3 | Dormakaba Australia Pty Ltd | Level 1 - Stage Door - Reception shutter has fault. Roller mechanism not working | Building | Roller Shutters | 220 | Pass | Pass | -1 | -1 | 1.0833 | 2022-08-26 12:49 | 2022-09-02 17:00 | 2022-08-26 15:05 | 2022-09-02 17:00 | 2022-08-26 16:10 |  |  | Door had lost some tension. Retentioned door and tested. All good.
MSA-DCA | WA5888032 | 1 | GPS Plumbing & Gas Services PtyLtd | No hot water from Stiebel Eltron unit PFM asset number A40035155C | Plumbing & Drainage | HWS/Units Electric & Gas | 170.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2022-09-16 12:02 | 2022-09-19 17:00 | 2022-09-16 13:05 | 2022-09-19 17:00 | 2022-09-16 14:10 |  |  | Hot water system working. Turned power back on
MSA-DCA | WA6722015 | 2 | GPS Plumbing & Gas Services PtyLtd | Smell coming from taps when turned on | Plumbing & Drainage | Drainage | 170.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2023-03-14 14:01 | 2023-03-17 17:00 | 2023-03-15 13:05 | 2023-03-17 17:00 | 2023-03-15 14:10
MSA-MRWA | WA4992656 | 1 | GPS Plumbing & Gas Services PtyLtd | Male Toilets - Right hand side toilets is constantly running | Plumbing & Drainage | Toilets/Cisterns | 293.535 | Pass | Pass | 0 | 0 | 1.0833 | 2022-01-06 15:00 | 2022-01-07 17:00 | 2022-01-06 16:15 | 2022-01-07 17:00 | 2022-01-06 17:20 |  |  | Cleaned and lubricated outlet valve. Replaced faulty bellow.
MSA-DTAG | WA5303676 | 1 | OCS SERVICES PTY LTD | Level 6 - Prisoners Review Board - see notes below | Cleaning | Emergency Cleans |  | Pass | Pass | 0 | 0 | 1.0833 | 2022-04-04 11:53 | 2022-04-05 17:00 | 2022-04-05 11:55 | 2022-04-05 17:00 | 2022-04-05 13:00 |  |  | Covid clean
MSA-DTWD | WA5312422 | 2 | AHS Services WA Pty Ltd (Anchor) | Back of Workshops - broken tap on newly installed drink trough | Plumbing & Drainage | Water | 163.2275 | Pass | Pass | 0 | 0 | 1.0833 | 2022-04-11 13:39 | 2022-04-14 17:00 | 2022-04-13 10:30 | 2022-04-14 17:00 | 2022-04-13 11:35 |  |  | Completed
MSA-DTAG | WA5380214 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Toilets - upstairs - First female toilet, the seat needs to be adjusted | Plumbing & Drainage | Toilets/Cisterns | 278.535 | Pass | Pass | -1 | -1 | 1.0833 | 2022-04-22 09:23 | 2022-04-28 17:00 | 2022-04-22 15:40 | 2022-04-28 17:00 | 2022-04-22 16:45 |  |  | Tightened seats. Replaced toggle kits on the lhs seat
MSA-DCA | WA5395631 | 2 | Techworks Electrical | Level 2 - Internal Stairwell - BOH - Light fitting loose, light will not turn on | Electrical | Lighting, Internal | 297.93 | Pass | Pass | -1 | -1 | 1.0833 | 2022-05-05 14:28 | 2022-05-10 17:00 | 2022-05-06 12:30 | 2022-05-10 17:00 | 2022-05-06 13:35 |  |  | Inspected light out, found it to be faulty. Sourced replacement, returned to site and replaced
MSA-DTWD | WA5401140 | 1 | Milners Tree Solutions Pty Ltd | Carpark 1 Large dead tree in staff parking area | Landscaping & Gardening | General Tree Works | 1000 | Fail | Fail | 0 | 0 | 1.0833 | 2022-05-10 16:55 | 2022-05-11 17:00 | 2022-05-12 06:30 | 2022-05-11 17:00 | 2022-05-12 07:35 |  |  | tree removed and stump grinding
MSA-DCA | WA5437926 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground level - Female Toilet in theatre foyer - 2nd basin tap is damaged | Plumbing & Drainage | Water | 856.7 | Fail | Fail | 0 | 0 | 1.0833 | 2022-05-16 11:36 | 2022-05-19 17:00 | 2022-05-20 13:15 | 2022-05-19 17:00 | 2022-05-20 14:20 |  |  | Replaced middle mixer in female toilet ground floor public foyer
MSA-DCA | WA5587975 | 1 | GPS Plumbing & Gas Services PtyLtd | Toilet will not stop flushing | Plumbing & Drainage | Toilets/Cisterns | 218.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2022-07-07 12:11 | 2022-07-08 17:00 | 2022-07-07 14:10 | 2022-07-08 17:00 | 2022-07-07 15:15 |  |  | Replaced inlet vakve on the 2nd cubicle. Job delayed as there was no parking around the building. Toilets on mezzanine floor male toilet not leaking. All working fine. Replaced inlet valve as in y opinion was playing up a bit. Unable to get staff to tell me precisely which cubicle was leaking
MSA-MRWA | WA5673462 | 0 | GPS Plumbing & Gas Services PtyLtd | brust pipe | Plumbing & Drainage | Water | 316.8825 | Pass | Pass | 0 | 0 | 1.0833 | 2022-07-20 15:50 | 2022-07-20 17:50 | 2022-07-20 16:00 | 2022-07-20 19:50 | 2022-07-20 17:05 |  |  | Repaired burst pipe
MSA-DTAG | WA5674141 | 1 | SONTEC WA PTY LTD | ground throughout-CCTV is not working throughout the facility | Security | CCTV Surveillance | 350 | Pass | Pass | 0 | 0 | 1.0833 | 2022-07-21 09:18 | 2022-07-22 17:00 | 2022-07-21 13:10 | 2022-07-22 17:00 | 2022-07-21 14:15 |  |  | 21/7/22 - Dylan ParslowFound main server offline. Reset.One PC in security office set to DHCP, programmed static ip and tested.All ok.
MSA-DTWD | WA5676367 | 2 | Swan Pest Control | corridor and external area. New rodent baiting required | Pest Control | General Pest | 279.75 | Pass | Pass | 0 | 0 | 1.0833 | 2022-07-25 08:03 | 2022-07-28 17:00 | 2022-07-28 11:00 | 2022-07-28 17:00 | 2022-07-28 12:05 |  |  | Installed 7 large rodent boxes to corridor of E-Block21 Ditrac Blocks
MSA-DTWD | WA5688007 | 1 | Milners Tree Solutions Pty Ltd | External To D Block - Fallen tree needs to be removed - Blocking exit gate | Landscaping & Gardening | Tree Lopping | 520 | Pass | Pass | 0 | 0 | 1.0833 | 2022-08-02 09:12 | 2022-08-03 17:00 | 2022-08-02 09:25 | 2022-08-03 17:00 | 2022-08-02 10:30 |  |  | fallen limb cut off fence and from tree. set aside for collection. made safe. Returned 04082022 debris had been removed
MSA-MRWA | WA5696816 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 6 - Female Bathroom - Right hand side cubicle is leaking when flushed | Plumbing & Drainage | Toilets/Cisterns | 319.0625 | Pass | Pass | 0 | 0 | 1.0833 | 2022-08-08 14:55 | 2022-08-09 17:00 | 2022-08-09 08:10 | 2022-08-09 17:00 | 2022-08-09 09:15 |  |  | Uninstalled leaking toilet, replaced faulty seals(kee seal and pan rubber, reinstalled toilet. Toilet flushed multiple times. Not leaking any more. Silicone applied around the pan. Therefore it can not be used for 24h. Left sign on the door.
MSA-DTWD | WA5735744 | 3 | ADVANCED LOCK & KEY | Replace/repair broken Barrel to lock inside B301 | Security | Locksmith | 717.96 | Fail | Fail | 2 | 2 | 1.0833 | 2022-08-16 15:07 | 2022-08-23 17:00 | 2022-09-09 15:40 | 2022-08-23 17:00 | 2022-09-09 16:45 |  |  | changed everything to make internal room B301 lockable
MSA-DCA | WA5834144 | 2 | TK Elevator Australia Pty Ltd | Lift 7 - Replace broken emergency switch key mechanism | Lifts | Lifts | 590 | Fail | Fail | 1 | 1 | 1.0833 | 2022-09-06 14:18 | 2022-09-09 17:00 | 2022-09-13 07:32 | 2022-09-09 17:00 | 2022-09-13 08:37 |  |  | Replaced the broken security key switch(9000) security keyswitch located in the lift c.o.p(left hand side facing towards the lift) is now back in service
MSA-DTAG | WA5978413 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - Visiting Judge’s Chamber - Leaking toilet – See notes below | Plumbing & Drainage | Toilets/Cisterns | 170.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2022-09-28 10:42 | 2022-09-29 17:00 | 2022-09-28 11:25 | 2022-09-29 17:00 | 2022-09-28 12:30 |  |  | Inspected possible leak in the toilet. Unable to find the cause of the water leak. No actions taken. Flushed toilet multiple time and run basin for severalMinuts.
MSA-MRWA | WA5987387 | 1 | GPS Plumbing & Gas Services PtyLtd | Basement Male toilet - Constantly running | Plumbing & Drainage | Toilets/Cisterns | 294.3225 | Pass | Pass | 0 | 0 | 1.0833 | 2022-10-03 11:20 | 2022-10-04 17:00 | 2022-10-03 13:15 | 2022-10-04 17:00 | 2022-10-03 14:20 |  |  | Replaced fulty outlet valve
MSA-DFES | WA6023017 | 1 | Water2water Pty Ltd | Kitchen - Billi System - no hot water | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1.0833 | 2022-10-14 14:37 | 2022-10-17 17:00 | 2022-10-14 16:30 | 2022-10-17 17:00 | 2022-10-14 17:35 |  |  | Hot pump failure. Replaced, everything working to specs CLAIMED AS A WARRANTY ON BEHALF OF CLIENT SO NO CHARGE PLEASE CLOSE OUT AND TAKE OFF PROMAP CLOSED.
MSA-DTWD | WA6074464 | 2 | Australian Airconditioning Services Pty Ltd | Evap AC unit constantly dumping water | Air Conditioning | Room Air Conditioners | 228.65 | Pass | Pass | 0 | 0 | 1.0833 | 2022-10-18 09:40 | 2022-10-21 17:00 | 2022-10-18 09:40 | 2022-10-21 17:00 | 2022-10-18 10:45 |  |  | complete
MSA-DCA | WA6373519 | 2 | GPS Plumbing & Gas Services PtyLtd | BOH Men’s Toilets Cubicle 1-, flush button not working, water apparently running-see notes | Plumbing & Drainage | Toilets/Cisterns | 256.1125 | Pass | Pass | 0 | 0 | 1.0833 | 2022-12-14 14:52 | 2022-12-19 17:00 | 2022-12-16 14:30 | 2022-12-19 17:00 | 2022-12-16 15:35 |  |  | Replaced fsulty outlet valve
MSA-MRWA | WA6393349 | 2 | GPS Plumbing & Gas Services PtyLtd | Female bathroom - LHS toilet won't flush | Plumbing & Drainage | Toilets/Cisterns | 226.3125 | Pass | Pass | 0 | 0 | 1.0833 | 2022-12-28 12:48 | 2023-01-03 17:00 | 2023-01-03 10:40 | 2023-01-03 17:00 | 2023-01-03 11:45
MSA-DTAG | WA6400620 | 1 | GPS Plumbing & Gas Services PtyLtd | Basement - Detention - Cell 4 - Cistern toilet is not flushing | Plumbing & Drainage | Toilets/Cisterns | 235.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2023-01-03 16:12 | 2023-01-04 17:00 | 2023-01-04 06:55 | 2023-01-04 17:00 | 2023-01-04 08:00
MSA-DTWD | WA6405590 | 2 | Water2water Pty Ltd | Staff office - Billi water dispenser keeps tripping breaker | Plumbing & Drainage | Water | 420.655 | Pass | Pass | 0 | 0 | 1.0833 | 2023-01-09 16:22 | 2023-01-12 17:00 | 2023-01-12 12:25 | 2023-01-12 17:00 | 2023-01-12 13:30
MSA-MRWA | WA6450260 | 3 | Water2water Pty Ltd | Zip under bench HWU not providing hot water, no flow, chilled is working | Plumbing & Drainage | HWS/Units Electric & Gas | 418.785 | Pass | Pass | -1 | -1 | 1.0833 | 2023-01-16 10:14 | 2023-01-23 17:00 | 2023-01-18 14:30 | 2023-01-23 17:00 | 2023-01-18 15:35
MSA-DCA | WA6482635 | 1 | GPS Plumbing & Gas Services PtyLtd | Upper circle - Auto flush is not working | Plumbing & Drainage | Toilets/Cisterns | 170.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2023-01-18 11:53 | 2023-01-19 17:00 | 2023-01-18 14:30 | 2023-01-19 17:00 | 2023-01-18 15:35
MSA-DTAG | WA6516783 | 1 | GPS Plumbing & Gas Services PtyLtd | Custody - Admissions Area - Hand basin is clogged - see notes | Plumbing & Drainage | Drainage | 170.6025 | Pass | Pass | 0 | 0 | 1.0833 | 2023-01-23 15:06 | 2023-01-24 17:00 | 2023-01-24 06:25 | 2023-01-24 17:00 | 2023-01-24 07:30
MSA-DTWD | WA6533794 | 1 | AWB Co. | Broken Power point | Electrical | General Electrical | 210.935 | Pass | Pass | 0 | 0 | 1.0833 | 2023-02-06 08:54 | 2023-02-07 17:00 | 2023-02-06 08:55 | 2023-02-07 17:00 | 2023-02-06 10:00
MSA-DTWD | WA6674572 | 3 | SENTINEL LOCK SERVICE PTY LTD | 2434 – Roof Exit Door - Faulty Door Lever | Security | Locksmith | 185.5 | Pass | Pass | 0 | 0 | 1.0833 | 2023-02-27 10:41 | 2023-03-07 17:00 | 2023-03-07 12:45 | 2023-03-07 17:00 | 2023-03-07 13:50
MSA-DTWD | WA6680771 | 2 | SENTINEL LOCK SERVICE PTY LTD | M13 Corridor - Faulty keypad lock on external door | Security | Locksmith | 640.3 | Pass | Pass | 0 | 0 | 1.0833 | 2023-03-01 14:16 | 2023-03-07 17:00 | 2023-03-07 12:45 | 2023-03-07 17:00 | 2023-03-07 13:50 |  | WACCES
MSA-DTWD | WA6680902 | 1 | LIGHTHOUSE LOCKSMITHS | multiple keys cut | Security | Locksmith | 448.8 | Pass | Pass | 0 | 0 | 1.0833 | 2023-03-01 16:26 | 2023-03-02 17:00 | 2023-03-02 08:30 | 2023-03-02 17:00 | 2023-03-02 09:35
MSA-DTAG | WA5694158 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground - Mens Public toilet - Leak coming from the 1st urinal in the men’s public toilet | Plumbing & Drainage | Water | 176.3125 | Pass | Pass | 0 | 0 | 1.0833 | 2022-08-05 08:26 | 2022-08-08 17:00 | 2022-08-05 08:50 | 2022-08-08 17:00 | 2022-08-05 09:55 |  |  | Replaced faulty and leaking duo valve. I believe that the valve had been leaking for a long time due to the fact that the hole in it was quite big and also because the door did swell(struggled to open it and unable to close it). Lights in the duct not working either
MSA-DTAG | WA6165774 | 2 | Schindler Lifts Australia | Lift not working - no power | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1.0833 | 2022-11-11 09:32 | 2022-11-16 17:00 | 2022-11-11 13:20 | 2022-11-16 17:00 | 2022-11-11 14:25 |  |  | Works completed - close out at $0
MSA-MRWA | WA6166068 | 0 | Schindler Lifts Australia | Lift making loud beep, display screen is intermittent and sensors intermittent | Lifts | Lifts |  | Fail | Fail | 1 | 1 | 1.0833 | 2022-11-11 11:57 | 2022-11-11 13:57 | 2022-11-16 13:20 | 2022-11-11 15:57 | 2022-11-16 14:25 |  |  | Works completed - close out at $0
MSA-DFES | WA5325989 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Relivers Block - Station officers Bathroom - Water pressure in the shower is low | Plumbing & Drainage | Water | 160.95 | Pass | Pass | 0 | 0 | 1.0667 | 2022-04-14 14:44 | 2022-04-26 17:00 | 2022-04-26 09:28 | 2022-04-26 17:00 | 2022-04-26 10:32 |  |  | Serviced taps, repaired toilet seat.
MSA-DCA | WA5696069 | 0 | TK Elevator Australia Pty Ltd | Lift is stuck below ground floor. | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 1.0667 | 2022-08-08 09:29 | 2022-08-08 11:29 | 2022-08-08 11:49 | 2022-08-08 13:29 | 2022-08-08 12:53 |  |  | Lift through bottom floor. Noted event codes. Drove the lift up on maintenance control, and reset to normal. Tested lift operation without further fault.Replaced the tape head reader board and the top of car bi-stable switch. Tested lift operation without fault. Cleared the log and returned the lift to service
MSA-DCA | WA6372727 | 2 | GPS Plumbing & Gas Services PtyLtd | First cubicle - Toilet constantly running. | Plumbing & Drainage | HWS/Units Electric & Gas | 268.7925 | Pass | Pass | 0 | 0 | 1.0667 | 2022-12-14 12:24 | 2022-12-19 17:00 | 2022-12-16 13:26 | 2022-12-19 17:00 | 2022-12-16 14:30 |  |  | Replaced faulty inlet vakve and putlet washer
MSA-MRWA | WA6560692 | 2 | Dormakaba Australia Pty Ltd | Exit gate - intermittent fault | Building | Automatic Doors | 366 | Pass | Pass | 0 | 0 | 1.0667 | 2023-02-13 12:06 | 2023-02-16 17:00 | 2023-02-13 14:45 | 2023-02-16 17:00 | 2023-02-13 15:49
MSA-DTAG | WA5099175 | 1 | Gilmour & Jooste Electrical | Registry - Ground - Wall near safe in registry - Move light switches away from door switch on wall | Electrical | General Electrical | 129.67 | Pass | Pass | 0 | 0 | 1.0667 | 2022-02-01 15:38 | 2022-02-02 17:00 | 2022-02-02 09:15 | 2022-02-02 17:00 | 2022-02-02 10:19 |  | WACCES | Investigated to move light switch away from fort switches on wall
MSA-DFES | WA5208640 | 1 | Anvil Doors | Engine Bay door controller - Faulty | Building | Automatic Doors | 790 | Pass | Pass | 0 | 0 | 1.0667 | 2022-03-09 09:55 | 2022-03-10 17:00 | 2022-03-09 09:56 | 2022-03-10 17:00 | 2022-03-09 11:00 |  |  | Attended Butler fire station and replaced GFA controller to bifold door Number #1. Note -- external alarm contactors had failed so controller needed to be replaced as part of the alarm installation. Please see attached signature slip and service report. Thank you
MSA-DCA | WA5792528 | 3 | GPS Plumbing & Gas Services PtyLtd | First Floor - Glass Room - Possible drain causing issues - See notes below | Plumbing & Drainage | Drainage | 127.8125 | Pass | Pass | -1 | -1 | 1.0667 | 2022-08-23 15:04 | 2022-08-30 17:00 | 2022-08-25 10:54 | 2022-08-30 17:00 | 2022-08-25 11:58 |  |  | Checked all drains they seem to be working fine the dishwasher was draining well and the smell is coming from the floor waste due to the sink that feeds the floor waste not being used Regularly
MSA-DTWD | WA6148662 | 1 | ACTION GLASS & ALUMINIUM | A106-two smashed windows | Glazing | Window Glass | 1597.54 | Pass | Pass | 0 | 0 | 1.0667 | 2022-11-04 07:44 | 2022-11-04 17:00 | 2022-11-04 15:56 | 2022-11-04 17:00 | 2022-11-04 17:00 |  |  | ATTENDED SITETEMP GLAZED BROKEN OVERSIZE PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-1751 X 2356PLUS 8 SQM OF SAFETY FILM TO THIS AND OTHER CRACKED OVERSIZE PANEL AND SILICONE***CLOSED OFF AS REQUESTED BY STEVE***
MSA-DCA | WA6531000 | 3 | TK Elevator Australia Pty Ltd | Lift 4 - Lock to level 4 security stack is turning around | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1.0667 | 2023-02-03 08:11 | 2023-02-10 17:00 | 2023-02-03 09:42 | 2023-02-10 17:00 | 2023-02-03 10:46
MSA-DCA | WA4992713 | 2 | GPS Plumbing & Gas Services PtyLtd | SDK/Assembley toilet -Sink Loose - Refix Sink to Wall | Plumbing & Drainage | Materials | 212.93 | Pass | Pass | 0 | 0 | 1.05 | 2022-01-06 16:47 | 2022-01-11 17:00 | 2022-01-11 08:33 | 2022-01-11 17:00 | 2022-01-11 09:36 |  |  | Refitted basin pulled away from the wall.
MSA-DTWD | WA6044254 | 3 | Dormakaba Australia Pty Ltd | East- L2E corridor auto door switch faulty | Building | Automatic Doors | 364.18 | Pass | Pass | -1 | -1 | 1.05 | 2022-10-17 10:09 | 2022-10-24 17:00 | 2022-10-17 13:41 | 2022-10-24 17:00 | 2022-10-17 14:44 |  |  | Inspected door and found that the mode pad had failed and required replacing, supplied and fitted new besam mode pad as necessary, checked overoperator and tested operation upon completion and left in good working order.
MSA-DCA | WA6165971 | 0 | TK Elevator Australia Pty Ltd | button has been pushed in and is stuck | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 1.05 | 2022-11-11 11:09 | 2022-11-11 13:09 | 2022-11-11 13:09 | 2022-11-11 15:09 | 2022-11-11 14:12 |  |  | Ground floor fire service key barrel pushed through surround.Found button housing and external housing damaged. Temporary fix, testeddurability and key barrel function, all ok.
MSA-DTWD | WA5001101 | 1 | CDA Air & Solar | Freezer in Coolroom - the freezer isnt working and temperature incorrect | Refrigeration | Freezers | 278.3 | Pass | Pass | 0 | 0 | 1.05 | 2022-01-11 08:55 | 2022-01-12 17:00 | 2022-01-12 11:47 | 2022-01-12 17:00 | 2022-01-12 12:50 |  |  | Found indoor fans not working due to controller relay not working. Rectified and now working.Found refrigerant issue. Pipework runs underground, under concrete blocks.Recommend coolroom Tech to attend.
MSA-DTAG | WA5186927 | 3 | Gilmour & Jooste Electrical | Multiple Locations - damaged light bulbs - see notes below | Electrical | Lighting, Internal | 125.58 | Pass | Pass | 0 | 0 | 1.05 | 2022-02-22 09:57 | 2022-03-01 17:00 | 2022-03-01 14:00 | 2022-03-01 17:00 | 2022-03-01 15:03 |  |  | Repaired lights throughout courts and completed stock order for new lamps. Lamps supplied by courts.
MSA-DTAG | WA5195829 | 1 | Gilmour & Jooste Electrical | Courtroom 1 - Lights out – Holding Pod to Court room1 | Electrical | Lighting, Internal | 83.72 | Pass | Pass | 0 | 0 | 1.05 | 2022-02-28 16:30 | 2022-03-01 17:00 | 2022-03-01 08:00 | 2022-03-01 17:00 | 2022-03-01 09:03 |  |  | Replaced tubes and starters to fitting. Tested and working. Tubes and starters supplied by site.
MSA-DTAG | WA5203742 | 2 | Gilmour & Jooste Electrical | Various locations - flickering lights - see notes below | Electrical | Lighting, Internal | 146.86 | Fail | Fail | 0 | 0 | 1.05 | 2022-03-03 16:12 | 2022-03-09 17:00 | 2022-03-10 07:15 | 2022-03-09 17:00 | 2022-03-10 08:18 |  |  | Replaced flickering fluro in toilet and court 1
MSA-DTWD | WA5565802 | 3 | AWB Co. | E502 - light out | Electrical | General Electrical | 136.06 | Pass | Pass | -1 | -1 | 1.05 | 2022-06-22 11:27 | 2022-06-29 17:00 | 2022-06-24 11:57 | 2022-06-29 17:00 | 2022-06-24 13:00 |  |  | Attended site and signed in. Completed JSA. Located E502. Used sites supplied tubes and starters and replaced as required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA6019933 | 2 | Dormakaba Australia Pty Ltd | Roller door not easy to close in M020 Plastering Workshop | Building | Roller Shutters | 351.95 | Pass | Pass | -1 | -1 | 1.05 | 2022-10-13 09:24 | 2022-10-18 17:00 | 2022-10-13 12:57 | 2022-10-18 17:00 | 2022-10-13 14:00 |  |  | Door is binding on top of right hand side guide. Adjusted guide, cleaned and lubricated both guides, checked tension, all ok door back to normal operation
MSA-DTAG | WA6517416 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground - Magistrates ladies Toilet - Toilet cubicle 2 is continually running | Plumbing & Drainage | Toilets/Cisterns | 295.6025 | Pass | Pass | -1 | -1 | 1.05 | 2023-01-24 09:36 | 2023-01-30 17:00 | 2023-01-24 12:45 | 2023-01-30 17:00 | 2023-01-24 13:48
MSA-DFES | WA5230745 | 0 | Australian HVAC Services Pty. Ltd. | No power loss - running on generators - check air conditions units | Air Conditioning | Room Air Conditioners | 130.05 | Pass | Pass | 0 | 0 | 1.0397 | 2022-03-15 07:10 | 2022-03-15 09:10 | 2022-03-15 07:55 | 2022-03-15 11:10 | 2022-03-15 08:57 |  |  | Attended site after power outage and inspected ac plant. Found all plant operating. Found nce mssb 1.2 not running properly. Reset controller. Reset toilet exhaust fan fault. Confirmed all plant operating correctly.
MSA-DCA | WA5495119 | 2 | Dormakaba Australia Pty Ltd | External - Front staff carpark - automatic gate - see details below | Building | General Building | 191.9 | Pass | Pass | -1 | -1 | 1.0333 | 2022-06-08 09:33 | 2022-06-13 17:00 | 2022-06-08 12:03 | 2022-06-13 17:00 | 2022-06-08 13:05 |  |  | Assessed gate a found flat batteries in safety beam. Fitted new batteries and reset safety beam. All ok. could not locate our ip or programmed asset. New ip 1153699
MSA-DTAG | WA5564670 | 2 | Seme Solutions Pty Ltd | Non contact interview room intercom not working | Security | Access Control |  | Pass | Pass | 0 | 0 | 1.0333 | 2022-06-21 11:43 | 2022-06-24 17:00 | 2022-06-22 10:06 | 2022-06-24 17:00 | 2022-06-22 11:08 |  |  | checked the intercoms in the non-contact visits room. The intercom system is working on both sides of the glass. I have attached photos of the installation. There is an intercom on either side and they connect to a hub located in the bench on visitor side. On the prisoner's side there is also an intercom face plate in the centre that is covering some holes in the bench. There is also a redundant flush mount microphone. This is a standalone system made by Cellguard.
MSA-DTAG | WA5978865 | 2 | AHS Services WA Pty Ltd (Anchor) | Female staff toilet - Water keeps running in one of the cubicles | Plumbing & Drainage | Water | 175.82 | Pass | Pass | 0 | 0 | 1.0333 | 2022-09-28 13:39 | 2022-10-03 17:00 | 2022-09-30 09:30 | 2022-10-03 17:00 | 2022-09-30 10:32 |  |  | Picked up and replaced faulty inlet valve and outlet washer to right hand side female toilet on the 11
MSA-DTWD | WA6257929 | 3 | Techworks Electrical | Corridor south end - faulty ceiling lights | Electrical | Lighting, Internal | 1020.14 | Pass | Pass | -1 | -1 | 1.0333 | 2022-11-25 08:58 | 2022-12-02 17:00 | 2022-11-25 08:58 | 2022-12-02 17:00 | 2022-11-25 10:00 |  |  | Replaced 2x lights within E-Block corridor
MSA-DTAG | WA6669094 | 3 | GPS Plumbing & Gas Services PtyLtd | Ladies Public Toilet - Cubilce 5 - Toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 215.68 | Pass | Pass | -1 | -1 | 1.0333 | 2023-02-22 14:12 | 2023-03-01 17:00 | 2023-02-24 09:41 | 2023-03-01 17:00 | 2023-02-24 10:43
MSA-MRWA | WA5437361 | 1 | TK Elevator Australia Pty Ltd | Lift 1 - out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.0333 | 2022-05-16 07:44 | 2022-05-16 17:00 | 2022-05-16 11:14 | 2022-05-16 17:00 | 2022-05-16 12:16 |  |  | Geared: Incorrect lift reported for callout. Actually lift4 that was shutdown.to be closed out at $0 cost
MSA-DTWD | WA5454809 | 2 | Dormakaba Australia Pty Ltd | T Block - Ground Floor - Library - Glass auto Door beeps every 30 minutes | Building | Automatic Doors | 304.1 | Pass | Pass | 0 | 0 | 1.0333 | 2022-05-17 14:47 | 2022-05-20 17:00 | 2022-05-18 08:05 | 2022-05-20 17:00 | 2022-05-18 09:07 |  |  | On inspection, found batteries faulty due to age.Replaced faulty batteries as required, tested and adjusted, all OK.
MSA-MRWA | WA5696534 | 1 | GPS Plumbing & Gas Services PtyLtd | blocked toilet unable to flush | Plumbing & Drainage | Water | 410.6725 | Pass | Pass | 0 | 0 | 1.0333 | 2022-08-08 12:35 | 2022-08-09 17:00 | 2022-08-09 06:08 | 2022-08-09 17:00 | 2022-08-09 07:10 |  |  | Replaced faulty bellows, outlet washer and buttons red washers
MSA-DTAG | WA5735515 | 2 | GPS Plumbing & Gas Services PtyLtd | L1 ladies toilet The screw holding the metal plate button was not screwed in. | Plumbing & Drainage | Toilets/Cisterns | 131.09 | Pass | Pass | 0 | 0 | 1.0333 | 2022-08-16 13:28 | 2022-08-19 17:00 | 2022-08-18 14:10 | 2022-08-19 17:00 | 2022-08-18 15:12 |  |  | Screwed button plate back onto wallmount for the button
MSA-DCA | WA6383871 | 0 | TK Elevator Australia Pty Ltd | Foyer - Lift 1 - Intermit faulty - audible fault message | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.0333 | 2022-12-20 14:38 | 2022-12-20 16:38 | 2022-12-20 15:56 | 2022-12-20 18:38 | 2022-12-20 16:58 |  |  | Lift 1 and 2 running on arrival, no errors on lifts. Apparently happened 2 again today after tech left site.Spoke to reception and tried to reproduce fault/noise. Tested phones on lift 1 and 2. Held door open until lightrsys started bussing. Wasn't the same noises. The staff have never heard the noise before. Apparently they is have never heard this noise before. Happened around 6am and 8ish but it isn't a regular occurrence.Checked contoller and transformer voltages all okay.Drive doesn't have any errors on them.Tried to speak to ryan, apparently he wasnt in the office atm or gone home.Tested the lift multiple times all okay, couldn't reproduce fault message, or any fault. Left units in service.
MSA-DCA | WA6408102 | 2 | Techworks Electrical | Switch for Bathroom Fan/Light in Dressing Room 7 is not working also loose | Electrical | General Electrical | 159.44 | Pass | Pass | 0 | 0 | 1.0333 | 2023-01-10 14:40 | 2023-01-13 17:00 | 2023-01-11 13:00 | 2023-01-13 17:00 | 2023-01-11 14:02
MSA-DTAG | WA6414782 | 0 | Sapio Pty Ltd | Level 5 - access control fault to level 5 doors - see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 1.0333 | 2023-01-11 09:49 | 2023-01-11 11:49 | 2023-01-11 11:30 | 2023-01-11 13:49 | 2023-01-11 12:32
MSA-DTAG | WA6572857 | 2 | Sapio Pty Ltd | Custody - Receiver 6 - Faulty | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1.0333 | 2023-02-14 09:13 | 2023-02-17 17:00 | 2023-02-14 14:08 | 2023-02-17 17:00 | 2023-02-14 15:10
MSA-DTWD | WA6690321 | 1 | Water2water Pty Ltd | Kitchen - Complaints of bad tasting water from Boiling Billi | Plumbing & Drainage | Water | 303.54 | Pass | Pass | 0 | 0 | 1.0333 | 2023-03-09 08:55 | 2023-03-10 17:00 | 2023-03-10 12:40 | 2023-03-10 17:00 | 2023-03-10 13:42
MSA-DTWD | WA6537313 | 1 | Dormakaba Australia Pty Ltd | Auto door is not working | Building | Automatic Doors | 186.95 | Pass | Pass | 0 | 0 | 1.0167 | 2023-02-07 08:41 | 2023-02-08 17:00 | 2023-02-07 12:37 | 2023-02-08 17:00 | 2023-02-07 13:38
MSA-DFES | WA6129378 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Male Toilet - Toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 189.09 | Pass | Pass | 0 | 0 | 1.0167 | 2022-10-27 14:28 | 2022-10-28 17:00 | 2022-10-28 07:29 | 2022-10-28 17:00 | 2022-10-28 08:30 |  |  | Arrived on site and singed in went to male toilet out the back of office. Mike showed me a blocked urinal had to go to Galvin and pick up bowl guard. Came back and cleaned blockage. Tested urinal and was working fine and blockage was going.
MSA-DCA | WA6671853 | 1 | GPS Plumbing & Gas Services PtyLtd | CRC - Loading Bay 7 - Mens toilets blocked | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 1.0167 | 2023-02-23 11:08 | 2023-02-24 17:00 | 2023-02-24 10:20 | 2023-02-24 17:00 | 2023-02-24 11:21
MSA-DTWD | WA5091751 | 3 | Water2water Pty Ltd | B6 - Level 2 - Staff Room - twin water filters for drinking water sink mounted outlet needs change | Plumbing & Drainage | Water | 233.54 | Pass | Pass | 0 | 0 | 1.0167 | 2022-01-27 10:53 | 2022-02-03 17:00 | 2022-02-01 12:27 | 2022-02-03 17:00 | 2022-02-01 13:28 |  |  | System working on arrival. Service due on system. Replaced filters, cleaned unit and checked under pressure. Normal operation
MSA-DTAG | WA5099961 | 0 | Gilmour & Jooste Electrical | Custody Corridor - Court room 2 - light is flickering - see details | Electrical | Lighting, Internal | 154.38 | Pass | Pass | 0 | 0 | 1.0167 | 2022-02-02 10:03 | 2022-02-02 12:03 | 2022-02-02 10:45 | 2022-02-02 14:03 | 2022-02-02 11:46 |  |  | Performed to fix flickering light in court room 2 custody corridor, replaced 2x fluro tubes, 2x s10 starters, and 1 tombstone. All in working order
MSA-DFES | WA5326054 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 2,4 and 5 - very slow draining vanity sinks | Plumbing & Drainage | Drainage | 218.78 | Pass | Pass | 0 | 0 | 1.0167 | 2022-04-14 16:16 | 2022-04-21 17:00 | 2022-04-19 13:59 | 2022-04-21 17:00 | 2022-04-19 15:00 |  |  | Room 2 plunged and cleared the blockage ran hot water down and all clear Room4 plunged and draining better put Moflow down and cleared the blockage tested and draining Room5 plunged and cleared the blockage
MSA-DFES | WA5392726 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Males Toilets' - First Cubicle - is blocked | Plumbing & Drainage | Toilets/Cisterns | 139.95 | Pass | Pass | 0 | 0 | 1.0167 | 2022-05-03 11:53 | 2022-05-06 17:00 | 2022-05-06 06:59 | 2022-05-06 17:00 | 2022-05-06 08:00 |  |  | Unblocking the toilet in male toilet on 1st floor. Cleared the excess paper. Plunged and flushed until all cleared. Tested, all drains good.
MSA-DTWD | WA5460353 | 1 | Dormakaba Australia Pty Ltd | F Block- Ground - Between F49 & F50 - Main automatic sliding door won’t open when entering building | Building | General Building | 717.92 | Pass | Pass | 0 | 0 | 1.0167 | 2022-05-18 13:20 | 2022-05-19 17:00 | 2022-05-18 15:06 | 2022-05-19 17:00 | 2022-05-18 16:07 |  |  | On inspection, found external sensor faulty due to general wear and tear. Replaced faulty sensor as required and approved by management. Tested and adjusted, all OK.Track wheels starting to show slight signs of wear and tear.
MSA-DTAG | WA5482742 | 3 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Magistrate 2 Office - Water damaged carpet requires further clean | Cleaning | Cleaning | 500 | Fail | Fail | 1 | 1 | 1.0167 | 2022-05-31 14:55 | 2022-06-08 17:00 | 2022-06-13 15:29 | 2022-06-08 17:00 | 2022-06-13 16:30 |  |  | As per work order No# WA5482742
MSA-DTAG | WA5833162 | 0 | Dormakaba Australia Pty Ltd | Underground - Garage - Custody Area - Garage door is not closing | Building | Automatic Doors | 351.95 | Fail | Pass | 0 | 0 | 1.0167 | 2022-09-06 08:28 | 2022-09-06 10:28 | 2022-09-06 10:42 | 2022-09-06 12:28 | 2022-09-06 11:43 |  |  | Gate had come off track due to dirt buildup. Cleaned track and put gate back on track. Tested and working normal.
MSA-DFES | WA6208266 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground floor male toilets - 3rd cubicle, Metal plate for flush button is breaking off wall. | Plumbing & Drainage | Toilets/Cisterns | 149.1 | Pass | Pass | 0 | 0 | 1.0167 | 2022-11-17 15:29 | 2022-11-24 17:00 | 2022-11-24 08:15 | 2022-11-24 17:00 | 2022-11-24 09:16 |  |  | Repaired flush button panel
MSA-DCA | WA6362848 | 0 | Techworks Electrical | L1 pathology - light switch is arching | Electrical | Lighting, Internal | 250.16 | Pass | Pass | 0 | 0 | 1.0167 | 2022-12-09 13:55 | 2022-12-09 15:55 | 2022-12-09 14:29 | 2022-12-09 17:55 | 2022-12-09 15:30 |  |  | Installed new switch mech. All working well.
MSA-DCA | WA6401358 | 1 | Dormakaba Australia Pty Ltd | Cable Gate switch showing fault light, not responding, and external box not responding to remote | Building | Automatic Doors | 366.95 | Pass | Pass | 0 | 0 | 1.0167 | 2023-01-04 11:20 | 2023-01-05 17:00 | 2023-01-04 12:49 | 2023-01-05 17:00 | 2023-01-04 13:50
MSA-DCA | WA6518041 | 1 | TK Elevator Australia Pty Ltd | Lift 6 keeps beeping and displaying overload sign-but is still working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.0167 | 2023-01-24 16:05 | 2023-01-25 17:00 | 2023-01-25 07:53 | 2023-01-25 17:00 | 2023-01-25 08:54
MSA-DCA | WA6526924 | 1 | TK Elevator Australia Pty Ltd | Lift stuck between B level and G level - Recurring fault | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1.0167 | 2023-02-01 12:02 | 2023-02-02 17:00 | 2023-02-01 13:45 | 2023-02-02 17:00 | 2023-02-01 14:46
MSA-DTAG | WA6531456 | 1 | GPS Plumbing & Gas Services PtyLtd | Custody - Cell 3 - Toilet cistern button has been pulled out | Plumbing & Drainage | Toilets/Cisterns | 362.68 | Pass | Pass | 0 | 0 | 1.0167 | 2023-02-03 11:57 | 2023-02-06 17:00 | 2023-02-06 07:32 | 2023-02-06 17:00 | 2023-02-06 08:33
MSA-DTAG | WA6544598 | 1 | Sapio Pty Ltd | Underground carpark - Pedestrian door - Not closing | Security | Keys & Access | 139.88 | Pass | Pass | 0 | 0 | 1.0167 | 2023-02-10 14:32 | 2023-02-13 17:00 | 2023-02-13 07:10 | 2023-02-13 17:00 | 2023-02-13 08:11
MSA-DTWD | WA6668899 | 3 | Techworks Plumbing | Capo - Level 1 - Male toilet is leaking | Plumbing & Drainage | Toilets/Cisterns | 237.05 | Pass | Pass | -1 | -1 | 1.0167 | 2023-02-22 12:27 | 2023-03-01 17:00 | 2023-02-22 14:30 | 2023-03-01 17:00 | 2023-02-22 15:31
MSA-DFES | WA5270391 | 0 | Australian HVAC Services Pty. Ltd. | Plant room - air con is not working | Air Conditioning | Room Air Conditioners | 130.05 | Pass | Pass | 0 | 0 | 1.0086 | 2022-03-18 07:28 | 2022-03-18 09:28 | 2022-03-18 08:03 | 2022-03-18 11:28 | 2022-03-18 09:03 |  |  | Attended site and inspected bms. Found nce controller bmsb 1 in fault. Reset controller and found operation restored. Inspected logs and found controller tripped this morning. Unsure if this is from existing issues with bms or related to works carried out this morning. System operating correctly and all plant running.
MSA-DFES | WA4983979 | 3 | Protek 24/7 Building & Maintenance | lids over pits in the paving under the outdoor dining area are lifting and becoming a trip hazard | Building | Foundations | 186.46 | Pass | Pass | -1 | -1 | 1 | 2021-12-23 15:57 | 2022-01-04 17:00 | 2021-12-30 10:30 | 2022-01-04 17:00 | 2021-12-30 11:30 |  |  | lifted pit lids cleaned and removed all waste then re installed them again and removed trip hazard. as they now sit flush.
MSA-DTAG | WA4984570 | 3 | Schindler Lifts Australia | Ground - Lift 9 - Lift not working, wire can be seen poking out | Lifts | Lifts |  | Pass | Pass | -2 | -2 | 1 | 2021-12-24 12:58 | 2022-01-05 17:00 | 2021-12-24 16:35 | 2022-01-05 17:00 | 2021-12-24 17:35 |  |  | When responding to the callback dated 24.12.2021, the Schindler Technician found a problem with your equipment. The landing doorcomponents were worn out. Following our attendance, the equipment was left in service.
MSA-DFES | WA4984703 | 3 | Complete Pest Management Services | Pest Control requires spray outside the station | Pest Control | Specialist Pest | 396.12 | Pass | Fail | 0 | 0 | 1 | 2021-12-26 09:26 | 2022-01-05 17:00 | 2022-01-05 17:00 | 2022-01-05 17:00 | 2022-01-05 18:00 |  |  | General Pest Spray to Exterior of Station
MSA-DTAG | WA4985521 | 3 | Midolo Building Services | External Door not self closing and handle loose | Building | Doors | 170.22 | Fail | Fail | 1 | 1 | 1 | 2021-12-29 15:10 | 2022-01-06 17:00 | 2022-01-10 07:30 | 2022-01-06 17:00 | 2022-01-10 08:30 |  |  | Repaired door handle
MSA-DCA | WA4986176 | 2 | GPS Plumbing & Gas Services PtyLtd | Tap head has come off the tap - see notes below | Plumbing & Drainage | Water | 360.41 | Pass | Pass | 0 | 0 | 1 | 2021-12-31 11:11 | 2022-01-06 17:00 | 2022-01-06 07:30 | 2022-01-06 17:00 | 2022-01-06 08:30 |  |  | Installed mini stops under basin and installed new disabled flick micker
MSA-DFES | WA4986241 | 2 | Australian HVAC Services Pty. Ltd. | Unit 16 - Dining/Kitchen - A/c Leaking large amount of water internal | Air Conditioning | Room Air Conditioners | 187.61 | Pass | Pass | -1 | -1 | 1 | 2021-12-31 12:55 | 2022-01-06 17:00 | 2021-12-31 14:00 | 2022-01-06 17:00 | 2021-12-31 15:00 |  |  | Attend site. Access kitchen AC leaking water. Remove cover from indoor unit and found drip tray full. Found drain to have blocked up. Locate end of drain and attach wet vacuum. Suck blockage out of drain. Found drain to clear. Run water through drain to test. Drain working as normal.
MSA-DFES | WA4990027 | 1 | Go Doors | gate south west not working | Security | Access Control | 540 | Pass | Pass | 0 | 0 | 1 | 2022-01-02 09:48 | 2022-01-04 17:00 | 2022-01-02 11:00 | 2022-01-04 17:00 | 2022-01-02 12:00 |  |  | Works completed
MSA-MRWA | WA4991086 | 3 | Dom's Total Grounds Maintenance | Northern Garden Bed - Split / Fallen Branch to be removed before falls | Landscaping & Gardening | Grounds Maintenance | 490 | Pass | Pass | -1 | -1 | 1 | 2022-01-04 15:06 | 2022-01-11 17:00 | 2022-01-06 06:30 | 2022-01-11 17:00 | 2022-01-06 07:30 |  |  | Tree loppers to remove fallen tree branches
MSA-DTWD | WA4991124 | 3 | AWB Co. | Faulty lights | Electrical | Lighting, Internal | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-01-04 15:30 | 2022-01-11 17:00 | 2022-01-10 12:30 | 2022-01-11 17:00 | 2022-01-10 13:30 |  |  | Daniel Hume (10/01/2022) - Work NoteAttended site and signed in. Completed JSA. Liaised with site about works going ahead. Inspected crèche. Found to be faulty lights. Spoke with site about replacing all with LED 4ft Battens. BRAF will need to be submitted.*Removal of suspended lights*12x 4ft LED Battens*Full day for works
MSA-DTWD | WA4991979 | 3 | Protek 24/7 Building & Maintenance | Unit 10 - 10F92 - Large magazine rack fallen off wall | Building | General Building | 196 | Pass | Pass | 0 | 0 | 1 | 2022-01-05 15:30 | 2022-01-12 17:00 | 2022-01-11 13:30 | 2022-01-12 17:00 | 2022-01-11 14:30 |  |  | Remove magazine rack
MSA-DCA | WA4992399 | 2 | Techworks Plumbing | ground -The hot water tap in cleaning store 8, located near the well, Tap constantly runs after use. | Plumbing & Drainage | Water | 402.58 | Pass | Pass | 0 | 0 | 1 | 2022-01-06 11:19 | 2022-01-11 17:00 | 2022-01-10 15:30 | 2022-01-11 17:00 | 2022-01-10 16:30 |  |  | Repair leaking tap
MSA-DCA | WA4992506 | 1 | Protek 24/7 Building & Maintenance | female toilets near G block - door vent missing | Building | Doors | 132.7 | Pass | Pass | 0 | 0 | 1 | 2022-01-06 12:48 | 2022-01-07 17:00 | 2022-01-07 11:45 | 2022-01-07 17:00 | 2022-01-07 12:45 |  |  | Reinstalled and secured surrounding fraome
MSA-DTWD | WA4992623 | 3 | AWB Co. | S block - room S215 - damaged Wifi units - detaching from ceilings | Building | Ceiling | 145.12 | Pass | Pass | 0 | 0 | 1 | 2022-01-06 14:38 | 2022-01-13 17:00 | 2022-01-13 11:00 | 2022-01-13 17:00 | 2022-01-13 12:00 |  |  | Attended site and signed in. Completed jsa. Met with IT guy on site and located wifi units and discussed where he wanted them, and what one was allocated to eat port on roof. Secured brackets to roof and connected cable from wifi box to port on roof. Took after pictures. Completed paperwork. Signed out.Job completed
MSA-DTAG | WA4993441 | 2 | AWB Co. | Level 13 - Comms room - GPO hanging out of the wall in comms room | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-01-07 14:00 | 2022-01-12 17:00 | 2022-01-11 12:00 | 2022-01-12 17:00 | 2022-01-11 13:00 |  |  | Job complete
MSA-DFES | WA4993638 | 3 | Go Doors | Staff carp park gate does not re-lapse correctly. Doesn’t lock once opened. | Building | Steel Fencing & Gates | 310 | Pass | Pass | -1 | -1 | 1 | 2022-01-08 15:12 | 2022-01-14 17:00 | 2022-01-10 11:45 | 2022-01-14 17:00 | 2022-01-10 12:45 |  |  | Completed works. See attachments.
MSA-DCA | WA4995144 | 1 | Site Environmental & Remediation Services Pty Ltd | exposer of ceiling - could potentially be asbestos please check&test | Building | Ceiling | 150 | Pass | Pass | 0 | 0 | 1 | 2022-01-10 10:20 | 2022-01-11 17:00 | 2022-01-10 12:45 | 2022-01-11 17:00 | 2022-01-10 13:45 |  |  | Called out to sample and analyse area for asbestos. Results came back negative for asbestos. No further action required on our end
MSA-DCA | WA4995596 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Boilers are in local mood and need to identify why not running from central plant | Mechanical Services | Boilers | 796.05 | Fail | Fail | 1 | 1 | 1 | 2022-01-10 14:25 | 2022-01-11 17:00 | 2022-01-20 08:00 | 2022-01-11 17:00 | 2022-01-20 09:00 |  |  | Organised Honeywell to rectify the Art Gallery local mode situation. Received conformation from Honeywell the art Gallery is now running in ETS mode.
MSA-DTWD | WA5001492 | 2 | Equans Mechanical Services Australia | F5 - air con is not working | Air Conditioning | Building HVAC Maintenance (Major Plant) | 83.72 | Pass | Pass | 0 | 0 | 1 | 2022-01-11 12:53 | 2022-01-14 17:00 | 2022-01-12 08:00 | 2022-01-14 17:00 | 2022-01-12 09:00 |  |  | Found the system fault light on, reset the power and ran up . Tested the operation all OK, fault was from 44deg days and it tripped on head pressure.
MSA-DFES | WA5001579 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Female change room - 3 x globes not working | Electrical | General Electrical | 195.7 | Pass | Pass | -1 | -1 | 1 | 2022-01-11 13:24 | 2022-01-18 17:00 | 2022-01-12 14:45 | 2022-01-18 17:00 | 2022-01-12 15:45 |  |  | Continued on site at 1445 investigate blown globes in female change rooms. Found two faulty lights in female change room above showers and one faulty light outside female change room door. Leftsite to collect parts from closest wholesaler. Returned to site and Replaced all faulty globes, tested and all lights working. Left site at 1545
MSA-DTWD | WA5009816 | 3 | AHS Services WA Pty Ltd (Anchor) | A154 - Cubicle one female toilet A Block ground East button not working | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Fail | Fail | 2 | 2 | 1 | 2022-01-12 07:04 | 2022-01-18 17:00 | 2022-02-02 13:30 | 2022-01-18 17:00 | 2022-02-02 14:30 |  |  | Checked all female toilets on the grid floor -all working ok
MSA-DTAG | WA5017254 | 3 | Seme Solutions Pty Ltd | Custody - Cell 1 - Cell call in cell 1 not working (possible warranty). | Security | Security Management System | 260 | Fail | Fail | 3 | 3 | 1 | 2022-01-13 12:06 | 2022-01-20 17:00 | 2022-02-08 13:30 | 2022-01-20 17:00 | 2022-02-08 14:30 |  |  | Inspected cell call push button, confirmed button for correct activations all OK, checked logic for mimic panel activation, found mimic buzzer not activating. Removed from Logic and re-applied, tested, all OK.
MSA-DCA | WA5018310 | 1 | Techworks Electrical | Greenroom - 1 x Exit sign out | Electrical | Lighting, Internal | 86.79 | Pass | Pass | 0 | 0 | 1 | 2022-01-14 10:53 | 2022-01-17 17:00 | 2022-01-17 13:30 | 2022-01-17 17:00 | 2022-01-17 14:30 |  | WACCES | No action taken on work order.This is a nexus fitting and requires a long lead time to order and replace.As discussed with Reese Withey, a new work order will be raised for rectification.
MSA-DTAG | WA5018439 | 2 | FSA (WA) Pty Ltd | Admin - Registry - Fault on fire panel - see further notes below | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | -1 | -1 | 1 | 2022-01-14 11:30 | 2022-01-19 17:00 | 2022-01-14 14:00 | 2022-01-19 17:00 | 2022-01-14 15:00 |  |  | Reset fire panel due to power outage reset instate auto door for registry
MSA-DFES | WA5030122 | 0 | Go Doors | Engine Room Double door to bay aren't closing properly | Building | Doors | 540 | Pass | Pass | 0 | 0 | 1 | 2022-01-16 15:27 | 2022-01-16 17:27 | 2022-01-16 17:00 | 2022-01-16 19:27 | 2022-01-16 18:00 |  |  | Works completed
MSA-DFES | WA5052776 | 2 | Australian HVAC Services Pty. Ltd. | Room 15 - water leaking from air conditioner | Air Conditioning | Room Air Conditioners | 145.05 | Pass | Pass | 0 | 0 | 1 | 2022-01-18 10:30 | 2022-01-21 17:00 | 2022-01-18 14:00 | 2022-01-21 17:00 | 2022-01-18 15:00 |  |  | Unblocked condensate drain for AC2 Cleaned indoor coil and applied insulation tape to Evap coil u-bend
MSA-DFES | WA5066639 | 1 | Australian HVAC Services Pty. Ltd. | A/C Units - Office and Living area - not working - HL Fault | Air Conditioning | Room Air Conditioners | 187.61 | Pass | Pass | 0 | 0 | 1 | 2022-01-19 09:25 | 2022-01-20 17:00 | 2022-01-19 10:30 | 2022-01-20 17:00 | 2022-01-19 11:30 |  |  | Acs out on external lockout due to fire service testing
MSA-DTAG | WA5069186 | 1 | Gilmour & Jooste Electrical | Ground - Outside of building - Broken light bollard outside near judicial carpark | Electrical | General Electrical | 457.48 | Pass | Pass | 0 | 0 | 1 | 2022-01-19 16:24 | 2022-01-20 17:00 | 2022-01-20 06:00 | 2022-01-20 17:00 | 2022-01-20 07:00 |  |  | Inspected vandalise bollard with expose cabling. Renewed one times bollard top. Checked and tested, all in working order.
MSA-DTWD | WA5069192 | 2 | CONNECT SECURITY SYSTEMS | T Block - 3 exit doors facing plant timing lock not working locking doors with key | Security | Monitoring | 153.18 | Pass | Pass | 0 | 0 | 1 | 2022-01-19 16:32 | 2022-01-24 17:00 | 2022-01-21 09:09 | 2022-01-24 17:00 | 2022-01-21 10:09 |  |  | Job completed 21/1/2022
MSA-DTWD | WA5080616 | 1 | AWB Co. | Level 2 - Library - Electrical sub-board tripped - will not re-set | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-01-20 08:00 | 2022-01-20 17:00 | 2022-01-20 09:30 | 2022-01-20 17:00 | 2022-01-20 10:30 |  |  | Attended site, signed in, completed jsa,spoke to fm about job, located dB and subboard in library area , found 2 RCDs tripped in each board , fm mentioned that western power was working on grid yesterday and turned power off for a short period of time , this caused RCDs to trip when western power re energised building, tested each circuit that was tripped , rcd working as intended and load test passed , closed up all boards , completed paperwork, signed out, ***job completed***
MSA-DTAG | WA5085639 | 2 | Midolo Building Services | Level 3 - Interview Room 3.6 Door - latch not engaging | Building | General Building | 162.52 | Pass | Pass | -1 | -1 | 1 | 2022-01-21 09:44 | 2022-01-27 17:00 | 2022-01-21 13:15 | 2022-01-27 17:00 | 2022-01-21 14:15 |  |  | HINGE REPAIRS - LATCH RE ATTACHED & ADJUSTED
MSA-DTWD | WA5087344 | 2 | ACTION GLASS & ALUMINIUM | C block, room 46 - upper panel on entry door damaged - unsecure | Glazing | Window Glass | 307.6 | Pass | Pass | 0 | 0 | 1 | 2022-01-24 08:37 | 2022-01-28 17:00 | 2022-01-25 15:00 | 2022-01-28 17:00 | 2022-01-25 16:00 |  |  | ATTENDED SITEREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-990 X 745
MSA-DTWD | WA5087886 | 2 | Protek 24/7 Building & Maintenance | Room F2 - ceiling fan blade is missing lock nuts | Equipment | Electrical Equipment | 132.7 | Pass | Pass | 0 | 0 | 1 | 2022-01-24 14:01 | 2022-01-28 17:00 | 2022-01-27 15:00 | 2022-01-28 17:00 | 2022-01-27 16:00 |  |  | Replace screws
MSA-DTWD | WA5089994 | 3 | AHS Services WA Pty Ltd (Anchor) | A Block - Level 1 - Urinal is not flushing | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | -1 | -1 | 1 | 2022-01-25 08:42 | 2022-02-02 17:00 | 2022-01-27 07:15 | 2022-02-02 17:00 | 2022-01-27 08:15 |  |  | Water was isolated to cistern, inspected cistern everything ok
MSA-DFES | WA5090547 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Room - battery needs to be replaced in FRS system | Electrical | General Electrical | 124.95 | Pass | Pass | 0 | 0 | 1 | 2022-01-25 13:36 | 2022-01-27 17:00 | 2022-01-27 07:30 | 2022-01-27 17:00 | 2022-01-27 08:30 |  | WACCES | Replacement of battery charger is outside scope of works.
MSA-DTWD | WA5091657 | 3 | Falcetta Plumbing and Gas | Block 7 - Ground - Male toilets - Leak from under handbasin | Plumbing & Drainage | Toilets/Cisterns | 140.12 | Pass | Pass | -1 | -1 | 1 | 2022-01-27 09:50 | 2022-02-03 17:00 | 2022-01-28 13:30 | 2022-02-03 17:00 | 2022-01-28 14:30 |  |  | replaced trap and waste
MSA-DCA | WA5091938 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground - Access Toilet - Toilet Seat Broken -see details below | Plumbing & Drainage | Water | 587.47 | Pass | Pass | -1 | -1 | 1 | 2022-01-27 12:26 | 2022-02-01 17:00 | 2022-01-28 13:10 | 2022-02-01 17:00 | 2022-01-28 14:10 |  |  | Replaced toilet seat
MSA-DTAG | WA5092112 | 2 | Midolo Building Services | Ground - Courtroom 6 - Hinge on bottom of public entrance door is coming off | Building | Doors | 198.53 | Pass | Pass | 0 | 0 | 1 | 2022-01-27 14:36 | 2022-02-01 17:00 | 2022-01-31 14:00 | 2022-02-01 17:00 | 2022-01-31 15:00 |  |  | NEW HINGES INSTALLED
MSA-DCA | WA5092201 | 0 | Techworks Electrical | Emergency light fitting - water leaking coming through please make safe | Electrical | General Electrical | 266.525 | Pass | Pass | 0 | 0 | 1 | 2022-01-27 16:19 | 2022-01-27 18:19 | 2022-01-27 16:30 | 2022-01-27 20:19 | 2022-01-27 17:30 |  |  | Water leak coming through em light. Location: dressing room under green room. Unplugged em light (still works) ready for re-install when leak is fixed .
MSA-DTWD | WA5092575 | 3 | Schindler Lifts Australia | Level 3, D block - Lift Button on Level 3 foyer doesnt work | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-01-28 08:11 | 2022-02-04 17:00 | 2022-01-28 08:15 | 2022-02-04 17:00 | 2022-01-28 09:15 |  |  | to be closed out at $0 cost
MSA-DTWD | WA5092584 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 2 - B211 - Repair leaking female toilet | Plumbing & Drainage | Toilets/Cisterns | 99.69 | Pass | Pass | 0 | 0 | 1 | 2022-01-28 08:13 | 2022-02-02 17:00 | 2022-01-31 09:30 | 2022-02-02 17:00 | 2022-01-31 10:30 |  |  | Replaced worn flush rubber
MSA-DCA | WA5092804 | 1 | GPS Plumbing & Gas Services PtyLtd | stage door - water leaking through ceiling of dressing rom 7 into exit sign - see notes | Plumbing & Drainage | Water | 200.43 | Pass | Pass | 0 | 0 | 1 | 2022-01-28 10:19 | 2022-01-31 17:00 | 2022-01-28 12:00 | 2022-01-31 17:00 | 2022-01-28 13:00 |  |  | Inspected the area change room 7 on the mezzanine level found that water is leaking from the ac unit, spoken to admin to get the ac contractors out to look at it.
MSA-DTWD | WA5098472 | 3 | AWB Co. | 3 phase plug locking ring missing | Electrical | General Electrical | 259.9 | Pass | Pass | 0 | 0 | 1 | 2022-02-01 09:39 | 2022-02-08 17:00 | 2022-02-07 09:45 | 2022-02-08 17:00 | 2022-02-07 10:45 |  |  | Attended site and signed in. Completed JSA. spoke to fm. Re Located smashed GPOs on wall. Went to wholesaler to pick up parts ( for 3 jobs ). Isolated power circuits. Made sure it was dead. Took off old isolators and mounted new ones. Connected up. Put covers on. Re energised circuits. Labelled isolators. Took pictures. Completed paperwork. Signed out.*** Job complete ***
MSA-DCA | WA5099081 | 2 | Techworks Electrical | Level 1 - Kitchenette - The two-gang switch mechanism is faulty | Electrical | General Electrical | 230.53 | Pass | Pass | 0 | 0 | 1 | 2022-02-01 13:58 | 2022-02-04 17:00 | 2022-02-03 11:00 | 2022-02-04 17:00 | 2022-02-03 12:00 |  |  | dentified circuit, isolated at DB and swapped faulty switch mechs for new.
MSA-DTWD | WA5099100 | 2 | AWB Co. | No power to aircon needs electrician | Electrical | General Electrical | 197.32 | Pass | Pass | 0 | 0 | 1 | 2022-02-01 14:15 | 2022-02-04 17:00 | 2022-02-03 09:00 | 2022-02-04 17:00 | 2022-02-03 10:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works. Located room. Tested aircon timer switch. Everything ok. Tested aircon. Power to unit. Test ran aircon. Working fine. Lady in office did inform there was roof works a few days prior. Could have been something to do with that. Unit is now working correctly **job complete**
MSA-DTWD | WA5099107 | 1 | Building Automation & Electrical Services Pty Ltd | Check supplied chiller 1 water valve solenoid not dispalying on BMS | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 1 | 2022-02-01 14:23 | 2022-02-02 17:00 | 2022-02-02 07:30 | 2022-02-02 17:00 | 2022-02-02 08:30 |  |  | Check supplied chiller 1 water valve solenoid not dispalying on BMS
MSA-DTAG | WA5100384 | 2 | Midolo Building Services | Level 4 - Court 42 - dock chair is loose | Furniture | Indoor Furniture | 167.49 | Pass | Pass | -1 | -1 | 1 | 2022-02-02 13:04 | 2022-02-07 17:00 | 2022-02-03 12:45 | 2022-02-07 17:00 | 2022-02-03 13:45 |  |  | REPAIRS MADE TO RESECURE SEAT
MSA-DTWD | WA5100625 | 2 | Equans Mechanical Services Australia | Level 3 -Staff room A312 - Air con not working | Air Conditioning | Room Air Conditioners | 120.35 | Fail | Fail | 16 | 16 | 1 | 2022-02-02 16:33 | 2022-02-07 17:00 | 2022-05-30 08:00 | 2022-02-07 17:00 | 2022-05-30 09:00 |  |  | COMPLETED INSPECTION - NO FAULT FOUND AND WORKING WITHPOUT FAULT
MSA-DTWD | WA5100910 | 2 | AHS Services WA Pty Ltd (Anchor) | Replace button female cubicle one A Block East end Ground | Plumbing & Drainage | Water | 130.82 | Pass | Pass | 0 | 0 | 1 | 2022-02-03 08:01 | 2022-02-08 17:00 | 2022-02-08 09:00 | 2022-02-08 17:00 | 2022-02-08 10:00 |  |  | 1st female cubicle grad floor.Removed button and found spring had come loose.Cleaned up, refitted and tested
MSA-DTWD | WA5101758 | 2 | Equans Mechanical Services Australia | Fault in Air con supply air Number 9 | Air Conditioning | Building HVAC Maintenance (Major Plant) | 125.1 | Fail | Fail | 6 | 6 | 1 | 2022-02-03 14:23 | 2022-02-08 17:00 | 2022-03-23 08:00 | 2022-02-08 17:00 | 2022-03-23 09:00 |  |  | ATTENDED SITE, SIGNED IN AND ACCESSED THE MECHANICAL PLANTROOM. FOUND THE FUSEBLOWN AND CIRCUIT BREAKER TRIPPED. REPLACED FUSE AND RESET CIRCUIT BREAKER.RECORDED THE AMP DRAWS AND MONITORED THE RUNNING OPERATION, RUNNING AS PERNORMAL AND AMP DRAWS WITHIN RANGE.
MSA-DTWD | WA5101861 | 1 | Damian Rak Electrical Pty Ltd | faulty RCD | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1 | 2022-02-03 15:52 | 2022-02-04 17:00 | 2022-02-04 15:00 | 2022-02-04 17:00 | 2022-02-04 16:00 |  |  | job completed - replace RCD GPO
MSA-DTWD | WA5101870 | 2 | Damian Rak Electrical Pty Ltd | Flat A and B - Faulty lights will not turn off | Electrical | General Electrical |  | Fail | Fail | 37 | 37 | 1 | 2022-02-03 16:00 | 2022-02-08 17:00 | 2022-10-28 13:30 | 2022-02-08 17:00 | 2022-10-28 14:30 |  |  | Completed
MSA-DTAG | WA5106653 | 2 | Schindler Lifts Australia | Ground - lift 4 - lift 4 is showing out of service | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-02-07 10:06 | 2022-02-10 17:00 | 2022-02-07 12:30 | 2022-02-10 17:00 | 2022-02-07 13:30 |  |  | to be closed out at $0 cost
MSA-DTAG | WA5106678 | 1 | Australian HVAC Services Pty. Ltd. | Registry / Court Rooms - Aircon isn’t working, hasn’t turned on | Air Conditioning | Building HVAC Maintenance (Major Plant) | 187.61 | Pass | Pass | 0 | 0 | 1 | 2022-02-07 10:21 | 2022-02-08 17:00 | 2022-02-07 12:30 | 2022-02-08 17:00 | 2022-02-07 13:30 |  |  | Checked controls while onsite carrying out pac 1& 2 repairs. Found bms & units running normally on control, suspect lower ambient temp changed how operation of unit is perceived
MSA-DCA | WA5108054 | 1 | Critical Fire Protection & Training | Stage Door reception - FIP - FIP fault - Dirty smoke detector may need replacment. M1180 | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-02-08 11:15 | 2022-02-09 17:00 | 2022-02-08 11:40 | 2022-02-09 17:00 | 2022-02-08 12:40 |  |  | Fire alarm and fault on panel. Zone was isolated smoke used for rehearsal. Reset panel. Dirty detector at stage door. Changed detector from theatre stock . Panel normal. Waited 15 minutes to confirm.
MSA-DTWD | WA5108622 | 1 | BAKE-QUIP PTY LTD | Convention leaking water and not working | Equipment | Catering Equipment | 230 | Pass | Pass | 0 | 0 | 1 | 2022-02-08 15:21 | 2022-02-09 17:00 | 2022-02-09 12:00 | 2022-02-09 17:00 | 2022-02-09 13:00 |  |  | Refer to service report - need another contactor to attend - Water Filtration unit issue not the Oven.
MSA-DCA | WA5108668 | 1 | Critical Fire Protection & Training | Ground Floor - Foyer - Fault in area 18 - Fire panel fault | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-02-08 16:07 | 2022-02-09 17:00 | 2022-02-09 08:00 | 2022-02-09 17:00 | 2022-02-09 09:00 |  |  | On arrival fire panel has no latched faults, no SYS1 faults logged on CodeRed and CodeRed operating correctlyInspected zone 18 no evident causes for alarm/fault in zone.Contacted FAMS- to investigate fault/alarms loggedFAMS reported last logged fault - Power outage (power supply fault)06.02.22 @12:09 Self Restored 06/02/2022 @ 16:04Panel sitting normal on arrival and departure
MSA-DCA | WA5108699 | 2 | Techworks Electrical | Geology lab - grounds level - cleaners store - faulty light see notes | Electrical | Lighting, Internal | 152.07 | Pass | Pass | 0 | 0 | 1 | 2022-02-08 16:58 | 2022-02-11 17:00 | 2022-02-10 11:00 | 2022-02-11 17:00 | 2022-02-10 12:00 |  |  | Replaced faulty light switch with new Clipsal push button
MSA-DCA | WA5109973 | 2 | Earth & Water Pty Ltd | Ground - External - Urban Orchard - see details below | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | -1 | -1 | 1 | 2022-02-09 14:43 | 2022-02-14 17:00 | 2022-02-10 11:00 | 2022-02-14 17:00 | 2022-02-10 12:00 |  |  | damaged drip line in urban orchard
MSA-DTWD | WA5111636 | 2 | SENTINEL LOCK SERVICE PTY LTD | B Block - Ground - BG21 - Door Lock keeps jamming | Security | Locksmith | 145.09 | Pass | Pass | 0 | 0 | 1 | 2022-02-10 09:45 | 2022-02-15 17:00 | 2022-02-14 13:30 | 2022-02-15 17:00 | 2022-02-14 14:30 |  |  | B Block - BG21 - Lock jamming.Lock repaired.
MSA-DTWD | WA5115897 | 2 | BAKE-QUIP PTY LTD | E-Block Restaurant underbench glass washer stuck on washing cycle | Equipment | Catering Equipment | 230 | Fail | Fail | 0 | 0 | 1 | 2022-02-11 09:57 | 2022-02-16 17:00 | 2022-02-17 14:00 | 2022-02-16 17:00 | 2022-02-17 15:00 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA5116033 | 2 | AWB Co. | C Block - Ground - C3 Servery - Heat lamp in Bain Marie has blown | Electrical | General Electrical | 223.16 | Pass | Pass | 0 | 0 | 1 | 2022-02-11 10:50 | 2022-02-16 17:00 | 2022-02-16 15:00 | 2022-02-16 17:00 | 2022-02-16 16:00 |  |  | Attended site signed in. Contacted fm and found job area. Replaced lamps with new and put anti seize on tombstones for better connectionTested ok informed site FM of job completion **job complete**
MSA-DTAG | WA5116310 | 2 | AWB Co. | Level 10 - various - see details below - | Electrical | General Electrical | 235.6 | Pass | Pass | 0 | 0 | 1 | 2022-02-11 13:33 | 2022-02-16 17:00 | 2022-02-15 14:45 | 2022-02-16 17:00 | 2022-02-15 15:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Replaced multiple 18w fluros throughout lvl 10 as requested by site. Notified site of completion. **job complete**
MSA-DTWD | WA5116316 | 2 | Equans Mechanical Services Australia | Block 8 - First Floor - 8F55 - R/H a/c not working | Air Conditioning | Room Air Conditioners | 204.07 | Fail | Fail | 2 | 2 | 1 | 2022-02-11 13:39 | 2022-02-16 17:00 | 2022-03-02 09:30 | 2022-02-16 17:00 | 2022-03-02 10:30 |  |  | LOCATE CLASSROOM, TURN ON BOTH A/C'S AND CHECK OPERATION. FOUND RIGHT HAND UNIT NOT COOLING, USE REMOTE CONTROL TO CHECK SETTINGS. MONITOR FOR A PERIOD OF TIME, UNIT IS COOLING. ACCESS CONDENSING UNIT, MONITOR RUNNING PRESSURES AND MONITOR COMPRESSOR AMP DRAWS. ALL OK AT THIS TIME.
MSA-DTWD | WA5116337 | 2 | Equans Mechanical Services Australia | Block 6 - Ground - 6F42 classroom - A/C leaking water | Air Conditioning | Room Air Conditioners | 204.07 | Fail | Fail | 2 | 2 | 1 | 2022-02-11 13:56 | 2022-02-16 17:00 | 2022-03-02 10:30 | 2022-02-16 17:00 | 2022-03-02 11:30 |  |  | LOCATE CLASSROOM AND INSPECT UNIT, REMOVE COVERS AND FOUND DRAIN HAD COME LOOSE FROM DRAIN TRAY. RE-CONNECT DRAIN AND TEST OPERATION, MONITOR FOR A PERIOD OF TIME. ALL OK ATTHIS TIME.
MSA-DTWD | WA5116342 | 1 | Damian Rak Electrical Pty Ltd | BLD 801 -Bathroom - Faulty light switch | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-02-11 14:00 | 2022-02-14 17:00 | 2022-02-11 15:00 | 2022-02-14 17:00 | 2022-02-11 16:00 |  |  | Job completed
MSA-DFES | WA5126843 | 0 | Anvil Doors | Roller Door 1 - smoke was pouring out of door, which caught fire from the motor | Building | Fire Door | 4927.34 | Pass | Pass | 0 | 0 | 1 | 2022-02-14 10:11 | 2022-02-14 12:11 | 2022-02-14 12:00 | 2022-02-14 14:11 | 2022-02-14 13:00 |  |  | Attended Perth Fire Station.Checked door number 1 and found defective Logic Control (PLC). Door requires a replacement GLME2 Logic controller, EB1 expansion Board and 3 x timer contacts. This door has been left tagged out of operation.Please see attached service report and signature slip.Please see attached BRAF- Quote and Service Report.Attended and completed controller replacement-- Please see attached Signature Slip and Service report
MSA-DTWD | WA5128079 | 1 | Equans Mechanical Services Australia | Room B5 - split system A/C will not start. | Air Conditioning | Ducted Split System | 204.07 | Fail | Fail | 0 | 0 | 1 | 2022-02-14 15:48 | 2022-02-15 17:00 | 2022-02-17 15:00 | 2022-02-15 17:00 | 2022-02-17 16:00 |  |  | LOGGED ON TO SITE. DISCUSSED ISSUE WITH MAINTENANCE ANDWAS INFORMED THAT THERE IS A FAULT LIGHT IN THE MSSB ON FIRST FLOOR AND T114 ROOM IS WARM. INVESTIGATED AND FOUND FCU CONTRACTOR OVERLOAD HAD TRIPPED. RESET AND CHECKED AMP DRAWS AND FOUND TO BE OK. TIGHTENED ALL ELECTRICAL CONNECTIONS. CHECKED AND FOUND FCU NOW OPERATING.MONITORED FOR SOME TIME AND RECHECKED AMP DRAWS, INCLUDING START UP AMPS. ALL FOUND TO BE WITHIN AMP SETTING RANGE. COMPLETED PAPERWORK AND LOGGED OFF JOB.
MSA-DCA | WA5128155 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Jubilee - Reflections Gallery - Main door will not close (Magnetic door release fauly) | Security | Keys & Access | 686.05 | Fail | Fail | 0 | 0 | 1 | 2022-02-14 16:03 | 2022-02-15 17:00 | 2022-02-16 13:30 | 2022-02-15 17:00 | 2022-02-16 14:30 |  |  | Works completed by Honeywell
MSA-DFES | WA5128309 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Administration - Ground - Male Toilet Near Reception -Sink draining very slowly | Plumbing & Drainage | Toilets/Cisterns | 140.05 | Pass | Pass | 0 | 0 | 1 | 2022-02-14 17:13 | 2022-02-21 17:00 | 2022-02-21 12:00 | 2022-02-21 17:00 | 2022-02-21 13:00 |  |  | Slow draining sink near reception in the male toilets ground floor I have plunged The sink and cleared the blockage what appears to be some gunk after I’ve tested everything is now working correctly
MSA-DTWD | WA5133225 | 2 | Falcetta Plumbing and Gas | T block - T048 - The air conditioner drain does not connect / flow into the tun dish under the sink. | Plumbing & Drainage | Water | 190.12 | Pass | Pass | 0 | 0 | 1 | 2022-02-15 08:27 | 2022-02-18 17:00 | 2022-02-18 12:00 | 2022-02-18 17:00 | 2022-02-18 13:00 |  |  | installed waterless trap and adapt to pipe offsets
MSA-DTWD | WA5133622 | 1 | Equans Mechanical Services Australia | BMS aircon - Ground - 205,215,216,219,229 - air con not cooling | Air Conditioning | Building HVAC Maintenance (Major Plant) | 120.35 | Fail | Fail | 1 | 1 | 1 | 2022-02-15 12:29 | 2022-02-16 17:00 | 2022-02-23 15:00 | 2022-02-16 17:00 | 2022-02-23 16:00 |  |  | Gathered tools and equipment, started operation and fault check on vrv controlling areas concerned. Started and completed electrical and resistance checks. No new faults located. Waiting on one compressor change to be completed on VRV that was taken off line. Only ambient conditions causing problems and doors being left open. All will be resolved when compressor replaced and VRV put back on line. Completed paperwork.
MSA-DTWD | WA5133763 | 2 | Lane's Plumbing | BLD 822 - Flat B Bathroom - Leaking Shower | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1 | 2022-02-15 13:50 | 2022-02-18 17:00 | 2022-02-15 15:00 | 2022-02-18 17:00 | 2022-02-15 16:00 |  |  | job completed - repaired leaking tap
MSA-DTWD | WA5133787 | 1 | Equans Mechanical Services Australia | Level 1 - AF04 - AC4 heating not cooling, everything looks right on BMS | Air Conditioning | Room Air Conditioners | 120.35 | Fail | Fail | 0 | 0 | 1 | 2022-02-15 14:06 | 2022-02-16 17:00 | 2022-02-17 09:00 | 2022-02-16 17:00 | 2022-02-17 10:00 |  |  | Checked operation all ok, A/C 4 SUPPLIES AF04& AF05. AF04 has main control and is unoccupied. AF05 has a averaging stat and is occupied and has computer's. AF04 getting to temp quicker causing other room to feel warm. No operation fault found. Temperature on BMS set to compensate accordingly.
MSA-DCA | WA5133887 | 1 | Techworks Electrical | Ground – external - External lights in front of cafe - 2 x lollipop lights are not working in front | Electrical | General Electrical | 245.91 | Pass | Pass | 0 | 0 | 1 | 2022-02-15 17:00 | 2022-02-16 17:00 | 2022-02-16 13:30 | 2022-02-16 17:00 | 2022-02-16 14:30 |  |  | Repaired faulty lights
MSA-DTWD | WA5141283 | 1 | Equans Mechanical Services Australia | ET16 Classroom - Split System AC not working see notes | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 1 | 2022-02-16 08:57 | 2022-02-17 17:00 | 2022-02-17 12:00 | 2022-02-17 17:00 | 2022-02-17 13:00 |  |  | ET16: TRIPPED BREAKER ON ROOF - RESET AND MONITORED. AMPS WELL UNDER BREAKER SIZE - UNIT OPERATING AS NORMAL
MSA-DTWD | WA5141364 | 0 | Critical Fire Protection & Training | central south side building - external - fire hydrant line - sprung a leak | Fire Protection Services | Fire Protection - Monitor System | 585.8 | Fail | Pass | 0 | 0 | 1 | 2022-02-16 09:43 | 2022-02-16 11:43 | 2022-02-16 12:00 | 2022-02-16 13:43 | 2022-02-16 13:00 |  |  | Attended site to investigate leak on hydrant system.Hydrant leak near hydrant in the middle of a block. There is a pin holeleak on a old hydrant riser.Could not repair today because of a total fire ban. I will need to weld upthe pipe.We have stopped the leak with a temporary fix however this will need tobe repaired.Will return to site next week once fire ban is lifted to rectify. 16/2 - BRAF submitted and never accepted
MSA-DTAG | WA5141483 | 1 | Water2water Pty Ltd | Ground kitchen - Kitchen in Judicial corridor - Hot water dispenser above the sink has stopped worki | Plumbing & Drainage | Water | 161.54 | Pass | Pass | 0 | 0 | 1 | 2022-02-16 10:29 | 2022-02-17 17:00 | 2022-02-16 13:50 | 2022-02-17 17:00 | 2022-02-16 14:50 |  |  | Removed air lock from hot water system to restore normal flow A40201149 Zip wallmount
MSA-DTAG | WA5141571 | 1 | OCS SERVICES PTY LTD | Basement - Cell 3 - Detention - COVID clean of cell 3 | Cleaning | Emergency Cleans |  | Pass | Fail | 0 | 0 | 1 | 2022-02-16 11:09 | 2022-02-17 17:00 | 2022-02-17 17:00 | 2022-02-17 17:00 | 2022-02-17 18:00 |  |  | Completed
MSA-DTAG | WA5141619 | 2 | Midolo Building Services | Level 3 - Court 38 - Door hinge cover has come off the door | Building | General Building | 144.92 | Pass | Pass | -1 | -1 | 1 | 2022-02-16 11:31 | 2022-02-21 17:00 | 2022-02-17 08:15 | 2022-02-21 17:00 | 2022-02-17 09:15 |  |  | RESECURED COVER PLATE
MSA-DTWD | WA5142126 | 3 | Building Automation & Electrical Services Pty Ltd | BMS - Rooms 325-327 - classroom too cold | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 1 | 2022-02-16 13:32 | 2022-02-23 17:00 | 2022-02-23 15:00 | 2022-02-23 17:00 | 2022-02-23 16:00 |  |  | Completed
MSA-DCA | WA5142323 | 2 | Protek 24/7 Building & Maintenance | Venue Management Office - office windows collapsed onto venue staff hands when trying to open. | Building | Windows | 570.5 | Pass | Pass | 0 | 0 | 1 | 2022-02-16 14:28 | 2022-02-21 17:00 | 2022-02-18 09:30 | 2022-02-21 17:00 | 2022-02-18 10:30 |  | WACCES | repair collapsed office window
MSA-DCA | WA5142544 | 1 | Techworks Electrical | Mezzanine - Female toilets - LED EEL in female toilets is not working | Electrical | General Electrical | 341.33 | Pass | Pass | 0 | 0 | 1 | 2022-02-16 14:54 | 2022-02-17 17:00 | 2022-02-17 11:00 | 2022-02-17 17:00 | 2022-02-17 12:00 |  |  | Found light to be faulty, replaced like for like
MSA-DCA | WA5142620 | 0 | EQUANS Mechanical Services (WA) Pty Limited | both chillers are off, water temp risen by 10 degrees | Air Conditioning | Building HVAC Maintenance (Major Plant) | 204.08 | Pass | Pass | 0 | 0 | 1 | 2022-02-16 19:33 | 2022-02-16 21:33 | 2022-02-16 20:00 | 2022-02-16 23:33 | 2022-02-16 21:00 |  |  | Found system running on ETS, no faults on the local system and ETS supplying 7 degree chilled water to the theatre. Set points satisfied with systems operating fine. Will look into local mode in business hours.
MSA-DFES | WA5151127 | 2 | AWB Co. | Main Admin - Ground - North Door - External Door is not self Closing | Building | Doors | 140 | Pass | Pass | 0 | 0 | 1 | 2022-02-17 11:02 | 2022-02-22 17:00 | 2022-02-21 12:00 | 2022-02-22 17:00 | 2022-02-21 13:00 |  |  | Attended site, filled out JSA, adjusted door lock and receiver where the lock was to tight to frame and rubbing, drilled out rivets to frame and pushed over to allow more gap on frame and door. Door closing correctly.
MSA-DTWD | WA5151561 | 2 | Lane's Plumbing | BLD 876 - Outside piggery office - Faulty Tap | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 1 | 2022-02-17 14:05 | 2022-02-22 17:00 | 2022-02-17 16:30 | 2022-02-22 17:00 | 2022-02-17 17:30 |  |  | Job completed - replaced faulty taps
MSA-DTWD | WA5151896 | 0 | Techworks Plumbing | Block S - Fire hydrant has burst and unable to isolate. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 175.85 | Pass | Pass | 0 | 0 | 1 | 2022-02-17 17:08 | 2022-02-17 19:08 | 2022-02-17 18:00 | 2022-02-17 21:08 | 2022-02-17 19:00 |  |  | Attend call out Murdoch tafe for fire hydrant issues
MSA-DCA | WA5155394 | 0 | EQUANS Mechanical Services (WA) Pty Limited | RO Tank Hi level alarm - Value 0 | Building | Materials | 204.08 | Pass | Pass | 0 | 0 | 1 | 2022-02-17 23:43 | 2022-02-18 01:43 | 2022-02-18 00:30 | 2022-02-18 03:43 | 2022-02-18 01:30 |  |  | Checked out BMS, with system showing RO hi limit fault. Checked the tank, water level as normal but slightly adjusted float valves to lower tank level. Tank had stopped filling at a normal level. Unable to reset the hi limit alarm. Will follow up in business hours.
MSA-DTWD | WA5163635 | 1 | Equans Mechanical Services Australia | H Block - Ground - H10 - Aircon not working | Air Conditioning | Room Air Conditioners | 120.35 | Fail | Fail | 0 | 0 | 1 | 2022-02-18 10:39 | 2022-02-21 17:00 | 2022-02-23 10:15 | 2022-02-21 17:00 | 2022-02-23 11:15 |  | WCAPPR | Completed checks on unit found to be nuisance tripping, had site get electrical test done. Returned they found isolator failed and replaced also RCD failure also replaced. All remaining tests all ok.
MSA-DTWD | WA5164047 | 3 | Falcetta Plumbing and Gas | Level 2 - Kitchen - Water overflowing, possible blockage in drain pipe | Plumbing & Drainage | Drainage | 125.12 | Pass | Pass | -1 | -1 | 1 | 2022-02-18 15:23 | 2022-02-25 17:00 | 2022-02-21 12:00 | 2022-02-25 17:00 | 2022-02-21 13:00 |  |  | Repaired damaged internal waste to trough near kitchen
MSA-DFES | WA5164113 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Dorm 5 + D - please see details below | Electrical | General Electrical | 216.95 | Pass | Pass | 0 | 0 | 1 | 2022-02-18 16:43 | 2022-02-23 17:00 | 2022-02-22 14:00 | 2022-02-23 17:00 | 2022-02-22 15:00 |  |  | Arrived on site at 1400 to attend lights not working in Dorm 5 bedroom and dorm 3 bathroom. Amended driver connection inDorm 5 and re-energised light fitting. Dorm 3 light tube replaced with stock from van and light reenergised. Left site at 1500.
MSA-DTWD | WA5175095 | 1 | SENTINEL LOCK SERVICE PTY LTD | Block 1 - Ground - East end entry door - Won’t unlock for auto operation | Security | Locksmith | 177.19 | Pass | Pass | 0 | 0 | 1 | 2022-02-21 10:16 | 2022-02-22 17:00 | 2022-02-21 13:30 | 2022-02-22 17:00 | 2022-02-21 14:30 |  |  | Block 1 - GF - entry door will not unlock.
MSA-DTWD | WA5175534 | 1 | Milners Tree Solutions Pty Ltd | block 6 car park - fence line - fallen tree onto neighboring property | Landscaping & Gardening | Tree Lopping | 640 | Pass | Pass | 0 | 0 | 1 | 2022-02-21 12:18 | 2022-02-22 17:00 | 2022-02-22 06:45 | 2022-02-22 17:00 | 2022-02-22 07:45 |  |  | FALLEN LARGE LIMB REMOVED FROM NEIGHBORING PROPERTY
MSA-DTAG | WA5188551 | 1 | Sapio Pty Ltd | Level 1 - President Buss chambers - Duress alarm – key is stuck and cannot be removed. | Security | Security Management System | 139.99 | Pass | Pass | 0 | 0 | 1 | 2022-02-23 09:44 | 2022-02-24 17:00 | 2022-02-24 08:00 | 2022-02-24 17:00 | 2022-02-24 09:00 |  |  | Replaced duress button and tested OK.Job completed.
MSA-DTWD | WA5188949 | 2 | Water2water Pty Ltd | zip boil unit water pressure has dropped | Plumbing & Drainage | Water | 255.81 | Pass | Pass | 0 | 0 | 1 | 2022-02-23 12:47 | 2022-02-28 17:00 | 2022-02-28 13:30 | 2022-02-28 17:00 | 2022-02-28 14:30 |  |  | replaced Tap Kit A40421667J / A403133519 Zip Hydroboil Mclarty P Block Ground Floor Kitchen
MSA-DTAG | WA5195620 | 1 | Sapio Pty Ltd | Marriage reception/ duress alarm - alarm goes of intermittently | Security | Monitoring | 145 | Pass | Pass | 0 | 0 | 1 | 2022-02-28 13:40 | 2022-03-01 17:00 | 2022-02-28 14:00 | 2022-03-01 17:00 | 2022-02-28 15:00 |  |  | Found a broken connection inside the duress button.Fixed problem and reset.
MSA-DTWD | WA5195685 | 2 | Protek 24/7 Building & Maintenance | Glass external door next to disable toilets frame is very wobbly | Building | Doors | 196 | Pass | Pass | 0 | 0 | 1 | 2022-02-28 14:22 | 2022-03-03 17:00 | 2022-03-03 09:30 | 2022-03-03 17:00 | 2022-03-03 10:30 |  |  | Repair glass to external door
MSA-DFES | WA5195712 | 2 | Australian HVAC Services Pty. Ltd. | Meeting Room - 2x fans are not working | Air Conditioning | Room Air Conditioners | 130.05 | Pass | Pass | 0 | 0 | 1 | 2022-02-28 14:50 | 2022-03-03 17:00 | 2022-03-02 08:00 | 2022-03-03 17:00 | 2022-03-02 09:00 |  |  | Attended service call, found fans in meeting room are working. Adjusted blades as out of balance, cannot eliminate all wobble due to design,( rubber mounted hanging pivot) allows some movement
MSA-DTWD | WA5195729 | 1 | BAKE-QUIP PTY LTD | A120 Cafe Kitchen - Lights on the Bain maire have tripped | Equipment | Catering Equipment | 245 | Pass | Pass | 0 | 0 | 1 | 2022-02-28 15:00 | 2022-03-01 17:00 | 2022-03-01 14:15 | 2022-03-01 17:00 | 2022-03-01 15:15 |  |  | REFER TO SERVICE REPORT.
MSA-DCA | WA5199106 | 2 | Protek 24/7 Building & Maintenance | Urban Orchard garden - garden bed sign hass been pulled out - see notes | Signage | General Signage | 202.09 | Pass | Pass | 0 | 0 | 1 | 2022-03-01 07:48 | 2022-03-03 17:00 | 2022-03-03 13:30 | 2022-03-03 17:00 | 2022-03-03 14:30 |  |  | Replace Garden bed sign
MSA-DTWD | WA5200685 | 1 | Precise Air Group | U010 - Fibre glass has dislodged in the evap unit | Air Conditioning | Evaporative Coolers | 193.62 | Pass | Pass | 0 | 0 | 1 | 2022-03-02 08:29 | 2022-03-03 17:00 | 2022-03-02 11:00 | 2022-03-03 17:00 | 2022-03-02 12:00 |  |  | Removed insulation from dropper
MSA-DCA | WA5201091 | 1 | Techworks Electrical | Loading bay 7 -Quarantine Room - Faulty light switch inside room. Vertical double switch | Electrical | General Electrical | 138.37 | Pass | Pass | 0 | 0 | 1 | 2022-03-02 11:30 | 2022-03-03 17:00 | 2022-03-02 15:30 | 2022-03-03 17:00 | 2022-03-02 16:30 |  |  | Identified faulty light switch that crackles and sparked once operated, isolated circuit and replaced switch mech.tested and confirmed correct operation of the above works.
MSA-DTWD | WA5201340 | 2 | SENTINEL LOCK SERVICE PTY LTD | Block 2 - Room T1 - Current faulty external door knobs need to be replaced with levers. | Security | Access Control | 280.8 | Fail | Fail | 1 | 1 | 1 | 2022-03-02 13:53 | 2022-03-08 17:00 | 2022-03-17 12:30 | 2022-03-08 17:00 | 2022-03-17 13:30 |  | WACCES | BLOCK 2 - Room T1 - Current faulty external door knobs need to be replaced with levers
MSA-DTWD | WA5201342 | 2 | SENTINEL LOCK SERVICE PTY LTD | Block 2 - Room T2 - Current faulty external door knobs need to be replaced with levers. | Security | Access Control | 280.8 | Fail | Fail | 1 | 1 | 1 | 2022-03-02 13:56 | 2022-03-08 17:00 | 2022-03-17 12:30 | 2022-03-08 17:00 | 2022-03-17 13:30 |  | WACCES | Block 2 - Room T2 - Current external door knobs are faulty - to be replaced with levers.
MSA-DTWD | WA5202880 | 0 | Nessco Pressure Systems | plant - oil & gas - Air compressor panel alarm keeps activating | Equipment | Compressors, Generators |  | Fail | Fail | 0 | 0 | 1 | 2022-03-03 09:10 | 2022-03-03 11:10 | 2022-03-04 09:00 | 2022-03-03 13:10 | 2022-03-04 10:00 |  |  | job completed - We need a service manual for intellysys controller. Unable to reset or acknowledge seperator alarm as machine is required to be not running. But cannot be switched off due to lectruers and students requiring it running. Compressor is running and doesn't have any faults at time of attendance. Unable to inspect apt6 fault as it requires isolation once again cannot be done today because compressor is being used
MSA-DFES | WA5203740 | 2 | Complete Pest Management Services | Whole of Station - scorpions sited on site | Pest Control | Specialist Pest | 264.71 | Pass | Pass | -1 | -1 | 1 | 2022-03-03 16:04 | 2022-03-09 17:00 | 2022-03-04 13:30 | 2022-03-09 17:00 | 2022-03-04 14:30 |  |  | Inspected and treated the tunic room and the fence line for scorpions
MSA-DFES | WA5203754 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilet - Near SimCen - Left hand Toilet System broken - see notes below | Plumbing & Drainage | Toilets/Cisterns | 287.23 | Fail | Fail | 1 | 1 | 1 | 2022-03-03 16:35 | 2022-03-11 17:00 | 2022-03-16 09:30 | 2022-03-11 17:00 | 2022-03-16 10:30 |  |  | Attended site for male toilets near Sim centre left-hand cubicle toilet cistern broken I replace broken cistern with a new one and tested cleaned up and packed up
MSA-DFES | WA5204953 | 3 | Protek 24/7 Building & Maintenance | Warehouse door has a corroded sill and the metalwork is flaking away (potential hazard)-see notes | Building | Doors | 119.5 | Pass | Pass | -1 | -1 | 1 | 2022-03-04 16:11 | 2022-03-14 17:00 | 2022-03-10 13:30 | 2022-03-14 17:00 | 2022-03-10 14:30 |  |  | Repairs to warehouse door
MSA-DCA | WA5205096 | 0 | Critical Fire Protection & Training | fault on deisel Fire pump | Fire Protection Services | Fire Protection - Monitor System | 533.46 | Pass | Pass | 0 | 0 | 1 | 2022-03-06 10:53 | 2022-03-06 12:53 | 2022-03-06 12:00 | 2022-03-06 14:53 | 2022-03-06 13:00 |  |  | On arrival no pumps running. Upon investigation diesel has not been running, was at normal temperature, hours the same and fuel at 100%. Spoke to Claremont Fire Station and they advised it was the electric pump that was running. Water temp on electric pump was high so flushed system until water cooled. Check all hydrants and found one twin not secured to the East of block U. Some water residue present in hydrant. Suspect hydrant has been activated after locking wheel was vandalised. Re-secured - with 2x locking wheels. Advised DCA about damage to roller door caused by DFES gaining access. Recommend DCA ensure the pump is monitored by security. 2x Techs
MSA-DTAG | WA5207454 | 1 | Sapio Pty Ltd | Courtside - Ground - Entrance desk - PA System not operational | ICT/Audiovisual | General AV works | 130 | Pass | Pass | 0 | 0 | 1 | 2022-03-08 13:11 | 2022-03-09 17:00 | 2022-03-08 15:00 | 2022-03-09 17:00 | 2022-03-08 16:00 |  |  | PA system had moved on to preset 1 when it should be on 2. Changed and tested.
MSA-DTWD | WA5209174 | 3 | AWB Co. | S Block - S109 - door squeaks badly | Building | General Building | 102.97 | Pass | Pass | -1 | -1 | 1 | 2022-03-09 14:42 | 2022-03-16 17:00 | 2022-03-10 12:30 | 2022-03-16 17:00 | 2022-03-10 13:30 |  |  | Replaced 2 old 100mm butt hinges and and replaced with new
MSA-DTWD | WA5214208 | 2 | ECO PLUMBING AND GAS PTY LTD | H007 - blocked floor waste drain the cool room | Plumbing & Drainage | Drainage | 141.28 | Pass | Pass | 0 | 0 | 1 | 2022-03-10 08:23 | 2022-03-15 17:00 | 2022-03-14 07:30 | 2022-03-15 17:00 | 2022-03-14 08:30 |  |  | cleared blockage
MSA-DFES | WA5215397 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Second floor - Mens toilet - last cubicle - toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 143.45 | Pass | Pass | 0 | 0 | 1 | 2022-03-10 11:45 | 2022-03-10 13:45 | 2022-03-10 12:30 | 2022-03-10 15:45 | 2022-03-10 13:30 |  |  | Went to second floor male toilets and unblocked far right hand side toilet tested and all clear
MSA-DFES | WA5226893 | 3 | MR POTHOLE | Driveway - sunken and pot holes see notes | Paving & Roadworks | Asphalt |  | Pass | Pass | -1 | -1 | 1 | 2022-03-14 14:48 | 2022-03-21 17:00 | 2022-03-16 09:10 | 2022-03-21 17:00 | 2022-03-16 10:10 |  |  | job completed - Repair sections of crazed asphalt at DFES Joondalup Fire Station 47 Drovers PI Joondalup2.3m x 1.2m area
MSA-DTWD | WA5230801 | 3 | Critical Fire Protection & Training | Entry foyer - Level 2 - Fault on EWIS panel | Fire Protection Services | Fire Protection - Monitor System | 2165.9 | Pass | Pass | -1 | -1 | 1 | 2022-03-15 07:53 | 2022-03-21 17:00 | 2022-03-15 09:00 | 2022-03-21 17:00 | 2022-03-15 10:00 |  |  | Carried out checks of system applicable zone. Noted speaker notinstalled correctly, left above ceiling, reinstalled- not issue withfault.Carried out checks suspect internal card issue -Re-attended - Supply and install QE90 Transformer Module
MSA-DTWD | WA5231109 | 2 | Lane's Plumbing | BLD 859 - Water meter faulty outside BLD 859 | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1 | 2022-03-15 09:23 | 2022-03-18 17:00 | 2022-03-15 12:00 | 2022-03-18 17:00 | 2022-03-15 13:00 |  |  | REPAIR FAULTY WATER Meter OUTSIDE BUILDING 859
MSA-DTWD | WA5231381 | 3 | Protek 24/7 Building & Maintenance | Large toilet roll holder to be re-attached to the wall | Building | Materials | 207 | Pass | Pass | -1 | -1 | 1 | 2022-03-15 10:56 | 2022-03-22 17:00 | 2022-03-15 12:30 | 2022-03-22 17:00 | 2022-03-15 13:30 |  |  | Reinstalled toilet roll holder
MSA-DCA | WA5231489 | 1 | Automatic Fire Protection (ARA) | Foyer – Fire Indication Panel - contacted site to advise. Please investigate | Fire Protection Services | Fire Protection - Monitor System | 345.18 | Pass | Pass | 0 | 0 | 1 | 2022-03-15 11:48 | 2022-03-16 17:00 | 2022-03-16 10:30 | 2022-03-16 17:00 | 2022-03-16 11:30 |  |  | L1S7 intermittent missing fault. Replaced 1x XP95 smoke, fault cleared
MSA-DFES | WA5238695 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | engine room (room 30) - second tanks charger has no power | Electrical | General Electrical | 75.24 | Pass | Pass | 0 | 0 | 1 | 2022-03-16 08:18 | 2022-03-17 17:00 | 2022-03-16 13:15 | 2022-03-17 17:00 | 2022-03-16 14:15 |  |  | Onsite 1335 signed in and shown charger with suspected fault. Tested voltage at all 4 outlets 2 large appliances running at 28v 2 small running at 14v checked fuse on charger. Checked voltage under load. Plugged charger into appliance but not amp draw was registered on charger. Got staff onsite to swap 2 small appliances and confirmed fault is internal to unit and not external. Informed staff and signed out at 1405
MSA-DTAG | WA5239116 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 11 - Bathroom - Shower handle in bathroom keeps falling off | Plumbing & Drainage | Water | 130.82 | Pass | Pass | 0 | 0 | 1 | 2022-03-16 10:08 | 2022-03-21 17:00 | 2022-03-18 07:15 | 2022-03-21 17:00 | 2022-03-18 08:15 |  |  | Found grub screw and re fitted handle.Shower level 11
MSA-DTWD | WA5239660 | 2 | Protek 24/7 Building & Maintenance | A block - A265 - Replace small section of carpet rotting in passage near water cooler with vinyl | Flooring | Vinyl | 2550.5 | Pass | Pass | -1 | -1 | 1 | 2022-03-16 14:06 | 2022-03-21 17:00 | 2022-03-17 11:00 | 2022-03-21 17:00 | 2022-03-17 12:00 |  | WACCES | Replace Rotting Carpet
MSA-DTWD | WA5239672 | 1 | High Tech Pest Control | Kendrew- A-Block car park has a bees nest in the tree base needs removing, next to disabled bay | Pest Control | General Pest | 239 | Pass | Pass | 0 | 0 | 1 | 2022-03-16 14:06 | 2022-03-17 17:00 | 2022-03-16 14:40 | 2022-03-17 17:00 | 2022-03-16 15:40 |  |  | Treatment to bee colony completed
MSA-DTAG | WA5239716 | 3 | Midolo Building Services | Soap Dispenser in Disable Tiolet leaking | Building | Internal Walls | 195.78 | Pass | Pass | -1 | -1 | 1 | 2022-03-16 14:57 | 2022-03-23 17:00 | 2022-03-17 13:30 | 2022-03-23 17:00 | 2022-03-17 14:30 |  |  | NEW SOAP DISPENSER INSTALLED
MSA-DCA | WA5255896 | 1 | Protek 24/7 Building & Maintenance | Main Building - Basement – Studio Underground - Studio Underground theatre | Building | General Building | 119.5 | Pass | Pass | 0 | 0 | 1 | 2022-03-17 10:35 | 2022-03-18 17:00 | 2022-03-18 08:45 | 2022-03-18 17:00 | 2022-03-18 09:45 |  |  | Tighten up screw
MSA-DTAG | WA5256210 | 3 | Elec Power Technologies | Clear alarms on UPS as per EATON recommendations reference to QT110125 | Security | Access Control |  | Fail | Fail | 1 | 1 | 1 | 2022-03-17 10:55 | 2022-03-24 17:00 | 2022-03-30 11:00 | 2022-03-24 17:00 | 2022-03-30 12:00 |  |  | Clear UPS alarms
MSA-DTWD | WA5257418 | 3 | AWB Co. | Ground - Metal Fab 2 workshop - 3 phase power point for plasma cutter not working | Electrical | General Electrical | 323.61 | Pass | Pass | -1 | -1 | 1 | 2022-03-17 11:48 | 2022-03-24 17:00 | 2022-03-18 14:00 | 2022-03-24 17:00 | 2022-03-18 15:00 |  |  | Attended site and signed in. Completed JSA. Located metal fab. Found faulty 3 phase outlet, tested to find power not switching at the isolator. Fuses all okay. RCD okay.. Located switchboard and isolated. Supply and replace with new 3 phase 32 amp switch. Reinstated power. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5258015 | 3 | Schindler Lifts Australia | Level 3 - Lift 4 - lift stuck on level 3 | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-03-17 13:36 | 2022-03-24 17:00 | 2022-03-17 14:00 | 2022-03-24 17:00 | 2022-03-17 15:00 |  |  | to be closed out at $0 cost
MSA-DTWD | WA5258092 | 3 | ADVANCED LOCK & KEY | A block, Level 2 - A205 - faulty lock to A205 door | Security | Locksmith | 344.57 | Pass | Pass | 0 | 0 | 1 | 2022-03-17 14:56 | 2022-03-24 17:00 | 2022-03-23 11:40 | 2022-03-24 17:00 | 2022-03-23 12:40 |  |  | Replaced mortice lock on a206 with new 3572sc and x cam
MSA-DTWD | WA5270950 | 2 | Damian Rak Electrical Pty Ltd | Pool Shed - faulty light | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-03-18 09:10 | 2022-03-23 17:00 | 2022-03-23 11:00 | 2022-03-23 17:00 | 2022-03-23 12:00 |  |  | job completed - replaced LED battern
MSA-DTAG | WA5278270 | 1 | OCS SERVICES PTY LTD | Level 3 CATS & Staff toilet - Full disinfectant Covid 19 clean required | Cleaning | Cleaning |  | Pass | Fail | 0 | 0 | 1 | 2022-03-18 14:02 | 2022-03-21 17:00 | 2022-03-21 17:00 | 2022-03-21 17:00 | 2022-03-21 18:00 |  | WACCES | Covid clean
MSA-DTAG | WA5285790 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 4 - Near court 41 - Male Toilet - leaking into the bowl | Plumbing & Drainage | Toilets/Cisterns | 99.69 | Pass | Pass | -1 | -1 | 1 | 2022-03-21 10:15 | 2022-03-28 17:00 | 2022-03-21 15:00 | 2022-03-28 17:00 | 2022-03-21 16:00 |  |  | Replaced water wafer outlet washer to male toilet on level 4
MSA-DTAG | WA5286987 | 2 | Midolo Building Services | Level 8 - Staff bathroom - see details below | Building | General Building | 185.09 | Fail | Fail | 0 | 0 | 1 | 2022-03-22 09:09 | 2022-03-25 17:00 | 2022-03-28 13:15 | 2022-03-25 17:00 | 2022-03-28 14:15 |  |  | repair made to locking latch & door
MSA-DTAG | WA5287699 | 3 | Midolo Building Services | Ground - Pillar near legal assistance desk -Broken tile on pillar by legal assistance volunteer desk | Building | General Building | 183.81 | Pass | Pass | 0 | 0 | 1 | 2022-03-22 14:28 | 2022-03-29 17:00 | 2022-03-28 12:00 | 2022-03-29 17:00 | 2022-03-28 13:00 |  |  | re secured tile
MSA-DTWD | WA5288240 | 1 | SCAVENGER SUPPLIES PTY LTD | RETROSPECTIVE WORK ORDER - NO ATTENDANCE REQUIRED | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 94.14 | Pass | Pass | 0 | 0 | 1 | 2022-03-23 08:31 | 2022-03-24 17:00 | 2022-03-23 09:00 | 2022-03-24 17:00 | 2022-03-23 10:00 | 1 |  | COMPLETED 22/02/2022TECHNICIN ALREADY ON SITE-NO CALL OUT FEE CHARGED.NO REPAIRS REQUIRED-MONITORING CONDITION
MSA-DTWD | WA5288748 | 3 | Falcetta Plumbing and Gas | Level 2 - Creche bathroom - Tap leaking from spindle on left hand sink when turned on | Plumbing & Drainage | Materials | 205.12 | Pass | Pass | -1 | -1 | 1 | 2022-03-23 13:03 | 2022-03-30 17:00 | 2022-03-24 13:30 | 2022-03-30 17:00 | 2022-03-24 14:30 |  |  | replaced tap and installed mini stop
MSA-DTWD | WA5289455 | 2 | AHS Services WA Pty Ltd (Anchor) | A-Block - 2nd Floor - East Ladies toilets has a toilet continuously running | Plumbing & Drainage | Toilets/Cisterns | 158.32 | Pass | Pass | -1 | -1 | 1 | 2022-03-24 09:36 | 2022-03-29 17:00 | 2022-03-25 13:30 | 2022-03-29 17:00 | 2022-03-25 14:30 |  |  | Completed
MSA-DTWD | WA5290939 | 1 | Damian Rak Electrical Pty Ltd | BLD 822 - FLAT C - Lounge - Faulty Electrical Breaker | Electrical | General Electrical |  | Pass | Pass | 0 | 0 | 1 | 2022-03-25 13:07 | 2022-03-28 17:00 | 2022-03-28 14:00 | 2022-03-28 17:00 | 2022-03-28 15:00 |  |  | works completed - repaired breaker
MSA-DFES | WA5291095 | 0 | Critical Fire Protection & Training | Fire panel is in alarm - showing smoke in plant room | Fire Protection Services | Fire Protection - Monitor System | 410.58 | Pass | Pass | 0 | 0 | 1 | 2022-03-25 15:01 | 2022-03-25 17:01 | 2022-03-25 15:45 | 2022-03-25 19:01 | 2022-03-25 16:45 |  |  | Found detector loop 3 device 99 in fault. Replaced detector and base (addressable notifier). System normal on departure.
MSA-DTAG | WA5294256 | 3 | Midolo Building Services | Level 3 - Courtroom 32 - Screw has come out of the TV wall mount in court 32 | Building | Materials | 115 | Pass | Pass | 0 | 0 | 1 | 2022-03-28 15:04 | 2022-04-04 17:00 | 2022-04-01 13:30 | 2022-04-04 17:00 | 2022-04-01 14:30 |  |  | inspected tv mount, all secure
MSA-DTWD | WA5294694 | 1 | OTIS ELEVATOR COMPANY PTY LTD | B Block - Level 1 - 4 - B Block Lift - Lift doors opening and lift car bumping up and down | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-03-29 08:37 | 2022-03-30 17:00 | 2022-03-29 12:30 | 2022-03-30 17:00 | 2022-03-29 13:30 |  |  | Repaired under warranty - No charge
MSA-DCA | WA5295140 | 1 | Techworks Electrical | Ground - Main Gallery - Lights continually blowing on gallery lighting tracks | Electrical | General Electrical | 125.59 | Pass | Pass | 0 | 0 | 1 | 2022-03-29 11:22 | 2022-03-30 17:00 | 2022-03-30 09:00 | 2022-03-30 17:00 | 2022-03-30 10:00 |  |  | Began investigation by going to supply, tested the supply for the dynalite boxes and tested each channel within the dynalite system, voltages are all good, surgery protectors are in place on each phase and are good. Voltage at the track itself is 233v which is good. One of the capacitors within the circuit board of the light fitting has blown, causing the fitting to fail. I spoke to Bryce who informed me there’s been about 6/7 or so blow in the last couple months, I asked to see these as well but they have already been sent to Germany for warranty. They appear to have got a bad batch of fittings and this will be a warranty job to rectify or replace each fitting. The supply for the track lightings is fine and working as it should.
MSA-DTWD | WA5295993 | 2 | BAKE-QUIP PTY LTD | E-Block - Restaurant Kitchen - Combi oven door handle loose and unstable needs re fixing | Equipment | Catering Equipment | 230 | Pass | Pass | -1 | -1 | 1 | 2022-03-30 08:25 | 2022-04-04 17:00 | 2022-03-30 08:45 | 2022-04-04 17:00 | 2022-03-30 09:45 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA5296086 | 1 | Precise Air Group | G113 - AC not working | Air Conditioning | Room Air Conditioners | 329.67 | Fail | Fail | 0 | 0 | 1 | 2022-03-30 09:02 | 2022-03-31 17:00 | 2022-04-01 12:00 | 2022-03-31 17:00 | 2022-04-01 13:00 |  |  | Attended site signed in and gained access to reported areas. Found someone had made incorrect adjustments to control. Re adjusted and carried out functional and safety checks on the unit. Unit left operational and in working order
MSA-DTWD | WA5296138 | 2 | Falcetta Plumbing and Gas | G Block - Ground - Night Dog Kennels - Drains keep blocking up | Plumbing & Drainage | Drainage | 515.12 | Pass | Pass | -1 | -1 | 1 | 2022-03-30 09:34 | 2022-04-04 17:00 | 2022-03-31 09:00 | 2022-04-04 17:00 | 2022-03-31 10:00 |  |  | unblocked external drains
MSA-DTWD | WA5296461 | 3 | Schindler Lifts Australia | Level 2 - Lift 3 - moves to each floor but doors do not open | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-03-30 12:29 | 2022-04-06 17:00 | 2022-03-30 12:45 | 2022-04-06 17:00 | 2022-03-30 13:45 |  |  | to be closed out at $0 cost
MSA-DTAG | WA5296635 | 1 | OCS SERVICES PTY LTD | Level 3 - Court 38 - see details below | Cleaning | Hazardous Materials |  | Pass | Fail | 0 | 0 | 1 | 2022-03-30 13:50 | 2022-03-31 17:00 | 2022-03-31 17:00 | 2022-03-31 17:00 | 2022-03-31 18:00 |  |  | Covid clean
MSA-DTAG | WA5297470 | 1 | Sapio Pty Ltd | LEVEL 3 - building managers Security computer - not connecting to server & unable to view cameras | Security | Security Management System | 130 | Pass | Pass | 0 | 0 | 1 | 2022-03-31 10:16 | 2022-04-01 17:00 | 2022-03-31 12:00 | 2022-04-01 17:00 | 2022-03-31 13:00 |  |  | Reconfigured workstation network setting. Workstation regained connection to Milestone ManagementServer. Level 3 Building Manager Security workstation now able to view all cameras.
MSA-DFES | WA5297789 | 2 | SONTEC WA PTY LTD | Communications Centre - Level 1 - Training room - The Automatic door faulty - see notes | Building | Automatic Doors | 310 | Pass | Pass | -1 | -1 | 1 | 2022-03-31 13:00 | 2022-04-05 17:00 | 2022-04-01 14:45 | 2022-04-05 17:00 | 2022-04-01 15:45 |  |  | 1/4/22 - Dylan ParslowAdjusted lock mechanism and tested.All working ok.
MSA-DTWD | WA5297908 | 1 | SCAVENGER SUPPLIES PTY LTD | Fault light on fire panel room B8 | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-03-31 13:57 | 2022-04-01 17:00 | 2022-03-31 15:00 | 2022-04-01 17:00 | 2022-03-31 16:00 |  |  | completed 31/3/21
MSA-DCA | WA5298192 | 2 | Protek 24/7 Building & Maintenance | Ground Level - UAT Toilet - Broken door latch to UAT behind main reception. | Building | Doors | 196 | Pass | Pass | 0 | 0 | 1 | 2022-03-31 16:00 | 2022-04-05 17:00 | 2022-04-05 09:00 | 2022-04-05 17:00 | 2022-04-05 10:00 |  |  | Broken Latch - Unable to Locate Reese Withey instructed to close the WO.
MSA-DFES | WA5298217 | 1 | SONTEC WA PTY LTD | MOC - faulty door | Building | Doors | 310 | Pass | Pass | 0 | 0 | 1 | 2022-03-31 16:35 | 2022-04-01 17:00 | 2022-04-01 14:45 | 2022-04-01 17:00 | 2022-04-01 15:45 |  |  | 1/4/22 - Dylan ParslowAdjusted lock mechanism and lubricated for MOC mortice door.
MSA-DTAG | WA5301513 | 2 | FSA (WA) Pty Ltd | Basement - fire panel room - Fault activated on Fire Alarm panel – Sensor Fault | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 1 | 2022-04-01 09:46 | 2022-04-06 17:00 | 2022-04-05 06:00 | 2022-04-06 17:00 | 2022-04-05 07:00 |  |  | Attended site to investigate fault on FIP. 2 x vesdas need to be replaced in Lvl 4 defendants. Technician to return.Arrived to check and fix vesda faults. Both vesdas on level 4 have had filters changed yesterday by someone else. I was able to plug into vesdas and see that it was fixed at about 10am. All clear on fire panel and ok.
MSA-DTWD | WA5303983 | 1 | PEEL LOCK SERVICES PTY LTD | J block - ground - Room J11 - both door handles missing/stolen | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1 | 2022-04-04 13:37 | 2022-04-05 17:00 | 2022-04-04 14:35 | 2022-04-05 17:00 | 2022-04-04 15:35 |  |  | job completed - replace handle
MSA-DFES | WA5304910 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Males changeroom/ Toilets - Level 2 - Workshop - One of the toilet seats in male toilet is broken | Plumbing & Drainage | Toilets/Cisterns | 191.01 | Fail | Fail | 0 | 0 | 1 | 2022-04-05 10:43 | 2022-04-08 17:00 | 2022-04-11 09:00 | 2022-04-08 17:00 | 2022-04-11 10:00 |  |  | Replaced toilet seat
MSA-DTWD | WA5306188 | 2 | AHS Services WA Pty Ltd (Anchor) | S Block - S102 - Repair toilet female cubicle | Plumbing & Drainage | Drainage | 156.32 | Pass | Pass | 0 | 0 | 1 | 2022-04-06 10:46 | 2022-04-11 17:00 | 2022-04-11 09:30 | 2022-04-11 17:00 | 2022-04-11 10:30 |  |  | Replaced faulty inlet valve to female cubicle one -a block -s102
MSA-DTWD | WA5306255 | 2 | AHS Services WA Pty Ltd (Anchor) | East Block - Exterior - Tap in front of East Block exterior | Plumbing & Drainage | Drainage | 111.69 | Pass | Pass | 0 | 0 | 1 | 2022-04-06 11:36 | 2022-04-11 17:00 | 2022-04-11 10:30 | 2022-04-11 17:00 | 2022-04-11 11:30 |  |  | Picked up and replaced handle and washer to outside tap by main entrance
MSA-DCA | WA5306604 | 2 | GPS Plumbing & Gas Services PtyLtd | Administration Building - Director’s toilet near kitchenette - see details below | Plumbing & Drainage | Toilets/Cisterns | 233.78 | Pass | Pass | 0 | 0 | 1 | 2022-04-06 15:20 | 2022-04-11 17:00 | 2022-04-08 15:00 | 2022-04-11 17:00 | 2022-04-08 16:00 |  |  | Reply faulty inlet valve, flexi and washers. Bathroon floor already wet on ny arrival due to leaking cistern
MSA-DFES | WA5307146 | 3 | Protek 24/7 Building & Maintenance | External Academy Area - Ground - Various - see details below | Building | General Building | 1714.5 | Pass | Pass | 0 | 0 | 1 | 2022-04-07 10:29 | 2022-04-14 17:00 | 2022-04-12 08:00 | 2022-04-14 17:00 | 2022-04-12 09:00 |  |  | Repair Lifting Pavers
MSA-DTWD | WA5307199 | 2 | AWB Co. | F16 Light Store - Faulty Light Switch - Very hard to switch on/off. Probably needs to be replaced | Electrical | General Electrical | 235.64 | Pass | Pass | -1 | -1 | 1 | 2022-04-07 11:09 | 2022-04-12 17:00 | 2022-04-08 07:15 | 2022-04-12 17:00 | 2022-04-08 08:15 |  |  | Attended site signed in completed jsa. Spoke with glen about job. Found faulty switch and replaced with new 20a switch. lights working now.*** job completed ***
MSA-DTWD | WA5307400 | 2 | AWB Co. | EG24 - LED light in disabled toilet not working | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-04-07 13:24 | 2022-04-12 17:00 | 2022-04-11 13:15 | 2022-04-12 17:00 | 2022-04-11 14:15 |  |  | Attended site signed in completed jsa. Spoke with frank site fm and showed me the job. No lights or power in toilet. Found switchboard adjacent to room. Found rcd in the off position. Turned on and now lights and power working in the room. *** job completed ***
MSA-DFES | WA5307776 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Professional Standards Office - Sound on and off in the ceiling like a toilet cistern refilling | Plumbing & Drainage | Toilets/Cisterns | 166.76 | Pass | Pass | 0 | 0 | 1 | 2022-04-07 16:52 | 2022-04-12 17:00 | 2022-04-11 13:30 | 2022-04-12 17:00 | 2022-04-11 14:30 |  |  | Arrived to floor 2 for a pound noise that sounds like water went around the hole of floor 2 and couldn’t hear anything.
MSA-DTWD | WA5308151 | 2 | Falcetta Plumbing and Gas | Female Staff Toilet - Cistern is leaking | Plumbing & Drainage | Toilets/Cisterns | 496.83 | Pass | Pass | 0 | 0 | 1 | 2022-04-08 09:07 | 2022-04-13 17:00 | 2022-04-12 17:00 | 2022-04-13 17:00 | 2022-04-12 18:00 |  |  | repaired cistern replaced seat
MSA-DTWD | WA5308277 | 2 | Protek 24/7 Building & Maintenance | K01 - Carpet lifting due to edge strip coming away Nth end near vending machines | Flooring | Carpet | 724.5 | Pass | Pass | 0 | 0 | 1 | 2022-04-08 10:19 | 2022-04-13 17:00 | 2022-04-12 08:45 | 2022-04-13 17:00 | 2022-04-12 09:45 |  | WACCES | Replace carpet edge strip
MSA-DTAG | WA5308310 | 3 | Midolo Building Services | Kitchen – judicial corridor (1903 building) - Kitchen draw broken | Building | General Building | 144.92 | Pass | Pass | -1 | -1 | 1 | 2022-04-08 10:38 | 2022-04-19 17:00 | 2022-04-14 12:00 | 2022-04-19 17:00 | 2022-04-14 13:00 |  |  | drawer re secured/repaired
MSA-DFES | WA5308543 | 2 | Complete Pest Management Services | Roof Space - Entire Station - see details below | Pest Control | General Pest | 223.31 | Pass | Pass | 0 | 0 | 1 | 2022-04-08 13:10 | 2022-04-13 17:00 | 2022-04-13 08:00 | 2022-04-13 17:00 | 2022-04-13 09:00 |  |  | Inspected roof void for pest activity.Rodent droppings concentrated around 2 openings into the roof void from outside patio.Re-baited 4 existing rodent stations in the roof void.Recommend the openings be enclosed to reduce rodent ingress to roof void.
MSA-DCA | WA5311523 | 0 | Techworks Electrical | Performance Space - water leak into light fitting - please remove light fitting | Electrical | General Electrical | 173.1 | Pass | Pass | 0 | 0 | 1 | 2022-04-11 07:44 | 2022-04-11 09:44 | 2022-04-11 09:00 | 2022-04-11 11:44 | 2022-04-11 10:00 |  |  | 1. Isolated light fitting by unplugging from 413, found water in plug top and 413, was able to dry them out with some contact cleaner and get it all fired up and working well. 2. Reece came over and after he spoke with pica people they decided to leave it down for the winter while it is raining or untill roofing issue is fixed.
MSA-DFES | WA5312112 | 2 | Australian HVAC Services Pty. Ltd. | Ground Floor - Reliving SO Dorm - Air-con leaking water on flooring dorm | Air Conditioning | Room Air Conditioners | 135.05 | Pass | Pass | 0 | 0 | 1 | 2022-04-11 11:12 | 2022-04-14 17:00 | 2022-04-11 13:30 | 2022-04-14 17:00 | 2022-04-11 14:30 |  |  | Carried out unblocking of condensate drain for FCU.6
MSA-DCA | WA5312502 | 1 | Precise Air Group | Studio 3 - Evaporative unit – water is not shutting off | Air Conditioning | Room Air Conditioners | 193.62 | Pass | Pass | 0 | 0 | 1 | 2022-04-11 14:37 | 2022-04-12 17:00 | 2022-04-11 15:00 | 2022-04-12 17:00 | 2022-04-11 16:00 |  |  | Attended site and gained access to roof space. Inspected unit and found water levels too high and running into overflow pipe. Readjusted floats and re tested water levels. Unit no longer over flowing and unit operating normally
MSA-MRWA | WA5318041 | 2 | Siemens Ltd | Eastern Courtyard Mag lock not engaging correctly | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1 | 2022-04-12 07:49 | 2022-04-14 17:00 | 2022-04-13 08:00 | 2022-04-14 17:00 | 2022-04-13 09:00 |  |  | job completed - repair faulty lock
MSA-DTWD | WA5318104 | 1 | FSA (WA) Pty Ltd | Fire panel - in fault - needs reset and sensor may be faulty | Fire Protection Services | Fire Protection - Monitor System | 209.64 | Pass | Pass | 0 | 0 | 1 | 2022-04-12 08:23 | 2022-04-13 17:00 | 2022-04-13 07:30 | 2022-04-13 17:00 | 2022-04-13 08:30 |  |  | Investigated false alarm and changed out faulty smoke detector and base. Tested and all ok. Reset fire panel and de isolated zone 2. Panel is all clear and normal.
MSA-DCA | WA5318300 | 1 | Protek 24/7 Building & Maintenance | Main Building - Floor - Entry paving - pavers are sunken | Paving & Roadworks | Paving | 119.5 | Pass | Pass | 0 | 0 | 1 | 2022-04-12 10:11 | 2022-04-13 17:00 | 2022-04-12 12:30 | 2022-04-13 17:00 | 2022-04-12 13:30 |  |  | Entry paving - pavers are sunkenTask canceled at Reese Withey's request via phone call, due to not being a proper breakdown task
MSA-DTAG | WA5323753 | 3 | Dom's Total Grounds Maintenance | Rear Of Court Secure Parking Area- Pine Tree Creating potential fire hazard - See notes | Landscaping & Gardening | General Tree Works | 80 | Fail | Fail | 1 | 1 | 1 | 2022-04-13 10:38 | 2022-04-22 17:00 | 2022-04-29 08:00 | 2022-04-22 17:00 | 2022-04-29 09:00 |  |  | Call Out to Inspect Pine TreeSubmitted BRAF to do works but BRAF was rejected.
MSA-DTWD | WA5324406 | 1 | OTIS ELEVATOR COMPANY PTY LTD | B Block - Ground - Passenger Lift - Lift door keeps on opening when it should be closing | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-04-13 14:48 | 2022-04-14 17:00 | 2022-04-13 15:30 | 2022-04-14 17:00 | 2022-04-13 16:30 |  |  | Repaired under warranty - No charge
MSA-MRWA | WA5324458 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | The ports to be tested 330 and 325 | Electrical | General Electrical | 196.42 | Pass | Pass | 0 | 0 | 1 | 2022-04-13 15:40 | 2022-04-14 17:00 | 2022-04-14 06:00 | 2022-04-14 17:00 | 2022-04-14 07:00 |  |  | Completed
MSA-DTWD | WA5324462 | 2 | Falcetta Plumbing and Gas | Boiler Room - water leaking from open pipework | Plumbing & Drainage | Water | 175.12 | Pass | Pass | -1 | -1 | 1 | 2022-04-13 15:45 | 2022-04-20 17:00 | 2022-04-14 15:30 | 2022-04-20 17:00 | 2022-04-14 16:30 |  |  | sealed pipe ends
MSA-DCA | WA5325392 | 2 | Techworks Electrical | Level 1-Hackett Hall-Hackett Bridge-Loose cable at LED strip lighting recess-Skirting level | Electrical | General Electrical | 133.09 | Pass | Pass | 0 | 0 | 1 | 2022-04-14 09:01 | 2022-04-21 17:00 | 2022-04-20 06:30 | 2022-04-21 17:00 | 2022-04-20 07:30 |  |  | Found cable to be loose from its fixings, reinstalled cable into fixings and provided some extra support by tucking the excess slack of the cable behind the escutcheon of the kickboard.
MSA-DTAG | WA5325421 | 1 | OCS SERVICES PTY LTD | Ground Floor - COVID Clean - Please see list below | Cleaning | Emergency Cleans |  | Pass | Fail | 0 | 0 | 1 | 2022-04-14 09:11 | 2022-04-19 17:00 | 2022-04-19 17:00 | 2022-04-19 17:00 | 2022-04-19 18:00 |  |  | Covid clean
MSA-DTAG | WA5325473 | 3 | OCS SERVICES PTY LTD | Level 3 - Judicial Support Office - Black mould on the ceiling in the female toilet | Cleaning | Cleaning |  | Pass | Fail | 0 | 0 | 1 | 2022-04-14 09:27 | 2022-04-26 17:00 | 2022-04-26 17:00 | 2022-04-26 17:00 | 2022-04-26 18:00 |  |  | Completed
MSA-DTAG | WA5325492 | 1 | Schindler Lifts Australia | 1987 - Level 2 - lift out of service - lift 1 not working | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-04-14 09:37 | 2022-04-19 17:00 | 2022-04-14 11:00 | 2022-04-19 17:00 | 2022-04-14 12:00 |  |  | Roa lift running no faults Tested all floors
MSA-DTWD | WA5325946 | 3 | Protek 24/7 Building & Maintenance | Room A51 - Worn carpet under desk chair - may need to be patched | Flooring | Carpet | 157.75 | Pass | Pass | -1 | -1 | 1 | 2022-04-14 14:21 | 2022-04-26 17:00 | 2022-04-21 07:30 | 2022-04-26 17:00 | 2022-04-21 08:30 |  |  | worn Carpet - Braf Declined
MSA-DCA | WA5335937 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Public Lift out of order - doors not opening | Lifts | Lifts |  | Fail | Pass | 0 | 0 | 1 | 2022-04-16 10:23 | 2022-04-16 12:23 | 2022-04-16 12:47 | 2022-04-16 14:23 | 2022-04-16 13:47 |  |  | Repaired under warranty - No charge for attendance
MSA-DFES | WA5368138 | 3 | Go Doors | Unit 1 - Ground - Outside carpark gate - Westside - see details below | Building | Steel Fencing & Gates | 402 | Pass | Pass | -1 | -1 | 1 | 2022-04-19 10:54 | 2022-04-27 17:00 | 2022-04-20 10:15 | 2022-04-27 17:00 | 2022-04-20 11:15 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5368963 | 2 | ACTION GLASS & ALUMINIUM | Broken window glass | Glazing | Window Glass | 392.2 | Pass | Pass | 0 | 0 | 1 | 2022-04-19 14:38 | 2022-04-22 17:00 | 2022-04-20 12:50 | 2022-04-22 17:00 | 2022-04-20 13:50 |  |  | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-1325 X 825PLUS 2 RIVETS
MSA-DTWD | WA5369072 | 2 | Equans Mechanical Services Australia | G09 - Compressor Room - air compressor solenoid has stuck and manual shit off valve is broken | Equipment | Compressors, Generators | 120.35 | Pass | Pass | 0 | 0 | 1 | 2022-04-19 15:48 | 2022-04-22 17:00 | 2022-04-21 09:30 | 2022-04-22 17:00 | 2022-04-21 10:30 |  |  | Checked the air compressor over , found the relief valve sticking open sometimes, due for service .Will send through quote to repair.
MSA-MRWA | WA5377543 | 2 | AWB Co. | LED downlight not working - see notes below | Electrical | Lighting, Internal | 194.26 | Pass | Pass | 0 | 0 | 1 | 2022-04-20 07:14 | 2022-04-22 17:00 | 2022-04-22 06:00 | 2022-04-22 17:00 | 2022-04-22 07:00 |  |  | Attended site and signed in. Completed JSA. Located faulty light fitting in level 4 male toilet. Grabbed 4ft ladder and pulled downlight out. Found it was not connected to anything. Located plug base in roofspace. Connected. Put light fitting back in position. Tested. Everything working as intended now. Took picture. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5378490 | 3 | AWB Co. | D204 Storeroom - Faulty light fitting | Electrical | General Electrical | 341.32 | Pass | Pass | 0 | 0 | 1 | 2022-04-20 14:43 | 2022-04-28 17:00 | 2022-04-26 15:00 | 2022-04-28 17:00 | 2022-04-26 16:00 |  |  | Attended site and signed in. Completed JSA. Located area for works, found old light fitting. Supply and replace with new led fitting above the printer. Supply and replace new light with led in hallway. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5378561 | 2 | Water2water Pty Ltd | B block - Second Level - Room B2220 - Faulty BWU in Staff Kitchen | Plumbing & Drainage | HWS/Units Electric & Gas | 1976.165 | Pass | Pass | 0 | 0 | 1 | 2022-04-20 15:52 | 2022-04-26 17:00 | 2022-04-26 12:30 | 2022-04-26 17:00 | 2022-04-26 13:30 |  |  | Button leaking, level sensor failing, tap leaking. Site requested replacement unit.
MSA-DCA | WA5379140 | 0 | Critical Fire Protection & Training | Stairwell 2 - Sprinkler pipe leaking - basement - please investigate | Fire Protection Services | Sprinkler Systems | 217.3 | Fail | Pass | 0 | 0 | 1 | 2022-04-21 08:45 | 2022-04-21 10:45 | 2022-04-21 11:00 | 2022-04-21 12:45 | 2022-04-21 12:00 |  |  | No leak present on arrival time spent investigating. Leak seemed to be coming fromhydrant head in basement L2. Hydrant head loose and I tightened up the spindle andwas all okay on departure.
MSA-DTWD | WA5381752 | 2 | Water2water Pty Ltd | Ground Level - T Block - Entrance - water fountain at entrance has a broken tap | Plumbing & Drainage | HWS/Units Electric & Gas | 2139.14 | Pass | Pass | 0 | 0 | 1 | 2022-04-26 11:19 | 2022-04-29 17:00 | 2022-04-28 08:45 | 2022-04-29 17:00 | 2022-04-28 09:45 |  |  | Fountain has been vandalised beyond repair, new fountain replacement required. Written report and admin will quote for replacement
MSA-DFES | WA5381930 | 2 | Critical Fire Protection & Training | Ground - Rear Yard - Fire hose is leaking - see notes below | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 269.5 | Pass | Pass | 0 | 0 | 1 | 2022-04-26 12:29 | 2022-04-29 17:00 | 2022-04-27 12:00 | 2022-04-29 17:00 | 2022-04-27 13:00 |  |  | After investigation we determined the leak to be coming from a flaredunion under the isolation valve.Shut off the water supply and re-flared the copper pipe.Turned back on the water supply and tested the fitting all okay ondeparture.
MSA-DTWD | WA5382918 | 1 | BAKE-QUIP PTY LTD | E75 Asian Kitchen - Faulty Fagor gas cooktop - Issues lighting cooktop and issues with pilot light | Equipment | Cleaning Equipment | 337.8 | Pass | Pass | 0 | 0 | 1 | 2022-04-27 10:07 | 2022-04-28 17:00 | 2022-04-27 15:00 | 2022-04-28 17:00 | 2022-04-27 16:00 |  |  | REFER TO SERVICE REPORT.
MSA-DTAG | WA5383377 | 1 | Schindler Lifts Australia | 1987 - Level 2 - Lift 1 - lift not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-04-27 14:55 | 2022-04-28 17:00 | 2022-04-27 15:30 | 2022-04-28 17:00 | 2022-04-27 16:30 |  |  | Landing lock not dropping in line level 2. Cleaned rail as dirty lock dropping in correctly. Teste no issues. Left in service.
MSA-DTWD | WA5383850 | 3 | Critical Fire Protection & Training | Level 2 - Entry Foyer - Continued intermittent faults on Fire Panel | Fire Protection Services | Fire Protection - Monitor System | 114.14 | Pass | Pass | -1 | -1 | 1 | 2022-04-28 07:55 | 2022-05-04 17:00 | 2022-04-28 12:30 | 2022-05-04 17:00 | 2022-04-28 13:30 |  |  | Attended site to investigate intermittent fault on fire panel. On arrival panel operating with all systems normal, used history log to identify cause of intermittent fault. Found detector L4,D79 had been intermittently in and out of battery low and device missing fault. Replaced 6xAA batteries in device an confirmed system still operating as normal on departure.
MSA-DTAG | WA5384009 | 0 | Sapio Pty Ltd | Judges Carpark - Basement 2 - keypad is not working | Security | Access Control | 130 | Pass | Pass | 0 | 0 | 1 | 2022-04-28 09:10 | 2022-04-28 11:10 | 2022-04-28 10:30 | 2022-04-28 13:10 | 2022-04-28 11:30 |  |  | Created report of Basement 2 Gallagher keypad / card reader PIN issues and emailed report to Kelly.
MSA-DTWD | WA5384291 | 3 | AWB Co. | F Block - Ground Level - Large LED Overhead light not working - Above Bay 36 | Electrical | Lighting, External | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-04-28 11:35 | 2022-05-05 17:00 | 2022-05-03 15:30 | 2022-05-05 17:00 | 2022-05-03 16:30 |  |  | Attended site , signed in , completed jsa , spoke to fm about job , located light that wasn’t working, fm said he would check if it was still under warranty, completed paperwork, fm confirmed it was under warranty and the previous contractor who installed the lights would come to replace , asked to close job off, signed out Job complete
MSA-DTWD | WA5384342 | 2 | Protek 24/7 Building & Maintenance | Roof Leak - See notes | Roofing | Concrete Roof Construction | 211.4 | Pass | Pass | -1 | -1 | 1 | 2022-04-28 12:03 | 2022-05-03 17:00 | 2022-04-28 14:00 | 2022-05-03 17:00 | 2022-04-28 15:00 |  |  | Repair Roof leaks
MSA-DTAG | WA5384645 | 2 | Midolo Building Services | Level 9 - Court 92 - Issues with Door - See notes | Building | Automatic Doors | 144.92 | Pass | Pass | -1 | -1 | 1 | 2022-04-28 14:22 | 2022-05-03 17:00 | 2022-04-29 11:15 | 2022-05-03 17:00 | 2022-04-29 12:15 |  |  | ADJUSTMENTS & REPAIRS MADE TO DOOR CLOSER
MSA-DTWD | WA5390271 | 2 | Protek 24/7 Building & Maintenance | EG19 Staff Toilet - Ground - Door closer isn’t working properly | Building | General Building | 119.5 | Pass | Pass | 0 | 0 | 1 | 2022-05-02 11:31 | 2022-05-05 17:00 | 2022-05-02 14:00 | 2022-05-05 17:00 | 2022-05-02 15:00 |  |  | Repair Toilet door
MSA-DCA | WA5393706 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Public Lift - Stuck on level 1 with doors open | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1 | 2022-05-04 09:43 | 2022-05-04 11:43 | 2022-05-04 14:40 | 2022-05-04 13:43 | 2022-05-04 15:40 |  |  | Completed
MSA-DTWD | WA5394214 | 1 | SENTINEL LOCK SERVICE PTY LTD | Block 2 - First Aid Room - Faulty pin code lock | Security | Locksmith | 125.09 | Pass | Pass | 0 | 0 | 1 | 2022-05-04 13:54 | 2022-05-05 17:00 | 2022-05-04 14:20 | 2022-05-05 17:00 | 2022-05-04 15:20 |  |  | Block 2 - first aid room - faulty pin lock.Lock serviced.
MSA-DTWD | WA5395198 | 2 | Critical Fire Protection & Training | A Block - Foyer Entrance - A-Block EWIS Pannel has low batteries need replacing | Fire Protection Services | Fire Protection - Monitor System | 783 | Pass | Pass | -1 | -1 | 1 | 2022-05-05 11:26 | 2022-05-10 17:00 | 2022-05-05 12:00 | 2022-05-10 17:00 | 2022-05-05 13:00 |  |  | Batteries require replacement.
MSA-DTWD | WA5396543 | 3 | AWB Co. | Room A16 - One of the fluorescent lights is out | Electrical | Lighting, Internal | 194.26 | Pass | Pass | 0 | 0 | 1 | 2022-05-06 09:52 | 2022-05-13 17:00 | 2022-05-11 10:15 | 2022-05-13 17:00 | 2022-05-11 11:15 |  |  | Attended site and signed in, located A16. Found faulty light fitting. Replaced fluros and starters. All now working. Cleaned out area. Informed Fm of job completion.Job completed.
MSA-DTWD | WA5396857 | 3 | Protek 24/7 Building & Maintenance | L Block - Fault description Doors not closing properly, hinges need to be adjusted - See notes below | Building | Doors | 132.7 | Pass | Pass | 0 | 0 | 1 | 2022-05-06 11:48 | 2022-05-13 17:00 | 2022-05-10 11:00 | 2022-05-13 17:00 | 2022-05-10 12:00 |  |  | Adjust door hinges
MSA-DFES | WA5397407 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | BA Cleaning Room & Storeroom - power points in both rooms are tripping out appliances are plugged | Electrical | General Electrical | 124.95 | Pass | Pass | 0 | 0 | 1 | 2022-05-06 16:24 | 2022-05-13 17:00 | 2022-05-13 14:15 | 2022-05-13 17:00 | 2022-05-13 15:15 |  |  | Arrived on site at 1415 to investigate power fault at vols station. When arrived on site power had already been reenergised. Was informed by officer that after plugging in battery charger circuit rcd had tripped but was reenergised from staff several days later without issue. Investigated relative socket outlets on circuit and discovered a wproof gpo outside unsealed. Sealed outlet up and conducted voltage, fault loop & rcd trip time tests. Found nothing of concern. Plugged battery charger in same socket outlet throughout visit and did not trip rcd. Left site at 1515.
MSA-DTWD | WA5398624 | 3 | Falcetta Plumbing and Gas | East Block - External to Fire Escape - Outdoor tap vandalized - pipework fractured | Plumbing & Drainage | Water | 402.06 | Pass | Pass | 0 | 0 | 1 | 2022-05-09 11:35 | 2022-05-16 17:00 | 2022-05-16 15:00 | 2022-05-16 17:00 | 2022-05-16 16:00 |  |  | repaired tap and refixed
MSA-DTWD | WA5399164 | 2 | Techworks Electrical | ground stores area has has a broken light switch cover | Electrical | Lighting, Internal | 222.95 | Pass | Pass | 0 | 0 | 1 | 2022-05-09 16:14 | 2022-05-12 17:00 | 2022-05-11 08:00 | 2022-05-12 17:00 | 2022-05-11 09:00 |  |  | Replaced faulty light switch
MSA-DCA | WA5399196 | 2 | FCT SURFACE CLEANING | Main Carpark - Right external management sign requires graffiti removal | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1 | 2022-05-09 17:29 | 2022-05-12 17:00 | 2022-05-11 11:00 | 2022-05-12 17:00 | 2022-05-11 12:00 |  |  | Removal of graffiti
MSA-DTAG | WA5399223 | 3 | AHS Services WA Pty Ltd (Anchor) | L5 Toilet seat needs replacing | Plumbing & Drainage | Toilets/Cisterns | 94.19 | Pass | Pass | -1 | -1 | 1 | 2022-05-09 19:13 | 2022-05-16 17:00 | 2022-05-11 08:45 | 2022-05-16 17:00 | 2022-05-11 09:45 |  |  | Adjusted toilet seats
MSA-DTAG | WA5413448 | 0 | AFD Contracting | Sally Port - its jammed and electronics are working but manually able to open | Building | Security Doors | 580 | Pass | Pass | 0 | 0 | 1 | 2022-05-12 11:05 | 2022-05-12 13:05 | 2022-05-12 12:30 | 2022-05-12 15:05 | 2022-05-12 13:30 |  |  | 12/05/22Attended site.Found roller door working.Problem is from control room access.Contractor to be called by client.
MSA-DTWD | WA5413511 | 3 | AWB Co. | Between C32 and C21 - Lights in covered walkway between hairdressing and C21 not working | Electrical | Lighting, Internal | 194.26 | Pass | Pass | 0 | 0 | 1 | 2022-05-12 11:40 | 2022-05-19 17:00 | 2022-05-17 06:30 | 2022-05-19 17:00 | 2022-05-17 07:30 |  |  | Attended site signed in completed jsa. Located faulty lighting. Found 8x globes and starters were I need of replacement. Replaced. Took picture. All working as intended. Job complete
MSA-DTWD | WA5413526 | 3 | SENTINEL LOCK SERVICE PTY LTD | Ground Level - Room 3 - Faulty Door Lock | Security | Locksmith | 175.59 | Pass | Pass | 0 | 0 | 1 | 2022-05-12 11:47 | 2022-05-19 17:00 | 2022-05-18 12:55 | 2022-05-19 17:00 | 2022-05-18 13:55 |  |  | ROOM 3 - FAULTY DOOR LOCK.Lock repaired - damaged keys replaced.
MSA-DTWD | WA5413531 | 2 | Protek 24/7 Building & Maintenance | BG08 - Please see details below | Building | General Building | 223.5 | Fail | Fail | 0 | 0 | 1 | 2022-05-12 11:47 | 2022-05-17 17:00 | 2022-05-18 12:30 | 2022-05-17 17:00 | 2022-05-18 13:30 |  |  | Repaired hinge on double door and draught excluder
MSA-DTWD | WA5413902 | 3 | AWB Co. | Room D04 - Light out (Tombstone Req.) | Electrical | Lighting, Internal | 194.26 | Pass | Pass | 0 | 0 | 1 | 2022-05-12 14:58 | 2022-05-19 17:00 | 2022-05-17 08:15 | 2022-05-19 17:00 | 2022-05-17 09:15 |  |  | Attended site signed in completed jsa. Located light fittings with faulty tombstones. Went to store room and collected all parts required for job. Replaced faulty to,bayonets starters and tubes. Tested lighting. Working as intended. Took picture. Job complete
MSA-DFES | WA5414113 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Light fluro tubes in locker room require replacing x 3 | Electrical | General Electrical | 201.87 | Pass | Pass | 0 | 0 | 1 | 2022-05-12 16:50 | 2022-05-19 17:00 | 2022-05-19 13:15 | 2022-05-19 17:00 | 2022-05-19 14:15 |  |  | Arrived on site at 13:15.went to locker room and located 2 x lights with flickering tubes, replaced both tubes and starters all okay. Found 1 x external light hanging from ceiling, resecured light and changed both tube and starter. Left site at 14:15Parts : 4 x 36w t8 840 tubes, 1 x 18w t8 865 tube, 4 x s10 starters, 1 x s2 starter, 1 x fixings
MSA-DFES | WA5416727 | 1 | Go Doors | Ground Floor - Entry - Exit Boom Gate damaged - not closing - doesnt scan | Security | Access Control | 473.2 | Pass | Pass | 0 | 0 | 1 | 2022-05-13 08:01 | 2022-05-16 17:00 | 2022-05-13 12:30 | 2022-05-16 17:00 | 2022-05-13 13:30 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5417247 | 0 | Techworks Plumbing | Whole Building - All Toilets - all toilets are blocked | Plumbing & Drainage | Toilets/Cisterns | 333.75 | Pass | Pass | 0 | 0 | 1 | 2022-05-13 11:28 | 2022-05-13 13:28 | 2022-05-13 12:30 | 2022-05-13 15:27 | 2022-05-13 13:30 |  |  | Plunge drains to clear blockage
MSA-DTAG | WA5417249 | 2 | Midolo Building Services | Ground Floor - Public Male Toilets - Soap dispenser is faulty | Equipment | Cleaning Equipment | 144.92 | Pass | Pass | 0 | 0 | 1 | 2022-05-13 11:29 | 2022-05-18 17:00 | 2022-05-16 09:30 | 2022-05-18 17:00 | 2022-05-16 10:30 |  | WACCES | DISPENSER REPAIRED
MSA-DTAG | WA5417284 | 3 | PPM Project Painting & Maintenance | Emergency Magistrate Exit - Graffiti on wall | Cleaning | Graffiti |  | Pass | Pass | -1 | -1 | 1 | 2022-05-13 11:32 | 2022-05-20 17:00 | 2022-05-14 12:00 | 2022-05-20 17:00 | 2022-05-14 13:00 |  |  | job completed - Apply stain blocker and apply two coats of Exterior low sheen to match existing
MSA-DTAG | WA5417714 | 2 | Midolo Building Services | Cleaner’s Office- 2 leaks in corners of cleaner’s office/storage room | Roofing | Tiled Roofing | 197.72 | Pass | Pass | 0 | 0 | 1 | 2022-05-13 15:32 | 2022-05-18 17:00 | 2022-05-17 11:45 | 2022-05-18 17:00 | 2022-05-17 12:45 |  |  | roof repaired/cleaned of potential leak spots
MSA-DTWD | WA5417738 | 2 | Lane's Plumbing | BATHROOM C - Tap are faulty ---- loose | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 1 | 2022-05-13 16:33 | 2022-05-18 17:00 | 2022-05-17 15:00 | 2022-05-18 17:00 | 2022-05-17 16:00 |  |  | Repair to loose taps
MSA-DTWD | WA5417739 | 2 | Lane's Plumbing | BATHROOM D - Tap are faulty ---- loose | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 1 | 2022-05-13 16:37 | 2022-05-18 17:00 | 2022-05-17 14:00 | 2022-05-18 17:00 | 2022-05-17 15:00 |  |  | Repaired loose tap
MSA-DTWD | WA5438155 | 3 | AWB Co. | Faulty light in the store room | Electrical | Lighting, Internal | 333.51 | Pass | Pass | -1 | -1 | 1 | 2022-05-16 12:47 | 2022-05-23 17:00 | 2022-05-19 14:00 | 2022-05-23 17:00 | 2022-05-19 15:00 |  |  | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Located L block storeroom and found 1x Light not working. Left site to get parts and returned. Supplied and replaced with new LED batten. Testing if it’s all working correctly. Notified of works completed. **job complete**
MSA-DTWD | WA5438204 | 2 | Securex Security Systems & Services | Ladies Toilet G152 - No alarm detected after door was forced - See notes below | Security | Monitoring | 368.25 | Pass | Pass | 0 | 0 | 1 | 2022-05-16 13:07 | 2022-05-19 17:00 | 2022-05-16 14:00 | 2022-05-19 17:00 | 2022-05-16 15:00 |  |  | 16/05/2022, 1400-1500No zone on toilets so added zone 41 G152 door.Also replaced battery in zone 31, had to relearn device into panel for fault to clear.
MSA-DCA | WA5451033 | 2 | Protek 24/7 Building & Maintenance | Jubilee - Level 1 - Reflections Gallery, Eastern Entry - Refit magnetic door catch box - see below | Building | General Building | 136.87 | Pass | Pass | 0 | 0 | 1 | 2022-05-17 07:30 | 2022-05-19 17:00 | 2022-05-19 12:00 | 2022-05-19 17:00 | 2022-05-19 13:00 |  |  | Refit magnetic door catch box to wall
MSA-DTWD | WA5454205 | 2 | AWB Co. | B16 staff room - Light switch pushed in / middle switch of three | Electrical | General Electrical | 203.06 | Pass | Pass | 0 | 0 | 1 | 2022-05-17 10:26 | 2022-05-20 17:00 | 2022-05-19 07:15 | 2022-05-20 17:00 | 2022-05-19 08:15 |  |  | Attended site signed in jsa completed. Spoke with pete about jobs with switches that need replacing. Found two mechs in two rooms which are intermediate switches. Sourced from wholesaler and replaced with new. Works fine now. *** job completed ***
MSA-DTWD | WA5454646 | 3 | AWB Co. | Room K01 - Pendant lights out x3 | Electrical | Lighting, Internal | 233.68 | Pass | Pass | -1 | -1 | 1 | 2022-05-17 13:07 | 2022-05-24 17:00 | 2022-05-19 15:00 | 2022-05-24 17:00 | 2022-05-19 16:00 |  |  | Attended site and signed in. Completed JSA. Liaised with FM about works going ahead. Located multiple lamp failures in canteen. Supplied and replaced 3x old faulty globes with 3x new led. Notified of works completed **job complete**
MSA-DFES | WA5454864 | 3 | AWB Co. | Gym - Gym Rubber dado lining glued to wall coming away - requires re adhesion | Building | Internal Walls | 127.5 | Pass | Pass | -1 | -1 | 1 | 2022-05-17 15:29 | 2022-05-24 17:00 | 2022-05-18 13:15 | 2022-05-24 17:00 | 2022-05-18 14:15 |  |  | Reglue dado rail back to wall
MSA-DCA | WA5459717 | 0 | Techworks Electrical | Admin Building - Level 1 - Section of building has no power and lights | Electrical | General Electrical | 240.71 | Pass | Pass | 0 | 0 | 1 | 2022-05-18 08:24 | 2022-05-18 10:24 | 2022-05-18 09:00 | 2022-05-18 12:24 | 2022-05-18 10:00 |  |  | Tested and reset RCBOs as testing came back clean. No surge diverters present in DB, suspected surge tripped breakers after power outage from last night
MSA-DTWD | WA5459836 | 0 | FSA (WA) Pty Ltd | Block S - Main Building - fire panel needs to be reset due to incident this morning | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-05-18 09:12 | 2022-05-18 11:12 | 2022-05-18 09:30 | 2022-05-18 13:12 | 2022-05-18 10:30 |  |  | Attended site and cleared false alarm due to contractors working. Left isolated until this afternoon when Steve will de isolate
MSA-DTWD | WA5461658 | 1 | FSA (WA) Pty Ltd | B Block - Print room - Fire detector - have been isolated - no detection | Fire Protection Services | Fire Protection - Monitor System | 261.94 | Pass | Pass | 0 | 0 | 1 | 2022-05-19 07:52 | 2022-05-19 17:00 | 2022-05-19 10:30 | 2022-05-19 17:00 | 2022-05-19 11:30 |  |  | Arrived to find smoke detector above fire panel went into false alarm last night. Unsure what happened as we were told no one was on site at the time. Replaced smoke detector and reset fire system. Spoke with Kim the building manager and notified him the system was back online.
MSA-DTWD | WA5468142 | 2 | AHS Services WA Pty Ltd (Anchor) | Plumbing Duct - West end - Grouns floor - Plumbing Pipe hums loudly when water being used | Plumbing & Drainage | Water | 130.82 | Pass | Pass | 0 | 0 | 1 | 2022-05-20 07:15 | 2022-05-24 17:00 | 2022-05-23 10:30 | 2022-05-24 17:00 | 2022-05-23 11:30 |  |  | Completed
MSA-DFES | WA5470340 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Second Floor - Injury Management POD - no power | Electrical | General Electrical | 124.95 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 09:43 | 2022-05-24 17:00 | 2022-05-23 11:15 | 2022-05-24 17:00 | 2022-05-23 12:15 |  |  | Arrived onsite at 11:15 to investigate no power to injury management POD, found RCD had tripped due to unknown cause (possibly rain) reset rcd and tested. Left site at 12:15
MSA-DTAG | WA5472029 | 1 | Midolo Building Services | Water leaking through roof & ceiling in the sally port - OSH issue | Roofing | Metal Roofing | 191.45 | Fail | Fail | 1 | 1 | 1 | 2022-05-23 13:42 | 2022-05-24 17:00 | 2022-06-03 09:30 | 2022-05-24 17:00 | 2022-06-03 10:30 |  |  | re sealed roof of potential leak sites. roof repaired & cleaned
MSA-DTWD | WA5472099 | 2 | AWB Co. | Faulty Fluro Tube Lights | Electrical | Lighting, Internal | 218.66 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 14:08 | 2022-05-26 17:00 | 2022-05-25 06:00 | 2022-05-26 17:00 | 2022-05-25 07:00 |  |  | Attended site and signed in. Completed JSA. Located faulty tubes. Replaced tubes and starters in 3x fittings. Took pics. Completed paperwork. Signed out.Job complete
MSA-DFES | WA5472107 | 2 | AWB Co. | Level 1 - Store room in engine room (16) - Heavy sliding door has come of runner at top | Building | Doors | 127.5 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 14:01 | 2022-05-26 17:00 | 2022-05-24 13:30 | 2022-05-26 17:00 | 2022-05-24 14:30 |  |  | Attended site and inspected all store room sliding doors. All in working order no works requiredno works undertaken - no jsa required
MSA-DTWD | WA5472180 | 2 | Protek 24/7 Building & Maintenance | B16 - Leak from sky light - Last one on left / South west skylight | Building | General Building | 196 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 15:13 | 2022-05-26 17:00 | 2022-05-26 13:30 | 2022-05-26 17:00 | 2022-05-26 14:30 |  |  | Repair Leak from Skylight
MSA-DTWD | WA5472251 | 1 | BAKE-QUIP PTY LTD | E74 - Prover not functioning properly | Equipment | Catering Equipment | 130 | Fail | Fail | 0 | 0 | 1 | 2022-05-23 16:44 | 2022-05-24 17:00 | 2022-05-25 12:30 | 2022-05-24 17:00 | 2022-05-25 13:30 |  |  | Refer to service report
MSA-DTWD | WA5472253 | 1 | BAKE-QUIP PTY LTD | E75 - Provers not functioning properly | Equipment | Catering Equipment | 266.3 | Fail | Fail | 0 | 0 | 1 | 2022-05-23 16:47 | 2022-05-24 17:00 | 2022-05-25 12:30 | 2022-05-24 17:00 | 2022-05-25 13:30 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA5472576 | 1 | AWB Co. | Wet carpet in Library due to rain | Flooring | Carpet | 309 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 08:32 | 2022-05-25 17:00 | 2022-05-25 09:00 | 2022-05-25 17:00 | 2022-05-25 10:00 |  |  | Wet carpet in Library due to rainno-one on site to sign
MSA-DTWD | WA5472667 | 1 | AWB Co. | Room 15 - power points arent working since this morning | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 09:32 | 2022-05-25 17:00 | 2022-05-24 10:30 | 2022-05-25 17:00 | 2022-05-24 11:30 |  |  | Attended site signed in jsa completed. Located room with no power. Found emergency stop pushed in with key for gas. Unlocked with site key and all power back on and running.** job completed **
MSA-DTWD | WA5472800 | 1 | BJ SYSTEMS | T U & V Blocks - Not arming up from main panel in A Block | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 10:39 | 2022-05-25 17:00 | 2022-05-24 11:45 | 2022-05-25 17:00 | 2022-05-24 12:45 |  |  | T, U and V Block not arming/disarming from A Block RAT. Ran report, found user DMC Cleaning having trouble with keypad. Invalid user code coming up, can see setting and un-setting. Looked at keypad, can get into keypad, all buttons are working. Advised Dennis to let cleaner try again and see what happens
MSA-DTWD | WA5472864 | 2 | BAKE-QUIP PTY LTD | Restaurant Kitchen the flat top grill has a split electrical cord | Equipment | Catering Equipment | 251 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 10:48 | 2022-05-27 17:00 | 2022-05-25 11:00 | 2022-05-27 17:00 | 2022-05-25 12:00 |  |  | Refer to service report
MSA-DTWD | WA5473476 | 1 | Securex Security Systems & Services | D33 - Please check if alarm sensors are redundant, if not make redundant and remove | Security | Monitoring | 327.85 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 15:40 | 2022-05-25 17:00 | 2022-05-25 14:00 | 2022-05-25 17:00 | 2022-05-25 15:00 |  |  | 25/05/2022, 1400-1500Completed site inductionMet Mike and he showed me sensors in machine roomThese are very old sensors from an old system that were never removedRemoved from wall as requested
MSA-DTAG | WA5476106 | 1 | OCS SERVICES PTY LTD | Level 11 - Kitchen and chambers (signs in place) - COVID Clean | Cleaning | Cleaning |  | Pass | Fail | 0 | 0 | 1 | 2022-05-25 10:57 | 2022-05-26 17:00 | 2022-05-26 17:00 | 2022-05-26 17:00 | 2022-05-26 18:00 |  |  | Completed
MSA-DTWD | WA5476499 | 3 | Schindler Lifts Australia | Lift Car Number 1 - lift doors opening and closing continuously | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-05-25 11:18 | 2022-06-01 17:00 | 2022-05-25 11:45 | 2022-06-01 17:00 | 2022-05-25 12:45 |  |  | to be closed out at $0 cost
MSA-DTWD | WA5477348 | 2 | Equans Mechanical Services Australia | Plant room aircon - Ground - Please check isolated unit - faulty | Air Conditioning | Room Air Conditioners | 120.35 | Pass | Pass | 0 | 0 | 1 | 2022-05-25 12:36 | 2022-05-30 17:00 | 2022-05-27 11:00 | 2022-05-30 17:00 | 2022-05-27 12:00 |  |  | Attended site, found the unit in question parts on order , the out of service tag had fallen off , reconnected . Parts arriving in days and work will be carried out. REFER WA5378559
MSA-DFES | WA5477352 | 3 | Go Doors | Main carpark electric gate -see details below | Building | Steel Fencing & Gates | 366 | Pass | Pass | -1 | -1 | 1 | 2022-05-25 13:09 | 2022-06-01 17:00 | 2022-05-27 15:30 | 2022-06-01 17:00 | 2022-05-27 16:30 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5478033 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Stair 4 External Door - getting stuck/jammed on occasion | Building | General Building | 119.5 | Pass | Pass | -1 | -1 | 1 | 2022-05-26 08:04 | 2022-06-02 17:00 | 2022-05-27 12:30 | 2022-06-02 17:00 | 2022-05-27 13:30 |  |  | Stair 4 External Door - getting stuck/jammed on occasion
MSA-DTWD | WA5478049 | 1 | Techworks Plumbing | AT 221 - Ground - Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 133.75 | Pass | Pass | 0 | 0 | 1 | 2022-05-26 08:20 | 2022-05-27 17:00 | 2022-05-26 12:00 | 2022-05-27 17:00 | 2022-05-26 13:00 |  |  | Attended site and signed in at office Used plunger to unblock the toilet then used bundles of toilet paper to flush down the toilet to see if it would block up again or removed any debrisTested toilet then signed out Completed paperwork
MSA-DCA | WA5479439 | 3 | Techworks Electrical | Admin Building - Ground Floor - Library - 4 Fluro's lights are broken - see notes below | Electrical | Lighting, Internal | 125.59 | Pass | Pass | 0 | 0 | 1 | 2022-05-27 09:37 | 2022-06-03 17:00 | 2022-05-31 14:00 | 2022-06-03 17:00 | 2022-05-31 15:00 |  |  | Replaced 4x fittings to led
MSA-DCA | WA5479661 | 3 | Techworks Electrical | RETROSPECTIVE WORK ORDER - HBRC - Ground - Replacement Light tubes and starters | Electrical | General Electrical | 142.03 | Pass | Pass | -1 | -1 | 1 | 2022-05-13 10:44 | 2022-05-20 17:00 | 2022-05-13 11:00 | 2022-05-20 17:00 | 2022-05-13 12:00 | 1 |  | replaced 2x 36w tubes and starters in weatherproof light in freezer.
MSA-DCA | WA5479991 | 3 | Techworks Electrical | Ground Level - History Offices - Fluoro lights & LED Lights are faulty | Electrical | Lighting, Internal | 184.42 | Pass | Pass | 0 | 0 | 1 | 2022-05-27 14:08 | 2022-06-03 17:00 | 2022-05-31 15:00 | 2022-06-03 17:00 | 2022-05-31 16:00 |  |  | Replaced 1x LED panel and various 36w tubes pointed out by sue. As well as 1x double switch.
MSA-DTAG | WA5480034 | 1 | AHS Services WA Pty Ltd (Anchor) | Custody Area - Basement - Custody Female Toilets - Tap has a slow leak and can’t be turned off | Plumbing & Drainage | Water | 133.32 | Pass | Pass | 0 | 0 | 1 | 2022-05-27 14:46 | 2022-05-30 17:00 | 2022-05-27 15:30 | 2022-05-30 17:00 | 2022-05-27 16:30 |  |  | Completed
MSA-DTAG | WA5481266 | 3 | Seme Solutions Pty Ltd | Sound of intercom bell at secured door too low for staff to hear | ICT/Audiovisual | General AV works | 130 | Pass | Pass | -1 | -1 | 1 | 2022-05-30 11:52 | 2022-06-07 17:00 | 2022-06-01 11:43 | 2022-06-07 17:00 | 2022-06-01 12:43 |  |  | Inspect device for fault, found client was turning wrong slider on side of device, showed proper method of use and tested okay.
MSA-DFES | WA5481395 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Mens change rooms - Faulty shower head | Plumbing & Drainage | Water | 231.72 | Pass | Pass | 0 | 0 | 1 | 2022-05-30 12:48 | 2022-06-02 17:00 | 2022-06-02 08:15 | 2022-06-02 17:00 | 2022-06-02 09:15 |  |  | Attended site for damage showerhead in the male change rooms on the ground floor I have replaced the showerhead after I’ve tested everything is working correctly cleaned up packed up
MSA-DTWD | WA5481666 | 3 | AWB Co. | Room 13G1 - LED light baton fallen down | Electrical | Lighting, Internal | 136.06 | Pass | Pass | -1 | -1 | 1 | 2022-05-30 15:50 | 2022-06-07 17:00 | 2022-06-02 12:00 | 2022-06-07 17:00 | 2022-06-02 13:00 |  |  | Attended site and signed in. Completed JSA. Located block 13. Found light hanging. Brackets broken off. Re secured brackets to light fitting and fitted back into base plate. Tested all okay. Signed out. Job complete
MSA-DCA | WA5482355 | 1 | Critical Fire Protection & Training | Stage Door – Fire Panel - Detector in Zone 40 began has been picking up a fault | Fire Protection Services | Fire Protection - Monitor System | 346.44 | Pass | Pass | 0 | 0 | 1 | 2022-05-31 11:28 | 2022-06-01 17:00 | 2022-05-31 12:00 | 2022-06-01 17:00 | 2022-05-31 13:00 |  |  | Attended site to investigate fault on fire panel. On arrival found panel operating all systems normal. After investigating history log found detector M4-127/ level 2 bar area had previously gone into a no answer fault status. Photos taken for reference. Fault has not re-occurred since Saturday (28/5/22) afternoon. Identified and replaced detector head with extension poles as access to base is only plausible through use of EWP. System operating as normal after head replaced. If fault re-occurs to the same device then further action would be to replace detector base with use of EWP.
MSA-DTWD | WA5482383 | 1 | Australian Airconditioning Services Pty Ltd | Room F59 - Daikin A/C cassette won’t turn on | Air Conditioning | Room Air Conditioners | 228.03 | Pass | Pass | 0 | 0 | 1 | 2022-05-31 11:41 | 2022-06-01 17:00 | 2022-06-01 11:45 | 2022-06-01 17:00 | 2022-06-01 12:45 |  |  | Informed Denies to tell a/c user to give the aircon time to turn on to allow heating to start before pressing the button again
MSA-DCA | WA5482579 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Dumb waiter - emergency control stop button doesnt work | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-05-31 13:16 | 2022-05-31 15:16 | 2022-05-31 14:15 | 2022-05-31 17:16 | 2022-05-31 15:15 |  |  | Repaired under warranty - Np charges for attendance
MSA-DFES | WA5486831 | 3 | Complete Pest Management Services | Administration Building - Ground - Near Radio Comms Toilets - see details below | Pest Control | General Pest | 1000 | Pass | Pass | 0 | 0 | 1 | 2022-06-01 10:42 | 2022-06-09 17:00 | 2022-06-07 13:30 | 2022-06-09 17:00 | 2022-06-07 14:30 |  |  | Installed a requiem termite bait station near mens toilet, also inspected the grounds found 3 trees with evidence oftermite activity but no nest found
MSA-DTWD | WA5487423 | 3 | AWB Co. | 6 lights not working | Electrical | Lighting, Internal | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-06-01 15:07 | 2022-06-09 17:00 | 2022-06-08 12:45 | 2022-06-09 17:00 | 2022-06-08 13:45 |  |  | Attended site signed in jsa completed. Found lights not working in n40. Need man lift to access and will need braf.x1 man lift hirex1 box 25 tubes 865 36wx25 starters s10x2 people as spotter needed.labour to be booked with other jobs that need manliftNEED BRAF**BRAF DECLINED - CLOSE COST TO DATE**
MSA-DTWD | WA5487438 | 3 | AWB Co. | - loose light switch in Foyer near N58 | Electrical | Lighting, Internal | 150.89 | Pass | Pass | 0 | 0 | 1 | 2022-06-01 15:18 | 2022-06-09 17:00 | 2022-06-08 11:45 | 2022-06-09 17:00 | 2022-06-08 12:45 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located switch in passage, isolated circuit and removed old switch,replaced with new, re-energised lighting circuit and tested, everything working as intended,completed paperwork,packed up ***job completed***
MSA-DTAG | WA5488042 | 3 | Seme Solutions Pty Ltd | Pacom Computer System - screen is missing the shortcuts screen | Security | CCTV Surveillance | 130 | Pass | Pass | -1 | -1 | 1 | 2022-06-02 09:55 | 2022-06-10 17:00 | 2022-06-03 13:30 | 2022-06-10 17:00 | 2022-06-03 14:30 |  |  | Attended site, inspected custody workstation site map, missing text and shortcutsInspected site map editor, missing text and shortcuts still setup.Found 'view layout' was unselected, selected and missing text and shortcuts repopulated.
MSA-DFES | WA5488708 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Bunker Comcen - Ground Level - Unisex Toilet - Toilet running constantly - See notes below | Plumbing & Drainage | Toilets/Cisterns | 287.23 | Pass | Pass | 0 | 0 | 1 | 2022-06-02 15:12 | 2022-06-08 17:00 | 2022-06-08 14:00 | 2022-06-08 17:00 | 2022-06-08 15:00 |  |  | After replacing the cistern in the uni sex toilets of the bunker everything is working correctly
MSA-DCA | WA5488764 | 1 | Protek 24/7 Building & Maintenance | Playground area - Wooden Plank has become dislodged - See notes below | Equipment | Recreation Equipment | 136 | Pass | Pass | 0 | 0 | 1 | 2022-06-02 16:18 | 2022-06-03 17:00 | 2022-06-03 08:15 | 2022-06-03 17:00 | 2022-06-03 09:15 |  |  | Repair
MSA-DTAG | WA5490944 | 1 | Seme Solutions Pty Ltd | Magistrates Court Chambers - Fault with duress - See notes below | Security | Security Management System |  | Fail | Fail | 2 | 2 | 1 | 2022-06-03 10:31 | 2022-06-07 17:00 | 2022-06-22 08:00 | 2022-06-07 17:00 | 2022-06-22 09:00 |  |  | Duress unit removed and reset operation checked ok alarm cleared from system.
MSA-DTWD | WA5493704 | 1 | LIGHTHOUSE LOCKSMITHS | M block kitchen corridor between ceiling fixing workshop - Door handle is loose - See notes below | Security | Locksmith | 280 | Pass | Pass | 0 | 0 | 1 | 2022-06-07 09:53 | 2022-06-08 17:00 | 2022-06-07 12:25 | 2022-06-08 17:00 | 2022-06-07 13:25 |  |  | Replaced damaged outside handles, serviced lock and adjusted strike on M Block door
MSA-DTWD | WA5493726 | 2 | AHS Services WA Pty Ltd (Anchor) | Kendrew- A-Block 1st Floor West disabled toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 437.33 | Pass | Pass | 0 | 0 | 1 | 2022-06-07 09:59 | 2022-06-10 17:00 | 2022-06-07 15:00 | 2022-06-10 17:00 | 2022-06-07 16:00 |  |  | Plunged toilet due to excessive toilet roll
MSA-DTAG | WA5493845 | 1 | EASTERN HILLS ELECTRICAL SERVICE | Ground Level - Custody - Cell 2 – Lights flickering - See notes below | Electrical | Lighting, Internal | 155.54 | Pass | Pass | 0 | 0 | 1 | 2022-06-07 10:43 | 2022-06-08 17:00 | 2022-06-08 07:30 | 2022-06-08 17:00 | 2022-06-08 08:30 |  |  | Replaced cell light tubes
MSA-DTWD | WA5494934 | 3 | Protek 24/7 Building & Maintenance | E100 - 8 x lino tiles damaged | Flooring | Tiling | 196 | Pass | Pass | 0 | 0 | 1 | 2022-06-08 08:23 | 2022-06-15 17:00 | 2022-06-14 08:00 | 2022-06-15 17:00 | 2022-06-14 09:00 |  |  | BRAF declined Investigate breakdown report per above workorder details and report to Protek247 OperationsPerform make safe, make good or repair as instructed to prevent further damage or harm to persons and property
MSA-DTWD | WA5494999 | 2 | M Construction (WA) | O Glasshouse - Two core flute roof panels slipping from frame | Roofing | Metal Roofing | 143.8 | Pass | Pass | 0 | 0 | 1 | 2022-06-08 08:56 | 2022-06-13 17:00 | 2022-06-10 12:00 | 2022-06-13 17:00 | 2022-06-10 13:00 |  |  | Attended site and re-fixed core flute panels.
MSA-DTWD | WA5495130 | 1 | AWB Co. | J125 - Unable to restore power to workshop | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-06-08 09:39 | 2022-06-09 17:00 | 2022-06-08 12:45 | 2022-06-09 17:00 | 2022-06-08 13:45 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located dB with power issue, checked all emergency stop buttons, went to dB and reset switch , all power now working as intended , completed paperwork, signed out ***job completed***
MSA-DTWD | WA5495797 | 3 | AWB Co. | N42 - 15 x lights out | Electrical | Lighting, Internal | 136.06 | Pass | Pass | -1 | -1 | 1 | 2022-06-08 15:39 | 2022-06-15 17:00 | 2022-06-10 14:00 | 2022-06-15 17:00 | 2022-06-10 15:00 |  |  | Milan Barjaktar (10/06/2022) - Work NoteAttended site signed in jsa completed. Found n42 with 66 tubes needed to be replaced as 33 fittings have faulty tubes in them. Will need man lift and 66 s10 starters and 66 tubes 865 colour.*** job needs BRAF***BRAF DECLINED
MSA-DTAG | WA5496312 | 3 | Midolo Building Services | Level 4 - Court welfare - White board attached to timber framework - fixings are slightly loose | Building | General Building | 147.89 | Pass | Pass | 0 | 0 | 1 | 2022-06-09 09:09 | 2022-06-16 17:00 | 2022-06-13 11:00 | 2022-06-16 17:00 | 2022-06-13 12:00 |  |  | WHITE BOARD RE FIXED
MSA-DTWD | WA5496485 | 2 | AHS Services WA Pty Ltd (Anchor) | Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 94.19 | Pass | Pass | -1 | -1 | 1 | 2022-06-09 10:31 | 2022-06-14 17:00 | 2022-06-09 15:00 | 2022-06-14 17:00 | 2022-06-09 16:00 |  |  | Plunged toilet due to excessive toilet roll
MSA-DTWD | WA5497007 | 3 | AHS Services WA Pty Ltd (Anchor) | A Block - Level 3 - East End - Male cubicle - opposite A350.1 - is not turning off | Plumbing & Drainage | Toilets/Cisterns | 94.19 | Pass | Pass | 0 | 0 | 1 | 2022-06-09 13:38 | 2022-06-16 17:00 | 2022-06-14 13:30 | 2022-06-16 17:00 | 2022-06-14 14:30 |  |  | Readjusted cistern back to wall so flush mechanism doesnt get jammed
MSA-DFES | WA5497196 | 2 | Australian HVAC Services Pty. Ltd. | Main Admin - Ground - Lecture room 9 - Air con blowing out cold air on heat setting | Air Conditioning | Room Air Conditioners | 187.61 | Pass | Pass | -1 | -1 | 1 | 2022-06-09 15:36 | 2022-06-14 17:00 | 2022-06-10 08:00 | 2022-06-14 17:00 | 2022-06-10 09:00 |  |  | Attended service call. Tested operation of training room 9 ,found controls were not set correctly, set controls to heat & tested operation. Ok
MSA-DTWD | WA5499215 | 2 | AWB Co. | Car park - Lights not working from entrance of Dixon Road to outside J Block | Electrical | Lighting, External | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-06-10 11:32 | 2022-06-15 17:00 | 2022-06-15 11:00 | 2022-06-15 17:00 | 2022-06-15 12:00 |  |  | Attended site signed in jsa completed. Found feed from j block for lights in F block board f60 class. Two poles had tripped breakers so werent on. Tested with pe cell and all working.*** job completed ***
MSA-DTAG | WA5504160 | 1 | Sapio Pty Ltd | Ground Floor - Middle Custody Gate won't latch again | Security | Access Control | 540 | Pass | Pass | 0 | 0 | 1 | 2022-06-11 10:10 | 2022-06-12 10:10 | 2022-06-11 15:30 | 2022-06-12 10:10 | 2022-06-11 16:30 |  |  | Arrived on site and found that the lock tongue sense spring was preventing mortice latch from fully sealing. Removedspring, tested door, tested OK.
MSA-DTWD | WA5511769 | 2 | Techworks Plumbing | AF18 staff lunch room - Kitchen tap split leaking | Plumbing & Drainage | Water | 295.38 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 08:48 | 2022-06-16 17:00 | 2022-06-15 13:30 | 2022-06-16 17:00 | 2022-06-15 14:30 |  |  | Attended site and signed in checked mixer and it had split on the spout. Went to supplier to get a replacement.returned to site and removed old mixer installed new mixercompleted work
MSA-DTWD | WA5511826 | 1 | BJ SYSTEMS | Main Auto Door - door not responding to open or close | Security | Access Control | 160 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 09:31 | 2022-06-14 17:00 | 2022-06-13 11:45 | 2022-06-14 17:00 | 2022-06-13 12:45 |  |  | Check Gallagher system on PC at Kendrew Crescent. Emergency release on P Block main auto door. Check breakglass and tripped, reset breakglass, door is ok
MSA-DTAG | WA5511926 | 1 | Bullant Security Pty Ltd | Ground Floor - Duty lawyer office- Barrell is loose and will not lock | Security | Locksmith | 305.91 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 10:59 | 2022-06-14 17:00 | 2022-06-14 09:55 | 2022-06-14 17:00 | 2022-06-14 10:55 |  |  | Attend site, service Astra mortice lock and replace broken latch springs Date on site: 14/06/2022Time on site: 09:55am - 10:55am
MSA-DCA | WA5511990 | 1 | Techworks Electrical | Faulty power supply to pump needs to be checked | Electrical | General Electrical | 392.47 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 11:58 | 2022-06-14 17:00 | 2022-06-13 12:00 | 2022-06-14 17:00 | 2022-06-13 13:00 |  |  | Tasks completed 1. arrived and met with Reese out at the wetlands. 2. Reese asked us to rest a power box that was full of outlets for power. All gpos had power and working well. 3. found the vsd was tripping sue to over current. This would be caused from failed windings over drawing current. 4. Reese is organising commercial aquatics to complete repairs.
MSA-DTWD | WA5512112 | 1 | Protek 24/7 Building & Maintenance | F4 - Roof leak | Roofing | Metal Roofing | 272.5 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 13:51 | 2022-06-14 17:00 | 2022-06-14 09:30 | 2022-06-14 17:00 | 2022-06-14 10:30 |  |  | cleaned and unblocked areas causing water ingress to building - F4
MSA-DTWD | WA5512115 | 1 | Protek 24/7 Building & Maintenance | roof leak | Roofing | Metal Roofing | 291.08 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 13:57 | 2022-06-14 17:00 | 2022-06-14 12:30 | 2022-06-14 17:00 | 2022-06-14 13:30 |  |  | Braf Declined Attempted to clean and re-seal but was unable
MSA-DTWD | WA5512183 | 3 | AWB Co. | C006 - 4 x lights out | Electrical | Lighting, Internal | 339.33 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 14:40 | 2022-06-20 17:00 | 2022-06-20 08:00 | 2022-06-20 17:00 | 2022-06-20 09:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located faulty lighting and made list of parts, went to wholesaler to pick up lamps like for like, returned to site and removed old lamps, replaced with new, tested all lights and they are working as intended , completed paperwork,packed up, signed out ***job complete** extra tubes and starter left on site for fm as requested
MSA-DTAG | WA5513190 | 1 | AAA Ability Locksmiths | Court 82 - Door not locking Properly | Security | Locksmith | 255 | Pass | Pass | 0 | 0 | 1 | 2022-06-14 08:31 | 2022-06-15 17:00 | 2022-06-15 10:30 | 2022-06-15 17:00 | 2022-06-15 11:30 |  |  | Attend site, service and repair lock.
MSA-DTWD | WA5513278 | 1 | Schindler Lifts Australia | T Block - Lift - Lift on right showing out of order - Lift provides access to plant room | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-14 09:08 | 2022-06-15 17:00 | 2022-06-14 11:00 | 2022-06-15 17:00 | 2022-06-14 12:00 |  |  | Found object stuck between landing doors , removed object and reset, completed inspection visit
MSA-DTWD | WA5513706 | 1 | Protek 24/7 Building & Maintenance | G23A - Roof leak along western wall - Box gutter is possible source of leak | Roofing | Metal Roofing | 207.64 | Pass | Pass | 0 | 0 | 1 | 2022-06-14 12:38 | 2022-06-15 17:00 | 2022-06-15 07:30 | 2022-06-15 17:00 | 2022-06-15 08:30 |  |  | Inspection of Roof leak Work completed on WA5513706
MSA-DTWD | WA5513977 | 1 | Schindler Lifts Australia | Block A - Ground Floor - Lift 1 - Appears phone line is not working inside lift | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1 | 2022-06-14 14:36 | 2022-06-15 17:00 | 2022-06-17 13:30 | 2022-06-15 17:00 | 2022-06-17 14:30 |  |  | Lift phone works in L block but asked to check A block but we do not service the lift very Hannah check if we have contact
MSA-DTAG | WA5513993 | 1 | Sapio Pty Ltd | Fault L30 Board PSU Low Battery | Security | Monitoring | 145 | Pass | Pass | 0 | 0 | 1 | 2022-06-14 14:41 | 2022-06-15 17:00 | 2022-06-15 09:30 | 2022-06-15 17:00 | 2022-06-15 10:30 |  |  | Attended site. Replaced batteries on Level 30. All OK.
MSA-DTWD | WA5518663 | 1 | Protek 24/7 Building & Maintenance | Roof Leak - Water dripping along A/C vent in center of room | Roofing | Metal Roofing | 196 | Pass | Pass | 0 | 0 | 1 | 2022-06-15 08:03 | 2022-06-16 17:00 | 2022-06-15 09:30 | 2022-06-16 17:00 | 2022-06-15 10:30 |  |  | Repair roof leak -
MSA-DTAG | WA5521061 | 1 | FSA (WA) Pty Ltd | ALS Office - Fire alarm in ALS office needs fixing | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-06-15 10:15 | 2022-06-16 17:00 | 2022-06-16 07:30 | 2022-06-16 17:00 | 2022-06-16 08:30 |  |  | Attended site to investigate device in ALS office, sensor triggered into alarm. Reset break glass sensor, system responding normally upon departure.
MSA-MRWA | WA5521817 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - See PFM for location- Slow data computer port - See notes below | Equipment | Electrical Equipment | 170.89 | Pass | Pass | 0 | 0 | 1 | 2022-06-15 11:01 | 2022-06-20 17:00 | 2022-06-20 08:00 | 2022-06-20 17:00 | 2022-06-20 09:00 |  |  | Tested both points under desk 157 and 158. 1 had minor cables not terminated correctly in patch panel. Reterminated and retested. No further issues found.
MSA-DCA | WA5522363 | 1 | Techworks Electrical | Ground Level - Hacket Hall - Stuio Foyer - Electrical Floor Box – Cover will not stay down -See note | Electrical | General Electrical | 152.14 | Pass | Pass | 0 | 0 | 1 | 2022-06-15 14:46 | 2022-06-16 17:00 | 2022-06-16 06:30 | 2022-06-16 17:00 | 2022-06-16 07:30 |  |  | No fault found, pressed the release back closed the lid and it stays down fine.
MSA-DTWD | WA5534694 | 2 | AWB Co. | faulty light | Electrical | Lighting, External | 198.2 | Pass | Pass | 0 | 0 | 1 | 2022-06-16 13:24 | 2022-06-21 17:00 | 2022-06-20 09:00 | 2022-06-21 17:00 | 2022-06-20 10:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located faulty lighting and made list of parts, replaced with new, tested all lights and they are working as intended , completed paperwork,packed up, signed out ***job complete**
MSA-DCA | WA5534868 | 1 | Techworks Electrical | Level 2 - Top of marble staircase, upper circle entry - Light not functioning | Electrical | General Electrical | 232.11 | Pass | Pass | 0 | 0 | 1 | 2022-06-16 15:08 | 2022-06-17 17:00 | 2022-06-17 09:00 | 2022-06-17 17:00 | 2022-06-17 10:00 |  |  | Took globe out and found light had no power. Found a loose connection in the terminal block, isolated , repaired light and cabling, all working again.
MSA-DCA | WA5534917 | 1 | Techworks Electrical | Dressing Rooms - Currently no power to Dressing Room GPOs, please reinstate power. DB L2-01 | Electrical | General Electrical | 214.55 | Pass | Pass | 0 | 0 | 1 | 2022-06-16 15:48 | 2022-06-17 17:00 | 2022-06-17 11:00 | 2022-06-17 17:00 | 2022-06-17 12:00 |  |  | Found tripped rcd. Reset, tested and all working well.
MSA-DCA | WA5548403 | 3 | Techworks Electrical | Stalls Foyer - Male Toilets - Hand Dryer Broken | Electrical | General Electrical | 214.55 | Pass | Pass | -1 | -1 | 1 | 2022-06-17 08:34 | 2022-06-24 17:00 | 2022-06-20 14:00 | 2022-06-24 17:00 | 2022-06-20 15:00 |  | WACCES | Tested unit and found motor to be burnt out, close off and quote required on replacement.
MSA-DTWD | WA5549034 | 3 | Falcetta Plumbing and Gas | 3B6 - Faulty floor waste | Plumbing & Drainage | Drainage | 163.88 | Pass | Pass | 0 | 0 | 1 | 2022-06-17 12:13 | 2022-06-24 17:00 | 2022-06-24 12:00 | 2022-06-24 17:00 | 2022-06-24 13:00 |  |  | sealed sink to prevent overflow
MSA-DFES | WA5549171 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Male & Female toilet - opposite Reception, Doors sticking and latches not turning | Building | Doors | 196 | Pass | Pass | 0 | 0 | 1 | 2022-06-17 13:56 | 2022-06-24 17:00 | 2022-06-22 09:00 | 2022-06-24 17:00 | 2022-06-22 10:00 |  |  | Repair sticking doors in male & female toilets
MSA-DTAG | WA5549194 | 1 | Schindler Lifts Australia | Lift 2 - Lift 2 carriage doors make a noise on closing | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-17 14:24 | 2022-06-20 17:00 | 2022-06-17 17:25 | 2022-06-20 17:00 | 2022-06-17 18:25 |  |  | Had trouble accessing site. Spoke with Ian to advise to see guards from district law courts. Security were busy and asked for usto return later. I advised I will am call for Monday morning. Text to ABS to advise of outcome
MSA-DCA | WA5555344 | 1 | OTIS ELEVATOR COMPANY PTY LTD | Main foyer - public lift is not working - doors are closed and not responding. | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-19 16:15 | 2022-06-20 16:15 | 2022-06-20 12:00 | 2022-06-20 16:15 | 2022-06-20 13:00 |  |  | Repaired under warranty - No charges for attendance
MSA-DFES | WA5562651 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Warehouse - Office - smoke alarm - alarming and not turning off | Electrical | General Electrical | 178.2 | Pass | Pass | 0 | 0 | 1 | 2022-06-20 08:55 | 2022-06-20 10:55 | 2022-06-20 09:30 | 2022-06-20 12:55 | 2022-06-20 10:30 |  |  | Arrived on site at 09:30 to investigate smoke alarm going off, found smoke alarm to be faulty. Replaced with new 240v smoke alarm and tested. Left site at 10:30
MSA-DTWD | WA5562720 | 1 | Equans Mechanical Services Australia | 3A60 - Ground - A/C in classroom not working | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 1 | 2022-06-20 09:23 | 2022-06-21 17:00 | 2022-06-21 11:00 | 2022-06-21 17:00 | 2022-06-21 12:00 |  |  | CHECKED AND FOUND HEAT PASTE OF BUT SCREW HAD COME LOOSE. TIGHTENED AND CHECK - NO FAULT AND RUNNING OK
MSA-DTAG | WA5562991 | 3 | Midolo Building Services | Level 5 - Court 57 - Protective strip of stair leading into gallery is loose | Flooring | Timber | 125.44 | Pass | Pass | -1 | -1 | 1 | 2022-06-20 11:23 | 2022-06-27 17:00 | 2022-06-21 08:15 | 2022-06-27 17:00 | 2022-06-21 09:15 |  |  | STAIR TREAD SECURED
MSA-DTWD | WA5563270 | 2 | Assa Abloy Entrance Systems Aust P/L-WA | Ground floor - Internal entry - swipe card door - please see details below | Building | Security Doors | 358 | Pass | Pass | 0 | 0 | 1 | 2022-06-20 13:24 | 2022-06-23 17:00 | 2022-06-21 08:15 | 2022-06-23 17:00 | 2022-06-21 09:15 |  |  | Attended site. Checked gates settings and adjustments all ok. Inspection found gates magnetic lock does not release immediately when using swipecard or push button. It pulls the gate back as it tries to open,but eventually opens after few seconds. Seems to be a security access system problem.Recommend to get a security access technician to fix the problem.
MSA-DTWD | WA5565119 | 2 | Techworks Plumbing | D015.2 - toilet system faulty | Plumbing & Drainage | Toilets/Cisterns | 223.9 | Pass | Pass | 0 | 0 | 1 | 2022-06-21 13:54 | 2022-06-24 17:00 | 2022-06-22 09:00 | 2022-06-24 17:00 | 2022-06-22 10:00 |  |  | Water inlet to the cistern was block with rubble. Removed the inlet valve and cleared out the service then put back together and test.
MSA-DFES | WA5565508 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Station Officers shower - tap washers are faulty | Plumbing & Drainage | Materials | 138.95 | Pass | Pass | -1 | -1 | 1 | 2022-06-22 08:33 | 2022-06-27 17:00 | 2022-06-22 09:45 | 2022-06-27 17:00 | 2022-06-22 10:45 |  |  | Went to shower receded shower breech. On the clod side on the seat there is a crackling and l can not receded it ou. Shower breech has to be replace.
MSA-DTWD | WA5565920 | 1 | SCAVENGER SUPPLIES PTY LTD | S block - Ground floor - North entry - Fault showing on fire panel S Block / Fault 0 | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-06-22 12:40 | 2022-06-23 17:00 | 2022-06-22 14:00 | 2022-06-23 17:00 | 2022-06-22 15:00 |  |  | COMPLETED 22/6/22
MSA-DTAG | WA5566831 | 1 | Schindler Lifts Australia | Ground floor - Lift #3 -Missing lock on panel above floor buttons, panel can be opened by public | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-23 11:49 | 2022-06-24 17:00 | 2022-06-23 14:00 | 2022-06-24 17:00 | 2022-06-23 15:00 |  |  | Cop lock missing. Secured cop. Obr raised for new lock. Lift rts.
MSA-DCA | WA5567123 | 1 | TK Elevator Australia Pty Ltd | Lift 7 broken down again - displaying Out of Order, Recurring issue. | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-23 15:03 | 2022-06-24 17:00 | 2022-06-23 17:00 | 2022-06-24 17:00 | 2022-06-23 18:00 |  |  | Lift7 Green Rm-Hydraulic :On arrival found lift stopped with TTElap error on bottom level with doors open, checked connections in releveling circuit, reset processor, lift started working as normal, left the lift working.
MSA-DCA | WA5568067 | 1 | Techworks Plumbing | Francis Street - Ground Level - UAT Behind reception - Toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 223.9 | Pass | Pass | 0 | 0 | 1 | 2022-06-24 15:13 | 2022-06-27 17:00 | 2022-06-24 15:30 | 2022-06-27 17:00 | 2022-06-24 16:30 |  |  | Attended site, went to front desk the receptionist showed me the blocked toilet behind the information bay, when arrived toilet was not blocked, gave it a flush and it started to Syphen in the trap, so kept flushing and plunging toilet it eventually gave in and freed up started to flush toilet paper to make sure the blocking was clear and then grabbed signature and signed out
MSA-DTWD | WA5568613 | 3 | AWB Co. | E527 classroom - Water dripping from ceiling | Building | General Building | 230.63 | Pass | Pass | -1 | -1 | 1 | 2022-06-27 07:34 | 2022-07-01 17:00 | 2022-06-27 14:45 | 2022-07-01 17:00 | 2022-06-27 15:45 |  |  | Attended and renewed seals to locations pictured
MSA-DTWD | WA5568776 | 2 | Securex Security Systems & Services | Hangar - Ground floor - entry - swipe card door - see details below | Security | Access Control | 220 | Pass | Pass | 0 | 0 | 1 | 2022-06-27 08:54 | 2022-06-30 17:00 | 2022-06-27 10:10 | 2022-06-30 17:00 | 2022-06-27 11:10 |  |  | 27/06/2022, 1010-1110Faulty controller not releasing maglock.De-energized maglock to allow mechanical door release to work correctly.Door secure. Client advised not to replace controller as maglock not required as double secured and ok
MSA-DTWD | WA5569538 | 2 | AWB Co. | Passageway outside 5F12 - Water leak through light | Building | Ceiling |  | Pass | Pass | 0 | 0 | 1 | 2022-06-27 15:39 | 2022-06-30 17:00 | 2022-06-30 15:30 | 2022-06-30 17:00 | 2022-06-30 16:30 |  |  | to be closed out at $0 cost
MSA-DTAG | WA5570505 | 2 | Sapio Pty Ltd | Level 30 - Doors playing up, Delay after swipe to get into floor | Security | Access Control | 195 | Pass | Pass | 0 | 0 | 1 | 2022-06-28 11:58 | 2022-07-01 17:00 | 2022-06-28 14:00 | 2022-07-01 17:00 | 2022-06-28 15:00 |  |  | Reset reader on Level 23 Goods Lift. Resynced controller 19, 20 & 21
MSA-DTWD | WA5570653 | 2 | Techworks Electrical | broken GPO on the window side | Electrical | General Electrical | 244.83 | Pass | Pass | 0 | 0 | 1 | 2022-06-28 13:28 | 2022-07-01 17:00 | 2022-07-01 09:30 | 2022-07-01 17:00 | 2022-07-01 10:30 |  |  | Replaced damaged gpo with new gpo, tested and labelled circuit
MSA-DTWD | WA5570996 | 3 | AHS Services WA Pty Ltd (Anchor) | Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | -1 | -1 | 1 | 2022-06-29 07:01 | 2022-07-05 17:00 | 2022-06-29 11:00 | 2022-07-05 17:00 | 2022-06-29 12:00 |  |  | Job completed
MSA-DTAG | WA5572047 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Custody - Custody toilets blocked - See notes below | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | 0 | 0 | 1 | 2022-06-29 13:24 | 2022-06-30 17:00 | 2022-06-30 11:00 | 2022-06-30 17:00 | 2022-06-30 12:00 |  |  | Job completed
MSA-DTAG | WA5572120 | 2 | Sapio Pty Ltd | Level 22 - Doors playing up, Delay after swipe to get into floor - See notes below | Security | Access Control | 130 | Pass | Pass | 0 | 0 | 1 | 2022-06-28 15:00 | 2022-07-01 17:00 | 2022-06-29 16:30 | 2022-07-01 17:00 | 2022-06-29 17:30 |  |  | Attended site power cycled controller and reader, checked logs and re tested door all working.
MSA-DTAG | WA5572130 | 2 | Sapio Pty Ltd | Level 23 -Doors playing up, Delay after swipe to get into floor | Security | Access Control | 130 | Pass | Pass | -1 | -1 | 1 | 2022-06-29 14:04 | 2022-07-04 17:00 | 2022-06-29 18:30 | 2022-07-04 17:00 | 2022-06-29 19:30 |  |  | Checked programming and resynced.
MSA-DTWD | WA5572161 | 2 | Lane's Plumbing | BLD 813 - Toilet - Leaking toilet Pan | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 1 | 2022-06-29 14:24 | 2022-07-04 17:00 | 2022-07-01 09:30 | 2022-07-04 17:00 | 2022-07-01 10:30 |  |  | Repairs to toilet
MSA-DTAG | WA5572269 | 3 | Midolo Building Services | Court 35 - Plaque to be secured to wall under photo (marked by sticky note) | Building | General Building | 172.75 | Pass | Pass | 0 | 0 | 1 | 2022-06-29 15:21 | 2022-07-06 17:00 | 2022-07-04 07:30 | 2022-07-06 17:00 | 2022-07-04 08:30 |  |  | secured plaque
MSA-DFES | WA5572710 | 1 | Go Doors | COMCEN - Server Room - lock is faulty | Building | Automatic Doors | 310 | Pass | Pass | 0 | 0 | 1 | 2022-06-30 09:41 | 2022-07-01 17:00 | 2022-06-30 13:15 | 2022-07-01 17:00 | 2022-06-30 14:15 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5572987 | 2 | Australian HVAC Services Pty. Ltd. | Training Room - Air conditioner in training room has ceased to operate | Air Conditioning | Room Air Conditioners | 130.05 | Pass | Pass | 0 | 0 | 1 | 2022-06-30 12:55 | 2022-07-05 17:00 | 2022-07-05 08:00 | 2022-07-05 17:00 | 2022-07-05 09:00 |  |  | Rhys Hall (05/07/2022) - Work NoteUpon trying to test the unit and some investigations realised there is no power to the unit. Isolation switches on and also on at main power board, spoke with Andrew and we came to the conclusion that when the building has been re wired the electricians haven't re connected the air-conditioning. Andrew is going to follow up with his contractorsUPDATE been called out for service call and still the same issue, had another firemen speak with Andrew on the phone and he said contractors still haven't been out and unsure on a date. Firemen may no be communicating about the AC with each other.
MSA-MRWA | WA5578606 | 1 | Automatic Fire Protection (ARA) | Basement Fire panel - Reset fault to server room | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-07-01 13:39 | 2022-07-04 17:00 | 2022-07-01 14:00 | 2022-07-04 17:00 | 2022-07-01 15:00 |  |  | BG 1/7/22Fault on MFIP due after server room works were performed, and subsequently vesda was isolated. De isolated zones and reset faults. Performed training with site personal on how to approach this in future.
MSA-DTAG | WA5578688 | 3 | Bullant Security Pty Ltd | Mandruah Court Registry - Occupied/Vacant lock to be installed on staff mens toilet | Security | Locksmith | 759.54 | Pass | Pass | -1 | -1 | 1 | 2022-07-01 14:32 | 2022-07-08 17:00 | 2022-07-04 09:10 | 2022-07-08 17:00 | 2022-07-04 10:10 |  |  | Attended site, installed new mortice lock, door furniture and cylinder to staff male toilet door.Date on site: 04/07/2022Time on site: 09:10am - 10:10am
MSA-DTWD | WA5585120 | 3 | AWB Co. | Repair & paint water damaged eaves lining following leak repair | Roofing | Metal Roofing | 995.96 | Pass | Pass | -1 | -1 | 1 | 2022-07-05 12:45 | 2022-07-12 17:00 | 2022-07-06 09:45 | 2022-07-12 17:00 | 2022-07-06 10:45 |  |  | Attended and investigated, another job is covering this leak, this will be for a painter once resolved.
MSA-DTAG | WA5585371 | 3 | AFD Contracting | Ground court room 3 gate-has come off and is “propped” up. Appears to have rusted | Building | Steel Fencing & Gates | 999 | Fail | Fail | 2 | 2 | 1 | 2022-07-05 15:33 | 2022-07-12 17:00 | 2022-07-27 08:45 | 2022-07-12 17:00 | 2022-07-27 09:45 |  |  | 27/07/22Workshop: Manufactured new brackets. Collected hinges.Site works: Cut off old hinges. Cleaned up weld, treated with paint. New brackets installed. Set hinges. Drilled hole for shute bolt.
MSA-DTWD | WA5585398 | 1 | OTIS ELEVATOR COMPANY PTY LTD | Lift lobby button - call button faulty - damaged | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-07-05 12:05 | 2022-07-06 17:00 | 2022-07-06 07:30 | 2022-07-06 17:00 | 2022-07-06 08:30 |  |  | Repaired under warranty - No charges for attendance
MSA-DTWD | WA5585856 | 2 | AWB Co. | ground CG10-Main breaker keeps tripping. | Electrical | General Electrical | 136.06 | Pass | Pass | -1 | -1 | 1 | 2022-07-06 08:52 | 2022-07-11 17:00 | 2022-07-06 14:45 | 2022-07-11 17:00 | 2022-07-06 15:45 |  |  | Attended site and signed in , completed jsa,spoke with fm about job,walked down to c block and located rcd , spoke with technician and he said that it wasn’t resetting, tested rcd and working as intended, technician wasn’t resetting it correctly, fm wanted me to replace cover on dol starter for him also, fm supplied cover and I changed it over also, packed up, completed paperwork, signed out, **job completed**
MSA-DTWD | WA5586783 | 2 | AWB Co. | Faulty fluoro light | Electrical | Lighting, Internal | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-07-06 14:43 | 2022-07-11 17:00 | 2022-07-08 14:00 | 2022-07-11 17:00 | 2022-07-08 15:00 |  |  | Attended site and signed in. Completed JSA. Located faulty lights in office. Replace lamps and starters and tombstones with site supplied stock. Tested all okay. Signed out. Job complete
MSA-DCA | WA5587879 | 0 | Critical Fire Protection & Training | ground floor - Fire panel - in fault | Fire Protection Services | Fire Protection - Monitor System | 240.58 | Pass | Pass | 0 | 0 | 1 | 2022-07-07 11:28 | 2022-07-07 13:28 | 2022-07-07 12:00 | 2022-07-07 15:28 | 2022-07-07 13:00 |  |  | Arrived on site as a call-out. Discussed call-out raised due to false alarm activated. Found warning system in isolated evacuate mode. Multiple isolates present throughout system due to current performances present. Found auxiliaries and external bell had activated but code red system did not call brigade. 1x history log of M2-200 GFA relay entered fault at 10:36 potentially the cause of alarm devices activating but not code red activating.During next annual confirmation of code red dial out system required to confirm if 3 minute delay is programmed in from EWIS evacuate tone to code red alarm activation. All system returned to normal operation with performance isolates present.
MSA-DCA | WA5588016 | 3 | Techworks Electrical | Administration Building - First Floor - Tombstones in fluro unit aren’t working. Extra led fitting | Electrical | Lighting, Internal | 135.15 | Pass | Pass | -1 | -1 | 1 | 2022-07-07 12:28 | 2022-07-14 17:00 | 2022-07-07 15:00 | 2022-07-14 17:00 | 2022-07-07 16:00 |  |  | Replaced fitting with new LED panel supplied by crc
MSA-DTWD | WA5588112 | 1 | Water2water Pty Ltd | Staff Kitchen - Wall Boiler Unit is leaking water from base | Plumbing & Drainage | HWS/Units Electric & Gas | 237.09 | Pass | Pass | 0 | 0 | 1 | 2022-07-07 13:13 | 2022-07-08 17:00 | 2022-07-07 15:25 | 2022-07-08 17:00 | 2022-07-07 16:25 |  |  | Replaced leaking solenoid
MSA-DTWD | WA5589009 | 2 | AHS Services WA Pty Ltd (Anchor) | E-Block Male toilets end cubicle has a broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 130.78 | Pass | Pass | -1 | -1 | 1 | 2022-07-08 09:11 | 2022-07-13 17:00 | 2022-07-08 13:30 | 2022-07-13 17:00 | 2022-07-08 14:30 |  |  | Completed
MSA-DTWD | WA5589012 | 2 | Techworks Electrical | Workshops disabled toilets lights not working | Electrical | Lighting, Internal | 205.73 | Pass | Pass | 0 | 0 | 1 | 2022-07-08 09:14 | 2022-07-13 17:00 | 2022-07-12 14:00 | 2022-07-13 17:00 | 2022-07-12 15:00 |  |  | Replaced electronic ballest and installed 2x new 28w T5 tubes.
MSA-DTWD | WA5589490 | 3 | AWB Co. | Water leaking through ceiling just inside main door | Roofing | Metal Roofing | 242.46 | Pass | Pass | -1 | -1 | 1 | 2022-07-08 13:25 | 2022-07-15 17:00 | 2022-07-11 14:00 | 2022-07-15 17:00 | 2022-07-11 15:00 |  |  | Inspect leak above pillars found no issue, inspected Balustarding found small splits in silicon in multiple areas carried out repairs. Would suggest that main leak is hidden byrubber membrane
MSA-DTWD | WA5589638 | 3 | Falcetta Plumbing and Gas | Block 3 - Cleaners room - Sink Blocked | Plumbing & Drainage | Toilets/Cisterns | 508.88 | Pass | Pass | -1 | -1 | 1 | 2022-07-08 15:10 | 2022-07-15 17:00 | 2022-07-11 09:00 | 2022-07-15 17:00 | 2022-07-11 10:00 |  | WCAPPR | drainsflush unblock cleaners sink
MSA-MRWA | WA5596699 | 2 | AWB Co. | Corridor Light switch side entrance - Faulty Light switch - See notes below | Electrical | Lighting, Internal | 151.28 | Pass | Pass | 0 | 0 | 1 | 2022-07-11 09:52 | 2022-07-14 17:00 | 2022-07-11 14:00 | 2022-07-14 17:00 | 2022-07-11 15:00 |  |  | Attended site and signed in, completed jsa, spoke with person on site about job, located switch , isolated circuit, removed switch and grid plate and replaced with new , re energised circuit, everything working as intended, completed paperwork,signed out ***job completed**
MSA-DTWD | WA5596746 | 3 | AWB Co. | water damaged light switch | Electrical | General Electrical | 184.73 | Pass | Pass | -1 | -1 | 1 | 2022-07-11 10:13 | 2022-07-18 17:00 | 2022-07-14 09:30 | 2022-07-18 17:00 | 2022-07-14 10:30 |  |  | Attended site signed in jsa completed. Found x2 lights not working in toilets due to broken switch. Replaced with new 20a mech and now working. Job completed
MSA-DFES | WA5597710 | 2 | AWB Co. | Ground Level - Dorm 7 - Door from dorm to shower area broken and unable to be opened | Building | Doors | 137.19 | Pass | Pass | 0 | 0 | 1 | 2022-07-11 15:16 | 2022-07-14 17:00 | 2022-07-12 10:30 | 2022-07-14 17:00 | 2022-07-12 11:30 |  |  | attended works - job had been cancelledJSA note required as no works completed
MSA-DTAG | WA5603306 | 1 | OCS SERVICES PTY LTD | Registry- Front Counter 3 & Desk near back pillar in back registry (signs on desks) - 2x Covid Clean | Cleaning | Emergency Cleans |  | Pass | Fail | 0 | 0 | 1 | 2022-07-12 09:34 | 2022-07-13 17:00 | 2022-07-13 17:00 | 2022-07-13 17:00 | 2022-07-13 18:00 |  |  | Covid clean complete
MSA-DTWD | WA5603942 | 3 | AWB Co. | Replace Fluro tubes | Electrical | Lighting, Internal | 183.21 | Pass | Pass | 0 | 0 | 1 | 2022-07-12 14:23 | 2022-07-19 17:00 | 2022-07-18 11:00 | 2022-07-19 17:00 | 2022-07-18 12:00 |  |  | Attended site and signed in. Completed JSA. Located faulty lights. Supply and replace tubes and starters to all lights out in room. Tested all okay. Signed out. Job complete
MSA-DCA | WA5608291 | 0 | Techworks Electrical | Electrical circuit tripped due to possible water in light fitting | Electrical | General Electrical | 163.3 | Pass | Pass | 0 | 0 | 1 | 2022-07-13 07:40 | 2022-07-13 09:40 | 2022-07-13 09:00 | 2022-07-13 11:40 | 2022-07-13 10:00 |  |  | Found no tripped circuits, someone had turned light switches off and not turned them back on. All water had dried up and found no left over water.
MSA-DTWD | WA5609019 | 2 | AWB Co. | Room S100A - Collapsed desk in S100A | Equipment | Office Appliances | 137.19 | Pass | Pass | -1 | -1 | 1 | 2022-07-13 13:31 | 2022-07-18 17:00 | 2022-07-14 15:45 | 2022-07-18 17:00 | 2022-07-14 16:45 |  |  | Attended site and contacted Steve for details. Then located area where desk parts had been left. Found that desk wasn’t complete then tracked down security officer. He gained me entry into building “B” to see if parts needed were in there. After some searching parts missing weren’t there. Contacted Steve and he said he would be back in contact.no works completed, nil jsa or signature slip required
MSA-DCA | WA5609616 | 1 | Dormakaba Australia Pty Ltd | External workshop – far right roller door - mechanism has failed. Door is hard to secure. | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 1 | 2022-07-13 15:11 | 2022-07-14 17:00 | 2022-07-14 07:30 | 2022-07-14 17:00 | 2022-07-14 08:30 |  |  | Inspection of door found door is Bradley rusting away on the edge of the curtain causing door to jam and get stiffUnable to repair door requires replacingQuote for new doorQuoteQuote to replace old roller door with new B&D series 1Opening hieght 2700mmOpening width 3040mmCentre lockColour domainX2 techsX1 gene lifterX1 flat bed trailer
MSA-DTAG | WA5611421 | 1 | AWB Co. | lights not working in foyer area | Electrical | Lighting, Internal | 180.93 | Pass | Pass | 0 | 0 | 1 | 2022-07-14 08:59 | 2022-07-15 17:00 | 2022-07-14 12:00 | 2022-07-15 17:00 | 2022-07-14 13:00 |  |  | Attended site signed in jsa completed. Found x4 lights flickering/ not working in foyer area. Replaced with x4 new 10w led globes. all operational nowJob completed
MSA-DCA | WA5611903 | 3 | Wilson Security | E Block - Retrospective WO for security call out for 2/7/2022 14.43 - See notes below | Security | Monitoring |  | Fail | Fail | 1 | 1 | 1 | 2022-07-02 14:45 | 2022-07-08 17:00 | 2022-07-14 15:00 | 2022-07-08 17:00 | 2022-07-14 16:00 | 1 |  | Completed
MSA-DTWD | WA5613689 | 3 | AWB Co. | Ground Level - Lift Room - Lights not working - See notes below | Electrical | Lighting, Internal | 165.55 | Pass | Pass | 0 | 0 | 1 | 2022-07-14 15:20 | 2022-07-21 17:00 | 2022-07-18 12:00 | 2022-07-21 17:00 | 2022-07-18 13:00 |  |  | Attended site signed in jsa completed.Found x6 tubes and starters faulty in lift lobby. Replaced with new and now operational.Job completed
MSA-DTWD | WA5613692 | 3 | OTIS ELEVATOR COMPANY PTY LTD | North Block - Level 3 - Lift No 4 - Lift stuck - doors open | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-07-14 15:21 | 2022-07-21 17:00 | 2022-07-14 15:30 | 2022-07-21 17:00 | 2022-07-14 16:30 |  |  | After hours 14 Jul 2022 Caller: wasc@programmed.com.au North Block Lift No 4 - Lift stuck level 3, doors open. Cause:Found lift isolated on m/room Maintenance pendant inspection mode & stop button pressed by previous lift company. Turnedback to automatic to see if lift would run but it crash stops 1.5 before floor level. Security said lift hasn't worked for a number ofweeks
MSA-DCA | WA5628664 | 1 | Critical Fire Protection & Training | zone 33 fire alarm activating | Fire Protection Services | Fire Protection - Monitor System | 106.93 | Pass | Pass | 0 | 0 | 1 | 2022-07-15 15:02 | 2022-07-18 17:00 | 2022-07-15 15:30 | 2022-07-18 17:00 | 2022-07-15 16:30 |  |  | During attendance, isolation completed as site is required to have the hot water unit looked at.CF to return once we are advised of the HWU repairs.26/7 - Hi EmmaIt was found that the HWU in the cleaners room is in perfect working condition and would not set off the detector.It looks like the cleaner may have filled a bucket full of hot water and left the room to the door closed causing the steam and setting off the detector.Could you please make notes for your tech to please deisolate zone 33, when they are onsite carrying out the August RMThank youDenise McCartney Building & Asset Maintenance Officer
MSA-DTWD | WA5656174 | 3 | ACTION GLASS & ALUMINIUM | Ground level - Block H17 - Louvers on courtyard door are damaged & needs to be replaced (see notes | Glazing | Specialist Glass | 387.6 | Pass | Pass | -1 | -1 | 1 | 2022-07-18 11:55 | 2022-07-25 17:00 | 2022-07-20 14:15 | 2022-07-25 17:00 | 2022-07-20 15:15 |  |  | ATTENDED SITEREMOVED DAMAGED LOUVRES FROM BOTTOM DOOR PANELREPLACED WITH GLASS PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-710 X 10358 L/M OF RUBBER USED
MSA-DTWD | WA5660325 | 2 | AWB Co. | water leak from roof | Building | Ceiling | 244.15 | Pass | Pass | 0 | 0 | 1 | 2022-07-19 08:33 | 2022-07-22 17:00 | 2022-07-19 13:15 | 2022-07-22 17:00 | 2022-07-19 14:15 |  |  | Found minor issues with silicone around extraction unit.found overlap of skylight sheets not sealed.carried out repairs
MSA-DTWD | WA5661051 | 2 | Water2water Pty Ltd | BG25a -Cold water tap needs a filter added | Plumbing & Drainage | Water | 461.37 | Pass | Pass | 0 | 0 | 1 | 2022-07-19 15:20 | 2022-07-22 17:00 | 2022-07-20 09:45 | 2022-07-22 17:00 | 2022-07-20 10:45 |  |  | Tech installed new Maxiflow filtration system as new capex asset. All okay on departure,
MSA-MRWA | WA5672921 | 2 | AWB Co. | Bitumen Spray Shed external - Broken pump switch housing - see notes below | Electrical | General Electrical | 341.6 | Pass | Pass | 0 | 0 | 1 | 2022-07-20 10:28 | 2022-07-25 17:00 | 2022-07-22 12:00 | 2022-07-25 17:00 | 2022-07-22 13:00 |  |  | Attended site and signed in. Completed JSA. Located contactor box to oil pump broken. Supply and replaced with new contactor box. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5673388 | 2 | Falcetta Plumbing and Gas | Urinal cistern leaking from delivery pipe | Plumbing & Drainage | Toilets/Cisterns | 178.88 | Pass | Pass | 0 | 0 | 1 | 2022-07-20 14:42 | 2022-07-25 17:00 | 2022-07-22 15:30 | 2022-07-25 17:00 | 2022-07-22 16:30 |  |  | replaced inlet valve and flex hose
MSA-DTWD | WA5673392 | 2 | Falcetta Plumbing and Gas | Broken float valve in male toilet cubical | Plumbing & Drainage | Toilets/Cisterns | 178.88 | Pass | Pass | 0 | 0 | 1 | 2022-07-20 14:44 | 2022-07-25 17:00 | 2022-07-22 16:30 | 2022-07-25 17:00 | 2022-07-22 17:30 |  |  | replaced inlet valve and flex hose
MSA-DTWD | WA5674129 | 2 | AWB Co. | Aberdeen St footpath-External light hanging from eaves | Electrical | Lighting, Internal | 265.29 | Pass | Pass | -1 | -1 | 1 | 2022-07-21 09:14 | 2022-07-26 17:00 | 2022-07-22 09:00 | 2022-07-26 17:00 | 2022-07-22 10:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Located light fitting hanging. Took down and disposed of. Went to wholesaler for parts. Returned to site and put new downlight in. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DFES | WA5674427 | 2 | AWB Co. | Middle Dorm EnSuite - The bottom hinge on the dorm fire door is missing a pin - Door is unstable | Building | Fire Door | 147.99 | Pass | Pass | 0 | 0 | 1 | 2022-07-21 11:49 | 2022-07-26 17:00 | 2022-07-25 09:00 | 2022-07-26 17:00 | 2022-07-25 10:00 |  |  | Purchase new hinge and swap out damaged one
MSA-DTAG | WA5674935 | 1 | OCS SERVICES PTY LTD | Judicial Support Office - Covid Clean - See notes below | Cleaning | Emergency Cleans |  | Pass | Fail | 0 | 0 | 1 | 2022-07-21 16:20 | 2022-07-22 17:00 | 2022-07-22 17:00 | 2022-07-22 17:00 | 2022-07-22 18:00 |  |  | Completed
MSA-DTWD | WA5675338 | 1 | Damian Rak Electrical Pty Ltd | Unit BLD 822 - Level Flat C - Hallway and Exit lights - Faulty lights | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-07-22 09:30 | 2022-07-25 17:00 | 2022-07-22 14:00 | 2022-07-25 17:00 | 2022-07-22 15:00 |  |  | Completed
MSA-DTWD | WA5675729 | 3 | Water2water Pty Ltd | Level 2 - W204 - 2 Student services Kitchen under bench Billy requires filter change | Plumbing & Drainage | Water | 272.82 | Pass | Pass | 0 | 0 | 1 | 2022-07-22 13:13 | 2022-07-29 17:00 | 2022-07-27 09:10 | 2022-07-29 17:00 | 2022-07-27 10:10 |  |  | Filter lock out and inlet solenoid replaced due to poor flow to tap.
MSA-DTAG | WA5676458 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire Panel Fault-showing, Run Fault stop Red f code AFE O (the o is flashing) .M System fault 1 | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-07-25 08:39 | 2022-07-28 17:00 | 2022-07-25 09:20 | 2022-07-28 17:00 | 2022-07-25 10:20 |  |  | COMPLETED 25/7/22Attended on site @ 0920Panel and Code red both showing fault. Diagnosed it was Vesda issue fault. See photos.The location was in the Defendants Courts.Ian (Facilities manager) informed me we don't have access to Defendants Court due to the prisonersheld there and it's taken care of by the District Court.Cleared fault on Panel and Code RedFinished on site 1020
MSA-DFES | WA5676575 | 3 | Australian HVAC Services Pty. Ltd. | Ground gym - A/C remote control not working | Air Conditioning | Room Air Conditioners | 139.94 | Pass | Pass | -1 | -1 | 1 | 2022-07-25 09:27 | 2022-08-01 17:00 | 2022-07-27 08:00 | 2022-08-01 17:00 | 2022-07-27 09:00 |  |  | Carried out investigations on AC3 remote control. Controller is operating correctly
MSA-DFES | WA5676579 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen/ Dining Room - BA Room smells as though there is a blockage in the waste pipes | Plumbing & Drainage | Drainage | 189.09 | Pass | Pass | 0 | 0 | 1 | 2022-07-25 09:32 | 2022-07-28 17:00 | 2022-07-28 07:30 | 2022-07-28 17:00 | 2022-07-28 08:30 |  |  | Arrived on site and singed in went to BA room to investigate smell out of waste pipe filled all 3 sink up and release them all at once could see at floor waste was filling up and sucking the waste dry used moflo down the floor waste and plunged the sink filled up all sinks smell has gone away.
MSA-DTWD | WA5677162 | 2 | LIGHTHOUSE LOCKSMITHS | 3 x Faulty padlocks - see notes below | Security | Locksmith | 460 | Pass | Pass | 0 | 0 | 1 | 2022-07-25 12:59 | 2022-07-28 17:00 | 2022-07-26 09:30 | 2022-07-28 17:00 | 2022-07-26 10:30 |  |  | replaced 3 damaged padlocks keyed to key system for v block
MSA-MRWA | WA5677533 | 2 | SONTEC WA PTY LTD | Main Entrance Gate - intercom not working | Security | Access Control | 310 | Pass | Pass | 0 | 0 | 1 | 2022-07-25 15:21 | 2022-07-28 17:00 | 2022-07-27 15:30 | 2022-07-28 17:00 | 2022-07-27 16:30 |  |  | 27/7/22 - Dylan ParslowReterminated connection at Intercom and tested, all ok
MSA-DTAG | WA5677563 | 1 | Sapio Pty Ltd | Registry - PACOM not working - see notes below | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-07-25 15:58 | 2022-07-26 17:00 | 2022-07-26 10:30 | 2022-07-26 17:00 | 2022-07-26 11:30 |  |  | Checked system status. Found Gallagher server needs rebooting after power outage. Reset both serversand KVM switch. Tested operation. OK
MSA-DTAG | WA5679028 | 3 | AHS Services WA Pty Ltd (Anchor) | Female public toilets - corner of Hay/Irwin street side - Toilet is running constantly | Plumbing & Drainage | Toilets/Cisterns | 760.3625 | Fail | Fail | 0 | 0 | 1 | 2022-07-26 10:08 | 2022-08-02 17:00 | 2022-08-04 13:30 | 2022-08-02 17:00 | 2022-08-04 14:30 |  |  | .
MSA-DCA | WA5679131 | 2 | Techworks Electrical | Level 1 - FOH - Foyer outside SEG adjacent to escalator 1 -Test & repair faulty GPO - See notes | Electrical | General Electrical | 225.77 | Pass | Pass | 0 | 0 | 1 | 2022-07-26 10:55 | 2022-07-29 17:00 | 2022-07-29 04:30 | 2022-07-29 17:00 | 2022-07-29 05:30 |  |  | Replaced faulty gpo
MSA-MRWA | WA5679606 | 2 | LYNX INTEGRATED SYSTEMS | Level 2, Desk 275 - Sensor Light 1.5.42 not working | Electrical | Lighting, Internal | 500 | Pass | Pass | 0 | 0 | 1 | 2022-07-26 15:38 | 2022-07-29 17:00 | 2022-07-29 08:00 | 2022-07-29 17:00 | 2022-07-29 09:00 |  |  | Upon investigation found sensor had failed. This was replaced with new & programmed to suit.
MSA-DFES | WA5680070 | 2 | Australian HVAC Services Pty. Ltd. | Dorm Room 1 - A/C continually breaks down. | Air Conditioning | Room Air Conditioners | 139.94 | Pass | Pass | -1 | -1 | 1 | 2022-07-27 09:32 | 2022-08-01 17:00 | 2022-07-27 11:00 | 2022-08-01 17:00 | 2022-07-27 12:00 |  |  | Carried out investigations on Dorm 1 AC. Found that unit seems to be operating correctly. Poor placement of indoor unit
MSA-DTWD | WA5680249 | 2 | Mizco Pty Ltd | Chiller faulty | Refrigeration | Chiller |  | Pass | Pass | -1 | -1 | 1 | 2022-07-27 10:51 | 2022-08-01 17:00 | 2022-07-27 11:00 | 2022-08-01 17:00 | 2022-07-27 12:00 |  |  | Repairs to chiller
MSA-DTAG | WA5680381 | 1 | AWB Co. | ground registry office-Light is flickering | Electrical | Lighting, Internal | 152.27 | Pass | Pass | 0 | 0 | 1 | 2022-07-27 11:48 | 2022-07-28 17:00 | 2022-07-28 11:00 | 2022-07-28 17:00 | 2022-07-28 12:00 |  |  | Attended site signed in jsa completed.Replaced x2 36w t8 tubes in office. Tested operational. Job completed
MSA-DTAG | WA5680633 | 1 | Water2water Pty Ltd | L10 admin kitchen- Main HWS issue - see notes | Plumbing & Drainage | Water | 173.82 | Pass | Pass | 0 | 0 | 1 | 2022-07-27 13:55 | 2022-07-28 17:00 | 2022-07-27 14:45 | 2022-07-28 17:00 | 2022-07-27 15:45 |  |  | Emptied water from tray where plumbers had drained hot water system. Reset and dried units and turned on. All ok.
MSA-DTWD | WA5680759 | 3 | Falcetta Plumbing and Gas | Investigate water leak (water supply) and mould growth along wall | Plumbing & Drainage | Water |  | Fail | Fail | 1 | 1 | 1 | 2022-07-27 15:48 | 2022-08-03 17:00 | 2022-08-08 16:30 | 2022-08-03 17:00 | 2022-08-08 17:30 |  |  | possibly caused by roof leak, monitor
MSA-DTAG | WA5680772 | 3 | Sapio Pty Ltd | L30 - Pacom Alarm list detailing issues with Door 30-02 - see notes below | Security | Access Control | 139.88 | Pass | Pass | -1 | -1 | 1 | 2022-07-27 15:53 | 2022-08-03 17:00 | 2022-07-28 12:30 | 2022-08-03 17:00 | 2022-07-28 13:30 |  |  | Found door input in armed state, disarmed area, all alarms cleared.
MSA-DTWD | WA5681265 | 1 | Nessco Pressure Systems | Metal Fabrication section - air compressor is faulty - see notes below | Equipment | Compressors, Generators |  | Pass | Pass | 0 | 0 | 1 | 2022-07-28 10:33 | 2022-07-29 17:00 | 2022-07-28 12:00 | 2022-07-29 17:00 | 2022-07-28 13:00 |  |  | job completed - NPS supply and fit replacement drive belts (XPA1320 x2)
MSA-DTWD | WA5681381 | 3 | AWB Co. | Replace light not working | Electrical | Lighting, Internal | 238.48 | Pass | Pass | 0 | 0 | 1 | 2022-07-28 11:35 | 2022-08-04 17:00 | 2022-08-03 13:15 | 2022-08-04 17:00 | 2022-08-03 14:15 |  |  | Attended site and signed in. Completed JSA. Located A228 and found faulty lights. Supply and replaced lights out as requested by the staff in the area. Tested all okay. Signed out. Job complete
MSA-DFES | WA5681689 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 4 bathroom, vanity flick mixer needs to be replaced - please bring new flick mixer | Plumbing & Drainage | Water | 260.27 | Pass | Pass | 0 | 0 | 1 | 2022-07-28 14:06 | 2022-08-04 17:00 | 2022-08-03 14:45 | 2022-08-04 17:00 | 2022-08-03 15:45 |  |  | HAD TO REPLACES A BASIN MIXER IN DORM 4 AND CISTERN STOP
MSA-DTWD | WA5682657 | 2 | High Tech Pest Control | A114-Rat activity and damage in Client Services Offices-see notes | Pest Control | General Pest | 492 | Pass | Pass | 0 | 0 | 1 | 2022-07-29 10:27 | 2022-08-03 17:00 | 2022-08-01 12:20 | 2022-08-03 17:00 | 2022-08-01 13:20 |  |  | Rodent Boxes and Treatment.
MSA-DTWD | WA5683024 | 3 | AWB Co. | Light switch’s faulty | Electrical | General Electrical | 235.82 | Pass | Pass | -1 | -1 | 1 | 2022-07-29 14:55 | 2022-08-05 17:00 | 2022-08-01 14:00 | 2022-08-05 17:00 | 2022-08-01 15:00 |  |  | Attended site signed in jsa completed. Found faulty switch plate as it was cracked and also one switch was stuck on. Replaced with new switch plate surround and two switch mechs. All working good nowJob completed
MSA-DFES | WA5686245 | 2 | Go Doors | Entry switch for door between comcen and corridor not working-see notes | Building | Automatic Doors | 310 | Pass | Pass | 0 | 0 | 1 | 2022-08-01 06:39 | 2022-08-03 17:00 | 2022-08-02 15:30 | 2022-08-03 17:00 | 2022-08-02 16:30 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5686488 | 3 | AWB Co. | Room A9 - Change light from sensor to on off | Electrical | Lighting, Internal | 217.83 | Pass | Pass | -1 | -1 | 1 | 2022-08-01 08:54 | 2022-08-08 17:00 | 2022-08-03 08:00 | 2022-08-08 17:00 | 2022-08-03 09:00 |  |  | Attended site signed in jsa completed. Found sensor annoying staff in T block. bypassed as requested by site onto switch plate next to it.Job completed
MSA-DTWD | WA5686720 | 2 | AWB Co. | Room F60 - Section of classroom lights not working - See notes below | Electrical | Lighting, Internal | 250.33 | Pass | Pass | 0 | 0 | 1 | 2022-08-01 10:26 | 2022-08-04 17:00 | 2022-08-03 11:00 | 2022-08-04 17:00 | 2022-08-03 12:00 |  |  | Attended site signed in jsa completed. half of classroom lights not working. found two timer switches faulty and replaced with two new mechs. problem solved and lights working. Job completed
MSA-DTWD | WA5686847 | 3 | AWB Co. | One of the lights in D101 is not working | Electrical | Lighting, Internal | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-08-01 11:18 | 2022-08-08 17:00 | 2022-08-08 15:30 | 2022-08-08 17:00 | 2022-08-08 16:30 |  |  | Attended site and signed in. Completed JSA. Located faulty lights. Used site supplied lamps to replace lights. tested all okay. Signed out. Job complete
MSA-DTAG | WA5687131 | 1 | Midolo Building Services | Registry (near phone desk) - 2x leaks on inside window near phone desk | Building | Windows | 123.74 | Pass | Pass | 0 | 0 | 1 | 2022-08-01 13:36 | 2022-08-02 17:00 | 2022-08-02 07:30 | 2022-08-02 17:00 | 2022-08-02 08:30 |  |  | no obvious signs of potential leak/leak spots. side ways rain more then likely the cause on temp leak.
MSA-DTWD | WA5687268 | 1 | AWB Co. | Water leak near light fittings & GPO’s need to have fittings & GPO’s isolated | Electrical | General Electrical | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-08-01 14:55 | 2022-08-02 17:00 | 2022-08-02 13:15 | 2022-08-02 17:00 | 2022-08-02 14:15 |  |  | Attended site and signed in. Completed JSA. Located d block classroom. Found water damage at the back of the room. Ceiling panels all fallen down. Isolated and made safe fittings. Stored on site. Checked gpos on floor on the right hand side and no power, checked into the switchboard and found isolated by downers. Water leak still not fixed. Signed out. Job complete
MSA-DTWD | WA5687278 | 2 | Falcetta Plumbing and Gas | Blocked floor drain in wash bay. | Plumbing & Drainage | Drainage |  | Fail | Fail | 1 | 1 | 1 | 2022-08-01 15:04 | 2022-08-04 17:00 | 2022-08-08 15:30 | 2022-08-04 17:00 | 2022-08-08 16:30 |  |  | drainsflush clear and camera line
MSA-DFES | WA5687332 | 3 | Protek 24/7 Building & Maintenance | Ground -carer and Cultural - slow leak from roof - See notes below | Roofing | Metal Roofing | 231.89 | Pass | Pass | -1 | -1 | 1 | 2022-08-01 16:09 | 2022-08-08 17:00 | 2022-08-04 09:00 | 2022-08-08 17:00 | 2022-08-04 10:00 |  |  | sealed Flashings with Silicone
MSA-DTWD | WA5687852 | 2 | AWB Co. | B Block - Ground Floor - Female Toilets - Replace broken Soap Container - See notes below | Equipment | Cleaning Equipment | 137.19 | Pass | Pass | 0 | 0 | 1 | 2022-08-02 07:51 | 2022-08-04 17:00 | 2022-08-04 11:00 | 2022-08-04 17:00 | 2022-08-04 12:00 |  |  | Attended site, signed in checked all soap dispensers in female toilets, block A and B all working correctly. Steve from Programmed we both said the soap bottle maybe not inserted correctly.JSA not required as no works undertaken
MSA-DTWD | WA5688039 | 0 | Protek 24/7 Building & Maintenance | Roof leak center of classroom - contractor currently onsite | Roofing | Metal Roofing | 307.46 | Pass | Pass | 0 | 0 | 1 | 2022-08-02 09:23 | 2022-08-02 11:23 | 2022-08-02 09:30 | 2022-08-02 13:23 | 2022-08-02 10:30 |  |  | Temporary oversealed roof fixings to prevent further leaks and unblocked the downpipe
MSA-DTWD | WA5691803 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire pump alarm – reset and investigate - Power outage overnight | Fire Protection Services | Fire Protection - Monitor System | 247.74 | Pass | Pass | 0 | 0 | 1 | 2022-08-03 08:08 | 2022-08-03 10:08 | 2022-08-03 09:30 | 2022-08-03 12:08 | 2022-08-03 10:30 |  |  | On site arrival the Electric Fire Pump was in fault due to a power fail, causing T Block FIP to go into alarm.After inspection the Electric Fire Pump needed its main isolation switch to be reset once the main power was returned to the system. Once the isolation switch was reset the alarm/fault cleared from T Block FIP.The Electric Fire Pump also requires a new 12V 7AH battery ASAP as it was due to be replaced on 28/7/22 and now especially after a power outage.All systems are now running normal and working to standard.
MSA-DFES | WA5692296 | 1 | SONTEC WA PTY LTD | Reception - Access Door - Swipe Door - not working | Security | Security Management System | 310 | Pass | Pass | 0 | 0 | 1 | 2022-08-03 11:54 | 2022-08-04 17:00 | 2022-08-03 15:20 | 2022-08-04 17:00 | 2022-08-03 16:20 |  |  | 3/8/22 - Dylan Parslow, Joshua ParkFault with access control appears to be a comms issue.Fault is intermittent and requires further time and investigating to find exact cause if it continues.
MSA-DFES | WA5692934 | 2 | Protek 24/7 Building & Maintenance | Stair 2 Ground Inner Door - Door is getting jammed - See notes below | Building | Doors | 229.66 | Pass | Pass | -1 | -1 | 1 | 2022-08-04 08:09 | 2022-08-09 17:00 | 2022-08-04 11:00 | 2022-08-09 17:00 | 2022-08-04 12:00 |  |  | Sand door down, Painted to seal door
MSA-DTAG | WA5692937 | 1 | Midolo Building Services | Custody - Cell One - Leak from ceiling - Causing puddling on the floor of the cell | Building | Ceiling | 214.38 | Pass | Pass | 0 | 0 | 1 | 2022-08-04 08:13 | 2022-08-05 17:00 | 2022-08-05 07:30 | 2022-08-05 17:00 | 2022-08-05 08:30 |  |  | repaired potential leak spots - Flashings
MSA-DTWD | WA5693351 | 2 | AWB Co. | Power keeps tripping out - Wall to the left when walking through door - PowerPoint | Electrical | General Electrical | 160.01 | Pass | Pass | 0 | 0 | 1 | 2022-08-04 11:39 | 2022-08-09 17:00 | 2022-08-09 12:30 | 2022-08-09 17:00 | 2022-08-09 13:30 |  |  | Attended site and signed in. Completed JSA. Located room with the faulty gpos. Found to have a RCD gpo at the door and the button was stuck in and not allowing to be reset. Check circuit and found already protected by RCD. Supply and replaced gpo with new standard double gpo. Tested all okay. Signed out. Job complete
MSA-MRWA | WA5693795 | 3 | AWB Co. | Admin Southern side near Eastern kitchen/cafeteria -DGPO has been pulled away from wall require-note | Electrical | General Electrical | 147.72 | Pass | Pass | 0 | 0 | 1 | 2022-08-04 15:22 | 2022-08-11 17:00 | 2022-08-09 09:45 | 2022-08-11 17:00 | 2022-08-09 10:45 |  |  | Attended site and signed in. Completed JSA. Spoke with staff on site and was a minor issue as site had no power. Got escorted to the outlet in damage. Replaced mounting clip into the wall and resecured gpo. Could not test the gpo as no power to site. Signed out. Job complete
MSA-MRWA | WA5694539 | 0 | AWB Co. | Lost all power to Ground floor only | Electrical | General Electrical | 146.41 | Fail | Pass | 0 | 0 | 1 | 2022-08-05 11:15 | 2022-08-05 13:15 | 2022-08-05 14:00 | 2022-08-05 15:15 | 2022-08-05 15:00 |  |  | Attended site and signed in. Completed JSA. Located transportable office with no power. Went to supply DB and found that the circuit breaker and the main switch was off. No one knows as to why. Switched both back on and tested power to be all okay. Signed out. Job complete
MSA-DTWD | WA5694633 | 2 | BAKE-QUIP PTY LTD | Main Bain Marie has a leak @ the back left hand corner near the leg- See notes below | Equipment | Catering Equipment | 230 | Fail | Fail | 1 | 1 | 1 | 2022-08-05 11:56 | 2022-08-10 17:00 | 2022-08-17 14:45 | 2022-08-10 17:00 | 2022-08-17 15:45 |  | WCAPPR | REFER TO SERVICE REPORT.
MSA-DCA | WA5694891 | 1 | Techworks Plumbing | Geologist Building-Clear toilet blockage.-see notes | Plumbing & Drainage | Toilets/Cisterns | 143.3 | Pass | Pass | 0 | 0 | 1 | 2022-08-05 14:20 | 2022-08-08 17:00 | 2022-08-05 17:00 | 2022-08-08 17:00 | 2022-08-05 18:00 |  |  | Arrived on site and signed in at the security desk. Then went to find the blocked toilet. I couldn't find it so I had security help me locate it. Once we finally located it I used plunger and unblocked it. Tested multiple times with paper and is now working perfectly.Returned to the security desk and signed out
MSA-DCA | WA5697507 | 0 | TK Elevator Australia Pty Ltd | lift in fault | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-08-09 10:02 | 2022-08-09 12:02 | 2022-08-09 10:30 | 2022-08-09 14:02 | 2022-08-09 11:30 |  |  | to be closed out at $0 cost
MSA-DTAG | WA5699582 | 2 | Midolo Building Services | Ground floor - listings - The perspex divider between desks has come loose | Carpentry | Joinery | 208.94 | Pass | Pass | 0 | 0 | 1 | 2022-08-10 10:28 | 2022-08-15 17:00 | 2022-08-15 13:30 | 2022-08-15 17:00 | 2022-08-15 14:30 |  |  | panel secured
MSA-DTWD | WA5699848 | 2 | AWB Co. | Leak in the roof, towards the back of the library. | Roofing | Metal Roofing | 261.46 | Pass | Pass | 0 | 0 | 1 | 2022-08-10 12:49 | 2022-08-15 17:00 | 2022-08-15 11:00 | 2022-08-15 17:00 | 2022-08-15 12:00 |  |  | Investigated leak.found screws in pan of sheet.found barge capping fixing raised and loose.found window frame not sealed to wall.found debris in sump box.carried outrepairs
MSA-DFES | WA5700061 | 1 | Go Doors | Front engine bay 1 - door stuck open | Building | Doors | 310 | Pass | Pass | 0 | 0 | 1 | 2022-08-10 14:40 | 2022-08-11 17:00 | 2022-08-10 15:45 | 2022-08-11 17:00 | 2022-08-10 16:45 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5706756 | 1 | Ballantyne Plumbing Gas & Electrical | Basement - Fault in Grease Trap Alarm – going off continuously. | Waste Management | Waste Removal |  | Pass | Pass | 0 | 0 | 1 | 2022-08-11 13:48 | 2022-08-12 17:00 | 2022-08-12 08:45 | 2022-08-12 17:00 | 2022-08-12 09:45 |  |  | Pulled probes and found grease build up on at high level Cleaned probe and cleared alarm.System left in auto
MSA-DTWD | WA5714700 | 1 | AWB Co. | GPO damaged in Manager Techs office B107 | Electrical | General Electrical | 157.66 | Pass | Pass | 0 | 0 | 1 | 2022-08-12 07:55 | 2022-08-12 17:00 | 2022-08-12 11:45 | 2022-08-12 17:00 | 2022-08-12 12:45 |  |  | Job complete
MSA-DTAG | WA5714882 | 1 | Dormakaba Australia Pty Ltd | Ground - Secure Carpark - Electronic gate stuck open- See notes below | Building | Steel Fencing & Gates | 345 | Pass | Pass | 0 | 0 | 1 | 2022-08-12 09:18 | 2022-08-15 17:00 | 2022-08-12 10:30 | 2022-08-15 17:00 | 2022-08-12 11:30 |  |  | Found a spider in PE beams. Cleaned out PE beam, silicone cable entry. Also carried out a service and adjusted rack.
MSA-DFES | WA5715426 | 2 | AWB Co. | front door-not closing alum/glass door jamming-please attend Monday morning | Building | Doors | 187.19 | Pass | Pass | 0 | 0 | 1 | 2022-08-12 15:13 | 2022-08-17 17:00 | 2022-08-15 14:00 | 2022-08-17 17:00 | 2022-08-15 15:00 |  |  | attended site, tried to adjust door, frame is twistedmeasured and quoted for new door
MSA-DTAG | WA5728230 | 1 | Schindler Lifts Australia | Level 2 (ground floor) – near security entry lift 9 faulty - see notes | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-08-15 15:03 | 2022-08-16 17:00 | 2022-08-15 15:45 | 2022-08-16 17:00 | 2022-08-15 16:45 |  |  | Lift running to floors ok but doors collapsing and not opening.Door operator in Error.No mechanical door issue.No errors in logafter the 2/8/22. possible inaccurate logging.Door operator learn run.Tested and monitored without issue.Returned to service.
MSA-DTWD | WA5735715 | 3 | AWB Co. | Light fitting coming loose disabled toilet - G10 | Electrical | Lighting, Internal | 270.29 | Pass | Pass | -1 | -1 | 1 | 2022-08-16 14:45 | 2022-08-23 17:00 | 2022-08-19 09:00 | 2022-08-23 17:00 | 2022-08-19 10:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located faulty light in toilet, went to wholesaler to pick up materials, returned to site, isolated lighting circuits and removed faulty lighting, replaced with new, re energised circuit and tested light, light working as intended, packed up, completed paperwork, signed out**job completed**
MSA-DTWD | WA5749438 | 2 | AWB Co. | roof leak above the toilet | Roofing | Metal Roofing | 246.41 | Pass | Pass | 0 | 0 | 1 | 2022-08-17 08:54 | 2022-08-22 17:00 | 2022-08-19 12:00 | 2022-08-22 17:00 | 2022-08-19 13:00 |  |  | Found perished silicone around extraction vent carried out repair
MSA-DTAG | WA5753312 | 2 | Sapio Pty Ltd | Level 6 - Open Office – North/East security screen - Issues with Security Monitors - See notes below | Security | Monitoring | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-17 15:43 | 2022-08-22 17:00 | 2022-08-19 11:00 | 2022-08-22 17:00 | 2022-08-19 12:00 |  |  | Attended site. Checked reported issue. Work station seems to be hot, however not fan noise. Client will monitor the unit.
MSA-DTWD | WA5753325 | 2 | Protek 24/7 Building & Maintenance | Outside northwest corner - A Block - No water coming out of downpipe | Roofing | Guttering | 210.91 | Pass | Pass | 0 | 0 | 1 | 2022-08-17 15:52 | 2022-08-22 17:00 | 2022-08-22 12:00 | 2022-08-22 17:00 | 2022-08-22 13:00 |  |  | Unblock Downpipe
MSA-DTWD | WA5761273 | 3 | AWB Co. | D07 - Flickering light main desk area. | Electrical | Lighting, Internal | 209.04 | Pass | Pass | -1 | -1 | 1 | 2022-08-18 07:47 | 2022-08-24 17:00 | 2022-08-19 08:00 | 2022-08-24 17:00 | 2022-08-19 09:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, went to library and located all faulty fittings, removed old tubes and replaced with new , tested all lights and working as intended, packed up, cleaned up, completed paperwork, signed out **job complete*
MSA-DTAG | WA5761416 | 2 | Midolo Building Services | Ground - Public Waiting Room - Seat has snapped off the bench | Furniture | Indoor Furniture | 129.73 | Pass | Pass | -1 | -1 | 1 | 2022-08-18 08:55 | 2022-08-23 17:00 | 2022-08-18 11:00 | 2022-08-23 17:00 | 2022-08-18 12:00 |  |  | SEAT HAS BEEN RE ATTACHED TO BENCH
MSA-DCA | WA5761453 | 2 | FCT SURFACE CLEANING | Gantry hoarding (Murray St side)-External Graffiti on hoarding -see notes | Cleaning | Graffiti |  | Fail | Fail | 0 | 0 | 1 | 2022-08-18 09:21 | 2022-08-23 17:00 | 2022-08-25 11:00 | 2022-08-23 17:00 | 2022-08-25 12:00 |  |  | Job is completed - Graffiti on hoarding gantry was removed
MSA-DTWD | WA5761771 | 2 | AWB Co. | Lights tripping RCD in main switchboard | Electrical | Lighting, Internal | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-08-18 11:44 | 2022-08-23 17:00 | 2022-08-23 12:00 | 2022-08-23 17:00 | 2022-08-23 13:00 |  |  | Daniel Hume (23/08/2022) - Work NoteAttended site and signed in. Completed JSA. Located lights not working. Found to be up high in the classroom. A whole row in the room not working and other lights are working with a couple out. Would advise to repair with upgrade to led hi bays. Site has 6 x hi bays on site to use for the job. However the class will need to be empty to be able to access all the lights to remove and install new hi bays. Braf required. Signed out. Job not completeBRAF declined - close costs to date
MSA-DTWD | WA5780395 | 2 | Protek 24/7 Building & Maintenance | Cover for louver window missing | Building | Windows | 234.04 | Pass | Pass | 0 | 0 | 1 | 2022-08-19 10:06 | 2022-08-24 17:00 | 2022-08-23 12:00 | 2022-08-24 17:00 | 2022-08-23 13:00 |  |  | Located and refitted window cover
MSA-DCA | WA5781070 | 2 | Techworks Electrical | W Block - Exposed wires - Make safe | Electrical | General Electrical | 372.665 | Pass | Pass | 0 | 0 | 1 | 2022-08-19 12:35 | 2022-08-24 17:00 | 2022-08-22 13:30 | 2022-08-24 17:00 | 2022-08-22 14:30 |  |  | Made safe data cables that where hanging down.
MSA-DCA | WA5781082 | 2 | Protek 24/7 Building & Maintenance | Remove fallen roofing wood from the site - photo's to follow in email | Roofing | Guttering | 320.4 | Pass | Pass | 0 | 0 | 1 | 2022-08-19 12:37 | 2022-08-24 17:00 | 2022-08-22 09:00 | 2022-08-24 17:00 | 2022-08-22 10:00 |  | WACCES | Removed 12 mt of Fascia, make electrical safe
MSA-DTWD | WA5781211 | 2 | JEM Carpentry | Sliding door to bedroom 3 faulty | Building | Doors |  | Pass | Pass | -1 | -1 | 1 | 2022-08-19 13:57 | 2022-08-24 17:00 | 2022-08-19 14:00 | 2022-08-24 17:00 | 2022-08-19 15:00 |  |  | lubricated rollers
MSA-DTWD | WA5790251 | 1 | OTIS ELEVATOR COMPANY PTY LTD | T Block - Lift - Left Lift - Left Lift showing fault light | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-08-22 09:31 | 2022-08-23 17:00 | 2022-08-22 13:50 | 2022-08-23 17:00 | 2022-08-22 14:50 |  |  | Repaired under warranty - No charges for attendance
MSA-DTAG | WA5790940 | 1 | Sapio Pty Ltd | Level 4 - Room 41 - Issues with swipe card reader - See notes below | Security | Access Control | 139.88 | Fail | Fail | 0 | 0 | 1 | 2022-08-22 13:37 | 2022-08-23 17:00 | 2022-08-24 08:00 | 2022-08-23 17:00 | 2022-08-24 09:00 |  |  | reset reader and confirmed correct operationknown issue with HID
MSA-DTAG | WA5790941 | 1 | Sapio Pty Ltd | Level 4 - Room 46 - Issues with swipe card reader - See notes below | Security | Access Control | 129.12 | Fail | Fail | 0 | 0 | 1 | 2022-08-22 13:39 | 2022-08-23 17:00 | 2022-08-24 09:00 | 2022-08-23 17:00 | 2022-08-24 10:00 |  |  | Reset door controller and tested
MSA-DTWD | WA5790981 | 2 | Techworks Electrical | Light not working in A214 | Electrical | Lighting, Internal | 151.65 | Pass | Pass | 0 | 0 | 1 | 2022-08-22 13:52 | 2022-08-25 17:00 | 2022-08-23 13:30 | 2022-08-25 17:00 | 2022-08-23 14:30 |  |  | Replaced fluro tubes in room A214
MSA-DCA | WA5791172 | 1 | CONNECT SECURITY SYSTEMS | Ground Level - ECP error – Intruder/Fire Alarm system – System A | Security | Monitoring | 288.42 | Pass | Pass | 0 | 0 | 1 | 2022-08-22 15:02 | 2022-08-23 17:00 | 2022-08-23 07:30 | 2022-08-23 17:00 | 2022-08-23 08:30 |  |  | Rebooted system, ECP error message disappeared. Remote access now possible, tested while on-site
MSA-DFES | WA5791521 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | East side of Appliance Bay - hot water storage unit profusely leaking - See notes be;pw | Plumbing & Drainage | HWS/Units Electric & Gas | 587.4 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 08:09 | 2022-08-30 17:00 | 2022-08-30 07:30 | 2022-08-30 17:00 | 2022-08-30 08:30 |  |  | Arrived on site and singed in went to Bathroom east side of Appliance bay and removed and installed a new stiebel Eltron Hwu 10l unit. Tested everything thing and running fine.
MSA-DTAG | WA5791678 | 1 | OCS SERVICES PTY LTD | Large staff kitchen and workspace closest to it - Covid Clean - See notes below | Cleaning | Emergency Cleans |  | Pass | Fail | 0 | 0 | 1 | 2022-08-23 09:06 | 2022-08-24 17:00 | 2022-08-24 17:00 | 2022-08-24 17:00 | 2022-08-24 18:00 |  |  | Completed
MSA-DTAG | WA5792023 | 2 | Midolo Building Services | Magistrates Corridor - Side skirting coming off wall, currently sticky taped together | Building | Internal Walls | 154.2 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 11:04 | 2022-08-26 17:00 | 2022-08-23 12:30 | 2022-08-26 17:00 | 2022-08-23 13:30 |  |  | SKIRTING REFIXED TO WALL
MSA-DFES | WA5792201 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Dorm 1 - Bed Light not working | Electrical | Lighting, Internal | 196.74 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 12:11 | 2022-08-26 17:00 | 2022-08-25 13:30 | 2022-08-26 17:00 | 2022-08-25 14:30 |  |  | Arrived onsite at 13:30 to investigate light in dorm 1, found that ballast was faulty, replaced ballast and tube, tested ok, advised staff of works and left site at 14:30.
MSA-DTAG | WA5792462 | 3 | Seme Solutions Pty Ltd | CCTV2 (49) Sally port (4) Not working | Security | CCTV Surveillance | 279.76 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 14:33 | 2022-08-30 17:00 | 2022-08-29 14:15 | 2022-08-30 17:00 | 2022-08-29 15:15 |  | WCAPPR | To be removed from system as per Anne-Marie's request on job WA5792446.
MSA-DTWD | WA5793985 | 3 | Equans Mechanical Services Australia | Chiller 2 in fault needs to be reset | Refrigeration | Chiller | 129.51 | Pass | Pass | -1 | -1 | 1 | 2022-08-24 11:34 | 2022-08-31 17:00 | 2022-08-26 07:15 | 2022-08-31 17:00 | 2022-08-26 08:15 |  |  | Attended call, found circuits A and C out on fault. Updated with Airvision. Reset and left operational
MSA-DCA | WA5794278 | 2 | Techworks Plumbing | Level Ground to First-Fire Escape Stairs-Repair leak or blockage in sewer riser/vent pipes located | Plumbing & Drainage | Sewer Drains & Septic Systems | 230.86 | Pass | Pass | 0 | 0 | 1 | 2022-08-24 13:40 | 2022-08-29 17:00 | 2022-08-29 12:30 | 2022-08-29 17:00 | 2022-08-29 13:30 |  |  | Attended sight signed in at security, got a contractors pass, met Neil maintenance manager he showed me the stair well that smell bad/sewer smell. When I arrived in stairwell it smelt off like open sewer. Had a walk around and found at the bottom of the stairs is a waste for the fire system to drain into. The trap in the ground was not watertight and leaking sewer into the stairwell. I’ve filled the trap with water to make it watertight. The stairwell doesn’t smell anymore and I’ve informed Neil the situation he will monitor if the trap dry's out again in the future. Signed out of security and contractors pass. Neil signed signature slip, completed paper
MSA-DTAG | WA5794326 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 2 (Ground) - Ladies staff toilet - Seat lid broken off furtherest toilet from door | Plumbing & Drainage | Toilets/Cisterns | 146.18 | Pass | Pass | -1 | -1 | 1 | 2022-08-24 14:01 | 2022-08-31 17:00 | 2022-08-25 10:30 | 2022-08-31 17:00 | 2022-08-25 11:30 |  |  | .
MSA-DFES | WA5794473 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - All toilets - toilets are blocked - see notes below | Plumbing & Drainage | Toilets/Cisterns | 458.68 | Pass | Pass | 0 | 0 | 1 | 2022-08-24 16:15 | 2022-08-25 17:00 | 2022-08-25 07:30 | 2022-08-25 17:00 | 2022-08-25 08:30 |  |  | Attend site to check out blocked toilet and flush buttons not working, on arrival found last cubicle in female toilets locked off. Opened cubicle and flushed toilet, drain away as it ghouls but found full flush button got stuck in. Removed button assembly and cleaned out. Clipped end of hose to ensure correctly fit. Re fitted buttons and tested. All,working correctly.
MSA-DTWD | WA5795297 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet Blocked | Plumbing & Drainage | Toilets/Cisterns | 179.2 | Pass | Pass | -1 | -1 | 1 | 2022-08-25 10:58 | 2022-08-30 17:00 | 2022-08-26 07:30 | 2022-08-30 17:00 | 2022-08-26 08:30 |  |  | Unblocked male toilets in Qblock Used bottle of moflo
MSA-DTWD | WA5795308 | 1 | SCAVENGER SUPPLIES PTY LTD | B8 - Fault showing on Fire panel - See notes below | Fire Protection Services | Fire Protection - Monitor System | 297.58 | Pass | Pass | 0 | 0 | 1 | 2022-08-25 11:04 | 2022-08-26 17:00 | 2022-08-25 12:45 | 2022-08-26 17:00 | 2022-08-25 13:45 |  |  | Completed 25/8/22On arrival 2 maintenance faults were present on B Block FIP.FLT 1: L1 S12 Z4 - South Chemical Storage Building (K Block).FLT 2: L1 S6 Z3 -West Workshop Propagation (Room B19).Chemical Storage (K Block) fault cleared after replacing the head on Sensor 12 and performing aLoop Test.Loop Test also cleared fault in West Workshop Propagation (Room B19) for Sensor 6, monitor sensorfor fault to reappear as the detector is at a unreachable height and I was unable to replace or inspectthe head of the detector. (Will require a scissor lift for access).If fault in Room B19 does reappear the head and base of sensor 6 will need to be replaced and willrequire a scissor lift for access.
MSA-DTWD | WA5795424 | 3 | Equans Mechanical Services Australia | Room N020 - Chiller 3 in fault | Refrigeration | Chiller | 129.51 | Pass | Pass | -1 | -1 | 1 | 2022-08-25 12:14 | 2022-09-01 17:00 | 2022-08-26 08:15 | 2022-09-01 17:00 | 2022-08-26 09:15 |  |  | Attended all, found chiller had tripped. NOTE CAVITATION IN CHILLED WATER LINE, RAISED JOB TO INVESTIGATE. Reset and left operational.WA5796241 raised
MSA-DTAG | WA5795499 | 2 | EASTERN HILLS ELECTRICAL SERVICE | ground registry-Light flickering in Remote Witness Room and in custody | Electrical | Lighting, Internal | 247.98 | Pass | Pass | -1 | -1 | 1 | 2022-08-25 12:51 | 2022-08-30 17:00 | 2022-08-25 15:00 | 2022-08-30 17:00 | 2022-08-25 16:00 |  |  | Replaced 2x LED batten lights
MSA-DCA | WA5795542 | 0 | Critical Fire Protection & Training | leisure gallery's speaker-multiple faults need to be cleared | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | 0 | 0 | 1 | 2022-08-25 13:18 | 2022-08-25 15:18 | 2022-08-25 14:00 | 2022-08-25 17:18 | 2022-08-25 15:00 |  |  | .
MSA-DFES | WA5795658 | 3 | AWB Co. | Roof inspection for potential leaks | Roofing | Metal Roofing | 225.96 | Pass | Pass | 0 | 0 | 1 | 2022-08-25 14:36 | 2022-09-01 17:00 | 2022-08-31 13:15 | 2022-09-01 17:00 | 2022-08-31 14:15 |  |  | roof leak report completed
MSA-DCA | WA5795740 | 1 | Techworks Plumbing | Level 3 - male toilets - broken Urinal | Plumbing & Drainage | Toilets/Cisterns | 201.06 | Pass | Pass | 0 | 0 | 1 | 2022-08-25 15:42 | 2022-08-26 17:00 | 2022-08-26 08:00 | 2022-08-26 17:00 | 2022-08-26 09:00 |  |  | Went up to level 3 for blocked urinal, unscrewed waste and plunged.Blockage was cleared, poured a couple buckets down to make sure
MSA-DTWD | WA5795950 | 2 | Techworks Electrical | switch tripping when numerous machines are turned on | Electrical | Lighting, Internal | 230.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-26 07:51 | 2022-08-30 17:00 | 2022-08-30 12:00 | 2022-08-30 17:00 | 2022-08-30 13:00 |  |  | Investigated machines that were causing trip Tested and all working no fault found
MSA-DTWD | WA5795953 | 2 | Techworks Electrical | Block Room C106 store room light not working | Electrical | Lighting, Internal | 246.62 | Pass | Pass | 0 | 0 | 1 | 2022-08-26 07:54 | 2022-08-30 17:00 | 2022-08-30 09:30 | 2022-08-30 17:00 | 2022-08-30 10:30 |  |  | Replaced fluro tubes in c block
MSA-DTAG | WA5797692 | 2 | PPM Project Painting & Maintenance | Ground (entry) - Hay St main entrance - Graffiti on building - See notes below | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1 | 2022-08-29 09:57 | 2022-09-01 17:00 | 2022-08-29 14:00 | 2022-09-01 17:00 | 2022-08-29 15:00 |  |  | Remove Graffiti off column at main Entry
MSA-DCA | WA5797731 | 0 | Wilson Security | Retrospective WO - NO ATTENDANCE NEEDED - See notes below | Security | Guards |  | Fail | Fail | 1 | 1 | 1 | 2022-08-20 11:00 | 2022-08-20 13:00 | 2022-08-29 10:15 | 2022-08-20 15:00 | 2022-08-29 11:15 | 1 |  | Completed
MSA-DTAG | WA5797865 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 10 (Coroners Court) - Female toilets - 2 x toilet water is filling up high and not going down | Plumbing & Drainage | Toilets/Cisterns | 179.2 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 11:04 | 2022-08-30 17:00 | 2022-08-30 09:00 | 2022-08-30 17:00 | 2022-08-30 10:00 |  |  | Unblocked female toilets and used bottle of no flo
MSA-DTWD | WA5797902 | 2 | Techworks Electrical | Light not working in A230 | Electrical | Lighting, Internal | 246.62 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 11:25 | 2022-09-01 17:00 | 2022-08-30 10:30 | 2022-09-01 17:00 | 2022-08-30 11:30 |  |  | Replaced fluro tubes in a block
MSA-DTWD | WA5798172 | 2 | COMMERCIAL PLUMBING AND GAS | 10G66 (Creche) - Blocked Toilet | Plumbing & Drainage | Toilets/Cisterns | 989.3 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 12:29 | 2022-09-01 17:00 | 2022-08-29 14:00 | 2022-09-01 17:00 | 2022-08-29 15:00 |  |  | drainsflush clear line as far as possible
MSA-DFES | WA5798348 | 1 | Protek 24/7 Building & Maintenance | Stairwell 2 - ground floor - inner door - door handle falling off | Building | Doors | 132.62 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 13:47 | 2022-08-30 17:00 | 2022-08-30 09:30 | 2022-08-30 17:00 | 2022-08-30 10:30 |  |  | Installed new screws to handle
MSA-DFES | WA5798356 | 2 | Protek 24/7 Building & Maintenance | stairwell 5 - ground floor - external door not latching properly | Building | Doors | 128.59 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 13:51 | 2022-09-01 17:00 | 2022-08-30 10:30 | 2022-09-01 17:00 | 2022-08-30 11:30 |  |  | Adjusted closer
MSA-DCA | WA5798578 | 1 | Techworks Plumbing | ground-male toilet 2nd sink-Sink is blocked – have put out of service. - see notes | Plumbing & Drainage | Drainage | 239.02 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 15:21 | 2022-08-30 17:00 | 2022-08-30 10:30 | 2022-08-30 17:00 | 2022-08-30 11:30 |  |  | Put bottle trap back together
MSA-DTWD | WA5799161 | 1 | AWB Co. | Hair dressing foyer - faulty light stitch, pushed in | Electrical | General Electrical | 255.01 | Pass | Pass | 0 | 0 | 1 | 2022-08-30 10:04 | 2022-08-31 17:00 | 2022-08-30 13:30 | 2022-08-31 17:00 | 2022-08-30 14:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located faulty light switch. Isolated circuit. Removed faulty 3 gang switch. Supplied and replaced with new switch plate and mechs. Energised and tested. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5799352 | 2 | SENTINEL LOCK SERVICE PTY LTD | Sticky lock on sliding door | Security | Locksmith | 154.42 | Pass | Pass | 0 | 0 | 1 | 2022-08-30 11:21 | 2022-09-02 17:00 | 2022-09-01 11:25 | 2022-09-02 17:00 | 2022-09-01 12:25 |  |  | EG14 - Lock sticking on sliding door.Lock repaired.
MSA-DTWD | WA5799380 | 2 | SENTINEL LOCK SERVICE PTY LTD | Sticky keypad lock on staff toilet door | Security | Locksmith | 104.42 | Pass | Pass | 0 | 0 | 1 | 2022-08-30 11:34 | 2022-09-02 17:00 | 2022-09-01 11:25 | 2022-09-02 17:00 | 2022-09-01 12:25 |  |  | AG23A - Sticky key pad lock on staff toilet door.Lock repaired.
MSA-DCA | WA5799513 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 2 in fault | Air Conditioning | Building HVAC Maintenance (Major Plant) | 564.4 | Pass | Pass | 0 | 0 | 1 | 2022-08-30 12:28 | 2022-08-31 17:00 | 2022-08-31 07:30 | 2022-08-31 17:00 | 2022-08-31 08:30 |  |  | Airvision attended site and carried out investigation. Chiller 2 found in hp alarm. Reset and tested operation, ok. Attended site. Checked over works and logs. Completed paperwork
MSA-DFES | WA5799785 | 2 | Protek 24/7 Building & Maintenance | 1st floor - Deployment Office - Door handle is coming loose | Building | Doors | 108.01 | Pass | Pass | 0 | 0 | 1 | 2022-08-30 14:19 | 2022-09-02 17:00 | 2022-09-01 09:30 | 2022-09-02 17:00 | 2022-09-01 10:30 |  |  | Removed door handle assembly and cover plate , filed down damaged edge of cover plate to allow striker assembly to function correctly
MSA-DCA | WA5800535 | 0 | Techworks Electrical | faulty power supply on the ground floor | Electrical | General Electrical | 230.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-31 10:43 | 2022-08-31 12:43 | 2022-08-31 11:00 | 2022-08-31 14:43 | 2022-08-31 12:00 |  |  | Tasks completed 1. arrived and site and Bryce showed us what was happening, and said it had happend before but nothing was found to be wrong. 2. The problem was particular lights they are hawing on the track are blowing a diode inside them.3. tested all voltages and HZ and found nothing wrong.Hz 50.05N-L1 240.6N-L2 245.1N-L3 241.24. I suggest maybe a surge diverter or some sort of a ripple filter.
MSA-DTWD | WA5800948 | 2 | AWB Co. | Q007 - Blown Light needs replacement | Electrical | Lighting, Internal | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-08-31 13:36 | 2022-09-05 17:00 | 2022-09-02 13:30 | 2022-09-05 17:00 | 2022-09-02 14:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located room Q007. Set up work area. Isolated circuit. Replaced various tubes that were out. Energised. Tested for correct operation. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DFES | WA5801330 | 1 | Go Doors | Front - Staff Carpark - Staff electric steel gate - keeps breaking down and not opening correctly | Building | Steel Fencing & Gates | 310 | Pass | Pass | 0 | 0 | 1 | 2022-08-31 15:04 | 2022-09-01 17:00 | 2022-08-31 15:30 | 2022-09-01 17:00 | 2022-08-31 16:30 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5801394 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Monitoring |  | Fail | Fail | 0 | 0 | 1 | 2022-08-27 15:45 | 2022-08-29 17:00 | 2022-08-31 16:30 | 2022-08-29 17:00 | 2022-08-31 17:30 | 1 |  | Completed
MSA-DCA | WA5801397 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Monitoring |  | Fail | Fail | 0 | 0 | 1 | 2022-08-28 00:54 | 2022-08-29 17:00 | 2022-08-31 16:30 | 2022-08-29 17:00 | 2022-08-31 17:30 | 1 |  | Completed
MSA-DCA | WA5801398 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Monitoring |  | Fail | Fail | 0 | 0 | 1 | 2022-08-27 11:56 | 2022-08-29 17:00 | 2022-08-31 16:30 | 2022-08-29 17:00 | 2022-08-31 17:30 | 1 |  | Completed
MSA-DTWD | WA5827396 | 2 | SENTINEL LOCK SERVICE PTY LTD | Door lock faulty | Security | Locksmith | 104.42 | Pass | Pass | 0 | 0 | 1 | 2022-09-01 10:08 | 2022-09-06 17:00 | 2022-09-05 09:00 | 2022-09-06 17:00 | 2022-09-05 10:00 |  |  | Rm 3 - Door lock faulty.Site advises its Rm 1 - both door locks checked.
MSA-DTAG | WA5828946 | 1 | Sapio Pty Ltd | Ventia control room - Court 5 duress alarm monthly testing shows open | Security | Security Management System | 160.3 | Pass | Pass | 0 | 0 | 1 | 2022-09-02 09:16 | 2022-09-05 17:00 | 2022-09-05 08:00 | 2022-09-05 17:00 | 2022-09-05 09:00 |  |  | replaced faulty duress button
MSA-DTWD | WA5829172 | 0 | CONNECT SECURITY SYSTEMS | Comms Failure in compound - unable to arm building - message comes up comms error | Security | Monitoring | 247.23 | Fail | Fail | 0 | 0 | 1 | 2022-09-02 10:45 | 2022-09-02 12:45 | 2022-09-02 13:46 | 2022-09-02 14:45 | 2022-09-02 14:46 |  |  | Reset tripped RCD to alarm system in Hort Shed. Configured AoIP Device to have battery backup as per standard requirement
MSA-DCA | WA5829616 | 1 | Techworks Electrical | Dressing Room 4 - Light switch no longer functional - see notes below | Electrical | Lighting, Internal | 240.55 | Pass | Pass | 0 | 0 | 1 | 2022-09-02 14:38 | 2022-09-05 17:00 | 2022-09-05 09:30 | 2022-09-05 17:00 | 2022-09-05 10:30 |  |  | Replaced light switch in dressing room 4
MSA-DCA | WA5829620 | 1 | Techworks Electrical | Dressing Room 8 - Light switch no longer functional - see notes below | Electrical | Lighting, Internal | 258.3 | Pass | Pass | 0 | 0 | 1 | 2022-09-02 14:39 | 2022-09-05 17:00 | 2022-09-05 10:30 | 2022-09-05 17:00 | 2022-09-05 11:30 |  |  | Replaced light switch in dressing room 8
MSA-DTWD | WA5831829 | 2 | AWB Co. | Cafeteria - 3 roof leaks | Roofing | Metal Roofing | 225.96 | Pass | Pass | 0 | 0 | 1 | 2022-09-05 08:56 | 2022-09-08 17:00 | 2022-09-07 09:30 | 2022-09-08 17:00 | 2022-09-07 10:30 |  |  | Cleaned out gutters and unblocked sumps. Job complete
MSA-DTWD | WA5831945 | 1 | SENTINEL LOCK SERVICE PTY LTD | Loose central barrel – keys getting stuck | Security | Locksmith | 189.42 | Pass | Pass | 0 | 0 | 1 | 2022-09-05 09:44 | 2022-09-06 17:00 | 2022-09-05 12:00 | 2022-09-06 17:00 | 2022-09-05 13:00 |  |  | Loose barrel - 10F94 - key getting stuck.Lock repaired.
MSA-MRWA | WA5832561 | 2 | GPS Plumbing & Gas Services PtyLtd | Wall tap beside urinal leaking | Plumbing & Drainage | Toilets/Cisterns | 110.64 | Pass | Pass | 0 | 0 | 1 | 2022-09-05 13:56 | 2022-09-08 17:00 | 2022-09-06 11:00 | 2022-09-08 17:00 | 2022-09-06 12:00 |  |  | Isolated water, advised site manager, replaced tap washer and reajusted tap to be facing downwards, water then turned back on after repair was done
MSA-DFES | WA5833132 | 0 | Go Doors | staff entry car park entry gate - will open a little then stops. | Building | Automatic Doors | 389.56 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 08:09 | 2022-09-06 10:09 | 2022-09-06 08:45 | 2022-09-06 12:09 | 2022-09-06 09:45 |  |  | Completed works. Please see attachments.
MSA-DTAG | WA5833236 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Female Toilet - Water continually running in ladies public toilet | Plumbing & Drainage | Water | 548.225 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 08:40 | 2022-09-07 17:00 | 2022-09-06 12:30 | 2022-09-07 17:00 | 2022-09-06 13:30 |  |  | Adjusted inlet valve to stop overflowing
MSA-DTWD | WA5833582 | 1 | AWB Co. | outside managers office - fluro light not working | Electrical | Lighting, External | 280.46 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 10:31 | 2022-09-07 17:00 | 2022-09-06 14:00 | 2022-09-07 17:00 | 2022-09-06 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to staff to see which light had been causing issues. Went to store room and collected 2x tubes and 2x starters. Got ladder from car and set up. Replaced tubes and starters. Light fitting is now working as intended. Took before and after pictures. Completed paperwork. Signed out. Job complete
MSA-DTAG | WA5834223 | 0 | Sapio Pty Ltd | Detention - Legal assistance wing door 6 - See notes below | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 14:23 | 2022-09-06 16:23 | 2022-09-06 15:00 | 2022-09-06 18:23 | 2022-09-06 16:00 |  | WACCES | Created new interlock group with all Sally Port Doors. Tested interlock, tested OK.
MSA-DTWD | WA5834278 | 3 | Protek 24/7 Building & Maintenance | Block T - Grounds - Trial sample plot - Damaged Fence - repair / replace - See notes below | Building | Steel Fencing & Gates | 200.64 | Pass | Pass | -1 | -1 | 1 | 2022-09-06 14:44 | 2022-09-13 17:00 | 2022-09-08 15:00 | 2022-09-13 17:00 | 2022-09-08 16:00 |  |  | BRAF DECLINED current fencing is not repairable.
MSA-DTWD | WA5834378 | 1 | COMMERCIAL PLUMBING AND GAS | Workshop - Broken tap in washup area | Plumbing & Drainage | Water | 198.88 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 15:53 | 2022-09-07 17:00 | 2022-09-06 18:00 | 2022-09-07 17:00 | 2022-09-06 19:00 |  |  | Replaced broken spout
MSA-DCA | WA5835429 | 2 | Critical Fire Protection & Training | Vault exterior - Fault light on Vault VESDA | Fire Protection Services | Fire Protection - Monitor System | 393.25 | Pass | Pass | 0 | 0 | 1 | 2022-09-07 08:37 | 2022-09-12 17:00 | 2022-09-12 08:00 | 2022-09-12 17:00 | 2022-09-12 09:00 |  |  | Diagnostic checks- no fault signaling, carried out reset via PCprogram - all ok following
MSA-DTWD | WA5836302 | 1 | Lane's Plumbing | Flat A Bathroom - Blocked vanity basins | Plumbing & Drainage | Drainage |  | Pass | Pass | 0 | 0 | 1 | 2022-09-07 11:09 | 2022-09-08 17:00 | 2022-09-07 15:00 | 2022-09-08 17:00 | 2022-09-07 16:00 |  |  | CLEAR BLOCKAGE TO FLAT A BASINS HUGHES HALL
MSA-DTAG | WA5836706 | 3 | Midolo Building Services | L1 links offfice-Reattach the privacy screen in the Links area – As for Lisa | Building | General Building | 156.63 | Pass | Pass | -1 | -1 | 1 | 2022-09-07 13:44 | 2022-09-14 17:00 | 2022-09-09 13:30 | 2022-09-14 17:00 | 2022-09-09 14:30 |  |  | SCREEN RE ATTACHED
MSA-DFES | WA5837753 | 3 | Protek 24/7 Building & Maintenance | Engine Room - Personnel access door - Strip above door is being pulled away from frame by closer | Building | Doors | 147.4 | Pass | Pass | 0 | 0 | 1 | 2022-09-08 08:46 | 2022-09-15 17:00 | 2022-09-13 07:30 | 2022-09-15 17:00 | 2022-09-13 08:30 |  |  | screwed the architrave back to the frame and nailed the door stop back into position
MSA-DTAG | WA5837971 | 1 | AWB Co. | Level 1 - DOC - Faulty lighting | Electrical | Lighting, Internal | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-09-08 09:53 | 2022-09-09 17:00 | 2022-09-08 13:15 | 2022-09-09 17:00 | 2022-09-08 14:15 |  |  | Job complete
MSA-DTWD | WA5838442 | 2 | AWB Co. | Faulty Light fitting - Broken Tombstone | Electrical | Lighting, Internal | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-09-08 13:26 | 2022-09-13 17:00 | 2022-09-13 11:45 | 2022-09-13 17:00 | 2022-09-13 12:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located a couple of reported fittings with faulty tombstones. Isolated circuits and replaced tombstones. Replaced tubes and starters also. Re energised. Working as intended. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5838636 | 1 | Total Security Systems Pty Ltd | east wing registry door-magnetic lock case has fallen apart and loose wires | Security | Locksmith | 240 | Pass | Pass | 0 | 0 | 1 | 2022-09-08 16:21 | 2022-09-09 17:00 | 2022-09-09 14:00 | 2022-09-09 17:00 | 2022-09-09 15:00 |  |  | 09/09/2022 - Comtec - A.Buzzard - Contractor - Travel to site reinstate wiring on mag lock - Tested, all working - Return travel.
MSA-DFES | WA5839733 | 3 | MR POTHOLE | multiple potholes down main driveway | Paving & Roadworks | Asphalt |  | Pass | Pass | 0 | 0 | 1 | 2022-09-09 15:23 | 2022-09-16 17:00 | 2022-09-16 12:45 | 2022-09-16 17:00 | 2022-09-16 13:45 |  |  | Repairs to potholes
MSA-DFES | WA5839842 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Hot water tap in the shower is running cant turn off | Plumbing & Drainage | HWS/Units Electric & Gas | 509.33 | Pass | Pass | 0 | 0 | 1 | 2022-09-09 18:36 | 2022-09-10 18:36 | 2022-09-09 20:00 | 2022-09-10 18:36 | 2022-09-09 21:00 |  |  | I have serviced the shower tap as lack of lubrication is cause the brass to deteriorate after I’ve tested everything is working correctly cleaned up packed up
MSA-DTWD | WA5853481 | 3 | AWB Co. | GPO loose on wall | Electrical | General Electrical | 209.04 | Pass | Pass | -1 | -1 | 1 | 2022-09-12 09:09 | 2022-09-19 17:00 | 2022-09-13 09:30 | 2022-09-19 17:00 | 2022-09-13 10:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located loose gpo. Resecure back to wall. All good now. Took picture. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5853511 | 1 | Mizco Pty Ltd | Chiller room - Fault on AC chiller board | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 1 | 2022-09-12 09:13 | 2022-09-13 17:00 | 2022-09-13 09:30 | 2022-09-13 17:00 | 2022-09-13 10:30 |  |  | After connection was reestablished, dialed in to site. Reset the chiller fault from the NCE graphics.
MSA-DFES | WA5853655 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Bathroom lights and exhaust fans, Toilet lights and exhaust fans, - see notes | Electrical | Lighting, External | 183.9 | Pass | Pass | -1 | -1 | 1 | 2022-09-12 10:02 | 2022-09-19 17:00 | 2022-09-15 11:00 | 2022-09-19 17:00 | 2022-09-15 12:00 |  |  | Continued on site at 11:00 to investigate exhaust fans and lights in dorm rooms staying on for 15 minutes. Found sensors to be set to 15 minutes, readjusted to 5 minutes and tested, notified staff of change. 12 sensors times changed total. Continued on site at 12:00
MSA-DTAG | WA5853828 | 1 | Schindler Lifts Australia | Ground - Lift 9 is showing “out of service” | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-09-12 11:33 | 2022-09-13 17:00 | 2022-09-12 13:15 | 2022-09-13 17:00 | 2022-09-12 14:15 |  |  | Lift parked, full safety’s. T2 errors in log. Software needs upgrading. Tested all ok rts
MSA-DTAG | WA5854196 | 1 | Sapio Pty Ltd | Courtroom 1 - Public court door lock is broken - See notes below | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-09-12 14:19 | 2022-09-13 17:00 | 2022-09-13 07:30 | 2022-09-13 17:00 | 2022-09-13 08:30 |  |  | Mortice misaligned.realigned and tested ok
MSA-DCA | WA5854204 | 1 | OTIS ELEVATOR COMPANY PTY LTD | RETROSPECTIVE WORK ORDER - Lift is stuck on the ground floor with doors open-DO NOT ATTEND | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-06 13:19 | 2022-06-07 17:00 | 2022-06-06 16:10 | 2022-06-07 17:00 | 2022-06-06 17:10 | 1 |  | Completed
MSA-DCA | WA5854248 | 1 | Techworks Electrical | Ground Floor - FOHM Desk - Light Globe above Fire Indicator Panel not working | Electrical | Lighting, Internal | 217.56 | Pass | Pass | 0 | 0 | 1 | 2022-09-12 14:40 | 2022-09-13 17:00 | 2022-09-13 09:30 | 2022-09-13 17:00 | 2022-09-13 10:30 |  |  | Arrived on site and began fault finding light, light is connected to the fire alarm panel door, when the door opens the light comes on, it is not on during normal operation if the door is shut, the door has a toggle switch on it when it opens it engages the light. No action has been taken as this is working as designed.
MSA-DTAG | WA5861475 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 8 - Male - Public Toilet - toilet seat is broken | Plumbing & Drainage | Toilets/Cisterns | 186.7 | Pass | Pass | 0 | 0 | 1 | 2022-09-13 09:41 | 2022-09-16 17:00 | 2022-09-15 09:45 | 2022-09-16 17:00 | 2022-09-15 10:45 |  |  | .
MSA-DFES | WA5862010 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | ground floor, ladies changeroom power point and gym pp no power | Electrical | General Electrical | 211.37 | Pass | Pass | 0 | 0 | 1 | 2022-09-13 13:12 | 2022-09-14 17:00 | 2022-09-13 14:00 | 2022-09-14 17:00 | 2022-09-13 15:00 |  |  | Explained why power was off
MSA-DTWD | WA5862144 | 1 | Precise Air Group | fridge freezing up | Refrigeration | Freezers | 208.34 | Pass | Pass | 0 | 0 | 1 | 2022-09-13 14:05 | 2022-09-14 17:00 | 2022-09-14 08:00 | 2022-09-14 17:00 | 2022-09-14 09:00 |  |  | Attended site and signed in. Access fridge in lunch of level 2 by A225. Found fridge plate and freezer iced up. Tested thermostat switch and found it was faulty causing compressor to run continuously leading to the ice build up. Called supplier for information on spare parts, as fridge is very old the parts are now discontinued and unavailable. Fridge will need to be replaced with new.Have left fridge running in the meantime as it still operates somewhat.
MSA-DTWD | WA5862275 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire hose reel in tiling has no spray attachment | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 247.74 | Pass | Pass | 0 | 0 | 1 | 2022-09-13 15:33 | 2022-09-16 17:00 | 2022-09-14 14:00 | 2022-09-16 17:00 | 2022-09-14 15:00 |  |  | Completed 14/09/2022
MSA-DTWD | WA5866707 | 2 | M Construction (WA) | The glass shelving behind the counter coming away from its fittings. | Building | Internal Walls | 159.23 | Pass | Pass | 0 | 0 | 1 | 2022-09-14 08:53 | 2022-09-19 17:00 | 2022-09-16 07:30 | 2022-09-19 17:00 | 2022-09-16 08:30 |  |  | Attended site and repaired glass shelving.
MSA-DTWD | WA5869487 | 3 | Critical Fire Protection & Training | EWIS panel in fault alarm - North L1 - Visual line fault | Fire Protection Services | Fire Protection - Monitor System | 429.55 | Pass | Pass | 0 | 0 | 1 | 2022-09-14 14:04 | 2022-09-21 17:00 | 2022-09-21 08:00 | 2022-09-21 17:00 | 2022-09-21 09:00 |  |  | .
MSA-DTAG | WA5869681 | 3 | Midolo Building Services | Level 3.6 - Interview room 3.6 - Desk is loose | Furniture | Office Furniture | 129.73 | Pass | Pass | -1 | -1 | 1 | 2022-09-14 15:56 | 2022-09-21 17:00 | 2022-09-15 11:45 | 2022-09-21 17:00 | 2022-09-15 12:45 |  |  | desk repaired & secure
MSA-DCA | WA5879781 | 2 | Techworks Plumbing | Level 3 UAT - Tap spout off | Plumbing & Drainage | Water | 135.14 | Pass | Pass | -1 | -1 | 1 | 2022-09-15 08:59 | 2022-09-20 17:00 | 2022-09-15 14:00 | 2022-09-20 17:00 | 2022-09-15 15:00 |  |  | Reinstalled a spout that had come off the wall.
MSA-DTAG | WA5879897 | 2 | Sapio Pty Ltd | Ground - Court front entry - doors need to be switched - see notes below | Security | Access Control | 139.88 | Pass | Pass | -1 | -1 | 1 | 2022-09-15 10:02 | 2022-09-20 17:00 | 2022-09-15 14:00 | 2022-09-20 17:00 | 2022-09-15 15:00 |  |  | added one off public holiday into gallagher schedule
MSA-DTAG | WA5887824 | 0 | AWB Co. | Ground floor - Information desk - Large light fixture has partially fallen from the ceiling, hanging | Electrical | Lighting, Internal | 220.33 | Fail | Pass | 0 | 0 | 1 | 2022-09-16 10:17 | 2022-09-16 12:17 | 2022-09-16 12:30 | 2022-09-16 14:17 | 2022-09-16 13:30 |  |  | Attended site and signed in. Completed jsa. Liaised with site about works going ahead. Located fallen light. Isolated. Resecured light fitting to wall. Energised. Notified of works completed. **job complete**
MSA-DCA | WA5888175 | 1 | Techworks Plumbing | Francis street - Ground floor - behind reception desk - Disabled toilet - seat broken off | Plumbing & Drainage | Materials | 239.02 | Pass | Pass | 0 | 0 | 1 | 2022-09-16 13:49 | 2022-09-19 17:00 | 2022-09-16 15:00 | 2022-09-19 17:00 | 2022-09-16 16:00 |  |  | Attended site and signed in spoke to Neil about a Broken toilet seat on the ground floor disabled toilets we went and inspected and found the toilet seat had just come loose and fallen off so we put it back on and tightened it to fit properly again once completed we cleaned up and left site completed paperwork
MSA-DTWD | WA5888201 | 3 | AWB Co. | Power outlet and box have come away from the wall | Electrical | General Electrical | 158.91 | Pass | Pass | 0 | 0 | 1 | 2022-09-16 14:02 | 2022-09-23 17:00 | 2022-09-21 10:30 | 2022-09-23 17:00 | 2022-09-21 11:30 |  |  | Job complete
MSA-DTWD | WA5888345 | 1 | COMMERCIAL PLUMBING AND GAS | Blocked floor drain - see notes below | Plumbing & Drainage | Drainage | 563.88 | Pass | Pass | 0 | 0 | 1 | 2022-09-16 16:10 | 2022-09-19 17:00 | 2022-09-19 15:00 | 2022-09-19 17:00 | 2022-09-19 16:00 |  |  | Drainsflush cleaned drains
MSA-DTAG | WA5961491 | 0 | Sapio Pty Ltd | Level 10-control room camera's are frozen- no motion detection . | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-09-19 08:17 | 2022-09-19 10:17 | 2022-09-19 09:00 | 2022-09-19 12:17 | 2022-09-19 10:00 |  |  | Reset display monitor PC. Set up monitor displays, checked, all OK.
MSA-DTWD | WA5961729 | 3 | COMMERCIAL PLUMBING AND GAS | External Nth East stairs-Broken toilet seat L3 men’s | Plumbing & Drainage | Toilets/Cisterns | 241.27 | Pass | Pass | -1 | -1 | 1 | 2022-09-19 09:35 | 2022-09-27 17:00 | 2022-09-21 16:30 | 2022-09-27 17:00 | 2022-09-21 17:30 |  |  | replaced concealed fixing seat
MSA-DTWD | WA5961749 | 1 | AWB Co. | Classroom lights inoperative | Electrical | Lighting, Internal | 247.83 | Pass | Pass | 0 | 0 | 1 | 2022-09-19 09:38 | 2022-09-20 17:00 | 2022-09-19 14:00 | 2022-09-20 17:00 | 2022-09-19 15:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located class D20. Upon Investigation found to be faulty sensor. Spoke to site and advised us to bypass sensor. Bypassed sensor. Tested lights, all operating correctly now. Packed up. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5961907 | 1 | Trane Thermo King Pty Ltd | RETROSPECTIVE WORK ORDER - Board room - Faulty chiller Fan-DO NOT ATTEND | Refrigeration | Chiller |  | Fail | Fail | 2 | 2 | 1 | 2022-09-06 14:45 | 2022-09-07 17:00 | 2022-09-19 11:00 | 2022-09-07 17:00 | 2022-09-19 12:00 | 1 |  | Repairs
MSA-DTWD | WA5970901 | 2 | Damian Rak Electrical Pty Ltd | 2 Emergency Lights faulty | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 1 | 2022-09-20 10:06 | 2022-09-23 17:00 | 2022-09-28 15:00 | 2022-09-23 17:00 | 2022-09-28 16:00 |  |  | Repairs to lights
MSA-DTAG | WA5971028 | 1 | Midolo Building Services | Ground - Registry - Seat in public waiting area is broken | Furniture | Indoor Furniture | 153.94 | Pass | Pass | 0 | 0 | 1 | 2022-09-20 11:08 | 2022-09-21 17:00 | 2022-09-20 12:00 | 2022-09-21 17:00 | 2022-09-20 13:00 |  |  | new chair installed
MSA-DTAG | WA5971468 | 2 | AHS Services WA Pty Ltd (Anchor) | Male public toilet, opposite CJS Office, Hay St end.-toilet is overflowing | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 1 | 2022-09-20 14:22 | 2022-09-23 17:00 | 2022-09-23 07:30 | 2022-09-23 17:00 | 2022-09-23 08:30 |  |  | Used plunger to clear blocked urinal
MSA-DTWD | WA5972743 | 2 | AWB Co. | Light fitting not working | Electrical | Lighting, Internal | 274.08 | Pass | Pass | -1 | -1 | 1 | 2022-09-21 08:22 | 2022-09-27 17:00 | 2022-09-21 11:00 | 2022-09-27 17:00 | 2022-09-21 12:00 |  |  | Attended site and signed in. Completed JSA. Located light fitting not working in office area. Supply and replaced with new led panel. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5972753 | 2 | AWB Co. | LED lights in store and dish washing room not working | Electrical | Lighting, Internal | 217.83 | Pass | Pass | -1 | -1 | 1 | 2022-09-21 08:26 | 2022-09-27 17:00 | 2022-09-21 12:00 | 2022-09-27 17:00 | 2022-09-21 13:00 |  |  | Attended site and signed in. Completed JSA. Located light fittings not working in kitchen area. Isolated power and turned off lights. Reinstated power and tested lights. All okay. No fault on lights found. Signed out. Job complete
MSA-DTWD | WA5973093 | 3 | BAKE-QUIP PTY LTD | Rotel Oven not rotating | Equipment | Catering Equipment | 230 | Pass | Pass | -1 | -1 | 1 | 2022-09-21 10:27 | 2022-09-29 17:00 | 2022-09-23 09:30 | 2022-09-29 17:00 | 2022-09-23 10:30 |  |  | REFER TO SERVICE REPORT - ROTATING WHEN ON SITE.
MSA-DTWD | WA5974154 | 2 | AWB Co. | Male Toilets - Q Block - Lights faulty in toilets | Electrical | Lighting, Internal | 217.83 | Pass | Pass | -1 | -1 | 1 | 2022-09-23 08:28 | 2022-09-29 17:00 | 2022-09-23 13:30 | 2022-09-29 17:00 | 2022-09-23 14:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located Q block male toilets. Found to be switch was faulty. Rectified problem. Energised and tested. Notified relevant personnel of works completed. **job complete**
MSA-DCA | WA5974411 | 3 | Techworks Electrical | Chicho Gelato - Leak remediated. - Reinstallation of lights required - See notes below | Electrical | Lighting, Internal | 392.81 | Fail | Fail | 2 | 2 | 1 | 2022-09-23 11:30 | 2022-10-03 17:00 | 2022-10-20 05:00 | 2022-10-03 17:00 | 2022-10-20 06:00 |  |  | Found rotary switch to be damaged from short circuit. found replacement switch and installed, stove is working as normal.
MSA-DTWD | WA5974481 | 2 | Protek 24/7 Building & Maintenance | Dogs outdoor enclosure - Insecure chain mesh fencing | Building | Steel Fencing & Gates | 122.38 | Pass | Pass | 0 | 0 | 1 | 2022-09-23 12:00 | 2022-09-29 17:00 | 2022-09-29 09:30 | 2022-09-29 17:00 | 2022-09-29 10:30 |  |  | Braf declined No action taken
MSA-DTWD | WA5974667 | 1 | AWB Co. | Wiring cover to the light pole near D Block has been removed and the wires are exposed | Building | General Building | 217.83 | Pass | Pass | -1 | -1 | 1 | 2022-09-23 14:30 | 2022-09-27 17:00 | 2022-09-23 15:30 | 2022-09-27 17:00 | 2022-09-23 16:30 |  |  | Attended site and signed in. Completed JSA . Liaised with fm about works going ahead. Located pole with missing cover. Isolated pole. Resecured cover back to pole. Energised. Packed up. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA5976622 | 2 | M Construction (WA) | Yellagonga - The hand soap dispenser has come away from the wall | Building | Internal Walls | 143.92 | Pass | Pass | 0 | 0 | 1 | 2022-09-27 10:21 | 2022-09-30 17:00 | 2022-09-29 07:30 | 2022-09-30 17:00 | 2022-09-29 08:30 |  |  | Refixed soap dispenser to wall with strong fixing
MSA-DTWD | WA5976683 | 2 | LIGHTHOUSE LOCKSMITHS | Reception - Refit digital lock to client service reception door and replace worn keys | Security | Locksmith | 460 | Pass | Pass | 0 | 0 | 1 | 2022-09-27 10:44 | 2022-09-30 17:00 | 2022-09-28 08:25 | 2022-09-30 17:00 | 2022-09-28 09:25 |  |  | replaced and refit damaged digital lock on f block door
MSA-DTWD | WA5976778 | 2 | M Construction (WA) | E40 signage has fallen off the door | Signage | General Signage | 149.42 | Pass | Pass | 0 | 0 | 1 | 2022-09-27 11:25 | 2022-09-30 17:00 | 2022-09-29 09:30 | 2022-09-30 17:00 | 2022-09-29 10:30 |  |  | Re - fill signage to door using adhesive
MSA-DTWD | WA5976794 | 2 | Techworks Electrical | 1st Floor Passageway - three lights not working | Electrical | Lighting, Internal | 376.16 | Pass | Pass | 0 | 0 | 1 | 2022-09-27 11:34 | 2022-09-30 17:00 | 2022-09-28 12:30 | 2022-09-30 17:00 | 2022-09-28 13:30 |  |  | Replaced light tubes and globes on first floor
MSA-DFES | WA5977044 | 3 | GRAFFITI FORCE PTY LTD | Ground floor car park - Graffiti on door of stair 4 and 2x graffiti on wall Linkage Ave. | Cleaning | Graffiti | 222 | Pass | Pass | -1 | -1 | 1 | 2022-09-27 13:16 | 2022-10-04 17:00 | 2022-09-30 10:50 | 2022-10-04 17:00 | 2022-09-30 11:50 |  |  | REMOVAL OF GRAFFITI FROM EXTERNAL WALLS ON LINKAGE AVE
MSA-DTWD | WA5978676 | 1 | OTIS ELEVATOR COMPANY PTY LTD | b block lift not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-09-28 12:17 | 2022-09-29 17:00 | 2022-09-28 14:15 | 2022-09-29 17:00 | 2022-09-28 15:15 |  |  | Repaired under warranty - No charge for attendance
MSA-DCA | WA5978685 | 1 | SCAVENGER SUPPLIES PTY LTD | old jail/goal ground admin office-smoke detector D40 zone 42 faulty | Fire Protection Services | Smoke and Heat Detection | 377.58 | Pass | Pass | 0 | 0 | 1 | 2022-09-28 12:32 | 2022-09-29 17:00 | 2022-09-29 12:00 | 2022-09-29 17:00 | 2022-09-29 13:00 |  | WACCES | INITIAL VISIT TO SITE - 28/9/22Subsequent visit not required.
MSA-MRWA | WA5979049 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Administration - Air con is too hot | Air Conditioning | Room Air Conditioners | 146.4 | Pass | Pass | 0 | 0 | 1 | 2022-09-28 15:03 | 2022-09-29 17:00 | 2022-09-29 07:30 | 2022-09-29 17:00 | 2022-09-29 08:30 |  |  | Attended call, found system set on heating for winter. Reset office temps for spring. Left operating.
MSA-DTWD | WA5980453 | 1 | Equans Mechanical Services Australia | air con- not cooling | Air Conditioning | Room Air Conditioners | 129.51 | Pass | Pass | 0 | 0 | 1 | 2022-09-29 14:59 | 2022-09-30 17:00 | 2022-09-30 08:00 | 2022-09-30 17:00 | 2022-09-30 09:00 |  |  | Found the Temperzone air-conditioning system had tripped on frost sensor due to low suction temperature during cold ambient days. Reset and checked cooling and heating cycles all OK.
MSA-DTAG | WA5982567 | 2 | Midolo Building Services | Ground (Level 2) -Public Waiting Area - 2 x broken chairs | Furniture | Office Furniture | 156.63 | Pass | Pass | 0 | 0 | 1 | 2022-09-30 12:26 | 2022-10-05 17:00 | 2022-10-04 08:00 | 2022-10-05 17:00 | 2022-10-04 09:00 |  |  | CHAIRS REPAIRED
MSA-DTWD | WA5982640 | 2 | OTIS ELEVATOR COMPANY PTY LTD | lift is not operating, lights are on, button lights up when you press it but nothing is working. | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-09-30 13:03 | 2022-10-05 17:00 | 2022-09-30 15:00 | 2022-10-05 17:00 | 2022-09-30 16:00 |  |  | Repaired under warranty - No charges
MSA-DFES | WA5982705 | 2 | SONTEC WA PTY LTD | Level 1 - Alarm system appears not to be operating - see notes below | Security | Security Management System | 310 | Pass | Pass | 0 | 0 | 1 | 2022-09-30 13:40 | 2022-10-05 17:00 | 2022-10-04 09:00 | 2022-10-05 17:00 | 2022-10-04 10:00 |  |  | 4/10/22 - Dylan ParslowInvestigated issues with alarm system.Found screamers unplugged.Alarms communicating to monitoring correctly.Reconnected screamers and tested, all working.
MSA-DTWD | WA5987306 | 2 | AWB Co. | Faulty light fitting - Breaker constantly tripping, no lights in store room | Electrical | General Electrical | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-10-03 10:23 | 2022-10-06 17:00 | 2022-10-03 14:00 | 2022-10-06 17:00 | 2022-10-03 15:00 |  |  | attended site signed in jsa completed. found light tripping rcd in c block. removed cover and found terminal block dripping some green liquid. By passed and put new one in and tested. Didnt trip and stayed on.job completed
MSA-DTWD | WA5988340 | 3 | AWB Co. | Room F 7 - Faulty Lights - Possible light sensor | Electrical | Lighting, Internal | 221.98 | Pass | Pass | -1 | -1 | 1 | 2022-10-04 08:34 | 2022-10-11 17:00 | 2022-10-06 14:00 | 2022-10-11 17:00 | 2022-10-06 15:00 |  |  | Attended site signed in jsa completed. Spoke to site about job. Removed sensor as it was not suited to classroom needs and is better on a normal switch. Blanked off and now runs off a switch.Job completed
MSA-DTWD | WA5990108 | 3 | COMMERCIAL PLUMBING AND GAS | Disabled seat come away from base | Plumbing & Drainage | Toilets/Cisterns | 352.27 | Pass | Pass | -1 | -1 | 1 | 2022-10-04 13:16 | 2022-10-11 17:00 | 2022-10-06 15:00 | 2022-10-11 17:00 | 2022-10-06 16:00 |  | WACCES | replaced disabled seat
MSA-DTWD | WA5992722 | 2 | M Construction (WA) | Damaged handle and lock to sliding door to E003. | Building | Doors | 152.72 | Fail | Fail | 0 | 0 | 1 | 2022-10-04 16:26 | 2022-10-07 17:00 | 2022-10-10 14:00 | 2022-10-07 17:00 | 2022-10-10 15:00 |  |  | Installed longer screws to lock and sealed with locktight.
MSA-DCA | WA5993381 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security Call out 23/09/2022 due to smashed glass. -DO NOT ATTEND | Security | Security Management System |  | Fail | Fail | 2 | 2 | 1 | 2022-09-23 04:00 | 2022-09-23 17:00 | 2022-10-05 10:15 | 2022-09-23 17:00 | 2022-10-05 11:15 | 1 |  | Completed
MSA-DTWD | WA5993583 | 3 | AWB Co. | B Block Exterior - Driveway Entrance - Remove Broken Bollard from Driveway entrance | Equipment | Electrical Equipment | 152.66 | Pass | Pass | 0 | 0 | 1 | 2022-10-05 11:11 | 2022-10-12 17:00 | 2022-10-12 11:15 | 2022-10-12 17:00 | 2022-10-12 12:15 |  |  | Hello, Could we please get the cancellation ticket sent through for this as per phone call this morning Kind regards Abbie O'DriscollAWB
MSA-DTWD | WA5994683 | 1 | CONNECT SECURITY SYSTEMS | Level 1 - T Block - Alarm keeps flashing, unable to disarm | Security | Security Management System | 164.81 | Pass | Pass | 0 | 0 | 1 | 2022-10-06 07:50 | 2022-10-06 17:00 | 2022-10-06 09:48 | 2022-10-06 17:00 | 2022-10-06 10:48 |  |  | Reprogrammed users into alarm system as they had dropped off
MSA-DCA | WA5995659 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Water on floor in plant room - Engie to investigate and make safe | Air Conditioning | Building HVAC Maintenance (Major Plant) | 168.92 | Pass | Pass | 0 | 0 | 1 | 2022-10-06 14:30 | 2022-10-06 16:30 | 2022-10-06 15:00 | 2022-10-06 18:30 | 2022-10-06 16:00 |  |  | Attended site. Investigated water leak in level 4 plantroom. Found water leaking from the RO membrane filter housings. Unable to repair it, works to be quoted. Mopped up excess water and have laid rags down to cope with leak until housings can get replaced. Completed paperwork.
MSA-DCA | WA5995666 | 1 | Wilson Security | Retrospective breakdown, no need to send contractor - Security Callout – 02/10/2022 14:32 | Security | Monitoring |  | Fail | Fail | 0 | 0 | 1 | 2022-10-02 14:32 | 2022-10-03 17:00 | 2022-10-06 14:45 | 2022-10-03 17:00 | 2022-10-06 15:45 | 1 |  | Completed
MSA-DFES | WA5995687 | 2 | Complete Pest Management Services | Ground - Tick infestation on site - See notes | Pest Control | General Pest | 376.21 | Pass | Pass | 0 | 0 | 1 | 2022-10-06 14:51 | 2022-10-11 17:00 | 2022-10-10 11:00 | 2022-10-11 17:00 | 2022-10-10 12:00 |  |  | Blankets sprayed all grass, gravel and sand outside the Fire Station for the management of ticks.
MSA-DTWD | WA5997691 | 2 | AWB Co. | Exterior - Rear Carpark entry - panel on lights pole currently open at base near plant room wall | Building | External Walls | 152.66 | Pass | Pass | 0 | 0 | 1 | 2022-10-07 08:56 | 2022-10-12 17:00 | 2022-10-12 10:15 | 2022-10-12 17:00 | 2022-10-12 11:15 |  |  | Job complete
MSA-DTWD | WA5998040 | 2 | PEEL LOCK SERVICES PTY LTD | door handle requires re- installation of locking barrel | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1 | 2022-10-07 11:34 | 2022-10-12 17:00 | 2022-10-12 07:30 | 2022-10-12 17:00 | 2022-10-12 08:30 |  |  | door handle requires re installation of locking barrel!
MSA-DCA | WA6000533 | 0 | Automatic Fire Protection (ARA) | fire panel - alarm going off, cant turn off or isolate | Fire Protection Services | Fire Protection - Monitor System | 258.87 | Pass | Pass | 0 | 0 | 1 | 2022-10-10 08:42 | 2022-10-10 10:42 | 2022-10-10 09:00 | 2022-10-10 12:42 | 2022-10-10 10:00 |  |  | On arrival 4 detectors in zone 9 were in alarm and isolated due to a smoke machine being used in area.Reset detectors, cleared alarms and deisolated zone 9.Noticed that entire building (all zones) were isolated and informed Bryce of this for which he was unaware and will take action.
MSA-DCA | WA6001296 | 1 | Wilson Security | Retrospective WO – no need to send contractor - Panel not working 08/10/22 | Security | Security Management System |  | Pass | Pass | 0 | 0 | 1 | 2022-10-08 23:55 | 2022-10-10 17:00 | 2022-10-10 15:00 | 2022-10-10 17:00 | 2022-10-10 16:00 | 1 |  | Completed
MSA-DTAG | WA6014287 | 3 | AHS Services WA Pty Ltd (Anchor) | L3-female toilet-Court 32 female toilet seat is broken | Plumbing & Drainage | Toilets/Cisterns | 238.84 | Pass | Pass | -1 | -1 | 1 | 2022-10-12 08:02 | 2022-10-19 17:00 | 2022-10-14 09:30 | 2022-10-19 17:00 | 2022-10-14 10:30 |  |  | Picked up and replaced broken toilet seat
MSA-DTWD | WA6014596 | 2 | ACTION GLASS & ALUMINIUM | Re fix loose window in R017. Access will be from the roof of R Block. | Glazing | Window Glass | 140.78 | Pass | Pass | -1 | -1 | 1 | 2022-10-12 10:24 | 2022-10-17 17:00 | 2022-10-13 15:30 | 2022-10-17 17:00 | 2022-10-13 16:30 |  |  | ATTENDED SITESECURED LOOSE WINDOW SHUT3 RIVETS USEDJOB COMPLETE
MSA-DFES | WA6019790 | 1 | Anvil Doors | engine room-rear engine room door not closing | Building | Automatic Doors | 377 | Pass | Pass | 0 | 0 | 1 | 2022-10-13 08:25 | 2022-10-14 17:00 | 2022-10-13 13:30 | 2022-10-14 17:00 | 2022-10-13 14:30 |  |  | Attended Osbourne Park fire station. Technician noted the CB^ boards were completely dead - power supply to boards was fine. Station crew advised that traffic lights were installed yesterday and doors were not working after the installation.
MSA-DTWD | WA6020020 | 1 | Equans Mechanical Services Australia | Fault description Canteen freezer control panel is not working, it is not displaying anything. | Refrigeration | Freezers | 129.51 | Pass | Pass | 0 | 0 | 1 | 2022-10-13 09:51 | 2022-10-14 17:00 | 2022-10-14 12:00 | 2022-10-14 17:00 | 2022-10-14 13:00 |  |  | Arrived on site signed in gathered tools and equipment, checked in with Sue. Went to freezer checked controller operation normal. Controller display had 1 on it nothing else. Checked manual found controller required a reset. While Sue present reset controller from switch off. Once reset functions returned to normal. Monitored temperature all ok, cleaned up and completed paperwork and signed out.
MSA-DCA | WA6020021 | 0 | Schneider Electric Australia Pty Ltd | BMS - Humidity readings are low | Equipment | Building Equipment |  | Pass | Pass | 0 | 0 | 1 | 2022-10-13 09:53 | 2022-10-13 11:53 | 2022-10-13 11:00 | 2022-10-13 13:53 | 2022-10-13 12:00 |  |  | Completed
MSA-DTAG | WA6020061 | 2 | Schindler Lifts Australia | Ground Floor - Lift 3 - Doors are faulty - WLG have locked it off on ground floor | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-10-13 10:25 | 2022-10-18 17:00 | 2022-10-13 12:00 | 2022-10-18 17:00 | 2022-10-13 13:00 |  |  | Technical comment:Lift on JRVP on arrival on lvlG, reported doors not functioning correctly. Found car door roller worn out. Replaced. Tested. All ok. Lift in service.
MSA-DTWD | WA6020282 | 2 | AHS Services WA Pty Ltd (Anchor) | Flick mixer tap continuously dripping | Plumbing & Drainage | Water | 101.35 | Pass | Pass | -1 | -1 | 1 | 2022-10-13 11:55 | 2022-10-18 17:00 | 2022-10-14 15:00 | 2022-10-18 17:00 | 2022-10-14 16:00 |  |  | Checked all taps found to be all good
MSA-DFES | WA6020371 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Replace faulty capacitator. Works in conjunction with previous work order WA5572087 | Electrical | General Electrical | 261.74 | Fail | Fail | 0 | 0 | 1 | 2022-10-13 12:29 | 2022-10-18 17:00 | 2022-10-20 09:30 | 2022-10-18 17:00 | 2022-10-20 10:30 |  |  | 1x capacitor1x 125w globe
MSA-DTWD | WA6020631 | 3 | COMMERCIAL PLUMBING AND GAS | male toilet-End cistern continually running-see notes | Plumbing & Drainage | Toilets/Cisterns | 123.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-13 15:00 | 2022-10-20 17:00 | 2022-10-20 12:00 | 2022-10-20 17:00 | 2022-10-20 13:00 |  |  | repaired and adjusted cistern
MSA-DCA | WA6021638 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Electrical box next to fire panel - making loud noise | Electrical | General Electrical | 134.46 | Pass | Pass | 0 | 0 | 1 | 2022-10-14 09:41 | 2022-10-14 11:41 | 2022-10-14 10:30 | 2022-10-14 13:41 | 2022-10-14 11:30 |  |  | Arrived onsite at 10:30 to investigate buzzing sound located fire panel cupboard. Gained acess to board and found buzzing sound was coming from what seemed to be a PA amplifier. Confirmed issue was not a dangerous electrical hazard and notified staff onsite. Continued onsite at 11:30
MSA-DFES | WA6041991 | 3 | Protek 24/7 Building & Maintenance | CFRS - Ground - Womens shower end - Shower door does not shut correctly, slip hazard | Building | Doors | 219.43 | Pass | Pass | -1 | -1 | 1 | 2022-10-17 08:11 | 2022-10-24 17:00 | 2022-10-18 10:15 | 2022-10-24 17:00 | 2022-10-18 11:15 |  |  | Remove door, clean, re fix bottom hinge
MSA-DCA | WA6044274 | 3 | Earth & Water Pty Ltd | Museum Plaza – AGWA side - Broken Retic - Photo in email | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 1 | 1 | 1 | 2022-10-17 10:23 | 2022-10-24 17:00 | 2022-10-31 09:00 | 2022-10-24 17:00 | 2022-10-31 10:00 |  |  | Attended to retic.Ran zone 4.Exposed leak.Repaired drip line in zone 4 ran and tested as ok.
MSA-DCA | WA6050116 | 2 | ACTION GLASS & ALUMINIUM | One of the two leaf doors was broken on the weekend. | Glazing | Window Glass | 259.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-17 14:57 | 2022-10-20 17:00 | 2022-10-18 15:30 | 2022-10-20 17:00 | 2022-10-18 16:30 |  |  | ATTENDED SITEREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-1215 X 370
MSA-DTWD | WA6050255 | 2 | AWB Co. | Room E010.2 - Flickering fluoro tube | Electrical | Lighting, Internal | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-10-17 15:04 | 2022-10-20 17:00 | 2022-10-18 09:45 | 2022-10-20 17:00 | 2022-10-18 10:45 |  |  | Attended site and signed in, spoke to fm and called security to get keys for site, completed jsa, located 10.2 e block, inspected all lighting and couldn’t find a faulty light, spoke with lecturers in the area and was informed that light had been fixed, completed paperwork,signed out , **job completed**
MSA-DTWD | WA6050727 | 2 | AWB Co. | Block 3 - Ground Floor - Metal Fabrication - Row of lights not working | Electrical | Lighting, Internal | 234.08 | Pass | Pass | 0 | 0 | 1 | 2022-10-17 15:34 | 2022-10-20 17:00 | 2022-10-18 14:00 | 2022-10-20 17:00 | 2022-10-18 15:00 |  |  | Attended site signed in jsa completed. John advised which switch was faulty in room. Replaced switch as hi bay lights were not on.All tested and working nowJob completed.
MSA-DTWD | WA6072626 | 2 | Water2water Pty Ltd | Hallway - Leaking water fountain outside skills 1 | Plumbing & Drainage | Water | 271.64 | Pass | Pass | 0 | 0 | 1 | 2022-10-18 08:50 | 2022-10-21 17:00 | 2022-10-20 12:00 | 2022-10-21 17:00 | 2022-10-20 13:00 |  |  | Replaced dripping bottle filler
MSA-DTWD | WA6075688 | 2 | ACTION GLASS & ALUMINIUM | Glass door requires indicators - See notes below | Glazing | Door Glass | 289.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-18 09:02 | 2022-10-21 17:00 | 2022-10-21 07:30 | 2022-10-21 17:00 | 2022-10-21 08:30 |  |  | SUPPLIED AND INSTALLED 6X DOOR DECALS
MSA-DTWD | WA6080791 | 2 | AWB Co. | Light switches faulty and arcing - see notes below | Electrical | General Electrical | 252.09 | Pass | Pass | 0 | 0 | 1 | 2022-10-18 14:06 | 2022-10-21 17:00 | 2022-10-20 11:00 | 2022-10-21 17:00 | 2022-10-20 12:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Isolated power. Supplied and replaced 2x switch mechs in classroom. Energised. Tested for correct operation. Packed and cleaned up site. Notified relevant personnel of works completed. **job complete**
MSA-DTWD | WA6090713 | 2 | Damian Rak Electrical Pty Ltd | Golf Cart shed - Faulty golf cart charger | Electrical | General Electrical |  | Pass | Pass | -1 | -1 | 1 | 2022-10-19 13:23 | 2022-10-24 17:00 | 2022-10-19 14:00 | 2022-10-24 17:00 | 2022-10-19 15:00 |  |  | repairs to charger
MSA-DTAG | WA6090985 | 2 | AHS Services WA Pty Ltd (Anchor) | Court 51 - Male toilet – Jury Room - Tap looose | Plumbing & Drainage | Water | 137.98 | Pass | Pass | -1 | -1 | 1 | 2022-10-19 15:53 | 2022-10-24 17:00 | 2022-10-20 07:30 | 2022-10-24 17:00 | 2022-10-20 08:30 |  |  | Tighten tap in jury room court 51
MSA-DCA | WA6109003 | 2 | ADVANCED LOCK & KEY | Laneway next to Car Park stairs-faulty lock - see notes | Security | Locksmith | 230 | Pass | Pass | -1 | -1 | 1 | 2022-10-20 12:48 | 2022-10-25 17:00 | 2022-10-21 10:10 | 2022-10-25 17:00 | 2022-10-21 11:10 |  |  | Opened door and supplied new was oval cyl with2 key for main electrical isolation room 1x was oval cyl
MSA-DTAG | WA6109221 | 3 | Midolo Building Services | Soap dispenser broken | Building | Materials | 156.63 | Pass | Pass | 0 | 0 | 1 | 2022-10-20 15:09 | 2022-10-27 17:00 | 2022-10-24 09:30 | 2022-10-27 17:00 | 2022-10-24 10:30 |  |  | soap dispensers secured
MSA-DTWD | WA6111570 | 1 | AWB Co. | C17 landscape classroom - No power to GPO in classroom/ workshop - See notes | Electrical | General Electrical | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-10-21 08:47 | 2022-10-24 17:00 | 2022-10-21 14:00 | 2022-10-24 17:00 | 2022-10-21 15:00 |  |  | Attended site signed in jsa completed.Found 8 rcd’s in off position. Almost every rcd was off in that chassis. Advised aircon company had done works in area and removed cover for board and possibly knocked all the rcds off. as they were all off site had assumed they were all on as all look the same. Turned on all rcds and all power back on no tripping.Job completed
MSA-DTWD | WA6112212 | 2 | Damian Rak Electrical Pty Ltd | Bathroom - Exhaust fans faulty | Equipment | Electrical Equipment |  | Fail | Fail | 1 | 1 | 1 | 2022-10-21 14:02 | 2022-10-26 17:00 | 2022-10-31 09:00 | 2022-10-26 17:00 | 2022-10-31 10:00 |  |  | Repairs to exhaust
MSA-DTWD | WA6112907 | 3 | AWB Co. | D113 - Missing fire exit sign | Electrical | Emergency & Exit Lighting | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-10-24 07:54 | 2022-10-28 17:00 | 2022-10-26 08:45 | 2022-10-28 17:00 | 2022-10-26 09:45 |  |  | Attended site and signed in. Completed jsa. Located exit light that needed to be relocated. De energised circuit. Relocated exit light above door as requested. Re energised. Working as intended. Completed paperwork. Signed out.Job complete
MSA-DFES | WA6112921 | 3 | Go Doors | External Side Entry/Exit Gate -Side gate requires re-programming - See notes below | Building | Automatic Doors | 333.56 | Pass | Pass | -1 | -1 | 1 | 2022-10-24 08:02 | 2022-10-31 17:00 | 2022-10-25 08:15 | 2022-10-31 17:00 | 2022-10-25 09:15 |  |  | Please see attachments.
MSA-DTWD | WA6113515 | 1 | AHS Services WA Pty Ltd (Anchor) | Tap has failed and water flowing constantly | Plumbing & Drainage | Water | 109.68 | Pass | Pass | 0 | 0 | 1 | 2022-10-24 12:18 | 2022-10-25 17:00 | 2022-10-25 07:30 | 2022-10-25 17:00 | 2022-10-25 08:30 |  |  | Picked up and changed faulty tap in room A107 next to A105
MSA-DCA | WA6113610 | 1 | Techworks Electrical | Community Arts Network Office - Light Flickering | Electrical | Lighting, Internal | 228.56 | Pass | Pass | 0 | 0 | 1 | 2022-10-24 13:13 | 2022-10-25 17:00 | 2022-10-25 09:00 | 2022-10-25 17:00 | 2022-10-25 10:00 |  |  | Rectified faulty lighting
MSA-DTWD | WA6127911 | 1 | Australian Airconditioning Services Pty Ltd | Exhaust fan not working | Equipment | Electrical Equipment | 177.54 | Pass | Pass | 0 | 0 | 1 | 2022-10-26 10:59 | 2022-10-27 17:00 | 2022-10-26 11:00 | 2022-10-27 17:00 | 2022-10-26 12:00 |  |  | Investigated exhaust fan and found tubing stopping fan blade from rotating. Removed tubing. Tested. Exhaust fan is fully operational.
MSA-DTWD | WA6127922 | 2 | AWB Co. | Hot works area welding bay exhaust fans not turning off by the black on/off switches | Electrical | General Electrical | 228.92 | Pass | Pass | 0 | 0 | 1 | 2022-10-26 11:05 | 2022-10-31 17:00 | 2022-10-28 12:00 | 2022-10-31 17:00 | 2022-10-28 13:00 |  |  | Attended site signed in jsa completed. Site has requested problem has been fixed with fault reset button. Tried to see if anything wrong but fans switching on and off from vsd. Replaced cord for pipe threader while on site. Job completed
MSA-DTWD | WA6128083 | 2 | Techworks Electrical | ceiling light not working | Electrical | Lighting, Internal | 228.17 | Pass | Pass | -1 | -1 | 1 | 2022-10-26 12:13 | 2022-10-31 17:00 | 2022-10-27 10:30 | 2022-10-31 17:00 | 2022-10-27 11:30 |  |  | Trent Broom (27/10/2022) - Work NoteReplaced tubes in P Block Ground floor office Materials used 2x 36w 840 tubes 2x s10 starters
MSA-DCA | WA6128252 | 1 | Critical Fire Protection & Training | Ground EWIS - Amplifier/speaker fault – Leisure Gallery | Fire Protection Services | Fire Protection - Monitor System | 132.255 | Pass | Pass | 0 | 0 | 1 | 2022-10-26 13:54 | 2022-10-27 17:00 | 2022-10-27 08:00 | 2022-10-27 17:00 | 2022-10-27 09:00 |  |  | Start time: 9:45amFinish time: 10:30amInvestigated fault to EWIS and found the fault occurring in Leisure Gallery Zone 4. An EWP Boom will be required to access 3rd speaker in zone positioned directly above valdura (boat).15m fully articulated boom with basket rotation required. Confirmed with site that EWIS will still operate in the event of a fire therefore not affecting insurance/safety.8/11 - BRAF submitted for further investigation.22/11 - BRAF not responded to.
MSA-DTAG | WA6128255 | 2 | Sapio Pty Ltd | Ground - Court of Appeal Registry - Duress alarm 20 located in CoA office not respondin | Security | Monitoring | 145.07 | Pass | Pass | -1 | -1 | 1 | 2022-10-26 13:58 | 2022-10-31 17:00 | 2022-10-27 09:00 | 2022-10-31 17:00 | 2022-10-27 10:00 |  |  | Arrived on site and investigated reported issue. Tested duress button sealing / unseal, tested OK. Tested Inovonicstransmitter battery and found that battery is low. Replaced battery, tested duress back to Control, tested OK.
MSA-DTWD | WA6128787 | 3 | ADVANCED LOCK & KEY | Locks on three doors are difficult to unlock, suspect barrels are worn - see notes below | Security | Locksmith | 325 | Pass | Pass | -1 | -1 | 1 | 2022-10-27 08:02 | 2022-11-03 17:00 | 2022-10-27 10:50 | 2022-11-03 17:00 | 2022-10-27 11:50 |  |  | Attend site to repin locks on 3x doors as per order 3x CYLINDER COMPONENTS MK 1050-1150
MSA-DTAG | WA6129242 | 1 | Sapio Pty Ltd | ground-Control room/Custody-Alarm in open state for Receiver 3-see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-27 12:45 | 2022-10-28 17:00 | 2022-10-27 15:00 | 2022-10-28 17:00 | 2022-10-27 16:00 |  |  | WA - Michael Tomlinson (27/10/2022) - Work NoteAttended site, found receiver 3 Inovonics with last input 12 in alarm state. reset all okay.
MSA-DTWD | WA6129422 | 3 | AWB Co. | Lights not working in B207 | Electrical | Lighting, Internal | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-10-27 14:50 | 2022-11-03 17:00 | 2022-10-31 08:00 | 2022-11-03 17:00 | 2022-10-31 09:00 |  |  | Completed JSA. Spoke to fm. Located room with “faulty lighting”. Turned lights off and on multiple times and nothing was wrong. Called up Steve and explained issue. He said if there’s is nothing wrong close the job off as he doesn’t know anything about it. Took pictures of dimming lights and normal lights working. Took picture. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6130667 | 0 | TK Elevator Australia Pty Ltd | Lift is stuck on basement level | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-10-28 14:09 | 2022-10-28 16:09 | 2022-10-28 14:45 | 2022-10-28 18:09 | 2022-10-28 15:45 |  |  | Lift1 PICA-Elevator > MRL > Gearless :Lift 100mm through bottom floor, no live fault on genuis board, traced travel curcuit. M, S , D relays all ok. Further investigation foundDown relay on VIM board (invertor interface) burnt out. Replaced all 5 relays on board and tightened all terminals into board abd drive. KF KS KD main contactors all ok. Ranlift extensively without fault and returned to service.to be closed out at $0 cost
MSA-DTWD | WA6130710 | 2 | Damian Rak Electrical Pty Ltd | BLD 824 Entry - 600mm fluoro faulty | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-10-28 14:37 | 2022-11-02 17:00 | 2022-10-31 08:00 | 2022-11-02 17:00 | 2022-10-31 09:00 |  |  | Completed
MSA-DCA | WA6132096 | 3 | Techworks Electrical | Extractor Fan not working | Electrical | General Electrical | 135.15 | Pass | Pass | -1 | -1 | 1 | 2022-10-31 11:27 | 2022-11-07 17:00 | 2022-11-01 09:00 | 2022-11-07 17:00 | 2022-11-01 10:00 |  |  | Attended site found exhaust fan in wall working but making a noise Cause is bearing is wearing down Will require replacement Waiting on wholesaler to order fitting Site requires a quote to be sent through before re attending to fix
MSA-DFES | WA6132481 | 2 | Anvil Doors | Daglish 2nd Pump Front Door - Front panel door 3 lower panel is dented | Building | Automatic Doors | 377 | Pass | Pass | 0 | 0 | 1 | 2022-10-31 14:06 | 2022-11-03 17:00 | 2022-10-31 15:00 | 2022-11-03 17:00 | 2022-10-31 16:00 |  |  | Attended Dalglish Fire Station and replaced cracked hinge to sectional door. Technician noted minor impact damaged to sectional door cladding however we are unable to quote for the replacement of the cladding as the manufacture of the sectional door cladding has been discontinued
MSA-DFES | WA6132510 | 3 | Protek 24/7 Building & Maintenance | Outside yard/foam area - Bitumen in yard has cracks resulting in trip hazard. | Paving & Roadworks | Concreting | 122.4 | Pass | Pass | -1 | -1 | 1 | 2022-10-31 14:38 | 2022-11-07 17:00 | 2022-11-03 12:00 | 2022-11-07 17:00 | 2022-11-03 13:00 |  |  | Bitumen is breaking up - photos and measurements taken Braf declined
MSA-DCA | WA6142876 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Female Toilet - Toilet cistern lid has been removed | Plumbing & Drainage | Toilets/Cisterns | 139.43 | Pass | Pass | 0 | 0 | 1 | 2022-11-01 09:36 | 2022-11-04 17:00 | 2022-11-03 08:00 | 2022-11-04 17:00 | 2022-11-03 09:00 |  |  | Replaced put button on 1 floor female toilets middle cubicle, buttons were missing springs,
MSA-DTWD | WA6143431 | 1 | Mizco Pty Ltd | Chiller computer-Fault description Mizco chiller computer not working | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 1 | 2022-11-01 12:24 | 2022-11-02 17:00 | 2022-11-01 12:45 | 2022-11-02 17:00 | 2022-11-01 13:45 |  |  | Billi Quadra H WS failed -completed
MSA-DTWD | WA6143443 | 1 | Lane's Plumbing | Sewer alarm faulty | Plumbing & Drainage | Sewage Treatment Plant |  | Pass | Pass | 0 | 0 | 1 | 2022-11-01 12:37 | 2022-11-02 17:00 | 2022-11-01 13:30 | 2022-11-02 17:00 | 2022-11-01 14:30 |  |  | Reset sewer alarm
MSA-DTAG | WA6143744 | 3 | AHS Services WA Pty Ltd (Anchor) | ground-cleaners room-Leaking tap in cleaners room adjacent to small kitchen in the registry. | Plumbing & Drainage | Water | 143.48 | Fail | Fail | 0 | 0 | 1 | 2022-11-01 14:19 | 2022-11-08 17:00 | 2022-11-09 11:00 | 2022-11-08 17:00 | 2022-11-09 12:00 |  |  | nil
MSA-DCA | WA6144550 | 1 | Automatic Fire Protection (ARA) | fire hydrant is leaking | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | 0 | 0 | 1 | 2022-11-02 07:47 | 2022-11-02 17:00 | 2022-11-02 09:00 | 2022-11-02 17:00 | 2022-11-02 10:00 |  |  | Attended site to a call out of a leaking hydrant. It turned out to be corroded copper pipe work to the interval hose reel that was leaking.Pipe work requires replacing however I believe it would be easier to drill through the wall and bring a new supply through to just below thehose reel. This will eliminate about 6m of copper pipe work.While on site I also discovered that the fire seems to be fed from the same supply as the domestic meaning that the amenities will not havewater for the duration of the job while the fire is turned off.I also recommend a new fixed hose reel as the existing is leaking.The client will need to be advised that there will be noise and dust as part of the works. I may require to isolate a few zones on the fip.Quote to followWorks to be carried out as an LVM
MSA-DTWD | WA6145731 | 1 | Complete Pest Management Services | 1F18 Construction office-Bad smell getting worse | Pest Control | General Pest | 212.41 | Pass | Pass | 0 | 0 | 1 | 2022-11-02 14:27 | 2022-11-03 17:00 | 2022-11-03 09:00 | 2022-11-03 17:00 | 2022-11-03 10:00 |  |  | Bad Smell in Construction OfficeInspected room 1f18 for bad smell.Found dead possum in the wall cavity unable to get to it .Applied surface spray of anotec odour to mask the bad smell.
MSA-DTWD | WA6145814 | 2 | AWB Co. | Room 006 - Fluro light will not start / flickering | Electrical | Lighting, Internal | 209.04 | Pass | Pass | -1 | -1 | 1 | 2022-11-02 15:27 | 2022-11-07 17:00 | 2022-11-03 14:00 | 2022-11-07 17:00 | 2022-11-03 15:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located faulty light. Replaced tubes and starters. Light working. Took pic. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6147810 | 1 | Techworks Plumbing | Ground Level - Geology Building - Male Toilets - Ambulant toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 239.02 | Pass | Pass | 0 | 0 | 1 | 2022-11-03 10:11 | 2022-11-04 17:00 | 2022-11-03 10:30 | 2022-11-04 17:00 | 2022-11-03 11:30 |  |  | Attended site, signed inLocated toiletPlunged blockage TestedCleaned up messTightened toilet seat as it was loosePacked upSigned out, left site
MSA-DTWD | WA6148898 | 2 | Lane's Plumbing | Training room 2-Fault description Leaking Evap | Plumbing & Drainage | Water |  | Pass | Pass | -1 | -1 | 1 | 2022-11-04 10:08 | 2022-11-09 17:00 | 2022-11-04 10:30 | 2022-11-09 17:00 | 2022-11-04 11:30 |  |  | REPAIR LEAKING PIPE TO AIRCON UNIT
MSA-DTAG | WA6149402 | 2 | GPS Plumbing & Gas Services PtyLtd | Ground - Male toilets near custody kitchen - Toilet not filling up with water | Plumbing & Drainage | Toilets/Cisterns | 113.43 | Pass | Pass | 0 | 0 | 1 | 2022-11-04 15:16 | 2022-11-09 17:00 | 2022-11-09 14:43 | 2022-11-09 17:00 | 2022-11-09 15:43 |  |  | Took inlet valve out to clear out the rust stuck in the pipe, flushed multiple times to get it out of the pipe,
MSA-DTWD | WA6152085 | 3 | GRAFFITI FORCE PTY LTD | Graffiti tagging exterior building | Cleaning | Graffiti | 123 | Fail | Fail | 2 | 2 | 1 | 2022-11-07 09:56 | 2022-11-14 17:00 | 2022-11-29 10:50 | 2022-11-14 17:00 | 2022-11-29 11:50 |  |  | REMOVAL OF GRAFFITI FROM EXTERIOR OF BUILDING
MSA-DTWD | WA6154477 | 2 | AHS Services WA Pty Ltd (Anchor) | Creche Bathroom between RM 3 & 4 - sink blocked | Plumbing & Drainage | Drainage | 133.61 | Pass | Pass | 0 | 0 | 1 | 2022-11-07 12:56 | 2022-11-10 17:00 | 2022-11-08 14:00 | 2022-11-10 17:00 | 2022-11-08 15:00 |  |  | Used internal plunger to clear drains
MSA-DCA | WA6154534 | 2 | Techworks Plumbing | Level Ground- Epoch café servery area - Hot/Cold Zip Tap stopped working | Plumbing & Drainage | Water | 230.86 | Pass | Pass | 0 | 0 | 1 | 2022-11-07 13:10 | 2022-11-10 17:00 | 2022-11-08 07:30 | 2022-11-10 17:00 | 2022-11-08 08:30 |  |  | Attended site and signed inLocated toilet, however it had already flushed away on its own.Checked all toilets and flushed continuously
MSA-DCA | WA6154556 | 2 | Techworks Plumbing | Level Ground- Epoch café servery area- Toilets - Toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 230.86 | Pass | Pass | 0 | 0 | 1 | 2022-11-07 13:33 | 2022-11-10 17:00 | 2022-11-08 07:30 | 2022-11-10 17:00 | 2022-11-08 08:30 |  |  | Attempted to plunge toilet in café, however toilet had already unblocked itself before we arrived.
MSA-DTAG | WA6154661 | 3 | Seme Solutions Pty Ltd | Camera Overlooking Custody Sallyport Door - Camera is faulty | Security | CCTV Surveillance | 139.88 | Pass | Pass | -1 | -1 | 1 | 2022-11-07 15:04 | 2022-11-14 17:00 | 2022-11-07 15:30 | 2022-11-14 17:00 | 2022-11-07 16:30 |  |  | ***SEE SIGSLIP FOR ACTUAL TIMES***Camera offline for over a month.Tested camera with CCTV tester - online.Powercycled Axis blade - camera back online on software.
MSA-DFES | WA6155693 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Gym - Western light switch is taped- See notes below | Electrical | General Electrical | 224.78 | Pass | Pass | -1 | -1 | 1 | 2022-11-08 12:32 | 2022-11-15 17:00 | 2022-11-09 08:00 | 2022-11-15 17:00 | 2022-11-09 09:00 |  |  | Matthew Kenney (09/11/2022) - Work NoteArrived on site at 08:00 to investigate light switch in gym taped for unknown reasons. Located 3 gang switch with switch for sensor fallen behind coverplate. Removed motion sensor switch as per site request and replaced with 2 gang cover plate. Notified staff of outcome and signed out at 09:00
MSA-DTWD | WA6155716 | 2 | SENTINEL LOCK SERVICE PTY LTD | 3F1 Test Cell - Faulty key lock in door | Security | Locksmith | 102.32 | Pass | Pass | 0 | 0 | 1 | 2022-11-08 12:49 | 2022-11-11 17:00 | 2022-11-10 10:35 | 2022-11-11 17:00 | 2022-11-10 11:35 |  |  | 3F1 - Test Cell - faulty Lock.Lock repaired.
MSA-DFES | WA6155914 | 1 | Australian HVAC Services Pty. Ltd. | Air con unit in dining area is dripping water | Air Conditioning | Room Air Conditioners | 201.88 | Pass | Pass | 0 | 0 | 1 | 2022-11-08 14:59 | 2022-11-09 17:00 | 2022-11-09 09:00 | 2022-11-09 17:00 | 2022-11-09 10:00 |  |  | Rhys Hall (09/11/2022) - Work NoteArrived on site and signed in.Located unit and began to investigate.Water was dripping from the indoor drain plug.Checked pump and working fine.Cleaned out drain etc. Sealed the plug and ran unit.Wasn't dripping now.Advised that if it continues to happen further investigation will be required, quite hard to access the pump and drain etc from inside the roof as it's a cassette unit with ceiling.
MSA-DCA | WA6155951 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Monitoring |  | Fail | Fail | 4 | 4 | 1 | 2022-10-19 09:00 | 2022-10-20 17:00 | 2022-11-18 15:45 | 2022-10-20 17:00 | 2022-11-18 16:45 | 1 |  | Completed
MSA-DTAG | WA6156875 | 0 | GPS Plumbing & Gas Services PtyLtd | External - Underground carpark - Effluent pump alarm has activated | Plumbing & Drainage | Water | 215.68 | Pass | Pass | 0 | 0 | 1 | 2022-11-09 11:20 | 2022-11-09 13:20 | 2022-11-09 12:14 | 2022-11-09 15:20 | 2022-11-09 13:14 |  |  | Unblocked the float to activate the pumps, electrician need to reset the control box in the main desk area,
MSA-DTWD | WA6157355 | 3 | SCAVENGER SUPPLIES PTY LTD | Doors loose on fire hydrant booster box | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 157.58 | Pass | Pass | -1 | -1 | 1 | 2022-11-09 15:49 | 2022-11-16 17:00 | 2022-11-10 11:20 | 2022-11-16 17:00 | 2022-11-10 12:20 |  |  | Doors loose on fire hydrant booster boxRe-attach catch and reinstall door holdersCompleted 10/11/2022
MSA-DFES | WA6159216 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Lights x2 in middle/central desk area- need replacing | Electrical | Lighting, Internal | 249.66 | Pass | Pass | -1 | -1 | 1 | 2022-11-10 13:14 | 2022-11-15 17:00 | 2022-11-11 09:45 | 2022-11-15 17:00 | 2022-11-11 10:45 |  |  | Arrived onsite at 9:45 to investigate 2x lights out at level 1 central desk area, found 2x fluro fittings out in central desk area and also 1x fluro fitting in level 1 kitchen area out replaced lamps at all 3 fittings (kitchen light requested by site), all 3 fittings now working, advised staff of works and left site at 10:45.
MSA-DTWD | WA6159385 | 3 | Australian Airconditioning Services Pty Ltd | A/C 11 compressor tripping | Air Conditioning | Building HVAC Maintenance (Major Plant) | 261.72 | Pass | Pass | -1 | -1 | 1 | 2022-11-10 15:13 | 2022-11-17 17:00 | 2022-11-10 15:14 | 2022-11-17 17:00 | 2022-11-10 16:14 |  |  | Found compressor tripping on high current. Cause found to be Condenser fan motor not running due to faulty connection on capacitor. Repaired connection and test ran unit. All ok
MSA-DCA | WA6178050 | 1 | ACTION GLASS & ALUMINIUM | Ground - Urban Orchard - PCC Information sign is broken - See Notes | Glazing | Specialist Glass | 184.88 | Pass | Pass | 0 | 0 | 1 | 2022-11-14 09:06 | 2022-11-15 17:00 | 2022-11-14 13:30 | 2022-11-15 17:00 | 2022-11-14 14:30 |  |  | ATTENDED SITE PATCHED TO MAKE SAFE BROKEN DISPLAY PANEL1 SQM OF SAFETY FILM USED1 MAN REQUIRED
MSA-DTWD | WA6178337 | 1 | AWB Co. | Level 2 - IT Office - No power to circuit White 18 - Reset circuit breaker, no change | Electrical | General Electrical | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-11-14 10:30 | 2022-11-15 17:00 | 2022-11-15 12:30 | 2022-11-15 17:00 | 2022-11-15 13:30 |  |  | Attended site and signed in. Completed jsa. Found circuit. Located board where circuit was fed from. Found breaker was tripped. Turned breaker on and didn’t trip. Load tested circuit. Working as intended. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA6178650 | 3 | Securex Security Systems & Services | Room D117 - UPS power board dead and back up batteries also dead for the alarm panels | Electrical | Distribution Board | 370 | Pass | Pass | -1 | -1 | 1 | 2022-11-14 12:44 | 2022-11-21 17:00 | 2022-11-17 12:45 | 2022-11-21 17:00 | 2022-11-17 13:45 |  |  | 17/11/2022, 1245-1345Job actually in arts building with concept.Replaced batteries in 3 units in interior decorating class.3 of 12V 7Ah batteries used.
MSA-DTWD | WA6184361 | 2 | Damian Rak Electrical Pty Ltd | BLD 832 - ground - conference room - faulty fluro | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-11-15 11:48 | 2022-11-18 17:00 | 2022-11-15 12:00 | 2022-11-18 17:00 | 2022-11-15 13:00 |  |  | Repairs to light
MSA-DTAG | WA6184514 | 2 | Water2water Pty Ltd | Level 12 - Kitchen - No hot water coming out of Billi Unit - See Notes | Plumbing & Drainage | HWS/Units Electric & Gas | 323.64 | Pass | Pass | 0 | 0 | 1 | 2022-11-15 12:53 | 2022-11-18 17:00 | 2022-11-16 15:00 | 2022-11-18 17:00 | 2022-11-16 16:00 |  |  | Adjusted Settings performed full service and filter change as was due tested and checked all okay
MSA-DTWD | WA6184623 | 2 | AWB Co. | Block D - Staff Toilets - mechanical Toilet exhaust fan not working | Equipment | Electrical Equipment | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-11-15 14:04 | 2022-11-18 17:00 | 2022-11-18 14:00 | 2022-11-18 17:00 | 2022-11-18 15:00 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, checked timer and working as intended, turned breaker on and tested both fans for duration of day, fan working as intended, spoke with fm and showed him fan working, site happy, completed paperwork,signed out**job complete**
MSA-DFES | WA6191037 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | L1 male toilet - no water is dispersing | Plumbing & Drainage | Toilets/Cisterns | 232.78 | Pass | Pass | 0 | 0 | 1 | 2022-11-16 12:18 | 2022-11-17 17:00 | 2022-11-17 08:15 | 2022-11-17 17:00 | 2022-11-17 09:15 |  |  | Serviced cistern. Is now working as intended.
MSA-DCA | WA6191222 | 1 | Protek 24/7 Building & Maintenance | Muster point area east of SLWA -Unsafe area. Temporary Fencing required | Building | Steel Fencing & Gates | 1332.4 | Pass | Pass | 0 | 0 | 1 | 2022-11-16 14:00 | 2022-11-17 17:00 | 2022-11-17 09:00 | 2022-11-17 17:00 | 2022-11-17 10:00 |  | WACCES | ? Installed 3x Temporary fencing panels onsite to prevent access to walkway? Carried out site measure to confirm materials required? Pull up and dispose of damaged & uneven pavers to storage area? Supply and install new floating pavers as required
MSA-DTWD | WA6191359 | 1 | AWB Co. | Painters house ground floor - repair cable entry J box | Electrical | General Electrical | 215.54 | Pass | Pass | 0 | 0 | 1 | 2022-11-16 15:36 | 2022-11-17 17:00 | 2022-11-17 06:00 | 2022-11-17 17:00 | 2022-11-17 07:00 |  |  | Attended site and signed in. Completed jsa. Located j box hanging off wall. Got screws and saddle and resecure j box to wall. Took picture. Completed paperwork. Signed out.Job complete
MSA-DCA | WA6230265 | 2 | GPS Plumbing & Gas Services PtyLtd | Dressing room toilet - Knocking water pipes - see notes | Plumbing & Drainage | Toilets/Cisterns | 161.43 | Pass | Pass | 0 | 0 | 1 | 2022-11-18 11:39 | 2022-11-23 17:00 | 2022-11-22 08:00 | 2022-11-23 17:00 | 2022-11-22 09:00 |  |  | Replaced inlet valve dressing room level 1
MSA-DFES | WA6231180 | 2 | Protek 24/7 Building & Maintenance | ground-Information Resources - see notes | Building | Doors | 122.4 | Pass | Pass | 0 | 0 | 1 | 2022-11-18 14:31 | 2022-11-23 17:00 | 2022-11-23 13:30 | 2022-11-23 17:00 | 2022-11-23 14:30 |  |  | Removed screw from under the cabinet runner
MSA-DCA | WA6231268 | 0 | Techworks Electrical | Main auditorium - emergency lighting activated fault in electrical fitting. | Electrical | General Electrical | 135.15 | Pass | Pass | 0 | 0 | 1 | 2022-11-18 17:35 | 2022-11-18 19:35 | 2022-11-18 18:00 | 2022-11-18 21:35 | 2022-11-18 19:00 |  |  | His majesty's theatreSite contact- Josh 0403070234Tripped lighting circuit, emergency lights on.Attend site and look at lighting circuit fault. Found 1x Edison screw lampholder to be loose and as the lighting people changed the globe it shorted. Disconnect and remove lamp holder and put cables into Connectors. Need some one to re attend to fix light.they also mentioned there are multiple lights they want looked at.
MSA-DFES | WA6249210 | 2 | Protek 24/7 Building & Maintenance | (Roof void above) Wellness Office - see notes below | Roofing | Metal Roofing | 122.4 | Pass | Pass | 0 | 0 | 1 | 2022-11-21 10:30 | 2022-11-24 17:00 | 2022-11-23 12:30 | 2022-11-24 17:00 | 2022-11-23 13:30 |  |  | HVAC to be organised by Deb
MSA-DFES | WA6249842 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Lecture room 6 - Fluoro globe faulty - see notes | Electrical | Lighting, Internal | 161.7 | Pass | Pass | -1 | -1 | 1 | 2022-11-21 15:36 | 2022-11-28 17:00 | 2022-11-23 11:00 | 2022-11-28 17:00 | 2022-11-23 12:00 |  |  | Arrived on site at 1100 to attend Ground - Lecture room 6 - Fluoro globe faulty. Obtained access and Identified 2 x faultyfluros. Replaced/reenergised, Informed staff of works and continued on site at 1200.
MSA-DCA | WA6253846 | 1 | Protek 24/7 Building & Maintenance | U Block - Ground - East Entry door damaged - see notes | Building | Doors | 159.9 | Pass | Pass | 0 | 0 | 1 | 2022-11-22 12:34 | 2022-11-23 17:00 | 2022-11-23 08:00 | 2022-11-23 17:00 | 2022-11-23 09:00 |  |  | Replaced hinge screws to re align doorReplaced screws in lock and screwed back in place
MSA-DTWD | WA6255050 | 2 | Securex Security Systems & Services | Security panel S Block Low battery alarm | Security | Monitoring | 320 | Pass | Pass | 0 | 0 | 1 | 2022-11-23 07:46 | 2022-11-25 17:00 | 2022-11-25 07:30 | 2022-11-25 17:00 | 2022-11-25 08:30 |  |  | 25/11/2022, 730-830Replaced 2 battery in panel and power supply.
MSA-DCA | WA6255307 | 1 | Earth & Water Pty Ltd | Ground - Retic is leaking | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 1 | 2022-11-23 09:45 | 2022-11-24 17:00 | 2022-11-23 10:30 | 2022-11-24 17:00 | 2022-11-23 11:30 |  |  | Replaced sprinkler heads
MSA-DCA | WA6255898 | 2 | Quality Pest & Weed Solutions PTY LTD | Beehive on the top western corner of M Block requires removal - see note | Pest Control | Specialist Pest |  | Pass | Pass | -1 | -1 | 1 | 2022-11-23 15:08 | 2022-11-28 17:00 | 2022-11-23 15:30 | 2022-11-28 17:00 | 2022-11-23 16:30 |  |  | removal of bee hive
MSA-DTWD | WA6255912 | 2 | AWB Co. | please replace blown fluro in ceiling mounted light within corridor outside S106 (near gents toilets | Electrical | Lighting, Internal | 125.29 | Pass | Pass | 0 | 0 | 1 | 2022-11-23 15:17 | 2022-11-28 17:00 | 2022-11-28 14:00 | 2022-11-28 17:00 | 2022-11-28 15:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Found to be a blown fluro outside gents toilet. When removing cover found to be light was a loose. Secured light to ceiling. Replaced tube and starter. Tested light. All working correctly. **job complete**
MSA-DFES | WA6256766 | 1 | SONTEC WA PTY LTD | Ground - Gate 2 - FOB activation is not working - see notes | Security | Access Control | 310 | Pass | Pass | 0 | 0 | 1 | 2022-11-24 08:50 | 2022-11-25 17:00 | 2022-11-24 13:30 | 2022-11-25 17:00 | 2022-11-24 14:30 |  |  | 24/11/22 - Joshua ParkInvestigated issues with gate 7.Found airkey receiver not working.Rebooted receiver and tested. All working.
MSA-DFES | WA6256986 | 3 | Dom's Total Grounds Maintenance | Ground - Lawn - Damaged sprinkler pop ups | Landscaping & Gardening | Grounds Maintenance | 240 | Pass | Pass | -1 | -1 | 1 | 2022-11-24 10:56 | 2022-12-01 17:00 | 2022-11-26 16:30 | 2022-12-01 17:00 | 2022-11-26 17:30 |  |  | Call Out & Replace 5 x Pop Ups
MSA-DTWD | WA6257937 | 3 | Techworks Electrical | Damaged lighting | Electrical | Lighting, Internal | 237.46 | Fail | Fail | 1 | 1 | 1 | 2022-11-25 09:09 | 2022-12-02 17:00 | 2022-12-07 12:00 | 2022-12-02 17:00 | 2022-12-07 13:00 |  |  | replaced in total 4 x 36w tubes and 4 x s10 starters
MSA-DCA | WA6290614 | 0 | TK Elevator Australia Pty Ltd | Kitchen - lift/dumbwaiter - doors not opening | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1 | 2022-11-28 09:31 | 2022-11-28 11:31 | 2022-11-28 12:45 | 2022-11-28 13:31 | 2022-11-28 13:45 |  |  | Lift 2 Art-Kitchen-Elevator > MR > Geared :Lift ooo on bottom floor, rope slip device tripped. Reset lift, ran lift ot all floors, lift in service.To be closed out at $0 cost
MSA-DTAG | WA6291431 | 1 | Seme Solutions Pty Ltd | Family Violence Support front door has stopped locking electronically - See notes | Security | Keys & Access | 154.88 | Pass | Pass | 0 | 0 | 1 | 2022-11-28 15:18 | 2022-11-29 17:00 | 2022-11-29 09:45 | 2022-11-29 17:00 | 2022-11-29 10:45 |  |  | Attended site checked and found the breakglass of the problem door is damaged and kept door unlock. Replaced the breakglass and tested all ok after replacement. Breakglass X 1.
MSA-DTWD | WA6292843 | 1 | SCAVENGER SUPPLIES PTY LTD | Break glass fire activation panel needs to be fixed and B Block fire panel re-set | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | 0 | 0 | 1 | 2022-11-29 13:46 | 2022-11-30 17:00 | 2022-11-30 09:00 | 2022-11-30 17:00 | 2022-11-30 10:00 |  |  | COMPLETED 30/11/2022NO FURTHER WORK REQUIRED
MSA-DTAG | WA6292990 | 1 | Midolo Building Services | Level 4 - Room 4.9 Adult Court Services - Door closer (see notes) | Building | Doors | 156.63 | Pass | Pass | 0 | 0 | 1 | 2022-11-29 15:34 | 2022-11-30 17:00 | 2022-11-30 07:30 | 2022-11-30 17:00 | 2022-11-30 08:30 |  |  | re attached/secured door closer
MSA-DFES | WA6293755 | 3 | Protek 24/7 Building & Maintenance | Ground-Family room-Middle cupboard door in family room broken off the hinge-see notes | Carpentry | Timber (all types) | 122.4 | Fail | Fail | 0 | 0 | 1 | 2022-11-30 10:33 | 2022-12-07 17:00 | 2022-12-08 13:30 | 2022-12-07 17:00 | 2022-12-08 14:30 |  |  | Straightened bracket to allow proper connection to the quick release clip. Checked all the hinges and realigned all the cupboard doors to allow for smooth operation.
MSA-DTAG | WA6298442 | 2 | Sapio Pty Ltd | Ground floor - Turnstile causing issues (see notes) | Security | Keys & Access | 139.88 | Fail | Fail | 0 | 0 | 1 | 2022-12-01 10:08 | 2022-12-06 17:00 | 2022-12-07 10:30 | 2022-12-06 17:00 | 2022-12-07 11:30 |  |  | Attended site. Reset card reader on Ground Floor. Turnstiles checked, all OK.
MSA-DTWD | WA6298741 | 0 | AWB Co. | Main light fitting blown in A254-see notes | Electrical | Lighting, Internal | 227.79 | Pass | Pass | 0 | 0 | 1 | 2022-12-01 12:44 | 2022-12-01 14:44 | 2022-12-01 14:00 | 2022-12-01 16:44 | 2022-12-01 15:00 |  |  | Attended site signed in jsa completed. Spoke with mark about job. Found all lights out in one row and need them on for 4pm. Replaced all tubes and starters in row with tubes site provided. All tested and operational.Job completed
MSA-DTWD | WA6299809 | 1 | ACTION GLASS & ALUMINIUM | A107-Patch broken window | Building | Windows | 887.18 | Pass | Pass | 0 | 0 | 1 | 2022-12-02 07:09 | 2022-12-02 17:00 | 2022-12-02 10:15 | 2022-12-02 17:00 | 2022-12-02 11:15 |  |  | ATTENDED SITEPATCHED TO SECURE BROKEN WINDOW AS REQUESTED6.38 CLEAR LAMINATED SAFETY GLASS1-1900 X 1220PLUS 2 TUBES OF SILICONE, 4 L/M OF DOUBLE SIDED TAPE AND 2.5 SQM OF SAFETY FILM
MSA-DTWD | WA6300146 | 1 | Damian Rak Electrical Pty Ltd | Exhaust Fan faulty | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-12-02 09:13 | 2022-12-05 17:00 | 2022-12-05 09:00 | 2022-12-05 17:00 | 2022-12-05 10:00 |  |  | Repairs to exhaust fan
MSA-DTWD | WA6300517 | 2 | Techworks Plumbing | Male toilet next to café blocked | Plumbing & Drainage | Toilets/Cisterns | 148.1 | Pass | Pass | -1 | -1 | 1 | 2022-12-02 10:43 | 2022-12-07 17:00 | 2022-12-02 13:30 | 2022-12-07 17:00 | 2022-12-02 14:30 |  |  | Attended site and signed inlocated toiletplunged waste down the line cleared blockage, tested flushcleaned upsigned out, left site
MSA-DTAG | WA6357036 | 1 | Sapio Pty Ltd | Ground exit door to Hay Street - Next to the C security lift is unlocked (See notes) | Security | Keys & Access | 423.57 | Fail | Fail | 0 | 0 | 1 | 2022-12-05 10:46 | 2022-12-06 17:00 | 2022-12-07 12:30 | 2022-12-06 17:00 | 2022-12-07 13:30 |  |  | Replaced faulty strike, checked and all ok.
MSA-MRWA | WA6357191 | 3 | GPS Plumbing & Gas Services PtyLtd | The 3rd last toilet is not working - see notes | Plumbing & Drainage | Toilets/Cisterns | 161.43 | Pass | Pass | 0 | 0 | 1 | 2022-12-05 11:40 | 2022-12-12 17:00 | 2022-12-09 07:55 | 2022-12-12 17:00 | 2022-12-09 08:55 |  |  | Replaced inlet valve in female toilets 3rd last toilet
MSA-DTWD | WA6358218 | 3 | SENTINEL LOCK SERVICE PTY LTD | Front Door - Lock faulty | Security | Keys & Access | 102.32 | Pass | Pass | -1 | -1 | 1 | 2022-12-06 08:27 | 2022-12-13 17:00 | 2022-12-08 09:00 | 2022-12-13 17:00 | 2022-12-08 10:00 |  |  | Front door lock faulty.Lock repaired.
MSA-DTWD | WA6359228 | 2 | AHS Services WA Pty Ltd (Anchor) | B209 - Female toilets - taps hard to turn off | Plumbing & Drainage | Water | 140.77 | Fail | Fail | 0 | 0 | 1 | 2022-12-06 13:22 | 2022-12-09 17:00 | 2022-12-12 14:00 | 2022-12-09 17:00 | 2022-12-12 15:00 |  |  | Checked all male and female toilets -found all working ok
MSA-DTWD | WA6359394 | 2 | Precise Air Group | F007 - Faulty filters in server room air cond unit | Air Conditioning | Room Air Conditioners | 208.34 | Pass | Pass | 0 | 0 | 1 | 2022-12-06 15:29 | 2022-12-09 17:00 | 2022-12-07 15:00 | 2022-12-09 17:00 | 2022-12-07 16:00 |  |  | Travel to site checked full operation,found on daiken control board ,filter timed schedule clean filter maintenance indicator came on ,filter not even dirty but cleaned again and adjusted filter probe in better position,reset control pad and checked full operation all working efficiently.
MSA-DCA | WA6360015 | 0 | TK Elevator Australia Pty Ltd | Level 1-lift is out of order no power | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-12-07 08:18 | 2022-12-07 10:18 | 2022-12-07 10:15 | 2022-12-07 12:18 | 2022-12-07 11:15 |  |  | Lift1 Main Foyer-Elevator > MRL > Gearless :Lift stopped level 1 door closed. Door lock not making.Moved lift into postion, cleaned and adjusted landing door locks. Checked car doors all okay. Tested operation all okay, returned unit to service. Couldn't reproduce fault, leftin serviceto be closed out at $0 cost
MSA-DCA | WA6360368 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security - DO NOT ATTEND | Security | Security Management System |  | Fail | Fail | 2 | 2 | 1 | 2022-11-18 22:32 | 2022-11-21 17:00 | 2022-12-07 11:00 | 2022-11-21 17:00 | 2022-12-07 12:00 | 1 |  | Completed
MSA-DCA | WA6360392 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security-DO NOT ATTEND | Security | Security Management System |  | Fail | Fail | 0 | 0 | 1 | 2022-12-02 12:13 | 2022-12-05 17:00 | 2022-12-07 11:15 | 2022-12-05 17:00 | 2022-12-07 12:15 | 1 |  | Completed
MSA-DTAG | WA6361580 | 2 | AHS Services WA Pty Ltd (Anchor) | Court 37 Female Toilet (toilet behind court)-toilet is not flushing | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | 0 | 0 | 1 | 2022-12-08 10:59 | 2022-12-13 17:00 | 2022-12-12 15:00 | 2022-12-13 17:00 | 2022-12-12 16:00 |  |  | Found flush to be a zern valve-removed , cleaned up then reinstalled and tested muilple times
MSA-DTWD | WA6361766 | 3 | AWB Co. | Various locations - B Block - faulty lighting - see notes below | Electrical | Lighting, Internal | 198.89 | Pass | Pass | 0 | 0 | 1 | 2022-12-08 12:59 | 2022-12-15 17:00 | 2022-12-13 11:00 | 2022-12-15 17:00 | 2022-12-13 12:00 |  |  | Attended site signed in jsa completed. Replaced 8 tubes in block. Tested operational and shown rick.Job completed
MSA-DTWD | WA6361920 | 2 | SENTINEL LOCK SERVICE PTY LTD | M13 Entry - Keypad Lock on External door has an intermittent fault | Security | Locksmith | 102.32 | Pass | Pass | 0 | 0 | 1 | 2022-12-08 16:10 | 2022-12-13 17:00 | 2022-12-13 10:30 | 2022-12-13 17:00 | 2022-12-13 11:30 |  |  | M13 - Digital lock has a fault.Lock repaired.
MSA-DCA | WA6362214 | 1 | Earth & Water Pty Ltd | Ground external-Please check controller and submit findings and watering schedules-see notes | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 1 | 2022-12-09 08:39 | 2022-12-12 17:00 | 2022-12-09 09:00 | 2022-12-12 17:00 | 2022-12-09 10:00 |  |  | Completed
MSA-DCA | WA6364451 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Art gallery 3,4,9 - AC3 - High humidity alarm. | Air Conditioning | Room Air Conditioners | 168.92 | Fail | Fail | 0 | 0 | 1 | 2022-12-12 11:54 | 2022-12-12 13:54 | 2022-12-12 15:30 | 2022-12-12 15:54 | 2022-12-12 16:30 |  |  | Investigated high humidity alarm in galleries 3, 4 and 9. Accessed bms and checked over values and trends. Humidity resolved itself, all 3 galleries sitting at 50%. No alarms throughout plant. Completed paperwork.
MSA-DTAG | WA6364777 | 1 | Sapio Pty Ltd | ground - PTZ - not- recording, data camera fail | Security | Security Management System | 129.12 | Pass | Pass | 0 | 0 | 1 | 2022-12-12 14:53 | 2022-12-13 17:00 | 2022-12-13 12:30 | 2022-12-13 17:00 | 2022-12-13 13:30 |  |  | Reset camera and reprogrammed streaming to Milestone.
MSA-DFES | WA6365568 | 1 | SONTEC WA PTY LTD | Bowen st workshop - Ground - Please see notes. | Security | Security Management System | 310 | Pass | Pass | 0 | 0 | 1 | 2022-12-13 10:46 | 2022-12-14 17:00 | 2022-12-14 15:30 | 2022-12-14 17:00 | 2022-12-14 16:30 |  |  | 14/12/22 - Joshua ParkDemonstrated to staff correct procedure to arm the system.One pin code not working, reset and tested, all ok.
MSA-DFES | WA6365734 | 3 | Australian HVAC Services Pty. Ltd. | Air Con unit on top of shed – casing has blown off and is damaged. | Air Conditioning | Building HVAC Maintenance (Major Plant) | 139.94 | Pass | Pass | 0 | 0 | 1 | 2022-12-13 11:48 | 2022-12-20 17:00 | 2022-12-19 08:00 | 2022-12-20 17:00 | 2022-12-19 09:00 |  |  | Oscar Holil (19/12/2022) - Work NoteArrived on site and spoke to site representative about the issue with the AC unit. Found out that due to high winds, a part of the unit had flown off and has been damaged. Found the part that had flown off and found out it was the condenser coil grille. Set up my ladder and made my way to the condenser unit. Tried to install the grille but found it to be too damaged and would fly off again. Looked up a replacement part from Daikin but found that they are no longer in stock. However, the grille is not essential to the operation of the unit and due to the unit located on the roof, doesn't need protection for the coils. Notified staff of my findings. Disposed of old grille.
MSA-DFES | WA6373558 | 2 | SONTEC WA PTY LTD | ground engine room-Alarm systems on station specifically to check Zone 5 -see notes | Security | Security Management System | 370 | Fail | Fail | 0 | 0 | 1 | 2022-12-14 15:28 | 2022-12-19 17:00 | 2022-12-22 09:20 | 2022-12-19 17:00 | 2022-12-22 10:20 |  |  | 22/12/22 - Dylan ParslowFound zone 5 PIR sensitivity too high.Replaced and tested.All working correctly.
MSA-DTAG | WA6375714 | 0 | Sapio Pty Ltd | L4 - L04-15-hearing room 46 duress in 4.6 | Security | Security Management System | 134.31 | Fail | Fail | 0 | 0 | 1 | 2022-12-15 10:05 | 2022-12-15 12:05 | 2022-12-15 14:00 | 2022-12-15 14:05 | 2022-12-15 15:00 |  |  | Investigated reported issue with Duress button.Replaced battery.Tested ok.
MSA-DTAG | WA6375725 | 0 | Sapio Pty Ltd | L7 L07-22-mediation room 714-duresss in 7.11 | Security | Security Management System | 134.31 | Fail | Fail | 0 | 0 | 1 | 2022-12-15 10:10 | 2022-12-15 12:10 | 2022-12-15 14:00 | 2022-12-15 14:10 | 2022-12-15 15:00 |  |  | Replaced battery in Duress , restored all okay.
MSA-DTAG | WA6376418 | 3 | Midolo Building Services | L5-Secure waiting area near Court 58-Chairs need tightening | Furniture | Commercial Furniture | 154.48 | Fail | Fail | 2 | 2 | 1 | 2022-12-15 15:03 | 2022-12-22 17:00 | 2023-01-04 12:00 | 2022-12-22 17:00 | 2023-01-04 13:00 |  |  | secure loose chairs
MSA-DTAG | WA6376419 | 3 | Midolo Building Services | L5-Shuttle room and Corridor near CCTV-Ceiling tiles are broken | Building | Ceiling | 135.34 | Fail | Fail | 2 | 2 | 1 | 2022-12-15 15:07 | 2022-12-22 17:00 | 2023-01-04 11:00 | 2022-12-22 17:00 | 2023-01-04 12:00 |  |  | replace ceiling tile
MSA-DTAG | WA6376424 | 3 | Midolo Building Services | L5-Public area outside Court 56-Chairs need tightening | Furniture | Office Furniture | 154.48 | Fail | Fail | 2 | 2 | 1 | 2022-12-15 15:12 | 2022-12-22 17:00 | 2023-01-04 09:00 | 2022-12-22 17:00 | 2023-01-04 10:00 |  |  | secure chairs
MSA-DTAG | WA6376467 | 3 | Midolo Building Services | Court 32 - Chairs loose - public area | Building | General Building | 168.23 | Fail | Fail | 3 | 3 | 1 | 2022-12-15 15:44 | 2022-12-22 17:00 | 2023-01-09 10:30 | 2022-12-22 17:00 | 2023-01-09 11:30 |  |  | LOOSE CHAIRS RESECURED
MSA-DTWD | WA6377324 | 2 | SCAVENGER SUPPLIES PTY LTD | Main Panel - Fault on main panel as advsied by Fire Monitoring | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | -1 | -1 | 1 | 2022-12-16 12:59 | 2022-12-21 17:00 | 2022-12-16 13:40 | 2022-12-21 17:00 | 2022-12-16 14:40 |  |  | Completed 16/12/2022Issues relating to WA6290634 / WA6254047 and will be completed on those work orders
MSA-DTAG | WA6378966 | 0 | Total Security Systems Pty Ltd | External - Staff Gate - gate isnt working | Building | Security Doors | 232 | Fail | Fail | 0 | 0 | 1 | 2022-12-19 08:28 | 2022-12-19 10:28 | 2022-12-19 13:30 | 2022-12-19 12:28 | 2022-12-19 14:30 |  |  | 19/12/2022 - Comtec DataAttended site, rocks were stuck in the wheels of the gate & track, removed and cleared any debris, gate is now working.
MSA-DTWD | WA6379171 | 3 | AWB Co. | Room T041 - door lock snap on cover is loose - see notes | Building | Doors | 137.19 | Pass | Pass | -1 | -1 | 1 | 2022-12-19 09:46 | 2022-12-28 17:00 | 2022-12-21 12:30 | 2022-12-28 17:00 | 2022-12-21 13:30 |  |  | Removed all parts and refitted tightening up all screws and with the grub screw into the barrel drilled it in slight to grab onto barrel housing.Cleaned up work area.Job Complete
MSA-DTWD | WA6379184 | 3 | AWB Co. | Room T040 - door locking plate comes out of the door | Building | Doors | 137.19 | Pass | Pass | -1 | -1 | 1 | 2022-12-19 09:50 | 2022-12-28 17:00 | 2022-12-21 13:30 | 2022-12-28 17:00 | 2022-12-21 14:30 |  |  | Attended Site Collected parts pulled apart refitted and tightened it all up and adjusting until door would lock. Cleaned up work area.
MSA-DTWD | WA6379189 | 3 | AWB Co. | Room T038 - lower lock on side door - cover plate loose | Building | Doors | 137.19 | Pass | Pass | -1 | -1 | 1 | 2022-12-19 09:53 | 2022-12-28 17:00 | 2022-12-21 15:00 | 2022-12-28 17:00 | 2022-12-21 16:00 |  |  | Reattach and tighten up loose parts to lock and barrels
MSA-DTAG | WA6379963 | 2 | Midolo Building Services | Ground-Room/Office-Legal Aid Commission Office-The key lock is loose in the door | Building | Doors | 195.13 | Fail | Fail | 3 | 3 | 1 | 2022-12-19 11:43 | 2022-12-22 17:00 | 2023-01-10 12:30 | 2022-12-22 17:00 | 2023-01-10 13:30 |  |  | REPAIRS COMPLETED TO LOOSE KEY LOCK
MSA-DFES | WA6381871 | 1 | Australian HVAC Services Pty. Ltd. | Dorm - West side - Aircon not working | Air Conditioning | Room Air Conditioners | 139.94 | Fail | Fail | 0 | 0 | 1 | 2022-12-19 15:43 | 2022-12-20 17:00 | 2022-12-21 15:00 | 2022-12-20 17:00 | 2022-12-21 16:00 |  |  | Oscar Holil (21/12/2022) - Work NoteArrived on site and spoke to site representative about the issue with the AC unit. Discovered that the AC in question has already been replaced.
MSA-DTAG | WA6381917 | 2 | Sapio Pty Ltd | Wilsons Security office-DOJ PACOM PC not working - see notes | Security | Security Management System | 406.53 | Fail | Fail | 1 | 1 | 1 | 2022-12-19 16:27 | 2022-12-22 17:00 | 2022-12-29 11:15 | 2022-12-22 17:00 | 2022-12-29 12:15 |  | WACCES | Replaced computer screen, all OK.
MSA-DCA | WA6382805 | 1 | Techworks Electrical | EPS lab (next to Geoff’s office) - faulty light switch | Electrical | General Electrical | 250.16 | Pass | Pass | 0 | 0 | 1 | 2022-12-20 08:05 | 2022-12-21 17:00 | 2022-12-20 09:00 | 2022-12-21 17:00 | 2022-12-20 10:00 |  |  | Replaced light switch in lab, Switch appears to have been pushed in hard which has damaged the mechanism
MSA-DCA | WA6382821 | 1 | Earth & Water Pty Ltd | Museum Plaza (Zone 14) - Broken sprinkler x 1 and leaking sprinkler x 1 | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 1 | 2022-12-20 08:23 | 2022-12-21 17:00 | 2022-12-20 14:00 | 2022-12-21 17:00 | 2022-12-20 15:00 |  |  | repairs to sprinkler
MSA-DTAG | WA6383817 | 1 | Sapio Pty Ltd | Court of Appeal Office & Buss P chambers - duress alarms faulty | Security | Monitoring | 174.52 | Fail | Fail | 0 | 0 | 1 | 2022-12-20 13:53 | 2022-12-21 17:00 | 2022-12-22 08:00 | 2022-12-21 17:00 | 2022-12-22 09:00 |  |  | Checked reported fault. Found faulty duress button. Replaced and tested. OK
MSA-DTWD | WA6385045 | 0 | COMMERCIAL PLUMBING AND GAS | L1-High Level fluid Alarm possible Lift shaft or Grease Trap | Plumbing & Drainage | Water | 123.88 | Pass | Pass | 0 | 0 | 1 | 2022-12-21 09:15 | 2022-12-21 11:15 | 2022-12-21 10:30 | 2022-12-21 13:15 | 2022-12-21 11:30 |  |  | lift tech locked lift and cleaned sump
MSA-DTAG | WA6386630 | 0 | Sapio Pty Ltd | Multiple Security Issues - see notes below | Security | Monitoring |  | Pass | Pass | 0 | 0 | 1 | 2022-12-21 10:47 | 2022-12-21 12:47 | 2022-12-21 11:00 | 2022-12-21 14:47 | 2022-12-21 12:00 |  |  | Closed out at $0 costWarranty
MSA-DTAG | WA6389785 | 1 | AWB Co. | Level 3 - South side - Water has leaked into power socket and has tripped the power | Electrical | General Electrical | 206.84 | Pass | Pass | 0 | 0 | 1 | 2022-12-21 16:38 | 2022-12-22 17:00 | 2022-12-22 07:30 | 2022-12-22 17:00 | 2022-12-22 08:30 |  |  | Attended site. Signed in. Completed jsa. Located faulty circuit on level 3, spoke with staff and found computer area affected by water, switched on circuit and it tripped, unplugged computer and reset circuit , power now working, spoke with staff and told them not to plug in computer to give it time to dry out , all power now working, completed paperwork, signed out **job completed**
MSA-DFES | WA6390427 | 2 | Go Doors | Workshop - Bay 8 - Roller door is only able to be opened manually | Building | Automatic Doors | 909.22 | Fail | Fail | 1 | 1 | 1 | 2022-12-22 09:02 | 2022-12-29 17:00 | 2023-01-03 11:00 | 2022-12-29 17:00 | 2023-01-03 12:00 |  |  | Technician could not find fault with the door while on site, all working fine at the time. Was told by site that they had a power failure and when the power came back on all the doors worked except for that one and it did not appear to have power the light on the controller was not lit. Please continue to monitor, suspect the transformer may be starting to fail and if it reoccurs will require replacing.
MSA-DTAG | WA6393804 | 3 | MALCO FLOORING PTY LTD | Level 7 - Meeting Room 7.4 - Loose carpet tiles | Flooring | Carpet | 216.4 | Pass | Pass | 0 | 0 | 1 | 2022-12-29 10:25 | 2023-01-06 17:00 | 2023-01-05 09:00 | 2023-01-06 17:00 | 2023-01-05 10:00
MSA-MRWA | WA6394209 | 2 | Schindler Lifts Australia | Level 9 - Lift 4 - not operating | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-12-30 09:19 | 2023-01-05 17:00 | 2022-12-30 09:30 | 2023-01-05 17:00 | 2022-12-30 10:30
MSA-DCA | WA6394248 | 2 | Dormakaba Australia Pty Ltd | Push button is not opening the automatic door that leads to the first floor toilet (see notes) | Building | Automatic Doors | 824.2 | Pass | Pass | 0 | 0 | 1 | 2022-12-30 10:12 | 2023-01-05 17:00 | 2023-01-05 12:02 | 2023-01-05 17:00 | 2023-01-05 13:02
MSA-DFES | WA6400029 | 3 | AWB Co. | Ground - Western engine room - fold down seat unserviceable. | Building | General Building | 137.19 | Pass | Pass | -1 | -1 | 1 | 2023-01-03 09:04 | 2023-01-10 17:00 | 2023-01-05 14:15 | 2023-01-10 17:00 | 2023-01-05 15:15
MSA-DTWD | WA6400319 | 2 | Protek 24/7 Building & Maintenance | North East room - Core flute panels blown off roof - see notes | Roofing | Polycarbonate | 122.38 | Pass | Pass | 0 | 0 | 1 | 2023-01-03 11:00 | 2023-01-06 17:00 | 2023-01-03 13:30 | 2023-01-06 17:00 | 2023-01-03 14:30
MSA-DFES | WA6400431 | 2 | Complete Pest Management Services | Main Administration - Corridor - Lecture Room 7 & 8 - Ceiling - possible dead aninmal | Pest Control | General Pest | 235.13 | Pass | Pass | 0 | 0 | 1 | 2023-01-03 12:33 | 2023-01-06 17:00 | 2023-01-04 14:15 | 2023-01-06 17:00 | 2023-01-04 15:15
MSA-DFES | WA6400454 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Administration - Staff Change Room - Floor drain in shower cubicle draining slowly (see notes) | Plumbing & Drainage | Drainage | 143.6 | Pass | Pass | -1 | -1 | 1 | 2023-01-03 12:48 | 2023-01-10 17:00 | 2023-01-04 10:30 | 2023-01-10 17:00 | 2023-01-04 11:30
MSA-DTAG | WA6400477 | 1 | Australian HVAC Services Pty. Ltd. | Stirling Gardens Complex - Mitchell JA chambers - Airconditioning broken | Air Conditioning | Ducted Split System | 201.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-03 13:03 | 2023-01-04 17:00 | 2023-01-03 14:00 | 2023-01-04 17:00 | 2023-01-03 15:00
MSA-DTWD | WA6400529 | 3 | AWB Co. | Emergency light not working outside Campus Managers office | Electrical | Emergency & Exit Lighting | 206.84 | Pass | Pass | 0 | 0 | 1 | 2023-01-03 13:45 | 2023-01-10 17:00 | 2023-01-10 11:00 | 2023-01-10 17:00 | 2023-01-10 12:00
MSA-DTAG | WA6401244 | 2 | Sapio Pty Ltd | Ground - Legal Aid Criminal Duty Lawyer – Room 1 - Duress alarm (see notes) | Security | Monitoring | 284 | Pass | Pass | -1 | -1 | 1 | 2023-01-04 10:14 | 2023-01-09 17:00 | 2023-01-04 15:00 | 2023-01-09 17:00 | 2023-01-04 16:00
MSA-DFES | WA6402444 | 3 | Protek 24/7 Building & Maintenance | Fleet appliance team area-skirting came off from one of the sides of the support columns in office | Flooring | Timber | 172.25 | Pass | Pass | -1 | -1 | 1 | 2023-01-05 11:40 | 2023-01-12 17:00 | 2023-01-06 09:00 | 2023-01-12 17:00 | 2023-01-06 10:00
MSA-DFES | WA6402446 | 3 | Protek 24/7 Building & Maintenance | Paper towel dispenser has come off wall in kitchen | Building | Internal Walls | 141.15 | Pass | Pass | -1 | -1 | 1 | 2023-01-05 11:46 | 2023-01-12 17:00 | 2023-01-06 08:00 | 2023-01-12 17:00 | 2023-01-06 09:00
MSA-DTAG | WA6402471 | 2 | Midolo Building Services | Ground Floor - Staff Female Toilet - door handle is loose | Building | Doors | 168.23 | Pass | Pass | 0 | 0 | 1 | 2023-01-05 11:55 | 2023-01-10 17:00 | 2023-01-09 12:00 | 2023-01-10 17:00 | 2023-01-09 13:00
MSA-DTWD | WA6402716 | 2 | Protek 24/7 Building & Maintenance | Building 1 - Office C707 - Carpet damaged and lifting | Flooring | Carpet | 914.38 | Pass | Pass | 0 | 0 | 1 | 2023-01-05 15:33 | 2023-01-10 17:00 | 2023-01-09 11:00 | 2023-01-10 17:00 | 2023-01-09 12:00
MSA-DFES | WA6403371 | 3 | Complete Pest Management Services | Ground - Wasps nests have been found and need to be removed (see notes) | Pest Control | General Pest | 240.55 | Pass | Pass | -1 | -1 | 1 | 2023-01-06 10:05 | 2023-01-13 17:00 | 2023-01-06 14:00 | 2023-01-13 17:00 | 2023-01-06 15:00
MSA-DFES | WA6403720 | 1 | Australian HVAC Services Pty. Ltd. | Gym - Aircon is leaking a lot of water | Air Conditioning | Room Air Conditioners | 201.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-06 14:10 | 2023-01-09 17:00 | 2023-01-06 15:00 | 2023-01-09 17:00 | 2023-01-06 16:00
MSA-DFES | WA6404608 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Kitchen - Kitchen sink is leaking into the cupboard below (see notes) | Plumbing & Drainage | Drainage | 197.24 | Pass | Pass | 0 | 0 | 1 | 2023-01-09 07:44 | 2023-01-11 17:00 | 2023-01-11 09:30 | 2023-01-11 17:00 | 2023-01-11 10:30
MSA-DTAG | WA6407288 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Unisex public toilet is blocked - see notes | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Fail | Fail | 0 | 0 | 1 | 2023-01-10 07:49 | 2023-01-10 17:00 | 2023-01-11 07:30 | 2023-01-10 17:00 | 2023-01-11 08:30
MSA-DTWD | WA6407379 | 3 | AWB Co. | Light switch stuck in 'on' position | Electrical | Lighting, Internal | 223.09 | Pass | Pass | -1 | -1 | 1 | 2023-01-10 08:32 | 2023-01-17 17:00 | 2023-01-10 12:00 | 2023-01-17 17:00 | 2023-01-10 13:00
MSA-DTWD | WA6407487 | 2 | Techworks Electrical | North wall GPO behind slicing machine is broken | Electrical | General Electrical | 183.015 | Pass | Pass | 0 | 0 | 1 | 2023-01-10 08:54 | 2023-01-13 17:00 | 2023-01-13 09:30 | 2023-01-13 17:00 | 2023-01-13 10:30
MSA-DFES | WA6407705 | 2 | Water2water Pty Ltd | Ground - Kitchen - Billy Water unit has tripped out | Plumbing & Drainage | Water | 173.82 | Pass | Pass | 0 | 0 | 1 | 2023-01-10 10:51 | 2023-01-13 17:00 | 2023-01-11 10:30 | 2023-01-13 17:00 | 2023-01-11 11:30
MSA-DFES | WA6414774 | 3 | Protek 24/7 Building & Maintenance | Retrospective work order - DO NOT ATTEND - Remaining ceiling tiles + labour (see notes) | Building | Ceiling | 300.43 | Pass | Pass | -1 | -1 | 1 | 2023-01-06 09:00 | 2023-01-13 17:00 | 2023-01-06 14:00 | 2023-01-13 17:00 | 2023-01-06 15:00 | 1
MSA-DFES | WA6414808 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Secretary Office - 1 Tubed light faulty - See Notes Below | Electrical | General Electrical | 168.78 | Pass | Pass | -1 | -1 | 1 | 2023-01-11 10:07 | 2023-01-18 17:00 | 2023-01-13 09:30 | 2023-01-18 17:00 | 2023-01-13 10:30
MSA-DTWD | WA6425334 | 2 | AHS Services WA Pty Ltd (Anchor) | Leaking toilet pan adaptor | Plumbing & Drainage | Toilets/Cisterns | 175.53 | Fail | Fail | 0 | 0 | 1 | 2023-01-12 08:59 | 2023-01-17 17:00 | 2023-01-19 09:30 | 2023-01-17 17:00 | 2023-01-19 10:30
MSA-DTWD | WA6425367 | 2 | Techworks Electrical | Student services - Back door - Ceiling light not working | Electrical | Lighting, Internal | 154.63 | Pass | Pass | -1 | -1 | 1 | 2023-01-12 09:29 | 2023-01-17 17:00 | 2023-01-12 12:30 | 2023-01-17 17:00 | 2023-01-12 13:30
MSA-DTWD | WA6425370 | 2 | Techworks Electrical | light not working above desk | Electrical | Lighting, Internal | 144.89 | Pass | Pass | -1 | -1 | 1 | 2023-01-12 09:30 | 2023-01-17 17:00 | 2023-01-12 13:30 | 2023-01-17 17:00 | 2023-01-12 14:30
MSA-DTWD | WA6426041 | 1 | BJ SYSTEMS | Eastern entry auto door -Block is in locked setting but this door opens | Security | Access Control | 180 | Pass | Pass | 0 | 0 | 1 | 2023-01-12 13:51 | 2023-01-13 17:00 | 2023-01-12 14:15 | 2023-01-13 17:00 | 2023-01-12 15:15
MSA-DTWD | WA6431425 | 2 | AHS Services WA Pty Ltd (Anchor) | unisex bathroom- toilet pan is leaking | Plumbing & Drainage | Toilets/Cisterns | 166.32 | Fail | Fail | 0 | 0 | 1 | 2023-01-13 14:28 | 2023-01-18 17:00 | 2023-01-19 12:30 | 2023-01-18 17:00 | 2023-01-19 13:30
MSA-DTWD | WA6449983 | 1 | SENTINEL LOCK SERVICE PTY LTD | Door not being able to open - locking randomly - see notes | Security | Locksmith | 139.42 | Pass | Pass | 0 | 0 | 1 | 2023-01-16 08:49 | 2023-01-17 17:00 | 2023-01-16 11:45 | 2023-01-17 17:00 | 2023-01-16 12:45
MSA-DTWD | WA6449994 | 1 | SENTINEL LOCK SERVICE PTY LTD | Door not being able to be locked | Security | Locksmith | 139.42 | Pass | Pass | 0 | 0 | 1 | 2023-01-16 08:53 | 2023-01-17 17:00 | 2023-01-16 11:45 | 2023-01-17 17:00 | 2023-01-16 12:45
MSA-DTWD | WA6450579 | 2 | AWB Co. | Office light flickering | Electrical | Lighting, Internal | 155.07 | Pass | Pass | 0 | 0 | 1 | 2023-01-16 12:21 | 2023-01-19 17:00 | 2023-01-17 09:45 | 2023-01-19 17:00 | 2023-01-17 10:45
MSA-DCA | WA6450886 | 2 | Techworks Electrical | On Stage Lighting Office- Men’s Toilets- Fluro light | Electrical | Lighting, Internal | 193.96 | Pass | Pass | 0 | 0 | 1 | 2023-01-16 15:47 | 2023-01-19 17:00 | 2023-01-18 09:30 | 2023-01-19 17:00 | 2023-01-18 10:30
MSA-DTWD | WA6462201 | 2 | COMMERCIAL PLUMBING AND GAS | Canteen kitchen - Hot water tap leaking | Plumbing & Drainage | Water | 188.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-17 08:45 | 2023-01-20 17:00 | 2023-01-20 15:30 | 2023-01-20 17:00 | 2023-01-20 16:30
MSA-DTWD | WA6467299 | 2 | ADVANCED LOCK & KEY | Creche Yard- Roller door lock jammed | Security | Locksmith | 662.72 | Pass | Pass | 0 | 0 | 1 | 2023-01-17 14:33 | 2023-01-20 17:00 | 2023-01-18 10:15 | 2023-01-20 17:00 | 2023-01-18 11:15
MSA-DCA | WA6482128 | 3 | Protek 24/7 Building & Maintenance | Undercroft -Doors are sticking and difficult to open. | Building | Doors | 200.68 | Pass | Pass | -1 | -1 | 1 | 2023-01-18 07:34 | 2023-01-24 17:00 | 2023-01-18 14:00 | 2023-01-24 17:00 | 2023-01-18 15:00
MSA-DTWD | WA6482206 | 3 | AWB Co. | faulty GPO's in fumehoods No 8 and No 9 Science Labs East Perth | Building | General Building | 173.61 | Pass | Pass | 0 | 0 | 1 | 2023-01-18 08:08 | 2023-01-25 17:00 | 2023-01-25 09:00 | 2023-01-25 17:00 | 2023-01-25 10:00
MSA-DTAG | WA6482395 | 1 | AAA Ability Locksmiths | Stirling Gardens Complex - Judicial door into Court 1 - Door lock not staying open (see notes) | Security | Locksmith | 273.24 | Pass | Pass | 0 | 0 | 1 | 2023-01-18 09:54 | 2023-01-19 17:00 | 2023-01-19 07:15 | 2023-01-19 17:00 | 2023-01-19 08:15
MSA-DTWD | WA6503869 | 2 | Techworks Electrical | range hood light not working | Electrical | General Electrical | 213.405 | Pass | Pass | 0 | 0 | 1 | 2023-01-19 11:50 | 2023-01-24 17:00 | 2023-01-23 09:00 | 2023-01-24 17:00 | 2023-01-23 10:00
MSA-DTWD | WA6503884 | 2 | Techworks Electrical | range hood light not working | Electrical | General Electrical | 243.67 | Pass | Pass | 0 | 0 | 1 | 2023-01-19 12:01 | 2023-01-24 17:00 | 2023-01-23 12:30 | 2023-01-24 17:00 | 2023-01-23 13:30
MSA-DTAG | WA6504133 | 1 | Bullant Security Pty Ltd | Level 1 G4S- Staff Kitchen- Unable to open plumbing duct door | Security | Keys & Access | 215 | Pass | Pass | 0 | 0 | 1 | 2023-01-19 13:35 | 2023-01-20 17:00 | 2023-01-20 12:05 | 2023-01-20 17:00 | 2023-01-20 13:05
MSA-DCA | WA6509331 | 1 | Techworks Electrical | Alexander Library Building - Stair 4 - Emergency Exit Light Faulty | Electrical | Emergency & Exit Lighting | 217.56 | Pass | Pass | 0 | 0 | 1 | 2023-01-20 09:50 | 2023-01-23 17:00 | 2023-01-23 09:30 | 2023-01-23 17:00 | 2023-01-23 10:30
MSA-DTWD | WA6509392 | 3 | AWB Co. | Children's toilets - toilet roll holder broken off | Building | General Building | 263.46 | Pass | Pass | -1 | -1 | 1 | 2023-01-20 10:24 | 2023-01-30 17:00 | 2023-01-24 06:30 | 2023-01-30 17:00 | 2023-01-24 07:30
MSA-DTWD | WA6516261 | 2 | Precise Air Group | Air-conditioning button broken- see notes | Air Conditioning | Room Air Conditioners | 152.03 | Pass | Pass | 0 | 0 | 1 | 2023-01-23 10:22 | 2023-01-27 17:00 | 2023-01-25 14:00 | 2023-01-27 17:00 | 2023-01-25 15:00
MSA-DTWD | WA6516474 | 1 | AWB Co. | Bathroom and shower areas - Lights not working (see notes) | Electrical | Lighting, Internal | 221.84 | Pass | Pass | 0 | 0 | 1 | 2023-01-23 12:02 | 2023-01-24 17:00 | 2023-01-24 11:00 | 2023-01-24 17:00 | 2023-01-24 12:00
MSA-DCA | WA6516609 | 1 | Techworks Plumbing | Epoch Café - Servery Area - Attend to alarm: Condenser Overtemp (see notes) | Plumbing & Drainage | Drainage | 135.14 | Pass | Pass | 0 | 0 | 1 | 2023-01-23 13:18 | 2023-01-24 17:00 | 2023-01-23 15:30 | 2023-01-24 17:00 | 2023-01-23 16:30
MSA-DFES | WA6516777 | 2 | Go Doors | Urban Pump front door not closing properly - leaving red warning lights on | Building | Fire Door | 333.56 | Pass | Pass | 0 | 0 | 1 | 2023-01-23 14:56 | 2023-01-27 17:00 | 2023-01-27 14:00 | 2023-01-27 17:00 | 2023-01-27 15:00
MSA-DTAG | WA6517431 | 1 | AAA Ability Locksmiths | Door to Court 55 - Can not be unlocked from the outside of the courtroom. | Security | Keys & Access | 258.24 | Pass | Pass | 0 | 0 | 1 | 2023-01-24 09:46 | 2023-01-25 17:00 | 2023-01-25 07:30 | 2023-01-25 17:00 | 2023-01-25 08:30
MSA-DFES | WA6517690 | 2 | Dom's Total Grounds Maintenance | Reticulation leak - Related to WA6361883 | Plumbing & Drainage | Materials | 246 | Pass | Pass | -1 | -1 | 1 | 2023-01-24 11:46 | 2023-01-30 17:00 | 2023-01-26 08:00 | 2023-01-30 17:00 | 2023-01-26 09:00
MSA-DTWD | WA6517718 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, Internal | 380.645 | Pass | Pass | -1 | -1 | 1 | 2023-01-24 11:56 | 2023-01-30 17:00 | 2023-01-24 13:30 | 2023-01-30 17:00 | 2023-01-24 14:30
MSA-DTWD | WA6518000 | 2 | AWB Co. | Room C706 - Whiteboard has come away from wall | Building | General Building | 320.345 | Pass | Pass | -1 | -1 | 1 | 2023-01-24 15:21 | 2023-01-30 17:00 | 2023-01-24 15:30 | 2023-01-30 17:00 | 2023-01-24 16:30
MSA-DTWD | WA6518478 | 2 | M Construction (WA) | Cubicle paper towel dispenser broken and come away from wall | Building | General Building | 464.3 | Pass | Pass | 0 | 0 | 1 | 2023-01-25 08:32 | 2023-01-31 17:00 | 2023-01-31 09:00 | 2023-01-31 17:00 | 2023-01-31 10:00
MSA-DCA | WA6519837 | 1 | Earth & Water Pty Ltd | Francis Street - Zone 2 - Sprinkler leaking resulting in total shutdown of system (see notes) | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1 | 2023-01-27 07:47 | 2023-01-27 17:00 | 2023-01-27 09:00 | 2023-01-27 17:00 | 2023-01-27 10:00
MSA-DTAG | WA6520418 | 0 | Sapio Pty Ltd | Level 2 - Room 201,202,203 &206 - Keypad has red light blinking - Doors not opening | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-27 14:21 | 2023-01-27 16:21 | 2023-01-27 15:30 | 2023-01-27 18:21 | 2023-01-27 16:30
MSA-DCA | WA6520482 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DONT ATTEND - See Notes | Security | Guards |  | Fail | Fail | 0 | 0 | 1 | 2023-01-24 08:28 | 2023-01-25 17:00 | 2023-01-27 12:45 | 2023-01-25 17:00 | 2023-01-27 13:45 | 1
MSA-DCA | WA6520506 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-Security Issue-DO NOT ATTEND-See notes | Security | Security Management System |  | Pass | Pass | 0 | 0 | 1 | 2023-01-26 14:45 | 2023-01-27 17:00 | 2023-01-27 15:45 | 2023-01-27 17:00 | 2023-01-27 16:45 | 1
MSA-DCA | WA6521334 | 2 | Techworks Electrical | Female toilet public - Hand dryer not working | Electrical | General Electrical | 135.15 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 09:59 | 2023-02-02 17:00 | 2023-02-02 14:00 | 2023-02-02 17:00 | 2023-02-02 15:00
MSA-DCA | WA6521362 | 2 | GPS Plumbing & Gas Services PtyLtd | North Foyer - 2nd Cubicle - Male Toilet - Broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 10:10 | 2023-02-02 17:00 | 2023-01-31 12:45 | 2023-02-02 17:00 | 2023-01-31 13:45
MSA-DFES | WA6521400 | 1 | Australian HVAC Services Pty. Ltd. | Room 14 - Aircon pouring water all over floor | Air Conditioning | Room Air Conditioners | 189.44 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 10:32 | 2023-01-31 17:00 | 2023-01-30 14:00 | 2023-01-31 17:00 | 2023-01-30 15:00
MSA-DTWD | WA6521569 | 3 | AWB Co. | Numerous lights faulty and inoperative | Electrical | Lighting, Internal | 390.59 | Pass | Pass | -1 | -1 | 1 | 2023-01-30 11:44 | 2023-02-06 17:00 | 2023-02-01 11:00 | 2023-02-06 17:00 | 2023-02-01 12:00
MSA-DTWD | WA6521850 | 3 | Australian Airconditioning Services Pty Ltd | ET05-Air Conditioner CB keeps Tripping-see notes | Air Conditioning | Room Air Conditioners | 182.92 | Pass | Pass | -1 | -1 | 1 | 2023-01-30 13:44 | 2023-02-06 17:00 | 2023-01-31 11:00 | 2023-02-06 17:00 | 2023-01-31 12:00
MSA-DTWD | WA6521910 | 3 | COMMERCIAL PLUMBING AND GAS | Lower ground-AT101 Storeroom -Oil separator will not switch off on automatic setting | Plumbing & Drainage | Drainage | 133.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 14:30 | 2023-02-06 17:00 | 2023-02-06 15:30 | 2023-02-06 17:00 | 2023-02-06 16:30
MSA-DTWD | WA6522990 | 2 | Australian Airconditioning Services Pty Ltd | Room ET16 - Split System AC – No Power - see notes | Air Conditioning | Room Air Conditioners | 182.92 | Pass | Pass | 0 | 0 | 1 | 2023-01-31 11:28 | 2023-02-03 17:00 | 2023-01-31 12:00 | 2023-02-03 17:00 | 2023-01-31 13:00
MSA-DTWD | WA6523435 | 1 | COMMERCIAL PLUMBING AND GAS | Workshop sink - Leaking tap | Plumbing & Drainage | Water | 288.97 | Pass | Pass | 0 | 0 | 1 | 2023-01-31 15:58 | 2023-02-01 17:00 | 2023-02-01 12:00 | 2023-02-01 17:00 | 2023-02-01 13:00
MSA-DTWD | WA6526659 | 1 | Techworks Electrical | Exposed electrical cable - OHS | Electrical | General Electrical | 151.5 | Pass | Pass | 0 | 0 | 1 | 2023-02-01 09:42 | 2023-02-02 17:00 | 2023-02-02 12:30 | 2023-02-02 17:00 | 2023-02-02 13:30
MSA-DTWD | WA6526833 | 3 | PEEL LOCK SERVICES PTY LTD | Faulty door lock | Security | Locksmith |  | Pass | Pass | -1 | -1 | 1 | 2023-02-01 11:16 | 2023-02-08 17:00 | 2023-02-01 12:30 | 2023-02-08 17:00 | 2023-02-01 13:30
MSA-DTWD | WA6527257 | 1 | AHS Services WA Pty Ltd (Anchor) | Faucet Broken at thread into wall | Plumbing & Drainage | Water | 135.19 | Pass | Pass | 0 | 0 | 1 | 2023-02-01 15:17 | 2023-02-02 17:00 | 2023-02-02 14:15 | 2023-02-02 17:00 | 2023-02-02 15:15
MSA-DTWD | WA6528962 | 1 | COMMERCIAL PLUMBING AND GAS | Kitchen-Water leak under sink - water flooding everywhere although they have managed to turn it off | Plumbing & Drainage | Water | 343.17 | Pass | Pass | 0 | 0 | 1 | 2023-02-02 13:12 | 2023-02-03 17:00 | 2023-02-03 12:00 | 2023-02-03 17:00 | 2023-02-03 13:00
MSA-DTWD | WA6531256 | 2 | Protek 24/7 Building & Maintenance | Block B6 - B333 - 4m x 0.5 meter section of Lino damaged and small hole in concrete underneath | Flooring | Vinyl | 1321.38 | Pass | Pass | 0 | 0 | 1 | 2023-02-03 10:35 | 2023-02-08 17:00 | 2023-02-06 07:30 | 2023-02-08 17:00 | 2023-02-06 08:30 |  | WACCES
MSA-DTAG | WA6531592 | 2 | Schindler Lifts Australia | Outside lift - Down arrow button is pushed in | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2023-02-03 12:49 | 2023-02-08 17:00 | 2023-02-06 06:45 | 2023-02-08 17:00 | 2023-02-06 07:45
MSA-DFES | WA6534265 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Vehicle battery charger ceased | Electrical | General Electrical | 134.46 | Pass | Pass | 0 | 0 | 1 | 2023-02-06 10:55 | 2023-02-07 17:00 | 2023-02-06 11:15 | 2023-02-07 17:00 | 2023-02-06 12:15
MSA-DCA | WA6534309 | 1 | Protek 24/7 Building & Maintenance | Chester building - Courtyard - Loose brick. see notes | Building | General Building | 141.15 | Pass | Pass | 0 | 0 | 1 | 2023-02-06 11:08 | 2023-02-07 17:00 | 2023-02-07 10:30 | 2023-02-07 17:00 | 2023-02-07 11:30
MSA-DTWD | WA6535137 | 1 | Milners Tree Solutions Pty Ltd | Campus-ground-Large tree branch fallen | Landscaping & Gardening | Tree Lopping | 1770 | Pass | Pass | 0 | 0 | 1 | 2023-02-06 14:35 | 2023-02-07 17:00 | 2023-02-07 06:30 | 2023-02-07 17:00 | 2023-02-07 07:30
MSA-DFES | WA6537552 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Second floor - Board room kitchen - Gas smell | Plumbing & Drainage | Gas | 143.6 | Pass | Pass | 0 | 0 | 1 | 2023-02-07 10:02 | 2023-02-08 17:00 | 2023-02-07 12:45 | 2023-02-08 17:00 | 2023-02-07 13:45
MSA-DTWD | WA6537668 | 1 | Equans Mechanical Services Australia | L1-BMS room-Air conditioning programming not working after hours.-see notes | Air Conditioning | Room Air Conditioners | 129.51 | Pass | Pass | 0 | 0 | 1 | 2023-02-07 10:50 | 2023-02-08 17:00 | 2023-02-07 13:30 | 2023-02-08 17:00 | 2023-02-07 14:30
MSA-DTWD | WA6539371 | 2 | Water2water Pty Ltd | North lift foyer - Water fountain not draining | Plumbing & Drainage | Water | 93.86 | Pass | Pass | -1 | -1 | 1 | 2023-02-08 12:43 | 2023-02-13 17:00 | 2023-02-09 10:10 | 2023-02-13 17:00 | 2023-02-09 11:10
MSA-DTWD | WA6539437 | 2 | AWB Co. | 2x LED panels not working - ATT Dan Hume | Electrical | Lighting, Internal | 206.84 | Pass | Pass | -1 | -1 | 1 | 2023-02-08 13:11 | 2023-02-13 17:00 | 2023-02-09 07:30 | 2023-02-13 17:00 | 2023-02-09 08:30
MSA-DTWD | WA6540231 | 2 | Techworks Electrical | Light is not working | Electrical | Lighting, Internal | 239.5 | Pass | Pass | 0 | 0 | 1 | 2023-02-09 09:24 | 2023-02-14 17:00 | 2023-02-13 08:00 | 2023-02-14 17:00 | 2023-02-13 09:00
MSA-DFES | WA6540728 | 3 | Publik Group | The DFES-supplied sign on the front of the VFRS building fell off, and is damaged. see notes | Signage | General Signage | 1442.58 | Fail | Fail | 0 | 0 | 1 | 2023-02-09 13:13 | 2023-02-16 17:00 | 2023-02-17 09:30 | 2023-02-16 17:00 | 2023-02-17 10:30
MSA-DFES | WA6540890 | 1 | Go Doors | Rear Engine room - Door 3 - Tension spring broken | Building | Automatic Doors | 333.56 | Pass | Pass | 0 | 0 | 1 | 2023-02-09 15:53 | 2023-02-10 17:00 | 2023-02-10 15:45 | 2023-02-10 17:00 | 2023-02-10 16:45
MSA-DTWD | WA6544493 | 2 | AHS Services WA Pty Ltd (Anchor) | Staff Retreat - room E108 - Leaking kitchen tap | Plumbing & Drainage | Water | 244.56 | Pass | Pass | 0 | 0 | 1 | 2023-02-10 13:15 | 2023-02-15 17:00 | 2023-02-15 11:00 | 2023-02-15 17:00 | 2023-02-15 12:00
MSA-DTWD | WA6544539 | 3 | AHS Services WA Pty Ltd (Anchor) | Ground floor - Male toilets - Urinal not flushing | Plumbing & Drainage | Toilets/Cisterns | 101.35 | Fail | Fail | 1 | 1 | 1 | 2023-02-10 13:41 | 2023-02-17 17:00 | 2023-02-21 10:30 | 2023-02-17 17:00 | 2023-02-21 11:30
MSA-DTWD | WA6560588 | 2 | AWB Co. | Room C002 - faulty fluro fitting | Electrical | Lighting, Internal | 300.59 | Pass | Pass | 0 | 0 | 1 | 2023-02-13 11:13 | 2023-02-16 17:00 | 2023-02-14 08:15 | 2023-02-16 17:00 | 2023-02-14 09:15
MSA-DCA | WA6560811 | 2 | Protek 24/7 Building & Maintenance | E block - Temporary replace missing glass panel with ply panel | Building | Windows | 141.15 | Pass | Pass | 0 | 0 | 1 | 2023-02-13 13:11 | 2023-02-16 17:00 | 2023-02-15 12:00 | 2023-02-16 17:00 | 2023-02-15 13:00
MSA-DTWD | WA6560977 | 1 | AHS Services WA Pty Ltd (Anchor) | Urinal not draining | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | 0 | 0 | 1 | 2023-02-13 15:20 | 2023-02-14 17:00 | 2023-02-14 09:30 | 2023-02-14 17:00 | 2023-02-14 10:30
MSA-DTWD | WA6572844 | 2 | AHS Services WA Pty Ltd (Anchor) | Tap running exterior between A and B Blocks | Plumbing & Drainage | Water | 153.33 | Pass | Pass | 0 | 0 | 1 | 2023-02-14 09:09 | 2023-02-17 17:00 | 2023-02-16 14:00 | 2023-02-17 17:00 | 2023-02-16 15:00
MSA-DCA | WA6572936 | 2 | Techworks Electrical | Building CRC - Ground Level - Loading Bay 7 - Geoff Deacons Office - Light Switch Faulty (see notes) | Electrical | Lighting, Internal | 197.91 | Pass | Pass | 0 | 0 | 1 | 2023-02-14 09:40 | 2023-02-17 17:00 | 2023-02-15 12:30 | 2023-02-17 17:00 | 2023-02-15 13:30
MSA-DTWD | WA6573444 | 2 | Equans Mechanical Services Australia | Glasshouse - Aircon 3 - leaking SE Corner | Air Conditioning | Room Air Conditioners | 129.51 | Pass | Pass | 0 | 0 | 1 | 2023-02-14 13:25 | 2023-02-17 17:00 | 2023-02-14 15:00 | 2023-02-17 17:00 | 2023-02-14 16:00
MSA-DTAG | WA6578907 | 2 | GPS Plumbing & Gas Services PtyLtd | No hot water - upstairs kitchen or bathroom | Plumbing & Drainage | HWS/Units Electric & Gas | 113.43 | Pass | Pass | -1 | -1 | 1 | 2023-02-15 12:58 | 2023-02-20 17:00 | 2023-02-15 14:20 | 2023-02-20 17:00 | 2023-02-15 15:20
MSA-DCA | WA6578933 | 1 | Techworks Electrical | Library - One flickering light and one fitting with both tubes out (see notes) | Electrical | Lighting, Internal | 135.15 | Pass | Pass | 0 | 0 | 1 | 2023-02-15 13:08 | 2023-02-16 17:00 | 2023-02-16 08:00 | 2023-02-16 17:00 | 2023-02-16 09:00
MSA-DCA | WA6585709 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - See notes | Security | Guards |  | Fail | Fail | 2 | 2 | 1 | 2023-01-31 13:30 | 2023-02-01 17:00 | 2023-02-16 10:30 | 2023-02-01 17:00 | 2023-02-16 11:30 | 1
MSA-DTWD | WA6602820 | 1 | AWB Co. | red 4 circuit faulty - cant reset | Electrical | General Electrical | 987.64 | Fail | Fail | 1 | 1 | 1 | 2023-02-17 11:48 | 2023-02-20 17:00 | 2023-03-02 09:45 | 2023-02-20 17:00 | 2023-03-02 10:45
MSA-DTWD | WA6603944 | 2 | AHS Services WA Pty Ltd (Anchor) | Leaking Uniral mens toilet | Plumbing & Drainage | Toilets/Cisterns | 173.25 | Pass | Pass | 0 | 0 | 1 | 2023-02-17 13:39 | 2023-02-22 17:00 | 2023-02-21 14:00 | 2023-02-22 17:00 | 2023-02-21 15:00
MSA-DCA | WA6649992 | 1 | Critical Fire Protection & Training | Ground Level - Fire Panel alert lights on, Audio and WIP | Fire Protection Services | Fire Protection - Monitor System | 435.78 | Pass | Pass | 0 | 0 | 1 | 2023-02-20 08:39 | 2023-02-21 17:00 | 2023-02-20 12:00 | 2023-02-21 17:00 | 2023-02-20 13:00
MSA-DTWD | WA6650320 | 3 | AWB Co. | Faulty ceiling lights | Electrical | Lighting, Internal | 194.03 | Pass | Pass | 0 | 0 | 1 | 2023-02-20 10:43 | 2023-02-27 17:00 | 2023-02-24 10:30 | 2023-02-27 17:00 | 2023-02-24 11:30
MSA-DTAG | WA6653820 | 1 | Sapio Pty Ltd | L4-L04 – 15 Hearing Room 46 DUR IN 4.6 – Duress Alarm Not Working-see notes | Security | Security Management System | 129.12 | Fail | Fail | 0 | 0 | 1 | 2023-02-21 07:15 | 2023-02-21 17:00 | 2023-02-22 09:30 | 2023-02-21 17:00 | 2023-02-22 10:30
MSA-DCA | WA6659472 | 1 | Wilson Security | RETROSPECTIVE - DO NOT ATTEND - Alarm zone 45 motion sensor to M block south lobby (see notes) | Security | Monitoring |  | Fail | Fail | 0 | 0 | 1 | 2023-02-17 10:44 | 2023-02-20 17:00 | 2023-02-21 12:00 | 2023-02-20 17:00 | 2023-02-21 13:00 | 1
MSA-DCA | WA6662044 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 1 - SEG - Aircon levels are faulty | Air Conditioning | Room Air Conditioners | 146.4 | Pass | Pass | 0 | 0 | 1 | 2023-02-21 12:32 | 2023-02-24 17:00 | 2023-02-24 14:00 | 2023-02-24 17:00 | 2023-02-24 15:00
MSA-DFES | WA6667892 | 2 | Critical Fire Protection & Training | Pillar hydrant in rear yard leaking. | Fire Protection Services | Sprinkler Systems | 269.5 | Pass | Pass | 0 | 0 | 1 | 2023-02-21 16:27 | 2023-02-24 17:00 | 2023-02-22 12:00 | 2023-02-24 17:00 | 2023-02-22 13:00
MSA-DCA | WA6668299 | 1 | Techworks Electrical | Sue Murray Area - A light switch which is sticking when people try to turn it on. | Electrical | Lighting, Internal | 146.24 | Pass | Pass | 0 | 0 | 1 | 2023-02-22 08:17 | 2023-02-23 17:00 | 2023-02-22 09:00 | 2023-02-23 17:00 | 2023-02-22 10:00
MSA-DTWD | WA6668354 | 1 | AHS Services WA Pty Ltd (Anchor) | Male toilet - Urinal blocked - May be causing smell passing through to other areas | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | 0 | 0 | 1 | 2023-02-22 08:41 | 2023-02-23 17:00 | 2023-02-22 08:45 | 2023-02-23 17:00 | 2023-02-22 09:45
MSA-DTAG | WA6669106 | 1 | Midolo Building Services | Ground - Registry - Cashiers 6 & 7 drawer locks need adjusted | Security | Locksmith | 129.73 | Pass | Pass | 0 | 0 | 1 | 2023-02-22 14:21 | 2023-02-23 17:00 | 2023-02-23 08:15 | 2023-02-23 17:00 | 2023-02-23 09:15
MSA-DFES | WA6669235 | 3 | ADVANCED LOCK & KEY | Main admin - Ground - Toilet doors are sticking | Security | Locksmith |  | Fail | Fail | 1 | 1 | 1 | 2023-02-22 16:00 | 2023-03-01 17:00 | 2023-03-07 14:35 | 2023-03-01 17:00 | 2023-03-07 15:35 |  | WACCES
MSA-DTAG | WA6671600 | 1 | AHS Services WA Pty Ltd (Anchor) | Male public toilet blocked – opposite Caffisimo | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 1 | 2023-02-23 09:03 | 2023-02-24 17:00 | 2023-02-23 13:15 | 2023-02-24 17:00 | 2023-02-23 14:15
MSA-DTWD | WA6671642 | 2 | AWB Co. | Emergency Exit in cut mine apperas to not be illuminating | Electrical | Lighting, External | 158.89 | Pass | Pass | 0 | 0 | 1 | 2023-02-23 09:31 | 2023-02-28 17:00 | 2023-02-27 09:00 | 2023-02-28 17:00 | 2023-02-27 10:00
MSA-DCA | WA6672282 | 1 | Dormakaba Australia Pty Ltd | Ground L1 - Foyer to Cafe - Glass siding door - Faulty | Building | Automatic Doors | 401.95 | Pass | Pass | 0 | 0 | 1 | 2023-02-23 14:20 | 2023-02-24 17:00 | 2023-02-23 15:14 | 2023-02-24 17:00 | 2023-02-23 16:14
MSA-DFES | WA6672379 | 3 | Protek 24/7 Building & Maintenance | Ground - Change room 2 - Towel rails coming away from wall | Building | General Building | 141.15 | Pass | Pass | -1 | -1 | 1 | 2023-02-23 15:57 | 2023-03-02 17:00 | 2023-02-24 13:30 | 2023-03-02 17:00 | 2023-02-24 14:30
MSA-MRWA | WA6673084 | 1 | Complete Pest Management Services | Ground floor - Office - Ant Infestation - in partition | Pest Control | General Pest | 240.08 | Pass | Pass | 0 | 0 | 1 | 2023-02-24 10:56 | 2023-02-27 17:00 | 2023-02-27 08:00 | 2023-02-27 17:00 | 2023-02-27 09:00
MSA-DTAG | WA6675134 | 1 | Midolo Building Services | Jury Room - Hinge on windows in jury room broken | Building | Windows | 156.63 | Fail | Fail | 0 | 0 | 1 | 2023-02-27 15:53 | 2023-02-28 17:00 | 2023-03-01 07:15 | 2023-02-28 17:00 | 2023-03-01 08:15
MSA-DCA | WA6680111 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level 5 - Plant Room - Heating Hot Water Boiler 3 - Unit in Fault | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | 0 | 0 | 1 | 2023-03-01 08:37 | 2023-03-02 17:00 | 2023-03-02 08:00 | 2023-03-02 17:00 | 2023-03-02 09:00
MSA-DTWD | WA6680424 | 1 | Equans Mechanical Services Australia | All rooms in S block - A/C Chiller showing 3 x alarms / cannot be reset | Air Conditioning | Ducted Split System | 173.01 | Pass | Pass | 0 | 0 | 1 | 2023-03-01 11:10 | 2023-03-02 17:00 | 2023-03-01 12:45 | 2023-03-02 17:00 | 2023-03-01 13:45
MSA-DTWD | WA6681576 | 1 | Precise Air Group | Wall air con switch has broken (see notes) | Air Conditioning | Evaporative Coolers | 152.03 | Pass | Pass | 0 | 0 | 1 | 2023-03-02 09:46 | 2023-03-03 17:00 | 2023-03-02 15:00 | 2023-03-03 17:00 | 2023-03-02 16:00
MSA-DCA | WA6681595 | 0 | Protek 24/7 Building & Maintenance | Stage door - Access Toilet - door stuck | Building | Doors | 234.82 | Fail | Pass | 0 | 0 | 1 | 2023-03-02 09:54 | 2023-03-02 11:54 | 2023-03-02 12:00 | 2023-03-02 13:54 | 2023-03-02 13:00
MSA-DFES | WA6681685 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | ground-engine room-gap around meter box needs to be rectified-see notes | Electrical | General Electrical | 153.27 | Pass | Pass | 0 | 0 | 1 | 2023-03-02 10:59 | 2023-03-10 17:00 | 2023-03-10 12:30 | 2023-03-10 17:00 | 2023-03-10 13:30
MSA-DTAG | WA6687835 | 1 | Sapio Pty Ltd | Custody area - Control Room - doors not able to be unlocked (see notes) | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1 | 2023-03-07 10:07 | 2023-03-08 17:00 | 2023-03-07 13:30 | 2023-03-08 17:00 | 2023-03-07 14:30
MSA-DTWD | WA6687873 | 2 | AHS Services WA Pty Ltd (Anchor) | push button in cubicle not working | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 1 | 2023-03-07 10:16 | 2023-03-10 17:00 | 2023-03-08 12:00 | 2023-03-10 17:00 | 2023-03-08 13:00
MSA-DTWD | WA6687922 | 2 | AHS Services WA Pty Ltd (Anchor) | toilet seat broken | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 1 | 2023-03-07 10:37 | 2023-03-10 17:00 | 2023-03-08 11:00 | 2023-03-10 17:00 | 2023-03-08 12:00
MSA-DFES | WA6688035 | 2 | Australian HVAC Services Pty. Ltd. | Station Officer Office -Aircon is not operating on “cool”. Unit turns on then turns off immediately. | Air Conditioning | Ducted Split System | 139.94 | Pass | Pass | 0 | 0 | 1 | 2023-03-07 11:14 | 2023-03-10 17:00 | 2023-03-08 12:30 | 2023-03-10 17:00 | 2023-03-08 13:30
MSA-DTAG | WA6688424 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 4 - Ladies staff toilet - seat loose | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 1 | 2023-03-07 14:32 | 2023-03-10 17:00 | 2023-03-09 11:00 | 2023-03-10 17:00 | 2023-03-09 12:00
MSA-DTWD | WA6689152 | 2 | AWB Co. | 10F90 - Faulty Lights | Electrical | Lighting, Internal | 151.81 | Pass | Pass | 0 | 0 | 1 | 2023-03-08 09:54 | 2023-03-13 17:00 | 2023-03-10 09:00 | 2023-03-13 17:00 | 2023-03-10 10:00
MSA-DTAG | WA6690515 | 1 | Gilmour & Jooste Electrical | Interview room 5 - Light is out in the interview room - very dark. (see notes) | Electrical | Lighting, Internal | 145.7 | Pass | Pass | 0 | 0 | 1 | 2023-03-09 10:01 | 2023-03-10 17:00 | 2023-03-09 10:30 | 2023-03-10 17:00 | 2023-03-09 11:30
MSA-DCA | WA6690713 | 2 | Property Fire Maintenance | Main Fire Panel - Fire Door to central archive fire door has a problem with the counter weight systm | Fire Protection Services | Fire Protection - Monitor System | 125 | Pass | Pass | 0 | 0 | 1 | 2023-03-09 11:55 | 2023-03-14 17:00 | 2023-03-13 08:00 | 2023-03-14 17:00 | 2023-03-13 09:00
MSA-DTWD | WA6691044 | 2 | ACTION GLASS & ALUMINIUM | Corridor between A&C blocks - Glass panels coming out of window frames (see notes) | Glazing | Window Glass | 139.88 | Pass | Pass | -1 | -1 | 1 | 2023-03-09 16:00 | 2023-03-14 17:00 | 2023-03-10 13:15 | 2023-03-14 17:00 | 2023-03-10 14:15
MSA-DTWD | WA6693596 | 2 | Water2water Pty Ltd | G/Floor entrance foyer area, the drink fountain is leaking water onto the floor | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1 | 2023-03-10 11:52 | 2023-03-15 17:00 | 2023-03-14 13:35 | 2023-03-15 17:00 | 2023-03-14 14:35
MSA-DTAG | WA6708331 | 1 | GPS Plumbing & Gas Services PtyLtd | Murphy JA chambers - Toilet is running but not filling up | Plumbing & Drainage | Toilets/Cisterns | 263.68 | Pass | Pass | 0 | 0 | 1 | 2023-03-13 16:08 | 2023-03-14 17:00 | 2023-03-14 12:30 | 2023-03-14 17:00 | 2023-03-14 13:30
MSA-DFES | WA6721885 | 0 | Anvil Doors | Building - Engine room - Truck doors not closing | Building | Automatic Doors |  | Fail | Fail | 0 | 0 | 1 | 2023-03-14 12:31 | 2023-03-14 14:31 | 2023-03-14 17:00 | 2023-03-14 16:31 | 2023-03-14 18:00
MSA-DTWD | WA6722045 | 1 | AHS Services WA Pty Ltd (Anchor) | Near the elevator - Blocked urinal drain | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 1 | 2023-03-14 14:36 | 2023-03-15 17:00 | 2023-03-15 11:00 | 2023-03-15 17:00 | 2023-03-15 12:00
MSA-DTWD | WA5195158 | 1 | SENTINEL LOCK SERVICE PTY LTD | Ground - Exit to block 10 - door lock jamming | Security | Locksmith | 211.63 | Pass | Pass | 0 | 0 | 1 | 2022-02-28 11:16 | 2022-03-01 17:00 | 2022-02-28 11:16 | 2022-03-01 17:00 | 2022-02-28 12:16 |  |  | Exit door to Block 10 - lock jamming.Lock repaired.
MSA-MRWA | WA6251525 | 2 | GPS Plumbing & Gas Services PtyLtd | Ambulant toilet constantly running | Plumbing & Drainage | Toilets/Cisterns | 778.5 | Pass | Pass | 0 | 0 | 1 | 2022-11-22 09:33 | 2022-11-25 17:00 | 2022-11-22 13:31 | 2022-11-25 17:00 | 2022-11-22 14:31 |  |  | Needs new cistern
MSA-DFES | WA6130565 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | multiple rooms - lights need changing - see notes | Electrical | Lighting, Internal | 192.78 | Pass | Pass | 0 | 0 | 1 | 2022-10-28 13:00 | 2022-11-04 17:00 | 2022-11-02 12:31 | 2022-11-04 17:00 | 2022-11-02 13:31 |  |  | Tasz Cumming (02/11/2022) - Work NoteArrived 1231Located faulty light over toilets near reception and inspected ,Replace 1x 18w 840 fluro tubesLocated faulty light in training room 7 and inspectedReplaced 1x 36w 840 fluro tube and S10 starterLocated faulty light in staff change room and inspectedReplaced 1x 36w 840 fluro tube and starterSigned out 1331
MSA-DCA | WA6504405 | 1 | Techworks Electrical | First Floor - Studio 0 - Outside Admin 3 - Emergency Exit Light is broken | Electrical | Emergency & Exit Lighting | 140.15 | Pass | Pass | 0 | 0 | 1 | 2023-01-19 15:31 | 2023-01-20 17:00 | 2023-01-19 15:31 | 2023-01-20 17:00 | 2023-01-19 16:31
MSA-DTAG | WA4985999 | 3 | AWB Co. | Level 10 - Criminal Injuries Compensation - Reception - see notes below | Electrical | Lighting, Internal | 160.26 | Pass | Pass | 0 | 0 | 1 | 2021-12-31 06:53 | 2022-01-07 17:00 | 2022-01-04 11:30 | 2022-01-07 17:00 | 2022-01-04 12:30 |  |  | Job complete
MSA-DCA | WA4991861 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground - cleaners room - Tap head needs to be able to have a standard garden hose attached to it. | Plumbing & Drainage | Materials | 183.41 | Pass | Pass | 0 | 0 | 1 | 2022-01-05 13:06 | 2022-01-06 17:00 | 2022-01-06 08:30 | 2022-01-06 17:00 | 2022-01-06 09:30 |  |  | Installed a hose tap and vacuum breaker
MSA-DTWD | WA4994958 | 3 | Milners Tree Solutions Pty Ltd | In Garden (next to slip road) - Tree has fallen down | Landscaping & Gardening | General Tree Works | 1000 | Pass | Pass | -1 | -1 | 1 | 2022-01-10 09:04 | 2022-01-17 17:00 | 2022-01-12 07:00 | 2022-01-17 17:00 | 2022-01-12 08:00 |  |  | Tree removed
MSA-DCA | WA4995199 | 2 | Techworks Electrical | Critical spares failed - faulty and need replacing | Electrical | General Electrical | 3189.33 | Pass | Pass | 0 | 0 | 1 | 2022-01-10 10:48 | 2022-01-13 17:00 | 2022-01-13 13:00 | 2022-01-13 17:00 | 2022-01-13 14:00 |  |  | Obtained additional tubes and globes for site stock for maintenance
MSA-DTWD | WA5018200 | 2 | Precise Air Group | Evaporative A/C - not working | Air Conditioning | Evaporative Coolers | 193.62 | Pass | Pass | 0 | 0 | 1 | 2022-01-14 09:52 | 2022-01-19 17:00 | 2022-01-19 07:00 | 2022-01-19 17:00 | 2022-01-19 08:00 |  |  | Restored power to units I was previously asked to isolate
MSA-DTWD | WA5018267 | 2 | Equans Mechanical Services Australia | Left A/C unit - AG16.1 is not working – when turned on vanes open then unit automatically turns off | Air Conditioning | Room Air Conditioners | 204.07 | Pass | Pass | 0 | 0 | 1 | 2022-01-14 10:27 | 2022-01-19 17:00 | 2022-01-17 08:30 | 2022-01-19 17:00 | 2022-01-17 09:30 |  |  | Reset and checked operation after U4 fault. All ok
MSA-DCA | WA5018332 | 1 | Techworks Electrical | Studio underground - East corridor and bio box corridor - 3 x exit lights not working | Electrical | Lighting, Internal | 122.53 | Pass | Pass | 0 | 0 | 1 | 2022-01-14 11:04 | 2022-01-17 17:00 | 2022-01-17 14:30 | 2022-01-17 17:00 | 2022-01-17 15:30 |  | WACCES | No action taken on work order.This is a nexus fitting and requires a long lead time to order and replace.As discussed with Reese Withey, a new work order will be raised for rectification.
MSA-DTWD | WA5038262 | 2 | Water2water Pty Ltd | Hot water rheem not working | Plumbing & Drainage | Water | 302.68 | Pass | Pass | 0 | 0 | 1 | 2022-01-17 11:43 | 2022-01-20 17:00 | 2022-01-19 12:15 | 2022-01-20 17:00 | 2022-01-19 13:15 |  |  | Replaced broken tap! All now flowing ok.
MSA-DCA | WA5053327 | 2 | Techworks Electrical | External - Urban Orchard - Reset lighting timings | Electrical | General Electrical | 122.53 | Pass | Pass | 0 | 0 | 1 | 2022-01-18 15:57 | 2022-01-21 17:00 | 2022-01-20 11:30 | 2022-01-21 17:00 | 2022-01-20 12:30 |  |  | Reset urban orchid and pcc events DB’s and Fiji room
MSA-DTWD | WA5067144 | 2 | Securex Security Systems & Services | L Block - Ground - Lift - swipe card reader for the lift is not working | Security | Monitoring | 389.27 | Pass | Pass | -1 | -1 | 1 | 2022-01-19 10:14 | 2022-01-24 17:00 | 2022-01-20 08:30 | 2022-01-24 17:00 | 2022-01-20 09:30 |  |  | Ian Fouche (20/01/2022, 830-930) - Work NoteChecked reader relay and tried shorting cable.The elevator not responding, the out of service lock is active
MSA-DTAG | WA5069041 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet blockage in disabled/parents toilet on ground floor behind listings. | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | -1 | -1 | 1 | 2022-01-19 14:12 | 2022-01-24 17:00 | 2022-01-20 13:00 | 2022-01-24 17:00 | 2022-01-20 14:00 |  |  | Cleared blocked toilet with plunger
MSA-DTWD | WA5069118 | 2 | AWB Co. | Broken light switch | Electrical | Lighting, Internal | 162.19 | Pass | Pass | -1 | -1 | 1 | 2022-01-19 15:11 | 2022-01-24 17:00 | 2022-01-20 10:45 | 2022-01-24 17:00 | 2022-01-20 11:45 |  |  | Attended site, signed in, completed jsa, spoke to fm about job, located lighting switch, isolated circuit, removed old switch, replaced with new, re energised lighting circuit, tested lights and working as intended , packed up, cleaned up, completed paperwork, signed out **job complete**
MSA-DTWD | WA5069195 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 278.35 | Pass | Pass | 0 | 0 | 1 | 2022-01-19 16:36 | 2022-01-27 17:00 | 2022-01-27 13:45 | 2022-01-27 17:00 | 2022-01-27 14:45 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B64 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box lcated in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DFES | WA5086874 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Training Room/Lounge Room - damaged antenna point | Electrical | General Electrical | 170.89 | Pass | Pass | 0 | 0 | 1 | 2022-01-21 15:05 | 2022-01-31 17:00 | 2022-01-28 07:00 | 2022-01-31 17:00 | 2022-01-28 08:00 |  |  | Arrived on site 0700 and proceeded to locate broken tv socket mechanism in theatre. Left site to go to supplier at 0710, and returned at 0720. Proceeded to replace switch plate and both tv socket mechs. Tested Tv for correct operation on antenna and paid tv. Both working correctly. Left site at 0800.
MSA-DTWD | WA5092127 | 2 | SCAVENGER SUPPLIES PTY LTD | Fire panel - Intermittent fault still showing - see details below | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | -1 | -1 | 1 | 2022-01-27 14:53 | 2022-02-01 17:00 | 2022-01-28 13:00 | 2022-02-01 17:00 | 2022-01-28 14:00 |  |  | COMPLETED 28/01/2022TECH NOTE:Note1:45 PM 28/01/2022 by BENRequest follow up on response to quote we have already done to fix this issue
MSA-DTWD | WA5094714 | 2 | AWB Co. | Electric switchboard next to A356 - Faulty electrical circuit | Electrical | General Electrical | 192.22 | Pass | Pass | 0 | 0 | 1 | 2022-01-31 13:13 | 2022-02-03 17:00 | 2022-02-03 07:00 | 2022-02-03 17:00 | 2022-02-03 08:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Went over to b5. Located switchboard. Found there was a power isolator that had tripped. Tried to reset and it wouldn’t. Went into room and looked for e stops. Found there was an e stop that may have accidentally been pushed in. Reset e stop. Went back to board to reset isolator and it reset. Took pictures of everything working. Everything is working as intended. Completed paperwork. Signed out.*** Job is complete ***
MSA-MRWA | WA5098480 | 1 | AWB Co. | multiple lights out due to circuit trip | Electrical | Lighting, Internal | 155.94 | Pass | Pass | 0 | 0 | 1 | 2022-02-01 09:43 | 2022-02-02 17:00 | 2022-02-01 13:45 | 2022-02-02 17:00 | 2022-02-01 14:45 |  |  | Attended site and signed in. Completed JSA. Spoke to reception at front desk and got passes. Spoke with manager and she came and showed us the issue with lights, gave us swipe card. Got her to show us the switchboard location. Looked at breakers and noticed a couple tripped. Turned on breakers. Walked around and tested lights. All lights that were out are now working as intended. Gave lights and ballasts time to heat up . Spoke to manager again to tell her what issue was. Called Craig and explained what we did and what happened. Took pictures. Completed paperwork. Checked lights were still on (lights were working for 45 mins before we left) Signed out. *** Job complete ***
MSA-DTWD | WA5098487 | 0 | Schindler Lifts Australia | Lift fault - not working - will get stuck going to first level from ground | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-02-01 09:46 | 2022-02-01 11:46 | 2022-02-01 10:00 | 2022-02-01 13:46 | 2022-02-01 11:00 |  |  | to be closed out at $0 cost
MSA-DTWD | WA5098795 | 1 | Dormakaba Australia Pty Ltd | C Block - Ground - Main Administration - Auto door sensor not working correctly | Building | Automatic Doors | 678.07 | Pass | Pass | 0 | 0 | 1 | 2022-02-01 11:19 | 2022-02-02 17:00 | 2022-02-01 13:20 | 2022-02-02 17:00 | 2022-02-01 14:20 |  |  | On inspection, found internal sensor working intermittently due to age, wear and tear.Replaced faulty sensor as required, tested and adjusted, all OK.
MSA-DTWD | WA5099735 | 1 | High Tech Pest Control | B2204 Library External (Seated Courtyard) - see notes below | Pest Control | General Pest | 364 | Pass | Pass | 0 | 0 | 1 | 2022-02-02 08:20 | 2022-02-03 17:00 | 2022-02-02 13:00 | 2022-02-03 17:00 | 2022-02-02 14:00 |  |  | Sprat Treatment for Ants around Library, Garden Beds and Pathways Completed
MSA-DTAG | WA5100111 | 1 | AAA Ability Locksmiths | Custody - Emergency key for the sally port door not working. see notes | Security | Locksmith | 370.89 | Pass | Pass | 0 | 0 | 1 | 2022-02-02 10:56 | 2022-02-03 17:00 | 2022-02-02 13:00 | 2022-02-03 17:00 | 2022-02-02 14:00 |  |  | Attend site, replaced lock in the sally port door
MSA-DTWD | WA5100941 | 0 | Schindler Lifts Australia | lift is making a loud locking / clunky noise when in operation from second floor down | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-02-03 08:20 | 2022-02-03 10:20 | 2022-02-03 08:30 | 2022-02-03 12:20 | 2022-02-03 09:30 |  |  | to be closed out at $0 cost
MSA-DTWD | WA5101334 | 1 | BAKE-QUIP PTY LTD | Oven 5 have been reported as faulty by lecturers. | Equipment | Catering Equipment | 230 | Fail | Fail | 2 | 2 | 1 | 2022-02-03 11:16 | 2022-02-04 17:00 | 2022-02-17 08:30 | 2022-02-04 17:00 | 2022-02-17 09:30 |  |  | see service report.
MSA-DCA | WA5101780 | 1 | Techworks Plumbing | Ground - Epoch Café Accessible Toilet - Hand basin water spout has broken/fallen off the wall * | Plumbing & Drainage | Water | 133.44 | Pass | Pass | 0 | 0 | 1 | 2022-02-03 14:42 | 2022-02-04 17:00 | 2022-02-03 16:00 | 2022-02-04 17:00 | 2022-02-03 17:00 |  |  | Attend site for call out to museum.sign in at the security desk and contact Neil.the spout for the hand basins has come off, it has come off due to the grub screw coming loose.I’ve had to isolate the sensor for the basins in the roof space to work on the spout, replaced the spout back on and tighten in the grub screw.return the power back on to the basin and test the spout out. In good working order
MSA-DTWD | WA5106455 | 1 | Protek 24/7 Building & Maintenance | G27 - Vindalized window - needs replacement | Building | Windows | 477 | Pass | Pass | 0 | 0 | 1 | 2022-02-07 08:31 | 2022-02-08 17:00 | 2022-02-07 11:30 | 2022-02-08 17:00 | 2022-02-07 12:30 |  | WACCES | Replace Vandalized window
MSA-DTWD | WA5106720 | 2 | Precise Air Group | E204 AC cannot be manually adjusted as its stuck on centrally controlled | Air Conditioning | Room Air Conditioners | 141.29 | Pass | Pass | 0 | 0 | 1 | 2022-02-07 10:48 | 2022-02-10 17:00 | 2022-02-07 13:00 | 2022-02-10 17:00 | 2022-02-07 14:00 |  |  | Attended site and completed pre start paperwork andsinged in.Located classroom and isolated system. Removed commscable for redundant central control. Test ran system and left unit In good working order.
MSA-DFES | WA5107144 | 2 | Protek 24/7 Building & Maintenance | Ground Floor - Training Room 2 & Info Resources - see details below | Building | General Building | 141.5 | Pass | Pass | 0 | 0 | 1 | 2022-02-07 14:52 | 2022-02-10 17:00 | 2022-02-09 07:00 | 2022-02-10 17:00 | 2022-02-09 08:00 |  |  | Loose door due to hinge having come off
MSA-DCA | WA5108129 | 2 | Protek 24/7 Building & Maintenance | James street entrance tunnel - Several bricks have lifted causing a trip hazard - see notes | Paving & Roadworks | Paving | 301.625 | Pass | Pass | 0 | 0 | 1 | 2022-02-08 11:52 | 2022-02-11 17:00 | 2022-02-10 08:30 | 2022-02-11 17:00 | 2022-02-10 09:30 |  |  | Relayed pavers
MSA-DFES | WA5108679 | 2 | SONTEC WA PTY LTD | Level 1 - Comcen Server Room - faulty green exit button in comcen server room | Security | Access Control | 406.73 | Pass | Pass | 0 | 0 | 1 | 2022-02-08 16:14 | 2022-02-11 17:00 | 2022-02-11 13:45 | 2022-02-11 17:00 | 2022-02-11 14:45 |  |  | 11/2/22 - Dean SimpsonReplaced RTE button and reset door controller.All working ok.
MSA-DTWD | WA5109217 | 1 | AWB Co. | E Block - Ground - E200 - Exposed wire on Forklift charging cable | Electrical | General Electrical | 199.72 | Pass | Pass | 0 | 0 | 1 | 2022-02-09 07:58 | 2022-02-09 17:00 | 2022-02-09 10:00 | 2022-02-09 17:00 | 2022-02-09 11:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located forklift charger with damaged cable. Took cover off box and opened up. Found where lugs were terminated. Took off lugs and slid multiple layers of heat shrink over exposed cabling. Re terminated lugs once we had finished with heat shrink. Put covers back on box. Took pictures. Everything all good now. Completed paperwork, Signed out. *** Job complete ***
MSA-DTWD | WA5111719 | 2 | BAKE-QUIP PTY LTD | E-Block - Skills kitchen 3 - lecturers oven does not stay on gas goes out | Equipment | Catering Equipment | 305.2 | Fail | Fail | 0 | 0 | 1 | 2022-02-10 10:30 | 2022-02-15 17:00 | 2022-02-17 13:00 | 2022-02-15 17:00 | 2022-02-17 14:00 |  |  | Refer to service report
MSA-DTWD | WA5111892 | 1 | Equans Mechanical Services Australia | Building 4 - Level 2 - Lecture Theatre D225 - Air Conditioning not working | Air Conditioning | Room Air Conditioners | 120.35 | Fail | Fail | 15 | 15 | 1 | 2022-02-10 11:52 | 2022-02-11 17:00 | 2022-05-30 13:00 | 2022-02-11 17:00 | 2022-05-30 14:00 |  |  | CARRIED OUT INSPECTION OF FCU 7 SERVING LECTURE THEARTERAND FOUND UNIT TO OPERATING TO BUILDING REQUIREMENTS. NOTED THAT LOGS SHOWS RECENT CHILLER ISSUES WHICH COULD HAVE LEAD TO REPORT OF A NORMAL SYSTEM OPERATION. CHILLER REPAIRS ARE SCHEDULED TO BE CARRIED OUT THIS WEEK. WORK AREA LEFT TIDY. NO FURTHER ACTION REQUIRED.
MSA-DTWD | WA5115725 | 2 | ECO PLUMBING AND GAS PTY LTD | Leaking tap | Plumbing & Drainage | Water | 237.35 | Pass | Pass | 0 | 0 | 1 | 2022-02-11 08:52 | 2022-02-16 17:00 | 2022-02-14 14:30 | 2022-02-16 17:00 | 2022-02-14 15:30 |  |  | Replaced leaking tap
MSA-MRWA | WA5115851 | 1 | Automatic Fire Protection (ARA) | Main fire Panel - reset panel and re-investigate fault | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-02-11 09:42 | 2022-02-14 17:00 | 2022-02-11 11:30 | 2022-02-14 17:00 | 2022-02-11 12:30 |  |  | 11/02/22 EIOn arrival liaised with FM.At the FIP the panel was reporting 4 faults.Zone 1 Basement CentreZone 5 Basement Comms roomZone 29 level 7 WestZone 88 West stairwellFM mentioned that level 6 Centre disabled toilet smoke detector went into fire alarm this morning & that they noticed these faults present onthe FIP after the fire alarm.History log records zone 27 level 6 fire alarm at 9:35 am & faults presenting there after.All faults reset Ok.Inspected the level 6 disabled toilet smoke detector L3D213.This toilet has an automatic deodoriser dispenser device within the disabled toilet.There appears to be a supply air vent but no return air vent.The travel path of the deodoriser is in line with the smoke detector.It is recommended that the dispenser be removed or relocated.Advised FM & re-instated the fire panel to normal operation.
MSA-DFES | WA5126250 | 1 | Protek 24/7 Building & Maintenance | Ground floor -Stair 2 -security door handle has damaged . | Building | Fire Door | 158 | Fail | Fail | 0 | 0 | 1 | 2022-02-14 06:58 | 2022-02-15 06:58 | 2022-02-15 07:00 | 2022-02-15 06:58 | 2022-02-15 08:00 |  |  | Damaged ground floor Security Handle
MSA-DTWD | WA5128078 | 1 | Equans Mechanical Services Australia | new split system A/C does not appear to cool any more. | Air Conditioning | Ducted Split System | 120.35 | Pass | Pass | 0 | 0 | 1 | 2022-02-14 15:46 | 2022-02-15 17:00 | 2022-02-15 13:00 | 2022-02-15 17:00 | 2022-02-15 14:00 |  |  | Checked out the high wall split in G1 , found on signal going from the evap to the compressor. No fault code comes up , unit is only a few months old , will get installers to look at .
MSA-DTAG | WA5141721 | 3 | Dom's Total Grounds Maintenance | Grounds - Reticulation around Old Court House has failed | Landscaping & Gardening | Grounds Maintenance | 140 | Pass | Pass | -1 | -1 | 1 | 2022-02-16 12:05 | 2022-02-23 17:00 | 2022-02-17 11:30 | 2022-02-23 17:00 | 2022-02-17 12:30 |  |  | Dom Labour 1 Hr & Retic Parts $60
MSA-DCA | WA5148039 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Main Building -Gallery 1 and 6 -making room temperature alarm | Building | Materials | 518.03 | Pass | Pass | 0 | 0 | 1 | 2022-02-17 03:22 | 2022-02-17 05:22 | 2022-02-17 04:00 | 2022-02-17 07:22 | 2022-02-17 05:00 |  |  | Ac1 301 perimeter temp high (23 degrees). Unit still running on ETS, water temperature was 7.9 degrees 100% chilled chilled water valve and 0% heating.
MSA-DFES | WA5150781 | 1 | Schindler Lifts Australia | ground floor - elevator - outside doors faulty will not close - elevator | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-02-17 08:29 | 2022-02-18 17:00 | 2022-02-17 10:02 | 2022-02-18 17:00 | 2022-02-17 11:02 |  |  | job completed - Ground floor landing door aircord come off pulley, refitted aircord and put back in serviceto be closed out at $0 cost
MSA-DTAG | WA5151415 | 2 | Midolo Building Services | Level 4 - Court 42 - the public door isn't sitting on its hinge properly | Building | Doors | 158.97 | Pass | Pass | 0 | 0 | 1 | 2022-02-17 12:36 | 2022-02-22 17:00 | 2022-02-22 13:00 | 2022-02-22 17:00 | 2022-02-22 14:00 |  |  | HINGE REQUIRED REPLACEMENT - COMPLETED
MSA-DCA | WA5164666 | 0 | EQUANS Mechanical Services (WA) Pty Limited | RO Plant tank low level alarm | Security | Monitoring |  | Pass | Pass | 0 | 0 | 1 | 2022-02-19 11:12 | 2022-02-19 13:12 | 2022-02-19 13:00 | 2022-02-19 15:12 | 2022-02-19 14:00 |  |  | Trent called job has been completed but unable to see from his promap:Checked BMS for faults:-RO Plant in low level and also high level fault-Checked tank water level all okay, unable to reset faults, believe to have faulty sensor.
MSA-DCA | WA5173273 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Chiller 1 in fault, chiller 2 has no lights on whatsoever | Air Conditioning | Room Air Conditioners | 204.08 | Pass | Pass | 0 | 0 | 1 | 2022-02-20 22:42 | 2022-02-21 00:42 | 2022-02-20 23:30 | 2022-02-21 02:42 | 2022-02-21 00:30 |  |  | Checked out chiller and condenser water pump in fault. Logged onto the BMS and checked, reset faults. Ran up chiller and watched water temperatures drop. Checked over chiller and pumps, all ok.
MSA-MRWA | WA5187281 | 2 | Dormakaba Australia Pty Ltd | Garage - Roller door not closing - see notes below | Building | Doors | 380 | Pass | Pass | 0 | 0 | 1 | 2022-02-22 12:30 | 2022-02-25 17:00 | 2022-02-23 10:00 | 2022-02-25 17:00 | 2022-02-23 11:00 |  |  | Assessed door and found faulty safety beam which is causing the door to stay openQuote will be done for new banner PB008 safety beam
MSA-DTWD | WA5187902 | 2 | AWB Co. | Flickering fluro in hallway outside male toilet | Electrical | Lighting, Internal | 142.06 | Pass | Pass | 0 | 0 | 1 | 2022-02-22 16:46 | 2022-02-25 17:00 | 2022-02-23 13:00 | 2022-02-25 17:00 | 2022-02-23 14:00 |  |  | Attended site signed in completed jsa, spoke with site FM about job. Found faulty globe. Replaced with new 18w 2P. Tested operation and works now.***job completed***
MSA-DTWD | WA5188470 | 3 | Protek 24/7 Building & Maintenance | Reception / Foyer - Loose wall fixtures to 2 small paintings | Building | Internal Walls | 229 | Pass | Pass | -1 | -1 | 1 | 2022-02-23 09:11 | 2022-03-02 17:00 | 2022-02-25 12:15 | 2022-03-02 17:00 | 2022-02-25 13:15 |  |  | Loose wall fixtures
MSA-MRWA | WA5189084 | 2 | SCHIAVELLO SYSTEMS (WA) PTY LTD | Level 2 - RTTO – Desk 13 - leaking Hydraulic Oil | Furniture | Indoor Furniture |  | Pass | Pass | 0 | 0 | 1 | 2022-02-23 13:49 | 2022-02-28 17:00 | 2022-02-25 07:00 | 2022-02-28 17:00 | 2022-02-25 08:00 |  |  | Work order closed out at $0 cost
MSA-DFES | WA5192014 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilet - Plumbing repair to male toilet – water running continually | Plumbing & Drainage | Toilets/Cisterns | 208.98 | Pass | Pass | 0 | 0 | 1 | 2022-02-25 11:00 | 2022-03-02 17:00 | 2022-03-02 08:30 | 2022-03-02 17:00 | 2022-03-02 09:30 |  |  | Had to replaces the inlet valve and mini stop and flexi hose on male toilet
MSA-DTAG | WA5195518 | 1 | Sapio Pty Ltd | Security Desk - Camera 41 - has lost connection to server and needs administrator action | Security | CCTV Surveillance | 145 | Pass | Pass | 0 | 0 | 1 | 2022-02-28 12:45 | 2022-03-01 17:00 | 2022-03-01 08:30 | 2022-03-01 17:00 | 2022-03-01 09:30 |  |  | Fault find on Camera 41 (Outside Court 30 found bad connection, fixed, tested OK.
MSA-DTWD | WA5199210 | 2 | Schindler Lifts Australia | Lift No4 - Lift stuck on level 3 doors open | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-03-01 08:13 | 2022-03-04 17:00 | 2022-03-01 08:30 | 2022-03-04 17:00 | 2022-03-01 09:30 |  |  | to be closed out at $0 cost
MSA-DTAG | WA5199465 | 1 | Bullant Security Pty Ltd | Level 4 - Interview Room 4.8 - lock on door is faulty | Security | Locksmith | 499.96 | Pass | Pass | 0 | 0 | 1 | 2022-03-01 09:41 | 2022-03-02 17:00 | 2022-03-01 10:00 | 2022-03-02 17:00 | 2022-03-01 11:00 |  |  | Attended site to supply and install new hardware for interview room door on level 4.Supplied new 1801, 1905 lever handles and 1800 scar plates both sides. Supplied an extended cylinder retaining screw and modified the lock hub to allow square bars to fit.Date on site: 01/03/2022Time on site: 10:00am - 11:00am
MSA-DFES | WA5199525 | 2 | Australian HVAC Services Pty. Ltd. | FF Dorm 2 - Aircon unit is dorm is leaking water on to the carpet. Blocked drain suspected. | Air Conditioning | Room Air Conditioners | 130.05 | Pass | Pass | 0 | 0 | 1 | 2022-03-01 10:05 | 2022-03-04 17:00 | 2022-03-01 11:30 | 2022-03-04 17:00 | 2022-03-01 12:30 |  |  | Arrived on site and spoke to site representative about the issue with the AC. Found that Dorm 2 AC had been leaking a day prior. Dismantled the unit and investigated. Found alot of build up in the condensate tray. Washed out condensate drain and tray. Tested the drain and found it to be working. Packed up and left site.
MSA-DTAG | WA5201308 | 0 | AWB Co. | ground - Court 3 - Court 3 JSO & Bench area has no power, no switches are tripped | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-03-02 13:30 | 2022-03-02 15:30 | 2022-03-02 14:30 | 2022-03-02 17:30 | 2022-03-02 15:30 |  |  | Attended site signed in completed jsa. Spoke with stuart about job, no power in bench. Found switch on side of bench which isolates bench. Turned on and power came back on.***job completed***
MSA-DTAG | WA5204391 | 1 | Bullant Security Pty Ltd | Courtside - Ground - Family Violence entry - The lock to the Family Violence door has ceased/ stop | Security | Locksmith | 366.37 | Pass | Pass | -1 | -1 | 1 | 2022-03-04 10:02 | 2022-03-08 17:00 | 2022-03-04 11:30 | 2022-03-08 17:00 | 2022-03-04 12:30 |  |  | Attended site to replace faulty mortice lock. Changed function so this lock is permanently unlocked at all times and cannot be locked, as requested by Stacey. The top 530dx lock will always be locked.Date on site: 04/03/2022Time on site: 11:30am - 12:30pm
MSA-DFES | WA5208459 | 1 | SONTEC WA PTY LTD | ground floor - Keys safe (electronic) showing running on batteries not AC power | Security | Security Management System | 310 | Pass | Pass | 0 | 0 | 1 | 2022-03-09 08:51 | 2022-03-10 17:00 | 2022-03-09 13:00 | 2022-03-10 17:00 | 2022-03-09 14:00 |  |  | 9/3/22 - Dylan ParslowFound keysafe all working.Tested operation and reset alarm.AC fail cleared. Tested all ok.
MSA-DFES | WA5216475 | 3 | Protek 24/7 Building & Maintenance | BA Front House - Ground - House - see details | Building | General Building | 182.78 | Pass | Pass | -1 | -1 | 1 | 2022-03-11 09:57 | 2022-03-18 17:00 | 2022-03-14 07:00 | 2022-03-18 17:00 | 2022-03-14 08:00 |  |  | Repaired door latch
MSA-DTWD | WA5216625 | 3 | AWB Co. | Chalk Cheese Cafe - Front malamine panel damaged on cash register bench | Building | General Building | 105 | Pass | Pass | -1 | -1 | 1 | 2022-03-11 11:37 | 2022-03-18 17:00 | 2022-03-11 14:30 | 2022-03-18 17:00 | 2022-03-11 15:30 |  |  | Arrived on site signed in and was shown the job, got materials cut to size and fitted, signed outalready on site so no call out fee
MSA-DTWD | WA5231358 | 1 | BAKE-QUIP PTY LTD | Restaurant kitchen blast chiller leaking water by resirvoir | Equipment | Catering Equipment | 230 | Pass | Pass | 0 | 0 | 1 | 2022-03-15 10:48 | 2022-03-16 17:00 | 2022-03-15 13:00 | 2022-03-16 17:00 | 2022-03-15 14:00 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA5231751 | 1 | BAKE-QUIP PTY LTD | E block - Cafeteria kitchen - Gas grill keeps going out and oven pilot light is hard to ignite. | Equipment | Catering Equipment | 266 | Fail | Fail | 2 | 2 | 1 | 2022-03-15 14:11 | 2022-03-16 17:00 | 2022-03-30 11:30 | 2022-03-16 17:00 | 2022-03-30 12:30 |  |  | Refer to service report
MSA-DTWD | WA5231825 | 3 | AWB Co. | B6 - Level 2 - Male Staff toilet - Hinges worn out, door will not close | Building | General Building | 138.75 | Pass | Pass | -1 | -1 | 1 | 2022-03-15 15:34 | 2022-03-22 17:00 | 2022-03-16 14:30 | 2022-03-22 17:00 | 2022-03-16 15:30 |  |  | Changed to new door hinge to create bigger gap
MSA-DTAG | WA5239005 | 3 | Schindler Lifts Australia | Level 3 - Outer plastic ring on lift call button is broken – call button between lifts 2 & 3 | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-03-16 09:56 | 2022-03-23 17:00 | 2022-03-16 10:47 | 2022-03-23 17:00 | 2022-03-16 11:47 |  |  | Job completed - Replaced button on level 3
MSA-DTWD | WA5272691 | 2 | SENTINEL LOCK SERVICE PTY LTD | B2208 Library - Lock to switchboard cabinet is faulty | Security | Locksmith | 145.09 | Pass | Pass | 0 | 0 | 1 | 2022-03-18 10:08 | 2022-03-23 17:00 | 2022-03-22 14:30 | 2022-03-23 17:00 | 2022-03-22 15:30 |  |  | B Block - B2210 - Library - Lock to switchboard faulty.Lock repaired
MSA-DTWD | WA5272896 | 2 | AWB Co. | C Block - Ground - Babies room - Faulty/loose ceiling fan | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-03-18 10:27 | 2022-03-23 17:00 | 2022-03-22 07:00 | 2022-03-23 17:00 | 2022-03-22 08:00 |  |  | Attended site signed in completed jsa. Found loose fan cover on fan in babies room. Tightened bolts on cover and now working perfect.*** job completed ***
MSA-DCA | WA5273096 | 2 | Techworks Electrical | Stairwell 2 - Level 4 - in stairwell just outside Door 6 entrance - Faulty light -with LED fitting | Electrical | General Electrical | 214.55 | Pass | Pass | 0 | 0 | 1 | 2022-03-18 10:32 | 2022-03-23 17:00 | 2022-03-22 10:00 | 2022-03-23 17:00 | 2022-03-22 11:00 |  |  | completed replacement as required
MSA-DTWD | WA5273292 | 3 | AWB Co. | Single phase power point burnt out. (White 2 ) | Electrical | General Electrical | 178.36 | Pass | Pass | -1 | -1 | 1 | 2022-03-18 10:27 | 2022-03-25 17:00 | 2022-03-18 13:00 | 2022-03-25 17:00 | 2022-03-18 14:00 |  |  | Attended site and signed in. Completed JSA. Located 8g13. Found faulty burnt out gpo in room. Located switchboard and isolated. Supply and replace with new 15a gpo. Reinstated power. Tested all okay. Signed out. Job complete
MSA-MRWA | WA5273889 | 2 | SCHIAVELLO SYSTEMS (WA) PTY LTD | Level 2 - Desk 14 - The desk does not go up and down. Control panel may need resetting | Equipment | Office Appliances |  | Fail | Fail | 1 | 1 | 1 | 2022-03-18 11:05 | 2022-03-23 17:00 | 2022-03-28 07:00 | 2022-03-23 17:00 | 2022-03-28 08:00 |  |  | Work order closed out at $0 cost
MSA-DTWD | WA5293924 | 1 | AWB Co. | S block - Western Entry - Evacuation panel fault light showing / Zone FLT | Electrical | General Electrical | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-03-28 11:10 | 2022-03-29 17:00 | 2022-03-28 13:00 | 2022-03-29 17:00 | 2022-03-28 14:00 |  |  | Attended site and signed in. Completed JSA. Located faulty fire panel and found not to be power supply issue. The evac panel has a zone fault. Tried to clear and locate fault. Will need tech to come and sort of the issue as per the check and test report done this month, there is a outstanding fault not repaired. Advised site. Signed out. Job complete
MSA-DTAG | WA5294009 | 2 | AWB Co. | Floor 5 - Courtroom 58 - fluorescent light in Court 58 that keeps making a loud crackling noise | Electrical | Lighting, Internal | 194.26 | Pass | Pass | 0 | 0 | 1 | 2022-03-28 12:03 | 2022-03-31 17:00 | 2022-03-28 13:00 | 2022-03-31 17:00 | 2022-03-28 14:00 |  | WCAPPR | Attended site and signed in, completed jsa,located court room with lighting issue , proceedings in court room had been ajourned for lunch , spoke with lady in room about issue(she was the person who reported fault), she said it wasn’t making sound anymore but was this morning(due to light being warm now) , pointed to a bank of 4 lights , other lights in the room had been replaced with 600x600 led panel (with recessed mounting kits) . As lady couldn’t pin point light fitting we can either return early in the morning in the hopes that the light will make the noise again,Or return and replace all 4 or replace lights in that area 1 by one until sound disappears . Asked lady to let colleagues using that room to try and pin point issue tomorrow morning if fitting is making noise , completed paperwork , signed out Follow up required **FOLLOWED UP WITH SITE - EMAIL FROM IAIN JOHNSON ATTACHED ADVISING SITE HAVE NOT ADVISED OF ANY FURTHER ISSUES** Closed out
MSA-DCA | WA5295341 | 1 | Precise Air Group | Plant room - White chemical substance leaking around bas of boilers. Please investigate. See attache | Air Conditioning | Room Air Conditioners | 141.29 | Pass | Pass | 0 | 0 | 1 | 2022-03-29 12:49 | 2022-03-30 17:00 | 2022-03-29 13:00 | 2022-03-30 17:00 | 2022-03-29 14:00 |  |  | Inspected boiler and found no active leaks from the actual boiler, found moisture present around the flue. Suspect moisture/ rain may be getting in. We will continue to monitor on maintenance.
MSA-DTWD | WA5296063 | 1 | ACTION GLASS & ALUMINIUM | a BLOCK - AG13 - Need safety screen removed from window. | Air Conditioning | Room Air Conditioners | 130 | Pass | Pass | 0 | 0 | 1 | 2022-03-30 08:53 | 2022-03-31 17:00 | 2022-03-30 10:00 | 2022-03-31 17:00 | 2022-03-30 11:00 |  |  | ATTENDED SITE AND REMOVED SECURITY SCREEN AND LEFT ON SITE AS REQUIRED
MSA-DTWD | WA5296112 | 1 | Precise Air Group | G116 - AC not working | Air Conditioning | Room Air Conditioners | 94.19 | Fail | Fail | 0 | 0 | 1 | 2022-03-30 09:07 | 2022-03-31 17:00 | 2022-04-01 13:00 | 2022-03-31 17:00 | 2022-04-01 14:00 |  |  | Attended site signed in and gained access to reported areas. Found someone had made incorrect adjustments to control. Re adjusted and carried out functional and safety checks on the unit. Unit left operational and in working order
MSA-DTWD | WA5297519 | 1 | Equans Mechanical Services Australia | Freezer Temp gauge is flashing and beeping | Refrigeration | Refrigerators | 183.14 | Pass | Pass | 0 | 0 | 1 | 2022-03-31 10:46 | 2022-04-01 17:00 | 2022-03-31 12:15 | 2022-04-01 17:00 | 2022-03-31 13:15 |  |  | Investigated issue and found all operating as normal. Reset and cleared controller. Alarm cleared and not reactivated. Unit cycled off at set point as required.
MSA-DFES | WA5304072 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | 2nd floor - Ladies toilet - Light blown in the entrance to the ladies toilet on the second floor | Electrical | General Electrical | 149.75 | Pass | Fail | 0 | 0 | 1 | 2022-04-04 14:04 | 2022-04-07 17:00 | 2022-04-07 16:45 | 2022-04-07 17:00 | 2022-04-07 17:45 |  |  | Arrived on site at 16:45 to investigate lights out in female toilets level 2, found 2 x blown 18w 4 pin globes. Replaced both all okay. Next job on same site continued on at 17:45 for work in comcenn after hours No signature available as after hours
MSA-DTAG | WA5305390 | 1 | Sapio Pty Ltd | Custody - Control Room - Camera 124 (Jury Corridor) not operating | Security | CCTV Surveillance | 130 | Pass | Pass | 0 | 0 | 1 | 2022-04-05 15:19 | 2022-04-06 17:00 | 2022-04-06 13:00 | 2022-04-06 17:00 | 2022-04-06 14:00 |  |  | Work performed by Drake Van der Merwe (06/04/2022):Attended site. Rebooted camera. View and recording restored.
MSA-DTAG | WA5306273 | 2 | AWB Co. | YJ - Team Leader’s Officer -Light brokem, needs replacing | Electrical | General Electrical | 200.64 | Pass | Pass | -1 | -1 | 1 | 2022-04-06 11:46 | 2022-04-11 17:00 | 2022-04-07 09:15 | 2022-04-11 17:00 | 2022-04-07 10:15 |  |  | Attended site and signed in, completed jsa,spoke with security about job, located light fitting in office, fLight was flickering, set up work area, removed old tubes and starters and replaced with new, (used 2x 2ft tubes and 2x s2 starters), tested lights and now working as intended, cleaned up , packed up, completed paperwork, signed outJob complete
MSA-MRWA | WA5306539 | 1 | Automatic Fire Protection (ARA) | FIP is faulty and showing an alarm for level 8 amplifier speaker fault | Fire Protection Services | Fire Protection - Monitor System | 146.44 | Pass | Pass | 0 | 0 | 1 | 2022-04-06 14:15 | 2022-04-07 17:00 | 2022-04-07 07:00 | 2022-04-07 17:00 | 2022-04-07 08:00 |  |  | Technician Note7/04/22 EIAttended site & met with maintenance.Directed to level 8 male toilet speaker which was partially hanging from the ceiling.EWIS panel status displaying normal with no faults present.Re-fitted level 8 male toilet speaker to ceiling.EWIS system status displaying normal on departure.
MSA-DFES | WA5306576 | 2 | Go Doors | Communications Centre - Level 1 - Training room - The Automatic door faulty - see notes | Building | Automatic Doors | 310 | Pass | Pass | -1 | -1 | 1 | 2022-04-06 14:39 | 2022-04-11 17:00 | 2022-04-07 12:15 | 2022-04-11 17:00 | 2022-04-07 13:15 |  |  | Attended site, works to be completed by Sontec due to access control issue
MSA-DTWD | WA5306906 | 2 | Techworks Electrical | T-Block - Room T003 - lights not working | Electrical | General Electrical | 342.05 | Pass | Pass | 0 | 0 | 1 | 2022-04-07 08:44 | 2022-04-12 17:00 | 2022-04-11 07:00 | 2022-04-12 17:00 | 2022-04-11 08:00 |  |  | Rectified lighting issues in room T003/T004
MSA-DFES | WA5307308 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Passage Way and Kitchen - Flickering and blown lightbulb | Electrical | General Electrical | 254.55 | Pass | Pass | 0 | 0 | 1 | 2022-04-07 12:12 | 2022-04-12 17:00 | 2022-04-12 08:30 | 2022-04-12 17:00 | 2022-04-12 09:30 |  |  | Attended site at 830. Found 3 x lights have blown or are flickering. Left site to pickup parts from nearest wholesaler. Returned to site and replaced 6 x 36w t8 840 fluro and 6 x s10 starters. Tested and notified staff. Left site at 930.
MSA-DTWD | WA5323431 | 1 | ACTION GLASS & ALUMINIUM | Next to C44 - WINDOW IS BROKEN | Building | Windows | 302.8 | Pass | Pass | 0 | 0 | 1 | 2022-04-13 08:08 | 2022-04-14 17:00 | 2022-04-13 11:48 | 2022-04-14 17:00 | 2022-04-13 12:48 |  |  | ATTENDED SITEREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-990 X 730
MSA-MRWA | WA5325631 | 1 | AWB Co. | Damaged GPO | Electrical | General Electrical | 257.51 | Pass | Pass | -1 | -1 | 1 | 2022-04-14 10:51 | 2022-04-19 17:00 | 2022-04-14 13:00 | 2022-04-19 17:00 | 2022-04-14 14:00 |  |  | Attended site signed in completed jsa. found gpo pulled apart on ground. isolated circuit and re labelled as was incorrect. Replaced gpo, drilled 40mm hole in desk for cables to avoid tripping hazards as per sites instructions. All tested ok*** job completed ***
MSA-DTAG | WA5326008 | 3 | Australian HVAC Services Pty. Ltd. | Level 6 - Plantroom - Attendance required Tuesday 19 April from 7:00am - see notes below | Air Conditioning | Building HVAC Maintenance (Major Plant) | 156.98 | Pass | Pass | -1 | -1 | 1 | 2022-04-14 15:05 | 2022-04-26 17:00 | 2022-04-19 07:00 | 2022-04-26 17:00 | 2022-04-19 08:00 |  |  | Attended site and carried out isolations for fire contractor works.
MSA-DTWD | WA5367606 | 3 | Critical Fire Protection & Training | Entry Foyer - Fire Panel multiple faults over weekend | Fire Protection Services | Fire Protection - Monitor System | 114.14 | Pass | Pass | -1 | -1 | 1 | 2022-04-19 09:17 | 2022-04-27 17:00 | 2022-04-19 14:30 | 2022-04-27 17:00 | 2022-04-19 15:30 |  |  | Replaced MCP batteries in wireless MCP L4,D85,Z4.All systems normal after battery replacement.
MSA-DTWD | WA5380716 | 1 | Falcetta Plumbing and Gas | Dog Wash Area - Blocked Trough Drain ‘Drains Flush’ | Plumbing & Drainage | Drainage | 510.12 | Pass | Pass | 0 | 0 | 1 | 2022-04-22 16:06 | 2022-04-26 17:00 | 2022-04-26 13:00 | 2022-04-26 17:00 | 2022-04-26 14:00 |  |  | unblocked drain G block
MSA-DTWD | WA5384531 | 0 | BJ SYSTEMS | Security system - not communicating with the campus - education security | Security | Monitoring | 160 | Pass | Pass | 0 | 0 | 1 | 2022-04-28 13:36 | 2022-04-28 15:36 | 2022-04-28 14:30 | 2022-04-28 17:36 | 2022-04-28 15:30 |  |  | Attend site, checked alarm as requested, sort a test alarm for monitoring, all working ok. Left site
MSA-DTWD | WA5389927 | 1 | ECO PLUMBING AND GAS PTY LTD | C20- Ladies toilets blocked and overflowed | Plumbing & Drainage | Toilets/Cisterns | 141.28 | Pass | Pass | 0 | 0 | 1 | 2022-05-02 08:56 | 2022-05-03 17:00 | 2022-05-02 16:00 | 2022-05-03 17:00 | 2022-05-02 17:00 |  |  | Cleared blockage using plunger
MSA-DTAG | WA5390985 | 1 | AAA Ability Locksmiths | Cell 1 Lock Fault – lock broken and cell unable to open | Security | Locksmith | 322.26 | Pass | Pass | 0 | 0 | 1 | 2022-05-02 15:45 | 2022-05-03 17:00 | 2022-05-03 07:00 | 2022-05-03 17:00 | 2022-05-03 08:00 |  |  | Attend site, replace broken bolt thrower, service and repair lock.
MSA-DTWD | WA5392522 | 1 | Falcetta Plumbing and Gas | EG19 - Blocked drains in male toilets | Plumbing & Drainage | Drainage | 453.88 | Pass | Pass | 0 | 0 | 1 | 2022-05-03 10:26 | 2022-05-04 17:00 | 2022-05-03 16:00 | 2022-05-04 17:00 | 2022-05-03 17:00 |  |  | unblocked drain with Drainsflush
MSA-DCA | WA5392716 | 1 | Techworks Electrical | Ground - External - Museum Plaza (opposite Polly Café) - 2 x "lollipop" lights not working | Electrical | Lighting, External | 214.55 | Pass | Pass | 0 | 0 | 1 | 2022-05-03 11:49 | 2022-05-04 17:00 | 2022-05-03 14:30 | 2022-05-04 17:00 | 2022-05-03 15:30 |  |  | Found RCBO to be tripped, reset breaker and circuit and lights are holding fine.
MSA-DTAG | WA5393633 | 1 | Schindler Lifts Australia | Lifts - Lift 3 - is showing “out of service | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-05-04 09:22 | 2022-05-05 17:00 | 2022-05-04 10:45 | 2022-05-05 17:00 | 2022-05-04 11:45 |  |  | Tech working on lift maintenance
MSA-DTWD | WA5393853 | 2 | ECO PLUMBING AND GAS PTY LTD | D015.1 - toilet wont stop running - losing water | Plumbing & Drainage | Toilets/Cisterns | 173.42 | Pass | Pass | -1 | -1 | 1 | 2022-05-04 10:44 | 2022-05-09 17:00 | 2022-05-05 14:30 | 2022-05-09 17:00 | 2022-05-05 15:30 |  |  | Cleaned out inlet valve and replaced one
MSA-DTWD | WA5396846 | 3 | Protek 24/7 Building & Maintenance | B Block - Doors not closing properly, hinges need to be adjusted - See notes below | Building | Doors | 119.5 | Pass | Pass | 0 | 0 | 1 | 2022-05-06 11:46 | 2022-05-13 17:00 | 2022-05-10 10:00 | 2022-05-13 17:00 | 2022-05-10 11:00 |  |  | Adjusted hinges to doors
MSA-DTWD | WA5398687 | 3 | AWB Co. | Light Switch not working (lights stay on) | Electrical | Lighting, Internal | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-05-09 12:01 | 2022-05-16 17:00 | 2022-05-16 14:30 | 2022-05-16 17:00 | 2022-05-16 15:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located switch, switch had mech replaced already, loosened switch a half turn and switch moved a lot better , completed paperwork, packed up, signed out, **job completed **
MSA-DTAG | WA5399213 | 3 | AHS Services WA Pty Ltd (Anchor) | L3 and 5 Missing a sink hole cover/strainer for water fountain | Plumbing & Drainage | Drainage | 143.03 | Pass | Pass | -1 | -1 | 1 | 2022-05-09 18:38 | 2022-05-16 17:00 | 2022-05-11 07:45 | 2022-05-16 17:00 | 2022-05-11 08:45 |  |  | Installed 2x new plug and wastes in drink fountain
MSA-DTAG | WA5399222 | 3 | Midolo Building Services | L5 Drink fountain outside of court 54 Veneer peeling off panel above drink fountain | Building | Internal Walls | 206.27 | Pass | Pass | -1 | -1 | 1 | 2022-05-09 19:10 | 2022-05-16 17:00 | 2022-05-12 10:45 | 2022-05-16 17:00 | 2022-05-12 11:45 |  |  | PEELING VENEER PANEL HAS BEEN REPAIRED
MSA-DTWD | WA5407950 | 3 | Protek 24/7 Building & Maintenance | 3A Electrical store - Water leak into store. Hole in ceiling | Building | Ceiling | 196 | Pass | Pass | -1 | -1 | 1 | 2022-05-11 15:21 | 2022-05-18 17:00 | 2022-05-12 14:30 | 2022-05-18 17:00 | 2022-05-12 15:30 |  |  | No Response from Client - email sent to Breakdown/Reactive Maintenance (WASC) (Pool email) wasc@programmed.com.au;Unable to Obtain signatures due to no response BRaf Rejected $3677.96 + GST and work to date invoiced
MSA-DTWD | WA5417355 | 1 | BAKE-QUIP PTY LTD | E58 Kitchen - Combi Oven is beeping - no water coming through | Equipment | Catering Equipment | 327.5 | Pass | Pass | 0 | 0 | 1 | 2022-05-13 12:15 | 2022-05-16 17:00 | 2022-05-13 13:00 | 2022-05-16 17:00 | 2022-05-13 14:00 |  |  | REFER TO SERVICE REPORT.
MSA-DTWD | WA5417736 | 2 | Lane's Plumbing | BATHROOMS A - Tap are faulty ---- loose | Plumbing & Drainage | Materials |  | Pass | Pass | 0 | 0 | 1 | 2022-05-13 15:09 | 2022-05-18 17:00 | 2022-05-17 13:00 | 2022-05-18 17:00 | 2022-05-17 14:00 |  |  | Repairs to loose taps
MSA-DTWD | WA5454841 | 2 | Diamond Lock & Security | D Block - Storage Building - Damaged Door lock | Security | Locksmith |  | Fail | Fail | 1 | 1 | 1 | 2022-05-17 15:09 | 2022-05-20 17:00 | 2022-05-26 11:30 | 2022-05-20 17:00 | 2022-05-26 12:30 |  |  | Installed dead bolt
MSA-DCA | WA5454902 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 4 - Female Toilet - Cubicle to 1st regular cubicle fails to flush | Plumbing & Drainage | Toilets/Cisterns | 174.78 | Pass | Pass | -1 | -1 | 1 | 2022-05-17 16:18 | 2022-05-24 17:00 | 2022-05-20 12:15 | 2022-05-24 17:00 | 2022-05-20 13:15 |  |  | Replaced fsulty inlet valve
MSA-DTAG | WA5460054 | 2 | Midolo Building Services | Level 8 - Court 82 - 2x lecterns to be tethered to desks with wire lanyards | Building | General Building | 167.49 | Fail | Fail | 1 | 1 | 1 | 2022-05-18 10:33 | 2022-05-23 17:00 | 2022-05-27 07:00 | 2022-05-23 17:00 | 2022-05-27 08:00 |  |  | LECTURNS SECURED
MSA-DTWD | WA5462488 | 3 | AWB Co. | Exterior Front Entrance - Repair Flag pole - cables no longer working | Building | General Building | 127.5 | Fail | Fail | 1 | 1 | 1 | 2022-05-19 15:36 | 2022-05-26 17:00 | 2022-06-03 07:00 | 2022-05-26 17:00 | 2022-06-03 08:00 |  |  | inspected flag poleno works completed - nil JSA rquiredBRAF declined - close costs to date
MSA-DFES | WA5462514 | 2 | ADVANCED LOCK & KEY | Back door - combination lock is faulty and fails to open. | Security | Locksmith | 540 | Pass | Pass | 0 | 0 | 1 | 2022-05-19 15:45 | 2022-05-24 17:00 | 2022-05-24 10:00 | 2022-05-24 17:00 | 2022-05-24 11:00 |  |  | Time onsite 1000-1100 Attend to replace faulty 530DX and rebuild to suit ‘night latch’ application to rear door. Access code CY0583
MSA-DTWD | WA5470213 | 1 | Techworks Plumbing | Canteen Area - Mens Toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 133.75 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 08:55 | 2022-05-24 17:00 | 2022-05-23 10:00 | 2022-05-24 17:00 | 2022-05-23 11:00 |  |  | Unblocked canteen toilet
MSA-DTWD | WA5470319 | 1 | AWB Co. | A 16 Male toilet - Faulty light switch | Electrical | General Electrical | 174.38 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 09:37 | 2022-05-24 17:00 | 2022-05-24 07:00 | 2022-05-24 17:00 | 2022-05-24 08:00 |  |  | Attended site signed in jsa completed. located faulty switch by staff. Isolated circuit and replaced with brand new mech. all tested ok and fine*** job completed ***
MSA-DTWD | WA5472139 | 1 | Protek 24/7 Building & Maintenance | E58 - Roof Leak - see notes below | Roofing | Metal Roofing | 212.5 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 14:42 | 2022-05-24 17:00 | 2022-05-24 11:30 | 2022-05-24 17:00 | 2022-05-24 12:30 |  |  | Repair Roof leak - E58
MSA-DCA | WA5472201 | 1 | Protek 24/7 Building & Maintenance | Near Technical office - Water pooling on floor from ceiling (level 2) | Building | General Building | 196 | Pass | Pass | 0 | 0 | 1 | 2022-05-23 15:32 | 2022-05-24 17:00 | 2022-05-24 14:30 | 2022-05-24 17:00 | 2022-05-24 15:30 |  | WCAPPR | Repair water leak in ceiling
MSA-DTAG | WA5472747 | 1 | Midolo Building Services | Courtroom 2 - Door slamming shut quickly - see notes below | Building | Doors | 144.92 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 10:09 | 2022-05-25 17:00 | 2022-05-24 13:45 | 2022-05-25 17:00 | 2022-05-24 14:45 |  |  | ADJUSTMENT MADE TO DOOR CLOSER
MSA-DTWD | WA5472853 | 1 | ACTION GLASS & ALUMINIUM | Block C - External Windows damaged - See notes below | Glazing | Window Glass | 161.9 | Pass | Pass | 0 | 0 | 1 | 2022-05-24 11:05 | 2022-05-25 17:00 | 2022-05-25 12:15 | 2022-05-25 17:00 | 2022-05-25 13:15 |  | WACCES | Repair fly screen need to return with new lock*****update - programmed has requested for us to invoice out for works done and close off job****
MSA-DTAG | WA5476040 | 2 | Midolo Building Services | Sally Port – leaking from the roof down the internal wall when we get a down pour of rain | Roofing | Metal Roofing | 146.9 | Fail | Fail | 0 | 0 | 1 | 2022-05-25 10:03 | 2022-05-30 17:00 | 2022-05-31 09:15 | 2022-05-30 17:00 | 2022-05-31 10:15 |  |  | roof flashing resealed
MSA-DTAG | WA5480010 | 3 | Midolo Building Services | Ground Floor - Registry - chair in the front row of the registry waiting area is broken | Furniture | Office Furniture | 144.92 | Pass | Pass | -1 | -1 | 1 | 2022-05-27 14:24 | 2022-06-03 17:00 | 2022-05-30 07:45 | 2022-06-03 17:00 | 2022-05-30 08:45 |  |  | repaired & secured chair
MSA-DTAG | WA5481152 | 2 | Schindler Lifts Australia | Ground floor lift - Lift 4 - out of order | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-05-30 11:15 | 2022-06-02 17:00 | 2022-05-31 16:00 | 2022-06-02 17:00 | 2022-05-31 17:00 |  |  | Lift on exclusive service via key switch with no errors in the error log. Turned key switch back to normal.
MSA-DFES | WA5481545 | 1 | SONTEC WA PTY LTD | Ground Floor Entry - Stair 5 - Automatic Lock Door is not locking | Security | Locksmith | 602.68 | Pass | Pass | 0 | 0 | 1 | 2022-05-30 14:03 | 2022-05-31 17:00 | 2022-05-31 09:15 | 2022-05-31 17:00 | 2022-05-31 10:15 |  |  | 31/5/22 - Dylan ParslowFound solonoid on lock faulty.Replaced electric strike and tested, all ok.
MSA-DTWD | WA5482157 | 2 | SENTINEL LOCK SERVICE PTY LTD | Ground Level - Internal passage door to Customer Service - Door wont lock | Security | Locksmith | 95.09 | Pass | Pass | 0 | 0 | 1 | 2022-05-31 09:23 | 2022-06-03 17:00 | 2022-05-31 10:00 | 2022-06-03 17:00 | 2022-05-31 11:00 |  |  | Customer Service door - internal - will not lock.Lock repaired
MSA-DTWD | WA5487392 | 2 | SENTINEL LOCK SERVICE PTY LTD | Ground - Front Door - Door lock not operating all the time | Security | Locksmith | 95.09 | Pass | Pass | -1 | -1 | 1 | 2022-06-01 14:47 | 2022-06-07 17:00 | 2022-06-03 08:30 | 2022-06-07 17:00 | 2022-06-03 09:30 |  |  | Front door - lock not operating all the time.Lock checked.
MSA-DTWD | WA5487405 | 3 | AWB Co. | 2 lights not working | Electrical | Lighting, Internal | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-06-01 14:53 | 2022-06-09 17:00 | 2022-06-08 13:45 | 2022-06-09 17:00 | 2022-06-08 14:45 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, located room and removed all faulty tubes and starters , replaced with new, tested lights and all working as intended, put old tubes in disposal bins on site, cleaned up, packed up, completed paperwork, signed out ,all materials supplied by site ***job completed***
MSA-DCA | WA5487992 | 2 | Protek 24/7 Building & Maintenance | Jubilee Bld - Ground Level - cleaners storeroom - loose door handle | Building | General Building | 204.28 | Pass | Pass | 0 | 0 | 1 | 2022-06-02 09:40 | 2022-06-08 17:00 | 2022-06-07 11:30 | 2022-06-08 17:00 | 2022-06-07 12:30 |  |  | Repair Loose door handle - Cleaners store room
MSA-DFES | WA5488094 | 2 | Protek 24/7 Building & Maintenance | Level 2 - Stores - Along back wall of stores - Leak in roof | Roofing | Metal Roofing | 119.5 | Pass | Pass | 0 | 0 | 1 | 2022-06-02 10:28 | 2022-06-08 17:00 | 2022-06-07 07:00 | 2022-06-08 17:00 | 2022-06-07 08:00 |  |  | Repair roof leak along back wall of stores
MSA-DTWD | WA5496790 | 3 | AWB Co. | F block - Seminal Room 2 - 2 x lights out | Electrical | General Electrical | 194.26 | Pass | Pass | 0 | 0 | 1 | 2022-06-09 12:34 | 2022-06-16 17:00 | 2022-06-13 11:30 | 2022-06-16 17:00 | 2022-06-13 12:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located 2x faulty 5ft fittings weren’t working, replaced tubes and starters. Lights now working as intended. Took pictures. Found a further 2x 4ft fittings faulty. Replaced tubes and starters in both fittings. Both are now working as intended, took pictures, completed paperwork. Signed out.Job complete
MSA-MRWA | WA5499137 | 1 | GPS Plumbing & Gas Services PtyLtd | Disabled toilet - left hand toilet - blocked | Plumbing & Drainage | Toilets/Cisterns | 134.78 | Pass | Pass | 0 | 0 | 1 | 2022-06-10 10:25 | 2022-06-13 17:00 | 2022-06-10 13:00 | 2022-06-13 17:00 | 2022-06-10 14:00 |  |  | Clear blocked toilet
MSA-DTWD | WA5499758 | 2 | AWB Co. | 10G72 - Light outside classroom not working | Electrical | General Electrical | 143.26 | Pass | Pass | 0 | 0 | 1 | 2022-06-10 14:09 | 2022-06-15 17:00 | 2022-06-13 11:30 | 2022-06-15 17:00 | 2022-06-13 12:30 |  |  | Attended site signed in jsa completed. Located faulty light in hallway. Turned overide on and light was out above classroom door. Found the globe was broken so replaced with new and now works fine. *** job completed ***
MSA-DTWD | WA5511771 | 2 | AHS Services WA Pty Ltd (Anchor) | Blocked toilet A Block level 1 Male East End | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 08:51 | 2022-06-16 17:00 | 2022-06-14 09:15 | 2022-06-16 17:00 | 2022-06-14 10:15 |  |  | Cleared blocked toilet
MSA-DTWD | WA5512193 | 3 | AWB Co. | C003-1 - 8 x lights out | Electrical | Lighting, Internal | 245.45 | Pass | Pass | 0 | 0 | 1 | 2022-06-13 14:50 | 2022-06-20 17:00 | 2022-06-20 07:00 | 2022-06-20 17:00 | 2022-06-20 08:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job, located faulty lighting and made list of parts, went to wholesaler to pick up lamps like for like, returned to site and removed old lamps, replaced with new, tested all lights and they are working as intended , completed paperwork,packed up, signed out ***job complete**
MSA-DFES | WA5513799 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 2 - Ladies Toilets - Blocked toilet in ladies toilet end cubicle | Plumbing & Drainage | Toilets/Cisterns | 133.45 | Pass | Pass | 0 | 0 | 1 | 2022-06-14 13:20 | 2022-06-17 17:00 | 2022-06-16 07:00 | 2022-06-17 17:00 | 2022-06-16 08:00 |  |  | Attended site for level two female toilets blocked in the end cubicle I found too much toilet paper has been used And has caused a blockage I have cleared the blockage and tested everything is now working correctly cleaned up
MSA-MRWA | WA5521763 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | See PFM for location - Failed Computer port - See notes below | Equipment | Electrical Equipment | 222.82 | Pass | Pass | 0 | 0 | 1 | 2022-06-15 10:48 | 2022-06-20 17:00 | 2022-06-20 07:00 | 2022-06-20 17:00 | 2022-06-20 08:00 |  |  | Inspected data points in office and tested. Replaced with clipsal mechs from car. Tested again and passed cat 6 testing.
MSA-DTWD | WA5534660 | 2 | AWB Co. | External - Replace sensor unit G block security lights | Electrical | Lighting, External | 235.89 | Pass | Pass | 0 | 0 | 1 | 2022-06-16 12:54 | 2022-06-21 17:00 | 2022-06-21 14:30 | 2022-06-21 17:00 | 2022-06-21 15:30 |  |  | Attended site signed in JSA completed. Found faulty pe cell sensor in G block. Had one in stock and replaced tested and confirmed operational see photos attached.*** job completed ***
MSA-DTWD | WA5534696 | 2 | AWB Co. | Faulty Security lights - Room J9 & J10 | Electrical | Lighting, Internal | 199.31 | Pass | Pass | 0 | 0 | 1 | 2022-06-16 13:26 | 2022-06-21 17:00 | 2022-06-21 07:00 | 2022-06-21 17:00 | 2022-06-21 08:00 |  |  | Attended site signed in completed jsa. Located faulty light fitting in j block. Replaced tube and starter. Tested sensor. Everything now working as intended. Took picture. Completed paperwork.Job complete
MSA-DTWD | WA5562758 | 1 | OTIS ELEVATOR COMPANY PTY LTD | Ground floor - between lift 1 and 2 - lift button faulty | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-06-20 09:45 | 2022-06-21 17:00 | 2022-06-20 12:40 | 2022-06-21 17:00 | 2022-06-20 13:40 |  |  | Repaired under warranty - No charges for attendance
MSA-MRWA | WA5564703 | 2 | AWB Co. | See Amanda or Chantelle for location - Broken data plate mounting block | Building | General Building | 139.12 | Pass | Pass | 0 | 0 | 1 | 2022-06-21 11:47 | 2022-06-24 17:00 | 2022-06-22 08:30 | 2022-06-24 17:00 | 2022-06-22 09:30 |  |  | Attended site signed in jsa completed. Located data point as per instructions from craig. Replaced data mounting block*** job is completed ***
MSA-MRWA | WA5565938 | 2 | SCHIAVELLO SYSTEMS (WA) PTY LTD | Level 2 - Desk 20 - Desk 20 Error Message E70 | Building | General Building |  | Pass | Pass | -1 | -1 | 1 | 2022-06-22 12:55 | 2022-06-27 17:00 | 2022-06-23 07:00 | 2022-06-27 17:00 | 2022-06-23 08:00 |  |  | to be closes out at $0 cost
MSA-DCA | WA5565999 | 3 | Techworks Electrical | Area 2 of the bulk wet store - Emergency Exit light is not working | Electrical | Emergency & Exit Lighting | 125.59 | Pass | Pass | 0 | 0 | 1 | 2022-06-22 13:37 | 2022-06-29 17:00 | 2022-06-28 16:00 | 2022-06-29 17:00 | 2022-06-28 17:00 |  |  | Inspected exit. Exit has been reported twice. Exit has been replaced on another work order
MSA-DTWD | WA5566533 | 3 | SENTINEL LOCK SERVICE PTY LTD | Main Entrance - Faulty door lock | Security | Locksmith | 162.45 | Pass | Pass | 0 | 0 | 1 | 2022-06-23 09:15 | 2022-06-30 17:00 | 2022-06-29 08:30 | 2022-06-30 17:00 | 2022-06-29 09:30 |  |  | Main entrance - faulty door lock.Lock repaired - new keys cut.
MSA-DTWD | WA5567114 | 2 | Protek 24/7 Building & Maintenance | Ground Floor -Kindy bathroom - Door handle Faulty | Building | Doors | 231.8 | Fail | Fail | 0 | 0 | 1 | 2022-06-23 14:59 | 2022-06-28 17:00 | 2022-06-29 13:00 | 2022-06-28 17:00 | 2022-06-29 14:00 |  |  | Replaced door handle and striker plate
MSA-DCA | WA5568596 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Lift 1- Public lift - Ground Floor - not working at all | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 1 | 2022-06-27 07:22 | 2022-06-27 09:22 | 2022-06-27 11:30 | 2022-06-27 11:22 | 2022-06-27 12:30 |  |  | no charge - warranty repair
MSA-DTWD | WA5568821 | 2 | AWB Co. | Heat Fan Faulty | Electrical | General Electrical | 135.76 | Pass | Pass | 0 | 0 | 1 | 2022-06-27 09:15 | 2022-06-30 17:00 | 2022-06-27 13:00 | 2022-06-30 17:00 | 2022-06-27 14:00 |  |  | Attended site signed in jsa completed.heater faulty and site requested removal. Put 4 blank plates in to cover holes. Plates left with site to be put on once wall is paintedJob completed
MSA-DTAG | WA5568956 | 0 | Go Doors | Details Auto Court Sliding Door jamming half way. Will not close fully. | Building | Automatic Doors | 305 | Pass | Pass | 0 | 0 | 1 | 2022-06-27 10:40 | 2022-06-27 12:40 | 2022-06-27 11:30 | 2022-06-27 14:40 | 2022-06-27 12:30 |  |  | Completed works. Please see attachments.
MSA-DCA | WA5568986 | 3 | Protek 24/7 Building & Maintenance | Rain dust has come down the side of buildings - See notes below | Building | General Building | 121.26 | Pass | Pass | -1 | -1 | 1 | 2022-06-27 10:43 | 2022-07-04 17:00 | 2022-06-30 10:45 | 2022-07-04 17:00 | 2022-06-30 11:45 |  |  | Inspected - dirt caused by rain dust down side of the building BRAF DECLINED
MSA-DTAG | WA5570211 | 2 | MALCO FLOORING PTY LTD | Court 32 - Carpet tile in jury seated area is lifting | Flooring | Carpet | 225 | Fail | Fail | 1 | 1 | 1 | 2022-06-28 08:23 | 2022-07-01 17:00 | 2022-07-11 07:00 | 2022-07-01 17:00 | 2022-07-11 08:00 |  | WACCES | Court 32 Carpet tile in jury seated area is liftingRefixed lifting carpet tiles to jury seated area level 3
MSA-DTWD | WA5570689 | 2 | BAKE-QUIP PTY LTD | Turbo fan oven internal glass door pannel broken & door seal | Equipment | Catering Equipment | 355.8 | Fail | Fail | 3 | 3 | 1 | 2022-06-28 13:40 | 2022-07-01 17:00 | 2022-07-19 16:00 | 2022-07-01 17:00 | 2022-07-19 17:00 |  |  | Refer to service report
MSA-DTWD | WA5571754 | 3 | ECO PLUMBING AND GAS PTY LTD | Level G - Room C45 - C45 Washing machine drain keeps overflowing | Plumbing & Drainage | Drainage | 141.28 | Pass | Pass | 0 | 0 | 1 | 2022-06-29 11:58 | 2022-07-06 17:00 | 2022-07-06 09:35 | 2022-07-06 17:00 | 2022-07-06 10:35 |  |  | cleared blockage
MSA-DTAG | WA5572127 | 2 | Sapio Pty Ltd | Level 24 - Doors playing up, Delay after swipe to get into floor - See notes below | Security | Access Control | 120 | Pass | Pass | 0 | 0 | 1 | 2022-06-28 15:00 | 2022-07-01 17:00 | 2022-06-29 17:30 | 2022-07-01 17:00 | 2022-06-29 18:30 |  |  | Resynced controller to server and tested.
MSA-DFES | WA5572714 | 1 | SONTEC WA PTY LTD | COMCEN - Auto Button - to open entrance into Comcen is faulty and not workiing | Security | Access Control | 310 | Pass | Pass | 0 | 0 | 1 | 2022-06-30 09:47 | 2022-07-01 17:00 | 2022-06-30 14:30 | 2022-07-01 17:00 | 2022-06-30 15:30 |  |  | 30/6/22 - Dean SimpsonTested switch and controller.Rebooted controller and tested, all ok.
MSA-DCA | WA5572804 | 2 | Techworks Electrical | Level 2 - VMO - Exit light is out (green door) | Electrical | Emergency & Exit Lighting | 357.73 | Pass | Pass | 0 | 0 | 1 | 2022-06-30 10:52 | 2022-07-05 17:00 | 2022-07-04 13:00 | 2022-07-05 17:00 | 2022-07-04 14:00 |  |  | Replaced faulty exit sign
MSA-MRWA | WA5582939 | 2 | AWB Co. | Level 1 - South East Corridor - 3 lights out above pictures - See notes | Electrical | Lighting, Internal | 136.06 | Pass | Pass | 0 | 0 | 1 | 2022-07-04 09:18 | 2022-07-07 17:00 | 2022-07-06 05:30 | 2022-07-07 17:00 | 2022-07-06 06:30 |  |  | Attended site signed in jsa completed. went to level 1 south east corridor and found the lights mentioned in the work order above picture on wall. All 3 lights are operational. no need to replace since working halogen gu10’sCalled danika to confirm she said if everything is ok on that level to close job off completejob is completed
MSA-DFES | WA5584975 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor eastern side - Printing/Utility area by RCA - faulty lighting | Electrical | Lighting, Internal | 136.22 | Pass | Pass | 0 | 0 | 1 | 2022-07-05 11:37 | 2022-07-12 17:00 | 2022-07-11 10:45 | 2022-07-12 17:00 | 2022-07-11 11:45 |  |  | Continued onsite at 10:00 to investigate lights not working located SOC printing / utility area. Found light had been replaced under another job and was working. Replaced seperate light in same area which wasn’t working. Tested light after replacing tubes and all good. Continued onsite at 10:45
MSA-DTWD | WA5587380 | 2 | ADVANCED LOCK & KEY | Services Room Office 1258-Repair locks to cupboard -see notes | Security | Locksmith | 230 | Pass | Pass | 0 | 0 | 1 | 2022-07-07 07:34 | 2022-07-11 17:00 | 2022-07-11 11:55 | 2022-07-11 17:00 | 2022-07-11 12:55 |  |  | 11:55-12:55 Made keys to cabinet lock 3x keys
MSA-DTWD | WA5588123 | 2 | SENTINEL LOCK SERVICE PTY LTD | Faulty Lock on office door | Security | Locksmith | 104.47 | Pass | Pass | 0 | 0 | 1 | 2022-07-07 13:18 | 2022-07-12 17:00 | 2022-07-12 09:15 | 2022-07-12 17:00 | 2022-07-12 10:15 |  |  | B2437 - Faulty lock on office door.Lock repaired.
MSA-DTWD | WA5589440 | 2 | AWB Co. | Fault description Guillotine has lose exposed wiring @ the back of the foot pedal. | Electrical | General Electrical | 202.43 | Pass | Pass | 0 | 0 | 1 | 2022-07-08 12:59 | 2022-07-13 17:00 | 2022-07-11 10:45 | 2022-07-13 17:00 | 2022-07-11 11:45 |  |  | Attended site signed in jsa completed. Found cables exposed as shown by frank. Re terminated gland and attached jackchain from pedal to box to prevent further issues. Job completed
MSA-DTWD | WA5589640 | 3 | Falcetta Plumbing and Gas | Block 6 - Cleaners room - Sink Blocked | Plumbing & Drainage | Drainage | 453.88 | Pass | Pass | -1 | -1 | 1 | 2022-07-08 15:12 | 2022-07-15 17:00 | 2022-07-11 10:00 | 2022-07-15 17:00 | 2022-07-11 11:00 |  | WCAPPR | drainsflush unblocked cleaners sink
MSA-DCA | WA5597029 | 0 | Protek 24/7 Building & Maintenance | Orchestral - broken stair | Building | Internal Walls | 194.54 | Pass | Pass | 0 | 0 | 1 | 2022-07-11 11:54 | 2022-07-11 13:54 | 2022-07-11 13:45 | 2022-07-11 15:54 | 2022-07-11 14:45 |  |  | Temp fix to broken stair
MSA-DTAG | WA5604043 | 2 | AHS Services WA Pty Ltd (Anchor) | Below Basement - Hot water pressure valve leaking | Plumbing & Drainage | Water | 227.67 | Fail | Fail | 1 | 1 | 1 | 2022-07-12 15:20 | 2022-07-15 17:00 | 2022-07-19 08:30 | 2022-07-15 17:00 | 2022-07-19 09:30 |  |  | Replaced faulty pressure relief valve on hwu
MSA-DTAG | WA5613674 | 3 | AHS Services WA Pty Ltd (Anchor) | Court 3 Waiting Room - Water can be heard running from the bathrooms from the courtroom | Plumbing & Drainage | Water | 249.68 | Pass | Pass | 0 | 0 | 1 | 2022-07-14 14:56 | 2022-07-21 17:00 | 2022-07-18 10:00 | 2022-07-21 17:00 | 2022-07-18 11:00 |  |  | Unable to locate any noise in court 3 but found the aerator missing in the disabled toilet causing a loud noise.Picked up and fitted new aerator.
MSA-DTWD | WA5627866 | 3 | AHS Services WA Pty Ltd (Anchor) | A110c - Female toilet - student services - Both cisterns leaking onto the floor- boot seals leaking | Plumbing & Drainage | Toilets/Cisterns | 156.51 | Pass | Pass | -1 | -1 | 1 | 2022-07-15 08:45 | 2022-07-22 17:00 | 2022-07-18 08:30 | 2022-07-22 17:00 | 2022-07-18 09:30 |  |  | Replaced flush cones to toilets, trip to supplier required.
MSA-DTWD | WA5628262 | 1 | AHS Services WA Pty Ltd (Anchor) | A110c : Female toilet : student services | Plumbing & Drainage | Toilets/Cisterns | 101.35 | Pass | Pass | 0 | 0 | 1 | 2022-07-15 12:47 | 2022-07-18 17:00 | 2022-07-18 07:00 | 2022-07-18 17:00 | 2022-07-18 08:00 |  |  | Cleared blocked toilet
MSA-DTWD | WA5660332 | 2 | AWB Co. | Child Care - Baby room kitchenette - Faulty electrical power point (GPO) | Electrical | General Electrical | 160.01 | Pass | Pass | 0 | 0 | 1 | 2022-07-19 09:01 | 2022-07-22 17:00 | 2022-07-22 07:00 | 2022-07-22 17:00 | 2022-07-22 08:00 |  | WACCES | Attended site signed in jsa completed. Mike showed me faulty powerpoint as it was cutting in and out with the active. Replaced with new double gpo and now working fine.Job completed
MSA-MRWA | WA5660883 | 3 | AWB Co. | Ground Floor - Office Male Toilets - Failed light fitting T5 | Electrical | Lighting, Internal | 233.06 | Pass | Pass | -1 | -1 | 1 | 2022-07-19 13:18 | 2022-07-26 17:00 | 2022-07-22 13:00 | 2022-07-26 17:00 | 2022-07-22 14:00 |  |  | Attended site signed in jsa completed. Spoke to craig about light playing up. Craig had replaced tube and light still would not work. removed light and replaced with new 28w electronic ballast from stock. Light now works and operational.Job completed
MSA-DTWD | WA5661052 | 1 | ECO PLUMBING AND GAS PTY LTD | Air con hearting cycle not working - gas heater - will require 2 people to access roof | Plumbing & Drainage | Water | 141.28 | Pass | Pass | 0 | 0 | 1 | 2022-07-19 15:19 | 2022-07-20 17:00 | 2022-07-20 13:00 | 2022-07-20 17:00 | 2022-07-20 14:00 |  |  | Reset unit and organised service agent to look into more
MSA-DTWD | WA5673120 | 3 | AHS Services WA Pty Ltd (Anchor) | N231 - Shower head missing | Plumbing & Drainage | Water | 151.27 | Pass | Pass | -1 | -1 | 1 | 2022-07-20 12:22 | 2022-07-27 17:00 | 2022-07-21 15:15 | 2022-07-27 17:00 | 2022-07-21 16:15 |  |  | Replaced missing shower head.
MSA-DTAG | WA5673384 | 3 | AWB Co. | Detention - Exit - Exit sign is flashing | Electrical | Emergency & Exit Lighting | 308.04 | Pass | Pass | 0 | 0 | 1 | 2022-07-20 14:40 | 2022-07-27 17:00 | 2022-07-25 07:00 | 2022-07-27 17:00 | 2022-07-25 08:00 |  |  | Attended site and signed in. Completed JSA. Located flashing exit light. Went to wholesaler for part. Returned to site. Replaced exit light. Working as intended. Took picture. Completed paperwork. Signed out. Job complete
MSA-DCA | WA5673992 | 1 | Techworks Electrical | lunch room ground Jubilee-light switch needs to be repaired | Electrical | Lighting, Internal | 684.11 | Pass | Pass | 0 | 0 | 1 | 2022-07-21 08:08 | 2022-07-22 17:00 | 2022-07-21 14:30 | 2022-07-22 17:00 | 2022-07-21 15:30 |  |  | Light applications found issue on the program, rectified.
MSA-DTWD | WA5674212 | 2 | Water2water Pty Ltd | S-Block - Ground Floor -Kitchen area - the billie Boil has no hot water | Plumbing & Drainage | HWS/Units Electric & Gas | 173.82 | Pass | Pass | 0 | 0 | 1 | 2022-07-21 09:43 | 2022-07-26 17:00 | 2022-07-25 09:15 | 2022-07-26 17:00 | 2022-07-25 10:15 |  |  | Unit found in ‘locked off’ mode. Changed to ‘locked on’ and readjusted settings for optimal use.Boiled water, checked and tested unit operation, all ok.
MSA-DFES | WA5674677 | 3 | AWB Co. | L1 front door-has bottom weather strip fallen off | Building | Doors | 137.19 | Pass | Pass | 0 | 0 | 1 | 2022-07-21 13:18 | 2022-07-28 17:00 | 2022-07-26 07:00 | 2022-07-28 17:00 | 2022-07-26 08:00 |  |  | Attended site and found that job had already been doneJSA not required as no works undertaken
MSA-DTAG | WA5675248 | 1 | AWB Co. | Level 1 -DOC office - Broken light – flickering and making a noise- See notes below | Electrical | Lighting, Internal | 152.79 | Pass | Pass | 0 | 0 | 1 | 2022-07-22 09:04 | 2022-07-25 17:00 | 2022-07-25 09:15 | 2022-07-25 17:00 | 2022-07-25 10:15 |  |  | Attended site and signed in, completed jsa,spoke with fm about issue, went up to level 1 and found the light , light needed tubes and starters replaced, noise was coming from tube tiring to fire up, replaced tubes and starters and light now working as intended , completed paperwork, packed up, signed out **job completed**
MSA-DTAG | WA5675504 | 2 | Midolo Building Services | Male Public Toilets - Basement-Soap Dispenser is broken and leaking - see notes | Building | Internal Walls | 210.83 | Pass | Pass | 0 | 0 | 1 | 2022-07-22 11:16 | 2022-07-27 17:00 | 2022-07-27 07:45 | 2022-07-27 17:00 | 2022-07-27 08:45 |  |  | NEW SOAP DISPENSER INSTALLED
MSA-DTAG | WA5675566 | 1 | Sapio Pty Ltd | Custody - 1 Screen in custoday not working | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-07-22 11:54 | 2022-07-25 17:00 | 2022-07-22 14:30 | 2022-07-25 17:00 | 2022-07-22 15:30 |  |  | Checked reported fault. Adjusted monitor view for CCTV System, tested OK.
MSA-DTWD | WA5675857 | 2 | Equans Mechanical Services Australia | Ground floor - A Block - AF17 - Aircon control panel showing faults on ALL Unit 2 aircon units | Air Conditioning | Room Air Conditioners | 129.51 | Pass | Pass | 0 | 0 | 1 | 2022-07-22 14:39 | 2022-07-27 17:00 | 2022-07-25 12:15 | 2022-07-27 17:00 | 2022-07-25 13:15 |  |  | Arrived on site, signed in, gathered tools and equipment. Started on fault find, unable to locate area. Checked with Karina, found wrong room reported. Located correctly and found executive sweet offices is shared by classrooms on same floor. Classroom has the master setting. This causes other rooms adjust accordingly to the master settings. Reported findings, completed paperwork and signed out.
MSA-DTWD | WA5676894 | 2 | LIGHTHOUSE LOCKSMITHS | storeroom - faulty lock | Security | Locksmith | 340 | Pass | Pass | 0 | 0 | 1 | 2022-07-25 11:19 | 2022-07-28 17:00 | 2022-07-26 08:30 | 2022-07-28 17:00 | 2022-07-26 09:30 |  |  | replaced 2 damaged cylinders on store room in m block, keyed replacement cylinder back onto key system
MSA-DTWD | WA5679165 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Ground floor - call button for both lifts has fallen off - someone experienced a tingle from | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-07-26 11:15 | 2022-07-26 13:15 | 2022-07-26 11:30 | 2022-07-26 15:15 | 2022-07-26 12:30 |  |  | Replaced Broken Button
MSA-DTWD | WA5679370 | 3 | M Construction (WA) | Repair broken wall fixings | Building | Internal Walls | 143.42 | Pass | Pass | -1 | -1 | 1 | 2022-07-26 13:16 | 2022-08-02 17:00 | 2022-07-27 07:00 | 2022-08-02 17:00 | 2022-07-27 08:00 |  |  | Inspected broken wall fixings in D236. Replaced broken fixings with new.
MSA-DTAG | WA5679585 | 3 | Total Security Systems Pty Ltd | Jury meeting room smoke detector false activating (possible warranty) | Security | Security Management System | 371.2 | Fail | Fail | 2 | 2 | 1 | 2022-07-26 15:25 | 2022-08-02 17:00 | 2022-08-19 08:30 | 2022-08-02 17:00 | 2022-08-19 09:30 |  |  | 19/8/2022 - Subcontractor attendanceAttended site. Tested and discovered base was faulty. Replaced smoke detector base and head. Checked seal and confirmed functional.
MSA-DTAG | WA5681253 | 3 | Midolo Building Services | Registry - Main Door - Soft closer on main door needs attention - See notes below | Building | Doors | 168.23 | Pass | Pass | 0 | 0 | 1 | 2022-07-28 10:34 | 2022-08-04 17:00 | 2022-08-02 10:00 | 2022-08-04 17:00 | 2022-08-02 11:00 |  |  | DOOR REPAIRS COMPLETED
MSA-DTAG | WA5681296 | 2 | AHS Services WA Pty Ltd (Anchor) | Level 5 - Male Toilet next to courtroom 57 - Blocked Urinal | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 1 | 2022-07-28 11:02 | 2022-08-02 17:00 | 2022-08-01 10:45 | 2022-08-02 17:00 | 2022-08-01 11:45 |  |  | Cleared blocked urinal.
MSA-DTWD | WA5681595 | 3 | AWB Co. | Carpentry and Joinery workshop - 3 Phase power point has faulty RCD (#333) | Electrical | General Electrical | 270.45 | Pass | Pass | 0 | 0 | 1 | 2022-07-28 13:23 | 2022-08-04 17:00 | 2022-08-01 13:00 | 2022-08-04 17:00 | 2022-08-01 14:00 |  |  | Attended site signed in jsa completed.found powerpoint tripping at the rcd but not at the board. Replaced with new rcd and now no tripping as rcd was faulty.job completed
MSA-DFES | WA5681599 | 2 | Protek 24/7 Building & Maintenance | Carpark entrance - side gate is not operating | Building | Steel Fencing & Gates | 232.69 | Pass | Pass | -1 | -1 | 1 | 2022-07-28 13:23 | 2022-08-02 17:00 | 2022-07-29 07:45 | 2022-08-02 17:00 | 2022-07-29 08:45 |  |  | Repair gate
MSA-DTAG | WA5681719 | 3 | Australian HVAC Services Pty. Ltd. | 1903-Technician required to attend from 07:00am Monday 1 August 2022 - check BMS after RCD testing | Air Conditioning | Room Air Conditioners | 139.94 | Pass | Pass | 0 | 0 | 1 | 2022-07-28 14:28 | 2022-08-04 17:00 | 2022-08-01 07:00 | 2022-08-04 17:00 | 2022-08-01 08:00 |  |  | Oscar Holil (01/08/2022) - Work NoteArrived on site and signed in at security. Signed out a set of keys and gained access to BMS near the foyer. ACs that serve court 6, 3 and 2 can be controlled from here. Found that they all seems to be displaying correct values and operating correctly. Made my way to the BMS located in the chiller plant room but found that the BMS has been disconnected by other contractors. Physically checked the operation of AC units: AC1 operatingBoiler operatingAC3 operatingAC2 operatingAHU 7 operating AHU 1 operating AHU8 operatingAHU MS operatingSigned out and signed keys back in at security.
MSA-DCA | WA5686552 | 0 | Critical Fire Protection & Training | Fire Panel - 2 Faults on panel | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Fail | Pass | 0 | 0 | 1 | 2022-08-01 09:19 | 2022-08-01 11:19 | 2022-08-01 11:30 | 2022-08-01 13:19 | 2022-08-01 12:30 |  |  | .
MSA-DTAG | WA5687217 | 1 | Automatic Fire Protection (ARA) | Level 2 - (1987 Wing) - Corridor - near Beech JA chambers- Speaker making noise - See notes below | Fire Protection Services | Smoke and Heat Detection | 258.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-01 14:17 | 2022-08-02 17:00 | 2022-08-02 07:00 | 2022-08-02 17:00 | 2022-08-02 08:00 |  |  | On arrival, panel and ewis were normal.On inspecting the speaker in question, could hear an intermittent vibration sound in ceiling.The sound is coming from a floor to ceiling vent cover though, not our speaker.Sound disappears when we press on or remove the vent.Have notified security of issue and recommended to them to get air con guys to check it out
MSA-DFES | WA5687839 | 2 | AWB Co. | L1 engine room-door jam and trim has broken off, still in good condition not to be replaced | Building | Doors | 244.71 | Pass | Pass | 0 | 0 | 1 | 2022-08-02 07:25 | 2022-08-04 17:00 | 2022-08-02 13:00 | 2022-08-04 17:00 | 2022-08-02 14:00 |  |  | Architrave re glued and pinned, gaps caulked
MSA-DFES | WA5688189 | 1 | AWB Co. | Gym - external door - the hinges have been damaged and unable to close the door | Building | Doors | 162.19 | Pass | Pass | 0 | 0 | 1 | 2022-08-02 10:25 | 2022-08-03 17:00 | 2022-08-02 16:45 | 2022-08-03 17:00 | 2022-08-02 17:45 |  |  | Attended site, top and middle hinge come away from door, filled out JSA, removed existing M8 screws inserted timber dowels in to existing holes and screwed hinge back to door with M10 screws to secure tight. Door closing and opening correctly.
MSA-DFES | WA5688392 | 2 | Protek 24/7 Building & Maintenance | Rear yard Metal fence sheets x 2 blown out of fence panels rear yard | Building | Steel Fencing & Gates | 218.27 | Pass | Pass | 0 | 0 | 1 | 2022-08-02 10:41 | 2022-08-05 17:00 | 2022-08-04 10:00 | 2022-08-05 17:00 | 2022-08-04 11:00 |  |  | Refix to fence sheets
MSA-DCA | WA5692963 | 2 | TK Elevator Australia Pty Ltd | Level 1 - Lift 6 service elevator - Key barrel has come loose- See notes below | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-08-04 08:26 | 2022-08-09 17:00 | 2022-08-04 13:00 | 2022-08-09 17:00 | 2022-08-04 14:00 |  |  | Lift6 Loading Dock-Hydraulic :Removed the car operating panel and tightened the exclusive service key switch. Also asked to check lift 7, oil appears to be running down oneof the panels inside the lift car. Checked on top of car, and down the side of the lift car. No oil leaking from ram. Oil appears to be old oil from the rail oilers,not recent oil leak.Cleaned up the car panel that had the oil marks. Both lifts back in service.Left spare hoistway door lock contacts in controller 7.to be closed out at $0 cost
MSA-DTWD | WA5693145 | 2 | Damian Rak Electrical Pty Ltd | External toilet The end toilet-Faulty LED light | Electrical | General Electrical |  | Fail | Fail | 4 | 4 | 1 | 2022-08-04 09:53 | 2022-08-09 17:00 | 2022-09-04 13:00 | 2022-08-09 17:00 | 2022-09-04 14:00 |  |  | Repair to light
MSA-DTWD | WA5693283 | 2 | BAKE-QUIP PTY LTD | D18 Baking Lab - Sottoriva Sprint 25 Spiral Mixer keeps cutting In and out under load | Equipment | Catering Equipment | 230 | Fail | Fail | 0 | 0 | 1 | 2022-08-04 11:06 | 2022-08-09 17:00 | 2022-08-12 11:30 | 2022-08-09 17:00 | 2022-08-12 12:30 |  |  | REFER TO ATTACHED
MSA-DTWD | WA5693304 | 1 | AHS Services WA Pty Ltd (Anchor) | L3 outside lift on left ladies toilet keeps running | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 1 | 2022-08-04 11:18 | 2022-08-05 17:00 | 2022-08-04 14:30 | 2022-08-05 17:00 | 2022-08-04 15:30 |  |  | Replaced inlet valve and outlet rubber / car stock
MSA-DFES | WA5693367 | 2 | AWB Co. | Stationery Area - Roof Water Leak above Stationery Area | Roofing | Metal Roofing | 270.96 | Pass | Pass | -1 | -1 | 1 | 2022-08-04 11:47 | 2022-08-09 17:00 | 2022-08-04 14:30 | 2022-08-09 17:00 | 2022-08-04 15:30 |  |  | Investigated area above roof leak, found 2 issues with aircon duct and aircon flashing. Carried out repairs
MSA-DTWD | WA5693416 | 2 | Securex Security Systems & Services | Zone 6 unable to arm panel shows LAN failure | Security | Security Management System | 220 | Pass | Pass | -1 | -1 | 1 | 2022-08-04 12:07 | 2022-08-09 17:00 | 2022-08-04 13:45 | 2022-08-09 17:00 | 2022-08-04 14:45 |  |  | 04/08/2022, 1345-1445No LAN fail showing on system upon arrival. Bypassed zones appear to be all around same area and walk tested a fewof them ok. There appears to be new security guards on site and sounds like they are arming system before closingdoors or walking around.
MSA-DCA | WA5694888 | 2 | Techworks Plumbing | Level 2 - UAT (unisex accessible toilet) - Repair/refit water-spout over hand basin | Plumbing & Drainage | Toilets/Cisterns | 135.14 | Pass | Pass | -1 | -1 | 1 | 2022-08-05 14:16 | 2022-08-10 17:00 | 2022-08-05 16:00 | 2022-08-10 17:00 | 2022-08-05 17:00 |  |  | Arrived on site and signed in at security.Once signed in I went and located the damaged water spout.Once I found it I could see the grub screw had just loosened over time or someone had wiggled the basin outlet out. Went to my Ute to get the correct tool to fix it back into position. Returned to bathroom and re installed.Tested for leaks.No leaks so I returned to the security desk and signed out.
MSA-DTWD | WA5694911 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilets to G Block require repairing | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 1 | 2022-08-05 14:36 | 2022-08-10 17:00 | 2022-08-08 11:30 | 2022-08-10 17:00 | 2022-08-08 12:30 |  |  | Cleared blocked toilets
MSA-DTWD | WA5696285 | 2 | Precise Air Group | Air Conditioner not heating | Air Conditioning | Room Air Conditioners | 208.34 | Pass | Pass | 0 | 0 | 1 | 2022-08-08 10:47 | 2022-08-11 17:00 | 2022-08-09 10:00 | 2022-08-11 17:00 | 2022-08-09 11:00 |  |  | Arrived at site checked operation found unit not heating checked operation found batteries were flat in remote put new ones in and system was set to cooling not heating adjusted controls for right conditions and checked units operation when left room was at 23c and supply air temp 42c all running efficiently
MSA-DCA | WA5696733 | 1 | Techworks Plumbing | Ground Level - UAT - Broken toilet seat - See notes below | Plumbing & Drainage | Toilets/Cisterns | 236.02 | Pass | Pass | 0 | 0 | 1 | 2022-08-08 14:08 | 2022-08-09 17:00 | 2022-08-09 07:00 | 2022-08-09 17:00 | 2022-08-09 08:00 |  |  | Started at the yard then proceeded to head to the museum arrived on site and signed in at the security office, had a chat to the cleaner on site to find the exact toilet that was broken, she showed us where it was. the toilet seat had just come loose so we tightened the lock nuts to make it tight again then we got a signature slip and signed out completed paperwork
MSA-DFES | WA5696871 | 2 | Complete Pest Management Services | Kitchen - Ants in kitchen drawers, mainly in west side drawers between the sinks. | Pest Control | General Pest | 183.66 | Pass | Pass | 0 | 0 | 1 | 2022-08-08 16:05 | 2022-08-11 17:00 | 2022-08-09 10:45 | 2022-08-11 17:00 | 2022-08-09 11:45 |  | WACCES | Inspected inside and outside of the kitchen, treated ants inside with gel bait and outside with biflex
MSA-DTWD | WA5697929 | 1 | Total Security Systems Pty Ltd | Ground floor - B7 - Fault with alarm software for monitoring - Alarms wont clear -rapid increase | Security | Security Management System | 245 | Pass | Pass | 0 | 0 | 1 | 2022-08-09 12:56 | 2022-08-10 17:00 | 2022-08-09 13:45 | 2022-08-10 17:00 | 2022-08-09 14:45 |  |  | 9/8/2022 - Anthony Lee - 1.45pm to 2.45pmCleared alarm backlog which had accumulated due to power outages. No further issues on site.
MSA-DCA | WA5699639 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Air con has dropped 9 deg-see notes | Air Conditioning | Room Air Conditioners | 146.4 | Pass | Pass | 0 | 0 | 1 | 2022-08-10 10:58 | 2022-08-11 17:00 | 2022-08-11 13:00 | 2022-08-11 17:00 | 2022-08-11 14:00 |  |  | Attended site. Investigated ac issues. Found public concourse in unoccupied but was scheduled to be on. Switched to occupied and unit started. Tested operation, all ok. Found main bar unit wasn't scheduled to be on. Completed paperwork.
MSA-DTWD | WA5735057 | 2 | COMMERCIAL PLUMBING AND GAS | Old Canteen - Stove - Cap off Gas | Plumbing & Drainage | Gas | 138.88 | Fail | Fail | 6 | 6 | 1 | 2022-08-16 11:09 | 2022-08-19 17:00 | 2022-09-27 13:00 | 2022-08-19 17:00 | 2022-09-27 14:00 |  |  | stripped piping
MSA-DTWD | WA5735168 | 1 | Protek 24/7 Building & Maintenance | Entry to 11G1 - Nib wall holding gate separating from building | Building | Internal Walls | 202.79 | Pass | Pass | 0 | 0 | 1 | 2022-08-16 11:37 | 2022-08-17 17:00 | 2022-08-16 13:00 | 2022-08-17 17:00 | 2022-08-16 14:00 |  |  | Braf Declined Inspect and make safe only
MSA-DFES | WA5749295 | 1 | Protek 24/7 Building & Maintenance | Admin Building - Eastern Entrance Door is broken - Door is almost off hinges | Building | Doors | 234.29 | Pass | Pass | 0 | 0 | 1 | 2022-08-17 08:47 | 2022-08-18 17:00 | 2022-08-17 10:00 | 2022-08-18 17:00 | 2022-08-17 11:00 |  |  | Hung the door with new rivets
MSA-DTAG | WA5752316 | 2 | MALCO FLOORING PTY LTD | Level 10 - Coroners - A few carpet tiles are lifting slightly in Coroners office – trip hazard | Flooring | Carpet | 256.4 | Fail | Fail | 0 | 0 | 1 | 2022-08-17 11:40 | 2022-08-22 17:00 | 2022-08-25 06:40 | 2022-08-22 17:00 | 2022-08-25 07:40 |  |  | Level 10 Coroners area a few carpet tiles are lifting slightly in Coroners office trip hazardMadegood lifting carpet tiles to L10 Coroners office
MSA-DTWD | WA5753216 | 3 | AWB Co. | 2 x Lights out over hand wash area - E401 | Electrical | Lighting, Internal | 209.04 | Pass | Pass | -1 | -1 | 1 | 2022-08-17 14:53 | 2022-08-24 17:00 | 2022-08-19 07:00 | 2022-08-24 17:00 | 2022-08-19 08:00 |  |  | Attended site and signed in. Completed JSA. located work area. Replaced faulty tubes and starters. Light working as intended. Took pictures. Completed paperwork. Signed out. Job complete
MSA-DTAG | WA5753352 | 1 | Sapio Pty Ltd | Custody control room - Control room door - is not working correctly - see notes below | Security | Access Control | 139.88 | Fail | Fail | 0 | 0 | 1 | 2022-08-17 16:45 | 2022-08-18 17:00 | 2022-08-19 08:30 | 2022-08-18 17:00 | 2022-08-19 09:30 |  |  | Attended site. Checked electronic door release in Custody control room. There is an intermittent fault with all 3 doorscontrolled by stand alone custom made door control system. Switching parts of the system are in use for a long time andan upgrade is required. Also, none of the doors or system itself are monitored for power loss or faults what can causesecurity breach if undetected.Recommended is upgrade to 4 door controller that can be integrated with security system on site and get monitoredcorrectly.05/09/2022 - BRAF declined, works to proceed under new LVM Work Order WA5832499.
MSA-DFES | WA5761225 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 -Dorm 2 Bathroom - Bathroom light for Dorm 2 needs replacement globe. | Electrical | Lighting, Internal | 207.96 | Fail | Fail | 0 | 0 | 1 | 2022-08-18 07:19 | 2022-08-24 17:00 | 2022-08-25 07:45 | 2022-08-24 17:00 | 2022-08-25 08:45 |  |  | Located faulty light. Found both lights were working one downlight was dull. Replaced faulty downlight with new. I was not able to reach the plug used a junction box and hardwire the light. Advised staff of work completed.
MSA-DTWD | WA5761666 | 2 | AWB Co. | faulty GPO | Electrical | General Electrical | 160.01 | Pass | Pass | 0 | 0 | 1 | 2022-08-18 10:57 | 2022-08-23 17:00 | 2022-08-22 07:00 | 2022-08-23 17:00 | 2022-08-22 08:00 |  |  | Attended site and signed in, completed jsa,got keys from security, located faulty gpo , isolated circuit and removed gpo, drilled out bigger hole behind gpo for new one to fit, installed new gpo, re energised circuit , tested gpo and working as intended, packed up, cleaned up, labelled gpo, completed paperwork, signed out, job completed, signature slips sent to Sheryl to be signed
MSA-DTAG | WA5766041 | 1 | Sapio Pty Ltd | Ground - Control Room - Screens/camera not working | Security | Monitoring | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-18 14:44 | 2022-08-19 17:00 | 2022-08-19 08:30 | 2022-08-19 17:00 | 2022-08-19 09:30 |  |  | The Custody user was locked because of too many incorrect password attempts, unlocked the user.Also had a look at the issue with them logging into the application each day.Job completed.
MSA-MRWA | WA5780293 | 1 | GPS Plumbing & Gas Services PtyLtd | Ambient toilet continually running | Plumbing & Drainage | Water | 158.43 | Pass | Pass | 0 | 0 | 1 | 2022-08-19 09:12 | 2022-08-22 17:00 | 2022-08-22 10:47 | 2022-08-22 17:00 | 2022-08-22 11:47 |  |  | Replaced leaking outlet valve washer, adjusted inlet valve
MSA-DTAG | WA5780523 | 3 | Schindler Lifts Australia | Level 2-Lift 2-out of order | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-08-19 11:20 | 2022-08-26 17:00 | 2022-08-19 14:21 | 2022-08-26 17:00 | 2022-08-19 15:21 |  |  | T5 error for level 4 fixed Tested and running
MSA-DTWD | WA5781136 | 1 | OTIS ELEVATOR COMPANY PTY LTD | lift not working, showing out of service | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-08-19 13:04 | 2022-08-22 17:00 | 2022-08-19 14:30 | 2022-08-22 17:00 | 2022-08-19 15:30 |  |  | Repaired under warranty - No charges for attendance
MSA-DCA | WA5790912 | 2 | FCT SURFACE CLEANING | Graffiti on downpipe - AGWA - Centenary Roe St -photo to follow | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1 | 2022-08-22 13:23 | 2022-08-25 17:00 | 2022-08-23 13:00 | 2022-08-25 17:00 | 2022-08-23 14:00 |  |  | Job is completed - Graffiti on downpipe was removed
MSA-DTWD | WA5791724 | 3 | AWB Co. | Electrical test required for faulty pump - 127 | Equipment | Electrical Equipment | 146.41 | Pass | Pass | -1 | -1 | 1 | 2022-08-23 09:18 | 2022-08-30 17:00 | 2022-08-23 14:30 | 2022-08-30 17:00 | 2022-08-23 15:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,fm took me to pump, spoke with lecturer about pump operation , tested pump , found that float wasn’t engaging properly, mounted float like same machine and pump works fine, removed out of service tag, packed up, completed paperwork,signed out **job completed**
MSA-DFES | WA5791912 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Male Changerooms - Sink on left side is not draining/ blocked | Plumbing & Drainage | Drainage | 154.6 | Pass | Pass | -1 | -1 | 1 | 2022-08-23 10:22 | 2022-08-30 17:00 | 2022-08-25 10:00 | 2022-08-30 17:00 | 2022-08-25 11:00 |  |  | Attend site to check out blocked hand basin in male change room ground floor. Found LH side locked and not draining away, removed trap and cleared out. Filled sink with hot water and used plunger to clear blockage. Checked RH basin and found slow to drain filled with hot water and plunged. Both basins running correctly
MSA-DTAG | WA5792010 | 2 | Midolo Building Services | Level 6 - PRB - Male staff toilet requires replacement door closer | Building | Doors | 680.4 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 11:01 | 2022-08-26 17:00 | 2022-08-23 11:30 | 2022-08-26 17:00 | 2022-08-23 12:30 |  |  | new door closer installed
MSA-DTWD | WA5792092 | 0 | Water2water Pty Ltd | Room 1354 - Under bench hot water system has a split filter | Plumbing & Drainage | HWS/Units Electric & Gas | 513.36 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 11:27 | 2022-08-23 13:27 | 2022-08-23 11:50 | 2022-08-23 15:27 | 2022-08-23 12:50 |  |  | Replaced damaged filter head and tested. All ok and cleaned up best I can .
MSA-DTWD | WA5792344 | 3 | AHS Services WA Pty Ltd (Anchor) | B Block Level 2 Male toilet Urinal Blocked | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | -1 | -1 | 1 | 2022-08-23 13:23 | 2022-08-30 17:00 | 2022-08-25 09:15 | 2022-08-30 17:00 | 2022-08-25 10:15 |  |  | .
MSA-DTAG | WA5792352 | 1 | AWB Co. | Circuit board cannot be reset – faulty fuse | Electrical | Distribution Board | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 13:28 | 2022-08-24 17:00 | 2022-08-24 11:30 | 2022-08-24 17:00 | 2022-08-24 12:30 |  |  | No fault found
MSA-DTWD | WA5792484 | 2 | AWB Co. | B2308 - Faulty GPO - switch sticking in on position | Electrical | General Electrical | 228.33 | Pass | Pass | 0 | 0 | 1 | 2022-08-23 14:48 | 2022-08-26 17:00 | 2022-08-25 07:00 | 2022-08-26 17:00 | 2022-08-25 08:00 |  |  | Attended site and signed in, completed jsa,got cleaner to open b block , located gpo, isolated circuit,removed old gpo, replaced with new, re energised circuit, tested gpo and working as intended ,packed up, cleaned up, completed paperwork,signed out, job completed
MSA-DTWD | WA5793590 | 2 | COMMERCIAL PLUMBING AND GAS | Sink / grease trap partially blocked | Plumbing & Drainage | Drainage | 793.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-24 08:46 | 2022-08-29 17:00 | 2022-08-29 13:00 | 2022-08-29 17:00 | 2022-08-29 14:00 |  |  | drainsflush jet grease lines through to arrestor
MSA-DTWD | WA5794691 | 2 | COMMERCIAL PLUMBING AND GAS | Disable toilet-Cistern leaks often after flushing. Worn components.-photo's to follow in email | Plumbing & Drainage | Toilets/Cisterns | 278.02 | Pass | Pass | 0 | 0 | 1 | 2022-08-25 07:12 | 2022-08-29 17:00 | 2022-08-26 14:30 | 2022-08-29 17:00 | 2022-08-26 15:30 |  |  | repaired disabled cistern
MSA-DTAG | WA5795591 | 1 | AWB Co. | Ground floor - Detention corridor door near echo chamber - Keypad not releasing door - | Electrical | General Electrical | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-08-25 13:27 | 2022-08-26 17:00 | 2022-08-26 09:15 | 2022-08-26 17:00 | 2022-08-26 10:15 |  |  | Attended site and signed in. Completed JSA. Spoke to receptionist who reported job. She showed us which door it was and explained this issue. Door was opening intermittently then didn’t open at all. Managed to get door open. Pulled off striker to have a look at wiring. Wiring was all okay. Tested locking mechanism and it seemed to be stiff. Put lubricant in striker and around door latch. Tested multiple times. Door and striker is now working as intended. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5795763 | 3 | AWB Co. | south block - S241 Creche Pram Room - Sparking, fizzing light switch | Electrical | General Electrical | 295.39 | Pass | Pass | -1 | -1 | 1 | 2022-08-25 16:13 | 2022-09-01 17:00 | 2022-08-26 12:15 | 2022-09-01 17:00 | 2022-08-26 13:15 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,spoke with manager of daycare and located switch in crèche ,tested light and was arcing , got materials, isolated lighting circuit, removed old switch mech and replaced with new ,re energised circuit and tested lights , lights working as intended ,completed paperwork,packed up, signed out**job completed**
MSA-DTWD | WA5795941 | 2 | Techworks Electrical | light not working | Electrical | Lighting, Internal | 246.3 | Pass | Pass | 0 | 0 | 1 | 2022-08-26 07:45 | 2022-08-30 17:00 | 2022-08-30 08:30 | 2022-08-30 17:00 | 2022-08-30 09:30 |  |  | Replaced fluro tubes in D Block
MSA-DTWD | WA5796767 | 2 | M Construction (WA) | East Side just before the 1st landing there are loose stairs | Building | General Building | 157.02 | Pass | Pass | 0 | 0 | 1 | 2022-08-26 13:32 | 2022-08-31 17:00 | 2022-08-29 07:00 | 2022-08-31 17:00 | 2022-08-29 08:00 |  |  | Packed underneath step to level out and filled with silicone to fix into place.
MSA-DCA | WA5797183 | 0 | EQUANS Mechanical Services (WA) Pty Limited | AC 2 Humidity alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 1685.9 | Pass | Pass | 0 | 0 | 1 | 2022-08-28 23:00 | 2022-08-29 01:00 | 2022-08-28 23:30 | 2022-08-29 03:00 | 2022-08-29 00:30 |  |  | Check out AC2 in my gallery with low humidity. Steam valve at 100% open and steam generators operating fine. System will come back into humidity range with time.Also reset ac 6 and 8 humidifiers in centenary as they were in fault.All OK.
MSA-DTAG | WA5797621 | 1 | Seme Solutions Pty Ltd | Service Failure on Pacom system (SEME) | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-08-29 09:31 | 2022-08-30 17:00 | 2022-08-29 10:00 | 2022-08-30 17:00 | 2022-08-29 11:00 |  |  | *SEE SIGSLIP FOR ACTUAL TIME*Attended site, staff stated they couldn't operate doors via software.Inspected software, confirmed unable to operate doors due to losing server connection.Attended server, operating super slow - software non-operable. Error stating no storage left on system.Unable to restart server softly, performed hard reset.Test operations - now operating successfully.Checked storage - more than 70% of storage available on server.
MSA-DCA | WA5798423 | 3 | Techworks Plumbing | Ground Floor - Admin UAT - Seal on sink is faulty - See notes below | Plumbing & Drainage | Water | 230.86 | Pass | Pass | -1 | -1 | 1 | 2022-08-29 14:16 | 2022-09-05 17:00 | 2022-08-30 11:30 | 2022-09-05 17:00 | 2022-08-30 12:30 |  |  | Attended sink with no seal in uat. Neil told me the trap just needs to be put back together with a seal he wasn’t sure what it needed, I just put the trap back together and tested it multiple times with no leaks, not sure what the problem was but the bottle trap is back to how it’s meant to be with no leaks so signed out and got my signature slips for both museum jobs and completed paperwork, contractor pass handed back
MSA-DTWD | WA5799247 | 3 | AWB Co. | Door to roof sun exposure damage | Building | Doors | 654.5 | Pass | Pass | -1 | -1 | 1 | 2022-08-30 10:36 | 2022-09-06 17:00 | 2022-09-02 07:00 | 2022-09-06 17:00 | 2022-09-02 08:00 |  |  | painting works to door completed
MSA-DTAG | WA5799286 | 1 | AHS Services WA Pty Ltd (Anchor) | Staff female toilet - toilet seat is broken | Plumbing & Drainage | Toilets/Cisterns | 214.27 | Pass | Pass | 0 | 0 | 1 | 2022-08-30 10:51 | 2022-08-31 17:00 | 2022-08-31 10:00 | 2022-08-31 17:00 | 2022-08-31 11:00 |  |  | Replaced toilet seat
MSA-DTAG | WA5800478 | 2 | AWB Co. | Level 4 - 2 x faulty lights in Adult Community Corrections corridor | Electrical | Lighting, Internal | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-08-31 10:21 | 2022-09-05 17:00 | 2022-09-02 11:30 | 2022-09-05 17:00 | 2022-09-02 12:30 |  |  | Job complete
MSA-DTWD | WA5827061 | 3 | AWB Co. | Next to Ladies Loo - Worn light switch | Electrical | General Electrical | 226.17 | Pass | Pass | 0 | 0 | 1 | 2022-09-01 07:50 | 2022-09-07 17:00 | 2022-09-05 13:00 | 2022-09-07 17:00 | 2022-09-05 14:00 |  |  | Attended site and signed in, completed JSA,spoke with fm about job, located light switch and isolated circuit,removed faulty switch and replaced with new, re energised circuit and tested, working as intended, packed up, completed paperwork,signed out **job completed**
MSA-DCA | WA5829613 | 1 | Techworks Electrical | Dressing Room 5 - Light switch no longer functional - see notes below | Electrical | Lighting, Internal | 236.64 | Pass | Pass | 0 | 0 | 1 | 2022-09-02 14:33 | 2022-09-05 17:00 | 2022-09-05 08:30 | 2022-09-05 17:00 | 2022-09-05 09:30 |  |  | Replaced light switch in dressing room 5
MSA-DTAG | WA5830131 | 1 | Midolo Building Services | Ground - Female Toilet door Stall 1 - Bracket to the door has come off hinges - See notes below | Building | Doors | 191.13 | Pass | Pass | 0 | 0 | 1 | 2022-09-02 16:15 | 2022-09-05 17:00 | 2022-09-05 07:45 | 2022-09-05 17:00 | 2022-09-05 08:45 |  |  | new fixings & threaded rods (hinges) installed
MSA-DFES | WA5832451 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Heritage Shed - Hot Water System on Transportable Toilet is leaking | Plumbing & Drainage | Water | 192.25 | Pass | Pass | 0 | 0 | 1 | 2022-09-05 13:20 | 2022-09-12 17:00 | 2022-09-12 07:00 | 2022-09-12 17:00 | 2022-09-12 08:00 |  |  | Ateend site to check out leak on hot water system on transportable toilet block at heritage shed. Found small 50L Rheem that was leaking from threaded fitting, removed and re thread taped. If this problem happens again we would look at replacement of quickie kit on hot water system. The hot water DOM 2016
MSA-DFES | WA5833592 | 2 | Protek 24/7 Building & Maintenance | ground floor - replace damaged ceiling tiles along toilet & corridors | Building | Ceiling | 128.59 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 10:37 | 2022-09-09 17:00 | 2022-09-06 11:30 | 2022-09-09 17:00 | 2022-09-06 12:30 |  |  | Removed damaged ceiling tiles and install new ceiling tiles as instructed by Debra on site
MSA-DFES | WA5833933 | 1 | Protek 24/7 Building & Maintenance | Mens Toilet - Door into men's toilet from warehouse - Door has fallen off hinges | Building | Doors | 210.91 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 12:37 | 2022-09-07 17:00 | 2022-09-07 13:00 | 2022-09-07 17:00 | 2022-09-07 14:00 |  |  | No apparent damage
MSA-DTWD | WA5833970 | 2 | AWB Co. | Roof leak - currently a bucket collecting the water underneath | Roofing | Metal Roofing | 249.72 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 12:52 | 2022-09-09 17:00 | 2022-09-07 14:30 | 2022-09-09 17:00 | 2022-09-07 15:30 |  |  | Found unsealed sheet joins lifted sheets and under sealed crank. Sealed apron joins.job complete
MSA-DFES | WA5834396 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Main Building - multiple faults - see notes below | Electrical | General Electrical | 234.72 | Pass | Pass | 0 | 0 | 1 | 2022-09-06 16:04 | 2022-09-09 17:00 | 2022-09-08 07:00 | 2022-09-09 17:00 | 2022-09-08 08:00 |  |  | complete
MSA-MRWA | WA5836487 | 2 | AWB Co. | Faulty fluoro light above deep fryer | Electrical | Lighting, Internal | 209.04 | Pass | Pass | -1 | -1 | 1 | 2022-09-07 12:19 | 2022-09-12 17:00 | 2022-09-08 14:30 | 2022-09-12 17:00 | 2022-09-08 15:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm about job. Located faulty light fitting in kitchen area above deep fryer. Got deep fryer covered. Took down diffuser. Replaced tubes and starters. Tombstone of one side of the fitting was burnt out and not useable. Fm said they may want to get 2x LEDs above fryers in future but this is good for now. Took pictures of light. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5836853 | 3 | CARRIER AUSTRALIA PTY LTD | Sacrificial anodes worn in chiller 1 | Refrigeration | Chiller |  | Pass | Pass | -1 | -1 | 1 | 2022-09-07 15:07 | 2022-09-14 17:00 | 2022-09-07 15:15 | 2022-09-14 17:00 | 2022-09-07 16:15 |  |  | Anode replacement in chiller 1
MSA-DFES | WA5837863 | 3 | Protek 24/7 Building & Maintenance | External - Personnel access door will not close - Latch is hitting door frame | Building | Doors | 122.4 | Pass | Pass | 0 | 0 | 1 | 2022-09-08 08:59 | 2022-09-15 17:00 | 2022-09-13 08:30 | 2022-09-15 17:00 | 2022-09-13 09:30 |  |  | eased the hinges so that the door fits better in the frame with a larger gap down the latch side
MSA-MRWA | WA5837916 | 1 | AWB Co. | Switchboard - Blue 14 - circuit tripping | Electrical | General Electrical | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-09-08 09:25 | 2022-09-09 17:00 | 2022-09-08 12:15 | 2022-09-09 17:00 | 2022-09-08 13:15 |  |  | Power surge caused rcd to trip
MSA-DTWD | WA5839020 | 3 | MR POTHOLE | Northern driveway - Carpark - Road needs repairing - Old rubber speed bump faulty | Paving & Roadworks | Paving |  | Fail | Fail | 3 | 3 | 1 | 2022-09-09 08:30 | 2022-09-16 17:00 | 2022-10-05 13:45 | 2022-09-16 17:00 | 2022-10-05 14:45 |  |  | speed hump removal
MSA-DTWD | WA5839326 | 2 | Securex Security Systems & Services | Issues with the existing Challenger/Titan swipecard security system. - Please see notes below | Security | Access Control | 423.85 | Pass | Pass | 0 | 0 | 1 | 2022-09-09 11:16 | 2022-09-14 17:00 | 2022-09-14 10:45 | 2022-09-14 17:00 | 2022-09-14 11:45 |  |  | 14/09/2022, 1045-1145IP address of Titan Software computer has changed, updated details and reconnected software.Checked all programming and tested cards etc all ok able to update.
MSA-DCA | WA5853588 | 1 | Ballantyne Plumbing Gas & Electrical | C&K - Kitchen - Spray-up tap has separated from hose - see notes below | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1 | 2022-09-12 09:40 | 2022-09-13 17:00 | 2022-09-12 10:00 | 2022-09-13 17:00 | 2022-09-12 11:00 |  |  | replacement
MSA-DFES | WA5853645 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Carpark-lights (currently stays on for one second) set to 4 minutes.-see notes | Electrical | Lighting, External | 211.38 | Pass | Pass | -1 | -1 | 1 | 2022-09-12 09:53 | 2022-09-19 17:00 | 2022-09-15 10:00 | 2022-09-19 17:00 | 2022-09-15 11:00 |  |  | Arrived on site at 10:06 to investigate car park lights, found that each light was set to 5 second motion activated. Changed each light to 5 minutes and tested all okay. Continued on site at 11:00
MSA-DTWD | WA5867159 | 2 | Protek 24/7 Building & Maintenance | Ground floor - roof fan outside café - The Whirly Bird fan in the roof bearings are seizing | Roofing | Metal Roofing | 200.64 | Pass | Pass | -1 | -1 | 1 | 2022-09-14 09:32 | 2022-09-19 17:00 | 2022-09-15 13:00 | 2022-09-19 17:00 | 2022-09-15 14:00 |  |  | BRAF Declined
MSA-DFES | WA5880699 | 1 | Anvil Doors | Door 4 engine room - won't close | Building | Doors | 377 | Pass | Pass | 0 | 0 | 1 | 2022-09-15 15:35 | 2022-09-16 17:00 | 2022-09-15 16:45 | 2022-09-16 17:00 | 2022-09-15 17:45 |  |  | Technician Attended and adjusted door 4 safety beams. Issue resolved
MSA-DTWD | WA5887897 | 3 | AWB Co. | D117 Pre Press - No power to GPO | Electrical | General Electrical | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-09-16 11:10 | 2022-09-23 17:00 | 2022-09-23 07:00 | 2022-09-23 17:00 | 2022-09-23 08:00 |  |  | Technician for machine had already been to site
MSA-DFES | WA5962531 | 1 | Critical Fire Protection & Training | Fire panel fault- activated zone 5 pump room causing pressure fluctuation panel isolated | Fire Protection Services | Fire Protection - Monitor System | 157.58 | Pass | Pass | 0 | 0 | 1 | 2022-09-19 14:55 | 2022-09-20 17:00 | 2022-09-19 16:00 | 2022-09-20 17:00 | 2022-09-19 17:00 |  |  | Arrived on site and signed in.Isolated code red, external bell, warning system, and EWIS.No alarms on panel, viewed isolated list and the same 2 isolates were on panel from this morning.Went in to pump room and diesel pump A40169564O was not running and was at 100% fuel.Ensured isolations are still in place and deisolated isolates (both relating to sprinkler). No issues with panel, took off warning bell, warning system, EWIS and code red isolated.
MSA-DTWD | WA5970720 | 0 | COMMERCIAL PLUMBING AND GAS | All male toilets blocked | Plumbing & Drainage | Toilets/Cisterns | 563.88 | Pass | Pass | 0 | 0 | 1 | 2022-09-20 09:00 | 2022-09-20 11:00 | 2022-09-20 10:45 | 2022-09-20 13:00 | 2022-09-20 11:45 |  |  | unblocked paper buildup in drain
MSA-DTWD | WA5971436 | 2 | PEEL LOCK SERVICES PTY LTD | The locking mechanism is faulty | Security | Locksmith |  | Fail | Fail | 1 | 1 | 1 | 2022-09-20 13:51 | 2022-09-23 17:00 | 2022-09-27 10:00 | 2022-09-23 17:00 | 2022-09-27 11:00 |  |  | Repairs to lock
MSA-DTWD | WA5971506 | 2 | Damian Rak Electrical Pty Ltd | Front door entry - Faulty spitfire light | Electrical | Emergency & Exit Lighting |  | Fail | Fail | 1 | 1 | 1 | 2022-09-20 14:40 | 2022-09-23 17:00 | 2022-09-29 10:00 | 2022-09-23 17:00 | 2022-09-29 11:00 |  |  | Repairs to light
MSA-DTWD | WA5971897 | 2 | Damian Rak Electrical Pty Ltd | Flat B - Ground Floor - Faulty toilet light | Electrical | Lighting, Internal |  | Pass | Pass | 0 | 0 | 1 | 2022-09-20 16:04 | 2022-09-23 17:00 | 2022-09-22 16:00 | 2022-09-23 17:00 | 2022-09-22 17:00 |  |  | Repairs to light
MSA-DFES | WA5974619 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Faulty door switch controller linked to the AC. | Electrical | General Electrical | 134.46 | Pass | Pass | 0 | 0 | 1 | 2022-09-23 14:18 | 2022-09-29 17:00 | 2022-09-28 10:45 | 2022-09-29 17:00 | 2022-09-28 11:45 |  |  | Arrived onsite at 10:45 to investigate AC not working located training room. Found staff were concerned aircon wasn’t working due to external door security reed switch was cutting it off when door was opened. Issue was already fixed by aircon technicians but security panel doesn’t work correctly now. Notified staff onsite issue is not electrical related and needs to be called in as a security job. Left site at 11:45
MSA-DTWD | WA5976737 | 2 | M Construction (WA) | Ground - East-side entrance - break glass door box has come away from wall fitting | Building | Internal Walls | 151.62 | Pass | Pass | 0 | 0 | 1 | 2022-09-27 11:01 | 2022-09-30 17:00 | 2022-09-29 08:30 | 2022-09-30 17:00 | 2022-09-29 09:30 |  |  | Refit door using both stronger fixings and glue.
MSA-DFES | WA5977258 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main Admin - Radio Comms admin office -There is a power point that is difficult to push a plug into, | Electrical | General Electrical | 154.46 | Pass | Pass | -1 | -1 | 1 | 2022-09-27 15:06 | 2022-10-04 17:00 | 2022-09-29 10:00 | 2022-10-04 17:00 | 2022-09-29 11:00 |  |  | Arrived on site at 1000 to attend Main Admin - Radio Comms admin office -There is a power point that is difficult to push aplug into. Identified 1 x single gpo with worn contacts. Replaced/reenergised gpo, informed staff and left site at 1100.
MSA-DCA | WA5977352 | 1 | Wilson Security | Retrospective Work order - ZONE PIR U BLOCK PASSAGE 6 AREA 5 JB# 3429 14/09/22 13:38 | Security | Guards |  | Fail | Fail | 2 | 2 | 1 | 2022-09-14 13:30 | 2022-09-15 17:00 | 2022-09-27 16:45 | 2022-09-15 17:00 | 2022-09-27 17:45 | 1 |  | Completed
MSA-DCA | WA5977354 | 1 | Wilson Security | PE BEAMS ZONE 117 5 U BLOCK WEST TO W BLOCK WEST JB# 3429 | Security | Guards |  | Fail | Fail | 1 | 1 | 1 | 2022-09-18 11:55 | 2022-09-19 17:00 | 2022-09-27 16:45 | 2022-09-19 17:00 | 2022-09-27 17:45 |  |  | Completed
MSA-DCA | WA5977356 | 1 | Wilson Security | Z117 PE BEAM U BLOCK WEST TO W BLOCK WEST - MULTIS - AUTHORISED TO BYPASS IF NEEDED JB# 3429 | Security | Guards |  | Fail | Fail | 1 | 1 | 1 | 2022-09-18 13:15 | 2022-09-19 17:00 | 2022-09-27 16:45 | 2022-09-19 17:00 | 2022-09-27 17:45 |  |  | Completed
MSA-DTAG | WA5978176 | 1 | PPM Project Painting & Maintenance | Outside on side of the building roofing - Graffiti | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1 | 2022-09-28 09:12 | 2022-09-29 17:00 | 2022-09-29 07:00 | 2022-09-29 17:00 | 2022-09-29 08:00 |  |  | Removal of graffiti
MSA-DTWD | WA5978745 | 2 | AWB Co. | Faulty fluro fitting | Electrical | Lighting, Internal | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-09-28 13:03 | 2022-10-03 17:00 | 2022-10-03 13:00 | 2022-10-03 17:00 | 2022-10-03 14:00 |  |  | Attended site signed in jsa completed. Found faulty tombstones in one fluro fitting. Replaced with two new tombstones and checked operation. All working ok now Job completed
MSA-DTWD | WA5987097 | 0 | AWB Co. | No power to cafe | Electrical | General Electrical | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-10-03 07:46 | 2022-10-03 09:46 | 2022-10-03 08:30 | 2022-10-03 11:46 | 2022-10-03 09:30 |  |  | Job complete
MSA-DTWD | WA5987263 | 1 | UNIVERSAL DOORS | Service area - Retractable security screen/grill jammed and will not retract onto | Building | Security Doors |  | Pass | Pass | 0 | 0 | 1 | 2022-10-03 08:51 | 2022-10-04 17:00 | 2022-10-03 15:15 | 2022-10-04 17:00 | 2022-10-03 16:15 |  |  | Completed
MSA-DFES | WA5987741 | 3 | Protek 24/7 Building & Maintenance | Ground - Rear of change room 2 - External Yard gate is not latching to close | Building | Steel Fencing & Gates | 225.68 | Pass | Pass | 0 | 0 | 1 | 2022-10-03 13:59 | 2022-10-10 17:00 | 2022-10-07 10:45 | 2022-10-10 17:00 | 2022-10-07 11:45 |  |  | Re instated latching mechanism with new fixing
MSA-DFES | WA5990109 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room door 3- door is faulting as per defects team | Electrical | General Electrical | 134.46 | Pass | Pass | 0 | 0 | 1 | 2022-10-04 13:20 | 2022-10-05 17:00 | 2022-10-04 13:45 | 2022-10-05 17:00 | 2022-10-04 14:45 |  |  | Located faulty roller door. Staff advised when the door is up the motor is still on. They also tried to turn it off with the the emergency stop but it didn’t work. Test the roller door several times and it was working also test the emergency stop and that was also working. Discussed with staff on site and they advised the roller door guys were on site yesterday looking at the door and motor. I think what the roller door guys did yesterday fixed the problem. I showed staff that the emergency stop does work and the motor does stop when the door is open.
MSA-DTAG | WA5993164 | 0 | Sapio Pty Ltd | ground main entry door glass door not opening by itself | Security | Access Control | 209.82 | Pass | Pass | 0 | 0 | 1 | 2022-10-05 08:53 | 2022-10-05 10:53 | 2022-10-05 10:00 | 2022-10-05 12:53 | 2022-10-05 11:00 |  |  | Found time zone out of sync with controller. Downloaded system to controller. Tested, all OK
MSA-DTWD | WA5995239 | 2 | Protek 24/7 Building & Maintenance | C Block - Roof - Walkway Outside C20 Customer Service- Reticulation (poly pipe) broken on roof | Roofing | Metal Roofing | 122.38 | Pass | Pass | -1 | -1 | 1 | 2022-10-06 11:38 | 2022-10-11 17:00 | 2022-10-06 13:00 | 2022-10-11 17:00 | 2022-10-06 14:00 |  |  | Replaced elbo bends x2 site supplied
MSA-DFES | WA5995732 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Disabled Toilet - Hinge on toilet seat is broken - See notes below | Plumbing & Drainage | Toilets/Cisterns | 529.45 | Pass | Pass | 0 | 0 | 1 | 2022-10-06 15:35 | 2022-10-11 17:00 | 2022-10-11 09:15 | 2022-10-11 17:00 | 2022-10-11 10:15 |  |  | Attended site for broken toilet seat in disabled toilet on ground floor I have replaced the broken toilet seat after I’ve tested everything is working correctly cleaned up packed up
MSA-DTWD | WA5997768 | 3 | COMMERCIAL PLUMBING AND GAS | Engineering Courtyard behind RM 128 - courtyard tap leaking through spigot | Plumbing & Drainage | Water | 143.88 | Pass | Pass | -1 | -1 | 1 | 2022-10-07 09:35 | 2022-10-14 17:00 | 2022-10-07 16:00 | 2022-10-14 17:00 | 2022-10-07 17:00 |  |  | Replaced hose tap
MSA-DTWD | WA5998217 | 2 | AWB Co. | Check power to up right belt sanding machine in the glazing workshop | Electrical | General Electrical | 217.83 | Fail | Fail | 0 | 0 | 1 | 2022-10-07 12:52 | 2022-10-12 17:00 | 2022-10-13 08:30 | 2022-10-12 17:00 | 2022-10-13 09:30 |  |  | Attended site signed in jsa completed. found belt sander in glazing as tech showed us what he needed done. Sander had been refurbished he needed it connected back up into motor and terminal box. All connected and working. Also one additional belt sander will be going for refurb, disconnected for client and left parts on side for tech. Job completed
MSA-DTAG | WA6000663 | 3 | PPM Project Painting & Maintenance | Exit ramp of Sally Port - Graffiti on air vent | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1 | 2022-10-10 09:34 | 2022-10-17 17:00 | 2022-10-17 07:00 | 2022-10-17 17:00 | 2022-10-17 08:00 |  |  | removal of graffit
MSA-DTWD | WA6001274 | 2 | High Tech Pest Control | Bee hive/swarm inside wall cavity outside E74 | Pest Control | Specialist Pest | 205.25 | Pass | Pass | 0 | 0 | 1 | 2022-10-10 14:34 | 2022-10-13 17:00 | 2022-10-11 07:00 | 2022-10-13 17:00 | 2022-10-11 08:00 |  |  | all completed it was a kill job due to being in the wall
MSA-DTWD | WA6008344 | 3 | AWB Co. | Heavy Plant workshop 3D20-Faulty fan switch on north wall | Electrical | General Electrical | 254.79 | Pass | Pass | 0 | 0 | 1 | 2022-10-11 13:33 | 2022-10-18 17:00 | 2022-10-18 13:00 | 2022-10-18 17:00 | 2022-10-18 14:00 |  |  | Attended site signed in jsa completed. Found switch in way of cupboard always being broken. Advised to move to other side wall. Moved with conduit and placed on north wall. Tested okJob completed
MSA-DTAG | WA6014871 | 1 | Sapio Pty Ltd | Ground-registry-Unable to select Pacom on computer-see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-12 12:36 | 2022-10-13 17:00 | 2022-10-12 13:00 | 2022-10-13 17:00 | 2022-10-12 14:00 |  |  | Investigated reported issue. Found there was a software issue with Pacom GMS and server was not registering keyboardinput. Restarted server, system all good.
MSA-DCA | WA6022962 | 3 | Techworks Electrical | Epoch Café- ground- Exposed wiring hanging down from the door rails.-see notes | Electrical | General Electrical | 230.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-14 13:51 | 2022-10-21 17:00 | 2022-10-19 08:30 | 2022-10-21 17:00 | 2022-10-19 09:30 |  |  | Redundant cable hanging from bifold doors, wire looks like it was tucked away rather than pulled out, we have pulled out redundant wire.
MSA-DTAG | WA6044377 | 1 | AWB Co. | ground - Courtroom 4 - Lights are very dim - See notes below | Electrical | Lighting, Internal | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-10-17 10:31 | 2022-10-18 17:00 | 2022-10-17 13:00 | 2022-10-18 17:00 | 2022-10-17 14:00 |  |  | Attended site signed in jsa complete. Found push button dimmer switch dimmed to lowest setting in room 4. Pushed back to correct setting and informed staff of job.Job completed
MSA-DTAG | WA6071855 | 0 | Sapio Pty Ltd | Detention - Gallagher system is down | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-10-18 08:22 | 2022-10-18 10:22 | 2022-10-18 08:30 | 2022-10-18 12:22 | 2022-10-18 09:30 |  |  | Logged into Gallagher and confirmed correct operation of system
MSA-DCA | WA6090867 | 1 | Protek 24/7 Building & Maintenance | Rear of State Library-tree Small BMX bike in tree, please remove safely.-see notes | Labour Hire | Handyperson LH | 122.4 | Pass | Pass | 0 | 0 | 1 | 2022-10-19 14:43 | 2022-10-20 17:00 | 2022-10-20 07:00 | 2022-10-20 17:00 | 2022-10-20 08:00 |  |  | Removed stunt bike from tree eliminating the risk of a falling object
MSA-DTWD | WA6105997 | 2 | AWB Co. | Flickering light in classroom R018 | Electrical | Lighting, Internal | 146.41 | Pass | Pass | 0 | 0 | 1 | 2022-10-20 07:44 | 2022-10-24 17:00 | 2022-10-21 08:30 | 2022-10-24 17:00 | 2022-10-21 09:30 |  |  | Attended site and signed in, completed JSA, located r018 , replaced tubes and starters, tested lights and working as intended, completed paperwork,signed out **job completed **
MSA-DTAG | WA6125677 | 1 | Sapio Pty Ltd | Issue with treasury access cards database - Please see notes | Security | Keys & Access | 139.88 | Fail | Fail | 0 | 0 | 1 | 2022-10-25 06:54 | 2022-10-25 17:00 | 2022-10-26 13:00 | 2022-10-25 17:00 | 2022-10-26 14:00 |  |  | Rectified card error
MSA-DTWD | WA6125942 | 3 | GRAFFITI FORCE PTY LTD | Graffiti - Aberdeen Exit doors and other external areas | Cleaning | Graffiti | 264 | Fail | Fail | 0 | 0 | 1 | 2022-10-25 09:33 | 2022-11-01 17:00 | 2022-11-03 08:50 | 2022-11-01 17:00 | 2022-11-03 09:50 |  |  | REMOVAL OF GRAFFITI FROM EXTERNAL WALLS OF BUILDING
MSA-DTAG | WA6128015 | 1 | High Tech Pest Control | Ground - Registry - Registry & admin area requires to be sprayed for midgies | Pest Control | General Pest | 454.41 | Fail | Fail | 1 | 1 | 1 | 2022-10-26 11:41 | 2022-10-27 17:00 | 2022-11-04 16:00 | 2022-10-27 17:00 | 2022-11-04 17:00 |  | WCAPPR | Recommend to seal the top of entrance doors to reception/foyer.
MSA-DTAG | WA6131820 | 3 | Midolo Building Services | 1987 - level 1 - Corridor - Investigate damp patches in ceiling outside lift 3 | Building | Ceiling | 170.63 | Pass | Pass | -1 | -1 | 1 | 2022-10-31 09:55 | 2022-11-07 17:00 | 2022-10-31 10:45 | 2022-11-07 17:00 | 2022-10-31 11:45 |  |  | potential roof leak spots sealed/cleaned/repaired - flashings
MSA-DTWD | WA6132194 | 2 | AWB Co. | Flickering light in Balga Library | Electrical | Lighting, Internal | 209.04 | Pass | Pass | 0 | 0 | 1 | 2022-10-31 12:20 | 2022-11-03 17:00 | 2022-11-01 11:30 | 2022-11-03 17:00 | 2022-11-01 12:30 |  |  | Attended site and signed in, completed JSA,spoke with fm and librarian about faulty lighting, replaced lights as requested by library staff, lights now working as intended, disposed of tubes in allocated bin on site, cleaned up, packed up, completed paperwork,signed out , **job complete*
MSA-DTWD | WA6132221 | 1 | BJ SYSTEMS | T, U & V Block - CCTV is not working (maybe needs new hard drive) | Security | CCTV Surveillance | 180 | Pass | Pass | 0 | 0 | 1 | 2022-10-31 12:36 | 2022-11-01 17:00 | 2022-11-01 08:30 | 2022-11-01 17:00 | 2022-11-01 09:30 |  |  | Attend site and signed in. Checked CCTV with Dennis and Michael, had a chat with IT and found NVR has been o?ine and powered down due to faults for some time. Customer has requested a quote to add in a 32 channel Hikvision NVR to run the cameras. Signed out and left site
MSA-DCA | WA6132556 | 3 | Techworks Electrical | Bottom of spiral staircase - no power to phase 3 outlet | Electrical | General Electrical | 326.61 | Pass | Pass | -1 | -1 | 1 | 2022-10-31 15:10 | 2022-11-07 17:00 | 2022-11-01 13:00 | 2022-11-07 17:00 | 2022-11-01 14:00 |  |  | arrived and Brvce showed me the outlet. It's a 40a 3 phase 56series with no isolator. Couldn't find anv breaker in anv board not on.Traced cable and it goes into the floor then we. Any find it. We couldn't lift floor boards as pica was open. To have a proper big look Into it, it'll need to be opened up on a Monday when pica isn't open to the public. Bryce has said its not a big deal for it not working as they can get power from elsewhere
MSA-DTWD | WA6147591 | 2 | COMMERCIAL PLUMBING AND GAS | AT07 Classroom - Water valve is seized - See notes below | Plumbing & Drainage | Water | 178.88 | Pass | Pass | -1 | -1 | 1 | 2022-11-03 08:33 | 2022-11-08 17:00 | 2022-11-04 14:30 | 2022-11-08 17:00 | 2022-11-04 15:30 |  |  | installed new valve, removed obsolete pipe
MSA-DTWD | WA6148377 | 0 | Securex Security Systems & Services | P.I.R. is in alarm | Security | Security Management System | 450 | Pass | Pass | 0 | 0 | 1 | 2022-11-03 16:06 | 2022-11-03 18:06 | 2022-11-03 17:30 | 2022-11-03 20:06 | 2022-11-03 18:30 |  |  | 03/11/2022, 1730-1830Found guard isolated multiple zonesChecked PSU DGP 2 and DGP 5Checked fuses to these All tested OkChecked zone 85 where glass had been replaced and found all terminals very loose Tightened all these up and tested Ok
MSA-DCA | WA6149401 | 0 | Critical Fire Protection & Training | Ground Floor - Fire Panel - System 7 - in alarm | Fire Protection Services | Fire Protection - Monitor System | 258.87 | Pass | Pass | 0 | 0 | 1 | 2022-11-04 15:12 | 2022-11-04 17:12 | 2022-11-04 16:00 | 2022-11-04 19:12 | 2022-11-04 17:00 |  |  | Upon arrival, all systems normal on the fire panel.Code red showing system 7 alarm due to an existing fuel leak on the secondary/standby diesel pump (in progress of repair). This is an advisory alarm to the monitoring company, not an actionable alarm that will call the brigade. A quote for repairs has been submitted for approval.
MSA-DTWD | WA6153288 | 0 | AWB Co. | Glass door fallen off hinges - door is swipe card accessed, cannot arm building | Glazing | Door Glass | 1313.42 | Fail | Fail | 0 | 0 | 1 | 2022-11-07 09:48 | 2022-11-07 11:48 | 2022-11-07 13:00 | 2022-11-07 13:48 | 2022-11-07 14:00 |  |  | Works completed
MSA-DTAG | WA6155656 | 3 | AWB Co. | Registry Hallway - Flickering Light in Hallway near Kitchen & Light cover has almost come off | Electrical | Lighting, Internal | 224.21 | Pass | Pass | -1 | -1 | 1 | 2022-11-08 12:13 | 2022-11-15 17:00 | 2022-11-11 10:00 | 2022-11-15 17:00 | 2022-11-11 11:00 |  |  | Attended site signed in jsa completed. Found light out as shown by staff and also diffuser hanging. Replaced light tubes in fitting and re secured diffuser in light. Job completed
MSA-DCA | WA6157226 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | Ground floor - side access door - staff reporting electric shock when button was touched | Electrical | General Electrical | 134.46 | Pass | Pass | 0 | 0 | 1 | 2022-11-09 13:57 | 2022-11-09 15:57 | 2022-11-09 14:30 | 2022-11-09 17:57 | 2022-11-09 15:30 |  |  | Tyler Beard (09/11/2022) - Work NoteAttended site at 1430 to investigate reported “electric shock”, received off a switch, by a staff member. Switch in question is a plastic switch and part of an ELV switching system, operating voltages of less than 3V were found when testing. I was unable to recreate or find any fault, which leads me to believe the reported shock was that of a potential static discharge. Informed staff of results of my visit and left site at 1530.Notes: The staff member that showed me the switch was the one who had received and reported the supposed “shock”. He had said that he received the shock a few days ago, reported it via a physical incident report, that was only found and immediately raised as a P0 today by the BMO. He had not barricaded the switch off or even labelled the switch as having an issue, and other staff members have told me the switch had been frequently used the past few days (I suspect even since the staff member believes he was shocked) and n
MSA-DCA | WA6157351 | 1 | Techworks Electrical | L3 and L5 - Stairwell 2 - White lights flickering or out in stairwell | Electrical | Lighting, Internal | 217.56 | Pass | Pass | 0 | 0 | 1 | 2022-11-09 15:46 | 2022-11-10 17:00 | 2022-11-10 14:30 | 2022-11-10 17:00 | 2022-11-10 15:30 |  |  | Replaced failed globes. All working well.
MSA-DCA | WA6157356 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Monitoring |  | Pass | Pass | 0 | 0 | 1 | 2022-11-09 15:51 | 2022-11-10 17:00 | 2022-11-09 16:00 | 2022-11-10 17:00 | 2022-11-09 17:00 | 1 |  | Completed
MSA-DTWD | WA6157387 | 0 | Casa Security Pty Ltd | C, D & E Block - Security Panel dropped out | Security | Monitoring | 407 | Pass | Pass | 0 | 0 | 1 | 2022-11-09 16:48 | 2022-11-09 18:48 | 2022-11-09 17:30 | 2022-11-09 20:48 | 2022-11-09 18:30 |  |  | 09/11 AFTER HOURS CALL OUTFOUND KEYPADS FOR C, D & E BLOCK ALL OPEN CIRCUITDETERMINED CABLE RELATED ISSUE CAUSING PROBLEMISOLATED EXTERNAL CABLES TO ALLOW GLOBAL ARMING FROM THE LIBRARYTEMPORARY FIX UNTIL WE CAN REATTEND IN NORMAL BUSINESS HOURSENSURED ALL WORKING OK BEFORE LEAVING SITERETURN VISIT 10/11TECHNICIAN FOUND UNIDENTIFIED CABLE CONNECTED TO D BLOCK HAD FAILEDDETERMINED CABLE NOT NEEDED - DISCONNECTEDENSURED SYSTEM SEALED & ALL WORKING
MSA-DTWD | WA6158826 | 1 | AHS Services WA Pty Ltd (Anchor) | toilet not flushing properly | Plumbing & Drainage | Toilets/Cisterns | 191.45 | Pass | Pass | 0 | 0 | 1 | 2022-11-10 09:24 | 2022-11-11 17:00 | 2022-11-10 14:30 | 2022-11-11 17:00 | 2022-11-10 15:30 |  |  | Adjusted cicten to be a bigger flush foam form a essence bottle was creating to much foam I advised that they take it out and use something different or less foamy
MSA-DFES | WA6158835 | 3 | ACTION GLASS & ALUMINIUM | Ground - Workshop - Cracked window - See notes below | Glazing | Window Glass | 323.68 | Pass | Pass | -1 | -1 | 1 | 2022-11-10 09:27 | 2022-11-17 17:00 | 2022-11-10 13:00 | 2022-11-17 17:00 | 2022-11-10 14:00 |  |  | ATTENDED SITE REGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-840 X 737PLUS 3.5 L/M OF RUBBER REPLACED
MSA-DCA | WA6158884 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Guards |  | Fail | Fail | 2 | 2 | 1 | 2022-10-23 06:00 | 2022-10-24 17:00 | 2022-11-10 10:00 | 2022-10-24 17:00 | 2022-11-10 11:00 | 1 |  | Completed
MSA-DCA | WA6158894 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - Request for security attendance - SEE NOTES | Security | Guards |  | Fail | Fail | 2 | 2 | 1 | 2022-10-23 09:00 | 2022-10-24 17:00 | 2022-11-10 10:00 | 2022-10-24 17:00 | 2022-11-10 11:00 | 1 |  | Completed
MSA-DTWD | WA6177874 | 2 | AWB Co. | Room F30 - Faulty light sensor | Electrical | Lighting, Internal | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-11-14 08:14 | 2022-11-17 17:00 | 2022-11-14 08:30 | 2022-11-17 17:00 | 2022-11-14 09:30 |  |  | Attended site signed in jsa completed. Found sensor connected in class. Instructed to disconnect behind sensor for light switch operation only.Job completed
MSA-DTWD | WA6178572 | 3 | AWB Co. | Kitchen - Store Room - LED light not working | Electrical | Lighting, Internal | 285.33 | Pass | Pass | -1 | -1 | 1 | 2022-11-14 12:13 | 2022-11-21 17:00 | 2022-11-17 08:30 | 2022-11-21 17:00 | 2022-11-17 09:30 |  |  | Attended site signed in jsa completed. Found dull light in store room with faulty driver. Replaced with new sal led wp fitting.Tested operational.Job completed
MSA-DTWD | WA6183943 | 2 | AWB Co. | Workshop F001 - emergency stop button needs replacing on drop saw - See notes below | Equipment | Electrical Equipment | 217.83 | Pass | Pass | 0 | 0 | 1 | 2022-11-15 09:16 | 2022-11-18 17:00 | 2022-11-16 08:30 | 2022-11-18 17:00 | 2022-11-16 09:30 |  |  | Attended site signed in jsa completed.Found loose emergency stop on saw. Unplugged and isolated. opened control box and tighten gland till it was back in position.Job completed
MSA-DTAG | WA6191282 | 2 | GPS Plumbing & Gas Services PtyLtd | Upstairs - Male toilet cubicle 2 - constantly running | Plumbing & Drainage | Toilets/Cisterns | 113.43 | Pass | Pass | -1 | -1 | 1 | 2022-11-16 14:43 | 2022-11-21 17:00 | 2022-11-17 15:08 | 2022-11-21 17:00 | 2022-11-17 16:08 |  |  | Raised cistern so the outlset valve can close properly, tested multiple times
MSA-DCA | WA6230771 | 1 | Techworks Electrical | James St Bollards - Bollards not lowering fully. | Electrical | General Electrical | 135.15 | Pass | Pass | 0 | 0 | 1 | 2022-11-18 12:42 | 2022-11-21 17:00 | 2022-11-18 13:00 | 2022-11-21 17:00 | 2022-11-18 14:00 |  |  | Removed face plate from bollard. Lowered bollard and pushed down as it went down to push up excess water built up underneath due to the wet weather. Issue is reacquiring during wet weather, there may be a drainage issue
MSA-DTWD | WA6249292 | 2 | AWB Co. | Front counter - flickering light | Electrical | Lighting, Internal | 225.21 | Pass | Pass | 0 | 0 | 1 | 2022-11-21 11:08 | 2022-11-24 17:00 | 2022-11-24 10:00 | 2022-11-24 17:00 | 2022-11-24 11:00 |  |  | Attended site and signed in. Completed JSA. Liaised with office ladies about flickering light. Supplied and replaced globes to fitting. Tested for correct operation. All working correctly. Notified relevant personnel of works completed. **job complete**
MSA-DCA | WA6253804 | 1 | Protek 24/7 Building & Maintenance | Fault description Damage in the fencing at Sunset, outside Q block towards P block. See notes | Building | Steel Fencing & Gates | 159.9 | Pass | Pass | 0 | 0 | 1 | 2022-11-22 12:14 | 2022-11-23 17:00 | 2022-11-23 07:00 | 2022-11-23 17:00 | 2022-11-23 08:00 |  |  | Re threaded wire through fence
MSA-DFES | WA6254091 | 0 | Anvil Doors | Engine room - Main roller door come off tracks on one side | Building | Automatic Doors | 565.5 | Pass | Pass | 0 | 0 | 1 | 2022-11-22 15:18 | 2022-11-22 17:18 | 2022-11-22 16:00 | 2022-11-22 19:18 | 2022-11-22 17:00 |  |  | Front Left ISLO shutterHas been hit on exitBottom 2 LH wheels and 1 RH have come out of the tracksTracks, wheels and hinges bentRemoved hinges and straightenedPut on new wheelsStraightened out tracksDoor is operationalHinges should be replacedx 2
MSA-DTWD | WA6257418 | 1 | Complete Pest Management Services | Ground floor - customer service centre - Infestation of possums | Pest Control | Specialist Pest | 103.3 | Pass | Pass | 0 | 0 | 1 | 2022-11-24 15:16 | 2022-11-25 17:00 | 2022-11-25 10:45 | 2022-11-25 17:00 | 2022-11-25 11:45 |  |  | I've Not scheduled jobs when they should have, coworker is away. Job completed 25/11/22
MSA-DTWD | WA6258643 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet seat has broken off pan. | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | 0 | 0 | 1 | 2022-11-25 14:07 | 2022-11-30 17:00 | 2022-11-30 10:00 | 2022-11-30 17:00 | 2022-11-30 11:00 |  |  | Refitted toilet seat
MSA-DTAG | WA6291398 | 1 | Schindler Lifts Australia | Lift 3 is showing “out of service” | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-11-28 14:44 | 2022-11-29 17:00 | 2022-11-29 09:40 | 2022-11-29 17:00 | 2022-11-29 10:40 |  |  | Found lift on JRVP. No errors in Log checked door operation. Fine. Lift left in service
MSA-DTAG | WA6298991 | 2 | Sapio Pty Ltd | Turnstyle - having issues with key cards not registering properly | Security | Security Management System | 129.12 | Fail | Fail | 0 | 0 | 1 | 2022-12-01 16:53 | 2022-12-06 17:00 | 2022-12-07 11:30 | 2022-12-06 17:00 | 2022-12-07 12:30 |  |  | Reset power on turnstiles, checked all ok.
MSA-DTWD | WA6301203 | 2 | OTIS ELEVATOR COMPANY PTY LTD | Lift button on Level 2 falling off | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 1 | 2022-12-02 15:09 | 2022-12-07 17:00 | 2022-12-02 15:15 | 2022-12-07 17:00 | 2022-12-02 16:15 |  |  | Completed
MSA-DCA | WA6358708 | 2 | FCT SURFACE CLEANING | Ground Floor Exterior - Gantry hoarding (Murray St side) - Graffiti on hoardin | Cleaning | Graffiti |  | Pass | Pass | 0 | 0 | 1 | 2022-12-06 09:25 | 2022-12-09 17:00 | 2022-12-09 10:00 | 2022-12-09 17:00 | 2022-12-09 11:00 |  |  | Ground Floor Exterior - Gantry hoarding (Murray St side) - Graffiti on hoardingRestored
MSA-DTWD | WA6358766 | 1 | SENTINEL LOCK SERVICE PTY LTD | 9G2 (old bookshop) - Door lock faulty | Security | Keys & Access | 137.32 | Pass | Pass | 0 | 0 | 1 | 2022-12-06 09:58 | 2022-12-07 17:00 | 2022-12-06 10:25 | 2022-12-07 17:00 | 2022-12-06 11:25 |  |  | 9G2 - (old bookshop) door lock faulty.Lock serviced.
MSA-DCA | WA6361908 | 1 | Techworks Electrical | 3x Lollipop lights not working - see notes below | Electrical | Lighting, External | 206.62 | Pass | Pass | 0 | 0 | 1 | 2022-12-08 15:43 | 2022-12-09 17:00 | 2022-12-09 14:30 | 2022-12-09 17:00 | 2022-12-09 15:30 |  |  | Reset tripped rcd, checked light that wasnt working, however historical fault in the cabling back to fiji has this light disconnected, 2 x lights back up and running tested and all OK.
MSA-DFES | WA6362885 | 3 | Protek 24/7 Building & Maintenance | Room 34 (BA room) - 3 windows no longer close as they have seized open | Building | Windows | 141.78 | Pass | Pass | 0 | 0 | 1 | 2022-12-09 14:33 | 2022-12-16 17:00 | 2022-12-13 07:45 | 2022-12-16 17:00 | 2022-12-13 08:45 |  |  | Lubricated chain mechanisms to all 4 windows in BA room
MSA-DCA | WA6363983 | 1 | GPS Plumbing & Gas Services PtyLtd | C&K - Restaurant - Hot water system has slow leak (near coffee machine) | Plumbing & Drainage | HWS/Units Electric & Gas | 285.81 | Pass | Pass | 0 | 0 | 1 | 2022-12-12 08:39 | 2022-12-13 17:00 | 2022-12-12 12:40 | 2022-12-13 17:00 | 2022-12-12 13:40 |  |  | Replaced faulty hot relief valves
MSA-DTAG | WA6364780 | 1 | Sapio Pty Ltd | ground Hay street stair internal-camera C004-getting date camera fail | Security | Security Management System | 129.12 | Pass | Pass | 0 | 0 | 1 | 2022-12-12 14:55 | 2022-12-13 17:00 | 2022-12-13 11:30 | 2022-12-13 17:00 | 2022-12-13 12:30 |  |  | Reset camera and reprogrammed to Milestone.
MSA-DFES | WA6365913 | 2 | Water2water Pty Ltd | Radio Comms Kitchen-Zip Boiler is leaking in Radio Communications Kitchen | Plumbing & Drainage | Water | 374.44 | Pass | Pass | 0 | 0 | 1 | 2022-12-13 13:14 | 2022-12-16 17:00 | 2022-12-16 10:20 | 2022-12-16 17:00 | 2022-12-16 11:20 |  |  | Replaced dripping tap to Zip Mini Boil and Tested
MSA-DCA | WA6366127 | 1 | Wilson Security | Retrospective work Order - No Attendance Required - Security attendance | Security | Guards |  | Fail | Fail | 0 | 0 | 1 | 2022-12-11 14:00 | 2022-12-12 17:00 | 2022-12-13 16:00 | 2022-12-12 17:00 | 2022-12-13 17:00 | 1 |  | Completed
MSA-DTWD | WA6375686 | 3 | AWB Co. | Fault light showing on S08 Board - Microbiology exhaust fan | Electrical | General Electrical | 122.1 | Pass | Pass | -1 | -1 | 1 | 2022-12-15 09:47 | 2022-12-22 17:00 | 2022-12-16 14:30 | 2022-12-22 17:00 | 2022-12-16 15:30 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Found to be fault light on exhaust fan in plant room. Upon investigation found to be thermal overload had tripped. Reset and ran exhaust fan. Tested cables to see how much motor is drawing and is drawing a little higher then normal. Motor is running. Have advised site of works and to keep an eye on it. **job complete**
MSA-DCA | WA6375815 | 1 | Techworks Electrical | Tree opposite Pollys Café - Light timer needs adjusting, lights are going off at 8pm rather than 11 | Electrical | General Electrical | 135.15 | Pass | Pass | 0 | 0 | 1 | 2022-12-15 10:51 | 2022-12-16 17:00 | 2022-12-15 14:30 | 2022-12-16 17:00 | 2022-12-15 15:30 |  |  | Re programmed timer
MSA-DTAG | WA6377003 | 3 | Midolo Building Services | Level 4 - Adult Community Corrections - Cupboard door has come off - see note | Building | General Building | 121.59 | Fail | Fail | 2 | 2 | 1 | 2022-12-16 10:08 | 2022-12-23 17:00 | 2023-01-04 10:00 | 2022-12-23 17:00 | 2023-01-04 11:00 |  |  | reattached door
MSA-DTAG | WA6377397 | 2 | Schindler Lifts Australia | Ground - Lift 10 - showing out of service | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 1 | 2022-12-16 13:46 | 2022-12-21 17:00 | 2022-12-19 07:00 | 2022-12-21 17:00 | 2022-12-19 08:00 |  |  | closed out at $0 cost
MSA-DCA | WA6381698 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - ATT 20/11-DO NOT ATTEND | Security | Security Management System |  | Fail | Fail | 4 | 4 | 1 | 2022-11-20 16:30 | 2022-11-21 17:00 | 2022-12-19 13:45 | 2022-11-21 17:00 | 2022-12-19 14:45 | 1 |  | Completed
MSA-DCA | WA6381703 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER-ATT 19/11-DO NOT ATTEND | Security | Security Management System |  | Fail | Fail | 4 | 4 | 1 | 2022-11-19 16:05 | 2022-11-21 17:00 | 2022-12-19 13:45 | 2022-11-21 17:00 | 2022-12-19 14:45 | 1 |  | Completed
MSA-DTWD | WA6383898 | 3 | AWB Co. | LED light fitting has come loose at one end and is hanging | Electrical | Lighting, Internal | 206.84 | Pass | Pass | -1 | -1 | 1 | 2022-12-20 15:03 | 2022-12-29 17:00 | 2022-12-21 07:00 | 2022-12-29 17:00 | 2022-12-21 08:00 |  |  | Arrived at site, signed in, completed jsa, talked with fm, reattached led light to roof, checked to see if everything is working, all working, packed up and cleaned up, sign out, completed paperwork. ***Job complete***
MSA-DTWD | WA6384382 | 1 | Dormakaba Australia Pty Ltd | Entrance/Exit - Auto sliding door inoperative and unable to be locked - see notes below | Building | Automatic Doors | 766.15 | Pass | Pass | 0 | 0 | 1 | 2022-12-21 08:26 | 2022-12-22 17:00 | 2022-12-21 11:37 | 2022-12-22 17:00 | 2022-12-21 12:37 |  |  | On inspection found that the door was showing Error 3 program switch. Replaced SK4 switch. Tightened loose floor guide and loose carriage bar guides. Performed full reset. Tested numerous times and all working fine. Left area clean and tidy.
MSA-DTAG | WA6384943 | 1 | Midolo Building Services | Level 13 - Judicial floor - Hallway near kitchen - Corner piece of skirting board | Carpentry | Materials | 195.13 | Fail | Fail | 1 | 1 | 1 | 2022-12-21 09:09 | 2022-12-22 17:00 | 2022-12-29 07:00 | 2022-12-22 17:00 | 2022-12-29 08:00 |  |  | re secured damaged skirting to wall
MSA-DTWD | WA6385756 | 0 | OTIS ELEVATOR COMPANY PTY LTD | Elevators 2 & 3-High level water alarm indicated Otis - see notes | Lifts | Lifts |  | Fail | Fail | 5 | 5 | 1 | 2022-12-21 10:03 | 2022-12-21 12:03 | 2023-01-22 07:00 | 2022-12-21 14:03 | 2023-01-22 08:00 |  |  | Repairs to lift
MSA-DFES | WA6389270 | 2 | Australian HVAC Services Pty. Ltd. | Ground - Station Officers Office - AC blows out room temp air - See Notes Below | Air Conditioning | Room Air Conditioners | 201.88 | Pass | Pass | 0 | 0 | 1 | 2022-12-21 14:17 | 2022-12-28 17:00 | 2022-12-28 08:30 | 2022-12-28 17:00 | 2022-12-28 09:30 |  |  | Arrived on site and spoke to site representative about the issue with the AC. Found out the indoor units served from CU.1 are not cooling. Turned all indoor heads setpoint to 17°C and got 20°C supply air with 22°C return air. Located the outdoor unit and found that the condenser fan was not running. Opened up the unit and Attached gauges. Reset the unit and allowed system to start up. When system starts up pressures are low. SET: -8°C and SCT: 26°C. Attempted to put system into test run but unit only ran in test mode for a moment before stopping the compressor. Unit didn't have any error messages on the indoor or outdoor unit. Fetched most recent retry error code and found E3 code which is faulty high pressure switch. Determined unit is low on refrigerant and requires gas leak investigation + repair.
MSA-DTAG | WA6390470 | 2 | High Tech Pest Control | Ground - Registry - Cockroaches around the office & kitchen | Pest Control | General Pest | 280.15 | Pass | Pass | 0 | 0 | 1 | 2022-12-22 09:30 | 2022-12-29 17:00 | 2022-12-29 16:00 | 2022-12-29 17:00 | 2022-12-29 17:00 |  |  | Cockroaches around the office & kitchenuse of goliath cockroach gel, seclira and Clear out flush
MSA-DTAG | WA6391752 | 1 | Sapio Pty Ltd | Level 6-seating room 6.03-insetion button is active and cannot be de activated | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 1 | 2022-12-22 16:08 | 2022-12-23 17:00 | 2022-12-23 08:30 | 2022-12-23 17:00 | 2022-12-23 09:30 |  |  | Work performed by Ken Moore (23/12/2022)Attended site. Restored Pacom controllers software on Level 6.Job completed.
MSA-DFES | WA6393034 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 4 - Disabled Toilet - Cistern intermittently filling | Plumbing & Drainage | Toilets/Cisterns | 232.23 | Pass | Pass | -1 | -1 | 1 | 2022-12-28 08:50 | 2023-01-03 17:00 | 2022-12-29 07:45 | 2023-01-03 17:00 | 2022-12-29 08:45
MSA-DCA | WA6394247 | 3 | Earth & Water Pty Ltd | Urban Orchard - Broken retic | Landscaping & Gardening | Grounds Maintenance |  | Fail | Fail | 3 | 3 | 1 | 2022-12-30 10:09 | 2023-01-09 17:00 | 2023-02-01 07:00 | 2023-01-09 17:00 | 2023-02-01 08:00
MSA-DTAG | WA6400335 | 0 | Seme Solutions Pty Ltd | Court room 2 - Electronic door to courtroom is in locked position and cannot be opened | Security | Access Control | 139.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-03 11:23 | 2023-01-03 13:23 | 2023-01-03 11:30 | 2023-01-03 15:23 | 2023-01-03 12:30
MSA-DTAG | WA6401508 | 2 | Midolo Building Services | 7.4 Pre Trial Room - Gate between staff desk and public isn't locking - Barrel isn't locking | Building | Doors | 160.09 | Pass | Pass | -1 | -1 | 1 | 2023-01-04 12:27 | 2023-01-09 17:00 | 2023-01-04 13:00 | 2023-01-09 17:00 | 2023-01-04 14:00
MSA-DFES | WA6402449 | 3 | Protek 24/7 Building & Maintenance | Seal has dislodged from glass panel in board room | Building | Windows | 141.15 | Pass | Pass | -1 | -1 | 1 | 2023-01-05 11:48 | 2023-01-12 17:00 | 2023-01-06 07:00 | 2023-01-12 17:00 | 2023-01-06 08:00
MSA-DTAG | WA6403168 | 0 | Sapio Pty Ltd | Level 6-L6.01 emergency lock interview room-tamper-open circuit-see notes | Security | Security Management System | 139.88 | Pass | Pass | 0 | 0 | 1 | 2023-01-06 08:50 | 2023-01-06 10:50 | 2023-01-06 10:00 | 2023-01-06 12:50 | 2023-01-06 11:00
MSA-DTWD | WA6403517 | 2 | Equans Mechanical Services Australia | W606,605,601-West end Level 6 4 x VAV not bringing temps down | Air Conditioning | Room Air Conditioners | 129.51 | Pass | Pass | 0 | 0 | 1 | 2023-01-06 11:10 | 2023-01-11 17:00 | 2023-01-11 10:00 | 2023-01-11 17:00 | 2023-01-11 11:00
MSA-DFES | WA6404621 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground - Shared Firefighters dorm - 1 light is not working, possible faulty globe | Electrical | Lighting, Internal | 286.71 | Pass | Pass | 0 | 0 | 1 | 2023-01-09 07:50 | 2023-01-13 17:00 | 2023-01-13 07:00 | 2023-01-13 17:00 | 2023-01-13 08:00
MSA-DFES | WA6405135 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room - 5 Fluro Light Globes not working | Electrical | Lighting, Internal | 624.62 | Pass | Pass | 0 | 0 | 1 | 2023-01-09 11:45 | 2023-01-12 17:00 | 2023-01-12 08:30 | 2023-01-12 17:00 | 2023-01-12 09:30
MSA-DTWD | WA6405474 | 2 | BAKE-QUIP PTY LTD | Canteen Kitchen - Oven does not heat up | Electrical | General Electrical | 245 | Pass | Pass | 0 | 0 | 1 | 2023-01-09 14:11 | 2023-01-12 17:00 | 2023-01-11 10:00 | 2023-01-12 17:00 | 2023-01-11 11:00
MSA-DCA | WA6405515 | 2 | Techworks Plumbing | JUB - Level G - UAT bathroom - Cubicle 1 flush plate not working (see notes) | Plumbing & Drainage | Toilets/Cisterns | 135.14 | Pass | Pass | 0 | 0 | 1 | 2023-01-09 14:54 | 2023-01-12 17:00 | 2023-01-11 07:00 | 2023-01-12 17:00 | 2023-01-11 08:00
MSA-DTWD | WA6407928 | 2 | AHS Services WA Pty Ltd (Anchor) | W204 - Staff Kitchen sink slow to drain | Plumbing & Drainage | Drainage | 140.77 | Pass | Pass | 0 | 0 | 1 | 2023-01-10 13:10 | 2023-01-13 17:00 | 2023-01-13 13:00 | 2023-01-13 17:00 | 2023-01-13 14:00
MSA-DFES | WA6414823 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Unit 21 - Ground - Exhaust fan over pump bay (Exhaust system No 1) isn’t working | Electrical | General Electrical | 134.46 | Pass | Pass | -1 | -1 | 1 | 2023-01-11 10:07 | 2023-01-16 17:00 | 2023-01-11 11:30 | 2023-01-16 17:00 | 2023-01-11 12:30
MSA-DFES | WA6415041 | 3 | MR POTHOLE | Asphalt in rear yard cracked and lifting (see notes) | Paving & Roadworks | Asphalt |  | Pass | Pass | 0 | 0 | 1 | 2023-01-11 11:56 | 2023-01-18 17:00 | 2023-01-16 08:30 | 2023-01-18 17:00 | 2023-01-16 09:30
MSA-DTWD | WA6425710 | 2 | Icon Logic Pty Ltd | BMS - Unable to change setting on controller | Air Conditioning | Building HVAC Maintenance (Major Plant) |  | Pass | Pass | -1 | -1 | 1 | 2023-01-12 11:08 | 2023-01-17 17:00 | 2023-01-12 11:30 | 2023-01-17 17:00 | 2023-01-12 12:30
MSA-DTWD | WA6425823 | 2 | Techworks Electrical | light not working | Electrical | Lighting, Internal | 156.29 | Pass | Pass | 0 | 0 | 1 | 2023-01-12 12:03 | 2023-01-17 17:00 | 2023-01-16 11:30 | 2023-01-17 17:00 | 2023-01-16 12:30
MSA-DTWD | WA6431487 | 1 | Precise Air Group | H Block South A/C is not working at all | Air Conditioning | Building HVAC Maintenance (Major Plant) | 345.17 | Fail | Fail | 0 | 0 | 1 | 2023-01-13 15:55 | 2023-01-16 17:00 | 2023-01-17 07:00 | 2023-01-16 17:00 | 2023-01-17 08:00
MSA-DTAG | WA6450037 | 0 | AWB Co. | Court 4 & 5 - Brakeout box to be investigated (see notes) | Electrical | Distribution Board | 206.84 | Fail | Pass | 0 | 0 | 1 | 2023-01-16 09:07 | 2023-01-16 11:07 | 2023-01-16 11:30 | 2023-01-16 13:07 | 2023-01-16 12:30
MSA-DFES | WA6450884 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen - Whilst running, water leaks out of base of tap | Plumbing & Drainage | Water | 165.77 | Pass | Pass | -1 | -1 | 1 | 2023-01-16 15:51 | 2023-01-23 17:00 | 2023-01-18 14:30 | 2023-01-23 17:00 | 2023-01-18 15:30
MSA-DCA | WA6482087 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Light fitting is damaged | Electrical | Lighting, Internal | 258.89 | Pass | Pass | -1 | -1 | 1 | 2023-01-18 07:11 | 2023-01-24 17:00 | 2023-01-20 12:15 | 2023-01-24 17:00 | 2023-01-20 13:15
MSA-DCA | WA6482131 | 3 | Protek 24/7 Building & Maintenance | Venue Management Office - Door handle is sticking and difficult to unlock | Building | Doors | 161.54 | Pass | Pass | -1 | -1 | 1 | 2023-01-18 07:37 | 2023-01-24 17:00 | 2023-01-18 12:15 | 2023-01-24 17:00 | 2023-01-18 13:15 |  | WACCES
MSA-DTWD | WA6482325 | 2 | AHS Services WA Pty Ltd (Anchor) | Leaking urinal men's toilet A104 | Plumbing & Drainage | Water | 105.35 | Pass | Pass | -1 | -1 | 1 | 2023-01-18 09:14 | 2023-01-23 17:00 | 2023-01-19 11:30 | 2023-01-23 17:00 | 2023-01-19 12:30
MSA-DTAG | WA6482464 | 3 | AWB Co. | Supervisor hub in office -Light cover falling - See Notes Below | Electrical | General Electrical | 206.84 | Pass | Pass | 0 | 0 | 1 | 2023-01-18 10:38 | 2023-01-25 17:00 | 2023-01-23 07:00 | 2023-01-25 17:00 | 2023-01-23 08:00
MSA-DFES | WA6504016 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Engine Room - Hot Water System continues to trip out the power and is no longer working. | Plumbing & Drainage | HWS/Units Electric & Gas | 2057.4175 | Pass | Pass | 0 | 0 | 1 | 2023-01-19 12:50 | 2023-01-24 17:00 | 2023-01-23 08:30 | 2023-01-24 17:00 | 2023-01-23 09:30
MSA-DTWD | WA6517429 | 2 | Techworks Electrical | Lights not working | Electrical | Lighting, Internal | 237.04 | Pass | Pass | -1 | -1 | 1 | 2023-01-24 09:46 | 2023-01-30 17:00 | 2023-01-24 14:30 | 2023-01-30 17:00 | 2023-01-24 15:30
MSA-DTWD | WA6518513 | 2 | COMMERCIAL PLUMBING AND GAS | Ground - C1 Staff Room - Leaking mixer in staff kitchen | Plumbing & Drainage | Water | 524.71 | Pass | Pass | 0 | 0 | 1 | 2023-01-25 08:59 | 2023-01-31 17:00 | 2023-01-31 13:00 | 2023-01-31 17:00 | 2023-01-31 14:00
MSA-DFES | WA6519341 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Main building - Area 35 (Outside front door) - Security Light Faulty | Electrical | Lighting, External | 264.48 | Pass | Pass | 0 | 0 | 1 | 2023-01-25 15:51 | 2023-02-02 17:00 | 2023-02-01 07:00 | 2023-02-02 17:00 | 2023-02-01 08:00
MSA-DTWD | WA6520212 | 2 | AWB Co. | One set of 2 Fluro globes not working | Electrical | Lighting, Internal | 216.04 | Pass | Pass | 0 | 0 | 1 | 2023-01-27 11:55 | 2023-02-01 17:00 | 2023-01-30 07:00 | 2023-02-01 17:00 | 2023-01-30 08:00
MSA-DTWD | WA6521331 | 2 | Precise Air Group | Aircon not working - Customer has a spare replacement switch | Air Conditioning | Room Air Conditioners | 208.34 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 10:00 | 2023-02-02 17:00 | 2023-01-30 11:30 | 2023-02-02 17:00 | 2023-01-30 12:30
MSA-DTWD | WA6521584 | 2 | Techworks Electrical | flickering light globe | Electrical | Lighting, Internal | 221.61 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 11:48 | 2023-02-02 17:00 | 2023-02-02 10:00 | 2023-02-02 17:00 | 2023-02-02 11:00
MSA-DTWD | WA6521601 | 2 | AWB Co. | lights keep turning off every 30 minutes | Electrical | Lighting, Internal | 212.59 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 11:56 | 2023-02-02 17:00 | 2023-02-02 13:00 | 2023-02-02 17:00 | 2023-02-02 14:00
MSA-DTWD | WA6521988 | 2 | AWB Co. | Carpet skirting falling from wall outside room W310 - Re glue carpet skirting to wall | Flooring | Carpet | 197.19 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 15:34 | 2023-02-02 17:00 | 2023-01-31 11:30 | 2023-02-02 17:00 | 2023-01-31 12:30
MSA-DTWD | WA6522011 | 2 | Australian Airconditioning Services Pty Ltd | Kitchen - Air cooler not cooling | Air Conditioning | Evaporative Coolers | 242.1 | Pass | Pass | 0 | 0 | 1 | 2023-01-30 16:11 | 2023-02-02 17:00 | 2023-01-31 10:00 | 2023-02-02 17:00 | 2023-01-31 11:00
MSA-DTWD | WA6523219 | 2 | AWB Co. | Faulty electrical faulty | Electrical | General Electrical | 195.16 | Pass | Pass | 0 | 0 | 1 | 2023-01-31 13:23 | 2023-02-03 17:00 | 2023-02-01 13:00 | 2023-02-03 17:00 | 2023-02-01 14:00
MSA-DTWD | WA6529071 | 2 | AHS Services WA Pty Ltd (Anchor) | east Disabled toilet blocked | Plumbing & Drainage | Toilets/Cisterns | 140.77 | Pass | Pass | -1 | -1 | 1 | 2023-02-02 14:16 | 2023-02-07 17:00 | 2023-02-03 10:00 | 2023-02-07 17:00 | 2023-02-03 11:00
MSA-DFES | WA6529110 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Co-location - Ladies Toilets - Blockage to toilets | Plumbing & Drainage | Toilets/Cisterns | 143.6 | Pass | Pass | 0 | 0 | 1 | 2023-02-02 14:40 | 2023-02-02 16:40 | 2023-02-02 15:15 | 2023-02-02 18:40 | 2023-02-02 16:15
MSA-DTWD | WA6529112 | 2 | AWB Co. | Room B333 - Cracked GPO | Electrical | General Electrical | 158.11 | Pass | Pass | 0 | 0 | 1 | 2023-02-02 14:45 | 2023-02-07 17:00 | 2023-02-07 13:00 | 2023-02-07 17:00 | 2023-02-07 14:00
MSA-DTWD | WA6529170 | 1 | PEEL LOCK SERVICES PTY LTD | Fault Description Q Block front door has damaged lock cannot close | Security | Locksmith |  | Pass | Pass | 0 | 0 | 1 | 2023-02-02 16:23 | 2023-02-03 17:00 | 2023-02-03 12:15 | 2023-02-03 17:00 | 2023-02-03 13:15
MSA-DTWD | WA6539180 | 2 | Techworks Electrical | Large Skills Kitchen- Female toilets - Lights out x3 | Electrical | Lighting, Internal | 576.49 | Pass | Pass | 0 | 0 | 1 | 2023-02-08 10:58 | 2023-02-13 17:00 | 2023-02-13 11:30 | 2023-02-13 17:00 | 2023-02-13 12:30
MSA-DCA | WA6539223 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - Wilsons call out - Do not attend see notes | Security | Security Management System |  | Fail | Fail | 0 | 0 | 1 | 2023-02-04 13:30 | 2023-02-06 17:00 | 2023-02-08 11:30 | 2023-02-06 17:00 | 2023-02-08 12:30 | 1
MSA-DTWD | WA6539282 | 2 | M Construction (WA) | Skirting board - library office door - become unstuck | Building | General Building | 149.11 | Fail | Fail | 0 | 0 | 1 | 2023-02-08 11:48 | 2023-02-13 17:00 | 2023-02-15 07:00 | 2023-02-13 17:00 | 2023-02-15 08:00
MSA-DTWD | WA6540036 | 2 | AWB Co. | Faulty light switch - Top one | Electrical | Lighting, Internal | 223.97 | Pass | Pass | -1 | -1 | 1 | 2023-02-09 07:35 | 2023-02-13 17:00 | 2023-02-09 08:30 | 2023-02-13 17:00 | 2023-02-09 09:30
MSA-DTWD | WA6540219 | 2 | Techworks Electrical | light not working | Electrical | Lighting, Internal | 256.74 | Pass | Pass | 0 | 0 | 1 | 2023-02-09 09:20 | 2023-02-14 17:00 | 2023-02-13 07:00 | 2023-02-14 17:00 | 2023-02-13 08:00
MSA-DCA | WA6540399 | 1 | EQUANS Mechanical Services (WA) Pty Limited | Level G - All rooms - Reported area too cold | Air Conditioning | Room Air Conditioners | 146.4 | Pass | Pass | 0 | 0 | 1 | 2023-02-09 10:37 | 2023-02-10 17:00 | 2023-02-09 13:00 | 2023-02-10 17:00 | 2023-02-09 14:00
MSA-DTWD | WA6540585 | 2 | AHS Services WA Pty Ltd (Anchor) | Disabled toilet continuously running | Plumbing & Drainage | Toilets/Cisterns | 122.85 | Pass | Pass | -1 | -1 | 1 | 2023-02-09 11:59 | 2023-02-14 17:00 | 2023-02-09 14:30 | 2023-02-14 17:00 | 2023-02-09 15:30
MSA-DTWD | WA6544470 | 2 | AHS Services WA Pty Ltd (Anchor) | Workshop - Sink bay - Tap is leaking | Plumbing & Drainage | Water | 140.77 | Pass | Pass | 0 | 0 | 1 | 2023-02-10 13:08 | 2023-02-15 17:00 | 2023-02-15 09:15 | 2023-02-15 17:00 | 2023-02-15 10:15
MSA-DCA | WA6544535 | 2 | Techworks Electrical | Reception - Light is humming quite badly (see notes) | Electrical | Lighting, Internal | 230.88 | Pass | Pass | 0 | 0 | 1 | 2023-02-10 13:34 | 2023-02-15 17:00 | 2023-02-15 10:00 | 2023-02-15 17:00 | 2023-02-15 11:00
MSA-DTWD | WA6560236 | 1 | Precise Air Group | Air con button is broken -Customer has a spare for replacement | Air Conditioning | Room Air Conditioners | 167.98 | Pass | Pass | 0 | 0 | 1 | 2023-02-13 08:47 | 2023-02-14 17:00 | 2023-02-13 10:00 | 2023-02-14 17:00 | 2023-02-13 11:00
MSA-DCA | WA6573790 | 1 | Automatic Fire Protection (ARA) | Main fire panel alarmed for zone 7 - fire service isolated - please reset zone 7 | Fire Protection Services | Fire Protection - Monitor System | 220.18 | Pass | Pass | 0 | 0 | 1 | 2023-02-14 20:55 | 2023-02-15 17:00 | 2023-02-15 10:00 | 2023-02-15 17:00 | 2023-02-15 11:00
MSA-DCA | WA6586023 | 1 | Earth & Water Pty Ltd | Retic Zone 11 - Broken Pipe | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 1 | 2023-02-16 12:46 | 2023-02-17 17:00 | 2023-02-17 07:00 | 2023-02-17 17:00 | 2023-02-17 08:00
MSA-DCA | WA6586253 | 2 | EQUANS Mechanical Services (WA) Pty Limited | Level 3 - ICT Room - AC - 2 & 3 - Error display | Air Conditioning | Room Air Conditioners | 146.4 | Fail | Fail | 0 | 0 | 1 | 2023-02-16 15:08 | 2023-02-21 17:00 | 2023-02-24 13:00 | 2023-02-21 17:00 | 2023-02-24 14:00
MSA-DTWD | WA6600113 | 1 | AHS Services WA Pty Ltd (Anchor) | Kitchen - The sink in the kitchen in the admin block is leaking (see notes) | Plumbing & Drainage | Drainage | 257.7 | Pass | Pass | 0 | 0 | 1 | 2023-02-17 09:08 | 2023-02-20 17:00 | 2023-02-17 14:30 | 2023-02-20 17:00 | 2023-02-17 15:30
MSA-DTWD | WA6650303 | 3 | AWB Co. | Faulty ceiling light | Electrical | Lighting, Internal | 152.79 | Pass | Pass | 0 | 0 | 1 | 2023-02-20 10:33 | 2023-02-27 17:00 | 2023-02-24 11:30 | 2023-02-27 17:00 | 2023-02-24 12:30
MSA-DCA | WA6650539 | 2 | Techworks Electrical | Festoon lights - timer needs adjusting (see notes) | Electrical | Lighting, External | 135.15 | Pass | Pass | 0 | 0 | 1 | 2023-02-20 11:44 | 2023-02-23 17:00 | 2023-02-22 07:00 | 2023-02-23 17:00 | 2023-02-22 08:00
MSA-DFES | WA6650788 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Coverplate for oven/hotplate isolation switch is broken x2 outside covers need replacing | Electrical | General Electrical | 145.95 | Pass | Pass | -1 | -1 | 1 | 2023-02-20 13:16 | 2023-02-27 17:00 | 2023-02-21 07:00 | 2023-02-27 17:00 | 2023-02-21 08:00
MSA-DTAG | WA6653813 | 1 | Sapio Pty Ltd | L3-Card reader for Judicial Door in Court Room 36 Flashing Red & Green-see notes | Security | Security Management System | 139.88 | Fail | Fail | 0 | 0 | 1 | 2023-02-21 07:12 | 2023-02-21 17:00 | 2023-02-22 08:30 | 2023-02-21 17:00 | 2023-02-22 09:30
MSA-DTWD | WA6653999 | 3 | Techworks Plumbing | Ground & 1st Floor - Cleaners stores - Taps dripping | Plumbing & Drainage | Water | 237.05 | Pass | Pass | -1 | -1 | 1 | 2023-02-21 08:51 | 2023-02-28 17:00 | 2023-02-22 08:30 | 2023-02-28 17:00 | 2023-02-22 09:30
MSA-DTWD | WA6671613 | 3 | AWB Co. | Ceiling fan will only rotate in one direction | Electrical | General Electrical | 206.84 | Pass | Pass | 0 | 0 | 1 | 2023-02-23 09:16 | 2023-03-02 17:00 | 2023-02-28 07:00 | 2023-03-02 17:00 | 2023-02-28 08:00
MSA-DFES | WA6673522 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Room 13 - Bathroom - Burst hose - Braided hose | Plumbing & Drainage | Water | 161.4625 | Pass | Pass | 0 | 0 | 1 | 2023-02-24 15:59 | 2023-02-27 17:00 | 2023-02-24 16:45 | 2023-02-27 17:00 | 2023-02-24 17:45
MSA-DTWD | WA6674352 | 2 | AHS Services WA Pty Ltd (Anchor) | There is a leak under the sink from the pipe, has flooded the bottom of the cupboard and carpet | Plumbing & Drainage | Drainage | 101.35 | Pass | Pass | 0 | 0 | 1 | 2023-02-27 09:25 | 2023-03-02 17:00 | 2023-03-01 08:30 | 2023-03-02 17:00 | 2023-03-01 09:30
MSA-DFES | WA6674561 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Staff change rooms - LED light panel flickering in the over the sinks | Electrical | Lighting, Internal | 315.89 | Pass | Pass | 0 | 0 | 1 | 2023-02-27 10:46 | 2023-03-02 17:00 | 2023-02-27 11:30 | 2023-03-02 17:00 | 2023-02-27 12:30
MSA-DTAG | WA6674655 | 2 | Midolo Building Services | Level 5 - Staff kitchen sink - cabinet door hinge is faulty | Building | Doors | 156.63 | Pass | Pass | 0 | 0 | 1 | 2023-02-27 11:20 | 2023-03-02 17:00 | 2023-03-01 10:00 | 2023-03-02 17:00 | 2023-03-01 11:00
MSA-DTWD | WA6676081 | 3 | AWB Co. | 6 Fluroescent lights not working in class room AF4 | Electrical | Lighting, Internal | 263.29 | Pass | Pass | -1 | -1 | 1 | 2023-02-28 11:40 | 2023-03-08 17:00 | 2023-03-02 08:30 | 2023-03-08 17:00 | 2023-03-02 09:30
MSA-DCA | WA6680045 | 1 | Techworks Electrical | Light Switch Faulty | Electrical | Lighting, Internal | 148.43 | Pass | Pass | 0 | 0 | 1 | 2023-03-01 08:15 | 2023-03-02 17:00 | 2023-03-01 08:30 | 2023-03-02 17:00 | 2023-03-01 09:30
MSA-DTWD | WA6680372 | 2 | AWB Co. | Light switch is sticky, needs to be replaced. -Contractor must contact site before attending | Electrical | Lighting, Internal | 162.66 | Pass | Pass | -1 | -1 | 1 | 2023-03-01 10:33 | 2023-03-07 17:00 | 2023-03-02 10:00 | 2023-03-07 17:00 | 2023-03-02 11:00
MSA-DTWD | WA6683451 | 0 | Equans Mechanical Services Australia | Chiller offline, can't be reset | Refrigeration | Refrigerators |  | Fail | Fail | 1 | 1 | 1 | 2023-03-03 09:08 | 2023-03-03 11:08 | 2023-03-10 10:00 | 2023-03-03 13:08 | 2023-03-10 11:00
MSA-DTWD | WA6683558 | 2 | LIGHTHOUSE LOCKSMITHS | Technicians rooms - Door locks sticking -See notes | Security | Locksmith | 160 | Pass | Pass | 0 | 0 | 1 | 2023-03-03 09:58 | 2023-03-09 17:00 | 2023-03-07 08:30 | 2023-03-09 17:00 | 2023-03-07 09:30
MSA-DFES | WA6683887 | 2 | Australian HVAC Services Pty. Ltd. | Split Aircon - Making loud noises | Air Conditioning | Room Air Conditioners | 201.88 | Pass | Pass | 0 | 0 | 1 | 2023-03-03 13:13 | 2023-03-09 17:00 | 2023-03-07 14:30 | 2023-03-09 17:00 | 2023-03-07 15:30
MSA-DTAG | WA6690598 | 1 | Sapio Pty Ltd | Interview room 2 - Alarm arose yesterday and security actioned it (see notes) | Security | Monitoring | 139.88 | Fail | Fail | 0 | 0 | 1 | 2023-03-09 10:57 | 2023-03-10 17:00 | 2023-03-13 08:30 | 2023-03-10 17:00 | 2023-03-13 09:30
MSA-DCA | WA6691027 | 1 | Wilson Security | Retrospective Workorder Do not Attend - (see notes) | Security | Monitoring |  | Fail | Fail | 3 | 3 | 1 | 2023-02-15 07:30 | 2023-02-15 17:00 | 2023-03-09 16:00 | 2023-02-15 17:00 | 2023-03-09 17:00 | 1
MSA-DFES | WA5462528 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Back door - Firefighters shower head leaks needs replaced. | Plumbing & Drainage | Water | 151.27 | Pass | Pass | 0 | 0 | 0.98389 | 2022-05-19 16:02 | 2022-05-24 17:00 | 2022-05-24 14:31 | 2022-05-24 17:00 | 2022-05-24 15:30 |  |  | Attend site to check out leaking shower head in main bathroom shower near back door. Located shower with shower head that was spraying water out of the joins and cracks in shower head. This can not be fixed and will be replaced. Supply and install new hand help shower head and new hose. Tested and checked all working correctly
MSA-DCA | WA5001691 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 4 - Staff Ladies Showers - see notes below | Plumbing & Drainage | Water | 187.02 | Pass | Pass | 0 | 0 | 0.98333 | 2022-01-11 15:13 | 2022-01-14 17:00 | 2022-01-13 09:01 | 2022-01-14 17:00 | 2022-01-13 10:00 |  |  | Replaced leaking and corroded taps
MSA-DFES | WA5306990 | 1 | Water2water Pty Ltd | Second Floor - Boardroom Kitchen - Zip tap are faulty | Plumbing & Drainage | Water | 590.735 | Pass | Pass | 0 | 0 | 0.98333 | 2022-04-07 09:18 | 2022-04-08 17:00 | 2022-04-07 15:55 | 2022-04-08 17:00 | 2022-04-07 16:54 |  |  | Replaced filter head and filter
MSA-DCA | WA5100133 | 3 | GPS Plumbing & Gas Services PtyLtd | Staff ladies bathroom – Once the cistern fills up, water keeps running in the toilet bowl | Plumbing & Drainage | Toilets/Cisterns | 288.43 | Pass | Pass | -1 | -1 | 0.98333 | 2022-02-02 11:13 | 2022-02-09 17:00 | 2022-02-03 08:31 | 2022-02-09 17:00 | 2022-02-03 09:30 |  |  | Service leaking cistern. Middle toilet
MSA-DCA | WA5106730 | 2 | GPS Plumbing & Gas Services PtyLtd | G Block - Male toilet - Wash basin - Bent tap in male toilet needs replacement | Plumbing & Drainage | Materials | 134.78 | Pass | Pass | 0 | 0 | 0.98333 | 2022-02-07 10:59 | 2022-02-10 17:00 | 2022-02-08 14:41 | 2022-02-10 17:00 | 2022-02-08 15:40 |  |  | Tap not bent, just loose. Get access to and retighten as required
MSA-DTWD | WA5107008 | 1 | Falcetta Plumbing and Gas | Ground - D Block - Blocked drains in sink near Room D23 | Plumbing & Drainage | Water | 125.12 | Pass | Pass | 0 | 0 | 0.98333 | 2022-02-07 13:36 | 2022-02-08 17:00 | 2022-02-08 16:00 | 2022-02-08 17:00 | 2022-02-08 16:59 |  |  | Located and unblocked gully
MSA-DTWD | WA5133349 | 2 | Falcetta Plumbing and Gas | Block 9 - First Floor - Male toilet - Urinal not flushing | Plumbing & Drainage | Toilets/Cisterns | 130.12 | Pass | Pass | 0 | 0 | 0.98333 | 2022-02-15 09:56 | 2022-02-18 17:00 | 2022-02-18 16:00 | 2022-02-18 17:00 | 2022-02-18 16:59 |  |  | Repaired cistern, adjusted inlet flow and sealed button into wall
MSA-DTWD | WA5191569 | 2 | Falcetta Plumbing and Gas | Female first floor toilet - Toilet cistern runs and doesn’t fully fill. Seal replaced but still run | Plumbing & Drainage | Toilets/Cisterns | 130.12 | Pass | Pass | 0 | 0 | 0.98333 | 2022-02-25 07:21 | 2022-03-01 17:00 | 2022-03-01 16:00 | 2022-03-01 17:00 | 2022-03-01 16:59 |  |  | repaired cistern outlet assembly
MSA-DFES | WA5193635 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Burst retic - pipe in the back right hand corner of the property | Plumbing & Drainage | Water | 149.71 | Pass | Pass | 0 | 0 | 0.98333 | 2022-02-25 12:34 | 2022-03-02 17:00 | 2022-03-02 07:00 | 2022-03-02 17:00 | 2022-03-02 07:59 |  |  | Use a 25mm pressure cap on a open end of a retic pipe
MSA-DTAG | WA5792047 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground - Staff kitchen -Leaking tap | Plumbing & Drainage | Water | 202.04 | Pass | Pass | 0 | 0 | 0.98333 | 2022-08-23 11:10 | 2022-08-24 17:00 | 2022-08-24 10:00 | 2022-08-24 17:00 | 2022-08-24 10:59 |  |  | Leaking mixer cartridge replace
MSA-DTWD | WA5853933 | 2 | Techworks Plumbing | Workshop Block - Level 1 - Male Toilets - Urinal water is running non stop | Plumbing & Drainage | Toilets/Cisterns | 230.86 | Pass | Pass | 0 | 0 | 0.98333 | 2022-09-12 12:08 | 2022-09-15 17:00 | 2022-09-14 07:30 | 2022-09-15 17:00 | 2022-09-14 08:29 |  |  | Arrived for a faulty urinal constantly leaking on arrival we checked the solenoid to the urinal it seemed to be working fine as it wasn’t running anymore took photos of the solenoid for future.
MSA-DTWD | WA5994790 | 2 | Techworks Plumbing | Wash Trot Area - Passageway Near J122 - Blocked drain to the wash trot | Plumbing & Drainage | Drainage | 435.26 | Pass | Pass | -1 | -1 | 0.98333 | 2022-10-06 08:42 | 2022-10-11 17:00 | 2022-10-06 13:30 | 2022-10-11 17:00 | 2022-10-06 14:29 |  |  | Cleared blocked floor waste gully with drain machine - tested ok
MSA-DCA | WA6031557 | 0 | Dormakaba Australia Pty Ltd | Perth WA Museum- ground floor Cafe door not locking | Building | Doors | 345 | Fail | Fail | 0 | 0 | 0.98333 | 2022-10-16 09:57 | 2022-10-16 11:57 | 2022-10-17 11:11 | 2022-10-16 13:57 | 2022-10-17 12:10 |  |  | Cafe stacker doors. Found too hinges loose causing doors to drop and not line up on locks, re fixed loose hinges and tested doors all ok. Advised Jimmy locks need to be repaired bylocksmith as they are not latching all the way in
MSA-DTWD | WA6132291 | 2 | COMMERCIAL PLUMBING AND GAS | Blocked cleaners sink - Plunger didn't work - See notes | Plumbing & Drainage | Drainage | 578.88 | Pass | Pass | 0 | 0 | 0.98333 | 2022-10-31 13:04 | 2022-11-03 17:00 | 2022-11-03 16:00 | 2022-11-03 17:00 | 2022-11-03 16:59 |  |  | unblock sink, drainsflush unblock floor waste
MSA-DTWD | WA6358936 | 1 | COMMERCIAL PLUMBING AND GAS | Ceramics Workshop - Tap leaking badly | Plumbing & Drainage | Drainage | 153.88 | Pass | Pass | 0 | 0 | 0.98333 | 2022-12-06 11:17 | 2022-12-07 17:00 | 2022-12-06 16:00 | 2022-12-07 17:00 | 2022-12-06 16:59 |  |  | Repaired tap
MSA-DTWD | WA6365989 | 1 | AHS Services WA Pty Ltd (Anchor) | Restaurant Kitchen-Floor waste in kitchen blocked-see notes | Plumbing & Drainage | Drainage | 137.98 | Pass | Pass | 0 | 0 | 0.98333 | 2022-12-13 13:53 | 2022-12-14 17:00 | 2022-12-14 07:26 | 2022-12-14 17:00 | 2022-12-14 08:25 |  |  | Completed
MSA-DTWD | WA6482418 | 2 | COMMERCIAL PLUMBING AND GAS | Creche yard - Leaking Tap | Plumbing & Drainage | Drainage | 153.88 | Pass | Pass | 0 | 0 | 0.98333 | 2023-01-18 10:13 | 2023-01-23 17:00 | 2023-01-23 16:00 | 2023-01-23 17:00 | 2023-01-23 16:59
MSA-DTWD | WA6516864 | 1 | COMMERCIAL PLUMBING AND GAS | E74 Commercial Cooking Kitchen-Faulty/leaking isolating valve supplying water to a proofer | Plumbing & Drainage | Water | 232.88 | Pass | Pass | 0 | 0 | 0.98333 | 2023-01-23 16:38 | 2023-01-24 17:00 | 2023-01-24 16:00 | 2023-01-24 17:00 | 2023-01-24 16:59
MSA-DCA | WA5018280 | 1 | Dormakaba Australia Pty Ltd | Ground - Green Room - Exit Rear Passage Door Not working near Green Room - See details | Building | Doors | 220 | Pass | Pass | 0 | 0 | 0.98333 | 2022-01-14 10:39 | 2022-01-17 17:00 | 2022-01-14 11:29 | 2022-01-17 17:00 | 2022-01-14 12:28 |  |  | Inspected door and found that site have an intermittent issue with the card reader not working etc, advised site to call out access tech.
MSA-DCA | WA5693446 | 1 | GPS Plumbing & Gas Services PtyLtd | Men’s Toilet Cubicle - Toilet won’t stop flushing – unusable - see notes below | Plumbing & Drainage | Toilets/Cisterns | 278.25 | Pass | Pass | 0 | 0 | 0.98333 | 2022-08-04 12:24 | 2022-08-05 17:00 | 2022-08-04 14:10 | 2022-08-05 17:00 | 2022-08-04 15:09 |  |  | Service 2 by cistern in male dress circle
MSA-DCA | WA5974897 | 0 | Dormakaba Australia Pty Ltd | Airlock door east is not responding to close demands | Building | Doors | 350 | Pass | Pass | 0 | 0 | 0.98333 | 2022-09-24 15:24 | 2022-09-24 17:24 | 2022-09-24 16:23 | 2022-09-24 19:24 | 2022-09-24 17:22 |  |  | Attended site and found that there was a broken bolt head in track causing door to go into obstruction closing, removed Bolt head also lifted door as it was too close to ground, sprayed belt dressing on belt. Tested and all working fine now. Left area clean and tidy.
MSA-DCA | WA6021759 | 0 | Dormakaba Australia Pty Ltd | Francis street building - Level 1 - Nth East CNR - Fault on auto sliding door | Building | Automatic Doors | 351.95 | Pass | Pass | 0 | 0 | 0.98333 | 2022-10-14 10:29 | 2022-10-14 12:29 | 2022-10-14 10:59 | 2022-10-14 14:29 | 2022-10-14 11:58 |  |  | Inspected door and found doors were dropped, jamming on ground, raised doors, tested all ok.
MSA-DTAG | WA5080668 | 0 | Gilmour & Jooste Electrical | Basement - Power supply to server room has been compromised | Electrical | General Electrical | 64.835 | Pass | Pass | 0 | 0 | 0.96667 | 2022-01-20 08:30 | 2022-01-20 10:30 | 2022-01-20 08:45 | 2022-01-20 12:30 | 2022-01-20 09:43 |  |  | Inspected fault to power loss to server. Found overload switch to be off behind bypass unit. Reset overload and tested. Now in working order.
MSA-DTWD | WA5190793 | 0 | Dormakaba Australia Pty Ltd | Main Entry - auto door is faulty | Building | Automatic Doors | 696.57 | Pass | Pass | 0 | 0 | 0.96667 | 2022-02-24 14:39 | 2022-02-24 16:39 | 2022-02-24 15:19 | 2022-02-24 18:39 | 2022-02-24 16:17 |  |  | Inspected door and found that the mode switch was faulty and that this was causing the door to fault, replaced as necessary with new sk4 type switch, checked over and tested operation upon completion and left in good working order.
MSA-MRWA | WA5417650 | 1 | TK Elevator Australia Pty Ltd | Lift 2 - out of order- making a loud clunk noise | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.96667 | 2022-05-13 14:54 | 2022-05-16 17:00 | 2022-05-13 15:56 | 2022-05-16 17:00 | 2022-05-13 16:54 |  |  | Lift2 DAC-Geared :On arrival lift on basement on ind service.Could not find out who called the fault and what was actual fault. As no text message received.Ran lift up down a few times no noise, security guard said its ground floor doors.Found door weight aircord out of roller, refitted and tested left in service ,new aircord roller required.Details sent to supervisorto be closed out at $0 cost
MSA-DFES | WA5987801 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Female bathroom-Shower head is leaking. Requires new washers to be installed. | Plumbing & Drainage | Water | 171.1 | Pass | Pass | 0 | 0 | 0.96667 | 2022-10-03 14:48 | 2022-10-06 17:00 | 2022-10-05 08:02 | 2022-10-06 17:00 | 2022-10-05 09:00 |  |  | Shower tap service
MSA-DCA | WA6526486 | 0 | Precise Air Group | Aircon is leaking | Air Conditioning | Evaporative Coolers | 304.055 | Pass | Pass | 0 | 0 | 0.96667 | 2023-02-01 08:01 | 2023-02-01 10:01 | 2023-02-01 08:56 | 2023-02-01 12:01 | 2023-02-01 09:54
MSA-DFES | WA6668536 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Reception - Ladies toilet - Broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 204.7 | Pass | Pass | 0 | 0 | 0.96667 | 2023-02-22 10:06 | 2023-03-01 17:00 | 2023-03-01 13:15 | 2023-03-01 17:00 | 2023-03-01 14:13
MSA-DTWD | WA6680783 | 2 | Dormakaba Australia Pty Ltd | West entry - S9 - Door wont open from inside External sensor/operation OK. (see notes) | Building | Automatic Doors | 186.95 | Pass | Pass | -1 | -1 | 0.96667 | 2023-03-01 14:28 | 2023-03-07 17:00 | 2023-03-02 08:00 | 2023-03-07 17:00 | 2023-03-02 08:58
MSA-DCA | WA5390214 | 1 | Earth & Water Pty Ltd | Urban Orchard - Ground – external - Nothern Side -Malfunctioning sprinklers, too much water flowing | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.96667 | 2022-05-02 11:02 | 2022-05-03 17:00 | 2022-05-03 09:17 | 2022-05-03 17:00 | 2022-05-03 10:15 |  |  | Work Completed:-Arrived on-site-Checked urban orchard for people before turning on and testing system. Man sleeping on lawn. Called PCC security to ask forhelp. No security on-site so I dealt with the situation myself.-Tested system-Found broken sprinkler body on zone 8. Replaced internals. Flushed system. Adjust heads and cleaned out 3x blocked heads.-Tested zone 10. No major issues. Flushed a couple heads and adjusted arcs.-Left area clean and tidy
MSA-MRWA | WA5715060 | 2 | Schindler Lifts Australia | Basement - Lift 3 - Lift 3 display screen is blank | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.96667 | 2022-08-12 10:46 | 2022-08-17 17:00 | 2022-08-12 12:06 | 2022-08-17 17:00 | 2022-08-12 13:04 |  |  | Works completed - close out at $0
MSA-DTWD | WA5800378 | 2 | AHS Services WA Pty Ltd (Anchor) | Female Staff toilet not working | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | -1 | -1 | 0.96667 | 2022-08-31 09:42 | 2022-09-05 17:00 | 2022-08-31 13:00 | 2022-09-05 17:00 | 2022-08-31 13:58 |  |  | Completed
MSA-DCA | WA6381940 | 1 | TK Elevator Australia Pty Ltd | Lift 2 Public lift - Power fault message over speakers | Lifts | Lifts | 590 | Pass | Pass | 0 | 0 | 0.96667 | 2022-12-19 20:33 | 2022-12-20 17:00 | 2022-12-20 08:05 | 2022-12-20 17:00 | 2022-12-20 09:03 |  |  | Lift running on arrival, lift reset itself.Spoke to security he infomred that they lift is still running but wants to make sure nothing is wronf with itErrors 0026, 0105, 0101, 0036, 0170, 0101, 0021Lost main AC and drive shutdown, lift reset itself after power was restored.Cleared errors all okay, couldn't reproduce fault left unit in service.
MSA-DTWD | WA5306635 | 3 | AHS Services WA Pty Ltd (Anchor) | D block - level 1 - room D119 - Cistern buttons have broken off - see notes | Plumbing & Drainage | Toilets/Cisterns | 162.01 | Pass | Pass | 0 | 0 | 0.95 | 2022-04-06 15:43 | 2022-04-13 17:00 | 2022-04-11 08:45 | 2022-04-13 17:00 | 2022-04-11 09:42 |  |  | Completed
MSA-DCA | WA5207681 | 2 | Techworks Plumbing | Hackett Hall - Level 1- Male Toilets - Fix toilet with continuously running water | Plumbing & Drainage | Toilets/Cisterns | 284.57 | Pass | Pass | 0 | 0 | 0.95 | 2022-03-08 15:35 | 2022-03-11 17:00 | 2022-03-09 08:30 | 2022-03-11 17:00 | 2022-03-09 09:27 |  |  | Access female left side toilet to find it continually running, removed face plate to find jammed flush mechanism, removed mechanism and inspected, no issues, greased up and tested function, reinstalled flush mechanism and flush plate, tested 10 times, no issue with toilet, working well,if problem persists recommend replace pneumatic flush with standard mechanical flush valve
MSA-DCA | WA5226964 | 1 | GPS Plumbing & Gas Services PtyLtd | Main Building - Basement - Men’s Toilets - see details | Plumbing & Drainage | Toilets/Cisterns | 232.78 | Pass | Pass | 0 | 0 | 0.95 | 2022-03-14 16:23 | 2022-03-15 17:00 | 2022-03-15 11:30 | 2022-03-15 17:00 | 2022-03-15 12:27 |  |  | Replaced inlet valve to urinal cistern RHSRefitted basin mixer to LHS basin.
MSA-DTAG | WA5789933 | 1 | Sapio Pty Ltd | Ground - Custody - Duress Alarm not working - See notes below | Security | Monitoring | 139.88 | Pass | Pass | 0 | 0 | 0.95 | 2022-08-22 08:03 | 2022-08-23 17:00 | 2022-08-22 08:03 | 2022-08-23 17:00 | 2022-08-22 09:00 |  |  | Work performed by Dirk Malan 22/08/2022:Attended site. Tested button relay, tested OK. Found that button appears activated on Austco panel despite not showingany active alarms on intercom unit in Custody. Suspect input on Austco unit is faulty.14/09/2022 - BRAF submitted for approval.03/10/2022 - BRAF declined, works to be completed under LVM WA5987697, invoice costs to date.
MSA-DFES | WA5799776 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Radio Comms - Male Toilet - Overflows when flushed | Plumbing & Drainage | Toilets/Cisterns | 221.38 | Pass | Pass | -1 | -1 | 0.95 | 2022-08-30 14:12 | 2022-09-06 17:00 | 2022-09-02 10:00 | 2022-09-06 17:00 | 2022-09-02 10:57 |  |  | Arrived on site and singed in went to male toilets located radio room could see that trap was blocked in the urinal gave it a plunge and used bowl guard and turned the water level down to 2l in cistern to stop it from overflowing tested everything and running.
MSA-MRWA | WA6537777 | 2 | Schindler Lifts Australia | Lift 1 – Level 5 call button for level 9 not illuminating / level 7 down light remaining illuminated | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.95 | 2023-02-07 11:40 | 2023-02-10 17:00 | 2023-02-09 11:22 | 2023-02-10 17:00 | 2023-02-09 12:19
MSA-DTWD | WA5393825 | 3 | Water2water Pty Ltd | Staff Kitchen 2-54 - Faulty Billi boiling water unit | Plumbing & Drainage | HWS/Units Electric & Gas | 183.3475 | Pass | Pass | 0 | 0 | 0.95 | 2022-05-04 10:28 | 2022-05-11 17:00 | 2022-05-10 10:23 | 2022-05-11 17:00 | 2022-05-10 11:20 |  |  | Video shows bad vibration in the water line. Ran water through system. Couldn’t make it happen. Drained both tanks and will leave and they will monitor unit. Maybe the Flexi and main isolation to unit
MSA-DCA | WA5511996 | 0 | TK Elevator Australia Pty Ltd | Ground Floor - Kitchen Lift 2 - Lift is not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.95 | 2022-06-13 12:02 | 2022-06-13 14:02 | 2022-06-13 13:10 | 2022-06-13 16:02 | 2022-06-13 14:07 |  |  | Lift 2 Art-Kitchen-Geared :Lift out of order, found on ground floor with doors open. Found safety circuit open. Found overspeed governor tripped. Reset and tested all ok. Left in service.to be closed out at $0 cost
MSA-DCA | WA6675841 | 1 | Dormakaba Australia Pty Ltd | Main Building Foyer - Foyer to Cafe - Glass doors don't align correctly (see notes) | Security | Access Control | 395 | Pass | Pass | 0 | 0 | 0.95 | 2023-02-28 09:48 | 2023-03-01 17:00 | 2023-02-28 12:04 | 2023-03-01 17:00 | 2023-02-28 13:01
MSA-DTWD | WA5204189 | 2 | Equans Mechanical Services Australia | Room C101/C102 - Please see details below - | Air Conditioning | Room Air Conditioners | 289.63 | Fail | Fail | 2 | 2 | 0.93333 | 2022-03-04 08:31 | 2022-03-10 17:00 | 2022-03-22 09:22 | 2022-03-10 17:00 | 2022-03-22 10:18 |  |  | Carried out schedule setup on I touch manager. Fcu 2.2.3 operates 0700-1700 Monday to Friday ,fcu-2.2.2 operates 24/7, no stop time with an auto restart at 7am every day in case turned off locally.Both units have push button with inbuilt 2 hour timer, advised not to use these as they override units onstatus and re enable timer.
MSA-DCA | WA5324448 | 1 | Techworks Electrical | Administration building - Emergency stairwell - 2 x Fluro sensor light fittings are not working | Electrical | Lighting, Internal | 257.45 | Pass | Pass | 0 | 0 | 0.93333 | 2022-04-13 15:26 | 2022-04-14 17:00 | 2022-04-14 13:30 | 2022-04-14 17:00 | 2022-04-14 14:26 |  |  | Replaced fluro tubes out in 3 lights
MSA-DFES | WA5471839 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Mens Change Room - Toilet Blocked | Plumbing & Drainage | Toilets/Cisterns | 138.95 | Pass | Pass | 0 | 0 | 0.93333 | 2022-05-23 13:26 | 2022-05-26 17:00 | 2022-05-24 09:20 | 2022-05-26 17:00 | 2022-05-24 10:16 |  |  | Unblocked the toilet
MSA-DFES | WA5660934 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ladies toilet Level 2 Blocked basin one the left side | Plumbing & Drainage | Drainage | 149.1 | Fail | Fail | 0 | 0 | 0.93333 | 2022-07-19 13:38 | 2022-07-26 17:00 | 2022-07-27 07:49 | 2022-07-26 17:00 | 2022-07-27 08:45 |  |  | Unblocked the basin.
MSA-MRWA | WA5695881 | 1 | Dormakaba Australia Pty Ltd | auto door to northern Carpark-not working and burning smell | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.93333 | 2022-08-08 08:20 | 2022-08-09 17:00 | 2022-08-08 09:49 | 2022-08-09 17:00 | 2022-08-08 10:45 |  |  | 1076623. Found water has leaked from roof above unit into housing and caused operator to short out, advised Danika of water issue and that unit will require replacement, when replacing unit we will need to seal cover as water issue is being rectified but may not be fixed when we return for replacement. Quotation required to replace ED250 with upgrade card and V2 slide channel. Pictures attached for reference
MSA-DCA | WA6159241 | 1 | Dormakaba Australia Pty Ltd | Ground - Airlock sliding glass doors - exterior west is knocking when opening | Building | Automatic Doors | 678.8 | Pass | Pass | 0 | 0 | 0.93333 | 2022-11-10 13:28 | 2022-11-11 17:00 | 2022-11-10 15:30 | 2022-11-11 17:00 | 2022-11-10 16:26 |  |  | Inspected door and found LHS door track wheels were noisy. Replaced 3 x heavy duty track wheels. Checked all fixings. Tested all OK
MSA-DTWD | WA6255520 | 3 | Dormakaba Australia Pty Ltd | Door closer pulling fixtures from doors and door frame. | Building | Automatic Doors | 351.95 | Pass | Pass | -1 | -1 | 0.93333 | 2022-11-23 11:14 | 2022-11-30 17:00 | 2022-11-24 09:29 | 2022-11-30 17:00 | 2022-11-24 10:25 |  |  | Found unit rocking heavily off the wall when activated. Re-secured unit and added more fixings as required. Tested and adjusted unit. All ok.
MSA-DTAG | WA6467798 | 1 | Dormakaba Australia Pty Ltd | Sally port has come out of the railings - See notes | Building | Doors | 420 | Pass | Pass | 0 | 0 | 0.93333 | 2023-01-17 15:57 | 2023-01-18 17:00 | 2023-01-17 19:30 | 2023-01-18 17:00 | 2023-01-17 20:26
MSA-DTWD | WA6671627 | 1 | Dormakaba Australia Pty Ltd | Hair Reception - Big glass entry doors beeing every half hour possibly needs new battery | Building | Automatic Doors | 526.05 | Pass | Pass | 0 | 0 | 0.93333 | 2023-02-23 09:14 | 2023-02-24 17:00 | 2023-02-23 10:43 | 2023-02-24 17:00 | 2023-02-23 11:39
MSA-DTAG | WA6680485 | 2 | Dormakaba Australia Pty Ltd | Registry - Ground - Door still not locking door not in alignment about 5cm out (see notes) | Building | Doors | 200 | Pass | Pass | -1 | -1 | 0.93333 | 2023-03-01 11:31 | 2023-03-07 17:00 | 2023-03-03 09:00 | 2023-03-07 17:00 | 2023-03-03 09:56
MSA-DTWD | WA5584693 | 2 | AHS Services WA Pty Ltd (Anchor) | Ground SK1-the hot water filter still leaking | Plumbing & Drainage | Water | 101.35 | Pass | Pass | 0 | 0 | 0.93333 | 2022-07-05 09:46 | 2022-07-08 17:00 | 2022-07-07 07:29 | 2022-07-08 17:00 | 2022-07-07 08:25 |  |  | Completed
MSA-DTWD | WA5203261 | 2 | UNIVERSAL DOORS | H Block - Roller Door - Motor has service light flashing and stops 1/3 of the way up | Building | Roller Shutters |  | Pass | Pass | -1 | -1 | 0.91667 | 2022-03-03 11:47 | 2022-03-09 17:00 | 2022-03-04 08:20 | 2022-03-09 17:00 | 2022-03-04 09:15 |  |  | JOB COMPLETED - ATTENDED SITE TO INSPECT & REPAIR THE REPORTED FAULTY ROLLERDOOR, UNABLE TO FAULT OPERATION, RESET CONTROLLER, CHECKEDOPERATION, ALL OK
MSA-DTAG | WA5369095 | 2 | Water2water Pty Ltd | Level 2 - Kitchen – Sheriff’s Office - Billi Tap not working on far end sink | Plumbing & Drainage | Water | 161.54 | Pass | Pass | 0 | 0 | 0.91667 | 2022-04-19 16:46 | 2022-04-22 17:00 | 2022-04-21 14:45 | 2022-04-22 17:00 | 2022-04-21 15:40 |  |  | Found fault code on Billi on arrival. Recalibrated hot water and tested. All okay on departure.
MSA-DTWD | WA5398648 | 1 | UNIVERSAL DOORS | Room AT106 - Heavy workshop bifold door (lower level) sprockets need replacing | Building | Doors |  | Fail | Fail | 12 | 12 | 0.91667 | 2022-05-09 11:50 | 2022-05-10 17:00 | 2022-08-04 11:45 | 2022-05-10 17:00 | 2022-08-04 12:40 |  |  | Job is completed - Activator refit to bifold door
MSA-DTWD | WA5462098 | 2 | Water2water Pty Ltd | Corridor outside B21 - one drinking water fountains not working | Plumbing & Drainage | Water | 252.73 | Pass | Pass | 0 | 0 | 0.91667 | 2022-05-19 11:09 | 2022-05-24 17:00 | 2022-05-23 09:50 | 2022-05-24 17:00 | 2022-05-23 10:45 |  |  | Replaced faulty bottle filler
MSA-DCA | WA5604066 | 2 | GPS Plumbing & Gas Services PtyLtd | Mezzanine - Dressing Room 5 - Septic smell in dressing room | Plumbing & Drainage | Water | 145.04 | Pass | Pass | 0 | 0 | 0.91667 | 2022-07-12 15:38 | 2022-07-15 17:00 | 2022-07-14 11:20 | 2022-07-15 17:00 | 2022-07-14 12:15 |  |  | Inspected plumbing in room 5. No issues found. No weird smelt
MSA-DCA | WA5693167 | 1 | GPS Plumbing & Gas Services PtyLtd | ground level - dressing room 3 - Leak from pipe under bathroom sink in Dressing Room 3 Ground Floor. | Plumbing & Drainage | Water | 275.04 | Pass | Pass | 0 | 0 | 0.91667 | 2022-08-04 10:05 | 2022-08-05 17:00 | 2022-08-04 13:15 | 2022-08-05 17:00 | 2022-08-04 14:10 |  |  | Service 2 X basin pillar taps
MSA-MRWA | WA6357206 | 3 | ADVANCED LOCK & KEY | Workstation 3.114 - Replacement of cabinet lock as key profile not available for cutting new key | Security | Locksmith | 245 | Pass | Pass | -1 | -1 | 0.91667 | 2022-12-05 11:44 | 2022-12-12 17:00 | 2022-12-08 12:05 | 2022-12-12 17:00 | 2022-12-08 13:00 |  |  | Checked out locks on lvl 3 cubicle 114 and discussed options and just picked locked lock open and supplied programmed with 11mm cam lock for hand towel dispenser that they were going to install themselves 1x 11mm l and f cam lock
MSA-DTAG | WA6400402 | 1 | Water2water Pty Ltd | Judicial floor - Kitchen - Cold water continuing to run after being switched off (see notes) | Plumbing & Drainage | HWS/Units Electric & Gas | 371.82 | Pass | Pass | 0 | 0 | 0.91667 | 2023-01-03 12:19 | 2023-01-04 17:00 | 2023-01-03 14:00 | 2023-01-04 17:00 | 2023-01-03 14:55
MSA-DTWD | WA4991150 | 2 | Water2water Pty Ltd | Front foyer - On right as enter main auto door - Billi Qadra hot & cold water dispenser not wokiing | Plumbing & Drainage | Water | 161.54 | Pass | Pass | 0 | 0 | 0.91667 | 2022-01-04 15:44 | 2022-01-07 17:00 | 2022-01-06 13:40 | 2022-01-07 17:00 | 2022-01-06 14:35 |  |  | themal overload tripped due to intermittent or interrupted power issue, reset and tested unit ok
MSA-DTWD | WA5080750 | 1 | Dormakaba Australia Pty Ltd | North Block - Level 2 - Aberdeen Street entry door- Auto door sensor fault | Building | Automatic Doors | 999.31 | Pass | Pass | 0 | 0 | 0.91667 | 2022-01-20 09:03 | 2022-01-21 17:00 | 2022-01-20 09:23 | 2022-01-21 17:00 | 2022-01-20 10:18 |  |  | Found that external sensor has failed also the battery was flat, replaced sensor and battery,tested all ok.
MSA-DTWD | WA5201116 | 2 | Swan Pest Control | Steele framed house/paint house - white ants activity - please inspect | Pest Control | General Pest | 240 | Pass | Pass | -1 | -1 | 0.91667 | 2022-03-02 11:42 | 2022-03-08 17:00 | 2022-03-02 12:55 | 2022-03-08 17:00 | 2022-03-02 13:50 |  |  | Inspected building and injected Fipronil into back room floor
MSA-DTAG | WA5589229 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Custody - Toilet seat in men’s toilets in custody is broken | Plumbing & Drainage | Toilets/Cisterns | 120.57 | Pass | Pass | 0 | 0 | 0.91667 | 2022-07-08 11:00 | 2022-07-11 17:00 | 2022-07-08 12:10 | 2022-07-11 17:00 | 2022-07-08 13:05 |  |  | Completed
MSA-MRWA | WA5611733 | 2 | GPS Plumbing & Gas Services PtyLtd | Roof - Water storage Tank - Split pipe in water storage tank | Plumbing & Drainage | Water | 145.04 | Pass | Pass | -1 | -1 | 0.91667 | 2022-07-14 09:21 | 2022-07-19 17:00 | 2022-07-14 12:25 | 2022-07-19 17:00 | 2022-07-14 13:20 |  |  | Investigated lekaing pipe on the roof. New float vakve required as well as harness. Job to be done preferably on a not rainy day. Danika advised- new work order will be raised by her for the repair.
MSA-DTAG | WA6088536 | 2 | High Tech Pest Control | 1987-L2-whole office-rodent feaces around the office - see notes | Pest Control | General Pest | 277.04 | Pass | Pass | -1 | -1 | 0.91667 | 2022-10-19 09:04 | 2022-10-24 17:00 | 2022-10-20 13:40 | 2022-10-24 17:00 | 2022-10-20 14:35 |  |  | 2 rat & 10 mouse stations loaded with bait installed in and around office
MSA-DTWD | WA6184050 | 2 | Dormakaba Australia Pty Ltd | East Block - Level 2 - Disabled toilet - Auto door not working / has power but not activating | Building | Automatic Doors | 379.95 | Pass | Pass | 0 | 0 | 0.91667 | 2022-11-15 09:53 | 2022-11-18 17:00 | 2022-11-15 10:51 | 2022-11-18 17:00 | 2022-11-15 11:46 |  |  | Inspected door and found external push button was faulty. Replaced faulty button, checked all fixings, tested door operation. All working fine.
MSA-DTWD | WA4990866 | 2 | PEEL LOCK SERVICES PTY LTD | A Block western entrance door mechanical key pad - see notes below | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.91667 | 2022-01-04 12:35 | 2022-01-07 17:00 | 2022-01-05 14:15 | 2022-01-07 17:00 | 2022-01-05 15:10 |  |  | job completed -
MSA-DFES | WA4992465 | 2 | Dom's Total Grounds Maintenance | Front & Rear yard - reticulation at some are blocked | Landscaping & Gardening | Grounds Maintenance | 282.5 | Pass | Pass | -1 | -1 | 0.91667 | 2022-01-06 12:10 | 2022-01-11 17:00 | 2022-01-07 06:45 | 2022-01-11 17:00 | 2022-01-07 07:40 |  |  | Out of Metro Call outSupply 5 x MP Rotors
MSA-DTWD | WA5188708 | 2 | AHS Services WA Pty Ltd (Anchor) | Disabled Toilet - Q018 leaking toilet between pan and wall when flushed | Plumbing & Drainage | Toilets/Cisterns | 130.82 | Pass | Pass | -1 | -1 | 0.91667 | 2022-02-23 10:56 | 2022-02-28 17:00 | 2022-02-23 13:30 | 2022-02-28 17:00 | 2022-02-23 14:25 |  |  | Completed
MSA-DTWD | WA5195839 | 3 | ECO PLUMBING AND GAS PTY LTD | electrician drained HW unit he notice the drain was missing the Tunn dish and flowing onto bathroom | Plumbing & Drainage | HWS/Units Electric & Gas | 151.28 | Fail | Fail | 0 | 0 | 0.91667 | 2022-02-28 16:57 | 2022-03-08 17:00 | 2022-03-09 07:20 | 2022-03-08 17:00 | 2022-03-09 08:15 |  |  | Directed water correctly with pvc fitting to stop spilling and leaking water
MSA-DTWD | WA5201162 | 2 | AHS Services WA Pty Ltd (Anchor) | Ladies toilet has a broken toilet seat | Plumbing & Drainage | Toilets/Cisterns | 336.02 | Fail | Fail | 0 | 0 | 0.91667 | 2022-03-02 12:10 | 2022-03-08 17:00 | 2022-03-09 08:50 | 2022-03-08 17:00 | 2022-03-09 09:45 |  | WACCES | Completed
MSA-DTAG | WA5298207 | 1 | GPS Plumbing & Gas Services PtyLtd | entrance to toilets - Disabled toilet will not stop flushing | Plumbing & Drainage | Toilets/Cisterns | 105.41 | Pass | Pass | 0 | 0 | 0.91667 | 2022-03-31 16:22 | 2022-04-01 17:00 | 2022-04-01 07:30 | 2022-04-01 17:00 | 2022-04-01 08:25 |  |  | Button was jammed, adjusted buttons flushed multiple times and is flushing properly
MSA-DTWD | WA5377837 | 3 | ADVANCED LOCK & KEY | F202 Doors - Lock and handle mechanism broken | Security | Locksmith | 511.55 | Pass | Pass | -1 | -1 | 0.91667 | 2022-04-20 09:26 | 2022-04-28 17:00 | 2022-04-22 11:15 | 2022-04-28 17:00 | 2022-04-22 12:10 |  |  | Onsite 50 minutes Replaced faulty lock and furniture on class room F block 1x3572 1xSQ-02V-25-SCP 1xSW-01C-25-SCP 1x serviced lock single sided
MSA-DTWD | WA5385633 | 2 | Water2water Pty Ltd | E009 - Staff kitchen - wall mounted hot water urn is not woriking | Plumbing & Drainage | Water | 319.63 | Pass | Pass | 0 | 0 | 0.91667 | 2022-04-29 11:19 | 2022-05-04 17:00 | 2022-05-04 10:30 | 2022-05-04 17:00 | 2022-05-04 11:25 |  |  | No water to unit on arrival. Isolated water. Flushed lines and replaced faulty solenoid and level sensors. Waited to get to temp. Normal operation
MSA-MRWA | WA5459787 | 2 | Water2water Pty Ltd | Mezzanine - Kitchenette - Filtered Water Tap not producing cold / hot water | Plumbing & Drainage | HWS/Units Electric & Gas | 304.22 | Pass | Pass | 0 | 0 | 0.91667 | 2022-05-18 08:53 | 2022-05-23 17:00 | 2022-05-23 10:50 | 2022-05-23 17:00 | 2022-05-23 11:45 |  |  | System locked off on arrival, no hot or cold water. Turned system to locked on. Ran system to temp. Slow flow out of cold. Billi filter change. System getting to temp. Normal operation
MSA-DTWD | WA5495094 | 2 | Water2water Pty Ltd | BG25 Wash area - Water Fountain lacking pressure | Plumbing & Drainage | Water | 209.4375 | Pass | Pass | 0 | 0 | 0.91667 | 2022-06-08 09:26 | 2022-06-13 17:00 | 2022-06-10 12:15 | 2022-06-13 17:00 | 2022-06-10 13:10 |  |  | Removed blockage from water inlet and replaced inlet Flexi hose to restore normal pressure.
MSA-DCA | WA5495695 | 2 | ADVANCED LOCK & KEY | Alexander Library Building - Door on right hand side a you come out of lift - | Security | Locksmith | 215 | Pass | Pass | 0 | 0 | 0.91667 | 2022-06-08 14:06 | 2022-06-13 17:00 | 2022-06-10 10:00 | 2022-06-13 17:00 | 2022-06-10 10:55 |  |  | Packed out front of 201 lock out with aluminium bar packer made in van.10:00-10:55
MSA-DFES | WA5694372 | 1 | ACTION GLASS & ALUMINIUM | ground floor-panel of glass coming away from the window and there is a gap | Glazing | Window Glass | 169.88 | Pass | Pass | 0 | 0 | 0.91667 | 2022-08-05 09:36 | 2022-08-08 17:00 | 2022-08-05 14:50 | 2022-08-08 17:00 | 2022-08-05 15:45 |  |  | ATTENDED SITEREMOVED RUBBER FROM LARGE PANELREPOSITIONED GLASS AND REFIT RUBBER PLUS 1.5 L/M OF NEW RUBBER.SEALED WITH BLACK SILICONE.
MSA-DTAG | WA5837906 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground Floor - Male Public Toilet - Urinal Blocked | Plumbing & Drainage | Drainage | 204.5375 | Pass | Pass | 0 | 0 | 0.91667 | 2022-09-08 09:20 | 2022-09-09 17:00 | 2022-09-08 09:20 | 2022-09-09 17:00 | 2022-09-08 10:15 |  |  | Cleared blocked urinal with plunger and moflo
MSA-DTWD | WA5976642 | 2 | AHS Services WA Pty Ltd (Anchor) | cool room E61 has a broken tundish causing water leak on the floor. | Plumbing & Drainage | Water | 146.79 | Pass | Pass | 0 | 0 | 0.91667 | 2022-09-27 10:36 | 2022-09-30 17:00 | 2022-09-29 07:20 | 2022-09-30 17:00 | 2022-09-29 08:15 |  |  | Completed
MSA-DTWD | WA5989252 | 1 | ACTION GLASS & ALUMINIUM | Window broken | Glazing | Window Glass | 454.84 | Fail | Fail | 0 | 0 | 0.91667 | 2022-10-04 12:42 | 2022-10-05 17:00 | 2022-10-07 13:20 | 2022-10-05 17:00 | 2022-10-07 14:15 |  |  | ATTENDED SITEMEASURED & MADE SAFE BROKEN LOWLITE1 SQM OF SAFETY FILM USEDRETURNED LATER DATE TO REGLAZE10.38 CLEAR LAMINATED SAFETY GLASS1-859 X 595
MSA-DCA | WA5990107 | 2 | GPS Plumbing & Gas Services PtyLtd | Alexander library building - Public area ladies bathroom - Blocked toilet | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 0.91667 | 2022-10-04 13:11 | 2022-10-07 17:00 | 2022-10-05 12:35 | 2022-10-07 17:00 | 2022-10-05 13:30 |  |  | Unblocked cubicle in female public
MSA-MRWA | WA6142718 | 0 | Schindler Lifts Australia | Lift 2 stuck on level 2 | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0.91667 | 2022-11-01 08:29 | 2022-11-01 10:29 | 2022-11-01 16:05 | 2022-11-01 12:29 | 2022-11-01 17:00 |  |  | Works completed - close out at $0
MSA-DTWD | WA6148783 | 2 | Water2water Pty Ltd | Zippy hot water not working – North side of bench | Plumbing & Drainage | Water | 272.46 | Pass | Pass | 0 | 0 | 0.91667 | 2022-11-04 09:10 | 2022-11-09 17:00 | 2022-11-08 10:45 | 2022-11-09 17:00 | 2022-11-08 11:40 |  |  | Replaced faulty hot pump.
MSA-DTAG | WA6190925 | 3 | SCAVENGER SUPPLIES PTY LTD | 2 x Fire Extinguisher to be mounted to wall in Court Custody area | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 177.255 | Pass | Pass | 0 | 0 | 0.91667 | 2022-11-16 11:39 | 2022-11-23 17:00 | 2022-11-22 14:15 | 2022-11-23 17:00 | 2022-11-22 15:10 |  |  | COMPLETED 22/11/22
MSA-DTWD | WA6509142 | 2 | LIGHTHOUSE LOCKSMITHS | Yellagonga office- two door locks are sticking | Security | Locksmith | 467.2 | Pass | Pass | -1 | -1 | 0.91667 | 2023-01-20 07:57 | 2023-01-24 17:00 | 2023-01-20 11:05 | 2023-01-24 17:00 | 2023-01-20 12:00
MSA-DTWD | WA6693732 | 2 | ADVANCED LOCK & KEY | Change 2 x lock barrels to W001 - Location see 2 x red dots on attachment | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.91667 | 2023-03-10 13:54 | 2023-03-15 17:00 | 2023-03-13 11:30 | 2023-03-15 17:00 | 2023-03-13 12:25
MSA-DTWD | WA6707694 | 1 | ADVANCED LOCK & KEY | J107-door lock damaged | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.91667 | 2023-03-13 08:34 | 2023-03-14 17:00 | 2023-03-13 14:05 | 2023-03-14 17:00 | 2023-03-13 15:00
MSA-DCA | WA6721569 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground floor- Unisex disabled toilet - Water not draining from toilet bowl | Plumbing & Drainage | Toilets/Cisterns | 42.79 | Pass | Pass | 0 | 0 | 0.91667 | 2023-03-14 09:40 | 2023-03-15 17:00 | 2023-03-14 14:35 | 2023-03-15 17:00 | 2023-03-14 15:30
MSA-DCA | WA5231512 | 0 | ADVANCED LOCK & KEY | Main Building - External door - not latching | Security | Locksmith | 200 | Fail | Pass | 0 | 0 | 0.91667 | 2022-03-15 11:56 | 2022-03-15 13:56 | 2022-03-15 14:10 | 2022-03-15 15:56 | 2022-03-15 15:05 |  |  | Attend to adjust door hinges and re secure door lock and strike and lube.
MSA-DTAG | WA5735553 | 3 | Water2water Pty Ltd | Level 2a - Kitchen - Billi Tap consistently flashing different symbols - see notes | Plumbing & Drainage | Water | 461.975 | Fail | Fail | 0 | 0 | 0.91667 | 2022-08-16 13:28 | 2022-08-23 17:00 | 2022-08-24 08:55 | 2022-08-23 17:00 | 2022-08-24 09:50 |  |  | System in filter overdue x 7 on arrival. Changed filter. Still poor flow out of solenoids. Changed both the inlet and dual solenoids. Ran system to temp. Normal operation
MSA-DFES | WA6463050 | 2 | Water2water Pty Ltd | Ground - Kitchen - Filtered water system taste foul and unable to drink | Plumbing & Drainage | Water | 273.55 | Pass | Pass | 0 | 0 | 0.91667 | 2023-01-17 09:40 | 2023-01-20 17:00 | 2023-01-18 13:25 | 2023-01-20 17:00 | 2023-01-18 14:20
MSA-DTWD | WA6578684 | 0 | LIGHTHOUSE LOCKSMITHS | faulty lock | Security | Locksmith | 819.2 | Pass | Pass | 0 | 0 | 0.91667 | 2023-02-15 11:23 | 2023-02-15 13:23 | 2023-02-15 11:55 | 2023-02-15 15:23 | 2023-02-15 12:50
MSA-DTWD | WA5190306 | 2 | AHS Services WA Pty Ltd (Anchor) | west male toilet continuously running | Plumbing & Drainage | Toilets/Cisterns | 146.32 | Pass | Pass | 0 | 0 | 0.9 | 2022-02-24 12:31 | 2022-03-01 17:00 | 2022-03-01 11:20 | 2022-03-01 17:00 | 2022-03-01 12:14 |  |  | Completed
MSA-MRWA | WA5564523 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground floor - female bathroom - left hand toilet - not flushing | Plumbing & Drainage | Toilets/Cisterns | 275.28 | Pass | Pass | 0 | 0 | 0.9 | 2022-06-21 11:15 | 2022-06-22 17:00 | 2022-06-21 14:35 | 2022-06-22 17:00 | 2022-06-21 15:29 |  |  | Replaced bellows and outlet washer to 1LHS toilet cubicle to ground floor female toilet.
MSA-DCA | WA5294621 | 2 | Techworks Plumbing | Boola Bardip - Level 2 - Refit or replace broken toilet flush button cover plate, see attached photo | Plumbing & Drainage | Toilets/Cisterns | 125.59 | Pass | Pass | 0 | 0 | 0.9 | 2022-03-29 08:10 | 2022-04-01 17:00 | 2022-03-29 09:00 | 2022-04-01 17:00 | 2022-03-29 09:54 |  |  | Reinstalled flush button
MSA-DCA | WA5534421 | 2 | Allpest WA | Ground – external - Area external to Polly Cafe - Small ant infestation externally to Polly café | Pest Control | General Pest | 160 | Pass | Pass | 0 | 0 | 0.9 | 2022-06-16 10:19 | 2022-06-21 17:00 | 2022-06-20 14:09 | 2022-06-21 17:00 | 2022-06-20 15:03 |  | WCAPPR | Allpest completed works 20.06.2022
MSA-MRWA | WA5693130 | 1 | GPS Plumbing & Gas Services PtyLtd | universal access toilet - toilet constantly running | Plumbing & Drainage | Water | 240.04 | Pass | Pass | 0 | 0 | 0.9 | 2022-08-04 09:30 | 2022-08-05 17:00 | 2022-08-05 06:36 | 2022-08-05 17:00 | 2022-08-05 07:30 |  |  | Replaced failty inlet valve, outlet washer and lubricated flushing mechanism
MSA-DTWD | WA5697234 | 1 | Dormakaba Australia Pty Ltd | main reception, Entry door - will not open or close | Building | Automatic Doors | 689.25 | Pass | Pass | 0 | 0 | 0.9 | 2022-08-09 07:29 | 2022-08-09 17:00 | 2022-08-09 11:00 | 2022-08-09 17:00 | 2022-08-09 11:54 |  |  | Found the safety monitoring board, mode board were corroded. Found that the exit button wasn't working. Cable coming from the exit button was corroded. Replaced corroded boards, repaired cable, tested all ok.
MSA-MRWA | WA5780187 | 1 | Schindler Lifts Australia | lift 3 - stuck on level 8 | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.9 | 2022-08-19 08:08 | 2022-08-22 17:00 | 2022-08-19 10:57 | 2022-08-22 17:00 | 2022-08-19 11:51 |  |  | Works completed - close out at $0
MSA-MRWA | WA5797618 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 10 - Water Storage Tank - over flowing | Plumbing & Drainage | Water | 145.04 | Pass | Pass | 0 | 0 | 0.9 | 2022-08-29 09:30 | 2022-08-30 17:00 | 2022-08-29 15:06 | 2022-08-30 17:00 | 2022-08-29 16:00 |  |  | Adjusted float valve to cold water storage tank on level 10 roof.
MSA-DTWD | WA6020130 | 2 | Dormakaba Australia Pty Ltd | entry auto door is not working. | Building | Automatic Doors | 186.95 | Pass | Pass | -1 | -1 | 0.9 | 2022-10-13 10:59 | 2022-10-18 17:00 | 2022-10-13 14:25 | 2022-10-18 17:00 | 2022-10-13 15:19 |  |  | Found that the controller was in fault, CPU failure. Managed to reset the controller. This unit is in very poor condition and requires an upgrade. As this is a slimline SL201 there a no longer any replacement parts for this unit.
MSA-DTAG | WA6520055 | 3 | Dormakaba Australia Pty Ltd | Court room 2 - Pubic entry door - slow to close and squeaky | Building | Automatic Doors | 345 | Pass | Pass | -1 | -1 | 0.9 | 2023-01-27 10:13 | 2023-02-03 17:00 | 2023-01-27 11:10 | 2023-02-03 17:00 | 2023-01-27 12:04
MSA-MRWA | WA4994953 | 2 | Dormakaba Australia Pty Ltd | Main door - automictic door slow closing **see notes | Building | Automatic Doors | 235 | Pass | Pass | 0 | 0 | 0.88333 | 2022-01-10 09:09 | 2022-01-13 17:00 | 2022-01-10 11:47 | 2022-01-13 17:00 | 2022-01-10 12:40 |  |  | 10/1/22 - Found that the unit will not open correctly, it will slowly open a little bit then stop, it will then open a bit more and stop again and then when it hits the fully open point it will sit there for a long time. I have reset the controller and it is currently working bit this will happen again. The unit is 7 years old and will require an urgent upgrade to an ed100 for reliable operation. BRAF will be raised and sent through.16/3/22 - BRAF no response - invoiced and submitted claim.
MSA-DFES | WA5087738 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Second Floor - Ladies toilets - first and second cubicle - toilet seat damaged | Plumbing & Drainage | Toilets/Cisterns | 224.27 | Pass | Pass | 0 | 0 | 0.88333 | 2022-01-24 12:18 | 2022-01-28 17:00 | 2022-01-25 11:07 | 2022-01-28 17:00 | 2022-01-25 12:00 |  |  | Replaced toilet seat
MSA-DCA | WA5673304 | 2 | GPS Plumbing & Gas Services PtyLtd | toilet will not flush-Out of order sign has been placed on toilet | Plumbing & Drainage | Sewer Drains & Septic Systems | 113.43 | Pass | Pass | 0 | 0 | 0.88333 | 2022-07-20 13:39 | 2022-07-25 17:00 | 2022-07-22 13:17 | 2022-07-25 17:00 | 2022-07-22 14:10 |  |  | Adjusted cistern outlet valve
MSA-DCA | WA6375901 | 0 | TK Elevator Australia Pty Ltd | Lift 6-stuck doors will not open | Lifts | Lifts | 1 | Pass | Pass | 0 | 0 | 0.88333 | 2022-12-15 11:33 | 2022-12-15 13:33 | 2022-12-15 13:19 | 2022-12-15 15:33 | 2022-12-15 14:12 |  |  | Lift stopped on level 4 with doors closed, controller in normal mode with no live error, ran lift from controller with door symbols active although doors would not open, only error being a 210 lift guardian error. Reset ASIC print and regained door operation, checked all relevant connections, could not reproduce fault, tested extensively and returned to service.
MSA-DCA | WA6586251 | 2 | Dormakaba Australia Pty Ltd | Dock Driveway - Gate - Recurring Fault | Building | Automatic Doors | 227.5 | Pass | Pass | -1 | -1 | 0.88333 | 2023-02-16 15:01 | 2023-02-21 17:00 | 2023-02-17 13:35 | 2023-02-21 17:00 | 2023-02-17 14:28
MSA-DCA | WA5038402 | 2 | GPS Plumbing & Gas Services PtyLtd | Rear of PICA Bar building – storm water drain - see notes below | Plumbing & Drainage | Drainage | 1019.93 | Pass | Pass | 0 | 0 | 0.88333 | 2022-01-17 12:49 | 2022-01-20 17:00 | 2022-01-19 07:53 | 2022-01-20 17:00 | 2022-01-19 08:46 |  |  | Pump out tank behind pica bar .
MSA-DTWD | WA5962561 | 2 | Dormakaba Australia Pty Ltd | Central stairway door - door closer broken | Building | Doors | 796.15 | Pass | Pass | 0 | 0 | 0.88333 | 2022-09-19 15:16 | 2022-09-22 17:00 | 2022-09-20 09:36 | 2022-09-22 17:00 | 2022-09-20 10:29 |  |  | Supplied and fitted new TS83 door closer as requested. Adjusted and tested operation upon completion and left in good working order.
MSA-DTWD | WA5101732 | 2 | Dormakaba Australia Pty Ltd | broken door closer | Building | Doors | 591.3 | Pass | Pass | -1 | -1 | 0.88333 | 2022-02-03 14:15 | 2022-02-08 17:00 | 2022-02-04 15:02 | 2022-02-08 17:00 | 2022-02-04 15:55 |  |  | Supplied and fitted new ts83 door closer as requested to room t103, tested operation upon completion and left in good working order.
MSA-DTWD | WA5174856 | 1 | Dormakaba Australia Pty Ltd | Block 1 - Ground - North entry auto door - Door wont close enough to allow locking | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.88333 | 2022-02-21 08:50 | 2022-02-22 17:00 | 2022-02-21 10:00 | 2022-02-22 17:00 | 2022-02-21 10:53 |  |  | 1046630. Asset A403131078. Call to site. Attend to auto door. Check and remove door. Realigned and lubricated floor guide. Refit door and test - all okay
MSA-DTWD | WA5681131 | 2 | AHS Services WA Pty Ltd (Anchor) | . E block. SK3. R/H front sink requires cold water tap to be repaired. Leaking at present | Plumbing & Drainage | Water | 267.32 | Pass | Pass | -1 | -1 | 0.88333 | 2022-07-28 09:22 | 2022-08-02 17:00 | 2022-07-29 13:20 | 2022-08-02 17:00 | 2022-07-29 14:13 |  |  | Completed
MSA-DTWD | WA5681813 | 1 | Dormakaba Australia Pty Ltd | Auto door jammed open | Building | Doors | 180 | Pass | Pass | 0 | 0 | 0.88333 | 2022-07-28 16:00 | 2022-07-29 17:00 | 2022-07-29 08:01 | 2022-07-29 17:00 | 2022-07-29 08:54 |  |  | On inspection found drive arm and hinges fixings were loose, tightened arm and hinges, checked all push buttons, tested door operation a number of times, left door in good working condition.
MSA-DCA | WA6165850 | 1 | Techworks Plumbing | Jubilee building - Ground floor - Toilet blockage/leaking and flooding | Plumbing & Drainage | Toilets/Cisterns |  | Pass | Pass | 0 | 0 | 0.88333 | 2022-11-11 10:07 | 2022-11-14 17:00 | 2022-11-11 10:07 | 2022-11-14 17:00 | 2022-11-11 11:00 |  |  | Attended site and signed inUnblocked toilets by plunging Tested toilets after unblocking Cleaned up and left siteCompleted paperwork
MSA-DTAG | WA6707865 | 0 | SCAVENGER SUPPLIES PTY LTD | Fire panel - Power fault and low battery | Fire Protection Services | Smoke and Heat Detection | 241.649 | Pass | Pass | 0 | 0 | 0.88333 | 2023-03-13 09:52 | 2023-03-13 11:52 | 2023-03-13 11:37 | 2023-03-13 13:52 | 2023-03-13 12:30
MSA-DTWD | WA6358736 | 2 | Dormakaba Australia Pty Ltd | Auto door to rooms F1 to F7 - Auto door opens but not close | Building | Automatic Doors | 186.95 | Pass | Pass | 0 | 0 | 0.88333 | 2022-12-06 09:47 | 2022-12-09 17:00 | 2022-12-07 09:08 | 2022-12-09 17:00 | 2022-12-07 10:01 |  |  | Attended site and found door working fine on arrival. On inspection found bottom of door was hitting on the weather strip causing door to obstruct and open up. Adjusted so door was not hitting. Tested and all working fine now. Left area clean and tidy.
MSA-DCA | WA5488285 | 3 | GPS Plumbing & Gas Services PtyLtd | Third Floor - Ladies Public Bathroom - Tap furthest from door loose and not working | Plumbing & Drainage | Water | 105.41 | Pass | Pass | -1 | -1 | 0.86667 | 2022-06-02 11:43 | 2022-06-10 17:00 | 2022-06-03 09:28 | 2022-06-10 17:00 | 2022-06-03 10:20 |  |  | Tightened loose nute under basin
MSA-DTWD | WA5879894 | 1 | Dormakaba Australia Pty Ltd | Fault description Push buttons operate but door only opens 6 inches then stops. | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.86667 | 2022-09-15 10:01 | 2022-09-16 17:00 | 2022-09-15 11:07 | 2022-09-16 17:00 | 2022-09-15 11:59 |  |  | Found door is turned off, however on/off switch has seized in the off position. Removed cover and inspected. Found unit had major fatigue due to age (approx 20 years old). The unit has a fixed mains input with no visible signs of isolation. Quote to follow in due course.
MSA-DTWD | WA5681816 | 2 | Water2water Pty Ltd | Tap on BWU is broken - see notes below | Plumbing & Drainage | Water | 292.18 | Pass | Pass | 0 | 0 | 0.86667 | 2022-07-28 16:16 | 2022-08-02 17:00 | 2022-08-02 11:18 | 2022-08-02 17:00 | 2022-08-02 12:10 |  |  | Tap broken on wall mounted urn on arrival. Difficult to get water out. Replaced RHEEM tap. Waited for unit to fill and get to temp. Normal operation
MSA-DTWD | WA5105820 | 2 | Dormakaba Australia Pty Ltd | Faulty Automatic door button outside of M block - The button is only just staying in the holder | Building | Automatic Doors | 561.78 | Pass | Pass | 0 | 0 | 0.86667 | 2022-02-04 14:36 | 2022-02-09 17:00 | 2022-02-07 08:28 | 2022-02-09 17:00 | 2022-02-07 09:20 |  |  | Found that both of the push buttons have failed, replaced buttons, tested all ok.
MSA-MRWA | WA5108145 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 -Female Bathrooms – RHS toilet - Toilet running continuously | Plumbing & Drainage | Toilets/Cisterns | 274.78 | Pass | Pass | 0 | 0 | 0.86667 | 2022-02-08 12:02 | 2022-02-11 17:00 | 2022-02-09 10:08 | 2022-02-11 17:00 | 2022-02-09 11:00 |  |  | Replaced outlet washer and one bellow
MSA-DTAG | WA5570888 | 1 | GPS Plumbing & Gas Services PtyLtd | Level - Registrar’s Kitchen - sink is blocked | Plumbing & Drainage | Drainage | 134.78 | Pass | Pass | 0 | 0 | 0.86667 | 2022-06-28 16:29 | 2022-06-29 17:00 | 2022-06-29 08:00 | 2022-06-29 17:00 | 2022-06-29 08:52 |  |  | Cleared blocked sink caused by food stuff
MSA-DTWD | WA5749664 | 2 | Dormakaba Australia Pty Ltd | P-Block Room P003 the door closer does not work anymore | Building | Doors | 681.15 | Pass | Pass | -1 | -1 | 0.86667 | 2022-08-17 09:06 | 2022-08-22 17:00 | 2022-08-17 15:08 | 2022-08-22 17:00 | 2022-08-17 16:00 |  |  | Removed faulty door closer and replaced with new TS83 closer. Adjusted and tested operation upon completion and left in good working order.
MSA-DTWD | WA5880278 | 1 | Dormakaba Australia Pty Ltd | Roller door is stuck in the up position | Building | Roller Shutters | 186.95 | Pass | Pass | 0 | 0 | 0.86667 | 2022-09-15 11:50 | 2022-09-16 17:00 | 2022-09-15 13:38 | 2022-09-16 17:00 | 2022-09-15 14:30 |  |  | Bottom rail had come out of LH guide due to guide being too far out. Returned bottom rail to guide and adjusted to prevent it happening again.
MSA-DTWD | WA6147680 | 2 | AWB Co. | Light switches faulty - AWB technician is currently onsite | Electrical | General Electrical | 422.16 | Pass | Pass | -1 | -1 | 0.86667 | 2022-11-03 09:07 | 2022-11-08 17:00 | 2022-11-03 09:08 | 2022-11-08 17:00 | 2022-11-03 10:00 |  |  | Attended site signed in jsa completed. Found faulty switch plate and mechs in class. Went to wholesaler and collect new one. Install and tested operational.Job completed
MSA-DCA | WA6515414 | 0 | GPS Plumbing & Gas Services PtyLtd | Gas smell on multiple levels of the building - Unknown cause | Plumbing & Drainage | Gas | 229.69 | Pass | Pass | 0 | 0 | 0.86667 | 2023-01-21 12:45 | 2023-01-21 14:45 | 2023-01-21 13:47 | 2023-01-21 16:45 | 2023-01-21 14:39
MSA-DTWD | WA6680399 | 1 | Water2water Pty Ltd | Broken digitial indicator on handles | Plumbing & Drainage | Water | 79.96 | Pass | Pass | 0 | 0 | 0.86667 | 2023-03-01 10:55 | 2023-03-02 17:00 | 2023-03-02 11:56 | 2023-03-02 17:00 | 2023-03-02 12:48
MSA-DCA | WA5018241 | 0 | GPS Plumbing & Gas Services PtyLtd | basement - Sewer pump room - sewer pump warning light is on | Plumbing & Drainage | Water | 166.49 | Pass | Pass | 0 | 0 | 0.85 | 2022-01-14 10:16 | 2022-01-14 12:16 | 2022-01-14 10:35 | 2022-01-14 14:16 | 2022-01-14 11:26 |  |  | Checked all tanks ,effluent levels ok.Reset fault on control panel that was caused by power surge.
MSA-DTWD | WA5200740 | 3 | AWB Co. | Buzzing noise coming from distribution board | Electrical | General Electrical | 197.32 | Pass | Pass | -1 | -1 | 0.85 | 2022-03-02 08:53 | 2022-03-10 17:00 | 2022-03-02 08:54 | 2022-03-10 17:00 | 2022-03-02 09:45 |  |  | Milan Barjaktar (02/03/2022) - Work NoteAttended site signed in completed jsa. Found noise in board to be the main buzz bar for the board. Will need to re torque bolts in whole board as it will make a hot spot if loose. Have advised site of this and mike has said he will speak to the installers of the board or manufacturer to come repair. Job is still open as he is not sure and needs time to decide.Approval needed**Advised close costs to date**
MSA-DTWD | WA5569009 | 3 | Water2water Pty Ltd | 3-29 Staff Lunchroom - Billi unit slow running | Plumbing & Drainage | HWS/Units Electric & Gas | 311.36 | Pass | Pass | -1 | -1 | 0.85 | 2022-06-27 11:15 | 2022-07-04 17:00 | 2022-06-28 09:30 | 2022-07-04 17:00 | 2022-06-28 10:21 |  |  | Replaced Billi filter and completed service to unit to restore flow of cold water
MSA-DCA | WA5572758 | 2 | GPS Plumbing & Gas Services PtyLtd | Dress Circle - Male Cubicles - Toilets are not flushing properly | Plumbing & Drainage | Toilets/Cisterns | 233.04 | Pass | Pass | 0 | 0 | 0.85 | 2022-06-30 10:23 | 2022-07-05 17:00 | 2022-07-04 14:35 | 2022-07-05 17:00 | 2022-07-04 15:26 |  |  | Service 2x leak toilets
MSA-DTWD | WA6707823 | 1 | Dormakaba Australia Pty Ltd | Main entry auto door - auto doors will not unlock although proxy swipe has gone green | Building | Automatic Doors | 180 | Pass | Pass | 0 | 0 | 0.85 | 2023-03-13 09:28 | 2023-03-14 17:00 | 2023-03-13 12:19 | 2023-03-14 17:00 | 2023-03-13 13:10
MSA-DCA | WA5285987 | 1 | Earth & Water Pty Ltd | Urban Orchard - Ground – external - Urban orchard garden bed – North west corner - see details below | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.85 | 2022-03-21 11:42 | 2022-03-22 17:00 | 2022-03-21 12:59 | 2022-03-22 17:00 | 2022-03-21 13:50 |  |  | Broken sprinkler causing damage and wasting water-Replaced 'Ix broken sprinkler body on zone 8
MSA-MRWA | WA6517795 | 0 | GPS Plumbing & Gas Services PtyLtd | Jacaranda Room - Water leak from ceiling | Plumbing & Drainage | Water | 267.3 | Pass | Pass | 0 | 0 | 0.85 | 2023-01-24 12:39 | 2023-01-24 14:39 | 2023-01-24 13:59 | 2023-01-24 16:39 | 2023-01-24 14:50
MSA-DTWD | WA5190796 | 2 | Water2water Pty Ltd | U011 - Machine workshop - water cooler is not working | Plumbing & Drainage | Water | 87.23 | Pass | Pass | 0 | 0 | 0.85 | 2022-02-24 14:41 | 2022-03-01 17:00 | 2022-02-28 10:09 | 2022-03-01 17:00 | 2022-02-28 11:00 |  |  | Investigated issue with the water cooler, found that the compressor has blown needs replacement submit quote to replace.
MSA-DCA | WA6043984 | 1 | TK Elevator Australia Pty Ltd | Level 1-Lift 7-stuck on HLT level - see notes | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.85 | 2022-10-17 09:58 | 2022-10-18 17:00 | 2022-10-17 16:07 | 2022-10-18 17:00 | 2022-10-17 16:58 |  |  | Lift7 Greem Rm-Elevator > MR > Hydraulic :*STE1AP* ERROR recorded on lift main print. Powercycled lift, lift running again, noticed lift door motor drive unit "ticking" over. Ran lift to all floors, lift back in service. Lift may need new door drive?.
MSA-DTAG | WA6154579 | 3 | GPS Plumbing & Gas Services PtyLtd | Magistrates Level Bathroom near stairs - running water in toilets | Plumbing & Drainage | Toilets/Cisterns | 185.04 | Pass | Pass | -1 | -1 | 0.85 | 2022-11-07 13:43 | 2022-11-14 17:00 | 2022-11-09 09:40 | 2022-11-14 17:00 | 2022-11-09 10:31 |  |  | Repaired leaking outlet valve to disabled toilet upstairs near the stairs.
MSA-DTAG | WA6655432 | 2 | Gilmour & Jooste Electrical | Family violence - Replace fluro tub light in family violence office - also making loud buzzing noise | Electrical | Lighting, External | 155.68 | Pass | Pass | 0 | 0 | 0.85 | 2023-02-21 10:25 | 2023-02-24 17:00 | 2023-02-23 12:15 | 2023-02-24 17:00 | 2023-02-23 13:06
MSA-DCA | WA5087025 | 0 | Critical Fire Protection & Training | Stage door - Fault on the fire panel. | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 267.9852 | Pass | Pass | 0 | 0 | 0.83333 | 2022-01-22 14:45 | 2022-01-22 16:45 | 2022-01-22 15:30 | 2022-01-22 18:45 | 2022-01-22 16:20 |  |  | Investigated main pump running. Jacking pump was in the off position. Set jacking pump back to auto. Issue looks to be a pressure fluctuation due to outside temp.Dropped valves back to 1200 kpa. System normal.
MSA-DTWD | WA5094412 | 1 | Complete Pest Management Services | Block 8 - 8F51 -Bad smell coming from roof space | Pest Control | General Pest | 240.91 | Pass | Pass | 0 | 0 | 0.83333 | 2022-01-31 10:58 | 2022-02-01 17:00 | 2022-02-01 13:40 | 2022-02-01 17:00 | 2022-02-01 14:30 |  |  | Bafx storeroom removed dead mouse behind cabinetBlock 8 room 51 cannot access roof void , used 2 x fresh wave iaq natural odour eliminator gel
MSA-DTWD | WA5207313 | 2 | AHS Services WA Pty Ltd (Anchor) | Library 1st Floor, the accessibility toilet is continuously running | Plumbing & Drainage | Toilets/Cisterns | 152.07 | Pass | Pass | 0 | 0 | 0.83333 | 2022-03-08 12:15 | 2022-03-11 17:00 | 2022-03-09 08:00 | 2022-03-11 17:00 | 2022-03-09 08:50 |  |  | Completed
MSA-DCA | WA5226960 | 1 | GPS Plumbing & Gas Services PtyLtd | Main Building - Ground Floor - Stalls Ladies Toilets - | Plumbing & Drainage | Toilets/Cisterns | 264.97 | Pass | Pass | 0 | 0 | 0.83333 | 2022-03-14 16:09 | 2022-03-15 17:00 | 2022-03-15 10:40 | 2022-03-15 17:00 | 2022-03-15 11:30 |  |  | Replaced leaking induct water wafer top entry inlet valve.
MSA-DTWD | WA5392968 | 2 | ACTION GLASS & ALUMINIUM | Room A234 - window top half has fallen down and cant push back up | Glazing | Window Glass | 130 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-03 13:45 | 2022-05-06 17:00 | 2022-05-05 10:40 | 2022-05-06 17:00 | 2022-05-05 11:30 |  |  | ATTENDED SITE AND SCREWED WINDOW SHUT AS REQUESTED BY FM
MSA-DTWD | WA5399034 | 2 | Swan Pest Control | Admin Area - treat area for Cockroaches | Pest Control | General Pest | 193 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-09 14:19 | 2022-05-12 17:00 | 2022-05-12 09:30 | 2022-05-12 17:00 | 2022-05-12 10:20 |  |  | Sprayed admin offices and external offices and gelled cupboard
MSA-DTAG | WA5472146 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground Level - Jury Room Toilet - Toilet Blocked | Plumbing & Drainage | Toilets/Cisterns | 203.88 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-23 14:44 | 2022-05-24 17:00 | 2022-05-24 08:00 | 2022-05-24 17:00 | 2022-05-24 08:50 |  |  | Completed
MSA-DTWD | WA5734630 | 2 | High Tech Pest Control | Pest control emergency exit door ant infected | Pest Control | General Pest | 222.6 | Fail | Fail | 0 | 0 | 0.83333 | 2022-08-16 08:30 | 2022-08-19 17:00 | 2022-08-22 14:45 | 2022-08-19 17:00 | 2022-08-22 15:35 |  |  | Treat ants in U19 rear emergency door, also located nest in bush and has been treated.
MSA-DTAG | WA5799904 | 1 | GPS Plumbing & Gas Services PtyLtd | Ladies toilet - Level 1 - First toilet is continually flushing | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 0.83333 | 2022-08-30 15:36 | 2022-08-31 17:00 | 2022-08-31 10:40 | 2022-08-31 17:00 | 2022-08-31 11:30 |  |  | Adjusted water level and cleaned up inlet valve
MSA-DTAG | WA5833509 | 1 | Dormakaba Australia Pty Ltd | Garage - Roller door is not operational | Building | Roller Shutters | 351.95 | Pass | Pass | 0 | 0 | 0.83333 | 2022-09-06 10:22 | 2022-09-07 17:00 | 2022-09-06 14:25 | 2022-09-07 17:00 | 2022-09-06 15:15 |  |  | Tested and inspected operation multiple times, door working correctly. During further investigation found safety beam working intermittently which may have been causing the fault. Quote to follow in due course.
MSA-DCA | WA5838480 | 3 | GPS Plumbing & Gas Services PtyLtd | staff male toilet - both cubicles - water leaking to pan | Plumbing & Drainage | Toilets/Cisterns | 110.64 | Pass | Pass | 0 | 0 | 0.83333 | 2022-09-08 13:45 | 2022-09-15 17:00 | 2022-09-13 09:10 | 2022-09-15 17:00 | 2022-09-13 10:00 |  |  | Replaced 2 outlet washers
MSA-DTWD | WA5973480 | 3 | Water2water Pty Ltd | Zip Boiler needs de scaling | Plumbing & Drainage | HWS/Units Electric & Gas | 173.82 | Pass | Pass | 0 | 0 | 0.83333 | 2022-09-21 13:21 | 2022-09-29 17:00 | 2022-09-27 15:30 | 2022-09-29 17:00 | 2022-09-27 16:20 |  |  | Descaled tap, improved water flow from outlet
MSA-DTWD | WA6151629 | 1 | CONNECT SECURITY SYSTEMS | A/Block alarm battery is flat - unable to lock front door | Security | Security Management System | 169.41 | Pass | Pass | 0 | 0 | 0.83333 | 2022-11-07 07:52 | 2022-11-07 17:00 | 2022-11-07 11:00 | 2022-11-07 17:00 | 2022-11-07 11:50 |  |  | Replaced dead battery
MSA-DTWD | WA6158637 | 3 | Water2water Pty Ltd | Foyer/Corridor - Cold Water Drinking Unit failed | Plumbing & Drainage | Water | 4573.36 | Pass | Pass | 0 | 0 | 0.83333 | 2022-11-10 07:55 | 2022-11-16 17:00 | 2022-11-15 10:15 | 2022-11-16 17:00 | 2022-11-15 11:05 |  |  | Carried out testing and diagnosis on failed water fountain. refrigeration failure. recommend replacement with like for like
MSA-MRWA | WA6377293 | 2 | GPS Plumbing & Gas Services PtyLtd | Toilet constantly running | Plumbing & Drainage | Toilets/Cisterns | 534.165 | Pass | Pass | 0 | 0 | 0.83333 | 2022-12-16 12:35 | 2022-12-21 17:00 | 2022-12-19 15:30 | 2022-12-21 17:00 | 2022-12-19 16:20 |  |  | Replaced faulty inlet valve
MSA-DCA | WA6520480 | 3 | CONNECT SECURITY SYSTEMS | G Block - Ward 2 - PIR beam faulty causing false alarms | Security | Security Management System | 224.7 | Pass | Pass | 0 | 0 | 0.83333 | 2023-01-27 15:07 | 2023-02-03 17:00 | 2023-01-31 14:00 | 2023-02-03 17:00 | 2023-01-31 14:50
MSA-DTAG | WA6675110 | 1 | GPS Plumbing & Gas Services PtyLtd | Ladies Bathroom near Court 10 & 11 - No water coming out of taps | Plumbing & Drainage | Drainage | 221.7275 | Pass | Pass | 0 | 0 | 0.83333 | 2023-02-27 15:27 | 2023-02-28 17:00 | 2023-02-28 08:00 | 2023-02-28 17:00 | 2023-02-28 08:50
MSA-DTWD | WA5383205 | 0 | Casa Security Pty Ltd | The Whole Block - no data communication to alarm panel | Security | Security Management System | 207.5 | Pass | Pass | 0 | 0 | 0.83333 | 2022-04-27 13:22 | 2022-04-27 15:22 | 2022-04-27 14:50 | 2022-04-27 17:22 | 2022-04-27 15:40 |  |  | Checked system M blockSpoke with Edsec (monitoring station)Faults on the keypad are zones that are openFull test of system. They received all communications Found nothing wrong with system at all *please note any future problems due to communications with the 4G monitoring module to the control room are not to do with Casa Security, would need to contact the company that installed the 4G device to communicate with edsec***
MSA-DCA | WA5511975 | 1 | Dormakaba Australia Pty Ltd | Level 1 - HLT dock – cable gate - roller door has come off rollers - See notes | Building | Roller Shutters | 210 | Pass | Pass | 0 | 0 | 0.83333 | 2022-06-13 11:45 | 2022-06-14 17:00 | 2022-06-13 13:20 | 2022-06-14 17:00 | 2022-06-13 14:10 |  |  | Door came down on top of truck, causing curtain to balloon and come out of guides, shifted and adjusted curtain, put curtain back into the guides, reset limits on the door, door tested and working well.
MSA-DTWD | WA5534334 | 1 | ECO PLUMBING AND GAS PTY LTD | Blockage in pipework leading to toilets overflowing | Plumbing & Drainage | Drainage | 141.28 | Pass | Pass | 0 | 0 | 0.83333 | 2022-06-16 09:13 | 2022-06-17 17:00 | 2022-06-17 15:20 | 2022-06-17 17:00 | 2022-06-17 16:10 |  |  | Cleared blockage using plunger
MSA-MRWA | WA5800319 | 1 | Water2water Pty Ltd | Hot water unit has failed | Plumbing & Drainage | HWS/Units Electric & Gas | 260.46 | Pass | Pass | 0 | 0 | 0.83333 | 2022-08-31 09:06 | 2022-09-01 17:00 | 2022-08-31 13:50 | 2022-09-01 17:00 | 2022-08-31 14:40 |  |  | Replaced faulty main power lead and it getting good connector to internal mother board. All now working okay!
MSA-DTAG | WA5861880 | 2 | Water2water Pty Ltd | Level 12 - Meeting Room - Billi Unit in Conference Room – Outage and lights flashing | Plumbing & Drainage | HWS/Units Electric & Gas | 796.245 | Pass | Pass | 0 | 0 | 0.83333 | 2022-09-13 11:59 | 2022-09-16 17:00 | 2022-09-15 11:20 | 2022-09-16 17:00 | 2022-09-15 12:10 |  |  | System in locked off and filter change x 9 fault on arrival. Changed filter and front pcb display board. Put in all numbers and offsets. Flushed filter and re calibrated unit. Ran to temp. Normal operation
MSA-DFES | WA6019605 | 1 | SONTEC WA PTY LTD | 17 door controllers off line | Security | Access Control | 310 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-13 07:03 | 2022-10-13 17:00 | 2022-10-13 08:50 | 2022-10-13 17:00 | 2022-10-13 09:40 |  |  | 13/10/22 - Dylan ParslowFound level 2 power supply not providing power to door controllers.Reset and tested, all working.
MSA-DTWD | WA6108722 | 1 | CONNECT SECURITY SYSTEMS | Block C - faulty Alarm system shows tamper fault | Security | Security Management System | 293.44 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-20 10:30 | 2022-10-21 17:00 | 2022-10-20 13:52 | 2022-10-21 17:00 | 2022-10-20 14:42 |  |  | Replaced faulty tamper switch to C Block Zone Expander Cabinet.
MSA-MRWA | WA6125836 | 2 | GPS Plumbing & Gas Services PtyLtd | Safety shower not alarming, actuator probably stuck | Plumbing & Drainage | Water | 145.04 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-25 08:48 | 2022-10-28 17:00 | 2022-10-26 12:50 | 2022-10-28 17:00 | 2022-10-26 13:40 |  |  | Clean sensor probe to emergency shower to Bitumen lab.
MSA-DTAG | WA6144737 | 1 | Water2water Pty Ltd | Level 11-Fault description Billi Unit cold water is slowing down. Filter might need replacement. | Plumbing & Drainage | Water | 347.115 | Pass | Pass | 0 | 0 | 0.83333 | 2022-11-02 08:51 | 2022-11-03 17:00 | 2022-11-02 11:35 | 2022-11-03 17:00 | 2022-11-02 12:25 |  |  | Slow flow in arrival. Making a funny noise, ran tests. Everything seems to be working ok, getting to levels. Changed Billi filter and flushed and checked under pressure
MSA-DTAG | WA6250539 | 1 | GPS Plumbing & Gas Services PtyLtd | Basement - Detention area - Cell 2 toilet continously running. Been running all weekend | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 0.83333 | 2022-11-22 09:04 | 2022-11-23 17:00 | 2022-11-22 12:50 | 2022-11-23 17:00 | 2022-11-22 13:40 |  |  | Removed foreign object/debri from valve seal. Flushed cistern multiple times-no issues
MSA-DCA | WA6360797 | 2 | GPS Plumbing & Gas Services PtyLtd | BOH Ladies Toilets - First cubicle toilet cistern is loose, coming away from wall. | Plumbing & Drainage | Toilets/Cisterns | 113.43 | Pass | Pass | 0 | 0 | 0.83333 | 2022-12-07 14:45 | 2022-12-12 17:00 | 2022-12-09 13:50 | 2022-12-12 17:00 | 2022-12-09 14:40 |  |  | Installed new bracket screws, old ones were broken
MSA-DTAG | WA6392896 | 1 | GPS Plumbing & Gas Services PtyLtd | Sheriff's office-1987-ladies Toilet is blocked and water is not draining out. | Plumbing & Drainage | Toilets/Cisterns | 145.04 | Pass | Pass | 0 | 0 | 0.83333 | 2022-12-28 06:55 | 2022-12-28 17:00 | 2022-12-28 13:20 | 2022-12-28 17:00 | 2022-12-28 14:10 |  |  | Unblocked lhs cubicle
MSA-DTWD | WA6494799 | 1 | Dormakaba Australia Pty Ltd | West end entrance - Automatic door is stuck on open - see notes | Building | Automatic Doors | 518.73 | Pass | Pass | 0 | 0 | 0.83333 | 2023-01-18 16:11 | 2023-01-19 17:00 | 2023-01-19 11:01 | 2023-01-19 17:00 | 2023-01-19 11:51
MSA-DTWD | WA6690439 | 1 | LIGHTHOUSE LOCKSMITHS | Faulty door handle and lock | Security | Locksmith | 472.8 | Pass | Pass | 0 | 0 | 0.83333 | 2023-03-09 09:31 | 2023-03-10 17:00 | 2023-03-09 09:50 | 2023-03-10 17:00 | 2023-03-09 10:40
MSA-DTWD | WA4990831 | 1 | Milners Tree Solutions Pty Ltd | B Block - Eternal lawn area - Large gum tree branch has fallen | Landscaping & Gardening | Tree Lopping | 1000 | Pass | Pass | 0 | 0 | 0.83333 | 2022-01-04 12:06 | 2022-01-05 17:00 | 2022-01-05 06:40 | 2022-01-05 17:00 | 2022-01-05 07:30 |  |  | LARGE FALLEN LIMB REMOVED. SMALL FALLEN LIMB REMOVED
MSA-DTWD | WA5052969 | 0 | Dormakaba Australia Pty Ltd | Door is stucked half way open and wont close | Building | Automatic Doors | 300 | Pass | Pass | 0 | 0 | 0.83333 | 2022-01-18 11:31 | 2022-01-18 13:31 | 2022-01-18 12:15 | 2022-01-18 15:31 | 2022-01-18 13:05 |  |  | Door not operating due to locked up sprocket. Free up sprocket lubricated all parts until working freely, reassembled and tested all working well .
MSA-DFES | WA5068927 | 3 | Water2water Pty Ltd | Heritage Shed - drink fountains not working | Plumbing & Drainage | Water | 207.845 | Pass | Pass | 0 | 0 | 0.83333 | 2022-01-19 12:29 | 2022-01-27 17:00 | 2022-01-24 10:10 | 2022-01-27 17:00 | 2022-01-24 11:00 |  |  | Replaced Bubbler insert on Fountain A40270985
MSA-DCA | WA5108665 | 2 | GPS Plumbing & Gas Services PtyLtd | Warehouse - ground floor - female toilets - toilet is leaking from the seal behind the bowl | Plumbing & Drainage | Water | 209.78 | Pass | Pass | 0 | 0 | 0.83333 | 2022-02-08 16:02 | 2022-02-11 17:00 | 2022-02-09 15:25 | 2022-02-11 17:00 | 2022-02-09 16:15 |  |  | Replaced leaking seals on the flush pipe
MSA-DTWD | WA5175010 | 1 | Dormakaba Australia Pty Ltd | auto door G/Floor West beeping continuously | Building | Automatic Doors | 316.64 | Pass | Pass | 0 | 0 | 0.83333 | 2022-02-21 09:44 | 2022-02-22 17:00 | 2022-02-21 12:00 | 2022-02-22 17:00 | 2022-02-21 12:50 |  |  | Inspected door and found lock mode reset error was displaying on the controller, found boards were faulty, replaced 1 mode connection board and security interface boards, tested door operation a number of times, all working fine.
MSA-DTWD | WA5192001 | 2 | PEEL LOCK SERVICES PTY LTD | F 1 animal Studies - Staff room - Door lock Brocken needs replacing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.83333 | 2022-02-25 10:43 | 2022-03-02 17:00 | 2022-02-28 13:00 | 2022-03-02 17:00 | 2022-02-28 13:50 |  |  | job completed - lock replaced
MSA-DCA | WA5207383 | 2 | GPS Plumbing & Gas Services PtyLtd | Male staff toilet - 2nd basin tap is very loose | Plumbing & Drainage | Materials | 233.43 | Pass | Pass | 0 | 0 | 0.83333 | 2022-03-08 12:44 | 2022-03-11 17:00 | 2022-03-11 10:30 | 2022-03-11 17:00 | 2022-03-11 11:20 |  |  | Installed ministop and refitted loose pillar tap to ground floor staff male toilet LHS.
MSA-DCA | WA5288570 | 1 | Earth & Water Pty Ltd | Urban Orchard – zone 15 -2 x retic leaks in garden beds | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.83333 | 2022-03-23 11:37 | 2022-03-24 17:00 | 2022-03-24 08:10 | 2022-03-24 17:00 | 2022-03-24 09:00 |  |  | job completed - -Fixed leak were drip line had split with 16mm barbed joiner-Fixed leak where drip to pvc threaded adapter had cracked by removing broken thread from pvc tee and replacing.-Tested system. Checked for any other issues.-Found one more split in dripline. Fixed with 16mm barbed joiner.-Photos added to diary-Unsuspended zone-Left area clean and tidy
MSA-DTWD | WA5291073 | 2 | PEEL LOCK SERVICES PTY LTD | B Block - Ground - B20 - Lock damaged needs replacing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.83333 | 2022-03-25 14:34 | 2022-03-30 17:00 | 2022-03-29 12:00 | 2022-03-30 17:00 | 2022-03-29 12:50 |  |  | faulty lock
MSA-DCA | WA5306614 | 2 | GPS Plumbing & Gas Services PtyLtd | Warehouse Building - Ground - Male toilet - Tap on hand basin is not working correctly | Plumbing & Drainage | Toilets/Cisterns | 130.02 | Pass | Pass | 0 | 0 | 0.83333 | 2022-04-06 15:26 | 2022-04-11 17:00 | 2022-04-08 16:00 | 2022-04-11 17:00 | 2022-04-08 16:50 |  |  | Rewashed badly seized taps
MSA-DCA | WA5309942 | 0 | GPS Plumbing & Gas Services PtyLtd | water leak from level one going down to ground floor | Plumbing & Drainage | Materials | 142.735 | Fail | Fail | 0 | 0 | 0.83333 | 2022-04-10 19:32 | 2022-04-10 21:32 | 2022-04-11 06:26 | 2022-04-10 23:32 | 2022-04-11 07:16 |  |  | On the night on the 10/4 I had a conversation with Georgia who advised me to come and look at the issue the following morning(Monday morning). After her description of the issue we figured out that there was a leak somewhere in the roof(started raining heavily that night). On my arrival on monday morning i was unable to see any leaks. Unable to check the roof due to roof being wet. A different contractor is required. Reese advised.
MSA-MRWA | WA5396749 | 1 | Water2water Pty Ltd | HWS - billie not working - no power | Plumbing & Drainage | HWS/Units Electric & Gas | 161.54 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-06 11:16 | 2022-05-09 17:00 | 2022-05-09 09:40 | 2022-05-09 17:00 | 2022-05-09 10:30 |  |  | CURRENT UNIT IS BEYOND ECONOMICAL REPAIR.
MSA-DFES | WA5399234 | 2 | Water2water Pty Ltd | Kitchen hot/cold water dispenser not working zip boil type - Billie Quadra | Plumbing & Drainage | Water | 161.54 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-09 19:49 | 2022-05-12 17:00 | 2022-05-11 10:00 | 2022-05-12 17:00 | 2022-05-11 10:50 |  |  | Fixed leak from waste line. Changed a few settings. Everything running to specs
MSA-DTWD | WA5462100 | 2 | Water2water Pty Ltd | Corridor outside B21 - one drinking water fountains not working | Plumbing & Drainage | Water | 252.73 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-19 11:17 | 2022-05-24 17:00 | 2022-05-23 09:00 | 2022-05-24 17:00 | 2022-05-23 09:50 |  |  | Replaced faulty bottle filler
MSA-DTWD | WA5478280 | 1 | AHS Services WA Pty Ltd (Anchor) | Kendrew- C-Block G/Floor Ladies toilet continuously running | Plumbing & Drainage | Toilets/Cisterns | 146.32 | Pass | Pass | 0 | 0 | 0.83333 | 2022-05-26 10:37 | 2022-05-27 17:00 | 2022-05-27 07:00 | 2022-05-27 17:00 | 2022-05-27 07:50 |  |  | Completed
MSA-DTWD | WA5494237 | 2 | Water2water Pty Ltd | Level 1 - F001 - metal fabrication work shop - water drink fountain keeps running - wont turn off | Plumbing & Drainage | Water | 238.8225 | Pass | Pass | 0 | 0 | 0.83333 | 2022-06-07 13:19 | 2022-06-10 17:00 | 2022-06-09 15:40 | 2022-06-10 17:00 | 2022-06-09 16:30 |  |  | Replaced faulty bubbler. AllNow working ok.
MSA-DTWD | WA5562534 | 1 | Dormakaba Australia Pty Ltd | Main entrance - Oxford Street - Roller door is not working | Building | Roller Shutters | 180 | Pass | Pass | 0 | 0 | 0.83333 | 2022-06-20 07:58 | 2022-06-20 17:00 | 2022-06-20 10:30 | 2022-06-20 17:00 | 2022-06-20 11:20 |  |  | Customer says door would sometimes stop closing whilst operating with key switch.Assessed key switch wiring, motor, c10 controller, door leaf and guides, tested door multiple times, checked all fixings and lubricated where necessary. No faults were found, door operating correctly.
MSA-DCA | WA5627937 | 1 | ACTION GLASS & ALUMINIUM | Ground level, between train station and art gallery entrance - Broken Glass on sign - See notes | Glazing | Specialist Glass | 256.88 | Pass | Pass | 0 | 0 | 0.83333 | 2022-07-15 09:28 | 2022-07-18 17:00 | 2022-07-15 12:00 | 2022-07-18 17:00 | 2022-07-15 12:50 |  |  | ATTENDED SITE AND MADE SAFE, HAVE BEEN ADVISED BY PROGRAMMED TO CLOSE WORKS OFF FOR MAKE SAFE "Hi Dom I have just followed up with the Dept and they will engage the original installer to complete the works. Please close of your breakdown with costs to date for the attendance and make safe. Thank you Kind regards Denise McCartney Building & Asset Maintenance Officer"
MSA-DTWD | WA5655750 | 1 | Dormakaba Australia Pty Ltd | Main entrance - Auto door not allowing entry on automatic setting | Building | Doors | 717.92 | Pass | Pass | 0 | 0 | 0.83333 | 2022-07-18 10:09 | 2022-07-19 17:00 | 2022-07-18 12:42 | 2022-07-19 17:00 | 2022-07-18 13:32 |  |  | Replace faulty external sensor due to wasp nest inside cover
MSA-DCA | WA5677501 | 3 | Critical Fire Protection & Training | Ground Floor - Security Control Room - EWIS panel has a System Fault light on | Fire Protection Services | Fire Protection - Monitor System | 75.975 | Pass | Pass | -1 | -1 | 0.83333 | 2022-07-25 14:51 | 2022-08-01 17:00 | 2022-07-26 11:40 | 2022-08-01 17:00 | 2022-07-26 12:30 |  |  | Start time: 11:40amFinish time: 12:30pmEWIS panel indicating generic system fault is present and will not reset latched fault. No faults indicated as part of any zones on warning system or on WIP system. Checked all amplifier cards in directors office and they are operating as normal. Unable to reset latched system fault indicator in auto/manual/isolate modes. Potential power cycle/ hard reset required or further investigations into potentially faulty card.As per Ben Hopper, this will be monitored until the monthly servicing as he cannot have the reset completed today.
MSA-DFES | WA5691637 | 2 | SONTEC WA PTY LTD | COMCEN Egress button under manager’s desk not opening comcen door | Security | Access Control | 310 | Pass | Pass | 0 | 0 | 0.83333 | 2022-08-03 06:31 | 2022-08-05 17:00 | 2022-08-04 11:10 | 2022-08-05 17:00 | 2022-08-04 12:00 |  |  | 4/8/22 - Dylan ParslowFound egress not responding on door controller.Reset and tested, all working correctly.If problem persists recommend replacing door controller.
MSA-DTWD | WA5793682 | 3 | ADVANCED LOCK & KEY | Replace door handle and lock barrel - See notes below | Security | Locksmith | 426.54 | Pass | Pass | -1 | -1 | 0.83333 | 2022-08-24 09:19 | 2022-08-31 17:00 | 2022-08-25 13:00 | 2022-08-31 17:00 | 2022-08-25 13:50 |  |  | installed mortice lock & cyl in place of mortice lock on A275 keyed to 22G
MSA-DCA | WA5797073 | 0 | TK Elevator Australia Pty Ltd | Maritime Museum Victoria Quay-Main Building-Ground Floor-Lift Machine Room- Lift not working | Lifts | Lifts | 1242 | Fail | Fail | 0 | 0 | 0.83333 | 2022-08-27 11:31 | 2022-08-27 13:31 | 2022-08-28 08:30 | 2022-08-27 15:31 | 2022-08-28 09:20 |  |  | Floor button broken. Replaced broken part with new one. Returned to service.
MSA-DTWD | WA5836875 | 3 | Water2water Pty Ltd | Faulty filter - water fountains | Plumbing & Drainage | Water | 381.37 | Pass | Pass | 0 | 0 | 0.83333 | 2022-09-07 15:27 | 2022-09-14 17:00 | 2022-09-12 13:00 | 2022-09-14 17:00 | 2022-09-12 13:50 |  |  | Installed new maxiflow system to original systems and sanitation.
MSA-DCA | WA5853954 | 2 | ADVANCED LOCK & KEY | Dinosaur gate key barrel is stuck - see notes below | Security | Locksmith | 220 | Pass | Pass | 0 | 0 | 0.83333 | 2022-09-12 12:17 | 2022-09-15 17:00 | 2022-09-13 15:40 | 2022-09-15 17:00 | 2022-09-13 16:30 |  |  | could not get lock apartas it seemed like the cam was holding the cover of the keyswitch on. told stage door to get Dorma to replace it since they said they could
MSA-DTWD | WA6020127 | 2 | LIGHTHOUSE LOCKSMITHS | Repair/replace door lock on R Block elect distribution board | Security | Locksmith | 132.8 | Pass | Pass | -1 | -1 | 0.83333 | 2022-10-13 10:57 | 2022-10-18 17:00 | 2022-10-13 15:40 | 2022-10-18 17:00 | 2022-10-13 16:30 |  |  | gained entry to jammed lock on elect distribution board on R block and repaired lock
MSA-DTAG | WA6078654 | 0 | Gilmour & Jooste Electrical | ground custody-Half of custody without power – possible RCD trip (3 phase RCD) | Electrical | General Electrical | 156.01 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-18 12:24 | 2022-10-18 14:24 | 2022-10-18 13:25 | 2022-10-18 16:24 | 2022-10-18 14:15 |  |  | Power tripped due to use of faulty kettle. Removed kettle - all in good working order. Reset RCD.
MSA-DFES | WA6127810 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 1 - Toilet - slowly re filling - Single Cistern | Plumbing & Drainage | Toilets/Cisterns | 172.09 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-26 10:19 | 2022-10-31 17:00 | 2022-10-28 10:25 | 2022-10-31 17:00 | 2022-10-28 11:15 |  |  | Arrived on site and singed in went to Dorm 1 and replaced the inlet valve and flexi hose and removed button and clean them because they were getting stuck tested everything and running fine
MSA-MRWA | WA6128261 | 2 | SONTEC WA PTY LTD | Admin - Faulty front door swipe & Amend gate 2 closure time to 3:30 (instead of 4pm) | Security | Access Control | 310 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-26 14:00 | 2022-10-31 17:00 | 2022-10-31 11:40 | 2022-10-31 17:00 | 2022-10-31 12:30 |  |  | 31/10/22 - Dylan ParslowFound BGU pressed for front door.Reset and tested, all working.Updated timezone as requested
MSA-DTWD | WA6128272 | 2 | LIGHTHOUSE LOCKSMITHS | Faulty door lock on external door to U016 (Eastern side of U Block) | Security | Locksmith | 132.8 | Pass | Pass | -1 | -1 | 0.83333 | 2022-10-26 14:06 | 2022-10-31 17:00 | 2022-10-27 13:00 | 2022-10-31 17:00 | 2022-10-27 13:50 |  |  | serviced and fixed lock on 4016 - key spinning
MSA-DFES | WA6130697 | 2 | SONTEC WA PTY LTD | 1st Floor - Comcen Data Centre -Egress button is not working to exit room | Security | Security Management System | 973.3 | Pass | Pass | 0 | 0 | 0.83333 | 2022-10-28 14:25 | 2022-11-02 17:00 | 2022-10-31 10:00 | 2022-11-02 17:00 | 2022-10-31 10:50 |  |  | 31/10/22 - Dylan ParslowReplaced door controller for Comcen data centre, after repeated issue with egress.Tested all ok.
MSA-DCA | WA6143842 | 0 | GPS Plumbing & Gas Services PtyLtd | Ceiling - possible burst pipe leaking through to the ground | Plumbing & Drainage | Water | 229.69 | Pass | Pass | 0 | 0 | 0.83333 | 2022-11-01 16:01 | 2022-11-01 18:01 | 2022-11-01 18:00 | 2022-11-01 20:01 | 2022-11-01 18:50 |  |  | Inspected leaking pipe. Pipe of the fire service. Denise advised. Bo actions taken. Pipe not leaking whilst on site
MSA-DTAG | WA6291055 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Men's toilet - flushing mechanism is broken | Plumbing & Drainage | Toilets/Cisterns | 185.04 | Pass | Pass | 0 | 0 | 0.83333 | 2022-11-28 11:45 | 2022-12-01 17:00 | 2022-11-29 15:00 | 2022-12-01 17:00 | 2022-11-29 15:50 |  |  | Foreign object/debris stuck on the putlet valve which damaged the outlet washer. Washer replaced. Flushed cistern multiple times. All ok
MSA-DTAG | WA6389337 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Public Toilet near Court Rooms - Women’s Toilets in the public area blocked | Plumbing & Drainage | Toilets/Cisterns | 137.98 | Pass | Pass | 0 | 0 | 0.83333 | 2022-12-21 14:37 | 2022-12-22 17:00 | 2022-12-22 07:25 | 2022-12-22 17:00 | 2022-12-22 08:15 |  |  | Completed
MSA-DCA | WA6393059 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Female Sick Bay, Lower Ground - Leaking pipe under the Sink - See Notes | Plumbing & Drainage | Water | 145.04 | Pass | Pass | -1 | -1 | 0.83333 | 2022-12-28 09:23 | 2023-01-03 17:00 | 2022-12-28 14:15 | 2023-01-03 17:00 | 2022-12-28 15:05
MSA-DTWD | WA6430862 | 2 | ADVANCED LOCK & KEY | Faulty Key see notes | Security | Locksmith | 255 | Pass | Pass | 0 | 0 | 0.83333 | 2023-01-13 09:38 | 2023-01-18 17:00 | 2023-01-18 09:00 | 2023-01-18 17:00 | 2023-01-18 09:50
MSA-DTWD | WA6520004 | 2 | Swan Pest Control | D Block - Ground floor - Ant problem | Pest Control | General Pest | 350 | Pass | Pass | 0 | 0 | 0.83333 | 2023-01-27 09:43 | 2023-02-01 17:00 | 2023-01-31 07:00 | 2023-02-01 17:00 | 2023-01-31 07:50
MSA-DTWD | WA6528585 | 2 | LIGHTHOUSE LOCKSMITHS | All Classrooms - Door locks are sticking and difficult to open with a key | Security | Locksmith | 187.2 | Pass | Pass | -1 | -1 | 0.83333 | 2023-02-02 10:58 | 2023-02-07 17:00 | 2023-02-03 14:40 | 2023-02-07 17:00 | 2023-02-03 15:30
MSA-DTWD | WA6578806 | 2 | Dormakaba Australia Pty Ltd | Stoor door F102 - Manual roller door has come off track | Building | Automatic Doors | 401.95 | Pass | Pass | -1 | -1 | 0.83333 | 2023-02-15 12:10 | 2023-02-20 17:00 | 2023-02-15 14:30 | 2023-02-20 17:00 | 2023-02-15 15:20
MSA-DFES | WA6650936 | 3 | SONTEC WA PTY LTD | CCTV cameras - Timing is out | Security | CCTV Surveillance | 310 | Pass | Pass | -1 | -1 | 0.83333 | 2023-02-20 14:50 | 2023-02-27 17:00 | 2023-02-22 13:00 | 2023-02-27 17:00 | 2023-02-22 13:50
MSA-DCA | WA4991187 | 2 | GPS Plumbing & Gas Services PtyLtd | Level four male staff toilet – second basin tap is loose | Plumbing & Drainage | Water | 139.02 | Pass | Pass | 0 | 0 | 0.81667 | 2022-01-04 16:21 | 2022-01-07 17:00 | 2022-01-06 10:41 | 2022-01-07 17:00 | 2022-01-06 11:30 |  |  | Replaced corroded washer and installed minjstop
MSA-DCA | WA4995683 | 1 | TK Elevator Australia Pty Ltd | Lift 5 - doors faulty on stage level | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.81667 | 2022-01-10 15:07 | 2022-01-11 17:00 | 2022-01-10 16:04 | 2022-01-11 17:00 | 2022-01-10 16:53 |  |  | Door shoe broken, removed debris, amd parts ordered
MSA-DCA | WA5087013 | 0 | Wilson Security | Sunset Hospital Heritage Precinct- alarm has gone off .please check around the site | Security | Monitoring |  | Pass | Pass | 0 | 0 | 0.81667 | 2022-01-22 12:40 | 2022-01-22 14:40 | 2022-01-22 13:05 | 2022-01-22 16:40 | 2022-01-22 13:54 |  |  | EXTERNAL AND INTERNAL PATROL DONE, NO PERSON ONSITE, ALL APPEARS TO BESECURE AND CORRECT NO SITE. DON'T HAVE PANEL CODE ANY MORE FOR SITE I HAVESET THE ALARM FOR ESCORT BLOCK CANT RESET IT. MONITORING ADVISED
MSA-DTWD | WA5107677 | 1 | OTIS ELEVATOR COMPANY PTY LTD | A Block - Ground - Passenger Lift - Bell/call button has fallen off inside of lift | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.81667 | 2022-02-08 08:30 | 2022-02-09 17:00 | 2022-02-08 11:20 | 2022-02-09 17:00 | 2022-02-08 12:09 |  |  | CAR OPERATING PANEL - BUTTONS - COMPONENT DAMAGED
MSA-DCA | WA5692028 | 1 | Dormakaba Australia Pty Ltd | South entry automatic door - External right side door is wobbling | Building | Automatic Doors | 278.57 | Pass | Pass | 0 | 0 | 0.81667 | 2022-08-03 09:47 | 2022-08-04 17:00 | 2022-08-03 11:02 | 2022-08-04 17:00 | 2022-08-03 11:51 |  |  | On inspection, found floor guide broken due to possible vandalism/weather.Replaced broken guide as required and secured other side.Tested unit. All ok.
MSA-DCA | WA5694925 | 3 | GPS Plumbing & Gas Services PtyLtd | Level 3 - Conservation Labs - Insulation needs to be reinstalled on pipe after investigation works | Plumbing & Drainage | Water | 280.68 | Pass | Pass | 0 | 0 | 0.81667 | 2022-08-05 14:55 | 2022-08-12 17:00 | 2022-08-09 14:24 | 2022-08-12 17:00 | 2022-08-09 15:13 |  |  | Install new lagging on copper pipe
MSA-DCA | WA5796900 | 0 | GPS Plumbing & Gas Services PtyLtd | solar panel leaking water | Plumbing & Drainage | Water | 129.89 | Pass | Pass | 0 | 0 | 0.81667 | 2022-08-26 14:33 | 2022-08-26 16:33 | 2022-08-26 15:00 | 2022-08-26 18:33 | 2022-08-26 15:49 |  |  | Solar leaking through old panels from being old looks to of split.isolated hwu via a solar loop in the floor belows bathroom. Will need replacing.site asked for power to be isolated also
MSA-DTWD | WA6088794 | 3 | AHS Services WA Pty Ltd (Anchor) | Female Student toilet 3-53 - Hand Basin Blocked | Plumbing & Drainage | Drainage | 115.4325 | Pass | Pass | -1 | -1 | 0.81667 | 2022-10-19 10:54 | 2022-10-26 17:00 | 2022-10-20 08:26 | 2022-10-26 17:00 | 2022-10-20 09:15 |  |  | Cleaned out trap
MSA-DTAG | WA5190199 | 2 | Water2water Pty Ltd | GCIP Business Area - Kitchenette - Zip tap hot water tap not working | Plumbing & Drainage | Water | 260.18 | Pass | Pass | -1 | -1 | 0.81667 | 2022-02-24 11:52 | 2022-03-01 17:00 | 2022-02-25 13:14 | 2022-03-01 17:00 | 2022-02-25 14:03 |  |  | Replaced faulty hot pump.
MSA-DCA | WA5697438 | 3 | GPS Plumbing & Gas Services PtyLtd | Ladies' 2nd toilet from the left stalls level, ½ flush button on the left not working. | Plumbing & Drainage | Toilets/Cisterns | 119.4775 | Pass | Pass | 0 | 0 | 0.81667 | 2022-08-09 09:29 | 2022-08-16 17:00 | 2022-08-15 10:45 | 2022-08-16 17:00 | 2022-08-15 11:34 |  |  | Fixed ladies toilet that wasn't flushing well
MSA-DCA | WA6051119 | 1 | TK Elevator Australia Pty Ltd | Public lift - when staff are using the lift the announcement advises | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.81667 | 2022-10-17 15:50 | 2022-10-18 17:00 | 2022-10-18 07:38 | 2022-10-18 17:00 | 2022-10-18 08:27 |  |  | No voltage from gsm. Installed new sim card. Tested operation 48volts from gsm. Tested emergency phone answered by tim from callcentre
MSA-MRWA | WA6394140 | 2 | Dormakaba Australia Pty Ltd | Hardstand Area Centre of Site - gate not opening probable limit switch failure | Building | Steel Fencing & Gates | 228.58 | Pass | Pass | -1 | -1 | 0.81667 | 2022-12-30 08:14 | 2023-01-05 17:00 | 2022-12-30 11:03 | 2023-01-05 17:00 | 2022-12-30 11:52
MSA-DFES | WA5301950 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | G Floor - Visitors Toilet - Toilet filling pipe is faulty cistern overrunning | Plumbing & Drainage | Toilets/Cisterns | 176 | Pass | Pass | 0 | 0 | 0.8 | 2022-04-01 15:18 | 2022-04-06 17:00 | 2022-04-06 07:42 | 2022-04-06 17:00 | 2022-04-06 08:30 |  |  | Serviced toilet cistern
MSA-DCA | WA5396115 | 3 | GPS Plumbing & Gas Services PtyLtd | Alexander Library Building - Level 1 - Staff Mens Toilet - Urinal Blocked - cleaner cannot unblock | Plumbing & Drainage | Toilets/Cisterns | 213.78 | Pass | Pass | -1 | -1 | 0.8 | 2022-05-06 08:29 | 2022-05-13 17:00 | 2022-05-09 10:17 | 2022-05-13 17:00 | 2022-05-09 11:05 |  |  | Unblocked uribal on level 1 staff
MSA-DCA | WA5473326 | 1 | GPS Plumbing & Gas Services PtyLtd | G block - Male toilet - Blocked toilet in male toilets. Cleaners unable to rectify. | Plumbing & Drainage | Water | 134.78 | Pass | Pass | 0 | 0 | 0.8 | 2022-05-24 13:54 | 2022-05-25 17:00 | 2022-05-25 08:00 | 2022-05-25 17:00 | 2022-05-25 08:48 |  |  | Umblocked toilet in g block male public
MSA-DTWD | WA5548913 | 3 | Dormakaba Australia Pty Ltd | Auto door keeps freezing requiring reset | Building | Automatic Doors | 180 | Pass | Pass | -1 | -1 | 0.8 | 2022-06-17 10:51 | 2022-06-24 17:00 | 2022-06-20 11:38 | 2022-06-24 17:00 | 2022-06-20 12:26 |  |  | Found that the doors were operating correctly on arrival, after thorough inspection i have found that the inverter has failed, the controller is in very poor condition, this unit is 20 years old and is about to fail permanently, my recommendation would be to upgrade the unit to an es200 non lock platform with ixio sensor and mode switch for reliable operation, poor access to unit, a piece of angle will need to be removed to open pelmet properly.
MSA-DTWD | WA5565469 | 1 | CONNECT SECURITY SYSTEMS | Alarm panel for block 10 sounding alarm continuously | Security | Security Management System | 234.49 | Pass | Pass | 0 | 0 | 0.8 | 2022-06-22 08:12 | 2022-06-23 17:00 | 2022-06-22 11:29 | 2022-06-23 17:00 | 2022-06-22 12:17 |  |  | Replaced tamper switch
MSA-DCA | WA5571625 | 2 | Techworks Electrical | Ground level - HBRC building - HBRC outside - Security lights outside HBRC not working - see notes | Electrical | Lighting, External | 125.59 | Pass | Pass | 0 | 0 | 0.8 | 2022-06-29 10:44 | 2022-07-04 17:00 | 2022-07-01 06:30 | 2022-07-04 17:00 | 2022-07-01 07:18 |  |  | Investigated lights out. Circuit was tripped. Turned back on and no longer tripping. Asked sue to report if tripping returns
MSA-DCA | WA6364072 | 2 | GPS Plumbing & Gas Services PtyLtd | Ladies cubicle 1 - Continual running water even with the tap off. | Plumbing & Drainage | Toilets/Cisterns | 118.64 | Pass | Pass | 0 | 0 | 0.8 | 2022-12-12 09:23 | 2022-12-15 17:00 | 2022-12-12 13:40 | 2022-12-15 17:00 | 2022-12-12 14:28 |  |  | Outlet valve washer replaced, old washer fell off.
MSA-DCA | WA5312444 | 1 | GPS Plumbing & Gas Services PtyLtd | Robert Steele Steam Machinery Exhibition - External Workshop -see details below | Plumbing & Drainage | Sewer Drains & Septic Systems | 134.78 | Pass | Pass | 0 | 0 | 0.8 | 2022-04-11 14:05 | 2022-04-12 17:00 | 2022-04-12 08:03 | 2022-04-12 17:00 | 2022-04-12 08:51 |  |  | Investigate sewer smell, no sewer around.Checked the storm drain no smell present at the time.Storm drain not holding any water.No issues found.
MSA-MRWA | WA5588057 | 3 | GPS Plumbing & Gas Services PtyLtd | outside court yard-Blocked drain in lunch area | Plumbing & Drainage | Drainage | 113.43 | Pass | Pass | 0 | 0 | 0.8 | 2022-07-07 12:44 | 2022-07-14 17:00 | 2022-07-11 14:22 | 2022-07-14 17:00 | 2022-07-11 15:10 |  |  | Unblocked drain outside lunch area
MSA-DCA | WA6249844 | 1 | Dormakaba Australia Pty Ltd | Roller Door 7 - is faulty and going up | Building | Automatic Doors | 345 | Pass | Pass | 0 | 0 | 0.8 | 2022-11-21 15:38 | 2022-11-22 17:00 | 2022-11-22 08:03 | 2022-11-22 17:00 | 2022-11-22 08:51 |  |  | Door has lost power, onsite electrician confirmed it is a security issue, customer is organising repair.
MSA-MRWA | WA4990881 | 1 | GPS Plumbing & Gas Services PtyLtd | Right hand urinal is blocked | Plumbing & Drainage | Toilets/Cisterns | 105.41 | Pass | Pass | 0 | 0 | 0.8 | 2022-01-04 12:43 | 2022-01-05 17:00 | 2022-01-05 14:42 | 2022-01-05 17:00 | 2022-01-05 15:30 |  |  | Unblocked rhs 2nd floor north east urinal,
MSA-DTWD | WA5687362 | 1 | SCAVENGER SUPPLIES PTY LTD | Block B10- Staff Kitchen EWS system has a fault | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 551.51 | Pass | Pass | 0 | 0 | 0.8 | 2022-08-01 17:24 | 2022-08-02 17:00 | 2022-08-02 09:00 | 2022-08-02 17:00 | 2022-08-02 09:48 |  |  | Building is experiencing power issues, due to this the FIP & EWIS system have transferred to battery power causing faults to appear but is not urgent or a risk?MATERIALS-BATTERIES 2 X 12V 40Ah to be ordered
MSA-DCA | WA6007869 | 0 | GPS Plumbing & Gas Services PtyLtd | Blocked Drain | Plumbing & Drainage | Drainage | 153.5975 | Pass | Pass | 0 | 0 | 0.8 | 2022-10-11 10:55 | 2022-10-11 12:55 | 2022-10-11 11:44 | 2022-10-11 14:55 | 2022-10-11 12:32 |  |  | Cleared blocked drain to the sink
MSA-DTWD | WA6292913 | 2 | AWB Co. | 2 x faulty Flouro's out H Block H307 | Electrical | Lighting, Internal | 104.245 | Pass | Pass | 0 | 0 | 0.8 | 2022-11-29 14:22 | 2022-12-02 17:00 | 2022-12-02 15:45 | 2022-12-02 17:00 | 2022-12-02 16:33 |  |  | Attended site and signed in. Completed JSA. Liased with site about works. Replaced various tubes out as directed by site. Parts supplied by site. **job Complete**
MSA-DCA | WA5392061 | 3 | GPS Plumbing & Gas Services PtyLtd | Ground -Toilet Disabled North Foyer - Minimal amount of water constantly running from tap | Plumbing & Drainage | Water | 134.78 | Pass | Pass | -1 | -1 | 0.78333 | 2022-05-03 07:21 | 2022-05-09 17:00 | 2022-05-04 14:00 | 2022-05-09 17:00 | 2022-05-04 14:47 |  |  | Rethread seal leak tap
MSA-DCA | WA5566308 | 1 | GPS Plumbing & Gas Services PtyLtd | Staff toilet Male - Hand Basin Tap Loose & tap leaking | Plumbing & Drainage | Drainage | 182.29 | Pass | Pass | 0 | 0 | 0.78333 | 2022-06-23 07:07 | 2022-06-23 17:00 | 2022-06-23 11:10 | 2022-06-23 17:00 | 2022-06-23 11:57 |  |  | Reseated leaking basin tap to male ground floor staff male toilet
MSA-DCA | WA5569489 | 2 | GPS Plumbing & Gas Services PtyLtd | Levels 1 & 2 - Corridors - Concerns over water taste in water units - filter change? | Plumbing & Drainage | Water | 160.2625 | Pass | Pass | 0 | 0 | 0.78333 | 2022-06-27 15:04 | 2022-06-30 17:00 | 2022-06-28 13:00 | 2022-06-30 17:00 | 2022-06-28 13:47 |  |  | Have advised that water 2 water, has to do the 6 months replacing water filter
MSA-DFES | WA5680036 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor – Change room - Blocked Toilet in male change room | Plumbing & Drainage | Toilets/Cisterns | 129.26 | Pass | Pass | -1 | -1 | 0.78333 | 2022-07-27 09:15 | 2022-08-01 17:00 | 2022-07-27 10:15 | 2022-08-01 17:00 | 2022-07-27 11:02 |  |  | Unblocked the toilet.
MSA-DTWD | WA5686972 | 3 | Water2water Pty Ltd | B Block - Main Entrance - Cold water drinking unit not working | Plumbing & Drainage | Water | 186.37 | Pass | Pass | -1 | -1 | 0.78333 | 2022-08-01 12:24 | 2022-08-08 17:00 | 2022-08-03 11:43 | 2022-08-08 17:00 | 2022-08-03 12:30 |  |  | Re plumbed fountain and tested
MSA-MRWA | WA5837944 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 2 - South Male Bathrooms - Blocked Urinal | Plumbing & Drainage | Drainage | 113.43 | Pass | Pass | 0 | 0 | 0.78333 | 2022-09-08 09:42 | 2022-09-09 17:00 | 2022-09-08 12:00 | 2022-09-09 17:00 | 2022-09-08 12:47 |  |  | Unblocked urinal
MSA-DCA | WA5838523 | 3 | GPS Plumbing & Gas Services PtyLtd | Second floor public male toilet - 2nd cubicle - water leaking to pan | Plumbing & Drainage | Toilets/Cisterns | 72.98 | Pass | Pass | 0 | 0 | 0.78333 | 2022-09-08 13:50 | 2022-09-15 17:00 | 2022-09-13 10:00 | 2022-09-15 17:00 | 2022-09-13 10:47 |  |  | Replaced outlet washer
MSA-MRWA | WA6015010 | 3 | GPS Plumbing & Gas Services PtyLtd | Female toilet-Cistern not filling, possible failed float valve - photo's to be emailed | Plumbing & Drainage | Toilets/Cisterns | 290.54 | Pass | Pass | -1 | -1 | 0.78333 | 2022-10-12 13:40 | 2022-10-19 17:00 | 2022-10-13 12:00 | 2022-10-19 17:00 | 2022-10-13 12:47 |  |  | Replaced faulty outlet and inlet valve
MSA-MRWA | WA6044119 | 1 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Men's Toilet - Southern End of Building - Toilet has no water pressure | Plumbing & Drainage | Toilets/Cisterns | 113.43 | Pass | Pass | 0 | 0 | 0.78333 | 2022-10-17 10:12 | 2022-10-18 17:00 | 2022-10-17 11:03 | 2022-10-18 17:00 | 2022-10-17 11:50 |  |  | Inspected south male toilets good pressure no issues found with the flush. Buttons faulty
MSA-DTAG | WA6166445 | 2 | Schindler Lifts Australia | Ground Floor - Lift 10 -Lift out of order - See notes below | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.78333 | 2022-11-11 15:22 | 2022-11-16 17:00 | 2022-11-11 18:25 | 2022-11-16 17:00 | 2022-11-11 19:12 |  |  | Works completed - close out at $0
MSA-DCA | WA6381916 | 1 | TK Elevator Australia Pty Ltd | Lift 1 - Ground floor - display is faulty | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.78333 | 2022-12-19 16:21 | 2022-12-20 17:00 | 2022-12-20 09:04 | 2022-12-20 17:00 | 2022-12-20 09:51 |  |  | Lift running on arrival. Error 0c81 afocAll lift displays on landing and in car not displaying correctly. Tried reseting ct24 board and afoc lift displays still faulty. Power down lift and checked display all okay. Took details of board in case it happens again.Tested lift multiple times all okay. Returned unit to service.
MSA-DTAG | WA6578148 | 2 | GPS Plumbing & Gas Services PtyLtd | 1987 - Sheriff’s Office - Ladies Toilet - Middle sink in ladies restroom not draining properly | Plumbing & Drainage | Toilets/Cisterns | 52.98 | Pass | Pass | 0 | 0 | 0.78333 | 2023-02-15 07:36 | 2023-02-17 17:00 | 2023-02-15 09:54 | 2023-02-17 17:00 | 2023-02-15 10:41
MSA-DCA | WA5496588 | 2 | Precise Air Group | Nank’s office - Bearing on fan has given up and is very noisy | Air Conditioning | Room Air Conditioners | 235.48 | Pass | Pass | -1 | -1 | 0.78333 | 2022-06-09 11:28 | 2022-06-14 17:00 | 2022-06-10 13:44 | 2022-06-14 17:00 | 2022-06-10 14:31 |  |  | Found fan motor vibrating causing a slight noise in office due to screw missing, secured fan motor, vibration has gone
MSA-DTAG | WA5238874 | 1 | Water2water Pty Ltd | PUBLIC CORRIDOR - Public Water Fountain - dispensed water is cloudy | Plumbing & Drainage | Water | 161.54 | Pass | Pass | 0 | 0 | 0.78333 | 2022-03-16 09:42 | 2022-03-17 17:00 | 2022-03-17 08:05 | 2022-03-17 17:00 | 2022-03-17 08:52 |  |  | Adjusted bubbler and flushed water through the system. All okay on departure.
MSA-DCA | WA6560383 | 2 | Dormakaba Australia Pty Ltd | Cable Gate is not operating - Stage door - showing fault | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.78333 | 2023-02-13 09:46 | 2023-02-16 17:00 | 2023-02-13 15:08 | 2023-02-16 17:00 | 2023-02-13 15:55
MSA-DTWD | WA5979990 | 1 | Dormakaba Australia Pty Ltd | Ground Floor - Entry - Secure gate motor not working- please see notes | Building | Automatic Doors | 351.95 | Pass | Pass | 0 | 0 | 0.76667 | 2022-09-29 11:35 | 2022-09-30 17:00 | 2022-09-29 14:20 | 2022-09-30 17:00 | 2022-09-29 15:06 |  |  | Gate was found manually released in the open position. Checked over automation and controller, tested operation and all ok. The DEA gate controller has the option for battery backup but this is not fitted. Instead a very large Ups is installed in an enclosure above. This ups appears to be in full working order. At time of test, the gate is working as expected.
MSA-DTWD | WA6298621 | 2 | Dormakaba Australia Pty Ltd | Workshop - W Block - Chain that lifts/operates the roller door into the workshop has come off | Building | Automatic Doors | 186.95 | Pass | Pass | -1 | -1 | 0.76667 | 2022-12-01 11:32 | 2022-12-06 17:00 | 2022-12-01 15:07 | 2022-12-06 17:00 | 2022-12-01 15:53 |  |  | Chain had fallen off drive sprocket. Removed chain and replaced one link with a half link to shorten chain. Motor has no adjustment due to a welded cross brace. All OK.
MSA-DCA | WA5001431 | 1 | Earth & Water Pty Ltd | city room - outside main entry - retic issue, multiple | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 0.76667 | 2022-01-11 12:13 | 2022-01-12 17:00 | 2022-01-11 12:14 | 2022-01-12 17:00 | 2022-01-11 13:00 |  |  | Job completed - fixed broken irrigation and leaksstart 16/12/21 10:00:00 - completed - 16/12/21 13:00:00
MSA-DFES | WA5230718 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | No power loss - running on generators | Electrical | Distribution Board | 100.095 | Pass | Pass | 0 | 0 | 0.76667 | 2022-03-15 07:02 | 2022-03-15 09:02 | 2022-03-15 09:01 | 2022-03-15 11:02 | 2022-03-15 09:47 |  |  | Aos 901 investigate UPS faults. Determined cause of power outage to be over/under frequency fault. Power was on ups from 656 to 733. Informed Tania and dfes staff of issue. Signed out 947
MSA-DCA | WA5797091 | 0 | TK Elevator Australia Pty Ltd | Main Building - 2x people stuck in the lift between Level 1 and Ground Floor. | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.76667 | 2022-08-27 16:37 | 2022-08-27 18:37 | 2022-08-27 17:25 | 2022-08-27 20:37 | 2022-08-27 18:11 |  |  | Lift 1 Art (large)-Elevator > MR > Geared :Upon arrival the swp was out and security had turned the lift off so when i turned the lift back to normal operation it ran correctly and i could not fault the lift running, however the door open time is very short though the curtain of light is working correctly. The lift was running correctly on departure.
MSA-DTWD | WA6298981 | 2 | Precise Air Group | Air conditioner blowing hot air only | Air Conditioning | Room Air Conditioners | 253.38 | Pass | Pass | 0 | 0 | 0.76667 | 2022-12-01 16:09 | 2022-12-06 17:00 | 2022-12-05 11:00 | 2022-12-06 17:00 | 2022-12-05 11:46 |  |  | Checked operation of system found unit is at end of life ,is R22 system compressor very corroded and gas has leaked out of stem valves and other places very little refrigerant in system unit needs to be scrapped 35 years old and very bad condition. Advised to close job as BRAF to be raised as quoted job.
MSA-DTWD | WA6669211 | 2 | Dormakaba Australia Pty Ltd | Foyer - Auto door - Faulty sensor | Building | Automatic Doors | 180 | Pass | Pass | -1 | -1 | 0.76667 | 2023-02-22 15:24 | 2023-02-27 17:00 | 2023-02-23 14:58 | 2023-02-27 17:00 | 2023-02-23 15:44
MSA-DCA | WA5253411 | 1 | Wilson Security | RETROSPECTIVE WORK ORDER - DO NOT ATTEND - see notes below | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.76667 | 2022-01-08 15:15 | 2022-01-10 17:00 | 2022-01-09 01:16 | 2022-01-10 17:00 | 2022-01-09 02:02 | 1 |  | job completed - EXTERNAL AND INTERNAL ALL APPEAR TO BE SECURE AND CORRECT ON SITE NO SIGNOF FORCED ENTRY OR DAMAGE FOUND, REST Q BLOCK PANEL AS IT WAS IN ALARM ONARRIVAL, CLEARED BY MONITORING PHIL
MSA-DTWD | WA5522270 | 3 | Water2water Pty Ltd | Fault description Zippy hot/cold water system registering a fault and works intermittently | Plumbing & Drainage | HWS/Units Electric & Gas | 139.7325 | Pass | Pass | 0 | 0 | 0.76667 | 2022-06-15 13:56 | 2022-06-22 17:00 | 2022-06-20 09:00 | 2022-06-22 17:00 | 2022-06-20 09:46 |  |  | Disconnected stirrer pump
MSA-DTWD | WA6143738 | 3 | Water2water Pty Ltd | A16 kitchen inside A19 - Drip from bottom of water boiler/urn | Plumbing & Drainage | Water | 173.82 | Pass | Pass | 0 | 0 | 0.76667 | 2022-11-01 14:11 | 2022-11-08 17:00 | 2022-11-07 10:30 | 2022-11-08 17:00 | 2022-11-07 11:16 |  |  | Tighten connections
MSA-DTAG | WA6528595 | 1 | AHS Services WA Pty Ltd (Anchor) | Urinal is blocked in male public toilet – Hay Street side of floor | Plumbing & Drainage | Toilets/Cisterns | 112.6425 | Pass | Pass | 0 | 0 | 0.76667 | 2023-02-02 11:09 | 2023-02-03 17:00 | 2023-02-02 12:44 | 2023-02-03 17:00 | 2023-02-02 13:30
MSA-DTWD | WA6407814 | 2 | AHS Services WA Pty Ltd (Anchor) | Hot water not working in B107 | Plumbing & Drainage | Water | 140.77 | Pass | Pass | 0 | 0 | 0.76667 | 2023-01-10 11:55 | 2023-01-13 17:00 | 2023-01-11 11:30 | 2023-01-13 17:00 | 2023-01-11 12:16
MSA-DTAG | WA6573497 | 1 | GPS Plumbing & Gas Services PtyLtd | Buss P chambers - Tap not working properly | Plumbing & Drainage | Drainage | 95.77 | Pass | Pass | 0 | 0 | 0.76667 | 2023-02-14 13:49 | 2023-02-15 17:00 | 2023-02-15 09:08 | 2023-02-15 17:00 | 2023-02-15 09:54
MSA-DCA | WA4990129 | 0 | EQUANS Mechanical Services (WA) Pty Limited | No BMS notification, | Building | Materials | 109.8875 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-03 12:55 | 2022-01-03 14:55 | 2022-01-03 14:15 | 2022-01-03 16:55 | 2022-01-03 15:00 |  |  | Attended site with Schneider and sent a test alarm output to security. Security recieved the alarm notification. Team viewer and the internet connection also checked.
MSA-DFES | WA4993639 | 3 | Go Doors | Staff car park gate next to the main entrance – does not open intermittently. | Building | Steel Fencing & Gates | 540 | Pass | Pass | -1 | -1 | 0.75 | 2022-01-08 15:19 | 2022-01-14 17:00 | 2022-01-10 12:00 | 2022-01-14 17:00 | 2022-01-10 12:45 |  |  | Completed works.
MSA-DFES | WA4995411 | 1 | Protek 24/7 Building & Maintenance | North west corner of fence line - fence has had a hole cut into it | Building | General Building | 116.875 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-10 12:43 | 2022-01-11 17:00 | 2022-01-10 13:30 | 2022-01-11 17:00 | 2022-01-10 14:15 |  |  | Repair lacing on chain mesh fence
MSA-DFES | WA5001130 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 2 - Workshop Bay 2 -GPO not working – was in service went to use today and now unserviceable | Electrical | General Electrical | 153.705 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-11 09:01 | 2022-01-14 17:00 | 2022-01-11 14:15 | 2022-01-14 17:00 | 2022-01-11 15:00 |  |  | Arrived on site at 1415, located 15A gpo without power. Found rcd to be tripped. Reset rcd and tested circuit,all working ok. Left site at 1500
MSA-DTAG | WA5009996 | 1 | Bullant Security Pty Ltd | Lower Level - Custody Hallway Door Lock jamming | Security | Locksmith | 318.64 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-12 09:07 | 2022-01-13 17:00 | 2022-01-12 11:10 | 2022-01-13 17:00 | 2022-01-12 11:55 |  |  | Attended site, replaced faulty mortice lock to custody hallway door for correct operation.Lockwood 3572 mortice lock installed. Date on site: 12/01/2022 Time on site: 11:10am - 11:55am
MSA-DTWD | WA5010171 | 1 | Swan Pest Control | E-Block rodents / rats sighted around the building | Pest Control | General Pest | 311 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-12 10:50 | 2022-01-13 17:00 | 2022-01-13 07:00 | 2022-01-13 17:00 | 2022-01-13 07:45 |  |  | Installed 12 large cardboard rodent stations and 24 Ditrac rodent blocks
MSA-DTWD | WA5017253 | 3 | AWB Co. | B208 - light in ladies toilet require replacing | Electrical | Lighting, Internal | 165.765 | Pass | Pass | -1 | -1 | 0.75 | 2022-01-13 12:05 | 2022-01-20 17:00 | 2022-01-13 14:00 | 2022-01-20 17:00 | 2022-01-13 14:45 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works. Located room B208. Found to be faulty lamp. Supplied and replaced 18w 2PIN PLC. Tested for correct operation. Notified of works completed. **job completed**
MSA-DTWD | WA5018232 | 2 | SENTINEL LOCK SERVICE PTY LTD | C18 storeroom - Faulty keys aren’t working in lock | Security | Locksmith | 205.85 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-14 09:50 | 2022-01-19 17:00 | 2022-01-18 09:20 | 2022-01-19 17:00 | 2022-01-18 10:05 |  |  | C18 - Storeroom - faulty keys and lock.Lock repaired and worn keys replaced.
MSA-DFES | WA5037940 | 2 | Protek 24/7 Building & Maintenance | Tunic Room Sliding Door - loose fixture causing issues with the door | Building | Doors | 109.175 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-17 08:51 | 2022-01-20 17:00 | 2022-01-18 08:15 | 2022-01-20 17:00 | 2022-01-18 09:00 |  |  | Refitted trim to existing position
MSA-DTWD | WA5069007 | 2 | PEEL LOCK SERVICES PTY LTD | Admin door keypad turning but door want unlock | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-01-19 13:40 | 2022-01-24 17:00 | 2022-01-21 10:45 | 2022-01-24 17:00 | 2022-01-21 11:30 |  |  | Repaired admni key pads and keys for front door faulty
MSA-DTWD | WA5069193 | 3 | AWB Co. | Light out not working | Electrical | Lighting, External | 160.44 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-19 16:35 | 2022-01-27 17:00 | 2022-01-27 10:30 | 2022-01-27 17:00 | 2022-01-27 11:15 |  |  | Attended site, signed in, completed jsa,spoke with fm , located lighting out in B57 , removed old tubes and starters, replace with new, tested lights and working as intended, put old tubes in disposal box lcated in h block , packed up , cleaned up , completed paperwork , signed out , **job completed **
MSA-DTWD | WA5080383 | 2 | AWB Co. | Power point is broken and hanging on the wall | Electrical | General Electrical | 152.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-20 07:27 | 2022-01-24 17:00 | 2022-01-24 08:00 | 2022-01-24 17:00 | 2022-01-24 08:45 |  |  | Replaced 2x broken gops in toilets T block
MSA-DTWD | WA5081082 | 3 | Securex Security Systems & Services | PIR sensor fault - zone will not arm | Security | Monitoring | 307.27 | Pass | Pass | -1 | -1 | 0.75 | 2022-01-20 10:50 | 2022-01-28 17:00 | 2022-01-21 10:30 | 2022-01-28 17:00 | 2022-01-21 11:15 |  |  | 21/1/2022Replaced PIR and tested
MSA-DTWD | WA5085662 | 3 | ADVANCED LOCK & KEY | Replace worn TE1 Barrel to Library A104 small room | Security | Locksmith | 202.5 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-21 09:50 | 2022-01-31 17:00 | 2022-01-31 11:20 | 2022-01-31 17:00 | 2022-01-31 12:05 |  |  | Replace cylinder Components
MSA-DTWD | WA5087965 | 3 | AWB Co. | Faulty plug on power operated disability desk | Electrical | General Electrical | 120.56 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-24 15:47 | 2022-02-01 17:00 | 2022-01-31 10:30 | 2022-02-01 17:00 | 2022-01-31 11:15 |  |  | Attended site and signed in. Completed JSA. Located faulty desk power plug. Found to be non compliant with tafe standards. Supply and replace with new plug. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5090099 | 3 | Equans Mechanical Services Australia | Block 9 - Ground floor - Library computer room - Failed wall controller center unit | Air Conditioning | Room Air Conditioners | 349.8 | Fail | Fail | 2 | 2 | 0.75 | 2022-01-25 09:36 | 2022-02-02 17:00 | 2022-02-14 15:00 | 2022-02-02 17:00 | 2022-02-14 15:45 |  | WACCES | ORDERED AND PICKED UP NEW MITSUBISHI WALL CONTROLLER. TRAVELLED TO SITE. GAINED ACCESS TO SITE. REMOVED OLD CONTROLLER. FITTED NEW BACKING PLATE TO WALL. WIRED IN NEW CONTROLLER AND STARTED UNIT. CHECKED OPERATION AND ALL OK. CLEANED UP WORK AREA AND DISPOSED OF RUBBISH. COMPLETED PAPERWORK AND LOGGED OFF JOB.
MSA-DFES | WA5090540 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Server Room - Globe in the server room has blown | Electrical | General Electrical | 122.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-25 13:12 | 2022-02-02 17:00 | 2022-02-01 10:00 | 2022-02-02 17:00 | 2022-02-01 10:45 |  |  | Arrived on site and was looking for the faulty light. The light was difficult to find as there was no one on site. I called the site contact and he advised the faulty light is in a room with a code door lock. He gave me the code and I was able to find the light. Replaced faulty globe with new.
MSA-DTAG | WA5092087 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Custody - Cell 2 - bio-clean – prisoner defecating | Cleaning | Hazardous Materials | 300 | Fail | Fail | 0 | 0 | 0.75 | 2022-01-27 13:58 | 2022-01-27 15:58 | 2022-01-27 19:30 | 2022-01-27 17:58 | 2022-01-27 20:15 |  |  | Job completed as per WO
MSA-DTAG | WA5092205 | 0 | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | Courtroom 1 - Dock Area - prisoner has spat | Cleaning | Hazardous Materials | 300 | Fail | Pass | 0 | 0 | 0.75 | 2022-01-27 16:26 | 2022-01-27 18:26 | 2022-01-27 18:30 | 2022-01-27 20:26 | 2022-01-27 19:15 |  |  | Job completed as per PO
MSA-DTAG | WA5094908 | 3 | Midolo Building Services | Level 6 - Public female toilet - Soap dispenser not able to be opened up to change soap supply | Building | General Building | 97.42 | Pass | Pass | -1 | -1 | 0.75 | 2022-01-31 15:30 | 2022-02-07 17:00 | 2022-02-03 13:45 | 2022-02-07 17:00 | 2022-02-03 14:30 |  |  | repairs made to soap dispenser
MSA-DCA | WA5094917 | 1 | Critical Fire Protection & Training | Mezzanine Level - Dressing Room 7 - | Fire Protection Services | Fire Protection - Monitor System | 122.905 | Pass | Pass | 0 | 0 | 0.75 | 2022-01-31 15:47 | 2022-02-01 17:00 | 2022-01-31 16:35 | 2022-02-01 17:00 | 2022-01-31 17:20 |  |  | Attended site however Rebecca Dilly advised the tech that the water was through an emergency light which is at reception now.They do not want zone 10 deisolating until after the performance and will deisolate it themselves.
MSA-DTWD | WA5099059 | 3 | AWB Co. | Bay 28 - mig welders damaged power leads | Electrical | General Electrical | 227.91 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-01 13:52 | 2022-02-08 17:00 | 2022-02-08 09:30 | 2022-02-08 17:00 | 2022-02-08 10:15 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty leads and plug top. Took off plug top and slid heat shrink down to affected area. Used heat gun to fit heat shrink. Disconnected plug top from cabling and replaced with new one. Test and tagged lead. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5099062 | 3 | AWB Co. | Bay 30 - mig welders damaged power leads | Electrical | General Electrical | 157.47 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-01 13:54 | 2022-02-08 17:00 | 2022-02-08 10:15 | 2022-02-08 17:00 | 2022-02-08 11:00 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty lead. Took off plug top and slid heat shrink down to affected area. Used heat gun to fit heat shrink. Test and tagged lead. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DTWD | WA5099063 | 3 | AWB Co. | Bay 32 - mig welders damaged power leads | Electrical | General Electrical | 157.47 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-01 13:56 | 2022-02-08 17:00 | 2022-02-08 11:00 | 2022-02-08 17:00 | 2022-02-08 11:45 |  |  | Attended site and signed in. Completed JSA. spoke to fm. Read fault tag on cord and found that it was missing a lock ring. Used lock ring out of technicians spares to fix this one. Plug top is now all good. Took pictures. Completed paperwork. Signed out. *** Job complete ***
MSA-DFES | WA5099824 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Room 8 Toilet - ight switch defective | Electrical | Lighting, Internal | 121.985 | Fail | Fail | 1 | 1 | 0.75 | 2022-02-02 09:02 | 2022-02-07 17:00 | 2022-02-14 10:30 | 2022-02-07 17:00 | 2022-02-14 11:15 |  | WCAPPR | Already on site from last job continued on at 10:30. Located faulty light switch in room 8 toilet. Left site at 10:40 to collect switch mechs from wholesaler arrived back at 10:50. Replaced cracked cover plate and installed 2 new switch mechs. Left site at 11:152 x 10a Clipsal switch mechs 1 x 2 Gang switch plate
MSA-DTWD | WA5099881 | 2 | LIGHTHOUSE LOCKSMITHS | K Block - tiny totts room - faulty push button keypad lock | Security | Locksmith | 390 | Pass | Pass | -1 | -1 | 0.75 | 2022-02-02 09:23 | 2022-02-07 17:00 | 2022-02-03 10:35 | 2022-02-07 17:00 | 2022-02-03 11:20 |  |  | replaced broken code pad lock on k block tiny totts room
MSA-DTWD | WA5100436 | 2 | LIGHTHOUSE LOCKSMITHS | External - New F shed. Replace damaged external door lock | Security | Locksmith | 210 | Pass | Pass | -1 | -1 | 0.75 | 2022-02-02 13:37 | 2022-02-07 17:00 | 2022-02-03 09:30 | 2022-02-07 17:00 | 2022-02-03 10:15 |  |  | replaced damaged oval cylinder on f shed rear door
MSA-DTWD | WA5101028 | 2 | AWB Co. | TIG welding room - Power point (3 phase) in bay 4 on R/H side has no power | Electrical | General Electrical | 159.765 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-03 09:06 | 2022-02-08 17:00 | 2022-02-08 14:45 | 2022-02-08 17:00 | 2022-02-08 15:30 |  |  | Attended site and signed in. Completed JSA. Located faulty tig welder outlet. Tested to find no white phase to outlet. Used sites spare fuses in stock to replace fuse. Tested all okay at outlet. Welder not there to fire up and run. Signed out. Job complete
MSA-DFES | WA5105303 | 1 | Go Doors | Rear Door 6 - roller door sensor is not working | Building | Roller Shutters | 310 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-04 09:26 | 2022-02-07 17:00 | 2022-02-04 11:00 | 2022-02-07 17:00 | 2022-02-04 11:45 |  |  | Completed works. See attachments.
MSA-DTWD | WA5105555 | 3 | AWB Co. | Drill Press power lead damaged | Electrical | General Electrical | 155.94 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-04 12:04 | 2022-02-11 17:00 | 2022-02-11 13:45 | 2022-02-11 17:00 | 2022-02-11 14:30 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located drill press and put a new tag on. Put out of service tag on. Took pictures. Completed paperwork signed out Job complete
MSA-DCA | WA5105723 | 1 | Critical Fire Protection & Training | Level 1 - Foyer - Fire Indication Panel - see details below | Fire Protection Services | Fire Protection - Monitor System | 122.905 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-04 13:21 | 2022-02-07 17:00 | 2022-02-04 14:15 | 2022-02-07 17:00 | 2022-02-04 15:00 |  |  | Start time: 2:15pmFinish time: 3pmNo fault on code red or fip on arrival. Checked address shows only isolate. Suspected isolate reminder buzzer. Spoke with fams regards faults whenever fip is isolated faults appear. No action required.
MSA-DFES | WA5105756 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Male Toilets Upstairs - blocked urinal | Plumbing & Drainage | Toilets/Cisterns | 165.64 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-04 13:44 | 2022-02-07 17:00 | 2022-02-04 15:30 | 2022-02-07 17:00 | 2022-02-04 16:15 |  |  | Unblocked the urinals
MSA-DTWD | WA5105816 | 2 | PEEL LOCK SERVICES PTY LTD | Main corridor electrical switchboard cupboard - switch board door lock broken | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-02-04 14:24 | 2022-02-09 17:00 | 2022-02-07 13:15 | 2022-02-09 17:00 | 2022-02-07 14:00 |  |  | job completed - replaced repaired lock
MSA-DTAG | WA5108016 | 3 | Midolo Building Services | Rockingham Court - Family Violence Office - see details | Building | General Building | 92.5 | Pass | Pass | -1 | -1 | 0.75 | 2022-02-08 10:57 | 2022-02-15 17:00 | 2022-02-11 13:15 | 2022-02-15 17:00 | 2022-02-11 14:00 |  | WACCES | CLOSE COST TO DATE - JOB NEEDS TO GO TO SPECILISED SECURITY DOOR ELECTRICIAN - ELECTRICAL DELAY ON DOOR MAGNET
MSA-DTAG | WA5116362 | 3 | Sapio Pty Ltd | Duress map not showing new duress points. | Security | Security Management System | 130 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-11 14:20 | 2022-02-18 17:00 | 2022-02-15 14:00 | 2022-02-18 17:00 | 2022-02-15 14:45 |  |  | Supplied passwords to 3rd party company. Fixed duress maps.Job completed.
MSA-DTAG | WA5127111 | 1 | Sapio Pty Ltd | Ground - Security - Court entry button to Court 1 is not working | Security | Keys & Access | 130 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-14 11:28 | 2022-02-15 17:00 | 2022-02-15 07:00 | 2022-02-15 17:00 | 2022-02-15 07:45 |  |  | Found that the logic block was in an unknown state. Reset system and tested
MSA-DCA | WA5133583 | 2 | Protek 24/7 Building & Maintenance | Ground - Stage Door - Courier opened Stage Door the wrong way and it does not open/close properly | Building | General Building | 100.375 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-15 12:03 | 2022-02-18 17:00 | 2022-02-18 10:30 | 2022-02-18 17:00 | 2022-02-18 11:15 |  |  | Repaired door
MSA-DFES | WA5133848 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Ground Floor - Room 5 Bathroom - light switch is faulty and arcing | Electrical | General Electrical | 136.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-15 15:15 | 2022-02-18 17:00 | 2022-02-17 07:00 | 2022-02-18 17:00 | 2022-02-17 07:45 |  |  | Fix faulty light switch
MSA-DTWD | WA5151557 | 3 | AWB Co. | Level 1 - E500 - spot welder faulty water cooler not coming on to cool tip | Electrical | General Electrical | 157.47 | Pass | Pass | -1 | -1 | 0.75 | 2022-02-17 14:00 | 2022-02-24 17:00 | 2022-02-18 08:45 | 2022-02-24 17:00 | 2022-02-18 09:30 |  |  | Attended site, signed in, completed jsa,spoke to fm about job, went to e block and spoke with technician about job, technician wanted gpo mounted on outside of the machine wired into the spot welder for water pump, raised issues with fm regarding voiding warranty of new machine as multiple holes would be drilled into framework and wiring would be altered , fm said not to modify and leave machine as is , spoke to technician about alternative solutions , completed paperwork, signed out , **Job completed**
MSA-DTWD | WA5163516 | 1 | Complete Pest Management Services | rooms U7 & U8 - Bad smell in classrooms coming from roof could be dead animal please investigate | Pest Control | General Pest | 227.27 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-18 09:48 | 2022-02-21 17:00 | 2022-02-21 12:00 | 2022-02-21 17:00 | 2022-02-21 12:45 |  |  | Inspected roof void for dead rodents nothing found smell appears to be coming from cavity, placed 3 freaky wavedeodoriser and one absorption bag
MSA-DFES | WA5163752 | 3 | Go Doors | Ground floor - stair 5 - Auto close door not working Door doesn’t shut properly - door not latching | Building | Automatic Doors | 310 | Pass | Pass | -1 | -1 | 0.75 | 2022-02-18 11:41 | 2022-02-25 17:00 | 2022-02-18 15:15 | 2022-02-25 17:00 | 2022-02-18 16:00 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5187904 | 2 | Protek 24/7 Building & Maintenance | Classroom 4 – glass in window loose – rubber seal is falling off both sides | Building | Windows | 998.15 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-22 16:49 | 2022-02-25 17:00 | 2022-02-25 13:15 | 2022-02-25 17:00 | 2022-02-25 14:00 |  | WACCES | Replace Glass in window
MSA-DFES | WA5191538 | 2 | Protek 24/7 Building & Maintenance | Various - Ground - Tunic room door off its runner. Requires fix & a stop mechanism | Building | General Building | 100.375 | Pass | Pass | 0 | 0 | 0.75 | 2022-02-25 07:05 | 2022-03-01 17:00 | 2022-02-28 15:00 | 2022-03-01 17:00 | 2022-02-28 15:45 |  | WACCES | Repair tunic room door
MSA-DTAG | WA5199785 | 3 | Midolo Building Services | Level 7 - Reception glass security divider is loose | Building | Windows | 197.72 | Pass | Pass | -1 | -1 | 0.75 | 2022-03-01 11:55 | 2022-03-09 17:00 | 2022-03-03 12:00 | 2022-03-09 17:00 | 2022-03-03 12:45 |  |  | REPAIRS MADE TO SECURE DIVIDER
MSA-DCA | WA5202932 | 2 | Schindler Lifts Australia | Alexander Library Building - Public lifts - Ground - Fireman’s key switch is loose | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.75 | 2022-03-03 09:25 | 2022-03-09 17:00 | 2022-03-04 09:30 | 2022-03-09 17:00 | 2022-03-04 10:15 |  |  | to be closed out at $0 cost
MSA-DFES | WA5204958 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Storeroom - Light not working | Electrical | Lighting, Internal | 163.755 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-04 16:22 | 2022-03-10 17:00 | 2022-03-08 14:45 | 2022-03-10 17:00 | 2022-03-08 15:30 |  |  | Located faulty light. Replaced faulty tube with new but the light still did not work. Replaced faulty electronic ballast with new and the light now works.
MSA-DTAG | WA5207462 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Staff Female Toilet - Water will not flush in one of the cisterns | Plumbing & Drainage | Toilets/Cisterns | 132.7725 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-08 13:19 | 2022-03-09 17:00 | 2022-03-09 10:30 | 2022-03-09 17:00 | 2022-03-09 11:15 |  |  | Completed
MSA-DTWD | WA5207641 | 2 | AHS Services WA Pty Ltd (Anchor) | A Block - West End - Male and Female last cubicle buttons not working | Plumbing & Drainage | Toilets/Cisterns | 107.2725 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-08 15:04 | 2022-03-11 17:00 | 2022-03-10 09:30 | 2022-03-11 17:00 | 2022-03-10 10:15 |  |  | Readjusted flush buttons tested multiple times all good
MSA-DTWD | WA5215588 | 2 | SENTINEL LOCK SERVICE PTY LTD | block B - Third floor - B2314 - Faulty lock on CAD room door | Security | Locksmith | 121.32 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-10 13:49 | 2022-03-15 17:00 | 2022-03-15 13:00 | 2022-03-15 17:00 | 2022-03-15 13:45 |  |  | B Block - B2314 - Lock faulty.Lock repaired.
MSA-DTWD | WA5216758 | 1 | AWB Co. | Light switch turned and made crackling sound | Electrical | General Electrical | 121.47 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-11 12:39 | 2022-03-14 17:00 | 2022-03-14 10:45 | 2022-03-14 17:00 | 2022-03-14 11:30 |  |  | Attended site and signed in. Completed JSA. Located J block, found classroom 4. Light switch working and a little bit crackly. Supply and replaced switch mech to wall plate. Tested all okay. Signed out. Job complete
MSA-DCA | WA5231584 | 2 | Protek 24/7 Building & Maintenance | Main Auditorium dressing room - see details below | Building | General Building | 100.375 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-15 12:25 | 2022-03-18 17:00 | 2022-03-17 10:00 | 2022-03-18 17:00 | 2022-03-17 10:45 |  |  | Investigate & report
MSA-DTWD | WA5231595 | 2 | AWB Co. | 40 Commerce Ave - Ground - Lights flashing in corridor -Flashing light | Electrical | General Electrical | 121.02 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-15 12:34 | 2022-03-18 17:00 | 2022-03-18 14:15 | 2022-03-18 17:00 | 2022-03-18 15:00 |  |  | Attended site signed in completed jsa.Found flickering plc lamp in foyer. Replaced with new 18w plc lamp.***job completed****
MSA-DTWD | WA5231741 | 3 | Swan Pest Control | Level 2 - room A213 - Mice evident in office | Pest Control | General Pest | 170 | Pass | Pass | -1 | -1 | 0.75 | 2022-03-15 14:08 | 2022-03-22 17:00 | 2022-03-17 12:45 | 2022-03-22 17:00 | 2022-03-17 13:30 |  |  | Rebaited the roof void and rodent stations in Room A213 with ditrac blocks
MSA-DTAG | WA5276990 | 1 | Sapio Pty Ltd | Custody - Cell 1 - CCTV camera keeps dropping out | Security | CCTV Surveillance | 130 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-18 13:03 | 2022-03-21 17:00 | 2022-03-21 08:00 | 2022-03-21 17:00 | 2022-03-21 08:45 |  |  | Work performed by Michael Tomlinson (21/03/2022) Attended site. Investigated and found camera dropped out around same time as power fail Tuesday 15th March and has since recovered stream ok. No issues present.
MSA-DTWD | WA5278489 | 1 | SCAVENGER SUPPLIES PTY LTD | J Block - JF06 -Fire alarm activated, suspect faulty heat sensor. Panel isolated for J & C Block | Fire Protection Services | Fire Protection - Monitor System | 378.76 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-18 15:51 | 2022-03-21 17:00 | 2022-03-18 16:00 | 2022-03-21 17:00 | 2022-03-18 16:45 |  |  | COMPLETED 18/03/2022
MSA-DTWD | WA5285812 | 2 | Securex Security Systems & Services | Level 2 - Securex Panel 21 - Faulty battery | Security | Monitoring | 240 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-21 10:22 | 2022-03-24 17:00 | 2022-03-21 11:00 | 2022-03-24 17:00 | 2022-03-21 11:45 |  |  | 21/03/2022, 1100-1145Replaced battery in dgp 21
MSA-DTAG | WA5286176 | 2 | Midolo Building Services | Level 3 - Admin Services - see below details | Building | General Building | 115.02 | Fail | Fail | 1 | 1 | 0.75 | 2022-03-21 12:56 | 2022-03-24 17:00 | 2022-03-28 14:15 | 2022-03-24 17:00 | 2022-03-28 15:00 |  |  | repairs to closing mechanisim
MSA-DFES | WA5287156 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Female Toilets - sink isnt working | Plumbing & Drainage | Drainage | 116.4 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-22 10:38 | 2022-03-25 17:00 | 2022-03-22 11:45 | 2022-03-25 17:00 | 2022-03-22 12:30 |  |  | Attended site for ground floor female toilets sink Blocked after inspection I have not found a blockage in the sink I have plunged the sink just in case everything is still running I’ve tested all three things for five minutes and also check the floor waste gully everything is clearing cleaned up packed up
MSA-DTAG | WA5287726 | 1 | Midolo Building Services | Ground (External) - Near Court 6 (back of building) - see details below | Building | General Building | 122.42 | Fail | Fail | 0 | 0 | 0.75 | 2022-03-22 15:03 | 2022-03-23 17:00 | 2022-03-24 08:15 | 2022-03-23 17:00 | 2022-03-24 09:00 |  |  | FLYSCREEN SECURED BACK TO FRAME
MSA-DTWD | WA5288494 | 2 | Morris Pest and Weed Control | BLD 838 - Please eradicate mice | Pest Control | General Pest |  | Pass | Pass | -1 | -1 | 0.75 | 2022-03-23 11:09 | 2022-03-28 17:00 | 2022-03-23 11:15 | 2022-03-28 17:00 | 2022-03-23 12:00 |  |  | Rodent baiting
MSA-DFES | WA5289452 | 1 | Go Doors | Engine Room Door 1 and 2- not closing automatically when leaving premise | Building | Automatic Doors | 310 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-24 09:30 | 2022-03-25 17:00 | 2022-03-24 12:00 | 2022-03-25 17:00 | 2022-03-24 12:45 |  |  | Completed works. Please see attachments.
MSA-DTWD | WA5290019 | 2 | SENTINEL LOCK SERVICE PTY LTD | CG12 - Locks to main entry are stick & lose, may need adjustment or possible replacement | Security | Locksmith | 71.32 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-24 15:22 | 2022-03-29 17:00 | 2022-03-29 10:55 | 2022-03-29 17:00 | 2022-03-29 11:40 |  |  | Block c - CG12 - Wash Room - lock is sticky/loose.Lock repaired.
MSA-DFES | WA5290568 | 2 | Complete Pest Management Services | Hot Water System - terminates have been located please treat | Pest Control | General Pest | 162.91 | Pass | Pass | 0 | 0 | 0.75 | 2022-03-25 10:06 | 2022-03-30 17:00 | 2022-03-28 09:30 | 2022-03-30 17:00 | 2022-03-28 10:15 |  |  | There is a high volume of mudding on the walls created by mud wasps which may have been mistaken for termitemudding.No evidence of termite activity found
MSA-DTWD | WA5295299 | 3 | AWB Co. | T Block - First floor - Passage outside T130 - Passage light no working / Fluro | Building | General Building | 119.915 | Pass | Pass | -1 | -1 | 0.75 | 2022-03-29 12:27 | 2022-04-05 17:00 | 2022-03-30 11:00 | 2022-04-05 17:00 | 2022-03-30 11:45 |  |  | Attended site and signed in. Completed JSA. Liaised with fm about works. Supplied and replaced 1x T5 tube. Tested for correct operation. All working. **job complete**
MSA-DTWD | WA5301805 | 1 | AWB Co. | AT228 Staff lunch room - Double GPO next to microwave damaged | Electrical | General Electrical | 126.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-04-01 12:47 | 2022-04-04 17:00 | 2022-04-04 07:30 | 2022-04-04 17:00 | 2022-04-04 08:15 |  |  | Attended site and signed in. Completed JSA. Located staff lunch room. Found gpo behind microwave to be damaged. Isolated power. Supply and replace with new double gpo. Reinstated power. Tested all okay. Signed out. Job complete
MSA-DFES | WA5301854 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Male Toilet - located Lower Ground North - light not working | Electrical | Lighting, Internal | 215.685 | Pass | Pass | 0 | 0 | 0.75 | 2022-04-01 13:24 | 2022-04-08 17:00 | 2022-04-05 13:45 | 2022-04-08 17:00 | 2022-04-05 14:30 |  |  | Onsite 1345 from previous job. Replaced light and tested light. Completed paperwork and signed out at 1430
MSA-DFES | WA5303132 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Stores - power keeps tripping | Electrical | General Electrical | 100.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-04-04 08:34 | 2022-04-05 17:00 | 2022-04-04 09:30 | 2022-04-05 17:00 | 2022-04-04 10:15 |  |  | Attended site at 0930. Investigated power tripped in Store. Found circuit W13 to be tripped and in the OFF position at board. Unplugged all equipment and reenergised circuit. Circuit remained energised once all equipment was plugged back into socket outlets. Monitored equipment for 15 minutes to ensure correct operation. All working okay. Informed staff and left site at 1015.
MSA-DTWD | WA5304502 | 2 | AHS Services WA Pty Ltd (Anchor) | A112 : café male toilet - Cistern pipe leaking | Plumbing & Drainage | Toilets/Cisterns | 129.7725 | Fail | Fail | 0 | 0 | 0.75 | 2022-04-05 08:01 | 2022-04-08 17:00 | 2022-04-11 08:00 | 2022-04-08 17:00 | 2022-04-11 08:45 |  |  | Completed
MSA-DTWD | WA5306595 | 1 | AWB Co. | 8G31 - Light switch arcing | Electrical | General Electrical | 152.14 | Pass | Pass | 0 | 0 | 0.75 | 2022-04-06 15:07 | 2022-04-07 17:00 | 2022-04-07 14:30 | 2022-04-07 17:00 | 2022-04-07 15:15 |  |  | Attended site signed in completed jsa. Found arching switch in room 8g31. Isolated and replaced with new switch.*** job completed ***
MSA-DTWD | WA5308412 | 3 | Protek 24/7 Building & Maintenance | Passageway outside Vehicle Body Building - 2 sections of ceiling slats fallen down - see notes | Building | Ceiling | 157.75 | Pass | Pass | -1 | -1 | 0.75 | 2022-04-08 11:46 | 2022-04-19 17:00 | 2022-04-11 11:00 | 2022-04-19 17:00 | 2022-04-11 11:45 |  |  | Repair 2 sections of ceiling slats
MSA-DTWD | WA5368960 | 1 | CAPS AUSTRALIA PTY LTD | Compressor Room - Level 1 - compressors not working | Equipment | Compressors, Generators |  | Fail | Fail | 5 | 5 | 0.75 | 2022-04-19 14:37 | 2022-04-20 17:00 | 2022-05-25 10:45 | 2022-04-20 17:00 | 2022-05-25 11:30 |  |  | new timer installed
MSA-DTAG | WA5380232 | 2 | Midolo Building Services | Youth Justice - Level 1 - Doors not latching onto magnets properly - See notes below | Building | Doors | 122.42 | Fail | Fail | 0 | 0 | 0.75 | 2022-04-22 09:39 | 2022-04-28 17:00 | 2022-04-29 12:15 | 2022-04-28 17:00 | 2022-04-29 13:00 |  |  | DOOR repairs & ADJUSTMENTS MADE
MSA-DFES | WA5382237 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | BA Servicing Room - fluorescent lighting in the room are not working | Electrical | Lighting, Internal | 168.795 | Fail | Fail | 0 | 0 | 0.75 | 2022-04-26 16:05 | 2022-04-29 17:00 | 2022-05-02 13:00 | 2022-04-29 17:00 | 2022-05-02 13:45 |  |  | Arrived on site at 1300 to investigate faulty fluros In servicing room. Located 3 x fluro’s out and 4 x faulty starters. Replacedcomponents and reenergised light fittings. Left site at 1345.
MSA-DTWD | WA5383023 | 1 | AWB Co. | Lighting circuit Blue 7 – eastern roadway lights - Blue 7 lighting circuit is tripping out | Electrical | General Electrical | 113.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-04-27 10:58 | 2022-04-28 17:00 | 2022-04-28 10:15 | 2022-04-28 17:00 | 2022-04-28 11:00 |  |  | Attended site signed in completed jsa. Spoke to mike about job. Circuit had been reported tripped. Ive turned circuit on while raining and no tripping. Ive had a look at bottom of poles all seems fine. left on for 5 hrs and no problems at all. Site will raise if issue persists further.*** job completed ***
MSA-DTWD | WA5390120 | 3 | Swan Pest Control | Outside B106 -Beehive needs to be removed | Pest Control | General Pest | 275 | Pass | Pass | -1 | -1 | 0.75 | 2022-05-02 10:25 | 2022-05-09 17:00 | 2022-05-04 09:15 | 2022-05-09 17:00 | 2022-05-04 10:00 |  |  | Sprayed bees with 30 litres Bifrenthrin in fence and removed most of the honeycomb
MSA-DTWD | WA5393125 | 2 | AWB Co. | Room CG02 - Light switch was crackling which caused RCD/MCB to trip - See notes | Electrical | Lighting, Internal | 174.41 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-03 15:12 | 2022-05-06 17:00 | 2022-05-06 11:30 | 2022-05-06 17:00 | 2022-05-06 12:15 |  |  | Attended site and signed in. Completed JSA. Spoke to fm about job. Located faulty light switch, replaced switch mech. Took picture. Everything working as intended. Completed paperwork. Signed out.*** job complete ***
MSA-DTWD | WA5393894 | 1 | SENTINEL LOCK SERVICE PTY LTD | 10F80 - Faulty door barrel | Security | Locksmith | 128.42 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-04 11:02 | 2022-05-05 17:00 | 2022-05-04 12:00 | 2022-05-05 17:00 | 2022-05-04 12:45 |  |  | 10F80 - Barrel loose.Door Handle and lock faulty.Repaired.
MSA-DTWD | WA5397017 | 3 | AWB Co. | Room D115 - Water leak from above | Roofing | Concrete Roof Construction | 168.75 | Pass | Pass | -1 | -1 | 0.75 | 2022-05-06 12:47 | 2022-05-13 17:00 | 2022-05-09 11:15 | 2022-05-13 17:00 | 2022-05-09 12:00 |  |  | Attended, waterproofing company required to assessadvising closing costs to date
MSA-DTWD | WA5398893 | 3 | AWB Co. | 5 x lights out | Electrical | Lighting, Internal | 411.6 | Fail | Fail | 0 | 0 | 0.75 | 2022-05-09 13:11 | 2022-05-16 17:00 | 2022-05-17 07:30 | 2022-05-16 17:00 | 2022-05-17 08:15 |  | WACCES | Attended site signed in completed jsa. Read work notes on job, 1 light out. Spoke to lecturer in area and asked him about the light. He said it’s a security light and it doesn’t come on with the rest. Tested security light circuit and light came on. Light is all good. Job complete
MSA-DTAG | WA5399204 | 3 | Midolo Building Services | Level 3, 5, 9 - Mould around the edge of the ceiling | Building | Ceiling | 88.4 | Pass | Pass | -1 | -1 | 0.75 | 2022-05-09 18:04 | 2022-05-16 17:00 | 2022-05-12 10:00 | 2022-05-16 17:00 | 2022-05-12 10:45 |  |  | ON INSPECTION IT WAS FOUND TO BE DUST BUILD UP, HAS BEEN CLEANED
MSA-DFES | WA5399238 | 2 | Protek 24/7 Building & Maintenance | METAL COVER NEEDS FIXING BACK INTO PLACE AT THE BOTTOM OF DORMITORY DOOR, | Building | Doors | 100.375 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-09 20:17 | 2022-05-12 17:00 | 2022-05-11 09:00 | 2022-05-12 17:00 | 2022-05-11 09:45 |  |  | Fix metal cover back to the bottom of door
MSA-DFES | WA5407563 | 3 | SONTEC WA PTY LTD | Front Forecourt/Foyer - Remove Alarm Function from Analytics Camera | Security | CCTV Surveillance | 270 | Pass | Pass | -1 | -1 | 0.75 | 2022-05-11 12:38 | 2022-05-18 17:00 | 2022-05-13 09:00 | 2022-05-18 17:00 | 2022-05-13 09:45 |  |  | 13/5/22 - Dylan ParslowDisabled loitering input for analytics camera.
MSA-DTWD | WA5407778 | 1 | FSA (WA) Pty Ltd | Fire alarm - Level 1 - alarm activated - please investigate and reset | Fire Protection Services | Fire Protection - Monitor System | 132.905 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-11 13:50 | 2022-05-12 17:00 | 2022-05-11 14:00 | 2022-05-12 17:00 | 2022-05-11 14:45 |  |  | Found alarm on break glass which was broken from a student in M block. Replaced break glass on mcp and reset alarm. De isolated zone and panel all clear and ok now
MSA-DTWD | WA5413318 | 2 | ECO PLUMBING AND GAS PTY LTD | D009 - Courtyard - leaking tap | Plumbing & Drainage | Materials | 131.425 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-12 10:17 | 2022-05-17 17:00 | 2022-05-17 14:00 | 2022-05-17 17:00 | 2022-05-17 14:45 |  |  | Replaced leaking hose tap
MSA-DTWD | WA5413423 | 2 | ECO PLUMBING AND GAS PTY LTD | ET14 - Toilet consistently flushing | Plumbing & Drainage | Toilets/Cisterns | 95.565 | Fail | Fail | 9 | 9 | 0.75 | 2022-05-12 11:02 | 2022-05-17 17:00 | 2022-07-20 16:00 | 2022-05-17 17:00 | 2022-07-20 16:45 |  |  | Replaced outlet washer
MSA-DCA | WA5416856 | 0 | TK Elevator Australia Pty Ltd | Ground Floor- Foyer - Lift - not responsive | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0.75 | 2022-05-13 08:55 | 2022-05-13 10:55 | 2022-05-13 15:00 | 2022-05-13 12:55 | 2022-05-13 15:45 |  |  | Discovered lift ooo, lift drove into bottom limit switch, 50mm below floor level, drove lift on inspection, power cycled lift, reset on main print board. Tested lift with multiple runs with empty cab and with person inside, lift running normal. Lift left in service.close out at $0 cost
MSA-DFES | WA5417344 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Lower Level Male Toilets - Ceiling - Reconnect Light in male toilets as roof has been repaired | Electrical | Lighting, Internal | 100.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-13 12:00 | 2022-05-20 17:00 | 2022-05-19 14:45 | 2022-05-20 17:00 | 2022-05-19 15:30 |  |  | Arrived on site at 14:45. Went to lower male toilets and located light that has been disconnected due to ceiling damage, checked light for water damage all okay. Reconnected light and tested. Left site at 15:30
MSA-DTAG | WA5417377 | 1 | AAA Ability Locksmiths | Custody Cells - Cell 4 - Hatch Lock requires attention | Security | Locksmith | 486.43 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-13 12:19 | 2022-05-16 17:00 | 2022-05-16 07:15 | 2022-05-16 17:00 | 2022-05-16 08:00 |  |  | Attend site, replace lock.
MSA-DCA | WA5461813 | 0 | Precise Air Group | Air con is faulty - too hot | Air Conditioning | Building HVAC Maintenance (Major Plant) | 156.99 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-19 09:07 | 2022-05-19 11:07 | 2022-05-19 09:30 | 2022-05-19 13:07 | 2022-05-19 10:15 |  |  | Attended site and signed in. Spoke to staff and found the heating coils were opening to 100%. This issue is from from the controls, contacted controls contractor and was told they will monitor remotely and have their engineers look into the problem. Left valves closed so space can cool.
MSA-DTWD | WA5462184 | 3 | PEEL LOCK SERVICES PTY LTD | Room B49 - Stolen lockable door handle needs replacing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-05-19 12:26 | 2022-05-26 17:00 | 2022-05-23 10:30 | 2022-05-26 17:00 | 2022-05-23 11:15 |  |  | Repairs to lock
MSA-DFES | WA5468544 | 2 | Complete Pest Management Services | Reception - Foyer - bad smell in reception foyer - suspected dead animal | Pest Control | General Pest | 208.36 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-20 10:26 | 2022-05-25 17:00 | 2022-05-23 07:30 | 2022-05-25 17:00 | 2022-05-23 08:15 |  |  | Inspected foyer of admin for rodent smell , lifted panels and checked void for dead rodent, could not locate may havefallen in cavity wall , placed odour eater bag in void next to wall where smell is worst , placed odour gel pot oncabinet in foyer.
MSA-DTAG | WA5469086 | 2 | Midolo Building Services | Level 3 - Court 36 - Witness Box - bracket has come loose | Building | General Building | 119.99 | Fail | Fail | 0 | 0 | 0.75 | 2022-05-20 15:39 | 2022-05-25 17:00 | 2022-05-27 08:00 | 2022-05-25 17:00 | 2022-05-27 08:45 |  |  | BRACKET HAS BEEN RESECURED
MSA-DTAG | WA5470485 | 2 | Midolo Building Services | Level 15 - Balcony door - Doors not closing properly | Building | Doors | 85.1 | Fail | Fail | 0 | 0 | 0.75 | 2022-05-23 10:28 | 2022-05-26 17:00 | 2022-05-27 10:30 | 2022-05-26 17:00 | 2022-05-27 11:15 |  |  | adjustment made to doors
MSA-DTWD | WA5472152 | 2 | Protek 24/7 Building & Maintenance | E26 Corridor (just outside E30 Kitchen) - Roof Leak | Roofing | Metal Roofing | 157.75 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-23 14:49 | 2022-05-26 17:00 | 2022-05-24 12:30 | 2022-05-26 17:00 | 2022-05-24 13:15 |  |  | Repair Roof leak - E26 Corridor
MSA-DFES | WA5472230 | 3 | AWB Co. | Radio Comms Store - Battery Shed (Boat Shed) - Roof of Boat Shed is leaking Rain | Building | General Building | 189.38 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-23 16:09 | 2022-05-30 17:00 | 2022-05-30 12:45 | 2022-05-30 17:00 | 2022-05-30 13:30 |  |  | Attended and found joint in flashing not sealed. Resealed area. Job complete.
MSA-DTWD | WA5473002 | 3 | AWB Co. | P16 - light above sink is not working | Electrical | Lighting, Internal | 113.82 | Pass | Pass | -1 | -1 | 0.75 | 2022-05-24 12:12 | 2022-05-31 17:00 | 2022-05-27 15:00 | 2022-05-31 17:00 | 2022-05-27 15:45 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, set up work area, replaced tube and starter , light now working, packed up, completed paperwork,signed out,*** job completed***
MSA-MRWA | WA5473290 | 3 | AWB Co. | Double Light switch failing - Switch mechs stiff and dislodging | Electrical | Lighting, Internal | 127.54 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-24 13:40 | 2022-05-31 17:00 | 2022-05-30 17:00 | 2022-05-31 17:00 | 2022-05-30 17:45 |  |  | Attended site and signed in. Completed JSA. Located level 8 kitchen and found light switch faulty and broken. Supply and replace with new 2 gang light switch. Tested all okay. Signed out. Job complete
MSA-DFES | WA5477979 | 2 | Protek 24/7 Building & Maintenance | Main Foyer - Engine bay roof has small holes along the ridge line | Roofing | Metal Roofing | 185.25 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-26 07:37 | 2022-05-30 17:00 | 2022-05-27 09:30 | 2022-05-30 17:00 | 2022-05-27 10:15 |  |  | Repair small holes to engine bay roof
MSA-DTWD | WA5479609 | 2 | Protek 24/7 Building & Maintenance | C Block roof - Childcare roof - Eave on roof has become distorted - see notes below | Building | General Building | 478.22 | Pass | Pass | 0 | 0 | 0.75 | 2022-05-27 10:22 | 2022-06-01 17:00 | 2022-06-01 12:30 | 2022-06-01 17:00 | 2022-06-01 13:15 |  | WACCES | Braf DeclinedTemp Fence provided
MSA-DFES | WA5481839 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Female Toilet Shower - shower head damaged - Water coming out when turned on | Plumbing & Drainage | Water | 200.9 | Fail | Fail | 1 | 1 | 0.75 | 2022-05-31 07:13 | 2022-06-02 17:00 | 2022-06-07 10:45 | 2022-06-02 17:00 | 2022-06-07 11:30 |  |  | I have replaced the broken showerhead with a new one I’ve been tested everything is working correctly cleaned up packed up
MSA-DCA | WA5482833 | 1 | TK Elevator Australia Pty Ltd | Level 1 - Green Room Corridor - Elevator 7 - displaying out of service - not moving | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.75 | 2022-05-31 16:22 | 2022-06-01 17:00 | 2022-05-31 17:00 | 2022-06-01 17:00 | 2022-05-31 17:45 |  |  | Lift7 Greem Rm-Hydraulic :Found run time error TTElap, reset lift and tested operation, couldnt fault and left in service
MSA-DTWD | WA5487411 | 1 | Equans Mechanical Services Australia | Block 1 - Ground Floor - Exhaust fans not working - See notes below | Equipment | Electrical Equipment | 350.58 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-01 14:55 | 2022-06-02 17:00 | 2022-06-02 08:15 | 2022-06-02 17:00 | 2022-06-02 09:00 |  |  | Fan operating when on-site. Was reported that fan not running several days before but was running the next day. Unit change over controller bridged out as 1 motor not operating and access was not available at that stage due to rain. Access difficult. Braf to be submitted to remove old fan from roof, (2 storey building) and install inline duct fan. Pricing required from installer before braf sent.
MSA-DTWD | WA5487419 | 3 | AWB Co. | Room N41 - 9 lights not working | Electrical | Lighting, Internal | 113.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-01 15:02 | 2022-06-09 17:00 | 2022-06-09 15:30 | 2022-06-09 17:00 | 2022-06-09 16:15 |  |  | Liam Sirr (09/06/2022) - Work NoteBraf required- man lift hire , 26 x 865 36w tubes , 26x s10 starters 4hours labour for 2 peopleBRAF declined - invoice works completed
MSA-DTAG | WA5491357 | 1 | Midolo Building Services | Chambers 14.05 - Partial roof collapse | Roofing | Metal Roofing | 92.5 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-03 14:52 | 2022-06-07 17:00 | 2022-06-07 07:30 | 2022-06-07 17:00 | 2022-06-07 08:15 |  | WACCES | INSPECT ONLY - OLD WORKS Closing cost to date to last attendance 07/06
MSA-DTWD | WA5493564 | 3 | Securex Security Systems & Services | Tamper Alarm on DGP14 - see details below | Security | Monitoring | 240 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-07 09:06 | 2022-06-14 17:00 | 2022-06-08 14:00 | 2022-06-14 17:00 | 2022-06-08 14:45 |  |  | Iain McGillemhaoil (08/06/2022, 1400-1445) - Work NoteBuilding is no longer used and requires decommissioning, advised David he needs to request in writing. Replaced panelbattery. Tamper switches ok. Faulty old swipe card reader causing random arming signals, and Ethernet fail as switcheson building turned off.
MSA-DTAG | WA5493889 | 2 | Bullant Security Pty Ltd | Ground - Registry Office Door - door handle is damaged | Security | Locksmith | 198.09 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-07 11:07 | 2022-06-10 17:00 | 2022-06-08 09:15 | 2022-06-10 17:00 | 2022-06-08 10:00 |  |  | Attend site, repair handle and replace broken fixing screws for correct operation Date on site: 08/06/2022 Time on site: 09:15am - 10:00am
MSA-DTWD | WA5495342 | 3 | AWB Co. | D07- Over computers 6 & 7 - near the main desk - light out | Electrical | General Electrical | 113.82 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-08 11:28 | 2022-06-15 17:00 | 2022-06-10 13:15 | 2022-06-15 17:00 | 2022-06-10 14:00 |  |  | Attended site signed in jsa completed. Spoke with library staff about job. Light about computer was flickering. Replaced with tubes on site and starters on site 4 in total. ***Job is now completed***
MSA-DTWD | WA5495662 | 3 | Water2water Pty Ltd | A49 - Broken plastic tap on water cooler | Plumbing & Drainage | Water | 184.6325 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-08 13:57 | 2022-06-15 17:00 | 2022-06-13 08:00 | 2022-06-15 17:00 | 2022-06-13 08:45 |  |  | REPLACED BOTH TAPS DUE TO BEING SNAPPED
MSA-DFES | WA5496831 | 1 | Go Doors | DOSS Office - Automatic Door - Office not latching properly | Building | Automatic Doors | 310 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-09 12:46 | 2022-06-10 17:00 | 2022-06-09 15:00 | 2022-06-10 17:00 | 2022-06-09 15:45 |  |  | Please see attachments.
MSA-DFES | WA5499920 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Applied training ground - Gantry - Leaking Valve on the gantry | Plumbing & Drainage | Water | 109.9 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-10 15:42 | 2022-06-13 17:00 | 2022-06-13 07:30 | 2022-06-13 17:00 | 2022-06-13 08:15 |  |  | We are unable to repair the gas leak as it requires a specialised gas license site will have to contact the company that Regli does the gas issues
MSA-DFES | WA5511722 | 2 | AWB Co. | Ground Level - Outside study rooms, east wall - Down pipe has dislodged from gutter | Building | General Building | 168.75 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-13 08:05 | 2022-06-16 17:00 | 2022-06-14 07:00 | 2022-06-16 17:00 | 2022-06-14 07:45 |  |  | Found downpipes dropped from outlets. Pushed back onto outlet and screwed together
MSA-DTWD | WA5511836 | 2 | LIGHTHOUSE LOCKSMITHS | Kendrew- A-Block Room A009 broken key to door lock | Security | Locksmith | 140 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-13 09:44 | 2022-06-16 17:00 | 2022-06-13 11:00 | 2022-06-16 17:00 | 2022-06-13 11:45 |  |  | Serviced lock and replaced damaged key for room A009
MSA-DCA | WA5512069 | 3 | Critical Fire Protection & Training | Level 1 - HLT Foyer - Dirty Smoke detector in stairwell 2 Causing Fault on Fire panel | Fire Protection Services | Smoke and Heat Detection | 250.605 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-13 12:59 | 2022-06-20 17:00 | 2022-06-14 12:30 | 2022-06-20 17:00 | 2022-06-14 13:15 |  |  | Start time: 12:30pmFinish time: 1:15pmAttended site and located faulty detector that was in fault due to being a “dirty device”.Replaced detector head and fault cleared from panel with all systems returned to normal operation. M4-147 LVL 3 east stairwell (Zn 2)
MSA-DTWD | WA5512155 | 3 | ECO PLUMBING AND GAS PTY LTD | C103 - leaking tap staff kitchen | Plumbing & Drainage | Water | 141.425 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-13 14:26 | 2022-06-20 17:00 | 2022-06-20 15:00 | 2022-06-20 17:00 | 2022-06-20 15:45 |  |  | replaced tap
MSA-DTWD | WA5512158 | 3 | AWB Co. | C103 - 2 x lights out | Electrical | Lighting, Internal | 157.47 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-13 14:29 | 2022-06-20 17:00 | 2022-06-16 08:15 | 2022-06-20 17:00 | 2022-06-16 09:00 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located faulty light fittings, removed old tubs and replaced with new, put old tubes in allocated boxes on site , packed up, completed paperwork, signed out** job completed**
MSA-DTWD | WA5512161 | 3 | AWB Co. | C106 - 2 x lights out | Electrical | Lighting, Internal | 157.47 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-13 14:30 | 2022-06-20 17:00 | 2022-06-16 09:45 | 2022-06-20 17:00 | 2022-06-16 10:30 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located faulty light fittings, removed old tubs and replaced with new, put old tubes in allocated boxes on site , packed up, completed paperwork, signed out** job completed**
MSA-DTWD | WA5512165 | 3 | AWB Co. | C109 - 2 x lights out | Electrical | Lighting, Internal | 157.47 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-13 14:32 | 2022-06-20 17:00 | 2022-06-16 09:00 | 2022-06-20 17:00 | 2022-06-16 09:45 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located faulty light fittings, removed old tubs and replaced with new, put old tubes in allocated boxes on site , packed up, completed paperwork, signed out** job completed**
MSA-DTWD | WA5513091 | 3 | AWB Co. | Library - Light above PC15 Flickering | Electrical | Lighting, Internal | 157.47 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-14 07:41 | 2022-06-20 17:00 | 2022-06-20 11:00 | 2022-06-20 17:00 | 2022-06-20 11:45 |  |  | Attended site and signed in, completed jsa,spoke with fm about job,located lighting and replaced tubes and starters, all lights working as intended , put tubes in allocated site bin, completed paperwork, signed out***job completed***
MSA-DTWD | WA5521673 | 0 | UNIVERSAL DOORS | Room AT102 - The door wont open - Tilt Doors - Press button automatic door | Building | Automatic Doors |  | Pass | Pass | 0 | 0 | 0.75 | 2022-06-15 10:39 | 2022-06-15 12:39 | 2022-06-15 12:15 | 2022-06-15 14:39 | 2022-06-15 13:00 |  |  | ATTENDED SITE TO INSPECT & REPAIR THE FAULTY BI-FOLDING DOOR,FOUND NO POWER FROM MAIN DISTRIBUTION BOARD, SITE ELECTRICIAN TOATTEND SITE TO TEST & REPAIR
MSA-DTAG | WA5521807 | 3 | Sapio Pty Ltd | Entrance Desk (Fish bowl) - PA System is cutting in and out - See notes below | Security | Security Management System | 130 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-15 10:52 | 2022-06-22 17:00 | 2022-06-15 14:45 | 2022-06-22 17:00 | 2022-06-15 15:30 |  |  | Found that the main unit had moved off preset 1. Returned to preset 1 so all channels now work.
MSA-DTWD | WA5521874 | 2 | AWB Co. | Jobs and Skills – room 3 -Faulty light switch noise when activated | Electrical | General Electrical | 143.28 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-15 11:04 | 2022-06-20 17:00 | 2022-06-20 08:15 | 2022-06-20 17:00 | 2022-06-20 09:00 |  |  | Attended site and signed in. Completed JSA. Located room 3 in jobs and skills. Found light switch to crackle arc flash and buzz when flicked on and off. Supply and replace with new 20amp switch mech. Tested all okay. Signed out. Job complete
MSA-DFES | WA5522397 | 3 | Protek 24/7 Building & Maintenance | SO Dorm into bathroom - Sliding door into the bathroom has come off its rails. | Building | Doors | 157.75 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-15 15:07 | 2022-06-22 17:00 | 2022-06-21 14:00 | 2022-06-22 17:00 | 2022-06-21 14:45 |  |  | Refix sliding door to rails
MSA-DTAG | WA5562854 | 2 | Midolo Building Services | Level 9 - Bathroom behind Court 91 - door has come off the top hinge | Building | General Building | 125.39 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-20 10:09 | 2022-06-23 17:00 | 2022-06-21 07:30 | 2022-06-23 17:00 | 2022-06-21 08:15 |  |  | DOOR RESECURED
MSA-DTWD | WA5564399 | 2 | ECO PLUMBING AND GAS PTY LTD | P13 - AMEP crèche at Midland - pipe under the sink in the main childcare room is leaking | Plumbing & Drainage | Drainage | 116.425 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-21 10:11 | 2022-06-24 17:00 | 2022-06-22 16:00 | 2022-06-24 17:00 | 2022-06-22 16:45 |  |  | Tightened fitting on on p trap
MSA-DFES | WA5565260 | 3 | AWB Co. | Radio Comms Kitchen - roof leak - see notes below | Roofing | Metal Roofing | 189.38 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-21 16:50 | 2022-06-28 17:00 | 2022-06-27 09:15 | 2022-06-28 17:00 | 2022-06-27 10:00 |  |  | Investigated and repair of roof leak over kitchen radio comms. Sealed up rivet holes on the anchor point. Job complete
MSA-DTWD | WA5566518 | 2 | AWB Co. | T206 -Internal room – no windows - Light switch button dislodged | Electrical | General Electrical | 113.82 | Pass | Pass | -1 | -1 | 0.75 | 2022-06-23 09:07 | 2022-06-28 17:00 | 2022-06-23 12:45 | 2022-06-28 17:00 | 2022-06-23 13:30 |  |  | Attended site and signed in. Completed JSA. Located t206. Found broken damaged light switch. Supply and replace with new single gang switch. Tested all okay. Signed out. Job complete
MSA-DFES | WA5567006 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Male toilets - toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 109.9 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-23 13:32 | 2022-06-24 17:00 | 2022-06-23 14:45 | 2022-06-24 17:00 | 2022-06-23 15:30 |  |  | Attended site for level one male toilet first cubicle blocked on inspection found is slightly blocked the toilet paper I have cleared the blockage with a toilet brush after I’ve tested everything is workingcorrectly cleaned up packed up
MSA-DTWD | WA5567995 | 3 | AWB Co. | B203.1 - Lights are faulty | Electrical | General Electrical | 176.3575 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-24 14:17 | 2022-07-01 17:00 | 2022-06-30 15:00 | 2022-07-01 17:00 | 2022-06-30 15:45 |  |  | Attended site and signed in. Completed JSA. Located room B203.1 and found flickering light and light out. Supply and replace tubes and starters as required. Tested all okay. Signed out. Job complete
MSA-DCA | WA5569967 | 0 | EQUANS Mechanical Services (WA) Pty Limited | Art Gallery of WA - Level 4 - RO Plant failed alarm | Air Conditioning | Building HVAC Maintenance (Major Plant) | 459.1625 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-27 22:02 | 2022-06-28 00:02 | 2022-06-27 22:45 | 2022-06-28 02:02 | 2022-06-27 23:30 |  |  | Checked BMS found RO plant in fault.Checked RO plant, no faults on controller.Checked BMS again and reset general alarm on chiller page.Fault cleared.Checked RO plant, operating as normal.
MSA-DTWD | WA5570293 | 3 | AWB Co. | East external wall 4 x walkway lights out | Electrical | Lighting, External | 113.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-28 09:13 | 2022-07-05 17:00 | 2022-07-05 08:15 | 2022-07-05 17:00 | 2022-07-05 09:00 |  |  | Attended site and signed in. Completed JSA. Located all overrides for walkway at E block. Turned on and checked out the walk way lighting. All lights are working. 1 pole light in garden is out and site advised the wall lights are ample if working. Signed out. Job complete
MSA-DTAG | WA5570428 | 1 | Complete Pest Management Services | Level 10 - Kitchen - Cockroach infestation/pest infestation - See notes below | Pest Control | General Pest | 504.65 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-28 10:59 | 2022-06-29 17:00 | 2022-06-28 11:30 | 2022-06-29 17:00 | 2022-06-28 12:15 |  |  | Inspected for cockroaches, applied seclira wth IGR and gel bait to appropriate surface's.Installed 2 rega slim monitors Applied clear out to all crack and crevices
MSA-MRWA | WA5570842 | 2 | AWB Co. | Level 4 - North East Lights - 4 Lights along north east windows out | Electrical | Lighting, Internal | 163.5975 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-28 15:42 | 2022-07-01 17:00 | 2022-07-01 06:00 | 2022-07-01 17:00 | 2022-07-01 06:45 |  |  | Attended site and signed in. Completed JSA. Investigated 4 lights not working on level 4. Found to be all lights working on floor. Spoke to Danika about works. Completed paperwork. No one on site to sign paperwork will email it through. **job complete**
MSA-DTWD | WA5571224 | 2 | AWB Co. | Classroom 1 - Flickering light - see notes below | Electrical | Lighting, Internal | 122.07 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-29 09:50 | 2022-07-04 17:00 | 2022-07-01 13:15 | 2022-07-04 17:00 | 2022-07-01 14:00 |  |  | Attended site and signed in. Completed JSA. Located room A1 and found all light to be on and none flickering, checked out site for flickering light. Awaited lady in room to call the lecturer to find out what light was reported. Found the light in failure. Supply and replaced lamps and starters. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5571722 | 3 | ECO PLUMBING AND GAS PTY LTD | Level G - Room E200 - Floor drain blocked near wash troughs | Plumbing & Drainage | Drainage | 122.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-29 11:18 | 2022-07-06 17:00 | 2022-07-06 10:35 | 2022-07-06 17:00 | 2022-07-06 11:20 |  |  | Cleared blockage using plunger
MSA-DFES | WA5572535 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Gym located in engine bay - Circuit breaker gone - lights are on but no electricity | Electrical | General Electrical | 100.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-30 08:15 | 2022-07-01 17:00 | 2022-06-30 10:00 | 2022-07-01 17:00 | 2022-06-30 10:45 |  |  | Arrived on site at 10:00 to investigate gym power points tripped and unable to reset. Found that gym circuit had tripped, old style rcd was able to reset by pushing off first. Tested circuit all okay. Left site at 10:45
MSA-DFES | WA5574118 | 1 | Go Doors | Engine Room - Rear door - Door 6 - Motor is struggling to pull door up - wobbling around | Building | Automatic Doors | 435 | Pass | Pass | 0 | 0 | 0.75 | 2022-06-30 15:02 | 2022-07-01 17:00 | 2022-07-01 14:30 | 2022-07-01 17:00 | 2022-07-01 15:15 |  |  | Completed. Please see attachments.
MSA-DTWD | WA5583205 | 3 | AWB Co. | 2 x lights out | Electrical | Lighting, Internal | 122.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-04 11:00 | 2022-07-11 17:00 | 2022-07-08 13:15 | 2022-07-11 17:00 | 2022-07-08 14:00 |  |  | Attended site and signed in. Completed JSA. Located faulty lights in lunch room. Replace lamps and starters with site supplied stock. Tested all okay. Signed out. Job complete
MSA-DFES | WA5584280 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | 2nd floor female toilets, pipes leaking under sink | Plumbing & Drainage | Water | 145.8825 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-05 08:10 | 2022-07-06 17:00 | 2022-07-05 11:00 | 2022-07-06 17:00 | 2022-07-05 11:45 |  |  | I have replaced the ring Nut For the plug and waste as it was leaking from there after I’ve tested and everything is working correctly
MSA-DTWD | WA5584811 | 2 | AWB Co. | Require a 3 Phase oven to be disconnected & wiring to be safely terminated. | Electrical | General Electrical | 113.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-05 10:33 | 2022-07-08 17:00 | 2022-07-06 14:00 | 2022-07-08 17:00 | 2022-07-06 14:45 |  |  | Attended site and signed in, completed jsa, spoke with fm about job, fm wanted oven disconnected, isolated circuit and removed oven circuit, coiled up cable , re energised circuit, completed paperwork, signed out **job completed**
MSA-DFES | WA5584859 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Meeting Room 2 - light switch in meeting room 2 is broken and cannot be turned off | Electrical | Lighting, Internal | 142.125 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-05 10:50 | 2022-07-08 17:00 | 2022-07-05 13:00 | 2022-07-08 17:00 | 2022-07-05 13:45 |  |  | Arrived onsite at 13:00 to investigate light switch not working located meeting room 2. Found meeting room 2 onsite and located faulty switch. Switch was pushed into wall and broken mechanically. Isolated power and replace switch. Renegerised and tested lights. Notified site of works completed and left site at 13:45
MSA-DFES | WA5585313 | 0 | Protek 24/7 Building & Maintenance | PPC storre, admin buiding door handle has snapped pff | Building | Doors | 126.125 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-05 14:35 | 2022-07-05 16:35 | 2022-07-05 14:45 | 2022-07-05 18:35 | 2022-07-05 15:30 |  |  | replace broken door handle
MSA-DFES | WA5585366 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Volunteer Association Office - Store room - see notes below | Electrical | Lighting, Internal | 164.855 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-05 15:29 | 2022-07-12 17:00 | 2022-07-06 14:30 | 2022-07-12 17:00 | 2022-07-06 15:15 |  |  | Arrived on site at 14:30. Went to volunteer office and located blown fluros in store room, replaced 4 x 36w tubes, 4 x s10 starters and cleaned lights diffusers. Left site at 15:15
MSA-DTAG | WA5585392 | 3 | AWB Co. | Magistrates Chamber’s 1 and 2 - Fluro light not working & Exit sign not working | Electrical | Lighting, Internal | 223.6075 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-05 16:01 | 2022-07-12 17:00 | 2022-07-08 15:30 | 2022-07-12 17:00 | 2022-07-08 16:15 |  |  | Attended site and signed in. Completed JSA. Located faulty lights not working in hallway. Supply and replace lamps to hallway light. Supply and replace exit sign to hallway. Tested all okay. Signed out. Job complete
MSA-DFES | WA5585770 | 1 | Securex Security Systems & Services | ground alarm system, has gone off again please investigate issues | Security | Security Management System | 667.27 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-06 08:11 | 2022-07-07 17:00 | 2022-07-06 10:30 | 2022-07-07 17:00 | 2022-07-06 11:15 |  |  | 06/07/2022, 1030-1115Replaced keypad(RAS) at garage entry door.Replaced back up battery.
MSA-DCA | WA5585990 | 3 | GPS Plumbing & Gas Services PtyLtd | Disabled toilet flush button has detached. | Plumbing & Drainage | Toilets/Cisterns | 150.6875 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-06 09:24 | 2022-07-13 17:00 | 2022-07-08 10:42 | 2022-07-13 17:00 | 2022-07-08 11:27 |  |  | Replaced flush buttons to ground floor disabled toilet
MSA-DTAG | WA5586012 | 1 | Bullant Security Pty Ltd | Ground - Court of Appeal Registry/Lobby - Lock for registry door is broken - see notes below | Security | Locksmith | 185 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-06 09:55 | 2022-07-07 17:00 | 2022-07-07 11:15 | 2022-07-07 17:00 | 2022-07-07 12:00 |  |  | Attend site pull lock of the door, service and lubricate lock so key operates lock correctly.Date on site: 07/07/2022Time on site: 11:15am - 12:00pm
MSA-DCA | WA5586191 | 1 | GPS Plumbing & Gas Services PtyLtd | Panel in male toilet has come off-check urinal pipe work is still intact and replace panel | Plumbing & Drainage | Toilets/Cisterns | 119.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-06 11:12 | 2022-07-07 17:00 | 2022-07-06 12:25 | 2022-07-07 17:00 | 2022-07-06 13:10 |  |  | Panel to urinal has fallen off.New panel required.Advised programmed they will send a cabinet fitter.
MSA-DFES | WA5587877 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | ground engine room-Pump charger cable broken | Electrical | General Electrical | 100.095 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-07 11:25 | 2022-07-08 17:00 | 2022-07-07 12:00 | 2022-07-08 17:00 | 2022-07-07 12:45 |  |  | Arrived onsite at 12:00 to investigate damaged ELV male plug for vehicle charging. Found cable had been damaged and had exposed cabling. Reterminated cable into ELV plug and tested for correct voltage. Notified staff of works and left site at 12:45
MSA-DTWD | WA5588364 | 2 | Complete Pest Management Services | Mouse Droppings | Pest Control | General Pest | 271.55 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-07 15:13 | 2022-07-12 17:00 | 2022-07-08 11:00 | 2022-07-12 17:00 | 2022-07-08 11:45 |  |  | Inspected room 8g3 for rodent activity found minimal rodent droppingsPlace rodent bait stations for rodent control
MSA-DTAG | WA5596642 | 1 | AWB Co. | Custody - Cell 2 - Flickering Light - | Electrical | Lighting, Internal | 136.8775 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-11 09:36 | 2022-07-12 17:00 | 2022-07-12 07:30 | 2022-07-12 17:00 | 2022-07-12 08:15 |  |  | Attended site and signed in. Completed JSA. Got escorted to cell 2. Found the light flickering away. Supply and replaced tubes and starters the light fitting and resecured the cover. Tested all okay. Signed out. Job complete
MSA-DCA | WA5627972 | 1 | Protek 24/7 Building & Maintenance | First Floor - Two offices facing rear Maritime Archaeology stairs- Water coming in through window | Building | Windows | 161.51 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-15 09:44 | 2022-07-18 17:00 | 2022-07-15 13:30 | 2022-07-18 17:00 | 2022-07-15 14:15 |  |  | Repair water leak
MSA-DCA | WA5635639 | 0 | TK Elevator Australia Pty Ltd | Lift #7 - not working | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.75 | 2022-07-16 09:13 | 2022-07-17 09:13 | 2022-07-16 11:45 | 2022-07-17 09:13 | 2022-07-16 12:30 |  |  | Green Rm-Hydraulic :Lift was out of service at bottom floor level with TTElap fault indicated on controller display. Reset by use of inspection buttons and lift reset and started operating correctly. Checked times between all travels up/down and checked against all timing parameters and all is setup ok. Could not get lift to reproduce the fault.Ran lift constantly for 45 minutes and left lift in service.to be closed out at $0 cost
MSA-DCA | WA5656575 | 3 | Protek 24/7 Building & Maintenance | Assembly Room - Concertina door broken | Building | Doors | 101.695 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-18 14:53 | 2022-07-25 17:00 | 2022-07-19 09:45 | 2022-07-25 17:00 | 2022-07-19 10:30 |  |  | attended site door had been fixed by staff
MSA-DTWD | WA5660498 | 0 | AWB Co. | Rooms B204, B205, B206 - overhead data projectors not working - power issue | Electrical | General Electrical | 122.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-19 10:08 | 2022-07-19 12:08 | 2022-07-19 10:30 | 2022-07-19 14:08 | 2022-07-19 11:15 |  |  | Attended site and signed in. Completed JSA. Located rooms with projectors not working. Pressed buttons on wall controllers and nothing happened. Tested for power and found to be dead. Checked out switchboard and all power was on. Went into each room and found power isolators for the projectors on the wall next to the light switches, lifted up cover to find isolator off. All isolators must be on for the projectors to work. Switched on and tested all projectors to be working. Notified Steve. Signed out. Job complete
MSA-DTWD | WA5671736 | 2 | ADVANCED LOCK & KEY | faulty lock | Security | Locksmith | 449.75 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-20 09:05 | 2022-07-25 17:00 | 2022-07-21 10:15 | 2022-07-25 17:00 | 2022-07-21 11:00 |  |  | Attend site to replace damaged lock on G103 storeroom
MSA-DTWD | WA5674202 | 2 | BJ SYSTEMS | PIR not working Zone 20 | Security | Security Management System | 172.05 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-21 09:38 | 2022-07-26 17:00 | 2022-07-22 13:00 | 2022-07-26 17:00 | 2022-07-22 13:45 |  |  | PIR false alarms reported. Replaced PIR sensor part. Cleaned spiders and webs. Walk tested, ok
MSA-DFES | WA5674465 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Training Room - Light fitting hanging down from the ceiling in training room. | Electrical | Lighting, Internal | 165.405 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-21 12:03 | 2022-07-26 17:00 | 2022-07-25 10:45 | 2022-07-26 17:00 | 2022-07-25 11:30 |  |  | Arrived on site at 10:45. Located light in volunteers hanging down from ceiling. Resecured light and left site at 11:30No signature available as officers left site.
MSA-DTWD | WA5674846 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 2 - S209/S210 - Faulty pump - see notes below | Plumbing & Drainage | Water | 115.4325 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-21 14:34 | 2022-07-22 17:00 | 2022-07-21 16:15 | 2022-07-22 17:00 | 2022-07-21 17:00 |  |  | pump float needed to be realigned.
MSA-DFES | WA5675242 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Dorm 1 & Dorm hallway - Electrical Issues - See notes below | Electrical | General Electrical | 203.205 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-22 09:01 | 2022-07-29 17:00 | 2022-07-29 13:00 | 2022-07-29 17:00 | 2022-07-29 13:45 |  |  | Arrived on site at 13:00. Was shown light switch in dorm 1 that has been arching, replaced with new 10a switch mech. Power point in hallway is intermittently working and loose when plug in, replaced with new single gpo and tested all okay. Left site at 13:45.
MSA-DTWD | WA5675278 | 1 | AWB Co. | faulty 10amp GPO | Electrical | General Electrical | 222.64 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-22 09:19 | 2022-07-25 17:00 | 2022-07-25 12:00 | 2022-07-25 17:00 | 2022-07-25 12:45 |  |  | Attended site and signed in. Completed JSA. Spoke to fm. Located faulty gpo. De energised circuit. Replaced gpo.had to drill out bigger hole for back of new gpo to fit. Reenergised circuit. Tested. Working as intended. Cleaned up. Completed paperwork. Signed outJob complete
MSA-DFES | WA5675391 | 3 | SONTEC WA PTY LTD | Level 1 - Server Room - CCTV Has a blank screen - chased back to power box - See notes below | Security | CCTV Surveillance | 270 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-22 10:07 | 2022-07-29 17:00 | 2022-07-25 10:00 | 2022-07-29 17:00 | 2022-07-25 10:45 |  |  | 25/7/22 - Dean SimpsonTested voltage all ok but no voltage to cameras.Found fuse had blown, replaced and tested all ok.
MSA-DFES | WA5675398 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Engine Bay -Tube Light underneath the light tanker is flickering - See notes below | Electrical | Lighting, Internal | 244.125 | Fail | Fail | 0 | 0 | 0.75 | 2022-07-22 10:20 | 2022-07-27 17:00 | 2022-07-28 14:45 | 2022-07-27 17:00 | 2022-07-28 15:30 |  |  | Arrived on site at 14:45. Was shown 2 x engine bay lights with blown and flickering tubes, replaced tubes and starters in both and tested all okay. Left site at 15:30
MSA-DFES | WA5677398 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Stores - Fluro light needing to be reattached to the racking. | Electrical | Lighting, Internal | 113.215 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-25 14:21 | 2022-07-26 17:00 | 2022-07-26 12:30 | 2022-07-26 17:00 | 2022-07-26 13:15 |  |  | Arrived on site at 12:30. Went to store area and located light hanging from racking after being hit, resecured fitting with metal plate and screws to prevent further damage. Left site at 13:15
MSA-DTWD | WA5677835 | 2 | PEEL LOCK SERVICES PTY LTD | Cupboard Lock needs repair | Security | Locksmith |  | Fail | Fail | 0 | 0 | 0.75 | 2022-07-26 07:49 | 2022-07-28 17:00 | 2022-07-29 10:45 | 2022-07-28 17:00 | 2022-07-29 11:30 |  |  | Repairs to lock
MSA-DTWD | WA5677840 | 2 | PEEL LOCK SERVICES PTY LTD | Door Lock needs repair | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-07-26 07:52 | 2022-07-28 17:00 | 2022-07-28 11:25 | 2022-07-28 17:00 | 2022-07-28 12:10 |  |  | Job completed - replaced lock
MSA-DTWD | WA5677936 | 2 | ADVANCED LOCK & KEY | Digital door lock not working | Security | Locksmith | 512.5 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-26 08:33 | 2022-07-29 17:00 | 2022-07-28 12:30 | 2022-07-29 17:00 | 2022-07-28 13:15 |  |  | Replace digital key pad
MSA-DCA | WA5680539 | 3 | Protek 24/7 Building & Maintenance | Window frame grip/handle has come of the frame | Building | Windows | 204.98 | Pass | Pass | -1 | -1 | 0.75 | 2022-07-27 13:00 | 2022-08-03 17:00 | 2022-07-29 11:00 | 2022-08-03 17:00 | 2022-07-29 11:45 |  |  | repaired handle
MSA-DFES | WA5681339 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Admin Building - Ground Floor - Electrical Issue - See notes be,ow | Electrical | General Electrical | 119.815 | Pass | Pass | 0 | 0 | 0.75 | 2022-07-28 11:18 | 2022-07-29 17:00 | 2022-07-28 12:45 | 2022-07-29 17:00 | 2022-07-28 13:30 |  |  | complete
MSA-DTWD | WA5686913 | 3 | AWB Co. | 2x classroom lights to be fixed | Electrical | Lighting, Internal | 122.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-01 11:41 | 2022-08-08 17:00 | 2022-08-08 14:45 | 2022-08-08 17:00 | 2022-08-08 15:30 |  |  | Attended site and signed in. Completed JSA. Located faulty lights. Used site supplied lamps to replace lights. tested all okay. Signed out. Job complete
MSA-DTWD | WA5687198 | 2 | Protek 24/7 Building & Maintenance | External Undercover area just outside café dining bi-fold doors - Roof Leak - See notes below | Roofing | Metal Roofing | 163.66 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-01 14:05 | 2022-08-04 17:00 | 2022-08-02 12:45 | 2022-08-04 17:00 | 2022-08-02 13:30 |  |  | Action taken: Removed all the leaves that had caused the blockage of the box gutter and down pipePrimary cause of failure: Poor or infrequent routine maintenanceBraf Declined
MSA-DTWD | WA5687354 | 2 | Milners Tree Solutions Pty Ltd | Herb Garden between E75 & E29 - Ponytail palm is rotting and dropping heavy branches- See notes | Landscaping & Gardening | Tree Lopping | 525 | Fail | Fail | 0 | 0 | 0.75 | 2022-08-01 16:51 | 2022-08-04 17:00 | 2022-08-06 08:40 | 2022-08-04 17:00 | 2022-08-06 09:25 |  |  | tree pruned
MSA-DTWD | WA5687846 | 2 | Falcetta Plumbing and Gas | CG47A - Centre cubicle is intermittently filling. It also leaks from the cistern. | Plumbing & Drainage | Toilets/Cisterns |  | Fail | Fail | 1 | 1 | 0.75 | 2022-08-02 07:47 | 2022-08-04 17:00 | 2022-08-12 12:00 | 2022-08-04 17:00 | 2022-08-12 12:45 |  |  | repaired cistern and adjusted 2 others
MSA-DFES | WA5691779 | 1 | Protek 24/7 Building & Maintenance | Back of the station - Fencing panels has blown down | Security | Security Management System | 189.25 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-03 07:24 | 2022-08-03 17:00 | 2022-08-03 15:00 | 2022-08-03 17:00 | 2022-08-03 15:45 |  |  | Secured fence panel with new fixings
MSA-DTWD | WA5691890 | 1 | AWB Co. | Ground Floor - The flats area - Lights Flickering - Near Main Entrance | Electrical | Lighting, Internal | 177.13 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-03 08:49 | 2022-08-04 17:00 | 2022-08-03 12:00 | 2022-08-04 17:00 | 2022-08-03 12:45 |  |  | Attended site and signed in. Completed JSA. located faulty light fitting. Replaced tubes and starters. Took picture. Completed paperwork. Signed out.Job complete
MSA-DFES | WA5692165 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Retrospective Work Order- Kitchen - Hot water unit is not functioning - Billie Unit under sink | Plumbing & Drainage | HWS/Units Electric & Gas | 118.26 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-02 11:00 | 2022-08-03 17:00 | 2022-08-03 07:45 | 2022-08-03 17:00 | 2022-08-03 08:30 | 1 |  | Inspecting the Billi Quadra unit in the kitchen. It worked good for a while, no faults showing on the display. Boiling water started to slow down after a while, even if water is not being used before for fewminutes. Staff mentioned that same issue is reappearing from time to time.I found a service log from Water2water technician. Called call center to organise them to attend.
MSA-DFES | WA5692506 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | kitchen faucet is popping out needs to be fixed | Plumbing & Drainage | Water | 141.03 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-03 13:56 | 2022-08-04 17:00 | 2022-08-04 07:45 | 2022-08-04 17:00 | 2022-08-04 08:30 |  |  | Replaced broken spout
MSA-DFES | WA5693006 | 0 | Seme Solutions Pty Ltd | alarm system multiple locations low battery alarm-error as battery was replaced 2 weeks ago | Security | Security Management System | 97.5 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-04 08:45 | 2022-08-04 10:45 | 2022-08-04 09:45 | 2022-08-04 12:45 | 2022-08-04 10:30 |  |  | Faulty battery charge circuit on the V8 Challenger PCB will organise a quote to have the system upgraded
MSA-DFES | WA5693206 | 0 | Go Doors | rear of the station has damaged security electronic gate | Building | Steel Fencing & Gates | 310 | Fail | Fail | 0 | 0 | 0.75 | 2022-08-04 10:21 | 2022-08-04 12:21 | 2022-08-04 16:00 | 2022-08-04 14:21 | 2022-08-04 16:45 |  |  | Completed works. Please see attachments.
MSA-DFES | WA5694145 | 3 | Critical Fire Protection & Training | Costume Store Room – Fire Panel Location - Fault with alarm bell - See notes below | Fire Protection Services | Fire Protection - Monitor System | 75.975 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-05 08:22 | 2022-08-12 17:00 | 2022-08-09 14:00 | 2022-08-12 17:00 | 2022-08-09 14:45 |  |  | Attended site to investigate fault to fire panel, on arrival found fire panel operating all systems as normal with no faults to rectify. After viewing history log found intermittent fault on brigade card present.If the fault appears again, a photo of the fault and further investigation will be required as it is intermittent.Also due to power outage, the fire panel date is reading incorrect (2008 instead of 2022). This has been reprogrammed to be reading the correct date and time.All systems operating as intended on departure with no faults isolates or alarms present.
MSA-DTWD | WA5694367 | 2 | AWB Co. | Library - PC network wall port - damaged, need to be fixed | Electrical | General Electrical | 126.1575 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-05 09:36 | 2022-08-10 17:00 | 2022-08-10 13:15 | 2022-08-10 17:00 | 2022-08-10 14:00 |  |  | Job complete
MSA-DFES | WA5694786 | 1 | Securex Security Systems & Services | Rear Gate - Key pads aren't working | Security | Access Control | 190 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-05 13:22 | 2022-08-08 17:00 | 2022-08-05 15:15 | 2022-08-08 17:00 | 2022-08-05 16:00 |  |  | 05/08/2022, 1515-1600Found water damaged wires in pit next to side gate. Pit is obviously getting full of water and cables sitting below waterline until water subsides. Joined broken cables and gate operating.
MSA-DTWD | WA5696765 | 2 | AWB Co. | Library - Replace flickering light in the Library | Electrical | Lighting, Internal | 122.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-08 14:24 | 2022-08-11 17:00 | 2022-08-10 14:00 | 2022-08-11 17:00 | 2022-08-10 14:45 |  |  | NA
MSA-DTWD | WA5696893 | 2 | AWB Co. | ET10 Corridor - Faulty Light Fitting - See notes below | Electrical | Lighting, Internal | 176.81 | Fail | Fail | 1 | 1 | 0.75 | 2022-08-08 16:59 | 2022-08-11 17:00 | 2022-08-16 14:00 | 2022-08-11 17:00 | 2022-08-16 14:45 |  |  | Attended site and signed in. Completed JSA. Replaced faulty tubes and starters. Working as should. Completed paperwork. Signed out. Job complete
MSA-DTWD | WA5697380 | 2 | AWB Co. | ground south entry-2 Emergency exit lights not working / Globes | Electrical | Lighting, Internal | 122.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-09 08:58 | 2022-08-12 17:00 | 2022-08-11 15:30 | 2022-08-12 17:00 | 2022-08-11 16:15 |  |  | Attended site and signed in. Completed JSA. Located D block and found the 2 x exit lights. Tried to change the lamps as asked but the fittings are LED. Checked and found no power. Inspected switchboard and found 2 x circuits switched off. No tag or reason why. Reinstated power to the exit signs and hallway lights. Tested all okay. Signed out. Job complete
MSA-DCA | WA5698231 | 1 | Protek 24/7 Building & Maintenance | Level 1 - Supervisors Office- Door is faulty - See notes below | Building | Doors | 217.76 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-09 15:54 | 2022-08-10 17:00 | 2022-08-10 13:45 | 2022-08-10 17:00 | 2022-08-10 14:30 |  |  | Installed vent back into door and secured with screws on both sides
MSA-DTWD | WA5699325 | 3 | Protek 24/7 Building & Maintenance | AF11 - Grill has fallen from roof apex. Access via roof | Building | Ceiling | 161.51 | Pass | Pass | -1 | -1 | 0.75 | 2022-08-10 08:38 | 2022-08-17 17:00 | 2022-08-12 12:15 | 2022-08-17 17:00 | 2022-08-12 13:00 |  |  | CLOSING OFF TASK - REPAIRS / REPLACEMENTS WILL BE CARRIED OUT UNDER JN20408(BRAF)INVOICE FOR 1st ATTENDANCE + CALL OUT
MSA-DCA | WA5722510 | 0 | Automatic Fire Protection (ARA) | Level 4 Plant room - Alarm is going off | Fire Protection Services | Smoke and Heat Detection | 630.28 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-13 09:11 | 2022-08-13 11:11 | 2022-08-13 10:00 | 2022-08-13 13:11 | 2022-08-13 10:45 |  |  | Issue not fire related. Security asked for aircon contractor, however, programmed call centre engaged fire contractor.
MSA-DTWD | WA5727835 | 0 | ADVANCED LOCK & KEY | Door locks broken - unable to lock | Security | Locksmith | 418.85 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-15 12:27 | 2022-08-15 14:27 | 2022-08-15 12:50 | 2022-08-15 16:27 | 2022-08-15 13:35 |  |  | removed stuck key & replaced mortice lock, cut replacement key.
MSA-DTWD | WA5727983 | 1 | SENTINEL LOCK SERVICE PTY LTD | Block 3 - Ground - 3E9 office - Door lock handle fallen off jamming lock | Security | Locksmith | 114.85 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-15 13:32 | 2022-08-16 17:00 | 2022-08-15 15:00 | 2022-08-16 17:00 | 2022-08-15 15:45 |  |  | 3E9 - Door handle has fallen off jamming lock.Lock repaired.
MSA-DFES | WA5753172 | 3 | Complete Pest Management Services | Ground Floor - Administration - Records Room Store Room #8 - bad smell, possible dead rodent in roof | Pest Control | General Pest | 186.57 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-17 14:18 | 2022-08-24 17:00 | 2022-08-23 14:45 | 2022-08-24 17:00 | 2022-08-23 15:30 |  |  | Inspected Ground Floor - Administration - Records Room Store Room #8 for badsmell.No odour permeating from ceiling void.No rodent activity evident inside storeroom.Applied deodorisers inside Storeroom 8 including space spray and 1 deodorisergel pot.
MSA-DTWD | WA5753211 | 3 | AWB Co. | 1 x Light out over hand wash area - E300 | Electrical | Lighting, Internal | 169.45 | Pass | Pass | -1 | -1 | 0.75 | 2022-08-17 14:50 | 2022-08-24 17:00 | 2022-08-18 13:15 | 2022-08-24 17:00 | 2022-08-18 14:00 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Located faulty lighting. Replaced tubes and starters. Took pictures. Completed paperwork. Signed out.Job complete
MSA-DCA | WA5753337 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Level1 - Exterior Flood Lights MM - Flood Lights not working | Electrical | Lighting, External | 110.2305 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-17 16:08 | 2022-08-18 17:00 | 2022-08-18 12:15 | 2022-08-18 17:00 | 2022-08-18 13:00 |  |  | Arrived on site at 12:15. To investigate external flood lights not working, 2 x flood lights mounted at 21ft heigh on outside landing top of stairs. Found that flood lights come on with override mounted in level 1 dB, faulty pe cell mounted at 6.3m already looked at under seperate job will need to be replaced. Advised staff and left site at 13:00
MSA-DFES | WA5761427 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | ground floor - Male change rooms - blocked toilet | Plumbing & Drainage | Water | 118.26 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-18 09:08 | 2022-08-19 17:00 | 2022-08-18 14:45 | 2022-08-19 17:00 | 2022-08-18 15:30 |  |  | Blocked pan cleared
MSA-DTAG | WA5781278 | 2 | Sapio Pty Ltd | Registry of Births Deaths and Marriages - Level 10 - Counter - Please see notes below | Security | Monitoring | 139.88 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-19 14:40 | 2022-08-24 17:00 | 2022-08-22 09:00 | 2022-08-24 17:00 | 2022-08-22 09:45 |  |  | Attended site. Found PA mixer was set quite high, adjusted to stop feed back. Job completed.
MSA-MRWA | WA5790915 | 2 | AWB Co. | Level 2 - Kitchen - Double light switch in Kitchenette Broken | Electrical | General Electrical | 182.45 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-22 13:26 | 2022-08-25 17:00 | 2022-08-24 06:00 | 2022-08-25 17:00 | 2022-08-24 06:45 |  |  | Attended site and signed in, completed jsa, located switch on level2 ,found switch was damaged/faulty, isolated circuit, removed switch, installed new switch, re energised circuit, tested lights , lights working as intended,signed out **job complete**
MSA-DCA | WA5792422 | 1 | Protek 24/7 Building & Maintenance | Venue Management Office-Fault description External Door Handle Broken-see notes | Building | Doors | 133.01 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-23 13:59 | 2022-08-24 17:00 | 2022-08-24 12:30 | 2022-08-24 17:00 | 2022-08-24 13:15 |  |  | Removed door handle assembly, lubricated with nylon based lubricant, repaired door hinge pin , re assembled lock and handle set to door , test operation, all ok
MSA-DTAG | WA5792443 | 3 | Seme Solutions Pty Ltd | CCTV1 (49) Magistrates parking not working | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-23 14:20 | 2022-08-30 17:00 | 2022-08-29 10:00 | 2022-08-30 17:00 | 2022-08-29 10:45 |  |  | Inspected camera on software - offline on CCTV 1.Inspected magistrates parking, 3 cameras total.Located a magistrates parking camera on CCTV 2 - (53) Magistrates Parking.
MSA-DTAG | WA5792445 | 3 | Seme Solutions Pty Ltd | CCTV2 (45) Other building front desk Not working | Security | CCTV Surveillance | 139.88 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-23 14:21 | 2022-08-30 17:00 | 2022-08-29 10:45 | 2022-08-30 17:00 | 2022-08-29 11:30 |  |  | Tested cam cable labelled 'other building' in ground floor comms - no image.Attended CJS site, now has standalone camera system on site - camera has been physically removed.
MSA-DTAG | WA5792464 | 3 | Seme Solutions Pty Ltd | CCTV2 (51) Sally port (5) Not working | Security | CCTV Surveillance | 279.76 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-23 14:33 | 2022-08-30 17:00 | 2022-08-29 15:15 | 2022-08-30 17:00 | 2022-08-29 16:00 |  | WCAPPR | To be removed from system as per Anne-Marie's request on job WA5792446.
MSA-DTWD | WA5794757 | 1 | ADVANCED LOCK & KEY | Door lock cannot be opened | Security | Locksmith | 172.5 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-25 07:49 | 2022-08-25 17:00 | 2022-08-25 10:15 | 2022-08-25 17:00 | 2022-08-25 11:00 |  |  | moved strike on a337 as dead latching trigger was falling into strike hole if the door was slightly slammed causing it to be hard to open
MSA-DTAG | WA5795013 | 1 | AWB Co. | Magistrate Chamber One - Flickering Light | Electrical | Lighting, Internal | 125.6675 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-25 09:17 | 2022-08-26 17:00 | 2022-08-25 14:30 | 2022-08-26 17:00 | 2022-08-25 15:15 |  |  | Attended site and signed in. Completed JSA. Located magistrates chambers and found light out. Supply and replaced tube and starter to light fitting. Tested all okay. Signed out. Job complete
MSA-DTWD | WA5799072 | 2 | AWB Co. | Faulty lights | Electrical | Lighting, Internal | 176.0425 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-30 09:24 | 2022-09-02 17:00 | 2022-08-30 14:30 | 2022-09-02 17:00 | 2022-08-30 15:15 |  |  | Attended site and signed in. Completed JSA. Liaised with site about works going ahead. Located room with faulty lights. Set up work area. Isolated circuit. Replaced multiple lamps as requested by site. Energised and tested. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DFES | WA5799637 | 2 | Protek 24/7 Building & Maintenance | meeting room 5 2nd floor-door handle is coming loose | Building | Doors | 108.01 | Pass | Pass | 0 | 0 | 0.75 | 2022-08-30 13:17 | 2022-09-02 17:00 | 2022-09-01 10:15 | 2022-09-02 17:00 | 2022-09-01 11:00 |  |  | Re secured door handle assembly to door . Filed back door striker plate to allow striker to engage door frame
MSA-DTAG | WA5800555 | 2 | Midolo Building Services | Ground Floor - Magistrate Dewsbury chambers - Door is broken | Building | Doors | 132.42 | Pass | Pass | -1 | -1 | 0.75 | 2022-08-31 10:52 | 2022-09-05 17:00 | 2022-09-01 13:45 | 2022-09-05 17:00 | 2022-09-01 14:30 |  |  | REPAIRS TO DOOR SEAL COMPLETED
MSA-DTWD | WA5827168 | 1 | AWB Co. | Level 1 main corridor next to T118 - Ceiling light need isolation due to water leak in ceiling space | Electrical | Lighting, Internal | 176.0425 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-01 08:40 | 2022-09-02 17:00 | 2022-09-01 11:45 | 2022-09-02 17:00 | 2022-09-01 12:30 |  |  | Attended site and signed in, completed jsa, spoke with fm about job,located light fitting and unplugged in roof space, liaised with fm to raise another job once leak has been rectified, light fitting now safe, completed paperwork,packed up, signed out **job complete**
MSA-DFES | WA5832070 | 3 | Protek 24/7 Building & Maintenance | Ground Floor Door - Foyer/to Mail Room - Door is getting jammed/stuck on frame | Building | Doors | 108.01 | Pass | Pass | -1 | -1 | 0.75 | 2022-09-05 10:51 | 2022-09-12 17:00 | 2022-09-05 12:30 | 2022-09-12 17:00 | 2022-09-05 13:15 |  |  | Adjusted door closer
MSA-DTWD | WA5832652 | 3 | COMMERCIAL PLUMBING AND GAS | Ladies toilet cistern running - L1 | Plumbing & Drainage | Toilets/Cisterns | 101.3575 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-05 14:39 | 2022-09-12 17:00 | 2022-09-09 13:15 | 2022-09-12 17:00 | 2022-09-09 14:00 |  |  | checked cisterns and adjusted fill volume
MSA-DTWD | WA5832751 | 2 | AWB Co. | 2 faulty lights in foyer/reception area | Electrical | Lighting, Internal | 188.8025 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-05 16:11 | 2022-09-08 17:00 | 2022-09-08 15:15 | 2022-09-08 17:00 | 2022-09-08 16:00 |  |  | Attended site and signed in. Completed JSA. Liaised with site going ahead. Located various lights out. Went and replaced fluros as directed by site. Packed up site. Notified relevant personnel of works completed. **job complete**
MSA-DTAG | WA5834096 | 1 | Bullant Security Pty Ltd | Legal assistance wing - Door 6 - Door lock won’t lock to office with door key 6 | Security | Locksmith | 185 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-06 13:30 | 2022-09-07 17:00 | 2022-09-07 12:00 | 2022-09-07 17:00 | 2022-09-07 12:45 |  |  | Attend site remove lock from door, pull apart lock, clean and lubricate internal mechanism so lock functions correctly.Date on site: 07/09/2022Time on site: 12:00pm - 12:45pm
MSA-DTWD | WA5834369 | 2 | AWB Co. | Glass House - Faulty GPO | Electrical | General Electrical | 223.015 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-06 15:40 | 2022-09-09 17:00 | 2022-09-09 14:45 | 2022-09-09 17:00 | 2022-09-09 15:30 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Was asked to investigate to see if power was in glass house PowerPoints. Figured there was power there however had been disconnected as it is not safe. Sprinklers in glass house, therefore not suitable for re energising as it is unsafe. Told fm and he is happy. Completed paperwork signed out.Job complete
MSA-DTWD | WA5836893 | 3 | Water2water Pty Ltd | Faulty filter - water fountains | Plumbing & Drainage | Water | 360.635 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-07 15:41 | 2022-09-14 17:00 | 2022-09-12 13:50 | 2022-09-14 17:00 | 2022-09-12 14:35 |  |  | Installed maxiflow system to original systems in place. Sanitation also complete
MSA-DFES | WA5839242 | 2 | Protek 24/7 Building & Maintenance | Damaged downpipe near door at rear of engine bay - come away from the wall | Roofing | Guttering | 179.04 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-09 10:39 | 2022-09-14 17:00 | 2022-09-13 07:00 | 2022-09-14 17:00 | 2022-09-13 07:45 |  |  | Re fix D/P section to existing D/P
MSA-DTAG | WA5839425 | 3 | Midolo Building Services | Court room 51 - Set of 3 chairs in gallery broken | Furniture | Indoor Furniture | 132.42 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-09 12:13 | 2022-09-16 17:00 | 2022-09-14 07:00 | 2022-09-16 17:00 | 2022-09-14 07:45 |  |  | secured chairs with new fixings
MSA-DCA | WA5853322 | 0 | Automatic Fire Protection (ARA) | fire panel, adjust lift riser L1 and L5 | Fire Protection Services | Fire Protection - Monitor System | 447.395 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-12 08:01 | 2022-09-12 10:01 | 2022-09-12 09:15 | 2022-09-12 12:01 | 2022-09-12 10:00 |  |  | Attended site and found level 1 Riser Adjacent Lift device 1005 Az 1 in maintenance fault.Device had AV 5 faulty access and fitted new detector reset and left normal.
MSA-DTWD | WA5861700 | 2 | SENTINEL LOCK SERVICE PTY LTD | Mail Room 1G29A - Lock will not operate from either side | Security | Locksmith | 101.47 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-13 10:43 | 2022-09-16 17:00 | 2022-09-14 09:45 | 2022-09-16 17:00 | 2022-09-14 10:30 |  |  | MAIL ROOM - 1G29A - lock faulty.Lock repaired.
MSA-DCA | WA5862238 | 1 | Protek 24/7 Building & Maintenance | Accessible Toilet Door Not Closing properly due to alignment issues. | Building | Doors | 102.83 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-13 14:59 | 2022-09-14 17:00 | 2022-09-14 09:30 | 2022-09-14 17:00 | 2022-09-14 10:15 |  |  | Adjusted loose screws
MSA-DTWD | WA5865458 | 2 | Protek 24/7 Building & Maintenance | The door swings loose both ways when unlocked. No Closer. please see notes below | Building | Doors | 1422.815 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-14 07:37 | 2022-09-16 17:00 | 2022-09-14 14:15 | 2022-09-16 17:00 | 2022-09-14 15:00 |  | WACCES | Change over transom closer and install plant on door stopsFor one way operation
MSA-DCA | WA5866199 | 2 | Protek 24/7 Building & Maintenance | Internal doors of Stairwell do not close (do not firmly shut and stay closed-see notes | Building | Doors | 102.83 | Pass | Pass | -1 | -1 | 0.75 | 2022-09-14 08:19 | 2022-09-19 17:00 | 2022-09-14 10:15 | 2022-09-19 17:00 | 2022-09-14 11:00 |  |  | Maintenance issue
MSA-DCA | WA5869648 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Light above internal entrance door dripping water from rain - Make Safe - See notes below | Electrical | General Electrical | 107.715 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-14 15:33 | 2022-09-15 17:00 | 2022-09-14 16:15 | 2022-09-15 17:00 | 2022-09-14 17:00 |  |  | Attended site at 1615. Proceeded to investigate lighting fixture on top floor, reported as leaking water. Found that the light fixture was damp, however water was no longer dripping water. I have disconnected the fixture from the 413 that was supplying it, the 413 is hanging above the ceiling and did not show any presence of moisture. The lighting fixture has been made safe and tagged out of order, it will need to be either replaced or reconnected once a roof plumber has rectified the leaking roof. Informed staff of outcomes. Left site at 1700.
MSA-DTAG | WA5887701 | 2 | AHS Services WA Pty Ltd (Anchor) | Male toilets (Hay st end) - Blocked urinal | Plumbing & Drainage | Toilets/Cisterns | 115.4325 | Fail | Fail | 0 | 0 | 0.75 | 2022-09-16 09:16 | 2022-09-21 17:00 | 2022-09-23 09:15 | 2022-09-21 17:00 | 2022-09-23 10:00 |  |  | Tested multiple times with paper-all working fine
MSA-DTWD | WA5888336 | 3 | Water2water Pty Ltd | Staff Kitchen - Reception Area - Repair broken tap on instant hot water unit | Plumbing & Drainage | HWS/Units Electric & Gas | 298.545 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-16 15:58 | 2022-09-23 17:00 | 2022-09-20 10:45 | 2022-09-23 17:00 | 2022-09-20 11:30 |  |  | Replaced broken tap on zip hot water unit
MSA-DCA | WA5906469 | 1 | TK Elevator Australia Pty Ltd | Main lift is not working, currently stuck on ground level | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.75 | 2022-09-17 18:39 | 2022-09-18 18:39 | 2022-09-17 19:45 | 2022-09-18 18:39 | 2022-09-17 20:30 |  |  | Lift1 Main Foyer-Elevator > MRL > Gearless :Found error ttelap, runtime error this fault is intermittently appearing, left switched off as its likely to fault again possibly trapping someone. Switched of at main switch awaiting further investigation
MSA-DFES | WA5961684 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | female toilet - toilet seat will not stay up, requires cistern removal to adjust | Plumbing & Drainage | Toilets/Cisterns | 145.1475 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-19 09:17 | 2022-09-22 17:00 | 2022-09-21 13:00 | 2022-09-22 17:00 | 2022-09-21 13:45 |  |  | Arrived on site and singed in went to room 1 female toilets could see that the seat was loose had to tighten the nuts up tested everything and work fine
MSA-DFES | WA5971566 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | Engine room - all lights have blown - 6 x fluro - see notes below | Electrical | Lighting, Internal | 107.715 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-20 15:39 | 2022-09-21 17:00 | 2022-09-21 10:45 | 2022-09-21 17:00 | 2022-09-21 11:30 |  |  | Arrived on site at 10:45am to investigate 6x faulty lights in engine bay. Found all lights to be working normally with no evident fault. Checked circuit is working correctly. Let staff know and signed out at 11:30am.
MSA-DTAG | WA5971761 | 1 | Bullant Security Pty Ltd | Ground Floor - Reception Counter 6 - Locking mechanism not working, unable to lock cash drawer | Security | Locksmith | 185 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-20 15:54 | 2022-09-21 17:00 | 2022-09-21 11:00 | 2022-09-21 17:00 | 2022-09-21 11:45 |  |  | Attend site, repair lock to reception counter 6 cash draw for correct operation. Date on site: 21/09/2022 Time on site: 11:00 - 11:45
MSA-DFES | WA5974597 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Murray St Pedestrian Accessway - Murray St bollards wont go down - See notes below | Equipment | Electrical Equipment | 107.715 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-23 14:02 | 2022-09-29 17:00 | 2022-09-28 10:15 | 2022-09-29 17:00 | 2022-09-28 11:00 |  |  | Arrived on site at 1015 to investigate faulty bollard lights around site. Staff informed upon arrival that all bollards were now operating correctly. Assessed all bollards & relative compressor unit/conducted necessary tests. Discovered nothing of concern. Informed staff to report faulty immediately if issue occurs again. Left site at 1100.
MSA-DCA | WA5976405 | 0 | SCAVENGER SUPPLIES PTY LTD | Frances street LB2 fire pump room-in alarm | Fire Protection Services | Fire Protection - Monitor System | 233.545 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-27 09:16 | 2022-09-27 11:16 | 2022-09-27 10:00 | 2022-09-27 13:16 | 2022-09-27 10:45 |  |  | **WAITING ON SIGNED SIG SLIP FROM NEIL DUCHAN. UNSIGNED SLIP ATTACHED.
MSA-MRWA | WA5979185 | 0 | Automatic Fire Protection (ARA) | Building fire alarm activated inspect and reset as required | Fire Protection Services | Fire Protection - Monitor System | 630.28 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-29 03:28 | 2022-09-29 05:28 | 2022-09-29 04:00 | 2022-09-29 07:28 | 2022-09-29 04:45 |  |  | 29/9/22 CS Attended site, on arrival 4 faults on panel, Checking history level 5 male toilet airlock point 3.152.1 went into pre alarm then alarmat 3:46am, inspected detector and found no sign of damage or smoke, however a smell of dust. Note: workers on site on level 5 in area.Detector not displaying a dirty value, left detector as is. Potential cause could be a bit of dust from workers cleaning up in area triggeringdetector
MSA-DTAG | WA5982676 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 1 - Staff Female Toilets - Hot water tap leaks water around rim of tap when on | Plumbing & Drainage | Water | 116.6875 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-30 13:23 | 2022-10-05 17:00 | 2022-10-03 09:00 | 2022-10-05 17:00 | 2022-10-03 09:45 |  |  | Service leak hot tap in ladies
MSA-DTWD | WA5982736 | 0 | Casa Security Pty Ltd | Room 007 - Alarm panel not working correctly | Security | Monitoring | 460 | Fail | Pass | 0 | 0 | 0.75 | 2022-09-30 14:06 | 2022-09-30 16:06 | 2022-09-30 16:15 | 2022-09-30 18:06 | 2022-09-30 17:00 |  |  | ATTENDED SITE AS PER WORK ORDER WA5982736ZONE 53 - FAULTYCHECKED DEVICE/REPLACED BATTERIESZONE WOULD NOT RESTORERECOMMENDED DEVICE BE REPLACED - AUTHORISED BY SILVIOREPLACED AND RELOCATED WIRELESS SENSORTESTED - ALL OKSYSTEM RESTORED TO NORMAL
MSA-DTAG | WA5982798 | 3 | Complete Pest Management Services | Front Entrance - Bee hive needing removal | Pest Control | General Pest | 425.68 | Pass | Pass | 0 | 0 | 0.75 | 2022-09-30 14:37 | 2022-10-07 17:00 | 2022-10-06 06:30 | 2022-10-07 17:00 | 2022-10-06 07:15 |  |  | Inspected and treated for feral bees, also sealed up several holes in the top of the brick work that the bees wereusing to gain access to the building
MSA-DTAG | WA5987246 | 0 | Complete Pest Management Services | Adjacent to carpark entry - Bee hive attached to building - Needs to be removed | Pest Control | General Pest | 240.91 | Fail | Pass | 0 | 0 | 0.75 | 2022-10-03 09:29 | 2022-10-03 11:29 | 2022-10-03 12:15 | 2022-10-03 13:29 | 2022-10-03 13:00 |  |  | Treated bees entering into pit from holes in the side where damage has occurred and the lid lifting hole. Recommend all holes be sealed to prevent reoccurrence.
MSA-DTWD | WA5987305 | 1 | AWB Co. | No power to power points in Q012 | Electrical | General Electrical | 169.45 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-03 10:28 | 2022-10-04 17:00 | 2022-10-03 16:30 | 2022-10-04 17:00 | 2022-10-03 17:15 |  |  | Attended site and signed in. Completed jsa. Spoke to fm. Located room with tripped powerpoints. Went to board and found there was a out of service tag on 2 power circuits, rang contact on tag. He said facilities are aware of the works going on. Told fm and he said it’s okay there’s nothing we can do. Completed paperwork. Signed out.Job complete
MSA-DTAG | WA5994066 | 2 | Automatic Fire Protection (ARA) | Ground -Main control/Fire Panel - Vesda alert/fault - see notes below | Fire Protection Services | Fire Protection - Monitor System | 208.23 | Pass | Pass | -1 | -1 | 0.75 | 2022-10-05 13:01 | 2022-10-10 17:00 | 2022-10-06 11:45 | 2022-10-10 17:00 | 2022-10-06 12:30 |  |  | Vesda in alert on arrival. Currently no smoke/dust being detected. Reset.
MSA-DTWD | WA5994942 | 2 | AWB Co. | Toilet fan not working in male toilet | Building | General Building | 169.45 | Pass | Pass | -1 | -1 | 0.75 | 2022-10-06 09:29 | 2022-10-11 17:00 | 2022-10-07 14:15 | 2022-10-11 17:00 | 2022-10-07 15:00 |  |  | Attended site and signed in. Completed JSA. located exhaust fan not working. Went to board and found breaker had tripped. Reset timer and breaker. Exhaust fan now working as intended. Took pic of breaker. Completed paperwork. Signed out.Job complete
MSA-DTWD | WA5997501 | 2 | LIGHTHOUSE LOCKSMITHS | F001 - Replace worn keys in F block | Security | Keys & Access | 320 | Pass | Pass | -1 | -1 | 0.75 | 2022-10-07 07:00 | 2022-10-11 17:00 | 2022-10-07 10:40 | 2022-10-11 17:00 | 2022-10-07 11:25 |  |  | replaced worn keys for f block
MSA-DTWD | WA6007436 | 1 | Securex Security Systems & Services | Security panel-System ID 1520 Zoone 000 Low Battery Alarm-see notes | Security | Security Management System | 251.82 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-11 08:02 | 2022-10-12 17:00 | 2022-10-11 11:30 | 2022-10-12 17:00 | 2022-10-11 12:15 |  |  | 11/10/2022, 1130-1215Located panel and replaced battery. Found zone 16 also low battery, replaced too. So 12v7ah and one 123a battery.
MSA-DTWD | WA6007609 | 2 | AWB Co. | Client Services - Replace flickering light at Client Services (located in the Library) | Electrical | Lighting, Internal | 176.0425 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-11 09:12 | 2022-10-14 17:00 | 2022-10-13 10:15 | 2022-10-14 17:00 | 2022-10-13 11:00 |  | WACCES | Attended site signed in jsa completed.Found 2 tubes out in staff office in library. Replaced with materials on site. All tested and working. Job completed
MSA-DTWD | WA6007626 | 2 | AWB Co. | Replace the fluorescent globe in the R Block staff room that is continuously flickering. | Electrical | Lighting, Internal | 176.0425 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-11 09:16 | 2022-10-14 17:00 | 2022-10-13 09:30 | 2022-10-14 17:00 | 2022-10-13 10:15 |  |  | Attended site signed in jsa completed. Found 3 tubes faulty and 3 starters as shown by staff in office area. Replaced with materials on site. All working and testedJob completed
MSA-DTWD | WA6007675 | 3 | PEEL LOCK SERVICES PTY LTD | F60 storeroom - Lock to storeroom damaged - see notes | Security | Locksmith |  | Pass | Pass | -1 | -1 | 0.75 | 2022-10-11 09:24 | 2022-10-18 17:00 | 2022-10-14 13:30 | 2022-10-18 17:00 | 2022-10-14 14:15 |  |  | Repairs to lock
MSA-DTWD | WA6007771 | 2 | LIGHTHOUSE LOCKSMITHS | Repair faulty door lock to Rm M002 | Security | Locksmith | 120 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-11 10:24 | 2022-10-14 17:00 | 2022-10-11 16:15 | 2022-10-14 17:00 | 2022-10-11 17:00 |  |  | serviced lock on m002 door
MSA-DCA | WA6014495 | 1 | Dormakaba Australia Pty Ltd | two automatic doors into our foyer are not opening when in auto-mode -see notes | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-12 09:36 | 2022-10-13 17:00 | 2022-10-12 10:55 | 2022-10-13 17:00 | 2022-10-12 11:40 |  |  | 1045728. Inspected doors and found both main entry doors are being locked via access control, removed access control cables to both doors and work as normal, once return doors lockand cannot be opened, advised staff access control will need to attend to repair
MSA-DTAG | WA6019946 | 2 | Midolo Building Services | ground public area-Fault description Missing a screw on public seating | Furniture | Commercial Furniture | 105.52 | Fail | Fail | 0 | 0 | 0.75 | 2022-10-13 09:30 | 2022-10-18 17:00 | 2022-10-19 12:00 | 2022-10-18 17:00 | 2022-10-19 12:45 |  |  | re secured seats with new fixings
MSA-MRWA | WA6020642 | 2 | GPS Plumbing & Gas Services PtyLtd | Level 2 - Female Toilets - Middle Toilet doesn't drain properly - See notes below | Plumbing & Drainage | Toilets/Cisterns | 52.98 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-13 15:07 | 2022-10-18 17:00 | 2022-10-17 11:50 | 2022-10-18 17:00 | 2022-10-17 12:35 |  |  | Inspected toilets north female buttons faulty need access to plumbing duckt no access, advised Craig
MSA-DTWD | WA6021425 | 2 | Protek 24/7 Building & Maintenance | Numerous carpet tiles lifting | Flooring | Carpet | 1217.51 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-14 07:52 | 2022-10-18 17:00 | 2022-10-17 09:30 | 2022-10-18 17:00 | 2022-10-17 10:15 |  | WACCES | Located numerous carpet tiles onsite where glue has broken down causing liftRe-glue damaged carpet tiles only, no replacement of materials to be carried out
MSA-DTWD | WA6022898 | 2 | AWB Co. | External security lighting running during the day, unable to disable. | Electrical | Lighting, External | 176.0425 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-14 12:51 | 2022-10-19 17:00 | 2022-10-18 10:15 | 2022-10-19 17:00 | 2022-10-18 11:00 |  |  | Attended site signed in jsa completed. Found two overide switches pushed in the on position in board. Switched off and lights turned off. Pe cell is brand new 2 months old. Told site and job completed
MSA-DFES | WA6042461 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Driveway - in front of engine room - Water leaking up through ground | Plumbing & Drainage | Water | 92.92 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-17 08:39 | 2022-10-17 10:39 | 2022-10-17 10:00 | 2022-10-17 12:39 | 2022-10-17 10:45 |  |  | Arrived on site and singed spoke to fire guy and explained to him we have raised the job and are waiting for Programmed to give us the go ahead.
MSA-DFES | WA6050328 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Level 1 - Comcen Kitchen - Kitchen sink and floor drains smelling | Plumbing & Drainage | Drainage | 118.26 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-17 15:14 | 2022-10-20 17:00 | 2022-10-20 09:00 | 2022-10-20 17:00 | 2022-10-20 09:45 |  |  | Attended site for smelly drains in com Centre kitchen upon inspection I’ve checked the kitchen sink and the floor drain I haven’t found any particular reason for the smell I have cleaned out the floor waste as well as the kitchen sink everything seems to be working correctly cleaned up packed up
MSA-DFES | WA6077279 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Main building - Main shower - faulty shower light, keeps flashing | Electrical | Lighting, Internal | 124.875 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-18 11:29 | 2022-10-21 17:00 | 2022-10-19 14:45 | 2022-10-21 17:00 | 2022-10-19 15:30 |  |  | Called the Fire station before leaving my last job and they were on site. When I arrived they received a call and were no longer on site. Waited a few minutes to see if they will return. They did return. Located faulty light. Replaced faulty tube and starter with new.
MSA-DCA | WA6080257 | 0 | Critical Fire Protection & Training | fire door magnet is not connecting | Fire Protection Services | Fire Protection - Monitor System | 132.255 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-18 13:39 | 2022-10-18 15:39 | 2022-10-18 14:00 | 2022-10-18 17:39 | 2022-10-18 14:45 |  |  | Attended site to inspect magnet latch for loading dock roller door. Attended door motor and re-inserted latching piston for manual and electrical operations. Tested both raising and dropping functions of roller door. No further actions required.
MSA-DTWD | WA6107120 | 1 | Securex Security Systems & Services | All Buildings - When arming security alarms “Comms failure’ showing on all panels | Security | Security Management System | 393.85 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-20 08:35 | 2022-10-21 17:00 | 2022-10-20 09:45 | 2022-10-21 17:00 | 2022-10-20 10:30 |  |  | 20/10/2022. 945-1030Faulty polling paths on Iris tried to restore, no luck. Edsec system at fault.
MSA-DTWD | WA6127952 | 1 | UNIVERSAL DOORS | Screen roller door is damaged and needs securing in roof space | Building | Roller Shutters |  | Pass | Pass | 0 | 0 | 0.75 | 2022-10-26 11:18 | 2022-10-27 17:00 | 2022-10-27 14:15 | 2022-10-27 17:00 | 2022-10-27 15:00 |  |  | Repairs to grille
MSA-DTAG | WA6128164 | 2 | Water2water Pty Ltd | Level 10 - Reception - Billi filtration unit system – orange light then 2 green lights flashing | Plumbing & Drainage | Water | 300.175 | Pass | Pass | -1 | -1 | 0.75 | 2022-10-26 12:47 | 2022-10-31 17:00 | 2022-10-27 14:35 | 2022-10-31 17:00 | 2022-10-27 15:20 |  |  | Lights flashing on Billi tap on arrival. In a filter overdue x 8 fault. Replaced filter, flushed filter, waited for system to get to temp. Normal operation
MSA-DTAG | WA6129126 | 3 | Midolo Building Services | car park entry - Paving stones located next to auto gate rail are loose – Irwin Street entry. | Paving & Roadworks | Paving | 99.53 | Pass | Pass | -1 | -1 | 0.75 | 2022-10-27 11:22 | 2022-11-03 17:00 | 2022-10-28 08:45 | 2022-11-03 17:00 | 2022-10-28 09:30 |  |  | Inspect only - close cost to date - done by others
MSA-DTAG | WA6129221 | 3 | AHS Services WA Pty Ltd (Anchor) | L3-staff toilet-Female toilet seat inside Court 32 jury room is broken | Plumbing & Drainage | Toilets/Cisterns | 213.5025 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-27 12:26 | 2022-11-03 17:00 | 2022-10-31 07:45 | 2022-11-03 17:00 | 2022-10-31 08:30 |  |  | Picked up and replaced broken seat
MSA-DCA | WA6129258 | 3 | GPS Plumbing & Gas Services PtyLtd | Toilet cistern missing button | Plumbing & Drainage | Toilets/Cisterns | 242.77 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-27 12:56 | 2022-11-03 17:00 | 2022-11-03 09:30 | 2022-11-03 17:00 | 2022-11-03 10:15 |  |  | Replaced bothe flush buttons in the public female toilets RHS
MSA-DTAG | WA6129349 | 3 | AHS Services WA Pty Ltd (Anchor) | Lvel 3 - Staff Toilet -Male toilet seat inside Court 32 jury room is loose | Plumbing & Drainage | Toilets/Cisterns | 174.0825 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-27 14:12 | 2022-11-03 17:00 | 2022-10-31 07:00 | 2022-11-03 17:00 | 2022-10-31 07:45 |  |  | Picked up and replaced broken seat
MSA-DTAG | WA6129364 | 3 | AHS Services WA Pty Ltd (Anchor) | Level 5 -Public toilet - Water in constantly running ( St Georges tce end) | Plumbing & Drainage | Toilets/Cisterns | 251.0825 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-27 14:20 | 2022-11-03 17:00 | 2022-10-31 08:30 | 2022-11-03 17:00 | 2022-10-31 09:15 |  |  | Picked up and replaced faulty inlet valve and outlet washer
MSA-DFES | WA6130071 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground Floor - Men's Changeroom Toilet near the Gym - Toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 145.1475 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-28 09:38 | 2022-10-31 17:00 | 2022-10-28 12:30 | 2022-10-31 17:00 | 2022-10-28 13:15 |  |  | Unblocked the toilet in male changerooms down stairs. Plumbed and flushed the excess paper. Flushed and tested all other toilets. All drains Good.
MSA-DTAG | WA6130187 | 2 | Schindler Lifts Australia | Ground Floor - Lift 10 - Lift is out of service | Lifts | Lifts |  | Pass | Pass | -1 | -1 | 0.75 | 2022-10-28 10:35 | 2022-11-02 17:00 | 2022-10-28 11:45 | 2022-11-02 17:00 | 2022-10-28 12:30 |  |  | Lift shutdown for clipping locks Needs car clutch set up
MSA-DTAG | WA6130350 | 1 | Midolo Building Services | Level 9 - Ceiling Panel - Ceiling panel above Magistrate’s chair is loose - See notes | Building | Ceiling | 132.42 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-28 11:33 | 2022-10-31 17:00 | 2022-10-28 13:30 | 2022-10-31 17:00 | 2022-10-28 14:15 |  |  | REPAIRS COMPLETED TO CEILING
MSA-DTAG | WA6130357 | 1 | AHS Services WA Pty Ltd (Anchor) | Level 4 - Disabled Toilet - Public disabled toilet is blocked. Water spilling onto floor | Plumbing & Drainage | Toilets/Cisterns | 115.4325 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-28 11:36 | 2022-10-31 17:00 | 2022-10-28 13:30 | 2022-10-31 17:00 | 2022-10-28 14:15 |  |  | Completed
MSA-DTAG | WA6130857 | 2 | GPS Plumbing & Gas Services PtyLtd | ground female toilet-Last toilet cistern flush button broken | Plumbing & Drainage | Toilets/Cisterns | 95.77 | Pass | Pass | 0 | 0 | 0.75 | 2022-10-28 16:53 | 2022-11-02 17:00 | 2022-10-31 13:35 | 2022-11-02 17:00 | 2022-10-31 14:20 |  |  | Increased pressure to valve to let more water through for flushing, no issues to buttons
MSA-DFES | WA6143211 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Main Admin - Ground - Unisex Ambulant Toilet - Seat is broken and moving around when sat on | Plumbing & Drainage | Toilets/Cisterns | 118.26 | Pass | Pass | -1 | -1 | 0.75 | 2022-11-01 11:21 | 2022-11-08 17:00 | 2022-11-03 09:30 | 2022-11-08 17:00 | 2022-11-03 10:15 |  |  | Attend site to check out toilet seat in disabled toilet on demountable building. Found loose toilet seat. Removed and cleaned fixings and refitted and tested.all working correctly.
MSA-DTWD | WA6143770 | 2 | LIGHTHOUSE LOCKSMITHS | Digital keypad not functioning | Security | Locksmith | 350 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-01 14:36 | 2022-11-04 17:00 | 2022-11-02 13:00 | 2022-11-04 17:00 | 2022-11-02 13:45 |  |  | Replaced broken dead latch on door D009
MSA-DTWD | WA6145139 | 3 | ADVANCED LOCK & KEY | A104C and A104B - Tumblers appear worn and locks difficult to turn | Security | Locksmith | 310 | Pass | Pass | -1 | -1 | 0.75 | 2022-11-02 11:20 | 2022-11-09 17:00 | 2022-11-04 10:05 | 2022-11-09 17:00 | 2022-11-04 10:50 |  |  | Attend site and repair cylinders on A104b and A104C 1x cylinder components MK (A104B) 1x LT 570 cylinder MK (A104C)
MSA-DFES | WA6148385 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 6 Bathroom - Shower has a blocked drain Water is backing up like drain is restricted | Plumbing & Drainage | Drainage | 118.26 | Pass | Pass | -1 | -1 | 0.75 | 2022-11-03 16:45 | 2022-11-10 17:00 | 2022-11-04 09:15 | 2022-11-10 17:00 | 2022-11-04 10:00 |  |  | Cleared blocked shower drain.
MSA-DTWD | WA6155243 | 2 | Protek 24/7 Building & Maintenance | A section of the ceiling near the corner of the room has collapsed due to water damage | Building | Ceiling | 102.815 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-08 08:54 | 2022-11-11 17:00 | 2022-11-11 08:00 | 2022-11-11 17:00 | 2022-11-11 08:45 |  |  | As discussed with Glen on site he will enquire with a plumber to fix the pipe
MSA-DTWD | WA6155471 | 2 | AWB Co. | A Block First Floor male toilets - The entry light button has been pushed into the box. Repair | Electrical | General Electrical | 138.7275 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-08 10:49 | 2022-11-11 17:00 | 2022-11-11 13:15 | 2022-11-11 17:00 | 2022-11-11 14:00 |  |  | Attended site signed in jsa completed. Found switch pushed in wall of toilets. Replaced with new. Tested operational.Job completed
MSA-DTAG | WA6155498 | 3 | Midolo Building Services | Level 3 - Court 32 - Hinges on door needs lubricating - See notes | Building | Doors | 119.33 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-08 11:03 | 2022-11-15 17:00 | 2022-11-14 08:45 | 2022-11-15 17:00 | 2022-11-14 09:30 |  |  | eased door hinges
MSA-DTWD | WA6156616 | 2 | UNIVERSAL DOORS | Roller door number 4 (manual) hard to open and close. | Building | Roller Shutters |  | Pass | Pass | 0 | 0 | 0.75 | 2022-11-09 09:13 | 2022-11-14 17:00 | 2022-11-11 13:30 | 2022-11-14 17:00 | 2022-11-11 14:15 |  |  | Service to roller door
MSA-DCA | WA6159284 | 1 | Wilson Security | RETROSPECTIVE - no need to send contractor - U Block alarm - see note | Security | Security Management System |  | Pass | Pass | 0 | 0 | 0.75 | 2022-10-30 15:03 | 2022-10-31 17:00 | 2022-10-30 15:15 | 2022-10-31 17:00 | 2022-10-30 16:00 | 1 |  | Completed
MSA-DFES | WA6166231 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen - Hole in sink tap - See notes below | Plumbing & Drainage | Water | 213.49 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-11 13:16 | 2022-11-16 17:00 | 2022-11-16 11:01 | 2022-11-16 17:00 | 2022-11-16 11:46 |  |  | Installed new mixer tap as the old one had a hole in it it was cracking and could not be fixed
MSA-DTWD | WA6178917 | 2 | PEEL LOCK SERVICES PTY LTD | ground G15-Lock on door not securing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-11-14 14:50 | 2022-11-17 17:00 | 2022-11-17 11:45 | 2022-11-17 17:00 | 2022-11-17 12:30 |  |  | Repairs to lock
MSA-DTWD | WA6184106 | 1 | Protek 24/7 Building & Maintenance | Staff Room - broken door closer | Building | Doors | 102.815 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-15 10:11 | 2022-11-16 17:00 | 2022-11-15 11:15 | 2022-11-16 17:00 | 2022-11-15 12:00 |  |  | Tighten the bolts and Alan key screws to the door closer
MSA-DTWD | WA6184773 | 2 | Water2water Pty Ltd | No water pressure in drinking fountain - photo's to follow in email | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-15 15:45 | 2022-11-18 17:00 | 2022-11-17 11:15 | 2022-11-18 17:00 | 2022-11-17 12:00 |  |  | Adjusted water inlet to bubblers and tested. All ok and working fine.
MSA-DFES | WA6184783 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Yard - Pump Controllers - lighting faulty - see notes below | Electrical | Lighting, Internal | 127.255 | Pass | Pass | -1 | -1 | 0.75 | 2022-11-15 15:56 | 2022-11-22 17:00 | 2022-11-17 14:15 | 2022-11-22 17:00 | 2022-11-17 15:00 |  |  | Sebastian Pino (17/11/2022) - Work NoteContinued on site at 1415 to attend faulty light in pump control rm. Located faulty light and discovered 1 x faulty ballast and 2 x faulty fluros within fitting. Replaced all faulty components and reenergised fitting. Informed staff of works and left site at 1500.
MSA-DCA | WA6190681 | 1 | TK Elevator Australia Pty Ltd | Foyer-Elevator stuck again | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.75 | 2022-11-16 09:55 | 2022-11-17 17:00 | 2022-11-16 12:00 | 2022-11-17 17:00 | 2022-11-16 12:45 |  |  | Lift1 PICA-Elevator > MRL > Gearless :Lift out of service wth doors closed, found lift below floor level and safety circuit tripped. Moved lift upon recall and tested, unable to reproduce fault, left in service.to be closed out at $0 cost
MSA-DTWD | WA6191389 | 3 | LIGHTHOUSE LOCKSMITHS | Fire escape door handle broken - C201 | Security | Locksmith |  | Pass | Pass | -1 | -1 | 0.75 | 2022-11-16 16:17 | 2022-11-23 17:00 | 2022-11-17 10:30 | 2022-11-23 17:00 | 2022-11-17 11:15 |  |  | Repairs to lock
MSA-DTWD | WA6208237 | 0 | LIGHTHOUSE LOCKSMITHS | urgently need a standard key or organize a key | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-11-17 15:00 | 2022-11-17 17:00 | 2022-11-17 16:15 | 2022-11-17 19:00 | 2022-11-17 17:00 |  |  | Repairs to lock
MSA-DTWD | WA6208280 | 2 | PEEL LOCK SERVICES PTY LTD | Lock on door not securing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-11-17 15:46 | 2022-11-22 17:00 | 2022-11-22 11:15 | 2022-11-22 17:00 | 2022-11-22 12:00 |  |  | Repair to lock
MSA-MRWA | WA6229855 | 3 | Dom's Total Grounds Maintenance | broken retic riser west of Staff carpark | Landscaping & Gardening | Grounds Maintenance | 157.5 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-18 10:43 | 2022-11-25 17:00 | 2022-11-23 17:10 | 2022-11-25 17:00 | 2022-11-23 17:55 |  |  | Call Out & Repair
MSA-DFES | WA6255460 | 3 | Protek 24/7 Building & Maintenance | Ground Floor - Door leading to Mail Room Area - Door slamming, door closer faulty | Building | Doors | 102.83 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-23 10:46 | 2022-11-30 17:00 | 2022-11-28 14:45 | 2022-11-30 17:00 | 2022-11-28 15:30 |  |  | Closer required adjustment
MSA-DCA | WA6255658 | 2 | GPS Plumbing & Gas Services PtyLtd | Leak on level 2 near toilet | Plumbing & Drainage | Toilets/Cisterns | 119.4775 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-23 12:30 | 2022-11-28 17:00 | 2022-11-28 08:30 | 2022-11-28 17:00 | 2022-11-28 09:15 |  |  | Inspected the floor 2nd floor near toilets no leaking toilets and floor is dry, spoke to the cleaner and they said it was coming from the ceiling
MSA-DFES | WA6257524 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Kitchen/ Oven & Hotplate - see notes below | Electrical | General Electrical | 107.715 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-24 16:45 | 2022-11-29 17:00 | 2022-11-28 08:45 | 2022-11-29 17:00 | 2022-11-28 09:30 |  |  | Attended site at 0845. Found oven and stove to be bypassing the DDL Status Switch contactor. PFM advised office that works are to be completed by original contractors. Left site at 0930.
MSA-DFES | WA6257882 | 1 | INSIGHT ELECTRICAL TECHNOLOGY | plant room - Power outage - See notes | Electrical | General Electrical | 107.715 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-25 08:31 | 2022-11-28 17:00 | 2022-11-25 09:45 | 2022-11-28 17:00 | 2022-11-25 10:30 |  |  | Arrived on site at 0945 to attend plant room - Power outage. Investigated plant rooom equipment and all relevant DB’s on site…found nothing of concern. Informed staff of outcome and left site at 1030.
MSA-MRWA | WA6258590 | 3 | GPS Plumbing & Gas Services PtyLtd | RHS Cubicle - Toilet cistern very slow to fill - see notes | Plumbing & Drainage | Toilets/Cisterns | 143.77 | Pass | Pass | -1 | -1 | 0.75 | 2022-11-25 13:40 | 2022-12-02 17:00 | 2022-11-28 12:40 | 2022-12-02 17:00 | 2022-11-28 13:25 |  |  | Replaced faulty inlet valve
MSA-DFES | WA6258749 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1-lost all lights to change room | Electrical | Lighting, Internal | 139.475 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-25 16:16 | 2022-11-30 17:00 | 2022-11-29 11:15 | 2022-11-30 17:00 | 2022-11-29 12:00 |  |  | Carson Marshall (29/11/2022) - Work NoteArrived on site at 1115. Located change room 7967 and found lights to be working other than 1. Replaced tubes for fitting and everything was in working order. Alerted staff and signed out at 1200
MSA-DCA | WA6292347 | 1 | Automatic Fire Protection (ARA) | Main fire panel - showing an alarm. | Fire Protection Services | Fire Protection - Monitor System | 371.43 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-29 09:32 | 2022-11-30 17:00 | 2022-11-29 10:45 | 2022-11-30 17:00 | 2022-11-29 11:30 |  |  | Attended site and found device 1016 Az 6 Temp Storage Area in alarm/isolated.Removed and fitted new detector reset and de isolated.Left system normal.
MSA-DCA | WA6292521 | 0 | Protek 24/7 Building & Maintenance | Level 2 - Storage Area 10 - Door hinge is faulty | Building | Doors | 195.68 | Fail | Pass | 0 | 0 | 0.75 | 2022-11-29 10:56 | 2022-11-29 12:56 | 2022-11-29 13:45 | 2022-11-29 14:56 | 2022-11-29 14:30 |  |  | Remove the splinted edge of door to let the door close correctly
MSA-DTWD | WA6292939 | 2 | AWB Co. | Room B41 - x2 Fluro Lights (see notes) | Electrical | Lighting, Internal | 104.245 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-29 14:43 | 2022-12-02 17:00 | 2022-12-02 15:00 | 2022-12-02 17:00 | 2022-12-02 15:45 |  |  | Attended site and signed in. Completed JSA. Liased with site about works. Replaced various tubes put as directed by site. Parts supplied by site. **job Complete**
MSA-DTAG | WA6294438 | 3 | Midolo Building Services | Level 1 - Courtroom 1 - Door stop faulty positioning - see notes | Building | Doors | 114.31 | Pass | Pass | 0 | 0 | 0.75 | 2022-11-30 16:18 | 2022-12-07 17:00 | 2022-12-05 12:45 | 2022-12-07 17:00 | 2022-12-05 13:30 |  |  | New door stop installed
MSA-DTWD | WA6299920 | 2 | PEEL LOCK SERVICES PTY LTD | Internal door will not close. | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2022-12-02 08:37 | 2022-12-07 17:00 | 2022-12-05 12:45 | 2022-12-07 17:00 | 2022-12-05 13:30 |  |  | Repair to lock
MSA-DCA | WA6356575 | 1 | Earth & Water Pty Ltd | Side of AGWA - Ground - Retic is leaking | Plumbing & Drainage | Water |  | Pass | Pass | 0 | 0 | 0.75 | 2022-12-05 08:14 | 2022-12-06 17:00 | 2022-12-05 09:30 | 2022-12-06 17:00 | 2022-12-05 10:15 |  |  | Completed
MSA-DFES | WA6357198 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Building - Ground - Washing basin does not drain well. Water fills up the bowl due to drainage | Plumbing & Drainage | Water | 118.26 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-05 11:39 | 2022-12-08 17:00 | 2022-12-06 15:00 | 2022-12-08 17:00 | 2022-12-06 15:45 |  |  | After plunging the sink everything is working correctly
MSA-DFES | WA6357674 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Light tanker bays - Re-secure loose light battern to the ceiling | Electrical | Lighting, External | 107.715 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-05 15:49 | 2022-12-08 17:00 | 2022-12-07 12:15 | 2022-12-08 17:00 | 2022-12-07 13:00 |  |  | Arrived on site at 1215, found three lights were hanging down, reinstated lights with appropriate fixings, alerted station of completion and Left site at 1300
MSA-DFES | WA6362733 | 2 | Complete Pest Management Services | Report of mouse in ground floor Rural Fire Division area. | Pest Control | General Pest | 295.67 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-09 12:30 | 2022-12-14 17:00 | 2022-12-13 10:00 | 2022-12-14 17:00 | 2022-12-13 10:45 |  |  | Inspected the ground floor in the area of Rural Fire Division replenish baits as required
MSA-DTWD | WA6364061 | 1 | SCAVENGER SUPPLIES PTY LTD | Fire Panel - Fire alarm activated over the weekend - see note below | Fire Protection Services | Fire Protection - Monitor System | 132.255 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-12 09:20 | 2022-12-13 17:00 | 2022-12-12 09:30 | 2022-12-13 17:00 | 2022-12-12 10:15 |  |  | ATTENDED 12/12/22 - Attended to rectify issue with FIP.
MSA-DCA | WA6364088 | 1 | Earth & Water Pty Ltd | Museum Plaza (Zone 14) - Broken retic. | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.75 | 2022-12-12 09:31 | 2022-12-13 17:00 | 2022-12-13 16:00 | 2022-12-13 17:00 | 2022-12-13 16:45 |  |  | repairs to retic
MSA-DCA | WA6364483 | 1 | ACTION GLASS & ALUMINIUM | Francis Street Entrance - Ground - information sign glass has been broken - see notes below | Glazing | Specialist Glass | 162.02 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-12 12:10 | 2022-12-13 17:00 | 2022-12-12 12:45 | 2022-12-13 17:00 | 2022-12-12 13:30 |  |  | ATTENDED SITE AND MADE SAFE ONLY BROKEN GLASS PANEL AS REQUESTED
MSA-DFES | WA6366036 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Main building - Shower - Washers are leaking | Plumbing & Drainage | Water | 167.1475 | Pass | Pass | -1 | -1 | 0.75 | 2022-12-13 14:17 | 2022-12-20 17:00 | 2022-12-15 10:15 | 2022-12-20 17:00 | 2022-12-15 11:00 |  |  | Arrived on site went to female toilets located in Gym area and had to replaces 2 tap washer and did tap service tested and everything was fine
MSA-DCA | WA6372951 | 1 | Assa Abloy Entrance Systems Aust P/L-WA | Entrance - West side entrance door making beeping noise | Building | Automatic Doors | 411.53 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-14 12:56 | 2022-12-15 17:00 | 2022-12-14 14:15 | 2022-12-15 17:00 | 2022-12-14 15:00 |  |  | Traced beeping noise to low battery alarm. Battery over 5 years old. Upgraded to TSM for replacement. All correct on departure.
MSA-DTAG | WA6373481 | 1 | Schindler Lifts Australia | Level 8-Lift 3 door closure problem | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.75 | 2022-12-14 14:23 | 2022-12-15 17:00 | 2022-12-15 06:45 | 2022-12-15 17:00 | 2022-12-15 07:30 |  |  | to be closed out at $0 cost
MSA-DCA | WA6376293 | 3 | Protek 24/7 Building & Maintenance | Exterior ground - Wooden steps east of SLWA - Step strips coming off - see notes | Building | Materials | 134.08 | Pass | Pass | -1 | -1 | 0.75 | 2022-12-15 13:19 | 2022-12-22 17:00 | 2022-12-16 10:00 | 2022-12-22 17:00 | 2022-12-16 10:45 |  |  | Added extra screws to secure strip in place
MSA-DFES | WA6376364 | 1 | Water2water Pty Ltd | Level 2 - Kitchen - Zip boiler has a gas smell | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-15 14:22 | 2022-12-16 17:00 | 2022-12-16 09:00 | 2022-12-16 17:00 | 2022-12-16 09:45 |  |  | Thoroughly checked all units on this level. All operating correctly which would indicate no gas leak from using. But also refrigerate gas small wouldn’t be recognised as “gas”.
MSA-DTAG | WA6376478 | 3 | Midolo Building Services | Level 3 - Court 37 Jury room - Ceiling tile cracked | Building | Ceiling | 99.53 | Fail | Fail | 3 | 3 | 0.75 | 2022-12-15 15:54 | 2022-12-22 17:00 | 2023-01-10 07:00 | 2022-12-22 17:00 | 2023-01-10 07:45 |  |  | CEILING TILE REPLACED
MSA-DFES | WA6384274 | 1 | Protek 24/7 Building & Maintenance | Warehouse - cordon off the following areas as per recent asbestos report completed- see notes below | Building | Internal Walls | 163.42 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-21 07:20 | 2022-12-21 17:00 | 2022-12-21 09:30 | 2022-12-21 17:00 | 2022-12-21 10:15 |  |  | Install signage as instructed
MSA-DTWD | WA6387757 | 1 | CONNECT SECURITY SYSTEMS | D32 commercial kitchen-fault alarm panel | Security | Security Management System | 123.6 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-21 11:48 | 2022-12-22 17:00 | 2022-12-21 13:45 | 2022-12-22 17:00 | 2022-12-21 14:30 |  |  | Completed 21/12/2022
MSA-DFES | WA6393255 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - Various - Spotlight damaged - See Notes Below | Electrical | General Electrical | 113.215 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-28 11:58 | 2023-01-03 17:00 | 2023-01-03 12:30 | 2023-01-03 17:00 | 2023-01-03 13:15
MSA-DTAG | WA6393959 | 3 | Sapio Pty Ltd | Front counter duress button wont release the key after reset. (possible warranty) | Security | Security Management System | 368.2 | Pass | Pass | 0 | 0 | 0.75 | 2022-12-29 13:12 | 2023-01-06 17:00 | 2023-01-03 09:00 | 2023-01-06 17:00 | 2023-01-03 09:45
MSA-DFES | WA6400034 | 3 | AWB Co. | Ground - Firefighter bathroom - door closer arm on bathroom door has pulled off the wall | Building | General Building | 114.9975 | Pass | Pass | -1 | -1 | 0.75 | 2023-01-03 09:08 | 2023-01-10 17:00 | 2023-01-05 15:15 | 2023-01-10 17:00 | 2023-01-05 16:00
MSA-DTAG | WA6408133 | 1 | Water2water Pty Ltd | Level 2A - Kitchen - billi unit faulty - see notes below | Plumbing & Drainage | Water | 596.505 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-10 15:07 | 2023-01-11 17:00 | 2023-01-11 11:55 | 2023-01-11 17:00 | 2023-01-11 12:40
MSA-MRWA | WA6408160 | 2 | Water2water Pty Ltd | Kitchenette - hot water urn is not heating | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-10 15:31 | 2023-01-13 17:00 | 2023-01-11 12:15 | 2023-01-13 17:00 | 2023-01-11 13:00
MSA-DFES | WA6425904 | 3 | Protek 24/7 Building & Maintenance | Ground - Undercroft - Door leading to courtyard is slamming hard on close | Building | Doors | 102.83 | Pass | Pass | -1 | -1 | 0.75 | 2023-01-12 12:40 | 2023-01-19 17:00 | 2023-01-13 09:15 | 2023-01-19 17:00 | 2023-01-13 10:00
MSA-DTWD | WA6450736 | 2 | AWB Co. | Painting & Decorating - Light fitting hanging loose | Electrical | General Electrical | 122.4775 | Pass | Fail | 0 | 0 | 0.75 | 2023-01-16 13:44 | 2023-01-19 17:00 | 2023-01-19 16:30 | 2023-01-19 17:00 | 2023-01-19 17:15
MSA-DCA | WA6467817 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Auditorium stage corner - Faulty light fitting in stage corner | Electrical | Lighting, Internal | 179.7175 | Pass | Pass | -1 | -1 | 0.75 | 2023-01-17 16:44 | 2023-01-24 17:00 | 2023-01-20 10:00 | 2023-01-24 17:00 | 2023-01-20 10:45
MSA-DTAG | WA6482469 | 1 | AWB Co. | Court 2 - Flickering light - See Notes Below | Electrical | Lighting, Internal | 122.4775 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-18 10:40 | 2023-01-19 17:00 | 2023-01-18 13:30 | 2023-01-19 17:00 | 2023-01-18 14:15
MSA-DTWD | WA6482644 | 2 | Critical Fire Protection & Training | E-Block Staff Room - Kitchenette - Extinguishers to be installed - See Notes below | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) | 120.995 | Pass | Pass | -1 | -1 | 0.75 | 2023-01-18 11:52 | 2023-01-23 17:00 | 2023-01-19 12:25 | 2023-01-23 17:00 | 2023-01-19 13:10
MSA-DTWD | WA6484186 | 2 | Swan Pest Control | Level 1 Room A113 and A114 - Large amount of cockroaches - See Notes | Pest Control | General Pest | 200 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-18 13:13 | 2023-01-23 17:00 | 2023-01-23 11:00 | 2023-01-23 17:00 | 2023-01-23 11:45
MSA-DTWD | WA6504314 | 2 | ACTION GLASS & ALUMINIUM | creche play area - door has a broken window | Glazing | Door Glass | 252.815 | Pass | Pass | -1 | -1 | 0.75 | 2023-01-19 14:42 | 2023-01-24 17:00 | 2023-01-20 13:45 | 2023-01-24 17:00 | 2023-01-20 14:30
MSA-DFES | WA6509549 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | Station Officer Bathroom - showerhead is leaking - please replace | Plumbing & Drainage | Water | 405.68 | Pass | Pass | -1 | -1 | 0.75 | 2023-01-20 12:00 | 2023-01-25 17:00 | 2023-01-20 14:45 | 2023-01-25 17:00 | 2023-01-20 15:30
MSA-DTWD | WA6516824 | 2 | Swan Pest Control | Bike Shed - Pidgeon spikes are missing or damaged | Pest Control | General Pest | 150 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-23 15:41 | 2023-01-27 17:00 | 2023-01-25 13:25 | 2023-01-27 17:00 | 2023-01-25 14:10
MSA-DTAG | WA6518821 | 2 | Midolo Building Services | Cell 1 - bubbling tinting and is peeling off - see notes | Building | Windows | 99.53 | Fail | Fail | 1 | 1 | 0.75 | 2023-01-25 11:04 | 2023-01-31 17:00 | 2023-02-06 10:30 | 2023-01-31 17:00 | 2023-02-06 11:15 |  | WACCES
MSA-DFES | WA6519182 | 2 | Dom's Total Grounds Maintenance | Level 1 - Large branch at rear of block requires removal | Landscaping & Gardening | Grounds Maintenance | 890 | Fail | Fail | 1 | 1 | 0.75 | 2023-01-25 13:36 | 2023-01-31 17:00 | 2023-02-04 10:00 | 2023-01-31 17:00 | 2023-02-04 10:45
MSA-DCA | WA6519351 | 3 | Protek 24/7 Building & Maintenance | Ground - Stairwell 3 - Exit door leading out of building - See Notes Below | Building | Doors | 102.83 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-25 16:28 | 2023-02-02 17:00 | 2023-01-30 12:00 | 2023-02-02 17:00 | 2023-01-30 12:45
MSA-DFES | WA6519948 | 3 | SONTEC WA PTY LTD | First Floor - State Operation Centre Door way - Egress button in auto door is not working | Building | Automatic Doors | 862.43 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-27 08:54 | 2023-02-03 17:00 | 2023-01-31 16:00 | 2023-02-03 17:00 | 2023-01-31 16:45
MSA-DCA | WA6521490 | 1 | ACTION GLASS & ALUMINIUM | Boardwalk - North facing window on boardwalk has been damaged - Crack in glass | Glazing | Window Glass | 162.02 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-30 11:14 | 2023-01-31 17:00 | 2023-01-30 15:00 | 2023-01-31 17:00 | 2023-01-30 15:45
MSA-DTWD | WA6521887 | 1 | AHS Services WA Pty Ltd (Anchor) | water leaking from cistern when flushed | Plumbing & Drainage | Toilets/Cisterns | 147.9325 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-30 14:01 | 2023-01-31 17:00 | 2023-01-31 08:45 | 2023-01-31 17:00 | 2023-01-31 09:30
MSA-DTAG | WA6521979 | 1 | AHS Services WA Pty Ltd (Anchor) | Prisoners Review Board Interior Office - Female toilet is not flushing | Plumbing & Drainage | Toilets/Cisterns | 115.4325 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-30 15:28 | 2023-01-31 17:00 | 2023-01-31 08:30 | 2023-01-31 17:00 | 2023-01-31 09:15
MSA-DTWD | WA6522561 | 1 | SCAVENGER SUPPLIES PTY LTD | Disabled Toilets - Check fire sensor in disabled toilets | Fire Protection Services | Fire Protection - Monitor System | 132.255 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-31 08:42 | 2023-02-01 17:00 | 2023-01-31 08:45 | 2023-02-01 17:00 | 2023-01-31 09:30
MSA-DTWD | WA6522751 | 1 | Protek 24/7 Building & Maintenance | Fault description The door to the creche is hitting the door frame & can not be closed | Building | Doors | 102.815 | Pass | Pass | 0 | 0 | 0.75 | 2023-01-31 10:04 | 2023-02-01 17:00 | 2023-01-31 11:30 | 2023-02-01 17:00 | 2023-01-31 12:15
MSA-DTWD | WA6526908 | 2 | ADVANCED LOCK & KEY | Room B120 - Unable to fit key to lock barrel on door B120 | Security | Locksmith | 265 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-01 11:50 | 2023-02-06 17:00 | 2023-02-06 10:15 | 2023-02-06 17:00 | 2023-02-06 11:00
MSA-DCA | WA6527280 | 1 | Protek 24/7 Building & Maintenance | Old Jail - Ground - Door between exhibition and CEO admin area | Building | Doors | 452.03 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-01 15:30 | 2023-02-02 17:00 | 2023-02-02 09:00 | 2023-02-02 17:00 | 2023-02-02 09:45
MSA-DTAG | WA6529082 | 1 | Midolo Building Services | Court 84 - Wooden gate attached to JSO bench is hanging off | Building | Steel Fencing & Gates | 105.52 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-02 14:27 | 2023-02-03 17:00 | 2023-02-03 07:30 | 2023-02-03 17:00 | 2023-02-03 08:15
MSA-DFES | WA6533900 | 0 | Go Doors | Engine Bay Door - Door 3 - No power to unit - Cannot open | Building | Automatic Doors | 2185.22 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-06 09:41 | 2023-02-06 11:41 | 2023-02-06 10:30 | 2023-02-06 13:41 | 2023-02-06 11:15
MSA-DFES | WA6537654 | 2 | Water2water Pty Ltd | Main building - Ground - Radio Comms Lunch room - Water cooler leaking | Refrigeration | Chiller |  | Pass | Pass | 0 | 0 | 0.75 | 2023-02-07 10:45 | 2023-02-10 17:00 | 2023-02-10 08:00 | 2023-02-10 17:00 | 2023-02-10 08:45
MSA-DFES | WA6539063 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Car park - outside toilet - external light | Electrical | Lighting, External | 133.775 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-08 10:16 | 2023-02-15 17:00 | 2023-02-14 09:15 | 2023-02-15 17:00 | 2023-02-14 10:00
MSA-DTWD | WA6539254 | 1 | PEEL LOCK SERVICES PTY LTD | M Block - MG50 - Computer Lab 1, unable to lock/unlock door (external door) | Security | Keys & Access |  | Pass | Pass | 0 | 0 | 0.75 | 2023-02-08 11:31 | 2023-02-09 17:00 | 2023-02-08 12:15 | 2023-02-09 17:00 | 2023-02-08 13:00
MSA-DTWD | WA6539484 | 2 | Water2water Pty Ltd | Billi HW unit in fault | Plumbing & Drainage | HWS/Units Electric & Gas | 435.735 | Pass | Pass | -1 | -1 | 0.75 | 2023-02-08 13:29 | 2023-02-13 17:00 | 2023-02-09 11:10 | 2023-02-13 17:00 | 2023-02-09 11:55
MSA-DTAG | WA6543972 | 3 | GPS Plumbing & Gas Services PtyLtd | Male Staff Bathroom - toilet dripping | Plumbing & Drainage | Toilets/Cisterns | 196.165 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-10 09:16 | 2023-02-17 17:00 | 2023-02-16 13:45 | 2023-02-17 17:00 | 2023-02-16 14:30
MSA-DTAG | WA6573186 | 2 | Midolo Building Services | Ground - ladies public toilet - Cubicle 1 door not closing and latching properly | Building | General Building | 182.53 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-14 11:27 | 2023-02-17 17:00 | 2023-02-15 08:30 | 2023-02-17 17:00 | 2023-02-15 09:15
MSA-DTWD | WA6573597 | 1 | Protek 24/7 Building & Maintenance | Window stuck open | Building | Windows | 161.51 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-14 14:56 | 2023-02-15 17:00 | 2023-02-14 15:15 | 2023-02-15 17:00 | 2023-02-14 16:00 |  | WACCES
MSA-DFES | WA6578777 | 3 | Protek 24/7 Building & Maintenance | Level G - Tunic Room - Broken Pelmet (see notes) | Building | General Building | 121.58 | Pass | Pass | -1 | -1 | 0.75 | 2023-02-15 11:58 | 2023-02-22 17:00 | 2023-02-16 12:45 | 2023-02-22 17:00 | 2023-02-16 13:30
MSA-DTWD | WA6585808 | 1 | PEEL LOCK SERVICES PTY LTD | Various rooms - Ground level - Manual key-pad locks require re-coding | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.75 | 2023-02-16 10:54 | 2023-02-17 17:00 | 2023-02-16 11:00 | 2023-02-17 17:00 | 2023-02-16 11:45
MSA-DTWD | WA6604054 | 2 | AWB Co. | Kitchen - Faulty GPO | Electrical | General Electrical | 167.8 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-17 15:24 | 2023-02-22 17:00 | 2023-02-21 07:45 | 2023-02-22 17:00 | 2023-02-21 08:30
MSA-DTWD | WA6604116 | 2 | AWB Co. | Light switch - replace with 30USM mechs | Electrical | Lighting, Internal | 193.8 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-17 16:29 | 2023-02-22 17:00 | 2023-02-21 14:00 | 2023-02-22 17:00 | 2023-02-21 14:45
MSA-DTWD | WA6650507 | 2 | AHS Services WA Pty Ltd (Anchor) | Toilet not flushing | Plumbing & Drainage | Toilets/Cisterns | 115.4325 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-20 11:38 | 2023-02-23 17:00 | 2023-02-22 14:00 | 2023-02-23 17:00 | 2023-02-22 14:45
MSA-DTWD | WA6650895 | 2 | AHS Services WA Pty Ltd (Anchor) | vanity tap won't turn off. | Plumbing & Drainage | Drainage | 133.5125 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-20 14:15 | 2023-02-23 17:00 | 2023-02-21 15:00 | 2023-02-23 17:00 | 2023-02-21 15:45
MSA-DFES | WA6651013 | 3 | INSIGHT ELECTRICAL TECHNOLOGY | Change room - Light globe blown | Electrical | Lighting, Internal | 137.9175 | Pass | Pass | -1 | -1 | 0.75 | 2023-02-20 16:06 | 2023-02-27 17:00 | 2023-02-22 14:30 | 2023-02-27 17:00 | 2023-02-22 15:15
MSA-DTWD | WA6657710 | 1 | High Tech Pest Control | Cabin crew office - Upstairs rooms - Bait boxes refilled / replaced see notes | Pest Control | General Pest | 285.85 | Fail | Fail | 0 | 0 | 0.75 | 2023-02-21 11:33 | 2023-02-22 17:00 | 2023-02-24 13:50 | 2023-02-22 17:00 | 2023-02-24 14:35
MSA-DTWD | WA6668747 | 1 | Protek 24/7 Building & Maintenance | Loose carpet tiles- trip hazard | Flooring | Carpet | 140.565 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-22 11:27 | 2023-02-23 17:00 | 2023-02-22 14:15 | 2023-02-23 17:00 | 2023-02-22 15:00
MSA-DFES | WA6669258 | 0 | ZAMBEZI PLUMBING & GAS PTY LTD | Blocked sewage pipe, septic is full | Plumbing & Drainage | Sewer Drains & Septic Systems | 498.33 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-22 18:42 | 2023-02-22 20:42 | 2023-02-22 18:45 | 2023-02-22 22:42 | 2023-02-22 19:30
MSA-DTWD | WA6672092 | 1 | Australian Airconditioning Services Pty Ltd | Cool room - Broken door handle | Refrigeration | Coolroom | 221.37 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-23 12:44 | 2023-02-24 17:00 | 2023-02-24 14:45 | 2023-02-24 17:00 | 2023-02-24 15:30
MSA-DFES | WA6672202 | 2 | Protek 24/7 Building & Maintenance | Door requires the gap to be closed between the lock and the frame - (see notes) | Building | Doors | 196.58 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-23 13:18 | 2023-02-28 17:00 | 2023-02-27 11:00 | 2023-02-28 17:00 | 2023-02-27 11:45
MSA-DFES | WA6672341 | 0 | INSIGHT ELECTRICAL TECHNOLOGY | MAin toilet - Electrical switches faulty | Electrical | General Electrical | 112.095 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-23 15:25 | 2023-02-23 17:25 | 2023-02-23 17:00 | 2023-02-23 19:25 | 2023-02-23 17:45
MSA-DFES | WA6672715 | 3 | Protek 24/7 Building & Maintenance | Shower number 2 - Bench in decontamination shower has come off wall (see notes) | Building | Internal Walls | 102.83 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-24 07:36 | 2023-03-02 17:00 | 2023-02-28 07:45 | 2023-03-02 17:00 | 2023-02-28 08:30
MSA-DFES | WA6673242 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Level 1 - DOSS Office - Light not working | Electrical | Lighting, Internal | 107.715 | Pass | Pass | -1 | -1 | 0.75 | 2023-02-24 12:04 | 2023-03-01 17:00 | 2023-02-24 14:00 | 2023-03-01 17:00 | 2023-02-24 14:45
MSA-DTWD | WA6674118 | 1 | Milners Tree Solutions Pty Ltd | Driveway - Large branch fall on driveway west end of block 10 | Landscaping & Gardening | Grounds Maintenance |  | Pass | Pass | 0 | 0 | 0.75 | 2023-02-27 08:08 | 2023-02-28 17:00 | 2023-02-27 08:30 | 2023-02-28 17:00 | 2023-02-27 09:15
MSA-DTAG | WA6676191 | 2 | Midolo Building Services | Court 1 - Magnetic panel for closure of door has come away from the door | Building | Doors | 132.42 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-28 12:20 | 2023-03-03 17:00 | 2023-03-01 08:30 | 2023-03-03 17:00 | 2023-03-01 09:15
MSA-DTWD | WA6676298 | 1 | Water2water Pty Ltd | Passage next to (T42) - Water leak under pan | Plumbing & Drainage | Water | 150.355 | Pass | Pass | 0 | 0 | 0.75 | 2023-02-28 13:21 | 2023-03-01 17:00 | 2023-03-01 08:00 | 2023-03-01 17:00 | 2023-03-01 08:45
MSA-DCA | WA6676343 | 0 | TK Elevator Australia Pty Ltd | Lift not working | Lifts | Lifts |  | Fail | Fail | 0 | 0 | 0.75 | 2023-02-28 13:39 | 2023-02-28 15:39 | 2023-02-28 17:00 | 2023-02-28 17:39 | 2023-02-28 17:45
MSA-DFES | WA6681339 | 2 | Protek 24/7 Building & Maintenance | Patio roof - Clear sheet is not being held secure and is flappig around and very loose | Roofing | Rooflights and Skylights | 192.79 | Pass | Pass | -1 | -1 | 0.75 | 2023-03-02 07:35 | 2023-03-07 17:00 | 2023-03-03 13:15 | 2023-03-07 17:00 | 2023-03-03 14:00
MSA-DTWD | WA6688504 | 2 | LIGHTHOUSE LOCKSMITHS | faulty lock | Security | Locksmith | 240 | Pass | Pass | 0 | 0 | 0.75 | 2023-03-07 15:37 | 2023-03-10 17:00 | 2023-03-08 11:25 | 2023-03-10 17:00 | 2023-03-08 12:10
MSA-DCA | WA6689026 | 3 | GPS Plumbing & Gas Services PtyLtd | L1-Sink not draining in VMO office | Plumbing & Drainage | Drainage | 168.715 | Pass | Pass | -1 | -1 | 0.75 | 2023-03-08 08:39 | 2023-03-15 17:00 | 2023-03-08 08:40 | 2023-03-15 17:00 | 2023-03-08 09:25
MSA-DFES | WA6689238 | 2 | INSIGHT ELECTRICAL TECHNOLOGY | Room 11 - FF’s Middle Dorm bathroom - The light/fan switch is broken (see notes) | Electrical | General Electrical | 214.5975 | Pass | Pass | 0 | 0 | 0.75 | 2023-03-08 10:29 | 2023-03-13 17:00 | 2023-03-13 13:15 | 2023-03-13 17:00 | 2023-03-13 14:00
MSA-DFES | WA6690573 | 2 | ZAMBEZI PLUMBING & GAS PTY LTD | 1st floor - comcen Kitchen - Water tap loose - Mixer tap | Plumbing & Drainage | Water | 145.1475 | Pass | Pass | -1 | -1 | 0.75 | 2023-03-09 10:39 | 2023-03-14 17:00 | 2023-03-10 11:30 | 2023-03-14 17:00 | 2023-03-10 12:15
MSA-DCA | WA6693738 | 2 | Protek 24/7 Building & Maintenance | Security peg on door side with "push/pull written on it, has come loose and slides down (see notes) | Building | General Building | 102.83 | Pass | Pass | 0 | 0 | 0.75 | 2023-03-10 13:43 | 2023-03-15 17:00 | 2023-03-15 08:45 | 2023-03-15 17:00 | 2023-03-15 09:30
MSA-DFES | WA6707770 | 1 | Complete Pest Management Services | Building - Mosquito infestation | Pest Control | General Pest | 207.44 | Pass | Pass | 0 | 0 | 0.75 | 2023-03-13 09:01 | 2023-03-14 17:00 | 2023-03-13 13:00 | 2023-03-14 17:00 | 2023-03-13 13:45
MSA-DTAG | WA6721589 | 1 | GPS Plumbing & Gas Services PtyLtd | Ladies toilets - Sink blocked unable to push plug up - filling with water | Plumbing & Drainage | Drainage | 129.6675 | Pass | Pass | 0 | 0 | 0.75 | 2023-03-14 09:59 | 2023-03-15 17:00 | 2023-03-14 13:30 | 2023-03-15 17:00 | 2023-03-14 14:15
MSA-DTAG | WA5413458 | 2 | Dormakaba Australia Pty Ltd | Front door - Front automatic door malfunctioning | Building | Automatic Doors | 1290.62 | Pass | Pass | -1 | -1 | 0.73333 | 2022-05-12 11:13 | 2022-05-17 17:00 | 2022-05-12 14:43 | 2022-05-17 17:00 | 2022-05-12 15:27 |  |  | Inspected door and found both safety p.e beam sensors failed, unable to replace p.e beam sensors due to cables get jammed in between the door frame, fitted new ixio sensor with pib kit , tested door operation a number of times, all working fine.
MSA-DCA | WA5549213 | 3 | ACTION GLASS & ALUMINIUM | Staircase glass panel -New glass panel installed on level 6 has a crack, water getting inside | Glazing | Window Glass | 130 | Pass | Pass | 0 | 0 | 0.73333 | 2022-06-17 14:39 | 2022-06-24 17:00 | 2022-06-23 08:20 | 2022-06-24 17:00 | 2022-06-23 09:04 |  |  | No glass Brocken no leaks from windows because internal.
MSA-DCA | WA6388179 | 1 | Techworks Electrical | Level 1 - Female Toilet - Auto light sensor is faulty, investigate and repair | Electrical | Lighting, Internal | 183.015 | Pass | Pass | 0 | 0 | 0.73333 | 2022-12-21 12:11 | 2022-12-22 17:00 | 2022-12-21 14:00 | 2022-12-22 17:00 | 2022-12-21 14:44 |  |  | Checked all toilets found no lighting fault
MSA-DCA | WA6689734 | 1 | GPS Plumbing & Gas Services PtyLtd | loading bay - eye wash faulty - see notes | Plumbing & Drainage | Water | 196.4575 | Pass | Pass | 0 | 0 | 0.73333 | 2023-03-08 15:03 | 2023-03-09 17:00 | 2023-03-09 12:48 | 2023-03-09 17:00 | 2023-03-09 13:32
MSA-DFES | WA6400018 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Ground - Firefighters Toilet - toilet seat is loose | Plumbing & Drainage | Toilets/Cisterns | 145.1475 | Pass | Pass | -1 | -1 | 0.73333 | 2023-01-03 08:56 | 2023-01-10 17:00 | 2023-01-03 13:30 | 2023-01-10 17:00 | 2023-01-03 14:14
MSA-DCA | WA5100149 | 3 | GPS Plumbing & Gas Services PtyLtd | Restricted access stack area(south end of stack)- Cold water tap at basin near unpacking area faulty | Plumbing & Drainage | Water | 120.5025 | Pass | Pass | -1 | -1 | 0.73333 | 2022-02-02 11:19 | 2022-02-09 17:00 | 2022-02-03 09:31 | 2022-02-09 17:00 | 2022-02-03 10:15 |  |  | Replace broken aerator on spout. Access hard to get into area as restricted zone
MSA-DCA | WA5994356 | 1 | GPS Plumbing & Gas Services PtyLtd | Technical Store - Water Leak in technical store - Please investigate | Plumbing & Drainage | Water | 145.04 | Pass | Pass | 0 | 0 | 0.73333 | 2022-10-05 15:46 | 2022-10-06 17:00 | 2022-10-06 14:14 | 2022-10-06 17:00 | 2022-10-06 14:58 |  |  | Investigate water leak. No issue found
MSA-DCA | WA6001046 | 1 | GPS Plumbing & Gas Services PtyLtd | water dripping on the ceiling panels above Debbie’s desk - see notes below | Plumbing & Drainage | Water | 119.4775 | Pass | Pass | 0 | 0 | 0.73333 | 2022-10-10 12:00 | 2022-10-11 17:00 | 2022-10-10 12:56 | 2022-10-11 17:00 | 2022-10-10 13:40 |  |  | Investigated a water leak dripping on the ceiling in one of the offices. No water pipes and it only drips when it rains. A roof plumber is required
MSA-DTWD | WA6132495 | 1 | Dormakaba Australia Pty Ltd | Near reception - auto door not working - have to open manuallly | Building | Automatic Doors | 583.94 | Pass | Pass | 0 | 0 | 0.73333 | 2022-10-31 14:28 | 2022-11-01 17:00 | 2022-10-31 14:59 | 2022-11-01 17:00 | 2022-10-31 15:43 |  |  | Inspected door and found that the battery backup had failed and required replacing, also the mode board was heavily corroded. Replaced 2x 12v batteries and 1x mode board. Checkedover and tested operation upon completion and left in good working order.
MSA-DCA | WA5105993 | 0 | GPS Plumbing & Gas Services PtyLtd | Crew and king kitchen experiencing flooding | Plumbing & Drainage | Water | 251.815 | Pass | Pass | 0 | 0 | 0.71667 | 2022-02-05 16:07 | 2022-02-05 18:07 | 2022-02-05 16:57 | 2022-02-05 20:07 | 2022-02-05 17:40 |  |  | Cleared blocked floor drain flooded by leaking coffee machine compressed.Isolated water supply and tagged out coffee machine.Contractor booked to fix the coffee machines
MSA-DTAG | WA5106842 | 2 | Dormakaba Australia Pty Ltd | Level 10 - Comms Room - Security door to comms room is faulty and unsecure | Building | Security Doors | 235 | Pass | Pass | 0 | 0 | 0.71667 | 2022-02-07 12:10 | 2022-02-10 17:00 | 2022-02-08 08:26 | 2022-02-10 17:00 | 2022-02-08 09:09 |  |  | Manual slider to comms room.On inspection, found timber board that track is secured to is loose.Advised management that a carpenter needs to attend to resolve this issue as there will be timber boards to be removed, plaster and painting required.
MSA-DFES | WA5163932 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | second floor - male toilets - last cubicle toilet is block | Plumbing & Drainage | Water | 144.7825 | Pass | Pass | 0 | 0 | 0.71667 | 2022-02-18 13:40 | 2022-02-21 17:00 | 2022-02-18 14:00 | 2022-02-21 17:00 | 2022-02-18 14:43 |  |  | Located to second floor male toilets due to they are blocked found it was the far toilet plunged and cleared the blockage did paper tests and all working correctly now.
MSA-DTAG | WA5204263 | 1 | AHS Services WA Pty Ltd (Anchor) | Ground - Staff Female Toilet - Water flowing and not stopping in one of the cisterns | Plumbing & Drainage | Toilets/Cisterns | 134.7725 | Pass | Pass | -1 | -1 | 0.71667 | 2022-03-04 09:22 | 2022-03-08 17:00 | 2022-03-04 12:17 | 2022-03-08 17:00 | 2022-03-04 13:00 |  |  | Completed
MSA-DFES | WA5238678 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Fire fighters toilets - Room 20 - blocked toilets | Plumbing & Drainage | Toilets/Cisterns | 162 | Pass | Pass | 0 | 0 | 0.71667 | 2022-03-16 08:09 | 2022-03-17 17:00 | 2022-03-16 10:17 | 2022-03-17 17:00 | 2022-03-16 11:00 |  |  | Had to plunge toilet next to Room 20 did paper test and check everywhere else and everything is running fine
MSA-DTWD | WA5469977 | 1 | Dormakaba Australia Pty Ltd | East Entrance - Automatic Door - stuck in the open position wont move from open position | Building | Automatic Doors | 235 | Pass | Pass | 0 | 0 | 0.71667 | 2022-05-23 07:10 | 2022-05-23 17:00 | 2022-05-23 09:12 | 2022-05-23 17:00 | 2022-05-23 09:55 |  |  | 1064275 cleaned sensors and PE tested auto door working ok.
MSA-DTWD | WA5479508 | 2 | LIGHTHOUSE LOCKSMITHS | A-Block shed - Shed key broken off in lock | Security | Locksmith | 126 | Pass | Pass | 0 | 0 | 0.71667 | 2022-05-27 10:00 | 2022-06-01 17:00 | 2022-05-31 10:00 | 2022-06-01 17:00 | 2022-05-31 10:43 |  |  | removed broken key from roller door lock, serviced lock and replaced key
MSA-DCA | WA5570417 | 1 | TK Elevator Australia Pty Ltd | Level 2 - Lift 7 broken down again - displaying Out of Order- See notes below | Lifts | Lifts |  | Pass | Pass | 0 | 0 | 0.71667 | 2022-06-28 10:53 | 2022-06-29 17:00 | 2022-06-28 13:26 | 2022-06-29 17:00 | 2022-06-28 14:09 |  |  | Lift7 Greem Rm-Hydraulic :Lift stopped with run time errors, replaced all pilot relays in lift 6&7, ran lift extensively and returned to service.
MSA-DCA | WA5799979 | 0 | Dormakaba Australia Pty Ltd | Front fo house glass sliding automatic doors are not closing properly | Building | Automatic Doors | 350 | Pass | Pass | 0 | 0 | 0.71667 | 2022-08-30 21:07 | 2022-08-30 23:07 | 2022-08-30 22:35 | 2022-08-31 01:07 | 2022-08-30 23:18 |  |  | Door operating correctly on arrival, after further inspection found that the unit is 20 years old and in poor condition. The aged unit is showing signs of wear and could be intermittently failing, the keyswitch is very worn and the exit button is sticky. The track wheels are also worn and the doors roll open when in the closed position, the bogie pins are snapped making it very difficult to adjust the door height, i managed to adjust the doors slightly as they were leaving a larger gap at the bottom.My recommendation is to upgrade the door and replace the track wheels/bogies for reliable operation.Quotation required to replace with an el301 locking upgrade kit, pib kit and ixio, new sk4, p2, 6x 12mm bogies with heavy duty track wheels, 2x techs required for frameless glass doors.
MSA-DCA | WA5832514 | 1 | Dormakaba Australia Pty Ltd | Alexander Library Building - North entrance inner door - faulty door sensor | Building | Automatic Doors | 688 | Pass | Pass | 0 | 0 | 0.71667 | 2022-09-05 13:43 | 2022-09-06 17:00 | 2022-09-05 14:47 | 2022-09-06 17:00 | 2022-09-05 15:30 |  |  | Inspected door and found external sensor was sticking due to internal sensor fault. Replaced faulty sensor, checked all fixings, tested door operation a number of times. Left door in good working condition.
MSA-DFES | WA6393200 | 3 | Anvil Doors | Ground - Engine Room - The door is not fully closing prior to touching the floor surface | Building | Roller Shutters | 3384.5 | Pass | Pass | -1 | -1 | 0.71667 | 2022-12-28 10:46 | 2023-01-05 17:00 | 2022-12-29 16:47 | 2023-01-05 17:00 | 2022-12-29 17:30
MSA-DTWD | WA6682094 | 2 | Water2water Pty Ltd | Water filter needs replacing | Plumbing & Drainage | Water | 298.535 | Pass | Pass | 0 | 0 | 0.71667 | 2023-03-02 15:26 | 2023-03-08 17:00 | 2023-03-07 08:50 | 2023-03-08 17:00 | 2023-03-07 09:33
MSA-DFES | WA5204389 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Dorm 4 - Shower - shower head snapped off | Plumbing & Drainage | Water | 174.31 | Pass | Pass | -1 | -1 | 0.7 | 2022-03-04 10:17 | 2022-03-08 17:00 | 2022-03-04 12:05 | 2022-03-08 17:00 | 2022-03-04 12:47 |  |  | Replaced shower head
MSA-DCA | WA5603341 | 1 | GPS Plumbing & Gas Services PtyLtd | Ground Floor - Female Toilets - Toilet out of order, please investigate | Plumbing & Drainage | Toilets/Cisterns | 143.77 | Pass | Pass | 0 | 0 | 0.7 | 2022-07-12 10:00 | 2022-07-13 17:00 | 2022-07-12 13:46 | 2022-07-13 17:00 | 2022-07-12 14:28 |  |  | Replaced faulty inlet valve in ground floor female toilet LHS
MSA-DFES | WA6684031 | 1 | Securex Security Systems & Services | Heritage Shed - Faulty movement sensor for security system | Security | Monitoring | 312.73 | Pass | Pass | -1 | -1 | 0.7 | 2023-03-03 16:02 | 2023-03-07 17:00 | 2023-03-03 16:03 | 2023-03-07 17:00 | 2023-03-03 16:45
MSA-DTWD | WA5307074 | 1 | Dormakaba Australia Pty Ltd | D21 - Foyer Auto doors won't close on Auto | Building | Automatic Doors | 436.19 | Pass | Pass | 0 | 0 | 0.7 | 2022-04-07 09:23 | 2022-04-08 17:00 | 2022-04-07 10:57 | 2022-04-08 17:00 | 2022-04-07 11:39 |  |  | Found that one of the pe sensors has failed, replaced faulty sensor and tested, all ok.
MSA-DCA | WA5473418 | 1 | Dormakaba Australia Pty Ltd | Main Gallery - ground - Roller door damaged due to bin getting stuck, not currently operational | Building | Automatic Doors | 220 | Pass | Pass | 0 | 0 | 0.7 | 2022-05-24 14:49 | 2022-05-25 17:00 | 2022-05-24 15:38 | 2022-05-25 17:00 | 2022-05-24 16:20 |  |  | Inspected door and found that the roller shutter starter had tripped, reset as necessary, checked over roller shutter and tested operation upon completion and left in good working order
MSA-DTAG | WA5511860 | 1 | Dormakaba Australia Pty Ltd | Admin - Front entrance/exit to Complex- automatic door has stopped working- see notes below | Building | Automatic Doors | 235 | Pass | Pass | 0 | 0 | 0.7 | 2022-06-13 10:13 | 2022-06-14 17:00 | 2022-06-13 12:57 | 2022-06-14 17:00 | 2022-06-13 13:39 |  |  | 638397 Find there is no 240 volts to ED250 GPO. They will get a electrician to check there switch board.
MSA-DTWD | WA5126452 | 0 | CONNECT SECURITY SYSTEMS | Level 1 - B/T Block alarm panels not arming | Security | Security Management System | 214.45 | Fail | Fail | 0 | 0 | 0.7 | 2022-02-14 07:54 | 2022-02-14 09:54 | 2022-02-14 11:48 | 2022-02-14 11:54 | 2022-02-14 12:30 |  |  | reprogrammed alarm after guards code disapeared from system
MSA-DFES | WA5306100 | 1 | ZAMBEZI PLUMBING & GAS PTY LTD | Kitchen - spout/fawcett - Main kitchen sink - leaking when in use | Plumbing & Drainage | Materials | 182.8 | Pass | Pass | 0 | 0 | 0.7 | 2022-04-06 10:20 | 2022-04-07 17:00 | 2022-04-06 14:03 | 2022-04-07 17:00 | 2022-04-06 14:45 |  |  | Replaced spout
MSA-DTWD | WA5511814 | 1 | Dormakaba Australia Pty Ltd | East entrance -- A-Block East, West entry auto door not opening from outside | Building | Doors | 259.88 | Pass | Pass | 0 | 0 | 0.7 | 2022-06-13 09:26 | 2022-06-14 17:00 | 2022-06-13 11:05 | 2022-06-14 17:00 | 2022-06-13 11:47 |  |  | 1069524, arrived onsite and signed in. Inspected unit and the mode board faulty and replaced it, tested operation in all modes and could not fault.
MSA-DTWD | WA5696772 | 3 | Water2water Pty Ltd | 30Ab: Billi water unit in fault - 114 | Plumbing & Drainage | Water | 300.175 | Pass | Pass | -1 | -1 | 0.7 | 2022-08-08 14:25 | 2022-08-15 17:00 | 2022-08-10 12:40 | 2022-08-15 17:00 | 2022-08-10 13:22 |  |  | System in fault on arrival, filter time out. Replaced Billi filter. Flushed filter and checked under pressure. Waited for unit to get to temp, normal operation
MSA-DFES | WA6125690 | 2 | Water2water Pty Ltd | Zip boil unit in kitchen - hot water not working. See notes | Plumbing & Drainage | Water | 248.995 | Pass | Pass | 0 | 0 | 0.7 | 2022-10-25 07:19 | 2022-10-27 17:00 | 2022-10-25 14:10 | 2022-10-27 17:00 | 2022-10-25 14:52 |  |  | Replaced hot pump and tested. All good
MSA-DCA | WA5679060 | 2 | GPS Plumbing & Gas Services PtyLtd | Parking area outside door DG/18-Blocked drain - see notes | Plumbing & Drainage | Drainage | 119.4775 | Pass | Pass | 0 | 0 | 0.68333 | 2022-07-26 10:17 | 2022-07-29 17:00 | 2022-07-26 15:10 | 2022-07-29 17:00 | 2022-07-26 15:51 |  |  | Cleared blocked storm water drain in the parking area outside door DG18.
MSA-DTAG | WA5101866 | 1 | Gilmour & Jooste Electrical | Ground - Power outage in Court 1 and 3 – only effecting hearing loop receivers | Electrical | General Electrical | 97.2525 | Pass | Pass | 0 | 0 | 0.68333 | 2022-02-03 15:52 | 2022-02-04 17:00 | 2022-02-04 11:30 | 2022-02-04 17:00 | 2022-02-04 12:11 |  |  | Inspected faulty power to court’s 1 & 3, no faults evident. Advised court management. Will inspect again on routine maintenance job.
MSA-DTWD | WA5150726 | 1 | Dormakaba Australia Pty Ltd | room A115 - auto door not working | Building | Doors | 180 | Pass | Pass | 0 | 0 | 0.68333 | 2022-02-17 08:07 | 2022-02-18 17:00 | 2022-02-17 08:30 | 2022-02-18 17:00 | 2022-02-17 09:11 |  |  | Found that the break glass has been activated, reset and tested, all ok. Checked all boards for corrosion, they all look new.
MSA-DTWD | WA5381605 | 2 | Water2water Pty Ltd | Block F - Level 1 - METAL Fabrication drinking fountain blocked no water coming out F/Block | Plumbing & Drainage | Water | 309.265 | Pass | Pass | 0 | 0 | 0.68333 | 2022-04-26 10:07 | 2022-04-29 17:00 | 2022-04-28 11:35 | 2022-04-29 17:00 | 2022-04-28 12:16 |  |  | Bubbler blocked on fountain. Replaced internal bubbler fitting and parts. Normal operation
MSA-DTAG | WA5459870 | 1 | Gilmour & Jooste Electrical | Ground - 2nd Magistrates Office - Water leak via light | Electrical | General Electrical | 129.68 | Pass | Pass | 0 | 0 | 0.68333 | 2022-05-18 09:28 | 2022-05-19 17:00 | 2022-05-18 13:00 | 2022-05-19 17:00 | 2022-05-18 13:41 |  |  | Isolated light with water damaged. Located water leak origin to be blocked down pipe. Court manager (Michelle) advised.
MSA-MRWA | WA5519061 | 2 | Dormakaba Australia Pty Ltd | Level 2 - Foyer auto doors - automatic doors keep opening and closing on their own | Building | Automatic Doors | 220 | Pass | Pass | -1 | -1 | 0.68333 | 2022-06-15 08:52 | 2022-06-20 17:00 | 2022-06-15 11:21 | 2022-06-20 17:00 | 2022-06-15 12:02 |  |  | 1045697/A411120323. Call to site. Check/assess auto door. Find internal safety sensor activating on closure (randomly). Complete fresh calibration and then test for multiple operations, tested operational and safety features. - all okay.
MSA-DCA | WA5586711 | 0 | GPS Plumbing & Gas Services PtyLtd | disabled toilet is blocked | Plumbing & Drainage | Toilets/Cisterns | 153.5975 | Pass | Pass | 0 | 0 | 0.68333 | 2022-07-06 14:00 | 2022-07-06 16:00 | 2022-07-06 14:24 | 2022-07-06 18:00 | 2022-07-06 15:05 |  |  | Cleared blocked disabled toilet drain.
MSA-DTAG | WA5727649 | 1 | AHS Services WA Pty Ltd (Anchor) | Ladies staff toilet in custody smells | Plumbing & Drainage | Toilets/Cisterns | 115.4325 | Pass | Pass | 0 | 0 | 0.68333 | 2022-08-15 10:56 | 2022-08-16 17:00 | 2022-08-15 13:14 | 2022-08-16 17:00 | 2022-08-15 13:55 |  |  | Completed
MSA-DTWD | WA6023036 | 1 | Dormakaba Australia Pty Ltd | L1-G 101 auto door-door not working | Building | Automatic Doors | 654.95 | Pass | Pass | 0 | 0 | 0.68333 | 2022-10-14 14:56 | 2022-10-17 17:00 | 2022-10-14 15:34 | 2022-10-17 17:00 | 2022-10-14 16:15 |  |  | Inspected door and found that the external activation sensor was intermittently failing, supplied and fitted new eagle one sensor as requested by John. Adjusted and tested operation upon completion and left in good working order.
MSA-DCA | WA6255394 | 0 | Techworks Plumbing | Geology - Epoch Cafe - Female toilet continuous flushing | Plumbing & Drainage | Toilets/Cisterns | 135.14 | Pass | Pass | 0 | 0 | 0.68333 | 2022-11-23 10:18 | 2022-11-23 12:18 | 2022-11-23 10:19 | 2022-11-23 14:18 | 2022-11-23 11:00 |  |  | Internal of cistern had misaligned when flushed and got stuck on. I opened the cistern up to removed and install new locking clip. Replaced all parts and tested
MSA-DTWD | WA6560760 | 1 | Dormakaba Australia Pty Ltd | Roller door number 6 not operating | Building | Automatic Doors | 206.95 | Pass | Pass | 0 | 0 | 0.68333 | 2023-02-13 12:45 | 2023-02-14 17:00 | 2023-02-13 13:30 | 2023-02-14 17:00 | 2023-02-13 14:11
MSA-DCA | WA5018479 | 1 | Critical Fire Protection & Training | Main Building - Ground - stage door - Fire Panel Fault in fault, navigational keys unresponsive. | Fire Protection Services | Fire Protection - Monitor System | 114.4324 | Pass | Pass | 0 | 0 | 0.66667 | 2022-01-14 11:57 | 2022-01-17 17:00 | 2022-01-14 14:00 | 2022-01-17 17:00 | 2022-01-14 14:40 |  |  | Buzzer not clearing. Went into internal panel and silenced the buzzer there.
MSA-DCA | WA5086925 | 0 | Critical Fire Protection & Training | Ground Floor- Stage door FIP alarm on fire panel indicates low pressure | Fire Protection Services | Fire Protection - Monitor System | 243.0904 | Pass | Pass | 0 | 0 | 0.66667 | 2022-01-21 17:45 | 2022-01-21 19:45 | 2022-01-21 18:50 | 2022-01-21 21:45 | 2022-01-21 19:30 |  |  | Investigate pressure sprinkler fault. Upon investigation, found 3 valves sitting at 1500 kpa.Dropped them back to 1200 kpa. Panel cleared. Normal.
MSA-DTWD | WA5142252 | 2 | PEEL LOCK SERVICES PTY LTD | A Block - A7 - Lock on door damaged needs replacing | Security | Locksmith |  | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-16 13:59 | 2022-02-21 17:00 | 2022-02-18 12:00 | 2022-02-21 17:00 | 2022-02-18 12:40 |  |  | job copmleted - replaced lock
MSA-DTWD | WA5150679 | 1 | CONNECT SECURITY SYSTEMS | Unable to arm A/C Block | Security | Security Management System | 102.63 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-17 07:45 | 2022-02-17 17:00 | 2022-02-17 12:43 | 2022-02-17 17:00 | 2022-02-17 13:23 |  |  | reprogrammed guards code on both alarm systems to ensure it is not deleted by others
MSA-DTWD | WA5151042 | 2 | Swan Pest Control | Level 2 - Koorlak Offices - Ants and rodents around the offices | Pest Control | General Pest | 270 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-17 10:20 | 2022-02-22 17:00 | 2022-02-22 09:50 | 2022-02-22 17:00 | 2022-02-22 10:30 |  |  | Sprayed perimeter of offices, kitchen and alfresco for ants. Baited for Rodents with ditrac blocks
MSA-DTWD | WA5163747 | 3 | FSA (WA) Pty Ltd | E300 - 4.5kg ABE Powder type Extinguisher area 50 - require replacement | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) | 112.185 | Pass | Pass | 0 | 0 | 0.66667 | 2022-02-18 11:41 | 2022-02-25 17:00 | 2022-02-23 08:15 | 2022-02-25 17:00 | 2022-02-23 08:55 |  | WACCES | Replaced used extinguisher
MSA-DTWD | WA5207328 | 3 | ADVANCED LOCK & KEY | Door lock faulty - will not unlock | Security | Locksmith | 157.5 | Pass | Pass | -1 | -1 | 0.66667 | 2022-03-08 12:22 | 2022-03-15 17:00 | 2022-03-11 12:30 | 2022-03-15 17:00 | 2022-03-11 13:10 |  |  | Repair lock and replaced
MSA-DTWD | WA5226617 | 1 | CONNECT SECURITY SYSTEMS | Block 1 - Faulty alarm panel for Block 10 | Security | Monitoring | 102.63 | Pass | Pass | 0 | 0 | 0.66667 | 2022-03-14 10:24 | 2022-03-15 17:00 | 2022-03-14 12:11 | 2022-03-15 17:00 | 2022-03-14 12:51 |  |  | re-secured resistor in Block 10 Zone Expander. Programmed out spare zones 106-111 to avoid future issues
MSA-DTWD | WA5306394 | 3 | ADVANCED LOCK & KEY | S123 - Repair window lock, large window wont open | Security | Locksmith | 145 | Pass | Pass | -1 | -1 | 0.66667 | 2022-04-06 13:04 | 2022-04-13 17:00 | 2022-04-08 13:15 | 2022-04-13 17:00 | 2022-04-08 13:55 |  |  | Repair window lock
MSA-DFES | WA5377712 | 3 | ZAMBEZI PLUMBING & GAS PTY LTD | Room/ Door 14 - Water ingress, water damage and mould on wall in dorm 14 | Plumbing & Drainage | Water | 109.9 | Pass | Pass | 0 | 0 | 0.66667 | 2022-04-20 08:40 | 2022-04-28 17:00 | 2022-04-26 10:48 | 2022-04-28 17:00 | 2022-04-26 11:28 |  |  | Inspected dorm 14 and 13 for mold but was no able to find the mold in the 2 dorms checked every other dorm and was all clear if it happens again will return for further investigation.
MSA-DFES | WA5460328 | 1 | ACTION GLASS & ALUMINIUM | RETROSPECTIVE WORK ORDER - Repair cracked window - DO NOT ATTEND | Glazing | Window Glass | 358.75 | Fail | Fail | 5 | 5 | 0.66667 | 2022-04-12 13:45 | 2022-04-13 17:00 | 2022-05-16 15:31 | 2022-04-13 17:00 | 2022-05-16 16:11 | 1 |  | *****ORIGINAL WORK ORDER WA5319242 *****"Good afternoon Cliff, We have raised a new work order under WA5460328 for invoicing purposes only, this has been labeled as Retrospective work order for your reference. Thank you and kind regards, Skye McCartney Service Centre Consultant "ATTENDED SITE, MADE SAFE BROKEN GLASS, GOT PUTTY TESTED FOR ASBESTOS, RESULTS CAME BACK POSITIVE, BRAF DECLINED
MSA-DTWD | WA5491291 | 1 | FSA (WA) Pty Ltd | C104 - Fire Fire detection Sensor beeping | Fire Protection Services | Fire Protection - Monitor System | 122.905 | Pass | Pass | -1 | -1 | 0.66667 | 2022-06-03 13:55 | 2022-06-07 17:00 | 2022-06-03 14:20 | 2022-06-07 17:00 | 2022-06-03 15:00 |  |  | Checked panel and no issue with fire panel issue is something else unrelated to fire system in c block. Advised Steve from east Perth and he is all ok and will resolve issue.