MSA-DCS | WA3589864 | yeeda office light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 13:30:00 | Pass | Repaired light
MSA-DCS | WA3589870 | Unit 4 - D Wing Double General Power Outlet on wall adjacent to window is burntout | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 08:30:00 | Pass | Investigate and replace gpo unit 4 D3
MSA-DCS | WA3589875 | zone 14 fence fence tamper alarm wont activate | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 15:15:00 | Pass | Attended site checked and found Zone14 Fence alarm not activating. Checked on field found a lot sensor cable cable tie lose. Recable tied sensor cable and tested fence alarm activated and reset correctly.
MSA-DCS | WA3589879 | Unit 4 - A13 Window has detatched from window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 07 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-07 14:45:00 | Pass | RE NEW SPIRAL BALANCES - WINDOW REFITTED
MSA-DCS | WA3589891 | Unit 4 - D Wing Window fails to open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 10:30:00 | Pass | SPIRAL BALANCE RENEWED
MSA-DCS | WA3589896 | Unit 4 - B6 Window frame/ latch failure | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 09:00:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3589905 | Unit 14 - C Wing north facing window next to the phone is smashed. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-15 14:15:00 | Fail | re glazed window
MSA-DCS | WA3589909 | Unit 1 - B Wing Showers missing cubicle door. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 09:15:00 | Pass | ALL CUBICLE DOORS PRESENT & IN WORKING ORDER
MSA-DCS | WA3589930 | Unit 2 - A & C door weather strip or rubber trim around door is coming off. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 14:00:00 | Pass | NEW DOOR SEAL FITTED
MSA-DCS | WA3589938 | Unit 4, D12 - sink requires leaking pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 10:00:00 | Pass | Nill
MSA-DCS | WA3589942 | unit 7 H5 Cell light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 10:30:00 | Pass | Replaced light switch
MSA-DCS | WA3589964 | Unit 5, Control Room - Handle and lock to control room door faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 08:28:08 | 2020-09-07 14:00:00 | Pass | Attended site and replaced handle to restore normal function
MSA-DCS | WA3589969 | unit 2 control room Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-09 14:55:00 | Pass | PCB required. Quoted on previous job. Closing job.
MSA-DCS | WA3589970 | Unit 7, control room - broken light fitting | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 11:30:00 | Pass | Repaired light
MSA-DCS | WA3589973 | Unit 9, D wing - lights in shower keep tripping | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 15:00:00 | Pass | Repaired shower lights
MSA-DCS | WA3589977 | Unit 8 A & B dayroom Leaking roof | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 08:40:11 | 2020-09-07 13:00:00 | Pass | SOURCE OF LEAK LOCATED & REPAIRED
MSA-DCS | WA3589979 | Unit 7, G wing - leaking shower | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-14 08:45:00 | Fail | Turned off water replacing tap valves and washers and reseating set
MSA-DCS | WA3590000 | Kitchen - roof leaking through a decommissioned air con vent | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-11-23 09:00:00 | Fail | SOURCE OF LEAK LOCATED & REPAIRED
MSA-DCS | WA3590011 | Unit 1, Auto boil not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-08 14:55:00 | Pass | Unit not heating or filling. Incoming water ok. Power ok. Advised by client to try fix outside of warranty if basic repair. Basic issues didn’t rectify issue. Warranty call required. Solenoid tested and ok. Recalibration and reset performed. Didn’t rectify. lodge warranty call with Rheem advised client and programmed
MSA-DCS | WA3590014 | Kitchen - light in range hood not working | Bandyup Prison | GMP-BR- HO | Electrical | Materials (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-16 13:00:00 | Fail | Replaced dilapidated lights under range hood
MSA-DCS | WA3590021 | WWTP sea container light tripping rcd | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 08:30:00 | Pass | Investigate and repair WWTP sea container light
MSA-DCS | WA3590029 | Kitchen - repair potato peeler base as damaged | Wooroloo Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 13:00:00 | Pass | Kitchen Potato Peeler base damaged. Check base, remove damaged hold down bolts. Fit new mungos & bolts. Alter drain & water pipe to suit. Assemble & test.
MSA-DCS | WA3590049 | kitchen, number 6 fridge - not reaching temperature | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 09:20:52 | 2020-09-24 08:15:00 | Fail | Leak check complete. Unit fully operational
MSA-DCS | WA3590061 | Unit 1, Cells 5, 6 &16 - Cell Call issues listed below | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 09:33:56 | 2020-09-07 13:11:00 | Pass | Incorrect namingReprogrammed and tested
MSA-DCS | WA3590129 | Unit 3, Cell D7- Toilet button stuck in & not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 13:00:00 | Pass | Nill
MSA-DCS | WA3590130 | Unit 4 K landing water filter housing leaking | Karnet Prison Farm | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-07 10:30:00 | Pass | Completed. Job used spare filter brought on job number wa3583601. Job start before reported.
MSA-DCS | WA3590189 | Gate control - monitor computer not working | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 13:00:00 | Pass | Collected parts and installed repaired workstation. New Gallagher software installed and upgraded to Windows 10 . Installed programmed and tested ok. Job complete
MSA-DCS | WA3590192 | unit 1 cell B 18 heater gpo broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 10:00:00 | Pass | Investigate and replace unit 1 cell B18 heater gpo
MSA-DCS | WA3590199 | kitchen work area Sinks and floor Drains Blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 10:50:27 | 2020-09-07 15:58:00 | Pass | Unblocked kitchen drain full of grease and rags.
MSA-DCS | WA3590203 | Unit 10, Cell B9- Basin Tap is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-14 15:48:00 | Fail | Turned off water replacing x2 quarter turn taps
MSA-DCS | WA3590206 | Unit 10, B9 - faulty bottom bunk light fitting | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 14:00:00 | Pass | Repaired bed light
MSA-DCS | WA3590210 | INF (10)- Water fountain is constantly dripping | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-16 10:20:00 | Fail | Replaced faucet and filter - checked unit
MSA-DCS | WA3590246 | Unit 7, C Wing - Kitchen Extractor fan vibrating badly, further notes below | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-14 15:45:00 | Fail | 14/09/2020Escorted to site Gain access Turn extractor hood on and test Found noisy and vibrating Extractor is part of building maintenance as tagged by "programme" : unit number A403966115
MSA-DCS | WA3590267 | Abattoir faulty pressure switch on cold water pump | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-21 16:00:00 | Fail | Investigate cold water pump not working. Found faulty pressure switch. Source new switch. Replace switch.
MSA-DCS | WA3590272 | Fire alarm will not reset - Possible break glass broken | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 11:28:31 | 2020-09-08 08:30:00 | Pass | replace break glass
MSA-DCS | WA3590277 | Unit 7, S wing - roof leaking causing Water leaking through light fitting | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 11:27:03 | 2020-09-07 15:30:00 | Pass | REPAIRED & RE SEALED FLASHING
MSA-DCS | WA3590291 | Unit 1, Hut ablutions wall exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-18 11:00:00 | Fail | Investigate unit 1 huts toilet exhaust fan.Source replacement parts.Replace exhaust fan.
MSA-DCS | WA3590312 | Unit 2, D wing - all windows at the end of wing landing, unable to be opened and closed. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-15 11:00:00 | Fail | WINDOW FITTED WITH NEW HARDWARE- NOW FULLY OPERATIONAL
MSA-DCS | WA3590319 | Manual trades cnc room lights faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 11:30:00 | Pass | Investigate and replace manual trades CNC room light
MSA-DCS | WA3590490 | Gatehouse zone 17 - inner perimer fence in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 14:07:18 | 2020-09-07 16:45:00 | Pass | located problem to be faulty splice kit. replace splice kit & tested ok. job complete
MSA-DCS | WA3590512 | Unit 6, Control Room- Exhaust fan in staff toilet not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-15 10:00:00 | Fail | Replaced ex fan
MSA-DCS | WA3590530 | Unit 4C, ablutions exhaust fan is noisy | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 12:00:00 | Pass | Replaced faulty exhaust fan
MSA-DCS | WA3590531 | Metal shop- loose wires n power point | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 14:43:00 | 2020-09-08 10:00:00 | Pass | Replaced cracked pendant outlet
MSA-DCS | WA3590534 | Gardens w/s 80ltr electric storage hot water unit leaking from base | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-08 12:45:00 | Pass | COMPLETED
MSA-DCS | WA3590568 | Fire alarms are activating | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 07 Sep 2020 | 2020-09-07 19:24:47 | 2020-09-08 11:00:00 | Fail | 8/9/20 MBMFIP showing loop 1 short circuit and thermal detector (L1 S53) in Hydrant Pump House missing faults on arrival.Checked underground cabling visually at all accessible pits. No apparent damage or water ingress.Replaced thermal detector and performed loop test, system returned to normal operation.
MSA-DCS | WA3590571 | Door 3 Gate House not working properly | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 15:10:21 | 2020-09-09 13:15:00 | Fail | Adjust door closer and repair latch.Recheck door closing adjustment.
MSA-DCS | WA3590609 | Unit 5, B3 - window sash, requires new spiral balances and catch | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 12:30:00 | Pass | SPIRAL BALANCES & FEET RENEWED
MSA-DCS | WA3592679 | Operations office front gate - Loud noise coming from fan on Gallagher security computer | Pardelup Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Sep 2020 | 2020-09-11 17:00:00 | 2021-03-02 15:30:00 | Fail | Removed fan from unit, cleaned dirt and corrosion from fan drive and tightened drive components.
MSA-DFES | WA3590151 | Bushfire Risk Management Branch & Radio Comms area- Recessed mats- See further details below | DFES Regional Office - Belmont | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-29 14:00:00 | Fail | Entry Matt works as per BRAF
MSA-DFES | WA3590412 | Applied traing ground near tower 2 eyewash station not working properly | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 16:00:00 | Pass | Attend site to investigate eye wash station near Tower 2 not working correctly. Adjusted flow with screw on face of eyewash. All working well.
MSA-DFES | WA3590488 | ground training room carpet tiles are lifting causing trip hazard | DFES Rescue Helicopter Base | GMP-BR | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-17 10:45:00 | Fail | Reglued carpet tiles where lifting in the ground training room
MSA-DFES | WA3590558 | Telephone wall socket is faulty | CFRS Duncraig | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-09 16:00:00 | Pass | Located Faulty cabling at DATA point D1, Fault was in the cable so we utilised the spare point P1. All is working and site is happy with works.
MSA-DTAG | WA3590081 | ground Judge Quail’s bathroom Toilet appears to have a slow leak | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 08:30:00 | Pass | Removed cistern replacing cistern sealing washer on close couple pan
MSA-DTAG | WA3590088 | Staff Carpark - Sewage Pump alarm going off. | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 07 Sep 2020 | 2020-09-07 13:48:34 | 2020-09-07 11:36:00 | Pass | Complete
MSA-DTAG | WA3590334 | Custody control room - Intercom system in the control room has gone down and is not operating | Joondalup Courthouse | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 07 Sep 2020 | 2020-09-07 16:14:41 | 2020-09-07 16:00:00 | Pass | Repairs to intercom
MSA-DTAG | WA3590395 | ground registry rear door Access card reader faulty | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 10:00:00 | Pass | 8/09/2020 - Dean Simpson & Ryan Vesty - Found electric strike to be faulty, replaced and tested.all working.
MSA-DTWD | WA3589861 | rear auto door to open passage doors not respondig to cards properly-see note | Perth Campus B5 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 15:00:00 | Pass | Checked and confirmed that the access control and BGU are operating correctly
MSA-DTWD | WA3589951 | D block L1 D111 Tube has been replaced, light is still out. Light fitting is suspended from ceiling | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-10 11:15:00 | Pass | Job complete
MSA-DTWD | WA3589965 | A block L1 A52 chiller chiller one condenser fan North side not running. (Chiller tripping off line) | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2021-03-29 08:00:00 | Fail | Found 2 contactors siezed Stage a low on gas Stage b oil fault
MSA-DTWD | WA3589985 | A block 10 flouro light fittings not working throughout building, repair or replace with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 13:30:00 | Pass | Arrived on site , signed in, spoke to pfm on site about job , located lighting and discussed with him what was to be done , went to wholesale to pick up materials, returned to site , isolated lighting circuit, replaced 9x Fluros with led batons, tested lighting , all working , cleaned up work area , completed paperwork, signed out, site happy ***job completed ***
MSA-DTWD | WA3590039 | west block ground a various other locations lights not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 10:39:00 | Pass | Repalced faulty light fitting to cleaners store and toilet corridor.job completed
MSA-DTWD | WA3590211 | Block 9 library communitcation alarm fault Education security not recieving montering data | Thornlie Campus | GMP-BR | Security | Monitoring (SE) | CONNECT SECURITY SYSTEMS | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2021-02-24 10:14:00 | Fail | Waiting on High Gain Antenna to improve Telstra Signal to unit. ETA this week
MSA-DTWD | WA3590223 | C block workshop fire alarm above work station keeps going off when welding | Munster Campus (ACEPT) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-10 12:39:00 | Pass | ChangeD two smoke detectors to thermal in welding shed, reprogram fire panel -COMPLETED
MSA-DTWD | WA3590253 | House 18 - no hot water, Unit does not appear to be working (no pilot light, no gas). | Muresk Institute | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Lane's Plumbing | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 17:00:00 | Pass | Repairs made to house 18
MSA-DTWD | WA3590308 | L2 cafe open deck area. Patio type roof area flashing rusted out - see notes | Perth Campus B1 | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 3 | CLOSE | 07 Sep 2020 | 2020-09-14 17:00:00 | 2020-11-26 08:00:00 | Fail | Removed flashings from site and dropped off to central metals to get new ones made up.Picked up flashing from central metals dropped to officeRope access works all complete as per quote
MSA-DTWD | WA3590364 | Tower block, level 4 west- 2x offices carpet is water damaged | West One Services | GMP-BR | Cleaning | Cleaning (CL) | Workzone Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-10 15:00:00 | Fail | Replaced damaged carpet with Lino as per approved BRAF
MSA-DTWD | WA3590407 | 2 ROOM/OFFICE: rear auto door to open passage electrionic board under pelmut appears blown | Perth Campus B5 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-11 15:47:00 | Fail | 7/9/20 - 608837. Found besam large mode/options board has blown and caused door to default to auto mode, advised client that door has had to be left turned off so door can be manually closed and wedged shut until we can return to replace board11/9/20 - Replaced faulty besam unislide mode board. Tested locking, all ok
MSA-DTWD | WA3590439 | E block, ground floor, E300 - We have a leaking tap in hand wash basin, tightening makes it worse | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 13:34:00 | Pass | Replaced spindle on hot tap for basin in automotive workshop
MSA-DTWD | WA3590537 | rooms T102 & T104 be checked two doors are set to free (green) you cant open them from outside | Murdoch Campus | GMP-BR | Security | Access Control (SE) | Total Security Systems Pty Ltd | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 14:30:00 | Pass | 8/9/2020 - Jose Pereira - 2pm to 2.30pmRemoved the 3 second pulse on the door. Door now unlocks from the outside.
MSA-DTWD | WA3590546 | C Block, Foyer - Light fittings not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-10-05 13:35:00 | Fail | Arrived on site, signed in, spoke to fm about lighting, completed jsa, removed old track lights from ceiling, replaced with led wide base lights , tested lights all worked , removed Fluro from ceiling as fm requested, put cables in box in roof space cleaned up work area, completed paperwork, signed out ***job complete***
MSA-DTWD | WA3590573 | U Block, Room U017- Roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 11:00:00 | Pass | Completed repairs to vent systems - site to monitor - vent design problematic, ideally the system would be better removed
MSA-DTWD | WA3590576 | L block, Blocked drain east side of L Block. Jetta machine will be required | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-16 09:59:00 | Fail | Cleared and cleaned out storm water tank
MSA-MRWA | WA3590305 | Outdoor Area, Broken electric conduit, please inspect, remediate | Don Aitken Centre MRWA Head Office-Main Building-Basement-Electrical Equipment Riser | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 11:44:00 | Pass | Repaired broken conduit. All safe now. Job completed
MSA-DCA | WA3590802 | Revolving door Investigate if any water leaks are present within the revolving door - see notes | Maritime Museum Victoria Quay-Main Building | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 09:15:00 | Pass | Technician attended the site of WA Maritime Museum, Revolving Door on 09/09/2020. Following a full test and inspection of door components found fault to be leak repairs. Technician has inspected the door with David De Villiers, as for him to confirm leak repairs organized by him, were satisfactory. David advised he was happy with the temporary silicone repairs and will follow up with Alysia in our office once parts arrive. Full test and inspection of door function completed prior to leaving site..
MSA-DCA | WA3590860 | Investigate and repair roof leak | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-08 13:00:00 | Pass | Have attended and carried out repair. Will need to monitor later this week when we are expecting rain.30/9 - No further leaks reported. Site agreed ok to close off
MSA-DCA | WA3591419 | Dripping pipe outside molecular lab | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Molecular Lab | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 13:20:00 | Pass | Replaced faulty rpz behind molecular lab
MSA-DCS | WA3590687 | L2 & L4 rear of the building 2x light globes blown, also ladies toilets | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 09:30:00 | Pass | Fixed faulty globes level 2 and 4
MSA-DCS | WA3590707 | front gate control transponder 3 has no communication | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Sep 2020 | 2020-09-08 11:17:24 | 2020-10-01 10:33:00 | Fail | Installed replacement Moxa server. Configured and tested Ok. Modified MDAS system to increase data communication efficiency and reliability. Performed backup and tested OKJob CompleteParts used (Seme Stock):Moxa Nport 6000 series.Consumables
MSA-DCS | WA3590748 | Security office workstation offline | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 Sep 2020 | 2020-09-14 17:00:00 | 2020-12-18 11:57:00 | Fail | Attended site and repaired system faults as per Security Officers and PFM.Job Complete
MSA-DCS | WA3590769 | zone 7 - internal microphonic in constants alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 08:11:03 | 2020-09-08 13:00:00 | Pass | Zone 7a ok, 7b regularly alarming. 1M Ohm end of line resistance tested ok. Replaced cable ties. Calibrated and tested ok. Parts used:Consumables
MSA-DCS | WA3590771 | Internal perimeter tracks zone 1 - constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 08:13:50 | 2020-09-08 10:30:00 | Pass | Reset SM module. Ran plot graph of zone. Walk tested and calibrated zone. Tested ok to gatehouse.
MSA-DCS | WA3590773 | Internal microwave, zone 1 - constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 08:14:52 | 2020-09-08 15:30:00 | Pass | Tested input power and alignment voltage. Removed weeds from around the microwaves. Tested ok.
MSA-DCS | WA3590812 | Acad/Acc wing dinning/kitchen ZIP Hydro tap not working.Power to system not to tap.No water-see note | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 14:30:00 | Pass | Replaced filter plv inlet solenoid tap head and hot pump
MSA-DCS | WA3590857 | Unit 5 - B2 B02 door medical hatch lock keeps opening when pulled.- see note | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-08 13:30:00 | Pass | Adjust hatch and lubricate lock.
MSA-DCS | WA3590865 | Turner, Cell A04- Smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 12:30:00 | Pass | CELL WINDOW REGLAZED
MSA-DCS | WA3590890 | MPU (8) - M17 Security require cctv footage download from cell M17 on the 7/9/20 | Casuarina Prison | WSM-MW-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 11:30:00 | Pass | Downloaded cctv video as requested, supplied to a Security SO Operations.
MSA-DCS | WA3590938 | Bakery new (Taglia Vini oven )burner fault ,unable to start or use . | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 09:49:54 | 2020-09-10 16:00:00 | Fail | COMPLETED 10/9/20
MSA-DCS | WA3590953 | Unit 2C, Ablutions - damaged whirly bird | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 09:55:34 | 2021-02-25 12:00:00 | Fail | old damaged whirly bird removed/ new one installed
MSA-DCS | WA3590987 | Unit 4, K02 - spinalds and spot to basin faulty, requiring replacing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-10-05 09:30:00 | Fail | COMPLETED
MSA-DCS | WA3590997 | Gatehouse, control - unable to reset external perimeter zone F04 Microwave - intermittently alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 10:20:18 | 2020-09-08 12:31:00 | Pass | Microwave zone F04 constant alarming. Found vegetation overgrown through zone. Cleared vegetation and retested zone. All tested and working ok
MSA-DCS | WA3591000 | Gatehouse, control room - Unable to reset external perimeter zone G02 microwave in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Sep 2020 | 2020-09-08 14:25:46 | 2020-09-08 11:30:00 | Pass | Perimeter zone G02 microwave constantly activating. Reset microwave and removed relay, cleared out degree from relay, re inserted and retested microwave. All working and alarms all cleared ok. Job complete
MSA-DCS | WA3591002 | Infirmary - rewire faulty lighting (control room and nurses station) | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 07:00:00 | 2020-09-10 15:00:00 | Fail | Found cables wired for infirmary control room and nurses station wired in ELV security cables which was unsuitable for its purpose and needed immediate replacement. Rewired and tested new lights.
MSA-DCS | WA3591011 | Abattoir - front freezer 4, iced up | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 14:00:00 | Pass | essential ref . attend site found coil iced up , de ice coil and found faulty fan motor , replace fan motor and relocate defrost sensor test and left operational.
MSA-DCS | WA3591026 | Kitchen - Tiles around drainage have lifted. | Banksia Hill Detention Centre | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2021-02-23 13:35:00 | Fail | The floor will require epoxy not tile replacement - a quote for epoxy treatment will be sent - a LVM job will need to be issued
MSA-DCS | WA3591044 | Lenard, Cell C03- Shower wont shut off | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-17 10:05:00 | Fail | Replaced button and control box for the shower
MSA-DCS | WA3591045 | ISU D10 Broken view window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 15:00:00 | Pass | NEW OBS PANEL FITTED
MSA-DCS | WA3591047 | ISU, D10 - Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 14:30:00 | Pass | Replaced light switch
MSA-DCS | WA3591060 | Health Centre - Wall mounted Zip Auto Boil leaking water (possibly from tank). | Boronia Pre-release | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 11:20:00 | Pass | Unit was leaking and had corroded through. Replaced unit. REPLACED CAPEX ASSET replaced rusted out Zip Econoboil with new Capex Asset number 2020012305030 Prog No A401402144
MSA-DCS | WA3591080 | computer room, CCTV Footage showing on screens in public areas when being reviewed and investigated | East Perth-Main Building-Level 2 | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 07:56:00 | Pass | Installed a program to view both screens and moved documents over
MSA-DCS | WA3591087 | Admin Kitchen - Hydro tap has low water flow and stops working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 11:28:21 | 2020-09-18 14:46:00 | Fail | Replaced filter inlet solenoid needs replacement alsoUnable to turn off mains water to unit as valve is faulty and needs replacement Could not locate building isolation valvePrison maintenance dept needs to replace valve to BILLI unitReplaced inlet solenoid
MSA-DCS | WA3591090 | Gardens w/s - disconnect & reconnect power to HWS AHS are replacing | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 15:00:00 | Pass | Disconnect and reconnect gardens hws
MSA-DCS | WA3591094 | Gacoyne, Lounge- Power point broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 10:00:00 | Pass | Fixed faulty PowerPoint in Gascoyne lounge
MSA-DCS | WA3591316 | Unit 13, B & D Wing- Metal strip on door frame bent and coming off | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-16 14:45:00 | Fail | New door seal installed
MSA-DCS | WA3591342 | Unit 4, broken retic line behind unit 4 | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-15 11:30:00 | Fail | tested system found broken pipe and replaced.
MSA-DCS | WA3591364 | Education, Music Room - Gas heater still does not function correctly | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-14 13:51:00 | Fail | Low gas pressure to room heater.Cut concrete and install new gas line to room heater in music room.Backfill and replace section of concrete.
MSA-DCS | WA3591377 | perimiter and gym are camera's are not showing on screens or monitor - see note | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Sep 2020 | 2020-09-08 18:20:48 | 2020-09-08 15:30:00 | Pass | investigated gym cameras going offline, reset encoder. tested ok
MSA-DCS | WA3591484 | Zone 1 Perimeter Fence - Not activating after test has been done. | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Sep 2020 | 2020-09-08 21:45:57 | 2020-11-02 12:00:00 | Fail | Attended site and reset zone 1 intelliflex controller, recalibrated zone and retested zone in multiple sections. All had reset and tested working ok. Job complete
MSA-DFES | WA3590805 | next to dinning room male urinal is blocked | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 15:00:00 | Pass | Cleared blockage in change rooms near dinning room
MSA-DFES | WA3590879 | access system for the doors cannot secure pin to building | VFRS Falcon | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 08 Sep 2020 | 2020-09-08 13:25:06 | 2020-09-08 17:30:00 | Fail | Replace Lockwood mechanical code pad
MSA-DFES | WA3591085 | F/F study door fram has come away from the wall preventing door closure | CFRS Vincent | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-09 15:00:00 | Pass | Liam Hanlon (09/09/2020) - Work NoteAttend site Sign in Inspect study door Sub frame coming away from wall fixings had failed Get tools Remove door and closer Undo acoustic seals Remove jamb from sub frame and angle Pull frame out as far as possible Sub frame fixed only with concrete nails shot into brick Drill and fit plugs and screws and wall anchors Re glue jamb and angle Measure openinng so parallel Refix jamb to subframe and secure Clean off excess glue Re hang door and fit closer Check closing correctly *noticed door stop could be causing door to bind if forced open *signed off by SO Steve DFES
MSA-DFES | WA3591350 | back of the station courier vehicle has reversed into pole and bent the pole | VFRS Falcon | GMP-BR | Building | Steel Work (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 08 Sep 2020 | 2020-09-08 17:56:52 | 2020-09-11 16:00:00 | Fail | 09/09/2020 09:11 AM (UTC+08:00) - crispin@protek247.com.au Attended site and assessed damage (roof is on no immediate risk of collapse) carried out make safe by straightening the post. Bunded area with danger tape. Will need to return with new post and materials to install BRAF will be required10/9/20 - scheduled for Sept 11 - New post installed
MSA-DFES | WA3591436 | ***Retrospective WO*** INTRUDER ALARM Z19 REED SWITCH BUNKER DOUBLE DOOR | DFES Regional Office - Belmont | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | COMPFIN | 08 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 08:18:00 | Pass | Job completed - INTERNAL AND EXTERNAL CHECK ALL APPEARS SECURE, CONTRACTORS ON SITE NAMED NATHAN JOHN EDWARDS, COMPANY NAME AWB, CLEARED BY OPS
MSA-DTAG | WA3590795 | L6 All cameras displaying “Connection to Server Failed-see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 12:00:00 | Pass | Resolved issue, however, further investigations into the fault appear to be related to core switches.
MSA-DTAG | WA3590817 | Level 5, Court Monitor Room behind Court 58 - door wont open all the way | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-08 09:20:00 | Pass | CLOSER ARM RESECURED
MSA-DTAG | WA3591294 | ground registry rear door Access card reader faulty - see notes | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 16:30:00 | Pass | 8/09/20 - Dean Simpson - re-terminated power cable for the lock as the connection was broken in the panel. move door function to a spare relay on the door controller.
MSA-DTAG | WA3591306 | External west laneway Several lights outside the sally port roller door have failed - see notes | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 11:30:00 | Pass | Need scissors left to replace globes
MSA-DTWD | WA3590758 | L block L1 staff room HWS faulty | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-09 12:37:00 | Pass | Hot water had been isolated. No evidence of how it happened. But re activated and hot working correctly.
MSA-DTWD | WA3590760 | F block F56 female toilet inlet and oulet rubber boots perished | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 17:04:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3590841 | U Block, Room U022.6, project store under aircon duct- Roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-11 11:30:00 | Pass | Identified areas of ingress/ac penetrations and skylight joint will return to complete.Rusted ductwork to AC Unit - cleaned and sealed, unit is old. Site to monitor eak, skylight may need changing if problem returns
MSA-DTWD | WA3590877 | J Block, Room J004- Repair damaged gutter | Balga Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-10 15:00:00 | Pass | Cleaned and re-sealed gutter joint, sealed and clipped gutters.
MSA-DTWD | WA3590885 | J Block, Carpark 1- Refix bollard to concrete base- see further notes below | Balga Campus | GMP-BR | Building | Steel Work (BU) | AWB Co. | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-10-02 15:00:00 | Fail | Concrete replaced and bollard rescured
MSA-DTWD | WA3590896 | Level 2, Corridoors - Approx 20 lights not working | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 11:15:00 | Pass | Attended site, signed in, spoke to pfm about job , completed jsa, set up work area, replaced various tubes , starters and lampholders , tested alllights and they are working as intended, replaced covers that were broken on lights , cleaned up work area , completed paper work ***job complete***
MSA-DTWD | WA3590952 | A-Block, ground level, A009 - security camera system faulty some cameras are not working | Joondalup Kendrew Campus | GMP-BR | Security | CCTV Surveillance (SE) | BJ SYSTEMS | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 12:45:00 | Pass | Check CCTV Dvtel equipment and CCTV. Cameras conflict with network. IT to rectify IP/Mac address on network. List of cameras given to Dave. Restarted Dvtel machine, browse/ping each camera for site
MSA-DTWD | WA3591016 | Lift stopped working and people are trapped inside | Leederville Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | COMP | 08 Sep 2020 | 2020-09-08 14:34:51 | 2020-09-08 12:15:00 | Pass | Released passenger from lift. Found safety circuit open before T3A, fault cleared whilst testing. Checked likely switches andreturned to service##Due to COVID-19, no signature is requested. Have spoken to customer on works completedTo be closed out at $0
MSA-DTWD | WA3591106 | admin records area lost power to exit and emergency lighting | West One Services | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 13:45:00 | Pass | Job complete
MSA-DTWD | WA3591125 | N Block, N48 Paint Store- Lost light to both fluros | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 14:30:00 | Pass | Arrived on site, located lights that weren’t working, completed jsa, set up work area, removed old tubes and tested light , removed starters and replaced with new starters and tubes , tested lights , all working, cleaned up work area, completed paperwork, signed out *** job complete***
MSA-DTWD | WA3591162 | T bloc, G.F unisex disabled toilet adjacent to cafe - leak from exposed wall toilet cistern | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 13:30:00 | Pass | Replaced water connections
MSA-DTWD | WA3591226 | F1 classroom for Dogs, Reception- High level halogen light not working above reception area | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-10-13 05:30:00 | Fail | Attended site and signed in. Located F1 and found faulty light fitting. Removed all associated parts to light fitting and installed new hi bay led light in place. Tested all okay. Job complete
MSA-DTWD | WA3591231 | D Block, Entrance Door, 2nd floor- Door 249 has a faulty lock release switch | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 13:30:00 | Pass | Sourced, Supplied and Replaced faulty switch with new.
MSA-DTWD | WA3591289 | eastern auto entrance door is not opening | Kwinana Automotive Centre | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 08:08:00 | Pass | 1086363. Found door in lock fault, reset operator and checked over all ok
MSA-DTWD | WA3591348 | Tower block, Level 4 west end - Broken & damaged blinds | West One Services | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-29 15:07:00 | Fail | COMPLETED
MSA-DTWD | WA3591400 | West Block, Rooms W111 to W121- Lights not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 12:30:00 | Pass | Job complete
MSA-DTWD | WA3591411 | lift not showing indicators for all levels | Leederville Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 08 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 12:13:00 | Pass | Found indicators not functioning, rebooted system and checked over connections accordingly. Returned the lift back in service after testing##Due to COVID-19, no signature requested. Have spoken to customer on works completed.To be closed out at $0
MSA-DTWD | WA3591434 | E Block, E74 Kitchen, Lecturers bench Oven – Issue with pilot light | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 08 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-08 16:30:00 | Pass | COMPLETED 8/9/20
MSA-DTWD | WA3591449 | E Block, E30 SSK- Tap leak between stations 12 & 13 | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 15:16:00 | Pass | Fix leaking taps
MSA-DTWD | WA3591453 | P Block - Security lights are not working along the pathway outside P Block | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2021-02-23 10:15:00 | Fail | Investigated fault with security lights outside P block. Could not find fault. Will need to reattend with a 12ft ladder to investigate light fittingsCompleted Collected scissor and installed the last of light. Tested and all in working order. Notified staff and signed out
MSA-DTWD | WA3591459 | A Block, AG23A Staff Toilet- Rattling Exhaust Fan/Light Combo - further notes below | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-30 10:00:00 | Fail | Replaced exhaust/light combo with new
MSA-DTWD | WA3591467 | Block 6, Bricklaying- Blocked sink drains | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-11 11:00:00 | Pass | Clean out and unblock area
MSA-DCA | WA3591712 | Ground Floor, Control Room - No lights can be turned on in the building. Issue with control software | Maritime Museum Victoria Quay-Main Building-First Floor-Control Room | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-11 12:00:00 | Fail | Once there, the end user software controlsoft had a backlog of messages, messages awaiting never changes. So end software seems to be inoperable dueto network conditions Next checked the PC node, with the node unplugged Dynet voltages from the field are bad. Opened commission software andcompleted a network search to see if any controllers are not replying. Some controllers seem to be offline. 4 channel controller #24. Mixed controller.ddmc801 #2. Old controller called project 12 #61 and #62. All panels reporting online. All sensors reporting online. Further investigation required hover asthere is definitely a network issueObserved comms issues. again. Once again, confirmed it wasn't being generated from Controlsoft, or the associated equipment. Began fault-finding the network. Located another DTK622-232 node inthe theatre, but unfortunately, this wasn't causing the problem. However, We did find 2 dimmer units offline, namely boxes 61 and 62 in DB-F. Upon further investigation, f
MSA-DCA | WA3592323 | BMS has lost power - Attention Craig | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-21 18:30:00 | Fail | BMS offline. No power at GPO serving UPS. Steam Boilers in alarm. Contractor had isolated power to GPO. Contractor ran a power lead to supply the UPS. Started server and logged in. Received over 170 alarms as system came on line. Reset RO plant and waited for empty tanks to fill. Once RO, top up, feed tanks were full, Reset the Steam Boilers and monitored. Reset all FCU Humidifiers and VSD for FCU 8. Unable to clear OSN 3, 6, 8 Status Fault Alarms and FCU 7 Humidity alarms, even though the Humidity is within range. Will discuss with controls technician in the morning.On going.Alarms are cleared but stuck on alarm screen. Controls contractor will remove when on site next. Visit scheduled for 22/09/2020.Closed job.
MSA-DCS | WA3591670 | Unit 13 - B & D B/D KITCHEN - sink seems to have a leak in the outlet pipe. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 16:00:00 | Pass | Nill
MSA-DCS | WA3591681 | Unit 2 D16 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 10:30:00 | Pass | Repaired light
MSA-DCS | WA3591687 | Unit 3, A10 - cell call faulty, bussing sound | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 15:33:00 | Pass | Power cycle the unit and tested. Unit 3 A10 Cell call back to normal operations.job completed.
MSA-DCS | WA3591688 | Unit 2 D1 Viewing hatch glass loose and cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 12:00:00 | Pass | GLASS RE-FIT, FRAMEWORK REPAIRS
MSA-DCS | WA3591689 | J zone - PE beam in constant alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-11-19 11:06:00 | Fail | Realign all cells in 3 metre PE beam set for Zone J1. Please note bottom beam set was bypassed and it was obvious that this is because of a design oversite where it conflicts with a fence line. All tested ok.
MSA-DCS | WA3591695 | unit 2 D1 Cell Call Faulty Buzzing Sound | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 12:30:00 | Pass | Tested the cell call and it’s working as normal, no fault was found. Job completed.
MSA-DCS | WA3591717 | unit 4 B14 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 11:30:00 | Pass | Replaced light
MSA-DCS | WA3591724 | kitchen Blast Chiller No 2 Chiller keeps going into Alarm | Hakea Prison | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-24 08:45:00 | Fail | Blast chiller now chilling to setpoint within required time.
MSA-DCS | WA3591736 | unit 1 A6 Cell Call Faulty. Constantly displaying active status | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 15:00:00 | Pass | Replaced defective cell call with new , tested ok and working. Job completed.
MSA-DCS | WA3591761 | unit 1 C2 GPO broken sink side | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 13:00:00 | Pass | Replaced gpo
MSA-DCS | WA3591776 | Gate Control Room - Text "Program Pattern 1 Remaining Storage 73%" | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-09 11:00:00 | Pass | Contacted site and found network issue on Indigo PC. Reset workstation and checked hard rive fault. All tested and cleared ok. Job complete
MSA-DCS | WA3591787 | key issue PAT alarm 88 not workiing - SEME on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 09:27:09 | 2020-09-09 11:30:00 | Pass | Job complete
MSA-DCS | WA3591848 | sallyport door in the gate house lock reciever not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 09 Sep 2020 | 2020-09-09 14:01:56 | 2020-09-09 15:15:00 | Fail | Made new fitting for Sally Port door Receiver ( Electronic Lock / Strike )Door Frame cut out to suit and mounting block fitted .
MSA-DCS | WA3591924 | unit 2 outside top landing damaged coaxial cable | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 14:00:00 | Pass | Repaired damaged MAW cables in Unit 2. Tested, OK.
MSA-DCS | WA3591937 | Monitor Room- Controller 6 intermittent bus fault | Boronia Pre-release | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 11:11:16 | 2020-10-06 10:08:00 | Fail | Investigated intermittent I2C Communication fault with controller 6. Found this is an internal communication bus fault between processor and real-time clock circuit.Installed replacement controller, programmed and tested OK.Monitored for correct operation.Parts Used: 1 x Gallagher 6000 controller
MSA-DCS | WA3591941 | Unit 1, Control Room- Air Con has mould growing in it. | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 11:30:00 | Pass | Cleaned entire unit removed all debris. All ok
MSA-DCS | WA3591979 | Lights out and light covers for those without covers- see list below | Mandurah | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-10-16 13:00:00 | Fail | Fixed faulty lights and investigated light coversReplaced 18x down lights
MSA-DCS | WA3591988 | EC1 powerfence offline - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-25 10:00:00 | Fail | removed trophy fence controller, installed 2x new F32 Gallagher fence controllersReconfigured cabling and programmed into Gallagher.Tested fence zone and confirmed correct operation
MSA-DCS | WA3591990 | Time sync across the site is incorrect - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-23 21:30:00 | Fail | Installed timesync server into rack 1 and cabled GPS receiver into control room for optimal GPS signal. programmed all servers and workstation to time server.They will sync every 15 minutes
MSA-DCS | WA3591994 | MWL zone 12 TX constant alarm - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-19 17:51:00 | Fail | Removed faulty MPS 4100 and replaced with Ultrawave.mounted ultrawave to post, programmed and calibrated.confirmed activation when performing walk test
MSA-DCS | WA3591997 | Communications room WS monitor has failed - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-16 13:42:00 | Fail | Removed faulty Monitors and disposed.installed 2 new monitors
MSA-DCS | WA3591999 | ICF monitor has failed . - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-16 13:40:00 | Fail | Removed faulty monitor and disposed.removed temporary monitor and installed new monitor
MSA-DCS | WA3592003 | Zone 5 PE in constant alarm. - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-19 17:52:00 | Fail | Replaced PE beam and aligned.confirmed correct operation
MSA-DCS | WA3592008 | Pedestrian gate not operating. - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-24 21:00:00 | Fail | Replaced relay and relay holder.Reconfigured cabling and programming for new relay.Control tested door operation from Gallagher, confimred correct operation.Tested override and confirmed working Parts used from Seme stock 24vdc relay and relay holder
MSA-DCS | WA3592013 | PTZ 3 camera distorted - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-11-11 15:20:00 | Fail | job to be invoiced at cost. a new work order WA3742241 was raised to complete the job
MSA-DCS | WA3592016 | Unit 1 office controller offline - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-09 14:10:00 | Pass | Controller offline, heartbeat lightno controller indicating failure.Attempted to factory reset, controller still offlineReplaced with site stock
MSA-DCS | WA3592020 | Spiritual centre unable to alarm - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-09 14:05:00 | Pass | Controller unable to hold firmware and software.Factory reset controller and attempted to reprogram. Still not working, replaced controller with site stock.Controller operational
MSA-DCS | WA3592059 | Unit 4, Control Room- Indigo system has gone down | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Sep 2020 | 2020-09-09 20:15:18 | 2020-09-10 13:00:00 | Fail | Replaced failed Indigo Workstation PC
MSA-DCS | WA3592113 | unit 1 cell 3 ceiling fan faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 10:00:00 | Pass | Replaced ceiling fan
MSA-DCS | WA3592133 | Unit 2, Cell A15- Taps are broken & leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 12:55:05 | 2020-09-10 10:30:00 | Pass | Completed, 1 x enware qtr turn detention spindle replaced.
MSA-DCS | WA3592134 | Unit 2, Cell A16- Tap are broken & leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 13:02:58 | 2020-09-10 10:00:00 | Pass | COMPLETED
MSA-DCS | WA3592136 | Unit 2, Cell A18- Tap is broken & leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 13:03:34 | 2020-09-10 09:15:00 | Pass | COMPLETED
MSA-DCS | WA3592145 | Unit 2, Outside Cell D1, 500x300- floor patching | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 12:56:50 | 2020-09-09 18:25:00 | Pass | damaged patch repaired
MSA-DCS | WA3592147 | Yeeda, C06 - toilet not flushing | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-17 12:49:00 | Fail | Relaced faulty button and control box for the toilet
MSA-DCS | WA3592194 | Unit 2, Cell A18- 1200x600- floor patching | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 13:47:19 | 2020-09-23 14:30:00 | Fail | DAMAGED AREA'S OF VINYL UPLIFTED & REPLACED
MSA-DCS | WA3592197 | Vinyl on stairs is lifting | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 13:51:08 | 2020-11-09 10:20:00 | Fail | vinyl on stair treads re glued
MSA-DCS | WA3592234 | Unit 9, B wing - Water leak in storeroom resulting in B wing flooding | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 14:12:02 | 2020-09-09 17:00:00 | Pass | Replaced 800mm section off burst pipe
MSA-DCS | WA3592288 | Gatehouse- Rear sally port doors are extremely nosiy when opening & closing | Casuarina Prison | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-11 09:30:00 | Pass | 10/09/20Attended site but could not begin work. No escort available.11/09/20Lubricate pins on sally port hinges. East, West front and rear door hinges all lubricated.
MSA-DCS | WA3592302 | Gate House - Lock fault on keywatcher door #3. - see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-11 09:00:00 | Pass | Replace lock body.
MSA-DCS | WA3592342 | Main prison gate control- indigo workstation keyboard fault | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-10 16:00:00 | Pass | Checked operation of keyboard, confirmed failure. Installed replacement keyboard and mouse. Confirmed operation.
MSA-DCS | WA3592394 | Gatehouse - Duress system having transponder failures | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Sep 2020 | 2020-09-10 01:42:34 | 2020-09-10 11:00:00 | Fail | Call back to prison and confirmed that workshop power back to normal already. MDAS EC cabinet back to normal working condition. Job completed.
MSA-DFES | WA3591801 | Dorm 5 - Window rollers are not working (right hand window) | CFRS Osborne Park | GMP-BR | Building | Windows (BU) | AWB Co. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 14:00:00 | Pass | Toby Bindon (09/09/2020) - Work NoteArrived at site, signed in and inspected faulty window. Picked up materials and returned to site. Removed old damaged rollers and replaced with new. Re-installed window and tested. Works fine now. Tidy area, pack away tools
MSA-DFES | WA3591813 | Heritage workshop- Rat Infestation please irradicate | FESA RHQ - Forrestfield | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-24 14:15:00 | Fail | Carried out a service for rodents at WA Fire and Emergency Services Academy. Installed six rodent stations to the heritage sheds. Monthly follow ups are highly recommended until the infestation is eradicated.Carried out a service for rodents at WA Fire and Emergency Services Academy. Inspected and replenished all existing rodent stations. Monthly follow ups recommended.
MSA-DFES | WA3591854 | Gym ground Air Conditioner will not turn off. | CFRS Joondalup | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 14:30:00 | Pass | Found air-con remote had lost Its code, reprogrammed the remote and tested. All ok.
MSA-DFES | WA3591914 | Staff Change Rooms- Toilet button sticking, further notes below | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-10 10:32:00 | Pass | Fit new cistern
MSA-DTAG | WA3591741 | Lvl 10, Staff Kitchen - Filtered tap water has very chlorine taste – may need filter changed | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 13:16:00 | Pass | Tested water and flushed filter again on arrival. Drained both tanks and waited for system to fill up. Very old machine. Spoke to Ian, he would like a quote to replace system - INSTALLED NEW CAPEX ASSET BILLI QUADRA COMPACT SN T086110585 PROGRAMMED NO A402011502
MSA-DTWD | WA3591573 | north block L1 N103 lock broken on cleaners store door | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 09 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 15:15:00 | Pass | secured handle to N103 Cleaners store
MSA-DTWD | WA3591882 | E Block, Restaurant - Interleading Auto door has a loud squeak when opening and closing | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-09 13:16:00 | Pass | Found that the floor guide was squeaking, lubricated guide and tested, all ok
MSA-DTWD | WA3591904 | E Block, Restaurant- 4x down ceiling lights not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-10 11:35:00 | Pass | Faulty lights in E block supplied and replace with LED lights
MSA-DTWD | WA3591951 | L Block, Alarm system is showing system fault. | Balga Campus | GMP-BR | Security | Monitoring (SE) | Casa Security Pty Ltd | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 10:15:00 | Pass | Rectified tamper fault
MSA-DTWD | WA3592051 | A Block, Front Carpark- lights not working perimeter lights Oxford Street Carpark | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-12 08:45:00 | Fail | Attended site and signed in, replaced 1x pole top with new and replaced 2x globes to fittings. Tested all working fine. Job complete.
MSA-DTWD | WA3592076 | Tower block, level 1 men toilet - urinal flush button is broken | West One Services | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-11 09:00:00 | Fail | Complete
MSA-DTWD | WA3592137 | G block ground workshop various - Possums entering workshop and messing everywhere - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-10-08 08:30:00 | Fail | Applied a repellant pesticide around the entry points to deter the possum off the area
MSA-DTWD | WA3592157 | Level 2, Mail room - electrical cables in mail room have become exposed | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 10:56:00 | Pass | Repaired gpos and data point in mail room and W606
MSA-DTWD | WA3592188 | Rear courtyard, Level 1 - feature fountain not working | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-10 13:54:00 | Pass | Complete
MSA-DTWD | WA3592206 | D block, Level 1, Exterior Courtyard - Sub Surface retic to Greenskills garden is running constantly | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | LD TOTAL | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 10:10:00 | Pass | Valve stuck on manual, fix damaged dripline
MSA-DTWD | WA3592219 | Tower level 1, south - Loose roof tile | West One Services | GMP-BR | Roofing | Tiled Roofing (RF) | AWB Co. | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-10 09:10:00 | Pass | As per attached sig slip
MSA-DTWD | WA3592229 | A Block, Room A13- Faulty 4’ light fitting (replace with LED) | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 14:45:00 | Pass | Attended site and signed in. Located faulty light. Went to wholesaler to pick up suitable replacement. Isolated power and replaced light. Re energised and tested. All ok. Completed paperwork and signed out. Job complete
MSA-DTWD | WA3592254 | Level 1, B155 - projector screen has fallen down | Perth Campus B6 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-21 08:30:00 | Fail | Liam Hanlon (15/09/2020) - Work NoteAttend east Perth site as per work orderNoticed reported by Brett not Steve Meyer Spoke to Steve at east Perth not one of his jobs Should be Aberdeen street Left site and drove to correct location Spoke to Brett and got keys issued Inspected room and new screen to be installed Got tools out Removed one bracket and re locate Class commencing Had to vacate and pack up Informed staff will return tomorrow to complete Liam Hanlon (21/09/2020) - Work NoteRe attend Measure and move brackets to match new projector screen length etc Drill and fit plugs Mount brackets and hang new screen Clean up
MSA-DTWD | WA3592273 | Lvl 4, C401- skirting board that runs along an office wall that has come adrift | Perth Campus B1 | GMP-BR | Carpentry | Joinery (CA) | AWB Co. | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 11:00:00 | Pass | Liam Hanlon (15/09/2020) - Work NoteAttend site Sign in and get keys Inspect skirting and area Get tools Remove nails Glue and tape whilst drying Repair skirting on wall behind Remove tape after some time Glue not gone off Got nails and fixed off Cleaned up
MSA-DTWD | WA3592311 | A Block, Room A250 Lecture theatre- lights not working, see notes below | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-23 12:19:00 | Fail | Repalced faulty light fittings with new in lecture heater.job completed
MSA-DTWD | WA3592349 | Level 3, female staff toilets - toilet running constantly | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 15:18:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3592354 | Lvl 1, Room B139-B133- Classroom door doesnt lock | Perth Campus B6 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 09 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 11:00:00 | Pass | repairs to lock
MSA-DTWD | WA3592363 | L Block, Security light not working Near Gate 1 | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-16 15:00:00 | Fail | Inspected L block floodlight. Tested cabling to light ,fault is present , reconnected cabling and tested lights stayed on and hasn’t tripped. Advised site of cable issue. Job completed
MSA-DTWD | WA3592364 | U Block security lights are not working around the building possible PE cell issue. | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-10-06 13:30:00 | Fail | Repalced faulty pe cell on roof.tested lights job completed
MSA-DTWD | WA3592366 | Q Block security light keep tripping the circuit breaker. | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 10:30:00 | Pass | Inspected lights to Q block. Tested and left on all day didn’t trip. All security lights are working. Job completed
MSA-DTWD | WA3592367 | Blocked ladies toilet | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 10:00:00 | Pass | unblocked toilet
MSA-DTWD | WA3592368 | M Block security lights are not working in various areas. | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 09 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-18 09:24:00 | Fail | Replaced faulty lamps to m block security lights .job completed
MSA-DTWD | WA3592372 | Block 8, Room 8F54- Rat activity | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-10 09:00:00 | Pass | Baiting to control rodents (rats reported). Baits in locked stations to discreet spots on ground level. Could not bait roof void (sealed, slatted construction - not accessible)
MSA-MRWA | WA3591826 | Lvl 2, Female toilet- Cistern continually running, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Second Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-09 15:35:00 | Pass | Replaced outlet washer. Wrong details uploaded on the work order. Nothing weong with the cubicles in the female’s toilet
MSA-MRWA | WA3591828 | Lvl 1, Male Toilet- Urinal out of service, please remediate | Don Aitken Centre MRWA Head Office-Main Building-First Floor-A1.02-Toilet and Shower-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-09 17:28:00 | Pass | Investigated faulty cistern. Replaced few parts but cistern still not operating as it should. New cistern required. Fixed leaking cistern instead in the same plumbing duct(lhs)-Brendan’s request. Rpelaced inlet valve and the outlet rubber
MSA-DCA | WA3592709 | not flushing toilet in cubicle | Art Gallery of WA - James St-Main Building (Block B)-Level 3-Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-10 13:07:00 | Pass | Service and adjusted toilet cistern.Flushing button was jammed.
MSA-DCA | WA3593005 | Exit door near collection box 4- Emergency Exit Light no. 176 is out | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 12:00:00 | Pass | Failed EXIT light replaced with new
MSA-DCA | WA3593176 | Potential trip hazard formed in walkway to stage door where a hole has formed in paving. notes below | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Door Entrance Area | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-11 11:00:00 | Pass | Attended site, removed damaged bricks, leveled and fitted new pavers to complete
MSA-DCA | WA3593220 | Emergency light not working - Attend before 9am | Subiaco Arts Centre-Main Building-Level 1-Studio | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 17:00:00 | 2020-10-08 09:30:00 | Fail | Arrived on site. Replaced emergency in theatre room and installed another new emergency on other side of theatre room
MSA-DCS | WA3592466 | PTZ 3 camera is not working | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Sep 2020 | 2020-09-10 10:29:18 | 2020-09-10 08:45:00 | Pass | PTZ Camera 3 works in progress to be completed through WA3521070.
MSA-DCS | WA3592522 | dairy HWS not gettting up to temp near dairy office | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 07:14:52 | 2020-09-14 16:00:00 | Fail | COMPLETED
MSA-DCS | WA3592542 | External stores inside door light switch damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 07:25:12 | 2020-09-10 08:30:00 | Pass | Fixed faulty light in external stores
MSA-DCS | WA3592552 | front gate sliding gate Sliding gate access panel on column door lock damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 10 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-10 13:00:00 | Pass | 10/09/20Lubricate lock, check hinges, find the problem. Outside scope of works - locksmith required - unable to remove key once it has been double locked
MSA-DCS | WA3592562 | laundry roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 10 Sep 2020 | 2020-09-16 17:00:00 | 2021-02-25 09:00:00 | Fail | REPAIRS TO SARKING & SEALS REPAIRED/REPLACED
MSA-DCS | WA3592564 | Gate house 2 x lights blown in visitor corridor | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-15 12:00:00 | Fail | Investigate and repair visitor corridor lights in gatehouse.Source replacement and install new light.
MSA-DCS | WA3592584 | internal zone 16 camera 17 not working - seme on site | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 07:57:54 | 2020-09-10 08:30:00 | Pass | No image on EBI. Tested camera at EC in zone 14. No image from camera. Reset power to camera. Image restored. Tested ok back to the gatehouse.
MSA-DCS | WA3592588 | Unit 4 - D12 water leak in sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 07:48:53 | 2020-09-10 10:30:00 | Pass | Prisoner in cell D12 has been twisting the basin tap to either side causing connection under sink to come loose
MSA-DCS | WA3592594 | Unit 14 - A & C vinyl has smalled rips | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-11-02 12:30:00 | Fail | REPAIR TO VINYL SKIRTING - NO DAMAGE VISIBLE TO RUBBER FLOORING
MSA-DCS | WA3592599 | Unit 4 - A11 toilet leaks at the joint with the floor. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-13 11:30:00 | Fail | Job requires braff
MSA-DCS | WA3592603 | security office lost all of camera's not network connection | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Sep 2020 | 2020-09-10 12:16:37 | 2020-09-10 13:26:00 | Fail | Sourced parts, attended site, repaired CCTV faults in security office, ISU unit and gatehouse recording fault.Tested OKJob CompleteParts: Consumables
MSA-DCS | WA3592649 | Hotham A4 bottom lock not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 09:45:00 | Pass | On site. Serviced lock and replaced worn/faulty part. Normal function restored.
MSA-DCS | WA3592654 | Eyre top lock not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 08:15:00 | Pass | 11/09/2020. On site. Requires parts to complete repair. 14/09/2020. Attend site. Supplied and fitted replacement lock cylinder to restore normal function.
MSA-DCS | WA3592712 | Gate house - PTZ cameras unable to swivel | Broome Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 02:54:00 | Pass | Reprogrammed user privileges
MSA-DCS | WA3592753 | Unit 1, Cell A11- top bunk side panel has been broken off | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 09:45:24 | 2020-09-11 14:30:00 | Fail | PANEL RE FIXED TO BED
MSA-DCS | WA3592755 | Unit 1, Cell A11- Door viewing hatch has been smashed | Casuarina Prison | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 09:48:01 | 2020-09-11 10:30:00 | Fail | obs window re glazed
MSA-DCS | WA3592758 | Unit 1, Cell A11- Cell window has been smashed (management style glass panel) | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 09:49:31 | 2020-09-11 13:00:00 | Fail | CELL WINDOW RE GLAZED
MSA-DCS | WA3592793 | Unit 1, Cell A1 - Window Frame has rust spot on the bottom left hand corner | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 09:59:58 | 2020-09-11 09:30:00 | Pass | RUST REMOVED/ FILLED & PAINTED
MSA-DCS | WA3592802 | Outcare- Air Con needs adjusting to a lower temp | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-10 12:30:00 | Pass | Adjusted temperature to cope with heat load all operational
MSA-DCS | WA3592845 | Administration PC crashed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-16 13:35:00 | Fail | Installed new Workstation and programmed.
MSA-DCS | WA3592903 | Unit 6, Cell A2- Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 07:48:00 | Pass | Pulled apart cistern replacing outlet washer and inlet valve
MSA-DCS | WA3592904 | Unit 10, Cell C13- Basin tap & waste pipe leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 13:50:00 | Pass | Replaced cold side only quarter turn tap and replaced plug and waste
MSA-DCS | WA3592908 | Unit 9, Cell 16- Leaking waste pipe to sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 12:18:00 | Pass | Had to remove basin from wall to replace plug and waste then refit
MSA-DCS | WA3592911 | Unit 9, C/D cleaning cupboard- Leaking cold water tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 14:43:00 | Pass | Turned off water replacing hot/cold Quarter turn spindle tap
MSA-DCS | WA3592924 | Unit 5, Cell A13- Leaking in the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 08:30:00 | Pass | Nill
MSA-DCS | WA3592996 | Unit 13, B & D Regi oven is missing a steam hose | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 11:46:39 | 2020-09-10 14:20:00 | Pass | Fit water hose to oven.
MSA-DCS | WA3593129 | Unit 2, B wing - Pipe leaking again feed to showers | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 11:30:00 | Pass | Nill
MSA-DCS | WA3593203 | Unit 5 - A & C wing DOOR HANDLE BROKEN. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-06 10:00:00 | Fail | Require Parts.Install new handles.
MSA-DCS | WA3593252 | front gate sliding gate Sliding gate access panel on column door lock damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AAA Ability Locksmiths | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-11 08:30:00 | Pass | Attended site. Replaced failed lock and adjusted hinges on Gate Control Access Door. Normal function restored.
MSA-DCS | WA3593413 | Bunbury Regional Prison - Unit 4 - Cameras have gone offline. | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Sep 2020 | 2020-09-11 02:06:02 | 2020-09-10 19:10:00 | Pass | Contacted PRU, found that the staff were not entering the Windows password correctly, ie did not put a Capital letter at the start of the word “Operator”.
MSA-DCS | WA3593417 | Wooroloo Prison Farm - Sallyport door in the Gatehouse is not automatically closing. | Wooroloo Prison Farm | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 12:00:00 | Pass | 11/09/20Adjusted auto closer to gatehouse pedestrian glass door (note - this isn't the sallyport door). Adjusted striker plate to fit flush.Tested door in multiple closing positions.Shutting automatically each position.
MSA-DFES | WA3592816 | Engine Room -Pig tail breakaway charging cords for appliances insulation has slipped out | Butler Career Fire Station | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 15:30:00 | Pass | COMPLETED
MSA-DFES | WA3593024 | ground external toilet perished grommet connecting bowl to toilet - see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-11 12:30:00 | Pass | Replaced pan cone in out side male toilet
MSA-DFES | WA3593108 | Main Change room - Extraction Fan unit is unserviceable. | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-24 12:15:00 | Fail | Located faulty fan in main changeroom. Proved power and confirmed the motor had seized. Internal diameter of cutout is 220mm and the mile was HPM.Will need to seek approval and replaced old with new.
MSA-DFES | WA3657308 | RETROSPECTIVE WORK ORDER- BYPASS ON ZONE 18 FRONT ROLLER BAY 1 DOOR REED SWITCH- SEE NOTES | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 10 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-10 00:58:00 | Pass | Despatch Comments:BYPASS ON ZONE 18 FRONT ROLLER BAY 1 DOOR REED SWITCHPatrol Resolution:ONE OF THE FIRE ENGINES IS NOT IN ITS BAY, PRESUMABLY OUT ON CALL. ALL EXTERNAL ROLLER DOORS APPEAR SECURE. GATES TO CARPARK REAR OF BUILDING ARE SECURE. CLEAR BY TRENT
MSA-DTAG | WA3592609 | Court Security Cameras and computers not working in control room - see notes | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Sep 2020 | 2020-09-10 12:20:11 | 2020-09-10 10:25:00 | Pass | Found ups turned off turn it on and tested all ok
MSA-DTAG | WA3592745 | Centralised Breach Unit Female toilet door difficult to open and closes very quickly - see notes | Central Law Courts-Main Building-Level 4 | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-11 08:15:00 | Pass | Door closer adjusted
MSA-DTAG | WA3592915 | A/C failure in all Courts & waiting areas | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-17 11:00:00 | Fail | Attend site. Access BMS and enter weekend time schedule for waiting area AC unit. Found units to start. Found FCU 5 still not running. Access plantroom above court 2 entrance. Carry out fault finding. Check for power at unit. Found to have power but no control voltage to fan contactor. Trace wiring back to ground electrical swith room. Check controller suppling voltage to be ok. Trace wiring to relay and found power going in and not coming out. Found relay contact to have failed. Found relay to have a spare set of contacts. Move wiring to other contact and check operation. Found to now have control voltage leaving relay. Check fan coil unit contactor and found to be pulled in. Check fan coil unit and found to now be running. Fan coil unit is now operating as normal.
MSA-DTWD | WA3592658 | 3 ROOM/OFFICE: A352 Light switch panel crackling - see notes | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-16 10:55:00 | Pass | Replaced faulty switch mecs to classroom.job completed
MSA-DTWD | WA3592676 | F block F56 Leaking toilet bowl outlet on end cubicle in ladies toilet | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-15 14:00:00 | Pass | Fixed toilet
MSA-DTWD | WA3592680 | F block, F-61 - Left hand switch is faulty | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 16:00:00 | Pass | Attended site, signed in , completed jsa, located switch , went to wholesaler to get suitable replacement, isolated lighting , replaced switch , tested switch , all working , cleaned up work area, completed paperwork , signed out ***job complete***
MSA-DTWD | WA3592867 | E block canteen drain in the kitchen floor water continues to flow | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-22 16:48:00 | Fail | Fix taps which fixed leak
MSA-DTWD | WA3592941 | A Block, Room A29, Female toilet - LH basin tap running | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-10 14:00:00 | Pass | Serviced leaking basin set in downstairs women’s toilet (A Block)
MSA-DTWD | WA3592958 | A Block, Disabled toilet- toilet seat is broken | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-15 08:20:00 | Pass | Install toilet seat
MSA-DTWD | WA3592971 | Lvl 2, Room 256- Window glass & frame are broken | Perth Campus B2 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-24 10:00:00 | Fail | Made safe panel used film need to return later to repair Return to site to repair window 4 men complete job
MSA-DTWD | WA3592988 | QO16 faulty door lock | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 10:45:00 | Pass | Replaced cylinder
MSA-DTWD | WA3593044 | A Block, Room A139, 1st Floor- Loose basin tap | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-21 08:30:00 | Fail | Complete
MSA-DTWD | WA3593059 | B Block, Room B106(facilities office)- Access control system not working.(Comms problem with control | Leederville Campus | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 10 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-11 16:00:00 | Pass | Attended site and spoke to John re access control faultLocated Leedervulle LIU controller.Found that the ppwer plug had been knocked from the GPO.Re inserted ppwer plug and comfirmed that the Xenta and LIU was on line.Condirmed contriller status and yransactions from device
MSA-DTWD | WA3593182 | Lvl 1, West Block- Pipe drain is leaking | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 15:21:00 | Pass | Replaced tap
MSA-DTWD | WA3593209 | A Block, AG26 Female Toilets- Blocked toilets | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 15:07:00 | Pass | Unblocked to toilets a and main drain
MSA-DTWD | WA3593276 | B Block - Chiller is not working | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-22 09:28:00 | Fail | Signed into site and picked up keys. Isolated and tagged out chiller. Checked for voltages within chiller. Removedcompressor 2 cables, control wiring and screws holding IGBT onto cooling plate. Removed all old heat transferpaste from cooling board. Installed new heat transfer paste on IGBT and installed into chiller. Installed all new boltsand torqued to York's specifications. Installed compressor cables and wired in control circuit wiring. Installedprotective covering and powered up chiller. As there was no cooling call had client put rooms on cooling andgenerate enough load to run chiller on circuit 2. Checked operations of drive including amps and temperatures andrefrigerant temperatures and board temperatures. Circuit ran and cycled until cooling call was lost. Circuit 1 wasenabled and site was cleaned up. Old IGBT was left with client.
MSA-DTWD | WA3593286 | T block, Level 4, male toilet - Urinal flush button is faulty | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-11 09:30:00 | Pass | Complete
MSA-DTWD | WA3593321 | I block - front security door is damaged, | Balga Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 10 Sep 2020 | 2020-09-15 17:00:00 | 2020-10-05 15:30:00 | Fail | Supply and install new stainless steel hinged security door Supply and install new built out frame to suit Supply and install new 3 point lock system 1 x 2190mm x 800mm ( approximate sizes as per photos provided by client )
MSA-DTWD | WA3593410 | leaking ceiing upstairs in admin building | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-11 12:10:00 | Pass | Replace broken 20mm ball valve and copper float and overflow pipe to outlet for chiller system water tank
MSA-MRWA | WA3593215 | nth west auto door Auto door open button in operable, please remediate. | Road Network Operation Centre (RNOC)-Main Building-Second Floor | GMP-BR | Building | Automatic Doors (BU) | Blue Force Pty Ltd | 1 | CLOSE | 10 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-11 09:15:00 | Pass | Replaced REX buttons as directed.
MSA-DCA | WA3597277 | orchid area bins have been ripped out - Please call Phill Golder ASAp | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 11 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 13:30:00 | Pass | Have attended site and carried out temp fix. Will need to prepare BRAF to install concrete footings to remount bins on a solid surface (Currently bolted to pavers).26/10 closed job and claiemd costs to date as per David de Villiers - BRAF Declined
MSA-DCA | WA3597393 | Half-flush not operating (2nd cubicle) | State Library of WA-Main Building-Level 3-3.97 - Staff Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 17:00:00 | Pass | Lubricated flushing mechanism
MSA-DCA | WA3597422 | Seat broken (2nd cubicle) | State Library of WA-Main Building-Ground Floor-Male Toilet - Rear Entrance Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 09:25:00 | Pass | Unable to find broken seats
MSA-DCA | WA3597429 | Female public toilet not flushing (middle cubicle) | State Library of WA-Main Building-Level 1-Female Toilets - Near Lift Foyer - East | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 17:47:00 | Pass | Replaced faulty inlet valve
MSA-DCA | WA3597436 | Level 2 public water fountain blocked | State Library of WA-Main Building-Level 2-East Lift Foyer Level 2 - Next to Stair 4 | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 07:45:00 | Pass | Inspected water fountain. The sink has it’s own fall already. Drain isn’t blocked. Water takes slightly longer to drain(design issue)
MSA-DCS | WA3597096 | CCU (11) - Office lights in office are flickering on and off like strobe lights | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-30 15:00:00 | Fail | Replaced damaged lights in CCU control room
MSA-DCS | WA3597099 | Unit 5 - A12 Bottom bunk is very bowed. | Casuarina Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Midolo Building Services | 3 | CLOSE | 11 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-14 11:00:00 | Pass | BED FRAME STRAIGHTENED AND RE WELDED
MSA-DCS | WA3597186 | Industries Administration, Void Transport - Badly leaking tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-14 11:30:00 | Pass | Nill
MSA-DCS | WA3597234 | Unit 14 - B & D Disconnect and reconnect power to BWU - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-15 14:00:00 | Pass | Disconnect and Reconnect Unit 14 B and BWU
MSA-DCS | WA3597239 | Outcare Window in Co-ordinators office of Reset Centre's springs are broken. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-14 09:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3597242 | Unit 1, Cell A2 - Water from cistern is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 14:00:00 | Pass | Nill
MSA-DCS | WA3597340 | Security Area - CCTV Camera not working in Lobby area | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Sep 2020 | 2020-09-12 10:15:16 | 2020-09-11 12:30:00 | Pass | 11/09/2020 10:30. Installed temp laptop in place of PC, removed PC to GH Equipment room and tested. Pc started correctly and operated in correct manner. Returned to location, reconnected and monitored in service. Unable to reproduce Fault.
MSA-DCS | WA3597352 | Staff Dining & Health - Ceiling lights ( Fluros) not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-23 10:36:00 | Fail | Replaced 8 tubes and starters replaced 4 tombstones in staff dinning, replaces 4 t5 tubes in medical.
MSA-DCS | WA3597369 | unit 4 office lock with handle barrel is broken | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 14:40:52 | 2020-09-11 12:40:00 | Pass | Replaced lock on door to Officers Unit 4 office
MSA-DCS | WA3597397 | SOG base, security sliding gate 2 wont close | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 14:58:46 | 2020-09-11 13:00:00 | Pass | Tested gate operation via software & fob button, working OK. Unable to replicate issue, increase DOTL.
MSA-DCS | WA3597418 | Unit 1, RCD GPO not working (labelled by staff) | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-15 08:30:00 | Pass | Investigate and replace Unit 1 office GPO
MSA-DCS | WA3597440 | Pharmacy air con clean filter” message keep appearing on the control panel | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-11 14:30:00 | Pass | Reset "clean filter" message on wall controller. explained to customer that the message is time based and not based on how dirty the filter is.
MSA-DCS | WA3597444 | Unit 3, D Wing, 3rd Shower - hot water spindle is spinning but no water is coming out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-14 13:00:00 | Pass | Nill
MSA-DCS | WA3597568 | Main Prison - gate control, duress screen 2 has multiple alarms | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-11 14:30:00 | Pass | Job complete
MSA-DCS | WA3597573 | Unit 4, cowling alarm on zones 2,3,4, 5,6,7,9 have failed to activate | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-11 16:30:00 | Pass | Job complete
MSA-DCS | WA3597576 | Unit 4, PRU- Cameras in zone 8 & 10 not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Sep 2020 | 2020-09-12 12:41:42 | 2020-09-11 15:30:00 | Pass | Job complete
MSA-DCS | WA3597606 | Jasper B cell C07 broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-17 10:00:00 | Fail | Replaced light switch jasper cell c07
MSA-DCS | WA3597611 | entry pod point 5 and 10 indicating alarm and faulting - seme on site | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Sep 2020 | 2020-09-12 13:06:46 | 2020-09-11 14:45:00 | Pass | Reset transponder communications, constant communications failure , tested with spare fiber modems and still offline. Reconnected fiber port to spare fiber port and retested. All tested and working ok. Job complete
MSA-DCS | WA3597643 | kitchen, tap has been pulled of by a prisoner | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-14 09:30:00 | Pass | Nill
MSA-DCS | WA3597650 | Unit 2 - B & D Keys are getting stuck in the door in the plantroom above or leading to the B/D Grill | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 13:00:00 | Pass | Replace bolt throw and service
MSA-DCS | WA3597661 | Unit 3, the right hand sink is blocked in the AC Day room. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-14 14:00:00 | Pass | Nill
MSA-DCS | WA3597721 | Unit 1 - A & C metal trim holding the glass in place on the A/C dayroom door needs Re-riveting, | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 11 Sep 2020 | 2020-09-12 14:29:44 | 2020-09-11 15:00:00 | Pass | RE FIXED GLAZING BEAD TO DOOR
MSA-DCS | WA3597738 | Staff Lunch room - Faulty Ceiling Panel Light | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 10:00:00 | Pass | Repaired lighting in staff lunch room.
MSA-DCS | WA3597751 | Unit 5/6 control- Data point in the wall is broken | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 14:00:00 | Pass | Replaced cracked data outlets
MSA-DCS | WA3597753 | Unit 6, Cell 13- exhaust fan broken | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-21 14:00:00 | Fail | Replaced ceiling exhaust fan
MSA-DCS | WA3597754 | Reset building - basin tap handle broken (no escort required) | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-22 08:00:00 | Fail | COMPLETED
MSA-DCS | WA3597812 | 1x broken pipe streaming water onto lawn- see further notes below | DCS - 4 Driscoll Drive Canning Vale | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Sep 2020 | 2020-09-12 15:54:18 | 2020-09-11 17:50:00 | Pass | Told to close the work order, Dean will advise when this will be done.House is vacant at the moment.
MSA-DCS | WA3597813 | Jasper wing - flooding (possible burst pipe) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 19:54:57 | 2020-09-11 19:30:00 | Pass | Fixed burst pipe
MSA-DCS | WA3597835 | Zone 7 - Cowling is in error ( red colour ) | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 20:48:56 | 2020-09-12 19:15:00 | Fail | Called back to prison and confirmed with control officer that Zone 7 crawling has been working properly. Also afternoon Perimeter test has been conducted and Zone 7 crawling activated and reset correctly. Job completed.
MSA-DFES | WA3597305 | engine room doors not operating in auto and door 4 needs to be manually forced to operate | CFRS Hope Valley | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 11 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 14:00:00 | Pass | ASSA technician attended and found electrician required. Electrician attended and advised: Attended site and inspected bi fold doors . Noted all doors operating in manual except door 4. Suspect door 4 may have a fault with safety beam wiring or pe connections. Requires plcpersonell to fault find further . Required to leave door 4 closed and others in manual operation.Subcontractor attended and advised: I attended site and found that there is a cable issue with sensor 18 on Door 4. I have bypassed this sensor in plc and tested a full auto cycle and door system is operational. We will need to go back and check cable and possibly run a new one. Requires 2 techs as the door guards/flashings will need to be removed, and either a scissor lift or large ladder. I will need to remove the bypass in the plc once the cable issue is sorted out.Quote to follow.
MSA-DFES | WA3597760 | Outside Lecture Room 6, South-West Corner- Pipe connected to outside Tap is leaking. | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-21 11:15:00 | Fail | Repair burst pipe in wall near room 6
MSA-DFES | WA3597798 | Radio Communication, kitchen - Back door is getting jammed at the bottom. | DFES Regional Office - Belmont | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 15:15:00 | Pass | Liam Hanlon (15/09/2020) - Work NoteAttend siteSign and get keysDoor having issues not latching and closing possible security issueGot toolsChecked door and marginsAdjusted bottom hinge and spread hinge to lift doorTighten screws on frame and hingesTest door a dozen times all latching securely from different opening locationsRe fit door stop trim missing rivetClean upShow client working correctly and secureSign out
MSA-DFES | WA3597814 | Rising damp on south west wall and central west wall.- see further notes below | CFRS Daglish | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-11-13 13:15:00 | Fail | dry out wall, apply waterproofing membrane
MSA-DFES | WA3597818 | Mens toilet in RCS- Cold tap hard to turn off to stop water dripping after use | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 08:00:00 | Pass | Fixed leaking cold tap in male toilets
MSA-DTAG | WA3597450 | 1903 lower ground level - Infrared safety beam not preventing roller door from closing when blocked | Supreme Court | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 11 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 16:05:00 | Pass | Found that roller door when closes and object in the way of pe beam when roller was previously up the PE does not work so investigated.Found that the access signal gives a latching closed signal and the way that the access is wired into the controller maybe causing issue. Will need access to change signal from latching to pulse.Will need to get advice from manufacture on what should happen with pe when signal is latched.Pe beam works if close signal is sent and then you obstruct pe.Tested else several times all fine.
MSA-DTAG | WA3597596 | Business support - don’t seem to have the ability to force unlock any door from our console | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 16:50:15 | 2020-09-11 15:45:00 | Pass | Job completed - Met with client on Level 6 and investigated. Pacom Unison appears to lock / unlock doors remotely as desired. Advisedgraphics won't update until even is "Acknowledged". All OK.Job completed.
MSA-DTAG | WA3597600 | “In Session” button located behind 5.06 appears to be faulty. | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 16:54:23 | 2020-09-11 14:30:00 | Pass | In Session button appears to be intermittent at times. It worked 4 out of 5 tries. Will defect and advise on Planned Maintenance Report.
MSA-DTAG | WA3597692 | Registry - Small patches of plaster have become detached from office wall | Joondalup Courthouse | GMP-BR-HO | Building | Internal Walls (BU) | PPM Project Painting & Maintenance | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-18 11:15:00 | Pass | Repair and paint damaged walls
MSA-DTAG | WA3597837 | Supreme Court - 6x front view cameras out. | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Sep 2020 | 2020-09-12 00:09:08 | 2020-09-23 13:59:00 | Fail | Invoice raised for costs to date as advised by Mario
MSA-DTWD | WA3597114 | B002A male public toilet all sinks urnial and toilets blocked | Naval Base | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 0 | CLOSE | 11 Sep 2020 | 2020-09-11 11:52:50 | 2020-09-11 09:30:00 | Pass | Pump truck required sourced by owner of property
MSA-DTWD | WA3597232 | H001 welding bay, roller has come of roller door | Naval Base | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 12:00:00 | Pass | 11/9/20 - Attended site and carried out temporary fix. Reattached loose roller bracket with tech screws as a temp fix. Will need to fit top of the door with nutserts and install 8 mm bolts to both doors.Scheduled to return Wednesday 16th Sept
MSA-DTWD | WA3597344 | IT staff kitchen - Faulty zip unit | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-14 11:15:00 | Pass | System off on arrival. plugged unit in power tripped. Tested tap - causing power to trip contacted manufacturer, arranged for Billi to attend and repair/replace tap under warranty.A40139138I BILLI QUADRA COMPACT MF T026101005
MSA-DTWD | WA3597472 | A block A22 Office – Fluro tube replacements – High scale ceiling | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 11 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 08:30:00 | Pass | attended site , signed in , located lights, completed jsa, replaced tubes and starters, cleaned up work area , completed paperwork , signed out ***job completed *** pfm not on site
MSA-DTWD | WA3597541 | Q block, Q-Block Lift has a vice message saying a telephone fault has been detected | Joondalup McLarty Campus | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 11 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-11 14:40:00 | Pass | CHECKED EMERGENCY PHONE INSTALLATION . FOUND SCHINDLER CUBE NOT PLUGGED INTO ADJACENT POWER MODULE. CUSTOMER INFORMED AND REQUESTED LIFT IS LEFT IN SERVICE.
MSA-DTWD | WA3597546 | Block 2 - Faulty keypad lock – unable to open | Thornlie Campus | GMP-BR | Security | Keys & Access (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 16:15:00 | Pass | Block 2 - faulty keypad lock will not open.Lock repaired.Hinges worn - door has dropped - carpenter required.
MSA-DTWD | WA3597580 | Faulty double GPO at front reception desk – right hand side | Armadale Campus - 40 Commerce Ave | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 10:45:00 | Pass | Attended site and signed in. Completed site induction. Completed jsa. Discussed works with pfm and came to conclusion. Started work, could not complete work as the circuit protection would need to be upgraded to an rcd as it was only protected by a circuit breaker. Called pfm for approval. Found another solution without having to upgrade circuit protection. Isolated and installed blank plate. Completed paperwork and informed staff of complete information of job.
MSA-DTWD | WA3597659 | L2, Student toilet - toilet broken next to the two lifts, not working | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-18 14:34:00 | Pass | Fix toilet
MSA-DTWD | WA3597747 | B200 staff room kitchen- new motorised vent in kitchen area makes a rattling noise | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 3 | CLOSE | 11 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-22 06:11:00 | Fail | Returned to site collected keys gained access and inspect Air flow damper. Confirmed with staff that damper vibration noise had not reoccured. Recheck adjustments. Work area left tidy. No further works required.
MSA-DTWD | WA3597834 | Block 6, 6A, Vehicle Body Building- Burnt out GPO in tig welding bay – GPO #15 | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 11 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 15:30:00 | Pass | Attended site and signed in. Located burn outlet. Left site to pick up part. Replaced outlet and tested. All now working. Informed staff of job completion
MSA-MRWA | WA3597799 | Full flush button not working please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Third Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Sep 2020 | 2020-09-14 17:00:00 | 2020-09-14 15:00:00 | Pass | Replaced leaking bellows
MSA-DCS | WA3603403 | Inner secure door at the gatehouse is not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Sep 2020 | 2020-09-12 11:15:46 | 2020-09-16 09:15:00 | Fail | Pickup part and travel to site to replace the faulty reed switch. Tested it ok after replacement. DPDT REED SWITCH X 1.
MSA-DCS | WA3603409 | Lost vision for unit 4 in the control room | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Sep 2020 | 2020-09-12 16:35:50 | 2020-09-12 09:30:00 | Pass | Contacted Security S/O Steve Heath whoadvised Lost Picture On Monitor in Gate Control. I asked Steve to go to the Gatehouse Equipment room and call me back. Steve advised that a staff member was cleaning the workstation keyboard when the outage happened. I instructed Steve where to find the Workstation PC and to operate the reset button. Mr Heath then advised that pictures had been restored.
MSA-DCS | WA3603430 | Unit 5 Health 10 cell call system is not working | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Sep 2020 | 2020-09-12 14:50:19 | 2020-09-12 13:15:00 | Pass | Attended site and investigated the fault.Found loose connection on media converter.Reconnected and conducted test.All back to normal and operational.
MSA-DCS | WA3603460 | Special handling unit control room one security monitor is unoperable | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Sep 2020 | 2020-09-13 13:06:32 | 2020-09-25 08:30:00 | Fail | Removed faulty monitor in the SHU and replaced with new LG monitor. Gained access and installed. All working ok, job complete.
MSA-DCS | WA3603495 | unit 10 - burst water pipe in the roof | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 12 Sep 2020 | 2020-09-12 19:32:49 | 2020-09-12 20:15:00 | Fail | Replaced section of burst pipe in u 10.Waited for the escort at the front gate for 50min. Once in the control room we had to wait for 45min as there was lock down time.
MSA-DCS | WA3603508 | Fire alarm panel is going off- Wont reset- battery is low- Mains is Ok- No FIre | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 12 Sep 2020 | 2020-09-13 17:44:26 | 2020-09-12 20:00:00 | Pass | Bandyup Prison12/09/20 EIAttended site & found POD FIP in alarm from unit 4 L block VESDA.Reset fire alarm & inspected VESDA in unit 4 OK.Whilst onsite checked unit 2 FIP which is displaying a battery fail fault.FIP PSU 240VAC OKPSU measured 27.3 VDC OKBatteries 27VDC dated 17/10/2018Recommend 2 x 26A/h batteries for unit 2 FIP to be replacedunit 4 K block.NOTE: Batteries have been changed but Power Supply is faulty and is overcharging. New Stand alone 24v Power Supply Unit required.Replaced PSU and system left with no faults
MSA-DCS | WA3606504 | Banksia Hill Detention Centre- DVM recording camera not recording in gatehouse | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Sep 2020 | 2020-09-14 10:52:32 | 2020-10-08 14:31:00 | Fail | Investigated fault, traced to faulty encoder card which was causing recording drop-outs. Repaired encoder card and tested OK.Monitored for correct operation.Job Complete
MSA-DCS | WA3606531 | cell lock has come off D1 unit-2 | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Lock It Locksmiths | 1 | CLOSE | 13 Sep 2020 | 2020-09-14 16:19:05 | 2020-09-14 09:05:00 | Pass | Replace mortise lock and strike plate.
MSA-DCS | WA3606532 | temper alarm zone 8 - perimeter fence, unable to reset | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Sep 2020 | 2020-09-14 01:10:01 | 2020-09-14 00:15:00 | Pass | Attended site.Found that Senstar processor in zone 8 showing tamper alarm.Checked connections and power.Power cycle the processor and conducted test.All ok at departure.
MSA-DCS | WA3606533 | Perimeter light not working 16A | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Sep 2020 | 2020-09-14 21:12:13 | 2020-09-14 00:30:00 | Pass | Electrician needs to attend site and check the fault.(Another contractor)
MSA-DCA | WA3608935 | caged pump house burst sprinkler pipe | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-21 11:19:00 | Fail | Attend site due to burst sprinkler pipe in pump roomMechanical contractors required to attend to remove and replace the damaged partsContractors had to order the parts for manufacture Attended site and installed
MSA-DCA | WA3609172 | Pneumatic station in fault due to power cut over the weekend and requires resetting. | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-14 18:30:00 | Pass | Multiple active alarms on arrival to site. Informed Programmed FM. Received job. Most Galleries low humidity. Stand alone air station in fault. Both Steam Boilers faulted on low gas pressure safety. Carried out all manual resets on faulted plant. Monitored operation and staging cycles of plant. All alarms cleared. Last active alarm was a reset at 11:09 on 11/09/2020. Poor space condition results in multiple galleries confirm plant faulted on Friday but no alarms raised the issue. Controls contractor required to investigate and identify cause. Site visit arranged for 22/09/2020.
MSA-DCA | WA3609298 | Chiller 2 water circuit issue | Perth Concert Hall-Main Building-Ground Floor-Plant Room | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-14 16:00:00 | Pass | Inspected chiller circuit 2 and found air cavitation in chilled water circuit.Bled air from lines but still has air in system.Carried out inspection on make up water system.Found make up is full and the expansion tank is full. Checked operation of make up water pump and found when activated the pump did not stop and the tank began to run dry.Had to hit the pressure switch to stop the pump.Suspect the pressure switch is faulty.Submitted braf to replace pressure switch and installextra air bleeds to remove air.
MSA-DCA | WA3609429 | External area - Blocked drain | PICA-Main Building-External Area | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 08:50:00 | Pass | Unblocked stormwater pipe on the lhs of the entry of the Pica building.
MSA-DCS | WA3608629 | Unit 10- Cell A2 - Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Sep 2020 | 2020-09-14 11:23:44 | 2020-09-14 09:30:00 | Pass | Rectified and Fixed the fault on cell call point, job completed.
MSA-DCS | WA3608649 | Hotham, Kitchen sink is leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 10:08:00 | Pass | Repair leak to kitchen sink and replaced missing floor grate.
MSA-DCS | WA3608651 | Gascoyne, Kitchen sink is leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 12:18:00 | Pass | Refitted leaking kitchen sink set in Gascoyne kitchen.
MSA-DCS | WA3608656 | Security Area - download footage from MPU M17 | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 11:30:00 | Pass | Downloaded requested video, delivered to security on supplied memory stick.
MSA-DCS | WA3608666 | Unit 6, Staff tea room- spout on the sink has blown off/broken away from housing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 15:00:00 | Pass | Nill
MSA-DCS | WA3608674 | Unit 6, A & C Dayroom- Fan in oven is making loud (rattling) noise when in operation | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 14 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 11:55:00 | Pass | Found cage to only have 2 screws in it and rattling around. Fixed properly & check all fan motor bolts. Tested operation of fan motor and no noise appeared.
MSA-DCS | WA3608680 | Unit 13, Cell C2- Door lock on cell is stiff, hard to lock & unlock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 14 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 10:00:00 | Pass | Service main lock
MSA-DCS | WA3608684 | Unit 3, Cell B1- Metal window spiral has come out of the window track | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 13:15:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3608702 | Health Admin, Tearoom- No power to fridge or Urn | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 12:00:00 | Pass | Restored power to health admin tea room. Found Overloaded with appliances
MSA-DCS | WA3608766 | Unit 1, Cell C11 - GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 09:00:00 | Pass | Replaced broken gpos
MSA-DCS | WA3608801 | unit 1 C2 cell call broken | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 08:50:22 | 2020-09-14 11:30:00 | Pass | Replaced damaged cell call unit with new. Test cell call ok and back to normal operations.
MSA-DCS | WA3608802 | Unit 14, Cell A14- Sink & showers reported as leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 10:30:00 | Pass | Nill
MSA-DCS | WA3608819 | PIR unit 3, outside cell 21 - constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 09:06:51 | 2020-10-01 15:00:00 | Fail | Replaced faulty PIR with new EV1100 PIR in unit 3 corridor Seme stock used, all installed and tested working ok. Job complete
MSA-DCS | WA3608821 | Unit 3, PIR, outside cell 2- constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 09:09:01 | 2020-10-01 13:30:00 | Fail | Replaced faulty PIR with new EV1100 PIR in unit 3 corridor Seme stock used, all installed and tested working ok. Job completeReccomend updating site plan to match corresponding PIRs, difficult to locate correct PIR and corresspond to physical device.
MSA-DCS | WA3608822 | Unit 2, PIR, oustide cell 17- constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 09:09:49 | 2020-10-01 12:00:00 | Fail | Replaced faulty PIR with new EV1100 PIR in unit 2 corridor Seme stock used, all installed and tested working ok. Job complete
MSA-DCS | WA3608828 | Unit 5, Cell 3- Cell Call, hard to hear and alot of static | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 09:10:37 | 2020-10-01 17:15:00 | Fail | Replaced faulty cell call with new cell call unit in unit 5 OBS cell 1, Seme stock used, all installed and tested working ok. Job complete
MSA-DCS | WA3608841 | Unit 3, D8 - Window not staying up, the spring is broken and wont keep the window up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 12:15:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3608873 | Unit 14 A2 - Power point badly cracked and damaged. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 09:24:07 | 2020-09-14 13:30:00 | Pass | Replaced damaged cell switch in unit 14 a2
MSA-DCS | WA3608929 | Lenard, Cell C03- toilet leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 11:15:00 | Pass | Relaced faulty button and control box
MSA-DCS | WA3608957 | Education Outside music room burst water line - contractor on site | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-14 14:01:00 | Pass | Water gashing out from the conrete floor outside the building. Started jack hammering the floor to find the cause of the leak. Once the water had been turned off and on the water leak had stopped. Water not leaking at the moment but we agreed with the maintenance guy to leave the tranch exposed to be able to see whether it starts leaking again in the next few days.
MSA-DCS | WA3608995 | Unit 14 - A & C shower leaking - see notes | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-17 12:00:00 | Pass | OLD SILICONE REMOVED AND SHOWER RESEALED
MSA-DCS | WA3609005 | Farm, Packing room - no power to packing machine 1 | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 10:12:37 | 2020-09-14 13:30:00 | Pass | Investigate and repair dairy packing machine
MSA-DCS | WA3609063 | Unit 3, Cell C11- Window Frame broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 11:30:00 | Pass | WINDOW AND FRAME REPAIRED
MSA-DCS | WA3609066 | Unit 13, Cell A6- Leaking shower, requires silicone around the base of the window. | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 12:30:00 | Pass | NEW SILICONE INSTALLED TO STOP LEAK
MSA-DCS | WA3609090 | Master control - Electronic Computer Control for Doors & Sally Port Intermittently not working | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Sep 2020 | 2020-09-14 15:02:55 | 2020-09-14 13:15:00 | Pass | Reset workstation for door control. Retested sallyport doors multiple times and confirmed all working ok. All doors in gatehouse tested ok. Job complete
MSA-DCS | WA3609094 | Kitchen, Opposite Ovens- Sink waste leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-14 16:48:00 | Pass | Replaced sink waste and repaired leaking trap to sink opposite ovens in main canteen.
MSA-DCS | WA3609095 | Stores Yard, Service Road Side- Tap Backflow valve leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 14:28:00 | Pass | Rplaxed and testes rpz
MSA-DCS | WA3609096 | Admin, kitchen - Fault description Hydro Tap Isolation Valve broken won’t turn off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 11:08:58 | 2020-09-14 15:40:00 | Pass | Replaced isolating valve to billi unit in admin kitchen under the sink.
MSA-DCS | WA3609103 | Education, Demountable Office - Smoke alarm in demountable has been disabled as it keeps beeping. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 14:55:00 | Pass | Replaced detector
MSA-DCS | WA3609162 | Unit 2 lower landing abultions disconnect & reconnect lights for midolo to renew ceiling | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 09:00:00 | Pass | Disconnect and remove light and exhaust fan for ceiling to be replacedReplace light and exhaust fan
MSA-DCS | WA3609183 | Unit 5, Cell B10- Hinges on door have dropped and required adjusting | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-30 11:00:00 | Fail | Replace hinges and fixings.Replace lock and weld on strike.
MSA-DCS | WA3609185 | Canteen whole unit air con not getting cool enough | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 14:30:00 | Pass | Unit operating as designed lowered setpoint and disconnected heating to prevent products melting.
MSA-DCS | WA3609204 | Bakery- Handle Broken on Door to prisoner changeroom. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-11-20 12:00:00 | Fail | Require Parts.Replace Chubb handles and hinges.
MSA-DCS | WA3609224 | Recreation prisoner WC - toilet pan or pipes in wall leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-05 12:00:00 | Fail | COMPLETED
MSA-DCS | WA3609225 | Recreation staff WC - Basin Tap leaking, spindle | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-05 14:00:00 | Fail | COMPLETED
MSA-DCS | WA3609238 | unit 2 Fire system keeps losing pressure and alarming on a bi-weekly basis | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 08:19:00 | Pass | 17.09.20went to unit and checked fire panelall normal with no alarmswent to valve room and checked systemall pressures were normal and nothing looked out of the ordinaryunsure what caused LP alarm but it wasn’t present when we were onsite
MSA-DCS | WA3609287 | Sewerage treatment plant - PRV valve on alumium solphat tank is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2021-02-02 10:30:00 | Fail | Complete
MSA-DCS | WA3609376 | 4C kitchen urn keeps tripping power | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 13:30:00 | Pass | Replaced element and thermal overload.Replumbed filter and flush due to bypass
MSA-DCS | WA3609378 | reception kitchen water filter faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-23 09:25:00 | Fail | Located power switch for unit once back on reset unit and turned cold water back on working fine
MSA-DCS | WA3609383 | Unit 9, Cell B5- Interference on cell call line | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 13:56:29 | 2020-09-15 09:00:00 | Pass | Checked and found U9 B5 cell call point faulty. It is heard for control to hear cell. Replaced the cell call point and tested it ok. CI-CC X 1 need to order one back to Hakea stock.
MSA-DCS | WA3609385 | Unit 7 kitchen Sink in kitchen area leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-23 10:48:00 | Fail | Turned off water supply changing tap washer and valves on hot and cold in h wing kitchen
MSA-DCS | WA3609386 | Unit 10, Cell A2- Interference on cell call line | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 13:58:23 | 2020-09-15 11:30:00 | Pass | Checked and found Unit 10 A2 cell call working properly. Problem has been fixed under work order number WA3608629
MSA-DCS | WA3609393 | Unit 8, Cell B1- Light switch faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 12:30:00 | Pass | Replaced light switch
MSA-DCS | WA3609407 | Reception Property high level light needs repair repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 11:00:00 | Pass | Repaired light
MSA-DCS | WA3609413 | units 1 and 4 MDAS reciever fault R1 and R0 | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 14:09:36 | 2020-09-17 15:30:00 | Fail | U1 - located receivers 8.5.0 and 8.5.1. Found 8.5.0 full of water and the PCB badly corroded. Removed and replaced receiver PCB after drying the enclosure. Sealed and stress tested from the gatehouse. Parts used:Bosch MDAS receiver EA102A-30AConsumables
MSA-DCS | WA3609416 | internal perimeter 1A MW internal zone | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 09:12:00 | Pass | Investigated intermittent microwave faults, traced to component fault on microwave PCB, disassembled microwave and repaired PCB, reassembled, calibrated and tested OK.Job CompleteParts Used:Consumables
MSA-DCS | WA3609443 | Lenard, Outside toilet block - Door is split | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-11-05 10:30:00 | Fail | new door fitted
MSA-DCS | WA3609447 | Karakin, Cell A06- Light switch cracked | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 11:00:00 | Pass | Replaced light switch karakin a06
MSA-DCS | WA3609448 | Lenard outside toilet block basin cracked | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-05 16:00:00 | Fail | Inspexted broken basin
MSA-DCS | WA3609450 | Lenard, Outside toilet block- Toilet cistern is broken | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-16 10:30:00 | Pass | Replaced cistern
MSA-DCS | WA3609459 | Entry/Pod- Perimeter gate infrared beam east- activating in fault | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Sep 2020 | 2020-09-14 18:34:49 | 2020-09-23 15:00:00 | Fail | Attended site and checked Gallagher report for PE Beam 1. All checked ok and no false alarms. Reset alarm and removed covers. Tested for correct resistance reading and make sure no damage to PE Beam covers. All tested and working ok. No false alarms. Job complete
MSA-DCS | WA3609472 | Gate Control Room - Indigo Monitor (Next to MDAS) is pixalting - monitor starting to fail. | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-15 08:00:00 | Pass | Job complete
MSA-DCS | WA3609531 | Visits CCTV workstation in fault | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-10-07 12:00:00 | Fail | installed & commissioned new work station
MSA-DCS | WA3609537 | Metal shop near entrance door - Fire hydrant door swollen and unopen able needs repair/changing | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 12:30:00 | Pass | NEW DOOR EASED AND HUNG
MSA-DCS | WA3609548 | Female Reception area - Motion sensor faulty, continually going off and unable to arm building | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 16:45:09 | 2020-09-24 18:00:00 | Fail | Replaced PIR and resistors.Tested PIR coverage, confirmed activation and stable when room is clear.Part used from PFM stock EV669 (360°)New part delivered to site stock
MSA-DFES | WA3608980 | SOTS Transportable Shower Block - Leaking shower head | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 11:43:00 | Pass | Replaced shower heads due to they were broken
MSA-DFES | WA3609016 | Electrician to seal and make safe the exposed cables from the junction box in the appliance bay | Emergency Management Network (WAERN) Project | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-16 05:15:00 | Pass | CompeteRescuers cables and made safe
MSA-DFES | WA3609021 | lock barrel to rear shed – existing key fits but does not open | Emergency Management Network (WAERN) Project | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 09:15:00 | Pass | Gain entry to jammed lock on sliding security door, service lock and made repairs to door.
MSA-DTAG | WA3608744 | Lvl 14,Magistrates Chambers- Blockage in male toilets | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-14 14:30:00 | Pass | Complete
MSA-DTAG | WA3608748 | L4 CJS- Kitchen No power to any applicanes in kitchen - see notes | Central Law Courts | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-15 08:00:00 | Pass | Kitchen circuit still overloaded if all appliances on
MSA-DTAG | WA3608773 | Front entry door- Doors opening prior to 0830am & should be secure | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 14 Sep 2020 | 2020-09-14 12:37:15 | 2020-09-14 10:00:00 | Pass | SAT/Supreme operator force unlocked door timezone at 8:00:25am and did not unforce, which is why doorwas opening to anyone. Door timezone unforced. Job completed.
MSA-DTAG | WA3609223 | 1903 Camera 98 – On Pole 2 facing the Sally Port not working | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 14 Sep 2020 | 2020-09-14 16:02:40 | 2020-12-04 11:30:00 | Fail | Attended site with EVVP, found damaged power cable. Replaced cable and reset camera. Camera in working order again.Job completed
MSA-DTAG | WA3609485 | Supreme Court - 6x front view cameras out. | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-14 17:30:00 | Pass | The 9 cameras that were offline were due to work being performed by electrical contractors at the time. Confirmed cameras are online and recording.
MSA-DTWD | WA3608767 | east wing L1 E105A Fault with the AV equipment. Needs to be removed from ceiling for repairs. | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-14 15:30:00 | Pass | Remove av equipment from ceiling and made safe
MSA-DTWD | WA3608779 | tower block L4 broken toilet seat female toilet | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-14 13:00:00 | Pass | Complete, correct start finish:12.00-13.00
MSA-DTWD | WA3608902 | C block - Damaged data & power conduit pole from ceiling to floor | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-08 11:00:00 | Fail | Repalced 1x service post ,need to return when classroom is free.not complete Attended site and signed in. Installed second service pole in c block. Tested, Job complete.
MSA-DTWD | WA3609041 | campus ground security grounds lighting from C to A not working | Bentley Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 11:44:00 | Pass | Rectified lighting issue from C to A block and ajusdted times on time clocks to suit appropriate conditions.
MSA-DTWD | WA3609044 | J block J56 window frame around lock is broken | Bentley Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 15:45:00 | Pass | ATTENDED SITE AND REFITTED STYLE BACK ON
MSA-DTWD | WA3609058 | E Block, Room EG15 - Hinged Entry Door, Damaged hinges, No longer closes properly. | Carlisle Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-18 16:00:00 | Fail | 14/9/20 - Attended site. Assessed works required. Will need to return with new hinges and fixings to complete repair - Reattend scheduled for Thursday 17/9/20
MSA-DTWD | WA3609097 | G Block, Room G16- Wooden door sagging doesn’t close properly | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 14 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 10:00:00 | Pass | Hinge screws worked loose - installed larger screws to secure
MSA-DTWD | WA3609125 | West end of admin building- damaged water pipe & is leaking | West One Services | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-15 16:00:00 | Pass | Complete
MSA-DTWD | WA3609144 | B block Hot/cold water urn clock out cannot get it back on | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 14 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 08:57:00 | Pass | GPO not functioning. Drilled hole through cupboard to utilise other GPO. All working ok now.A40190488N Wilson unit - was a GPO issue drilled through bench and connected to new available GPO unit tested working well
MSA-DTWD | WA3609293 | B Block, B208 Male Urinal button keeps flushing | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 17:00:00 | 2020-10-19 01:30:00 | Fail | Complete
MSA-DTWD | WA3609359 | Tower level 4, kitchen - Auto boil unit, water has a odour | West One Services | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 14 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-15 09:40:00 | Pass | Replaced filter and flushed replaced jg fitting and descaled tap.
MSA-DCA | WA3614164 | Boiler 2 & Chiller 2 in fault - Please contact Sue Murray for site access and further info | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-External Plant | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-30 10:00:00 | Fail | Completed investigation and repair works to faulting chiller and boiler. Please refer to work logs and attached Boilertronics service report for in depth analysis and alterations and works carried out. Works completed boiler 2 and chiller 2 out back in to Auto control and operation.
MSA-DCA | WA3625658 | Livingstones Cafe opposite the Wetland Area - Outdoor tap has been vandalised and needs replacing | Perth Cultural Centre Precinct-Wetland Area-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 23:55:21 | 2020-09-15 21:28:00 | Pass | Tap had been stolen. Due to high water pressure and not being able to find an isolation valve i have installed a normal outdoor tap and cut the handle off.
MSA-DCS | WA3614017 | Perimeter, mircophonics in zone 1 constantly alarming | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 07:21:03 | 2020-09-30 11:00:00 | Fail | Removed faulty sensor cable in Zone 1. Run new sensor cable and calibrate. Tested all ok after work.
MSA-DCS | WA3614020 | Perimeter, mircophonics in zone 9 constantly alarming | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 07:22:58 | 2020-10-30 00:00:00 | Fail | Replaced faulty cable and repaired controller fault, calibrated and tested OK.Job Complete
MSA-DCS | WA3614044 | Unit 8, Door control computer has failed | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 11:30:52 | 2020-09-15 11:00:00 | Pass | Checked and found Unit 8 EBI workstation for door control and CCTV monitors is not working properly. Restart workstation and application and tested all ok.
MSA-DCS | WA3614047 | Front Gate- Tree requires pruning where police and justices park branches hitting cars | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | General Tree Works (LG) | KENNEDY'S TREE SERVICES | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 06:47:09 | 2020-09-17 08:45:00 | Fail | Works completed, no issues
MSA-DCS | WA3614052 | Unit 1, D Wing- second last light cover is damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-15 10:00:00 | Pass | Investigate and replace Unit 1 D Wing Light cover
MSA-DCS | WA3614068 | Unit 14, Cell C02- Personal lock, officers keys getting stuck & hard to open | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 15 Sep 2020 | 2020-09-21 17:00:00 | 2020-11-02 11:30:00 | Fail | Unable to complete due to No available escort officer.Replace mortise lock, requires customs strike.Replace worn strike with oversize strike.
MSA-DCS | WA3614069 | Unit 1, Cell D12- Latch is constantly getting stuck & also when you push the door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 15 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-17 12:00:00 | Pass | Replace door plate, lock and weld on strike plate
MSA-DCS | WA3614070 | Unit 1, Cell D8- Latch gets stuck & doesnt always come out | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 10:00:00 | Pass | Replace door plate and lock.Weld on strike plate.
MSA-DCS | WA3614077 | Unit 1, Cell D9- Door latch is faulty- further notes below | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-18 10:30:00 | Fail | Remove broken strike and weld on new strike plate.
MSA-DCS | WA3614079 | Unit 1, Cell D8- Window spiral balances are faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-16 09:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3614080 | SOG east sliding gate will not close after 20 or 30 seconds | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 15 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-15 11:30:00 | Pass | 15/09/20Adjusted beam and cleaned covers on Eastern SOG gate
MSA-DCS | WA3614081 | Unit 1, Cell D4- Window spiral balances are faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-16 10:30:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3614082 | kitchen Two C51 robo coup’s faulty - see notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 15 Sep 2020 | 2020-09-17 17:00:00 | 2020-10-01 13:30:00 | Fail | Returned Repaired Robo Coupes to site
MSA-DCS | WA3614085 | Unit 1, Cell D5- Window spiral balances are faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-16 09:45:00 | Pass | RE NEW SPIRAL BALANCES - REPAIR WINDOW AND FRAME
MSA-DCS | WA3614087 | Visits Area - Lobby Area video cameras lobby area not working- see notes | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-15 11:30:00 | Pass | Removed Indigo workstation pc from Rack. Tested onboard power supply. Found no output on +12v pin. Ordered and picked up replacement pc power supply. Installed new power supply in workstation pc and tested. Returned pc to Visits Lobby Equipment Rack, reconnected and brought online. System fully operational.
MSA-DCS | WA3616047 | Kitchen, Staff Toilet- toilet cistern spilt (invisi toilet cistern) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 14:30:00 | Pass | Replaced invisi cistern. Unable to commence work earlier due to lock down.
MSA-DCS | WA3620319 | Visits Area - Lobby Area Lobby lights Flickering Possibly require new starters or tubes | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-05 15:00:00 | Fail | Found and repaired damaged cable in roof space above visits centre. Tested and commissioned circuits
MSA-DCS | WA3621069 | unit 1 pod 4 kitchen small HW system has a cracked -see notes | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-15 14:02:00 | Pass | Will need a plumber to attend unit is a Boiling Water Heater Unit (not drinking water system) plumber required to replaced hot water system - cracked tank A403479994
MSA-DCS | WA3622146 | Gate House CCTV Footage required Gatehouse 4/09/2020 | Casuarina Prison | WSM-GR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 09:30:00 | Pass | Identified area and downloaded 5 hours of video as per Security Managers request.
MSA-DCS | WA3623798 | Check leaking water meter | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-01 15:00:00 | Fail | Work order complete
MSA-DCS | WA3623911 | Unit 6 - C7 blocked toilet. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 08:30:00 | Pass | Nill
MSA-DCS | WA3623927 | social visits main hall passage door Lock Barrel Jamming unable to turn | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 11:15:16 | 2020-09-15 15:30:00 | Pass | Attended site. Lock repaired by replacing lock cylinder. Cylinder supplied by DOJ
MSA-DCS | WA3623935 | unit 2 B3 Toilet Bowl Leaking Sewerage Water from the base into the Shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 11:21:30 | 2020-09-15 15:55:00 | Pass | Replaced leaking kee seal and pan rubber on the toilet.
MSA-DCS | WA3623937 | Murchison, B wing, Cell B03- 2x broken power points (doubles) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 13:00:00 | Pass | Replaced 1x DGPO Murchison cells b03 and b01
MSA-DCS | WA3623957 | SHU (9) - Perimeter Fence Camera 295 north enrty has no PTZ functions and is frozen in one area | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 11:31:52 | 2020-09-16 12:30:00 | Fail | Unable to activate PTZ function from Maxpro system or direct on data feed to camera. Power reset camera, PTZ function restored.
MSA-DCS | WA3623959 | Unit 1, Main Abultions - toilets blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3623961 | Unit 1, hut ablutions - urnial blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 10:00:00 | Pass | COMPLETED
MSA-DCS | WA3623972 | Unit 14 - Toilet Lights not working staff toilet need new tubes. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-15 15:30:00 | Pass | Investigate and repair Unit 14 Staff toilet lights
MSA-DCS | WA3623979 | Unit 14 - C9 toilet leaking into shower from bottom | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-13 15:00:00 | Fail | Requires braff
MSA-DCS | WA3623982 | Abattoir - 2 broken lights in smallgoods area | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 09:00:00 | Pass | Investigate and repair/replace lights in small goods area
MSA-DCS | WA3624882 | Gate House - Front Entrance Water chiller is blocked and won't drain | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 11:06:00 | Pass | Cleared drain and replaced filter
MSA-DCS | WA3625262 | Perimeter detection Microwave sensor, zone F04 - fails alarms, constantly activating | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 12:47:40 | 2020-10-15 14:30:00 | Fail | Two techs attended MW beam set and realigned. Alignment voltage initially showing as 0.5vdc, on completion alignment voltage showing as 2.4vdc.
MSA-DCS | WA3625282 | Level 1, Male toilet - blocked | East Perth-Main Building-Level 1 | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 13:01:51 | 2020-09-15 15:00:00 | Pass | Complete
MSA-DCS | WA3625377 | perimerter camera 35 tamper - seme on site | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 13:53:26 | 2021-03-19 12:00:00 | Fail | EWP required approval required. Fault previously reported in maintenance round.24/8/21 job has been rectified under WA3625382
MSA-DCS | WA3625380 | perimeter camera 34 tamper | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 13:56:48 | 2021-08-24 11:00:00 | Fail | Isolated camera tamper on camera 34, confirmed ok.job has been rectified & CLOSED on WA3625382
MSA-DCS | WA3625386 | gate house EC IS network fault | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 13:58:44 | 2020-10-08 14:55:00 | Fail | Installed Planet IGS-10020MT and programmed
MSA-DCS | WA3625389 | gate house indigo data base fault | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 13:59:58 | 2020-09-17 08:00:00 | Fail | Merged Database and programmed users.Tested setup
MSA-DCS | WA3625393 | gate house senstar PSU fault | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 14:01:03 | 2020-09-30 11:44:00 | Fail | Removed faulty PSU and installed with refurbished unit.tested alarm outputs on senstar system and confirmed correct operation
MSA-DCS | WA3625445 | Reset Building- Air con gas pipe is leaking (no esort required) | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-11-10 13:30:00 | Fail | Waiting for approval. Completed
MSA-DCS | WA3625468 | Unit 6, Cell C6- Blocked drain directly under the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-16 09:30:00 | Pass | Nill
MSA-DCS | WA3625508 | Unit 2 A4 Door Top Hinge Bolts Pulled out of the Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 14:48:45 | 2020-11-06 10:00:00 | Fail | 16/09/2020. Attended site. Further rectification works required.06/11/2020. Attend site (2 locksmiths). Weld mounting plate and hinge to door frame and replace fixings.
MSA-DCS | WA3625516 | Sally port - inner roller door playing up - intermittent not closing | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 18:49:00 | 2020-09-15 17:00:00 | Pass | 15/09/20Inspect internal roller door.Inspect control board.Reset thermal overload switch.Ran roller door 5 times with no issue.Other contractors working in control room could be the possible reason for switches flicking.
MSA-DCS | WA3625518 | Unit 1, Cell A3- Blocked Toilet & Shower Drain | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 14:52:54 | 2020-09-15 16:48:00 | Pass | Unblcoked toilet and shower
MSA-DCS | WA3625542 | Unit 1, Cell B10 - Toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 14:37:10 | 2020-09-16 10:10:00 | Pass | Cleared blocked toilet in unit 1 cell B10 caused by an orange stuck in the toilet.Adjusted cistern.
MSA-DCS | WA3625571 | unit 2 cells A1, A2, A9 and A10 fire alarms not working | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 19:46:08 | 2020-09-15 17:32:00 | Pass | both cells found to be operating with charger faults
MSA-DCS | WA3625655 | Control Room - Honeywell computer system (main monitor) has crashed | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 22:46:19 | 2020-09-15 20:45:00 | Pass | Rectified and fixed the fault from EBI ws 2, job completed.
MSA-DFES | WA3614058 | 1st Floor, Kitchen near ICT- Zip unit is leaking | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-15 17:00:00 | 2020-09-15 12:00:00 | Pass | Replaced plv safety solenoid hot solenoid and strip sensors
MSA-DFES | WA3622165 | Rear yard entry(Stubbs Terrace)-Yellow back gate electrical code pad is not working to enter station | CFRS Daglish | GMP-BR | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-10-05 09:05:00 | Fail | Reported fault "Codepad for Rear yard entry (Stubbs Terrace)-Yellow back gate electrical code pad is not working to enter station."Codepad fault replaced with another codepad from building side door as per request from OIC due to gate being primary means of entry. Replacment codepad to be sourced to replace codepad taken from building side entry.
MSA-DFES | WA3623724 | ground land use planning section light not working - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-15 14:30:00 | Pass | Replaced faulty fluros with new
MSA-DFES | WA3623913 | Perimeter electric fence has been cut | FESA RHQ - Forrestfield | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 14:00:00 | Pass | 15/9/20 - Repaired electric fence and pruned light shrubs off fence line
MSA-DFES | WA3624691 | applied training ground Paterson’s Curse in Applied Training Ground requires spraying | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-03 07:30:00 | Fail | Dom Coniglio Weedspray 6.30 am-7.30 am
MSA-DFES | WA3625550 | rear engine room door not working up or down only manually flashing | CFRS Canning Vale | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-20 10:15:00 | Fail | Technician attended the site of Canning Vale Fire Station, Engine room door W20577 on 16/09/2020. Following a full test and inspection of door components found fault to be door is not working. Waiting on parts to do the repair. The door will only work from the chain till the parts come in. Door is tagged out. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3625604 | Septic tank - Emptying of septic Tank system at O’Connor workshop | Fleet Management Services - O'Connor Workshop | GMP-BR | Waste Management | Plant & Pumps (WM) | Western Resource Recovery Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-10-01 11:31:00 | Fail | COMPLETED 25/9/20
MSA-DTAG | WA3614180 | ground external Tree roots are lifting a few pavers outside the Old Court House Law Museum OHS issue | Supreme Court | WSM-BR-SITE | Paving & Roadworks | Paving (PR) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 14:00:00 | Pass | PAVERS REMOVED, ROOTS CUT OUT & PAVERS REPLACED
MSA-DTAG | WA3615666 | most floors in SAT building alarms going off includint a couple of duress alarms | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 13:19:42 | 2020-09-15 12:00:00 | Pass | Level 6, Room 6.01 duress activated on 14th September at 9pm. Sirens activated and alarms generated. Emergency lock shut door and secured door until the physical duress is reset, and alarm acknowledged by operators. Ran full log of previous 24hrs for Alarm Events, Access Events and Operator Events. Advised both Jill on L10 DMJC Control Room, and advised Peter Sermon at SAT Level 6. Appears cleaner activated duress and did not report incident. Inputs were disarmed on Unison and thus causing access issues due to door dependencies. Full Report emailed to client(s) on site. Job completed
MSA-DTAG | WA3617524 | Lvl 10, Reception Area- Air conditioning unit is vibrating and rattling | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-18 14:00:00 | Pass | Return to site. Access level 10 and remove grill from wall. Fit stripping to back of louvers with silicone and secure. Replace grill in wall and secure. Test operation of air through grill and found vibration noise to stop. Ac working as normal.
MSA-DTAG | WA3620202 | Lvl 6- striker on room 6.01 is not working and the door is not locking | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 15 Sep 2020 | 2020-09-15 14:08:36 | 2020-09-15 13:30:00 | Pass | Duress on 6.01 (emergency lock) activated on 14/09/2020 at 21:00 (cleaners?). Input disabled on Unison and caused access issues. Reports provided to clients on site. All reset and OK. Job completed.
MSA-DTAG | WA3624480 | Level 24 - Security card reader failure in goods lift area | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 16:00:00 | Pass | Spoke with Mark Hi!ditch, meeting him at Level 24 about 2pm to confirm fault and rectify if any. Checked door and appears door not working correctly with free handle egress operation. Programming appears fine, door force allows keypad to beep but not generating alarms to operators. Reed magnet for mortice lock is not operational. Must be using reed on top of door frame. Still testing full functionality but appears to be the door blowing inwards and outwards against the wind of goods lift lobby elevator. Adjusted Egress Operation on Pacom and advised to report if fault still persists. Door however, was tested and all functions working fine. Emailed Mark Hi!ditch with update and he's happy.Job completed.
MSA-DTAG | WA3625039 | External, bin store - Internal door lock in bin store is not engaging | Central Law Courts | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 13:00:00 | Pass | Attended site to adjust 2x doors to bin store as not latching, fit 2x client supplied cylinders to doors.
MSA-DTAG | WA3625616 | Secured courtroom 2 - door not automatically closing and time delay button not working | Rockingham Justice Complex | WSM-BR-SITE | Building | Automatic Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 13:30:00 | Pass | Court 2 door not securing. Found that armature plate not contacting with Maglock on door. Readjusted plate and fixings. Tested operation and all is in working order.
MSA-DTWD | WA3613972 | A Block, Room A146- Security CCTV Software not working in facilities office | East Perth Campus | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-21 17:00:00 | 2020-10-14 09:45:00 | Fail | 15/09/2020, 1015-1030Steve asked if we can rebook or Wednesday as someone is fixing his computer ATM16/09/2020, 930-1030Found software and downloaded it but without admin access can't install.Rang IT and they advised me that Steve has to email apps with the software to be installed and they can do it .Will have to return once it's installed to configure. Steve left to go to another site while onsite and I've advise him of whathe needs to email14/10/2020, 915-945Got cctv software working on Steve's PC
MSA-DTWD | WA3614035 | West Block Male toilet- Tap water leaking | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 15 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 14:35:00 | Pass | Fix leak
MSA-DTWD | WA3614075 | E Block, E72 Skills kitchen- Deep fryer & salamander wont ignite | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 15 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-18 08:45:00 | Fail | COMPLETED 8.45AM 18/9/20
MSA-DTWD | WA3614084 | D Block, Level 2, marketing area- blinds requires fixing & resetting | Joondalup Kendrew Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-22 10:33:00 | Fail | COMPLETED
MSA-DTWD | WA3614355 | L1 William street entry Inner Auto Door not closing | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-15 10:45:00 | Pass | Found that the doors have dropped and were jamming in the floor guides, raised both doors and tested, all ok.
MSA-DTWD | WA3615597 | BLD 822, Dempster hall A wing- Toilets blocked and vanity basins blocked | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 15:00:00 | Pass | Unblocked toilets
MSA-DTWD | WA3618101 | 3-01 to -3-05 Warm - seems like no air | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-09 13:20:00 | Fail | Returned to site before normal hours as per discussion with site FM David Gaff. Gained access to unoccupied classrooms and inspected VAV control zones boxes. Confirmed location and box operation. Rechecked and confirmed AHU was active and operating. Checks set points and air flows registered for rooms. All ok. Checked AHU time schedule. Recheck main plant equipment for signs of fault. All ok. Note boiler 2 was found to have tripped. Equipment was reset and returned to normal operation. Cause of trip is unclear. Work area has been left tidy.
MSA-DTWD | WA3620136 | A Block, Male toilet- Blocked urinal | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 15 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 12:50:00 | Pass | Blocked with build up cleaned and unblocked
MSA-DTWD | WA3622930 | A Block, Room A316- Repair roof leak | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-15 12:00:00 | Pass | lift flashing along eaves in close proximity to leak point, clean rubbish in sheet ends, water test, do additional and seal or completion
MSA-DTWD | WA3623142 | B Block, Room B312 / B313- Repair roof leak | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2021-06-30 13:00:00 | Fail | ROOF REPAIRS MADE TO RECTIFY LEAK
MSA-DTWD | WA3623252 | A Block, Room A236/ A308- Repair roof leak | Leederville Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2021-06-28 13:30:00 | Fail | repair flashings and replace chimney flashings
MSA-DTWD | WA3625392 | House 804 - HWS faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 16:00:00 | Pass | Job completed - Replace faulty valves to HWS at house 4
MSA-DTWD | WA3625406 | L2 Leakage in Koolark Kitchen Cupboard | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 15 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 14:36:00 | Pass | Replace sling unit and tap
MSA-DTWD | WA3625483 | Block 2, G Floor, Disabled toilet- Door lock damaged and won’t accept key | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-16 15:15:00 | Pass | BLock c - G Floor - Disabled toilet door lock jammed.Lock repaired.
MSA-DTWD | WA3625541 | Block 9 L1 main entrance Door won’t close when in auto mode. | Thornlie Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-15 16:24:00 | Pass | 1046098. Found setting switch on side of operator was in wrong position and external button was inter getting stuck in, adjusted switch setting and re fixed external button and tested door all ok
MSA-DTWD | WA3625570 | L block, stone masonry section - vinyl floor titles need to be tested for asbestos. | Balga Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 15 Sep 2020 | 2020-09-16 17:00:00 | 2020-09-21 11:30:00 | Fail | Asbestos sample collected and tested- No Asbestos detected in sample
MSA-DCA | WA3628120 | 2x rubbish bins are loose - see notes | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Building | Internal Walls (BU) | ICS Australia | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 14:30:00 | Pass | Removed the old fixings and installed 8 new ramset fixings. 4 per bin. Removed the old fixings from site.
MSA-DCS | WA3627348 | Numerous cameras not showing on video wall. | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Assistant Superintendent - Offender Services | GMP-BR- HO | Electrical | Materials (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 10:26:14 | 2020-09-16 08:45:00 | Pass | Vid wall screens not working. Windows error present that software failed. Rectified error when looking through log details with virtual memory. Also showed staff how to change maps on Gallagher as when they were selecting visits it was showing Perimeter.
MSA-DCS | WA3627390 | Unit 3, A wing - toilets blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3627409 | Unit 1, D Wing Showers- Plastic waste under basin broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-23 12:20:00 | Fail | Once into unit replaced snapped pipework and trap into wall and refitted plug and waste
MSA-DCS | WA3627411 | Unit 2, Cell A12- Cistern is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-23 13:48:00 | Fail | Repaired broken cistern replacing outlet washer and inlet valve and refitting broken part in bottom off unit
MSA-DCS | WA3627424 | Camera 17 & 173 no vision | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 07:39:59 | 2020-09-17 08:30:00 | Fail | Camera 17- checked throughput the day, tested ok. Camera 173- no image on EBI. Camera ok at EC. Reset power to transmitter fiber modem. Tested ok at the gatehouse.
MSA-DCS | WA3627426 | Entry Pod, Fire alarm battery fault | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 11:43:33 | 2020-09-16 11:02:00 | Pass | Batteries replaced
MSA-DCS | WA3627431 | Kitchen- Combi oven- jets/hoses need clean | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-22 10:40:00 | Fail | Replaced single solenoid & ran oven on cleaning cycle. Returned & replaced water pipe on bratt pan, fitted and tested ok.
MSA-DCS | WA3627437 | Kitchen, Work Area- Small Convotherm showing fault E23 | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-10-16 11:10:00 | Fail | While on site to another job advised that oven fault cannot be repaired.
MSA-DCS | WA3627448 | Unit 5, B & C wings kitchens- Flume hoods grease filters require cleaning | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | DUNBAR SERVICES (WA) PTY LTD | 3 | SSP | 16 Sep 2020 | 2020-09-22 17:00:00 |  | Overdue
MSA-DCS | WA3627459 | Entry, Air lock door lock faulty/magnetic/electric | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 12:08:50 | 2020-09-16 11:58:00 | Pass | Sourced parts, attended site, tested lock and traced fault to door alignment. Found upper door stopper bracket screws loose and lower door stopper bracket broken. Tightened screws on upper bracket and tested door OK but lower bracket requires replacement. Advised security that mechanical contractors are required to replace broken bracket.Job Complete
MSA-DCS | WA3627463 | Unit 13 - A & C fire alarm cell fault system | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-18 08:21:00 | Pass | Wing b/d cells 15&16 intermittent airflow fault caused by prisoners blocking sampling points to smoke in cells, cleared and left normal
MSA-DCS | WA3627468 | Bakery, Workshop- Office door dropped on hinges, hard to open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 13:00:00 | Pass | Replace hinges and fixings
MSA-DCS | WA3627472 | Unit 4, PA system making squealing noise when used | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-11-09 15:30:00 | Fail | Feedback heard when Officer accesses PA while standing beside open Day Room window. Reduced PA Gain minor ammont. No problems occurred when control officer used PA while seated in front of the control console. No further action.
MSA-DCS | WA3627476 | CCTV desktop in Security Office is not down loading footage (access denied) | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 08:17:13 | 2020-09-16 10:30:00 | Pass | Security login did not have permissions to download video from this camera. Corrected permissions list and checked other cameras to confirm correct programming.
MSA-DCS | WA3627479 | Laundry, Tap dripping badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-16 13:00:00 | Pass | Nill
MSA-DCS | WA3627486 | Abattoir, Packing area- Broken drain pipe | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2021-01-29 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3627517 | Unit 7 - A10 Showerhead continuously drips when taps turned off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-18 08:30:00 | Pass | Nill
MSA-DCS | WA3627542 | Unit 1 cell A2 toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 08:43:16 | 2020-09-16 11:02:00 | Pass | Cleared blocked toilet in Unit 1 cell A2, could not see cause of blockage.Adjusted cistern.
MSA-DCS | WA3627554 | Outpatients Area - Tearoom urn not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 10:15:00 | Pass | All working on arrival Power testing yesterday on site
MSA-DCS | WA3627558 | Library East, Office- Air Con blowing warm air | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-10-01 09:00:00 | Fail | Arrived on site and signed in, checked over aircond found thermostat set at 23 degrees, track down key to open anti vandal box,adjust to 21.5 and test run unit all running ok at present.
MSA-DCS | WA3627575 | Video link, Cell 4/5 and plant room - Reed switches damaged | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 09:18:58 | 2020-09-23 08:00:00 | Fail | Replaced reed switch magnets in the middle doors of holding cells 4 and 5. Tested ok. Parts used:2 x 25mm recessed reed switch magnets Consumables
MSA-DCS | WA3627576 | Unit 1, C Wing, Cell C12- toilet will not flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 15:00:00 | Pass | Nill
MSA-DCS | WA3627595 | Unit 7, Cell H17- Main lock faulty, unable to secure cell | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 13:43:20 | 2020-09-16 14:45:00 | Fail | Attended site. Replace main door lock and strikes to main and personal lock. Normal function restored.
MSA-DCS | WA3627628 | Unit 13, B/D side - kitchen sink leaking water from underneath the Unit, flooding the kitchen | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 13:07:00 | Pass | Nill
MSA-DCS | WA3627658 | Gym, North west entry- cracked window approx 650x650 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 13:15:00 | Pass | re glazed window
MSA-DCS | WA3627672 | Unit 6, court yard - Roots have pushed the expansion joints on the entry pathway up , | Casuarina Prison | SPA-BR | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2021-02-25 12:00:00 | Fail | DAMAGED CONCRETE REMOVED & NEW PATH LAID
MSA-DCS | WA3627730 | Unit 4, A13 - Key jams in lock. Unit 4 A13 | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-25 10:30:00 | Fail | Replace barrel, hub and backing plate.
MSA-DCS | WA3627735 | Bakery- S/S panel on the bottom of the door has fallen off | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-25 10:15:00 | Fail | SEAL REPLACED TO FREEZER ROOM DOOR
MSA-DCS | WA3627741 | Unit 3 - C Wing Door handle on shower block entry handle broken. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-10-29 12:00:00 | Fail | Require parts.Replace handles and spindle.
MSA-DCS | WA3627746 | Unit 4, Cell C3- personal lock needs to be changed, key has been lost | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-25 12:30:00 | Fail | Replace hinges, door plate, lock barrel and weld on strike.
MSA-DCS | WA3627781 | Entry, Perimeter gate bracket broken | Bandyup Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Schlager Construction Group | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 12:14:29 | 2020-09-17 13:00:00 | Fail | Attended site and assessed what repairs where required.Reattended site and carried out repairs to perimeter airlock door.
MSA-DCS | WA3627799 | Metal Shop, Workshop - Hand grinder cable damaged | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-17 12:30:00 | Pass | Repaired damaged grinder in metal shop
MSA-DCS | WA3627878 | control - zone 10 internal microwave is in constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 12:27:46 | 2020-09-17 13:30:00 | Fail | Tested input voltagesto receiver and transmitter microwaves. Checked alignment and removed weeds. Traced fault to input on Sennet module. Repaired and tested ok.
MSA-DCS | WA3627917 | Textiles workshop - faulty light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-17 12:30:00 | Pass | Repaired faulty lights in textiles work shop
MSA-DCS | WA3627955 | Unit 1 A wing - GPO in day room scorched | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 13:03:14 | 2020-09-16 16:30:00 | Pass | Replaced damaged power point
MSA-DCS | WA3627958 | Unit 5 House 4 - Day room Pin is stuck in GPO | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 13:05:22 | 2020-09-16 15:30:00 | Pass | Replaced cracked power point
MSA-DCS | WA3627974 | laundry No 3 electrical smell | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 13:19:10 | 2020-10-07 11:35:00 | Fail | Found motor burnt. To get repaired and return to site to fit repaired motor and overload relay.
MSA-DCS | WA3627977 | orchid pump sump filter split and leaking | Wooroloo Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-19 12:00:00 | Pass | Orchid Pump Sump filter split and leaking badly. Check filter, isolate no.2. Drain water & remove sand. Clean up leaking cracks. Weld leaks. Reconnect to pipework. Run under pressure, all working correctly.
MSA-DCS | WA3627979 | orchid pump sump filter sand levels low req filling | Wooroloo Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-10-27 12:30:00 | Fail | Orchid pump sump filter sand levels low. Check filters, source and sizes & supplier. Order & pick up 10 bags. Deliver to pump shed.
MSA-DCS | WA3628035 | main PTZ camera 20 keeps pointing t ground | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-12-09 13:00:00 | Fail | Replace camera PTZ20 . Program and test ok.
MSA-DCS | WA3628063 | Unit 10, front grille - Lock faulty (buzzer from control, access control issue) | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 14:01:35 | 2020-09-17 11:45:00 | Pass | Checked and found Unit 10 front grill gate not operating and making buzzer sound. Further check and located problem to be gate controller problem. Restart gate controller and tested all ok.
MSA-DCS | WA3628086 | Unit 5 - B10 Possible electrical fault. Prisoner is getting a shock of the tap in his cell. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 14:16:08 | 2020-09-17 16:00:00 | Fail | Investigated prisoner electric shock in unit 5 b10, tested cell. Nothing found all ok.
MSA-DCS | WA3628134 | S O P - A2 reading light bulb needs faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 11:30:00 | Pass | Repaired faulty lights in SOP a2
MSA-DCS | WA3628138 | Education light cover in prisoner in tea room broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 08:30:00 | Pass | Repaired damaged diffusers in education
MSA-DCS | WA3628143 | Unit 3 - East Solinoid not shutting off and there is a leak on the main line. | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-23 08:45:00 | Fail | work completed as per supporting documents
MSA-DCS | WA3628166 | sewage plant - blocked sew line | Wooroloo Prison Farm | SPA-BR | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 19:08:44 | 2020-10-07 13:03:00 | Fail | Priority "0" Watercon employee attended site over 3 days 16-18/09/2020.EMAILED - Nial Dwyer Wed 14/10/2020 for BRAF Approval.EMAILED - Nial Dwyer Wed 04/11/2020 for BRAF Approval.
MSA-DCS | WA3628307 | Unit 1 - has no hot water - issue with boiler | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Boilertronics | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 21:28:22 | 2020-09-17 07:15:00 | Fail | Travelled to site, signed in and completed tool check.The water heater had no power to it.Checked the incoming power and found that there was no control power to the BMS relays.The circulation pumps were not running either.Check the panel and nothing had tripped.Went downstairs and heard alarm from the control room.Alarm was on the fire panel and most likely preventing the boiler from starting.Not able to reset faults.There was also power outages in other areas of the unit.They had lost essential power.Not able to check the water heater until they are able to sort out the power in the unit.The LFL was in start position so the burner should start as soon as the power comes back on and there is a call for hotwater.Advised the guards to call our office if the heater does not start when the power comes back on to it.Signed out and completed tool check.
MSA-DCS | WA3628311 | Gatehouse - Rack 2 - High temp alarm is constantly on the screen in the equipment room | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 21:31:11 | 2020-09-16 20:00:00 | Pass | BA2 Temperature Alarm. Checked aircon in server room and all is working. Temperature for room is 21 degrees. Tested thermo stat and intermittently false alarming on relay. Power cycled unit and tested operatio, all is ok.
MSA-DCS | WA3628320 | Sally port - inner roller door playing up - intermittent not closing | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 16 Sep 2020 | 2020-09-16 22:18:26 | 2020-09-16 19:45:00 | Pass | 16/09/20Identify fault. Faulty PE Beam.240v device - electrician required to replace.AFD will supply device from stock.
MSA-DFES | WA3627360 | blown 10/12 Fluro Lights in the roof of Pump House | VFRS Kwinana | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-25 11:00:00 | Fail | Arrived to site at 11:00 and inspected faulty lights will need to swap left site at 11:15Collected gear and attended site. Replaced faulty fluros in engine bay. All in working order
MSA-DFES | WA3627622 | Pump House- Garden Reticulation controller is working, but pump has an error light and not working | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-18 15:30:00 | Pass | Murray Hay Electrician 1.30 pm to 3.30 pm
MSA-DFES | WA3627668 | Reception Area - Flickering light | DFES Regional Office - Joondalup | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-16 12:45:00 | Pass | Repaired flickering fluro light and notified staff
MSA-DFES | WA3627931 | Ground floor, foyer - CQRIT safe Keys for 1& 15 wont release | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-21 11:15:00 | Fail | 17/9/20 - Dylan ParslowUnable to access hardware to keybox due to new keybox installed by others.21/9/20 - Dylan ParslowInvestigated issues with keys 1 & 15.Found connections for some of the mechanisms loose.Likely knocked out of place by installation of new cable for lock boxes.Reassembled and tested all keys.All working ok.
MSA-DFES | WA3628140 | kitchen cupboard door in front of - door has fallen off the hinges due to rot. | CFRS Maddington | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 15:00:00 | Pass | Replaced hinges to kitchen cupboard door
MSA-DFES | WA3628145 | Towel Roll Dispensers in Kitchen and Relieving Bathroom 1 are loose | CFRS Maddington | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 15:00:00 | Pass | Reattached towel dispensers with new fixings
MSA-DFES | WA3628197 | ground disable toilet hand basin front of admin building very slow to drain | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 08:28:00 | Pass | Fwg block cleared
MSA-DTAG | WA3627562 | Retic leaking between access gate and garden next to court room 3 | Armadale Courthouse | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-11-27 16:00:00 | Fail | BRAF Raised 22/09/20There was a delay in getting parts to complete this job
MSA-DTAG | WA3627567 | Lift 3 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 16 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-16 16:00:00 | Pass | Monitored lift for intermittent fault, nothing present. Left lift in service
MSA-DTAG | WA3627580 | Female Public Disabled Toilets - not flushing and water does not appear to be going into the cistern | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-16 13:45:00 | Pass | COMPLETED
MSA-DTAG | WA3627617 | ground court 1 registry Fire Sensor in Court 1 beeping - see notes | Mandurah Courthouse | GMP-BR-HO | Fire Protection Services | Smoke and Heat Detection (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 14:30:00 | Pass | Investigated fire panel fault
MSA-DTWD | WA3627377 | Science block, Male Toilet S9 3.1- WC pan blocked and urinal overflowing on to floor | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 16 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 12:51:00 | Pass | Fix toilets
MSA-DTWD | WA3627386 | Graffiti Around outside of building to be removed | Perth Campus B6 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 16 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 11:15:00 | Pass | REMOVAL OF GRAFFITI FROM VARIOUS LOCATIONS AROUND CAMPUS
MSA-DTWD | WA3627540 | C Block, barrel to Gate/ door to C102 Masonry room needs repair | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-16 10:30:00 | Pass | replace faulty LW3782 mortice lock C102
MSA-DTWD | WA3627544 | A Block,Student Services Female toilet - light not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-16 14:54:00 | Pass | Replaced faulty lamps to toilet light job completed
MSA-DTWD | WA3627549 | M002 lock is faulty - Staff only door | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 13:30:00 | Pass | Replaced cylinder
MSA-DTWD | WA3627559 | U017 lights constantly tripping | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-17 13:00:00 | Pass | Replaced faulty lamps and fittings
MSA-DTWD | WA3627571 | G Block, Room G123- 1 x toilet flooding, 1 x toilet blocked and cleaners sink blocked. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-16 15:29:00 | Pass | Cleared blockage using jetter
MSA-DTWD | WA3627644 | Workshop Male toilets - urinal auto flush not working | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-23 09:44:00 | Fail | Installed new sensor and solenoid
MSA-DTWD | WA3627970 | A block AM105 conference room - faulty sensor, turns lights off after 30 seconds | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 13:01:00 | Pass | Attended site, signed in, spoke with fm about problem, completed jsa, investigated reason sensor wasn’t working correctly, switch on wall has an auto setting for the sensor and a manual setting to have lights come on ad stay on , spoke to fm and he said leave as is , completed paperwork signed out ***job complete***
MSA-DTWD | WA3628091 | D block, D3 - leaking tap | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-18 14:38:00 | Pass | Fix taps
MSA-DTWD | WA3628148 | L2 corridor Low Pressure in water tap | Perth Campus B4 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 14:32:00 | Pass | Fix pressure issues
MSA-DTWD | WA3628205 | L block, garden bed - damaged storm water lid in garden bed | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-12-02 11:00:00 | Fail | Replaced concrete lid of pit
MSA-DTWD | WA3628222 | Plant room Air con not working | Perth Campus B4 | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 16 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 06:13:00 | Pass | Contacted by site facilities and advised on numerous hot complaints from build 4. Attended site gained access and carried out inspection of plant. Chiller was found to be in alarm indicating that the cooling interlock had not been made. This can occur if the system is trying to start and no water flow is registered by the equipments sensor. Checked pump operation all ok. Confirmed good flow and reset chiller monitored equipment operation. All ok. No further fault occured. System will be monitored over the next site PM inspection for further signs of fault. Work area has been left tidy.
MSA-DTWD | WA3628231 | north side L block damaged bollard | Balga Campus | GMP-BR | Building | General Building (BU) | AWB Co. | 2 | CLOSE | 16 Sep 2020 | 2020-09-21 17:00:00 | 2020-10-05 11:00:00 | Fail | Pine Bollard to match existingIncludes time spent procuring
MSA-DTWD | WA3628238 | B block B2110 – Damaged GPO | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 16 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 14:00:00 | Pass | Rectified loose cable to gpo . Tested power all working now. Job completed
MSA-DCA | WA3641652 | back of house 6 and7 staff lift out of service due to object in lift shaft | State Library of WA-Main Building-Level 1-1.15 - Staff Workroom | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 16:30:00 | Pass | Retrieved mop head from pit and sent lift back into service
MSA-DCA | WA3641676 | playground Temp fencing required to fence off the playground | Sunset Hospital Heritage Precinct-External Area | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-10-14 14:30:00 | Fail | Installed 48 panels of temp fencing - 4 weeks hire - fence now removed at PFM request
MSA-DCA | WA3641695 | Termite inspection for outdoor playground | Sunset Hospital Heritage Precinct | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 13:15:00 | Pass | Works completed 17/09/2020
MSA-DCS | WA3641558 | Doors in front gate has dropped | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 11:30:02 | 2020-09-17 09:30:00 | Pass | Attended site. Repaired lock/fixing tag and tightened all fixings. Normal function restored
MSA-DCS | WA3641559 | Kitchen - Blast Chiller no 2 is not working | Hakea Prison | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 07:28:47 | 2020-09-17 09:15:00 | Pass | Duplicate job. Closing job.
MSA-DCS | WA3641562 | Unit 5, All Cells- Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 11:34:24 | 2020-09-17 09:30:00 | Pass | Attended site checked and found Unit 5 cell call system not working properly. Control can’t make PA call through cell call. Reboot control panel in office and tested ok after.
MSA-DCS | WA3641583 | PE door sensor 240V is not responding | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 07:47:49 | 2020-09-17 11:00:00 | Pass | Investigate sally port door - source parts and replace door sensor
MSA-DCS | WA3641591 | Cog Skills, Kitchen sink tap is dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 14:57:00 | Pass | Nill
MSA-DCS | WA3641593 | Unit 14, Cell A8- shower drain is blocked and shower head is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-17 09:30:00 | Pass | Nill
MSA-DCS | WA3641598 | INF (10)- lock has snapped off on staff toilet door in the infirmary. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 17 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-23 10:00:00 | Fail | Replace toilet indicator lock bolt
MSA-DCS | WA3641599 | Unit 2, B & D- no display on the urn and no water is dispensing from it. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 17 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-23 09:45:00 | Fail | All working on arrival Electrician required to test RCD is okay - advised site of this and that Rheem recommend this unit to be hard wired.
MSA-DCS | WA3641618 | Unit 2 - C Wing GRILL NOT WORKING MECHNICALLY | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 10:15:00 | Pass | 17/09/20Replace broken limit switch
MSA-DCS | WA3641641 | Unit 1, Control Room- Computer screens that operate doors are down | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 12:29:12 | 2020-09-17 10:00:00 | Pass | Unit 1 Door Control not working. Found Door Control and CCTV computer are both switched off. Switched both PCs back on and setup screens. Tested operation and all is ok.
MSA-DCS | WA3641647 | Unit 3 all cells calls not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 12:34:39 | 2020-09-17 10:15:00 | Pass | Attended site checked and found Unit 3 cell call system not working properly. Control can’t make PA call through cell call. Reboot control panel in office and tested ok after.
MSA-DCS | WA3641714 | medical centre Pharmacy Inside Wall by the Entrance door-alarm pulled out of wall | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 09:15:35 | 2020-09-17 11:15:00 | Pass | Pharmacy Keypad off the wall. Re-fixed keypad and terminated. Tested operation and all is working.
MSA-DCS | WA3641737 | EC in zone 8 & 9 comms fail | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-08 14:54:00 | Fail | Installed Planet IGS-10020MT and programmed
MSA-DCS | WA3641741 | Senstar tamper 15 | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-12-04 15:26:00 | Fail | Cabling complete system operational
MSA-DCS | WA3641743 | Gatehouse control failed | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 09:19:00 | Pass | Complete under WA3644560
MSA-DCS | WA3641745 | Gallagher no audio | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 09:17:00 | Pass | Completed under WA3644560
MSA-DCS | WA3641777 | Unit 5 - B Wing tap does not turn off - contractor on site | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-17 11:30:00 | Pass | Nill
MSA-DCS | WA3641779 | Unit 3, Cell B12- Hatch window cracked | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-18 14:30:00 | Pass | OBS PANEL REPLACED/ FRAME REPAIRED
MSA-DCS | WA3641796 | ABATTOIR STORE ROOM 2 light fittings broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-18 09:00:00 | Pass | Investigate and repair/replace lights in abattoir store room
MSA-DCS | WA3641809 | Internal Grounds, Oval- Retic Solenoids not working | Melaleuca Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 09:00:00 | Pass | system inspected and no fault found, reset system and programmed.
MSA-DCS | WA3641825 | Gate house - blocked drains | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-17 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3641847 | Unit 5, Cell B10- door is not closing correctly and is jamming | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-02 12:00:00 | Fail | Obtain further job details - Job is Unit 3 B10.Replace hinges, lock and weld on strike.
MSA-DCS | WA3641850 | Library- 3 bays of 2 fluro light are out- 5.4metres high | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-07 13:30:00 | Fail | Repaired numerous faulty lights in library using scissor lift
MSA-DCS | WA3641898 | ISU (Harding), Cell A08- Broken power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 15:00:00 | Pass | Replaced single gpo isu cell a08
MSA-DCS | WA3641900 | ISU (Harding), Cell A04- Broken power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-17 14:00:00 | Pass | Replaced broken light switch isu cell a04
MSA-DCS | WA3641905 | Lenard C wing Cell C07 Faulty Toilet solinoid | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 10:39:00 | Fail | Reppaced solenoid
MSA-DCS | WA3641920 | Unit 2, Control Room- Air con Faulty- further notes below | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 07:45:00 | Fail | Fault already known about. Parts ordered and due to arrive 25/09. Closing job
MSA-DCS | WA3641960 | Unit 13, Cell D13- Low water pressure in shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 14:41:00 | Pass | Nill
MSA-DCS | WA3641977 | Reset- Demountable has dropped away from ramp and requires repair to make safe | Hakea Prison | GMP-BR- HO | Building | Steel Work (BU) | Midolo Building Services | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 11:52:51 | 2020-09-18 15:00:00 | Fail | LOOSE BLOCK PAVERS REMOVED & CONCRETE IN PLACE
MSA-DCS | WA3642070 | ladies toilet door bracket on door has come off the door- | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 16:32:47 | 2020-09-18 10:00:00 | Fail | Attended site supplied and fitted a new hydraulic closer to female toilet door.Resecured push plate to the face of toilet doorFilled and sanded old fixing holes and painted to match existing door colour.
MSA-DCS | WA3642159 | MDAS failed:-see notes | West Kimberley Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 21:40:57 | 2020-09-21 13:13:00 | Fail | , following dInvestigated fault, attended site, traced fault to a moxa device in Unit 3 Office, replaced and programmed, monitored OK. next day same fault reoccured. Traced to Moxa device in Unit 3 houses. Replaced and programmed and tested OK.Job CompleteParts:2 x Moxa Nport 6150 - Site StockConsumables - SEME StockInvoice raised for costs to date
MSA-DCS | WA3642167 | EC2 constantly alarming | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 15:00:00 | Pass | Tamper alarm not sealing,Removed tamper switch from faulty PE beam and installed into zone 5.Tamper circuit sealed. Cables corroded, recabled from PE beam to surge protection
MSA-DCS | WA3642177 | Lenard C wing kitchen water not staying hot (suspect pump issue) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-10-05 12:50:00 | Fail | Inspected faulty recirculating system. Waited for 1:20h fro access die to busy sally port. Unable to get in the unit on time due to lock down.
MSA-DCS | WA3642186 | S O P - A7 MAIN LIGHT NEEDS FIXING AS IT FLICKERS | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 13:00:00 | Pass | Repaired faulty lights in SOP a7
MSA-DCS | WA3642220 | Omnitrax zone 4 and 11 constantly alarming. | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-19 13:53:00 | Pass | Investigated zone faults, recalibrated zone 4 and 11, monitored for correct operation and tested OK.Job Complete
MSA-DCS | WA3642266 | unit 1 pod 4 HW urn unit tank split | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 15:06:25 | 2020-09-21 15:00:00 | Fail | Complete
MSA-DCS | WA3642329 | Gate control room - Indigo Monitor (Next to MDAS) has stopped working and states Indigo programme | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-18 08:00:00 | Pass | Job complete
MSA-DCS | WA3642377 | Security officer - Duress alarm #16 constantly alarming | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 16:28:39 | 2020-09-18 09:30:00 | Pass | Attended site checked and found MDAS 16 is faulty. Replaced and programmed with new duress pendant. Tested it ok after replacement. Bosch SE2S-SN-304 X 1.
MSA-DFES | WA3641974 | G Floor - Numerous carpet tiles have lifted off the floor and require re-sticking. | CFRS Perth | GMP-BR | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-30 16:10:00 | Fail | Attended site and reglued lifting carpet tiles in areas required.
MSA-DFES | WA3642062 | ground dorm 5 A/C in dorm 5 will not heat | CFRS Kiara | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-12-19 15:59:00 | Fail | COMPLETED
MSA-DFES | WA3642069 | Training Room 2- aluminium framed window has come loose on right hand side | SESU Northshore | GMP-BR | Building | Windows (BU) | AWB Co. | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 13:00:00 | Pass | Liam Hanlon (21/09/2020) - Work Note*not a manned site Training facilities SESCare taker Ronda lives next door Trade attendance is usually Thursday Wednesday evening training for volunteers Attend site and got access Inspect window Rivets have failed and window come loose from angle and timber frame Need to return after 11 when care taker has returned from appointment Arrived 1130 Got access Removed blinds Re fit window to angle and angle to timber frame work Cut old padlock as instructed by DFES to get hinges grate open Cleaned area Locked grate with a bolt (temp) Silicone RHS inside framework Vacuum and clean up
MSA-DFES | WA3642071 | Ops Room / Generator Room- set of outside lights have stopped working - further info below | SESU Northshore | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-22 09:30:00 | Pass | Locate faulty lights. Replaced faulty tubes and starters with new. Test PEcell on the roof and it is working fine.
MSA-DFES | WA3642089 | Foyer- battery fault alarm has activated on the fire indicator panel | CFRS Ellen Brook | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 08:30:00 | Pass | Soft plus hard reset completed. New batteries installed 2 x 12 a/h. Panel functioning correctly.
MSA-DFES | WA3642285 | ground engine room Front engine door (door 3) not opening fully | CFRS Daglish | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 07:45:00 | Pass | Technician attended the site of Daglish Fire Station, Engine bay door 3 A403522139/ W23726 on 18/09/2020. Following a full test and inspection of door components found fault to be not opening fully and closing a bit too hard. Technician has adjusted limits to make door open fully and close properly. Carried out full test of operation ok. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3642293 | L1 back veranda outdoor tap next to water heater leaking | DFES Rescue Helicopter Base | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-18 14:15:00 | Pass | Fit new hose tap and vacuumed breaker
MSA-DFES | WA3642297 | L1 Engineering office leak in ceiling - see notes | DFES Rescue Helicopter Base | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-18 15:15:00 | Pass | Located suspected leak and applied silicone. Will need further rain to confirm if leak has been resolved29/9 - Max on site confirmed no further leaks reported and agreed to close off job.
MSA-DFES | WA3657289 | RETROSPECTIVE - MULTI ON MULTI - do not attend as already attended | DFES Regional Office - Belmont | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 19:56:00 | Pass | EXTERNAL SECURE NO SINGS OF FORCED ENTRY NO SINGS OF DAMAGE NO PEOPLE FOUND ON SITE NO DAMAGE TO THE CARS ON SITE CAN'T ACCESS SOME OF THE BUILDING GOOD SEAL BY TRENT
MSA-DTAG | WA3641861 | G Floor, Male Public Toilets- One of the male public toilets, opposite Caffisimo, is blocked. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-18 09:45:00 | Pass | Complete
MSA-DTAG | WA3641949 | Front Steps - Tile has broken off | Perth Children's Court | GMP-BR-HO | Flooring | Tiling (FL) | Midolo Building Services | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-18 14:00:00 | Pass | TILE RE ATTACHED
MSA-DTAG | WA3642291 | 1903 ground court 2 Air Conditioning Failure | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 19:29:23 | 2020-09-18 09:00:00 | Fail | Attend site. Access AC unit serving court 2. Found unit not running. Go through safety control circuit and found compressor 1 tripped on high pressure. Reset high pressure switch. Reset unit lockout. Check operation, found condenser water pump to operate as normal. Access roof and check cooling tower. Found water going through tower as normal, check operation of cooling tower fans by adjust thermostat. Fans work as normal. Return to unit and check refrigerant head pressure, normal. Unit is now working ok.Will return and further test operation in morning.Return to site. Carry out further operational testing of court 2 AC. Found to be working as normal with no issues.
MSA-DTWD | WA3641519 | A Block, Plant Room - Boiler not activating in morning start up schedule- further notes below | Leederville Campus | GMP-BR | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 17 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-17 15:30:00 | Pass | Drive to site meet client and gain access to plant room carried out some checks on heater but could not check BMS was on as no water be could turn it on, i believe the problem is a BMS fault and not a heater fault
MSA-DTWD | WA3641568 | C block, Level 2, Mens toilet - Sink taps leaking | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 14:30:00 | Pass | Complete
MSA-DTWD | WA3641572 | Science- air gas bottle in the gas gage area is leaking badly | Murdoch Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC | 1 | CLOSE | 17 Sep 2020 | 2020-09-17 17:00:00 | 2020-09-17 13:00:00 | Pass | Repairs to leak
MSA-DTWD | WA3641628 | E block ground E600 top hinge and closer on swinging glass door is damaged and needs repair. | Midland Campus | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-21 11:01:00 | Fail | 17/9/20 - Door closer has failed, revisit required to replace with an rts85 en4 with a side load arm to suit.21/9/20 - Removed door from opening and re-secured door leaf as necessary, replaced transom closer and drive arm, rehung door, realigned , adjusted and tested. (No programme asset number on this door)
MSA-DTWD | WA3641670 | Corridor A256 - Repaint Door | Perth Campus B5 | GMP-BR | Painting | Internal (PA) | AWB Co. | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 11:00:00 | Pass | Prepped and painted double door & frame
MSA-DTWD | WA3641706 | house 807 bathroom Burst water pipe inside wall | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 13:30:00 | Pass | Job completed - Remove weather boards to outside of House 7to repair leaking copper water pipe in
MSA-DTWD | WA3641709 | A Block, Hot water system is not working | Murdoch Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-23 15:30:00 | Fail | Need hws installed
MSA-DTWD | WA3641757 | S100 female toilets blocked | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 17 Sep 2020 | 2020-09-17 13:36:50 | 2020-09-17 15:45:00 | Fail | Attended site,Locate blocked sewer lines to s100,Collect jet wash and use to clear blockage. Note: plenty of female products removed from sewer. Tested works on completion
MSA-DTWD | WA3641808 | door behind beauty counter cannot be opened | Perth Campus B2 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 09:35:00 | Pass | gain entry and replace faulty lw3572 mortice lock
MSA-DTWD | WA3642017 | A Block, ROom A208- Lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-06 11:45:00 | Fail | Attended site and signed in. Inspected lights not working. Ran new cable to lighting circuit. Tested all working fine. Job complete.
MSA-DTWD | WA3642032 | block 10 ground male toilet Ceiling collapsing above urinal | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 17 Sep 2020 | 2020-09-18 17:00:00 | 2020-09-17 14:30:00 | Pass | Plumber required - major works. Site asked us to close it off
MSA-DTWD | WA3642047 | L2 fault on panel | Perth Campus B1 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 17 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 08:30:00 | Pass | .Fault on EWIS panel "north LVL 2" - other trades wiring in ceiling disconnected cable from 1 speaker. Found speaker and refit cable with fault cleared.
MSA-DTWD | WA3642143 | C and J block ground J125 Please repair 2 x double outlet single phase GPO's with faulty switches. | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 13:45:00 | Pass | Located 2x faulty Gpo and 1x faulty light switch in C&J block Replace Gpo and repaired switch. All now working
MSA-DTWD | WA3642244 | P block L1 : McLarty. P block. P107. Data port PP1-7-1 faulty. Will require repair | Joondalup McLarty Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 14:00:00 | Pass | Tested data point and found it to be faulty, re-terminated and re-tested.
MSA-DTWD | WA3642248 | Lvl 10, G Floor, Male Toilet- Leaking urinal | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 19:14:00 | Pass | Fix leaks in plumbing ducts
MSA-DTWD | WA3642258 | A Block, AAC2 fan status fault | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 17 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-18 16:00:00 | Pass | Signed in and booked out the keys. Found air-conditioning system number 2 in A block not cooling, found the circuit breaker for the compressor had tripped. Checked the compressor and contactor for problems, all ok . Reset and ran up amp draws 11-12amps per phase which is within manufacturer recommendation , monitored the operation to make sure the circuit breaker didn't trip again.Found the air sensor for the evap fan status had a cracked line , replaced the line and the switch works ok.
MSA-DCA | WA3642698 | Beaufort st entrance- bollards are not dropping | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 13:31:00 | Pass | Investigated bollards, cleaned out where possible, set air pressures tested system and safety loops all working
MSA-DCA | WA3643258 | next to staff area restore lighting that was remove due to leak | State Library of WA-Main Building-Level 3-Print Room - Next to Finance | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 15:17:00 | Pass | Repaired light and reinstalled
MSA-DCA | WA3643449 | RO Plant low water level alarm going off. | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-LV Switch Room and Disaster Recovery Store | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 21:27:07 | 2020-09-19 00:00:00 | Pass | DLGSC made contact regarding Low RO Water Alarm at AGWA.Logged into BMS remotely. Besides alarm, no active faults or noticable problems.Call-out logged. Attended site. All water pressures ok, no mech plant faults. RO storage tanks almost empty. RO CMD manual stop. Returned to Auto. Controls contractor to investigate. Monitored staging. All alarms cleared.Closed job.
MSA-DCS | WA3642660 | Kitchen, Back passage- checker plate damaged | Hakea Prison | GMP-BR- HO | Building | Steel Work (BU) | Midolo Building Services | 3 | CLOSE | 18 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 13:30:00 | Pass | SECURED CHECKER PLATE
MSA-DCS | WA3642672 | Kitchen, Medium cooking bell - water taps and bracket damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 18 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 08:05:00 | Pass | Turned off water replacing tap washer and valve straightend bracket and tightens fixtures
MSA-DCS | WA3642675 | Kitchen, Rear grill gate - Lexan damaged on grill | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 3 | CLOSE | 18 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 13:30:00 | Pass | Ryan Nicholson (21/09/2020) - Work NoteTravel to site. Got escorted to gate. Found rear grill manual gate has perspex broken at the bottom left hand corner. Cannot fix. Recommend a screening/perspex company to install new sheet.
MSA-DCS | WA3642681 | Unit 3, Regi steel folding shelf - 3 hinges are damaged | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 18 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 12:30:00 | Pass | INSTALLED NEW HINGES
MSA-DCS | WA3642687 | Unit 6, Cell C1- Toilet not flushing properly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 09:25:00 | Fail | Removed cistern replacing inlet valve and outlet washer
MSA-DCS | WA3642692 | Unit 6, Cell C2- Toilet not flushing properly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 10:48:00 | Fail | Removed cistern replacing inlet valve and outlet valve
MSA-DCS | WA3642694 | Unit 6, Cell C6- Toilet not flushing properly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 12:20:00 | Fail | Removed cistern replacing outlet washer
MSA-DCS | WA3642700 | Unit 6, Cell B1- Tap leaking keeps running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 13:48:00 | Fail | Replaced pillar tap/inlet valve / and outlet washer all at unit 6 b1
MSA-DCS | WA3642701 | Unit 6, Cell B4- Toilet keeps running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 15:20:00 | Fail | Removed cistern replacing outlet washer
MSA-DCS | WA3642703 | Unit 6, Cell D3- Toilet keeps running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-24 16:40:00 | Fail | Removed cistern replacing outlet washer
MSA-DCS | WA3642716 | Unit 5, Cell C2- Water leaking though tiles into the cell | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2021-03-19 14:30:00 | Fail | NEW TILES AND GROUT INSTALLED
MSA-DCS | WA3642735 | unit 2 recreation yard Fence has been tampered with and needs repair | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 07:57:03 | 2020-09-18 10:15:00 | Pass | 18/09/20Inspect and repair damaged fence at Unit 2B Wing.Workshop - load tools and source materials.
MSA-DCS | WA3642738 | Unit 5, B & D Wing- Wall heater broken | Hakea Prison | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-02 14:00:00 | Fail | 2 x Broken wall heaters Unit 5 Replaced
MSA-DCS | WA3642754 | Gatehouse, Control Pod- Cameras VIS-Cam 004 & GHB-Cam 001 are not working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 08:25:10 | 2020-09-22 17:04:00 | Fail | Sourced parts, installed and configured replacement temporary network switch to restore camera function. Complete repairs under existing job WA3454453.Tested OKConfirmed recording.Job Complete
MSA-DCS | WA3642755 | Investigate damaged asbestos and make safe/seal to Section 94 Shed-see notes | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-12-04 10:45:00 | Fail | ASBESTOS RE SEALING COMPLETED
MSA-DCS | WA3642756 | Unit 2, Cell D13- Shower tap won’t turn off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 08:40:55 | 2020-09-18 13:34:00 | Pass | Replaced leaking spindles in the showr
MSA-DCS | WA3642841 | SOP - Door handle to main door has come off leaving it only to be open by pulling the key. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-22 13:30:00 | Fail | Requires new handles.Install new handles and fill old holes.
MSA-DCS | WA3642859 | Youth Psychological Services Faulty Ceiling Panel Light | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-18 15:30:00 | Pass | Replaced broken lights with new ones, test ran ok .
MSA-DCS | WA3642951 | Zone 7 fence not alarming | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 10:17:09 | 2021-02-22 15:00:00 | Fail | Replaced 80M microphonics cable and calibrated sensitivities. Job completed.
MSA-DCS | WA3642952 | Que - camera 109 not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 10:18:41 | 2020-09-18 12:30:00 | Pass | Attended site checked and found Camera 109 not showing on EBI or Maxpro. Further check located problem to be the Fiber modem not working properly. Rebooted Fiber modem and tested it all ok.
MSA-DCS | WA3642954 | Zone 13 microwave in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 10:19:22 | 2020-09-18 14:00:00 | Pass | Zone 13 microwave was in constant alarm. Checked in field found microwave receiver out of alignment. Aligned the microwave receiver. Tested alarm activated and reset correctly.22/9/20 reattend as job recalled. see signature slip
MSA-DCS | WA3643050 | Lenard A wing Cell# A01 Faulty Toilet solinoid | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 12:30:00 | Pass | Replaced faulty solenoid
MSA-DCS | WA3643085 | Laundry, officers lunch room- Sink hot water system not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 15:20:00 | Pass | Hwu not getting hot got electrison to check power unit was on but buggerd replaced with new
MSA-DCS | WA3643092 | Bakery Bun Rounder lever will not engage when under pressure | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 11:52:46 | 2020-09-18 14:15:00 | Pass | 18/09/2020Arrived at site liaise reception, walk to bakery, identify bun rounder, isolate remove panels, test/fault find diagnose and found the roller pin has snapped off removed broken pin supply and replace pin reassemble all components and tested all components for correct function all okay.
MSA-DCS | WA3643240 | Cleaning- Polishing machine from unit 14 is not working | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 13:30:00 | Pass | Repaired damaged floor polisher in cleaning workshop
MSA-DCS | WA3643289 | Front Gate, Front Door- Dock lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 18 Sep 2020 | 2020-09-18 18:26:40 | 2020-09-21 08:45:00 | Fail | 18/09/2020. Attended site. Apparent intermittent fault. Likely failing key switch. Replacement required. 21/09/2020. On site. Replaced key switch.
MSA-DCS | WA3643293 | control room mouse that drives computer for security system is not left clicking | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Sep 2020 | 2020-09-18 18:29:20 | 2020-09-18 16:15:00 | Pass | Attended site checked and found SEC2 workstation monitor frozen, no response to mouse and keyboard. Further check located the problem to SEC2 workstation computer not working properly upstairs in equipment room. Reboot ASEC2 workstation and tested all ok.
MSA-DCS | WA3643432 | Unit 3 Crisis care key stuck in lock going out to back garden | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 18 Sep 2020 | 2020-09-18 20:58:22 | 2020-09-18 18:00:00 | Pass | Replaced lock in door to Garden Unit 3 / Crisis care
MSA-DCS | WA3643436 | West Kimberley Regional Prison - Broken fence electrical wire in zones 11 and 12. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-25 14:46:00 | Fail | Used 100m of Gallagher fence wire and repaired fence 100m Gallagher fence wire from PFM stock
MSA-DCS | WA3643438 | Wooroloo Prison Farm - Gatehouse - Key watcher's door needs repairing. | Wooroloo Prison Farm | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 12:00:00 | Pass | Attended site and serviced pivot pins on key cabinet doors.
MSA-DCS | WA3643439 | Wooroloo Prison Farm - Sewerage Pond - lock needs to be replaced to an e-key | Wooroloo Prison Farm | GMP-BR- HO | Carpentry | Materials (CA) | ACE LOCK & SAFE | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 15:45:00 | Pass | Rekeyed lock on new demountable unit at sewarage Pond Lock keyed to E Key as requested .
MSA-DCS | WA3646679 | Sewerage plant, blocked sewer line | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Sep 2020 | 2020-09-19 14:00:00 | 2020-09-18 18:30:00 | Pass | Complete
MSA-DFES | WA3643039 | female toilet is cubicle toilet is flooding and please check other toilets | VFES Karnup | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 14:59:00 | Pass | Investigate flooding toilet located remain cubicle Turn water mains on to locate leak, small water leak at top of flush pipe near cistern nut, also leaking from flush pipe keeseal rubber,remove both rubbers/seals and supply and install new 50mm flush pipe rubber and new 40mm keeseal rubber, remove silicone and debris from flush pipe and toilet pan to create better sealTest operation and check for leaks, pack up and clean up worksite
MSA-DFES | WA3643123 | roof Front Gutter of Pump House is falling off. | VFRS Kwinana | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 14:45:00 | Pass | Scheduled for attendance today 22/9/20
MSA-DFES | WA3643133 | front of station Front Sprinklers been broken. | VFRS Kwinana | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 12:35:00 | Pass | Call out, Labour & Retic Parts
MSA-DFES | WA3643242 | alarm system keeps activating - please see notes | DFES Baldivis | GMP-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 16:17:00 | Pass | Found zone 14 south entry door false alarming, replace reed switch and magnet, test, all ok
MSA-DFES | WA3643310 | ground tunic room light sensor faulty - see notes | CFRS Malaga | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-22 11:30:00 | Pass | Locate faulty sensor. Put both sensors on the lowest time settings and test both sensors are working fine. Asked staff for further information. But they were not sure one. we showed one of the guys that the sensors are working. If the fault is called again I recommend replacement of both sensors.
MSA-DTAG | WA3642834 | Sewage Pump alarm going off. This is the 3rd time this fault has been logged in September . | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 13:09:00 | Pass | COMPLETED
MSA-DTAG | WA3643110 | ground custody Gurgling sound coming from cells 1,2,3 & 4 toilets | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-29 15:00:00 | Fail | Complete
MSA-DTAG | WA3643216 | Court 53-Public gallery seating is noisy impacting on Court directions,chairs & mountings loose | Central Law Courts | WSM-BR-SITE | Furniture | Indoor Furniture (FU) | Midolo Building Services | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 09:45:00 | Pass | REPAIRED SEATING
MSA-DTAG | WA3643267 | Custody Shutdown of custody servies - see notes | Supreme Court | WSM-BR-SITE | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-20 18:00:00 | Pass | Job completed - Attended site after hours to turn off all services due to electrical works. All servers & work stations turned off & UPSturned off. Technician to return to site tomorrow when electrical works are completedAttended site after hours. Electrical works completed. Booted up all systems. Checked all cameras. Gallagher hasrestored to normal state OK.
MSA-DTAG | WA3643301 | Blocked Male Public Toilet | Rockingham Justice Complex | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 11:14:00 | Pass | Complete
MSA-DTWD | WA3642597 | Student Kitchen - ceiling lights Broken and diffusers missing x2 | Jandakot Campus - Annex | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-22 11:45:00 | Pass | Arrived on site, signed in to book as iPad sign in wasn’t working , spoke to manager on site , completed jsa , located lighting,isolated lighting, removed old lights , replaced with new , tested , all working as intended, cleaned up work area, completed paperwork, signed out ***job complete***
MSA-DTWD | WA3642785 | U Block, U022 - Emergency exit lights constantly tripping | Balga Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 10:29:00 | Pass | Replaced faulty light fitting causing lights to trip. Job completed
MSA-DTWD | WA3642962 | Block 6 ground female toilet Broken toilet seat in disabled cubical | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-21 19:16:00 | Pass | Fix toilet seats
MSA-DTWD | WA3642984 | block 9 ground Student common room Power points and charger points not working on student couches. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-22 14:45:00 | Pass | Arrived on site, signed in, spoke to fm about job, completed jsa ,set up work area, tested gpos in couches , removed old tags and put up to date tags on leads , located sgpo , got librarians to save work on computers as gpo didn’t have circuit labeled, isolated power, installed new dgpo , labeled circuit , tested gpo , test passed , gave electrical quad power board to librarian , cleaned up work area, completed paperwork, signed out *** job complete***
MSA-DTWD | WA3643066 | ground toilet duct lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 16:15:00 | Pass | Attended site , signed in , spoke to fm about job, located lighting in duct area , completed jsa, isolated lighting circuit, removed old lights , replaced with led batons , re energised circuit, tested lighting , all working as intended , labelled door , cleaned up work area , completed paperwork, signed out ***job complete***
MSA-DTWD | WA3643096 | U Block, Smoke alarm detector is faulty and activating alarm | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 12:45:00 | Pass | U Block east classroom was activating. Found was hanging off ceiling, resecured. Tested, is sealed
MSA-DTWD | WA3643100 | Lvl 2, Room S216- Tap to billi leaking water | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-25 11:11:00 | Pass | Fix tap
MSA-DTWD | WA3643137 | House 809 Outside gully trap blocked | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-18 17:45:00 | Pass | job complete - clear blockage
MSA-DTWD | WA3643189 | Roof, 19Ab roof - remove/clean pigeon droppings | Perth Campus B6 | GMP-BR | Cleaning | Cleaning (CL) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-15 11:30:00 | Fail | COMPLETED
MSA-DTWD | WA3643197 | K Block, Room K12- 1 x Male toilet blocked. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 12:30:00 | Pass | Cleared blockage with jetter.
MSA-DTWD | WA3643205 | D block, D208 - several fluro tubes need replacing on high scale ceiling | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-06 11:00:00 | Fail | Attended site, signed in, spoke to fm about job, completed jsa,replaced various tubes and starters that were left to do , all lights now operating as intended, cleaned up work area , completed paperwork ***job complete***
MSA-DTWD | WA3643214 | Lvl 3, Room A305- Running water in toilet | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-30 14:00:00 | Fail | Installed new Univision’s cistern with push dual flush button
MSA-DTWD | WA3643223 | L1 B154 card swipe not working | Perth Campus B6 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 18 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-21 13:00:00 | Pass | Returned to site and replaced lock.
MSA-DTWD | WA3643264 | main trades area ground male toilets blocked toilet behind mech/ele W/S | Clarkson Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-25 07:45:00 | Fail | COMPLETED
MSA-MRWA | WA3643375 | male toilet blocked and overflowing | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 13:10:00 | Pass | Used drain cleaner and cleared blocked urinal in level 7 LHS
MSA-MRWA | WA3643379 | L1 male toilet Urinal constantly running | Don Aitken Centre MRWA Head Office-Main Building-First Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 14:53:00 | Pass | Repaired urinal cistern LHS and replaced seal kit to flushing buttons to toilet LHS all in level 1
MSA-MRWA | WA3643384 | full flush button has been snapped/broken within the toilet cistern - see notes | Heavy Vehicle Services-Main Building-Ground Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 14:41:00 | Pass | Cleared disabled toilet was blockedReplace button adjusters and platforms on cistern in 5th female cubicle
MSA-DCS | WA3644446 | Electricity to the mains power has tripped out to the communication rack | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 10:26:03 | 2020-09-19 10:00:00 | Pass | Investigate power issue and reset
MSA-DCS | WA3644463 | Hakea Prison-Unit 1- Cell D!0 emergency cellcall not working | Hakea Prison | GMP-BR- HO | Security | Safes (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 13:48:04 | 2020-09-19 12:00:00 | Pass | Unit 1 D10 not working. Checked system and found call still active in software. Cleared call and went to cell. Tested operation and all is in working order.
MSA-DCS | WA3644490 | Main CCTV for the permiter has broken down | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 15:26:50 | 2020-09-19 13:45:00 | Pass | Main CCTV not working. Showed staff how to bring up video explorer to drag cameras over. Replaced 2x AA Batteries for visits keyboard as it’s not working. Tested operation and all is working.
MSA-DCS | WA3644544 | Can't secure Zone 1 - won't secure on panel | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Sep 2020 | 2020-09-20 15:03:16 | 2020-09-19 17:00:00 | Pass | Zone 1 unable to be secured. Checked system and showing Zone 1 tamper. Showed staff how to clear alarms on screen. Able to secure zone and tested operation. All is in working order.
MSA-DCS | WA3644556 | Casuarina Prison - Unit 16 - No hot water. | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 21:30:37 | 2020-09-19 21:00:00 | Pass | Investigate no hot water to unit 16. Restore power to gas solenoid and reset boiling water units
MSA-DCS | WA3644560 | all security systems down, due to lightning | Karnet Prison Farm | GMP-BR-RC | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 23:33:30 | 2020-12-02 16:00:00 | Fail | Commissioned indigo and Gallagher workstations set up indigo database and changed indigo privileges replaced all damaged and broken hardware
MSA-DCS | WA3644561 | unit 4 no power | Karnet Prison Farm | GMP-BR-RC | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 23:59:45 | 2020-09-21 14:00:00 | Fail | Investigate and repair loss of power throughout site due to lightning strike
MSA-DCS | WA3644563 | Fire panel not working. | Karnet Prison Farm | GMP-BR-RC | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 19 Sep 2020 | 2020-09-20 01:20:51 | 2020-11-10 14:50:00 | Fail | All systems back online
MSA-DTAG | WA3644525 | Supreme Court Building-Ground Floor-Two Emergency and one Security door are not secured-Main doors o | Supreme Court-Supreme Court Building-Ground Floor | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 19 Sep 2020 | 2020-09-19 17:49:57 | 2020-09-19 17:00:00 | Pass | Attended site after hours. All external doors not locking. Found controllers offline due to electrical works. Ran temporarypower & locked doors.Job completed.
MSA-DCS | WA3645096 | Po SITE COST Gate in Lenard unit can't be opened. Main pedestrian gate. | Banksia Hill Detention Centre | WSM-BR-SITE | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 20 Sep 2020 | 2020-09-20 11:15:00 | 2020-09-20 09:45:00 | Pass | Attend site after hours. Forcibly open gate and replace mortice lock to restore normal function.
MSA-DCS | WA3645106 | PTZ camera 7 and 9 - no movement- PTZ 8 shows just green and says no video input. | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Sep 2020 | 2020-09-21 08:27:50 | 2020-10-06 13:00:00 | Fail | Following an electrical storm on 20/09 three perimeter PTZ Cameras partially or completely failed. We reset the fibre Modems for two of the three cameras and restored service. In the third camera we found the PoE injector had failed. We replaced the PoE injector. All cameras operating correctly
MSA-DCS | WA3645109 | P0 SITE COST HAKEA-GATEHOUSE-Camera 1 no signal. | Hakea Prison-Main Gatehouse | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Sep 2020 | 2020-09-20 12:48:25 | 2020-09-21 14:15:00 | Fail | Once mains power to UPS circuits was restored, recalled power supplies to original positions. Tested ok.
MSA-DCS | WA3645120 | No power to the CCTV in OPS POST 9 | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-21 11:30:00 | Pass | Reset power and replaced gpo
MSA-DCS | WA3645184 | P0 SITE COST Door in unit 2 won't lock | Melaleuca Prison | WSM-BR-SITE | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 20 Sep 2020 | 2020-09-20 18:18:20 | 2020-09-20 15:45:00 | Pass | Attend site after hours. Gain entry to cell and replace mortice lock to restore normal function.
MSA-DCS | WA3645192 | Karnet Prison Farm-Dairy Cool Room - York Chiller is not working. | Karnet Prison Farm-Dairy Cool Room | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 2 | COMPFIN | 20 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-30 14:00:00 | Fail | essential ref. attended, found controller faulty due to lightning strike . replace controller and left system operational
MSA-DFES | WA3645143 | Osborne Park FS-Main Building-front engine room door not operating automatically | CFRS Osborne Park-Main Building | GMP-BR | Electrical | Materials (EL) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 20 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 11:00:00 | Pass | Technician attended the site of Osborne Park Fire Station to the Engine Room Bi-Fold # W2771 on 21/09/2020. Following a full test and inspection of door components found fault to be engine room door 2 not working in automatic mode. Technician first off checked manual mode, ok, then switched to auto and pressed external timer, also ok. He then programmed his remote to check this function and door opened and closed on timer as should, then went back to check the auto button and door opened and closed on timer. Could not find a fault with door. Full test and inspection of door function completed prior to leaving site.
MSA-DCS | WA3645305 | Potable chlorine plant - lighting strike has burnt the analyser | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | TRILITY Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 07:02:11 | 2020-09-21 15:32:00 | Pass | Attended site to investigate analyser fault. Replaced fuse.Carried out cylinder change at WWTP while onsite.
MSA-DCS | WA3645310 | Waste water treatment plant - dissolved oxygen analyser damaged from lighting strike | Karnet Prison Farm | GMP-BR-RC | Plumbing & Drainage | Water (PD) | MAK Industrial Water Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 07:06:06 | 2020-12-14 13:59:00 | Fail | Service Report WA8281
MSA-DCS | WA3645344 | Level 2 CCTV system Camera is not showing on screen, synchronising of times | East Perth | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 09:27:00 | Pass | Moved camera back on screen and trained site on system
MSA-DCS | WA3645349 | Spirac tank not working due to lightning strike | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 07:24:59 | 2020-09-24 12:30:00 | Fail | Investigate spirac tank not working.Source replacement parts.Replace parts.
MSA-DCS | WA3645413 | Unit 5, D Wing- Window winder has ceased operating | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-25 17:00:00 | 2021-03-02 14:30:00 | Fail | NEW WINDER BOX INSTALLED
MSA-DCS | WA3645415 | Unit 4, Cell B9- Window not staying open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 11:30:00 | Pass | NEW SPIRAL BALANCES & FEET FITTED TO WINDOW
MSA-DCS | WA3645417 | Unit 4, Cell C8- Window not staying open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 10:00:00 | Pass | NEW SPIRAL BALANCES & FEET FITTED TO WINDOW
MSA-DCS | WA3645420 | Unit 3, Cell A11- window does not remain in the open position | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 12:30:00 | Pass | RE NEW SPIRAL BALANCES AND REFIX TOP SASH
MSA-DCS | WA3645426 | Perimeter power module faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Sep 2020 | 2020-09-21 11:59:44 | 2020-09-21 11:45:00 | Pass | Perimeter PM3 and PM4 offline. No power from GPO in Obs post 4. Traced fault to RCD on the UPS in the Training Centre. Restored power with help from DANNY HELWINGS electrical contractor. UPS in training centre and Obs 4 tested ok.
MSA-DCS | WA3645431 | Unit 3, Cell A3- Window does not remain open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 10:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3645435 | Unit 3, Cell C5- Window does not remain open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 13:30:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3645447 | Unit 6 - Cell A4 Bottom bunk is damaged | Casuarina Prison | GMP-BR- HO | Building | General Building (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 11:15:00 | Pass | WELDED SUPPORT BAR TO BED - REPAIRED
MSA-DCS | WA3645466 | Unit 1, Cell B13- Both glass panels of the cell window has been smashed | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 13:00:00 | Pass | NEW SASHES, SPIRAL BALANCE FITTED TO WINDOWS
MSA-DCS | WA3645470 | INF (East), Cell C2- Aluminium door flashing and rubber seal has come loose. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-10-02 10:00:00 | Fail | RENEWED DOOR SEAL TO DOOR FRAME
MSA-DCS | WA3645471 | Unit 4 Dayroom - Window smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 08:11:27 | 2020-09-21 13:45:00 | Pass | RE GLAZE WINDOW
MSA-DCS | WA3645477 | INF (10), Door seal & flashing has perished & come loose making the door difficult to close. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 14:00:00 | Pass | DOOR INSPECTED, NO OBVIOUS SIGN OF DAMAGE - POSSIBLE DOUBLE UP
MSA-DCS | WA3645481 | ODP, Room 1 - Carpet in door way is splitting ar seam (approx 26cm Long) | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2021-03-23 14:00:00 | Fail | DAMAGED SECTION OF CARPET LIFTED & REPLACED WITH NEW CARPET TILES
MSA-DCS | WA3645491 | Unit 3 - Cell A8 window does not remain in the open position | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 11:00:00 | Pass | RE NEW SPIRAL BALANCES AND REFIX FRAME
MSA-DCS | WA3645492 | Unit 4, Cell A11- Pipe underneath sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 13:59:00 | Pass | Nill
MSA-DCS | WA3645496 | Unit 5, Cell A6- toilet is broken in cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-07 15:00:00 | Fail | Nill
MSA-DCS | WA3645499 | Unit 13, Cell D12- Sink & toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-21 14:42:00 | Pass | Nill
MSA-DCS | WA3645525 | Unit 4 Cell C13 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 08:25:43 | 2020-09-21 11:30:00 | Pass | Travel to site checked and found Unit 4 C13 cell call LED stuck on red and not working. Reboot Node and cell call point from controller. Tested cell call working ok after.
MSA-DCS | WA3645530 | Unit 4 Cell C12 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 08:33:03 | 2020-09-21 13:15:00 | Pass | Checked and found Unit 4 C12 cell call LED stuck on red and not working. Reboot Nod and cell call point from controller. Tested cell call working ok after.
MSA-DCS | WA3645534 | Cog Skills- Toilet seat is cracked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 14:47:00 | Pass | Nill
MSA-DCS | WA3645537 | Kitchen - burst hot water pipe on dishwasher | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 08:35:51 | 2020-09-21 15:20:00 | Pass | Replaced half a length off 20mm copper
MSA-DCS | WA3645538 | Unit 1, D Wing Shower- middle one has been leaking & progressively getting worse | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 15:00:00 | Pass | Nill
MSA-DCS | WA3645543 | Unit 4 - Regi Oven not sealing & not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 08:39:46 | 2020-09-24 13:15:00 | Fail | Fitted new door switch, tested ok.
MSA-DCS | WA3645545 | Unit 13, Cell D7 - Shower drain is blocked, water flows back up & starts to flood | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 14:44:00 | Pass | Nill
MSA-DCS | WA3645547 | Unit 14, Cell C15- Leaking tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 08:30:00 | Pass | Nill
MSA-DCS | WA3645552 | Unit 14, Cell D11- Shower drain is clogged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 09:30:00 | Pass | Nill
MSA-DCS | WA3645557 | Unit 13, Day Room- Sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 16:00:00 | Pass | Nill
MSA-DCS | WA3645581 | PTZ 19 - Broken picture | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 08:53:52 | 2020-09-21 12:15:00 | Pass | PTZ19 checked image and slowly deteriorates then comes good. Went to EC cabinet and measured between 21 - 22VAC on PSU for PTZ and 21.4VAC on Fiber modem. Power cycled both units and now measuring 24.1VAC. Tested operation and all is in working order.
MSA-DCS | WA3645598 | Unit 4, Cell D10- Toilet wont flush, button wont push in | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 13:51:00 | Pass | Nill
MSA-DCS | WA3645605 | Unit 1 - Cell B10 Main lock is broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 11:45:00 | Pass | Attended site. Lock repaired by replacing worn component. Normal function restored.
MSA-DCS | WA3645618 | Unit 13, Cell D1- Bottom bed light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 08:30:00 | Pass | Repaired faulty lights in unit 13 D1
MSA-DCS | WA3645620 | Unit 14, Cell D9- Reading light bottom bunk not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 08:30:00 | Pass | Repaired faulty lights in unit 14 D9
MSA-DCS | WA3645629 | House 4 - Please check sewer lines for obstruction pipes keep blocking | Boronia Pre-release-AL10 - Prisoner Accommodation House 4 and 5 | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 11:00:00 | Pass | Complete
MSA-DCS | WA3645635 | unit 4 no tv reception from lightning strike | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-25 11:00:00 | Fail | Attended site, found that Unit 4 A Wing & B VVing have TV reception but all other wings do not. Tested 6 way splitter in Unit 4, found that splitter was giving out poor output signal. Splitter input signal tested ok. Suspect splitter was damaged in lighting. Needs to be replaced. Also noticed that 2 modulators in Unit 3 office appear to be faulty as one unit does not display anything and menu cannot be accessed and the other unit also displays nothing but alarm indicator LED is lit.Replaced 6 way splitter power pass. Tested multiple cells, all TVs working. Job completed
MSA-DCS | WA3645644 | Visits Veranda decking boards are deteriorated and unsafe | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor | GMP-BR- HO | Carpentry | Timber (all types) (CA) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-30 14:00:00 | Fail | WORN DECKING REMOVED & REPLACED
MSA-DCS | WA3645646 | KITCHEN fan controls faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 09:30:00 | Pass | Investigate and replace faulty and damaged fan controllers in kitchen
MSA-DCS | WA3645655 | UNIT 4 CELL A4 toilet cistern not flushing | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2021-06-21 11:24:00 | Fail | job completed under WA4201347
MSA-DCS | WA3645660 | unit 1 cell A 2 window jammed closed wont open | Karnet Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 12:15:00 | Pass | FRAMEWORK REPAIRED AND REGLAZED SLIDING SASH
MSA-DCS | WA3645669 | Lvl 4, ladies toilet - Light out | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-25 09:01:00 | Fail | Replace lamp in ladies toilet.
MSA-DCS | WA3645672 | unit 3 cell C4 light fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 08:30:00 | Pass | Investigate and replace unit 3 cell C4 light fitting
MSA-DCS | WA3645675 | entrance to prison main driveway, leaking main water line | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 09:25:07 | 2020-09-24 11:58:00 | Fail | COMPLETED
MSA-DCS | WA3645687 | Gatehouse- Unable to reset external Perimeter alarm F01 PTX due to it being in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 09:07:37 | 2020-09-21 13:00:00 | Pass | Cleared alarm activation on this Zone and monitored zone for return Alarm. No alarm activations during monitored period. Ran trace on alarm activity, no indication of excessive noise on Zone. Unable to reproduce.
MSA-DCS | WA3645689 | Gatehouse- Unable to reset external Perimeter Zone A04 MW due to it being in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 09:31:08 | 2020-09-21 14:00:00 | Pass | Cleared all alarms from this input, monitored input for further alarm activation. Unable to reproduce Fault. Checked zone prior to departure from the Prison, no alarms present.
MSA-DCS | WA3645690 | Unit 5, Cell D12 - Cell call not working, see notes below | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 09:32:42 | 2020-09-21 16:00:00 | Pass | Replaced failed cell call. See notes for details.
MSA-DCS | WA3645695 | Unit 3, Cell A13- Cell Call alarm, reciever cannot hear the caller when alarm is activated | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 09:34:23 | 2020-09-23 12:00:00 | Fail | Cleared out toothpaste from blocked cell call in unit 3 Cell A13. All cleared out and tested working ok. Job complete
MSA-DCS | WA3645704 | Unit 2, Front door getting stuck | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 09:36:20 | 2020-09-29 16:30:00 | Fail | Cut off existing weld on hinges, install heavy duty hinges, reinstall door closer arm with new slide block, install door stop and fill holes from old hinges.
MSA-DCS | WA3645758 | Cabinet Shop- Leak in the roof between bandsaw and work bench. | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2021-03-17 09:00:00 | Fail | repairs to skylights carried out
MSA-DCS | WA3645820 | Pedestrain, Glass door is not locking | Wooroloo Prison Farm | GMP-BR- HO | Security | Access Control (SE) | ACE LOCK & SAFE | 0 | CLOSE | 21 Sep 2020 | 2020-09-21 14:30:38 | 2020-09-22 14:30:00 | Fail | Made repairs to door frame which was stopping ( hindering ) door closing New door closer needed to replace existing unit which is not functioning properly.Will return ASAP to finish.Returned 22/9 Fitted new door closer - job completed , lock and closer funtioning correctly
MSA-DCS | WA3645836 | Unit 1 CD Wing Office control room network ports are damaged | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 21 Sep 2020 | 2020-09-21 14:36:39 | 2020-09-21 14:30:00 | Pass | Repaired network points
MSA-DCS | WA3645878 | Main Prison- Camera 21 PTZ will not tilt | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 11:03:35 | 2020-09-22 08:15:00 | Pass | On arrival tested camera 21 (located on pole in front of Gatehouse). Operated this camera thru all positions. Camera PTZ (Pan/Tilt/Zoom) functions all working correctly. No fault found.
MSA-DCS | WA3645880 | Unit 10 No hot water to showers entire unit | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 11:05:29 | 2020-09-21 13:50:00 | Pass | Checked water supply and for any signs off burst pipes or blockages narrowed it down to no power supply referee to dean
MSA-DCS | WA3645907 | zone 1 control roller dor not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 11:21:17 | 2020-09-21 12:30:00 | Pass | Checked zone 1 roller door
MSA-DCS | WA3645915 | Amenities - several broken sprinklers and two leaking solinoids | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 10:15:00 | Pass | completed as per attached supporting documents
MSA-DCS | WA3645924 | Unit 2, Cell C1- Window spring struts broken off | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 09:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3645926 | unit 2 A-B 1-2 Vesda has a Stuck Valve | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-10-08 18:57:00 | Fail | completed check of Vesda - BRAF declined unit not replaced21/09/20 EIUnit 2Wing AB Cell 1/2 VESDA reporting a fault which is identified as pipe 2 stuck open fault.Test VESDA operation OK however the fault will not reset even when performing a valve scan test.Recommend replacing the VESDA for new. Cells currently have smoke detection coverage however unit will remain with faults until replaced.
MSA-DCS | WA3645934 | Unit 2 A-B 3-4 PSU Damaged | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 11:31:43 | 2020-09-21 12:08:00 | Pass | PSU faulty - replacement required
MSA-DCS | WA3645943 | Unit 2 A-B 11-12 PSU Damaged | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 11:37:38 | 2020-09-21 12:02:00 | Pass | PSU faulty - requires replacement
MSA-DCS | WA3645951 | Unit 5, A wing cleaning cupboard sink is blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 13:53:00 | Pass | Nill
MSA-DCS | WA3645979 | Dairy kitchen- Hot water Urn is not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 11:52:00 | Pass | Replaced thermostat and overload kitAll okay
MSA-DCS | WA3646076 | Unit 8 control room faulty fluro light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-05 13:00:00 | Fail | Replaced lights
MSA-DCS | WA3646117 | U9 Top end of C Wing window & frame needs repair & refixing | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-25 15:00:00 | Fail | Resecured window and frame work
MSA-DCS | WA3646133 | Front gate sally port - Broken GPO | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 14:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3646141 | Unit 3, Cell C14- Top window cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-10-05 14:30:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA3646148 | Unit 1, Cell C11- External light needs fixing | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 12:30:00 | Pass | Repaired cell light
MSA-DCS | WA3646154 | Unit 4, Cell A7- Water coming up from drain under toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-30 13:30:00 | Fail | Drain rod used to unblock floor waste
MSA-DCS | WA3646158 | Unit 1, Cell C9- Smoke detector faulty | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 11:08:00 | Pass | replaced vesda sampling point as damaged
MSA-DCS | WA3646181 | laundry- Number 5 washing machine showing fault “low Oil” | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 13:48:42 | 2020-09-22 14:49:00 | Fail | W/M 5 Low oil error - Inspect and test washing machine, trace fault to low oil.Supply and fit 1L of lube oilAssemble and test washing machine, washing machine tests ok.
MSA-DCS | WA3646184 | unit 1 C9 Tiles coming off wall needs repairing | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2021-02-24 14:10:00 | Fail | INSPECTIONS ONLY - PRISON ADVISED ALL TILES ON SPLASH BACK IN CELLS ARE NO LONGER ALLOWED - ALL TILES ALREADY REMOVED AND PRISON DIDNT WANT ANY MORE LAYED
MSA-DCS | WA3646203 | Gymnasium west Fire hydrant 87/88 near western gym leaking needs urgent attention | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 14:14:10 | 2020-10-16 16:17:00 | Fail | Arrived on site and inspected leaking fire hydrantFire hydrant is unserviceable and will require replacementSpoke with the Industries manager who asked that we book in a time for the replacement as there is no free escorts available todayAttended site 16/10/2020 to carry out hydrant works as requested. Isolated and drained hydrant system. Overhauled hydrant located near gym. Refilled and tested system. Repaired leaking packing gland on the domestic fed wash down hose reel.
MSA-DCS | WA3646208 | Unit 2, End of B Wing- Light not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 09:30:00 | Pass | Repaired light
MSA-DCS | WA3646212 | Unit 2,Control Pod First Office L/H Side -Faulty Light Switch makes a crackling noise when turned on | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 14:23:47 | 2020-09-22 08:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3646215 | Unit 1 A14 light not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 14:21:58 | 2020-09-22 15:00:00 | Fail | Repaired cell light
MSA-DCS | WA3646228 | C-Wing Grill Lock jamming when opening and closing | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 14:30:54 | 2020-09-22 10:15:00 | Pass | Attend site. Service main grill lock and restore normal function. Tested ok with DOJ Staff.
MSA-DCS | WA3646244 | Unit 2, house 2, Cell 3- cell call hard to hear audible issues | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 12:30:00 | Pass | Tested cell call,Unable to clearly hear officers.Removed and tested new cell call, loud and clear.Modified to fit and re-tested, loud and clear communication Part used from PFM stock 1x Cellguard CI-CC
MSA-DCS | WA3646249 | Kitchen, sally port doors reed magnet fallen off gate | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 14:45:00 | Pass | Located 4x Sentrol 2202A onsiteInstalled in Kitchen and confirmed gates working.4x Sentrol 2202A used from PFM stock
MSA-DCS | WA3646322 | Check MATV functionally | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 11:30:00 | Pass | Surveyed & identified MAW equipment across site. Identified Network Topology.Job completed.
MSA-DCS | WA3646333 | SMS controller off line - no communication with camera or cell calls. | West Kimberley Regional Prison-External Area | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 18:00:00 | Pass | Checked UPS and confirmed batteries are charging,Power cycled controller and confirmed onlineTested all inputs amd outputs.Tested cell call aand confirmed all operational
MSA-DCS | WA3646340 | East inner sally port door will not open or close- failing to response | Casuarina Prison | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 19:06:03 | 2020-09-22 12:30:00 | Pass | 22/09/20Hire Scissor Lift on trailer.Collect scissor lift. Inspect doors.No fault found.Take photos for possible replacement controller.Off hire scissor lift.
MSA-DCS | WA3646347 | Unable to control main gate, sally port etc from Gallagher control system | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Sep 2020 | 2020-09-22 01:26:08 | 2020-09-21 23:30:00 | Pass | Afterhours callout. Travelled to site and found master Gallagher PC had lost its network connection. Reset main server and repowered PC and monitor. All powered up ok. Reloaded Gallagher and site plan loadouts all working ok. Job complete
MSA-DCS | WA3646508 | Unit 16, Water not heating up - see further notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 13:49:00 | Pass | The boys who did the cut in on 17/18th of September, did purge the line and ensured gas was available
MSA-DFES | WA3645666 | Door # 6 pin has fallen and roller door has come crashing down | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 21 Sep 2020 | 2020-09-21 13:15:47 | 2020-09-21 09:45:00 | Pass | Technician attended the site of Welshpool Fire Station to the Engine Room Door No. W23709 on 21/09/2020. Following a full test and inspection of door components found fault to be door in closed position with damaged top panel and track wheels out of track. Upon further inspection found various other issues with door such as motor shuttle assembly faulty and worn, door heavy due to incorrect springs. Made door safe, isolated, tagged out and quote for replacement. Quote was has been declined. BRAF declined, Door has been made safe and isolated. Closed off.
MSA-DFES | WA3645673 | Door # 1 has no power - not operating | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 21 Sep 2020 | 2020-09-21 13:23:59 | 2020-09-21 12:45:00 | Pass | Technician attended the site of Welshpool Fire Station to the Engine room rear panel lift door on 21/09/2020. Following a full test and inspection of door components found fault to be photo electric cell out of alignment and close limit running on too far. Technician has adjusted and secured photo electric cell, adjusted limit and test door multiple times. All okay. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3645727 | Lvl 1, Male bathroom - Right hand basin not draining water. | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 11:33:00 | Pass | Unblocking the basin
MSA-DFES | WA3645763 | Foyer key box is hot please investigate | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 10:45:00 | Pass | Removed key lock box so Sontech could access their key lock box to repair faulty key mechanism
MSA-DFES | WA3645777 | External garden reticulation not working or damaged. Check all retic | DFES Regional Office - Belmont | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2021-01-30 16:00:00 | Fail | Works finally completed on 30/01/21
MSA-DFES | WA3645809 | Gym- Large glass sliding door difficult to open and close, see below notes | CFRS Joondalup | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 14:50:00 | Pass | Removed door and changed wheels x 4 Fitted rattle blocks and straighten and adjusted locks - door now in working good order.
MSA-DFES | WA3646059 | ground nth east entry need to be changed handle lock mec keeps being left unlocked - see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-22 09:00:00 | Pass | Change function of lock and replace internal handle to East side entry door
MSA-DFES | WA3646128 | L1 FF's end dorm 1st & 3rd bed GPO's behind beds need to be removed 200mm to the left - see notes | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 13:15:00 | Pass | Locate faulty GPO’s. Found two GPO’s behind the bed that can not be used. Discussed with the station officer about new locations. Investigate how easy or hard it will be to move them. It was not to difficult to do the work. Station captain was happy for us the move the GPOs today. Steve from PrOgramme was also on site he advised he was happy for us to do the work. Move the GPOs to new locations and test. Advised staff of work completed.
MSA-DTAG | WA3645590 | 1878 ground office No power to part of office - see notes | Armadale Courthouse | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 15:30:00 | Pass | Work Complete.
MSA-DTAG | WA3645891 | 1903 basement server room UPS in Vaults server room has failed | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Elec Power Technologies | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 09:30:00 | Pass | Job completed - Emergency site attendance to investigate fault on attached UPS.
MSA-DTAG | WA3646007 | L6 Prisoners Review Board Male Staff Toilet cracked and leaks some water when flushed | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-11-24 11:00:00 | Fail | Complete
MSA-DTWD | WA3645212 | South Metro TAFE-Munster Campus: Room TM169 - One of the windows has been smashed | Munster Campus (ACEPT) | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 21 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-29 10:00:00 | Fail | ATTENDED SITE AFTER HOURSTEMP GLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-691 X 10671.5 L/M OF RUBBER REPLACED PLUS .3 SQM SAFETY FILM AND 4 RIVETSRETURNED LATER DATE TO REGLAZE6.38 BRONZE LAMINATED SAFETY GLASS1-691 X 1067PLUS NEW ANGLE 1-1200 mm AND SILICONE AND 8 RIVETS
MSA-DTWD | WA3645333 | Gate on the oval, locking mechanism has been vandalised | Munster Campus (ACEPT) | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 21 Sep 2020 | 2020-09-21 17:00:00 | 2020-09-21 16:15:00 | Pass | Welded new shoot bolt onto gate
MSA-DTWD | WA3645588 | Level 1 - B013 & B162 Repair exposed wiring at old telephone points | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 13:07:00 | Pass | Covered holes in wall next to phone ports.job completed
MSA-DTWD | WA3645624 | E block EG16 male toilet Middle cubicle toilet leaking onto floor | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-21 16:56:00 | Pass | Fixed leaking toilet
MSA-DTWD | WA3645702 | P block ground P007 Power point with faulty switch | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 11:30:00 | Pass | Replaced faulty gpo in P007
MSA-DTWD | WA3645711 | Plant room number of faulty lights | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-22 15:05:00 | Pass | Replaced multiple lamps/ballasts as per list supplied by site.job completed
MSA-DTWD | WA3645739 | lift 4 phone error - please see below notes | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-21 15:10:00 | Pass | Temp repairs made - to be closed out at $0
MSA-DTWD | WA3645819 | A block AF20 courtyard side Electreonic keypad not unlocking door latch - see notes | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-06 10:00:00 | Fail | 21/09/2020, 1445-1515Code appears to work ok on keypad, door not unlocking, possible faulty lock or cable.22/09/2020, 1215-1245Door was working ok. No faults found.23/09/2020, 1315-1345Was looking at wrong door.The Rosslare keypad had defaulted itself.Re programmed user codeClient would like to replace the keypad as it could happen again and the screw to open it has been rusted away.06/10/2020, 915-1000Replaced Rosslare keypadProgrammed and tested ok.
MSA-DTWD | WA3645827 | block 7 ground floor kitchen bain marie unit not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 14:45:00 | Pass | Attended site and signed in. Located b7 and checked Bain Marie. Found burnt cable but no other fault. Replaced cable and retested. All now working. Informed staff of job completion
MSA-DTWD | WA3645898 | U block ground U011 repair to electrical cord | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-23 15:23:00 | Pass | Repalced faulty cord and lead . Repaired faulty lights also in U block .job completed
MSA-DTWD | WA3645962 | ground whole of campus multiple broken sprinkler heads | Joondalup Kendrew Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 14:00:00 | Pass | 22 and 24//2020 - Run through irrigation system replace damaged sprinklers and broken pipes.
MSA-DTWD | WA3645987 | J Block west, external wall North side- 1 x Running tap cannot be turned off | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 15:00:00 | Pass | Replaced 2x taps
MSA-DTWD | WA3646020 | G block room G23A wet carpet from a roof leak - needs blowers to dry carpet | Rockingham Campus | GMP-BR | Cleaning | Cleaning (CL) | Workzone Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-22 13:30:00 | Pass | Visit site, leave carpet dryer overnight to dry out carpet
MSA-DTWD | WA3646094 | Whole Building - Various lights out throughout building | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 14:45:00 | Pass | Job complete
MSA-DTWD | WA3646098 | Church toilet- toilet is constantly running | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-25 18:23:00 | Fail | Complete
MSA-DTWD | WA3646116 | E Block, FT15 Plantroom- GPO in plant room not working | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 10:45:00 | Pass | Arrived on site , signed in , contacted and waited for fm to come to office , located gpo, completed jsa, isolated power, removed old gpo, replaced with new , tested , all good , cleaned up work area, completed paperwork, signed out **job complete**
MSA-DTWD | WA3646155 | L1 print shop Repair broken glass in UV Machine | Perth Campus B4 | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-10-08 13:35:00 | Fail | ATTENDED SITEREPLACED GLASS TO UV MACHINE8MM CLEAR TOUGHENED SAFETY GLASS1-1055 X 744POLISHED ALL EDGES
MSA-DTWD | WA3646170 | C block Cafeteria Coolroom – Faulty wiring to compressor - see notes | Bentley Campus | GMP-BR | Equipment Hire | Compressors, Generators (EH) | Equans Mechanical Services Australia | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-05 16:30:00 | Fail | Works completed by contractor
MSA-DTWD | WA3646255 | G23A Roof Leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-10-19 13:00:00 | Fail | Removed rusty box gutter and replaced with new and stop ends
MSA-DTWD | WA3646271 | E block ground E617 Male toilet Urinal not draining | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 14:00:00 | Pass | Cleared blockage
MSA-DTWD | WA3646316 | Lvl 1, Room B154- Broken door handle | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 21 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 12:15:00 | Pass | 24/09/20: need to return with parts29/09/20: Replace broken handles to room B154
MSA-DTWD | WA3646329 | B block L1 chiller plant room Investigate fault on Condensed Water Pump 1 & 2 via BMS - see notes | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 2 | COMPFIN | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 00:00:00 | Pass | completed - Work order to be closed out at $0 cost
MSA-MRWA | WA3645715 | Lvl 8, Room 834- Light switch mech worn please replace. | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 09:00:00 | Pass | Arrived on site, signed in, spoke to pfm,located switch that needed replacing , completed jsa, isolated circuit, replaced mech, reenergised circuit , tested switch, switch is working as intended, cleaned up work area , completed paperwork ,signed out **job complete**
MSA-MRWA | WA3646266 | Main entry gate inoperative please rectify- see notes below | Materials Engineering Branch-External Area-Ground Floor-Auto Gate Entrance | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-21 16:37:00 | Pass | Note IP number 1078236, arrived onsite and found unit working then failed after several tests , traced problem to faulty UPS, rewired unit to bypass UPS till new one is fitted, require a 5000VA type.
MSA-DCA | WA3646828 | Replacement of relay as burnt out. | State Library of WA-Main Building-Level 3-10 Degree Stacks Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 12:00:00 | Pass | Low Humidity in 10°c Stack on L3. Control delay enabling start/stop burnt. Contacts sticking. Arranged replacement parts and a spare to be left on site. Replaced faulty relay with new relay and left one new relay on site. Checked cycling and monitored conditions.
MSA-DCA | WA3646839 | blocked urinal | State Library of WA-Main Building-Ground Floor-Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 10:15:00 | Pass | Check all male staff and public’s toilets all working good no blockage found Advised David about the issues
MSA-DCA | WA3646841 | Leaking tap | State Library of WA-Main Building-Ground Floor-Male Toilet | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 11:51:00 | Pass | Replaced push button tap 15 sec tap and mini stop to basin RHS
MSA-DCA | WA3647018 | Leaking valve on hot water pump in CRC plantroom | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor-Plant Room | GMP-BR | Mechanical Services | Pumps (MS) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-30 09:00:00 | Fail | Completed repair works to leaking defective ball valve. Please refer to PFM work logs for attendance and completion dates and in depth work description. Works completed.
MSA-DCS | WA3646480 | Unit 5, house 7 - front door electronic lock faulty 9 can open with key,unable to open from control) | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 07:31:14 | 2020-09-22 15:16:00 | Pass | Lock repaired.
MSA-DCS | WA3646488 | control - Camera 62 & 17 have no feed | Hakea Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 07:35:27 | 2020-12-18 16:00:00 | Fail | Replaced faulty analog internal perimeter camera 17 with new Axis IP camera. Test and check DVM functions, all ok. Job completed.
MSA-DCS | WA3646493 | Reception, Resident toilet - toilet not flushing | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 07:39:39 | 2020-09-22 16:49:00 | Pass | Repaired x3 leaking toilets in reception replacing x3 inlet valves and x3 outlet washers
MSA-DCS | WA3646496 | Hotham, B6 - Toilet continually running | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 18:00:00 | Pass | Replaced outlet washer and inlet valve
MSA-DCS | WA3646504 | CCU(11), D wing, Cell D4 - camera broken by prisoner overnight and requires urgent replacement | Casuarina Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 07:46:34 | 2020-10-29 16:30:00 | Fail | Damaged camera removed, new CAT6 cable installed from cctv Equipment Rack to cell location. New wall penetration installed to get cable into cell. Cable terminated both ends and tested. New corner mount Axis camerainstalled. DCS staff determined vision had too many blind spots. Arranged for Modello to build out cabinet to make flush with TV Cabinet below. Camera reinstalled, staff advised view satisfactory.
MSA-DCS | WA3646512 | Zone 11 - sensor cover has fallen off. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-22 13:45:00 | Pass | Attended site checked and found Zone 11 PE BEAM top section cover has been blown off. Managed put cover back on and secure it. Tested all ok after work.
MSA-DCS | WA3646514 | Unit 6, A Wing Cleaning Store- Double socket is loose on wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 08:01:52 | 2020-09-22 15:00:00 | Pass | Replaced damaged gpo in unit 6 cleaning store
MSA-DCS | WA3646520 | MDAS offline Transponder TR13 Unit 2 Office | West Kimberley Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 08:07:19 | 2020-09-23 15:30:00 | Fail | Checked transponder and confirmed power, Unable to ping Moxa. Power cycled, still unable to connect to moxa.Replaced with PFM site stock. Programmed and installed, transponder communication to server.Site stock was replaced with new part
MSA-DCS | WA3646521 | Perimeter Receiver (1.4) Perimeter Z15 offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 08:08:28 | 2020-09-24 10:00:00 | Fail | Located damaged enclosure and receiver.Replaced and tested.Parts used from PFM stock 1x Bosch outdoor enclosure1x Bosch receiver
MSA-DCS | WA3646524 | Hotham, Laundry- wash machine not spinning - belts slipping | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-27 09:15:00 | Fail | AMS697721 WA3646524 - Wandoo Rehab W/M not spinning.23/9 - Travelled to site - could not get access due to a broken salyport door.27/9 - Returned and picked up washing machine in CLS workshop.13/10 - Traced fault to a sock stuck between the drum and outer shell, removed sock supplied and fitted new belt. Assembled and tested. Tests ok.27/10 - Washing machine returned to stores.
MSA-DCS | WA3646555 | Unit 10- Electrical fault to Hot Water unit no hot water to all showers in unit | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 08:34:55 | 2020-09-22 11:00:00 | Pass | Hwu not working.
MSA-DCS | WA3646575 | Unit 4, PTZ camera 68 - not moving, | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-25 16:15:00 | Pass | Tested from Gatehouse Equipment room. Camera has good picture, no PTZ function. Attended camera EC (7) and power reset the S732DVT-EST fibre modem. Contacted Gate Control to test, no change. Reset the PTZ Camera and again requested Gate Control Test camera, still no PTZ function. Connected test monitor to camera data feed (Address =1) and tested, confirmed PTZ operating correctly. Returned to Gate house equipment room, connected test monitor to fibre modem, unable to move camera. Power reset fibre modem, camera now operating with all PTZ functions.
MSA-DCS | WA3646596 | kitchen 3 teir pizza oven door hinges faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-02 17:00:00 | Fail | 23/09/2020Arrive at site to check pizza oven door hinges faulty. Found missing circlips and washers so hinge brackets falling off occasionally. Recommend to replace all to new. Will need to clean up hinge pins where circlips sit on return with some emery cloth.Parts required24 x washers 24 x circlips 1 x emery cloth02/10/2020Called as requested to to fit parts required fitted tested all working correctly now.
MSA-DCS | WA3646680 | Mulcher shed- Mulcher not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Gardening / Landscaping Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-22 14:00:00 | Pass | Mulcher shed muncher not working. Remove muncher from shed to workshop. Dismantle completely. Check & run motor, refit control box. Check, all parts need replacing. Agent reports no parts available. Report to staff.
MSA-DCS | WA3646681 | gate house zone 10 MW tamper alarm - seme on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-22 11:45:00 | Pass | Zone 10 Microwave tamper alarm activating intermittently. Checked on field found tamper switch activating and reset alarm correctly. Suspected the lever of switch not set correctly. Adjusted angle of lever. Checked it ok after work.
MSA-DCS | WA3646722 | Unit 7, H Wing Day Room- Water taps leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-30 11:42:00 | Fail | Turned off water replacing hot/cold taps
MSA-DCS | WA3646744 | Unit 7, Vents in S wing not extracting no power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-11-26 14:00:00 | Fail | Repaired fan
MSA-DCS | WA3646745 | Unit 7 control room Water leaking behind fridge, see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-30 12:36:00 | Fail | Tighten and rethreaded leaking union on uv light
MSA-DCS | WA3646748 | flick mixer tap leaking | Boronia Pre-release-AK19 - Library, Education Personal Development-Ground Floor-Community Room 4 | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-29 09:00:00 | Pass | Complete
MSA-DCS | WA3646798 | unit Cell B14 water coming up through floor and wall damaged pipe | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-06 09:30:00 | Fail | COMPLETED
MSA-DCS | WA3646804 | unit 4 cell L2 shower leaking may need washer or spindle | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-05 11:00:00 | Fail | COMPLETED
MSA-DCS | WA3646808 | assessmnets air con is smelling quite bad | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-25 10:30:00 | Pass | Arrived to site and met with Maintenance for escort.Accessed Assessments block and looked for smelly A/C.Could not pin point location so I chemically treated 3 units in the area.Applied chemical spray and awaited.Started fans.Allowed rooms to vent the cleaning smell.Systems working okay.
MSA-DCS | WA3646809 | unit 2 B wing first shower in right hand side 600 ml light fitting broken | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-06 13:00:00 | Fail | Replaced internal wiring of light with LEDs
MSA-DCS | WA3646897 | unit 5 A wing water ingress from cleaners room - see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-23 00:00:00 | Pass | Nill
MSA-DCS | WA3646931 | MPU (8)- 2 weather strips (Fly Flaps) on the doors damaged | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-12-02 14:35:00 | Fail | ADVISED TO CLOSE THIS JOB OFF WITH COSTS TO DATE BY JOELIAN MCDONNELL AT CASUARINA. NEW WORK ORDER ISSUED ON WA3826275
MSA-DCS | WA3646980 | Unit 9 control room light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-01 15:00:00 | Fail | Replaced broken light
MSA-DCS | WA3647077 | Kitchen- Bakers oven is not heating up & is tripping out | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 13:56:39 | 2020-09-23 12:15:00 | Pass | completed 23/9/20
MSA-DCS | WA3647084 | Unit 10, A Wing Grille- key sometimes hard to turn in lock, feels like getting stuck | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 14:45:00 | Pass | Attended site. Serviced lock and restored to normal function
MSA-DCS | WA3647096 | Outpatients Area, Western Courtyard Gate hinge has dropped, gate will not double lock. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-11-10 09:00:00 | Fail | Service lock, lock requires rebuild.Remove lock, secure gate with chain and padlock, rebuild lock in workshop, install rebuilt lock.
MSA-DCS | WA3647119 | Farm RCD will not reset to farm soak pump | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-01 13:30:00 | Fail | Investigate rcd at farm soak not resetting.Source parts.Replace faulty components.
MSA-DCS | WA3647135 | Unit 13 - Office PTZ and monitors not working due to power outage | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 10:15:00 | Pass | Travelled to site and reset indigo PC for unit 13 control. Reloaded camera layouts on Indigo PC. All loaded and working ok. Job complete
MSA-DCS | WA3647150 | Unit 2, Cell D05- Light damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-24 10:30:00 | Pass | Repaired light
MSA-DCS | WA3647152 | Unit 5, A Wing- Window leaking into day room, where the bins are stored | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-11-26 10:00:00 | Fail | bottom of windows re sealed and frames repaired
MSA-DCS | WA3647155 | Security + HR Faulty controller for Air Cond. system | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-01 10:30:00 | Fail | Checked over aircond found remote for split a/c faulty and not turning unit on,replaced remote with universal remote,programme remote and test operation all running ok at present.
MSA-DCS | WA3647192 | CCU pod cell camera's have gone down | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Sep 2020 | 2020-09-22 19:32:07 | 2020-09-22 17:07:00 | Pass | Investigated fault with CCU computer, found no power at UPS power outlet on wall. Corrected supply issue and repaired workstation software fault after unexpected power outage.Tested OK.Job Complete
MSA-DCS | WA3647242 | Control to emergency access road is inoperable - near gates 18 and 26. | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Sep 2020 | 2020-09-23 19:09:21 | 2020-09-22 22:00:00 | Pass | Contacted site and found that issue is related to the new Gates which related back to Honeywell. Relayed information to direct manager which was passed onto Grant at PFM. Requires Honeywell attendance
MSA-DFES | WA3647179 | DO Office Ensuite/Toilet- Toilet bowl is leaking effluent on to the tiled floor | CFRS Perth | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 12:00:00 | Pass | Replace pan rubber due to the old one was split and leaking
MSA-DTAG | WA3646572 | Lvl 10, Front Counter - 1x light in the marriage service hallway flickering | Westralia Square | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 13:00:00 | Pass | Job complete
MSA-DTAG | WA3646741 | Lower ground level - Message ‘Out of Order’ displayed when button is pressed | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2021-09-23 12:50:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA3646965 | Basement, underground car park - Isolate FIP from 16.30pm Tuesday 22 Sept until 23.00pm Tuesday Sept | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 14:30:00 | Pass | Isolate 22/09/20 at 16:30De-isolate 22/09/20 at 20:30Isolate 23/09/20 at 06:00De-isolate 23/09/20 at 14:00
MSA-DTAG | WA3647121 | 1903 ground ct 1 corridor 3 Automated roller blinds require new batteries and to be re-programmed | Supreme Court | GMP-BR-HO | Building | Windows (BU) | NEYLOR | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-27 11:36:00 | Fail | completed & Invoiced
MSA-DTWD | WA3646439 | Lift L1-L3 - - Lift broken down | Perth Campus B6 | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 22 Sep 2020 | 2020-09-22 17:00:00 | 2020-09-22 10:51:00 | Pass | RUNNING ON ARRIVAL. MINOR ISSUES RECORDED IN FAULT LOGS. NO SIGNATURE AVAILABLE.EQUIPMENT RUNNING, BACK TO NORMAL OPERATION
MSA-DTWD | WA3646564 | Block 6, Wash Room Painting & Decorating- Light fitting is broken & not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-23 13:15:00 | Pass | Arrived on site, signed in, spoke with fm about job, located lighting,completed jsa, isolated lighting, removed old light, replaced with new light, reenergised circuit,tested light and was working as intended, cleaned up work area,completed paperwork ***job complete ***
MSA-DTWD | WA3646568 | Block 7, Mens Toilet - Light fitting is broken & not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-23 12:15:00 | Pass | Arrived on site, signed in, spoke with fm about job, located lighting,completed jsa, isolated lighting, removed old light, replaced with new light, reenergised circuit,tested light and was working as intended, cleaned up work area,completed paperwork ***job complete ***
MSA-DTWD | WA3646590 | Block 7, Mezzanine Floor- Lights not working in booths. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-24 13:30:00 | Pass | Attended site , signed in, located lighting , completed jsa, isolated lighting circuit, removed lighting from the bottom of the duct , mounted lighting to the side of ducting , replaced ducting covers that were missing ,re energised circuit, lighting working as intended , site happy , cleaned up work area, completed paperwork, signed out *** job completed ***
MSA-DTWD | WA3646610 | T block - door wont unlock | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 0 | CLOSE | 22 Sep 2020 | 2020-09-22 13:10:41 | 2020-09-22 10:55:00 | Pass | Job completed - replaced Legge mortice lock body
MSA-DTWD | WA3646633 | B Block, Room B16- Roof leak, classroom on south window under box gutter | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 13:15:00 | Pass | Sealed suspected leak with silicone. Dennis on site confirmed leak resolved.
MSA-DTWD | WA3646641 | E block, Bistro Kitchen - combi Oven handle has fallen off | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 15:45:00 | Pass | COMPLETED
MSA-DTWD | WA3646668 | ramp east side of B Block - 100mm Retic pipe leaking beside | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 10:15:00 | Pass | Excavate to expose leak in the mainline, carry out repairs.
MSA-DTWD | WA3646682 | L1, Wood workshop- Dust extractor not extracting dust properly | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2021-01-29 08:30:00 | Fail | BRAF works have been completed on equipment as per approved lines by campus facilities manager. Equipment has been restored to normal operation.
MSA-DTWD | WA3646732 | F Block, FG02 Male Toilets- Far right hand cubicle cistern constantly leaking | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 17:34:00 | Pass | Replace leaking and Bowed cistern
MSA-DTWD | WA3646806 | Tower block, ground floor- stairwell door lock is faulty | West One Services | GMP-BR | Security | Locksmith (SE) | DIAMOND LOCK AND KEY | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 10:30:00 | Pass | repairs to lock
MSA-DTWD | WA3646871 | unit 7 ground male toilet Urinal cistern continuously running | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-22 13:15:00 | Pass | Partially blocked outlet and adjusted water flow on flauh
MSA-DTWD | WA3646880 | Turf Area - Spotlights not working | Murdoch Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-25 14:30:00 | Pass | Arrived on site, signed in, spoke to pfm on site about the job,located lighting, completed jsa,testied lighting to identify the problem, isolated lighting, dropped swinging pole down to work on lights , replaced 1x lamp in 1 light and removed 2 lights , replaced with led flood lights, put pole back in upright position, secured pole , re energised circuit, tested lighting, working as intended , cleaned up work area, completed paperwork, signed out ***job completed ***
MSA-DTWD | WA3646925 | admin kitchen blocked sink drains slowly - AHS on site | West One Services | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-25 16:30:00 | Pass | Complete
MSA-DTWD | WA3647035 | B Block, Driveway near Store, Metal Gatic cover is damaged | Leederville Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-09 08:30:00 | Fail | Re weld grate
MSA-DTWD | WA3647053 | A Block, A001.2 Reception (Main swing doors)- Swing door header keeps dislodging | Balga Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-09 12:00:00 | Fail | Fitted off new angles to top of door and and adjusted both doors Job complte
MSA-DTWD | WA3647056 | F Block, FG32 Evap Unit Room- Top of door is getting jammed | Carlisle Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 15:45:00 | Pass | Lifted sagging frame with acroprop and fitted steel post to the back of the frame to hold it in position and provide support. Doors now operating freely
MSA-DTWD | WA3647126 | U Block, Room U006 & U019- Multiple fluro lights not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-29 14:30:00 | Pass | Job complete
MSA-DTWD | WA3647156 | Chiller Plant Room- Rectify Collapsed Condensed water pipe and test Condensed water pumps | East Perth Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-23 13:00:00 | Pass | Works completed by Carrier
MSA-DTWD | WA3647161 | A Block, Supply Temp Aircon units due to critical damage to Chiller Plant | East Perth Campus | WSM-BR-RC | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2020-10-06 11:15:00 | Fail | Removed portable units. Works completed by Carrier
MSA-DTWD | WA3647172 | Water leak on campus can not detect were it is coming from | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-03 18:17:00 | Fail | located and repaired water leak, lodged leak allowance claim with water corp
MSA-MRWA | WA3646967 | cleaners cabinet Investigate source of smell and remediate if able. | Traffic Operations Centre-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 12:23:00 | Pass | Checked all amenities in the area no smells found.
MSA-DCS | WA3647589 | Drug Detection unit, office complex - electrical fault with the lights the, keep tripping | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 07:50:46 | 2020-09-23 13:00:00 | Pass | Repaired lights
MSA-DCS | WA3647658 | Administration - Lunch Room Both taps are leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 14:00:00 | Pass | Nill
MSA-DCS | WA3647674 | Social Visits Centre, Family room - glass door aluminium strip has detached - | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 09:30:11 | 2020-09-24 14:30:00 | Fail | Replaced damaged door seal
MSA-DCS | WA3647689 | U9, Day rooms - faulty ceiling fan in day room | Hakea Prison | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-14 15:00:00 | Fail | Repaired ceiling fans
MSA-DCS | WA3647722 | Unit 2 - B & D RCD keeps tripping - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-12 15:00:00 | Fail | Replaced damaged urn in unit 2 dayroom
MSA-DCS | WA3647734 | Unit 7, A Wing, Store room - lights are not working, see notes below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-25 11:30:00 | Pass | Repaired faulty lights in scu store rooms
MSA-DCS | WA3647737 | Unit 7, A Wing, laundry- lights are not working, see notes below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-25 10:00:00 | Pass | Repaired faulty lights in scu A wing laundry
MSA-DCS | WA3647747 | Unit 1, POD 3, kitchen - Lights and fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 10:33:53 | 2020-09-23 16:30:00 | Pass | Replaced ballast, tubes and exhaust fan
MSA-DCS | WA3647749 | Medical centre - TV signal not working | Wooroloo Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 10:35:25 | 2020-09-24 11:30:00 | Fail | Job completed - Attended site. Tested all TV points, no signal. Traced cables in roof back to cupboard in Reception. Amplifier in cabinetwas offline. Tested power output of double GPO, no output. Found circuit breaker had tripped due to lightning. Resetbreaker, retuned TVs. All working ok.
MSA-DCS | WA3647757 | Outside basketball court- Light at northern end broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 13:00:00 | Pass | Replace faulty flood at basketball courts with new led 150w flood light
MSA-DCS | WA3647798 | Maintenance, Office- Window will not stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 09:00:00 | Pass | NEW SPIRAL BALANCES FITTED TO WINDOW
MSA-DCS | WA3647813 | entry control pod, multiple alarm faults paperwork will be left at entry pod | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 11:10:55 | 2020-09-23 14:00:00 | Pass | Cleared all multiple alarm faults reprogrammed duress fault, reset Gallagher controller for perimeter alarms. All alarms cleared and rectified as per job notes in Bandyup control pod
MSA-DCS | WA3647867 | Social visits - Roof Leaking water onto PDA repeater box on the left side wall | Melaleuca Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2021-02-15 12:00:00 | Fail | no charges - closed off compfin.
MSA-DCS | WA3647886 | unit 2 control room Air condition not blowing cold air | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 12:06:23 | 2020-09-24 13:45:00 | Fail | Fault already known about. Parts ordered and due to arrive 25/09. Closing job
MSA-DCS | WA3647973 | Industries Administration - BGA Fire alarm going off, Maintenance can not reset, only isolate alarm. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 13:06:19 | 2020-09-24 09:30:00 | Pass | 24/09/20 EIAttended site to investigate fire alarm MCP that won’t reset in the industries area, Zone 20 on Void SFIP.Liaised with industries Maintence & identified that the old brickworks MCP area has been recently refurbished and is now the new Kitchen area.The old MCP has been removed by others & the old cabling & MCP are presumed redundant and in the roof space, location unknown.Disconnected zone 20 in SFIP & made safe redundant cable, placed information tag on redundant cable in SFIP.It is noted that during the investigation the new kitchen area is still labelled zone wise on the SFIP as the “Brickworks area”.Recommend The Void area SFIP (AMPAC FireFinder V6) be reprogramming to reflect the correct customer zone text for the sprinkler flow switch from “Brickworks” to “Kitchen” & removal of the redundant “Brickworks MCP”.It is presumed the new works is still under DLP.Advised Maintence.
MSA-DCS | WA3647976 | Unit 6, Cell D1- Toilet system is leaking when toilet is flushed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-25 10:30:00 | Pass | Held up for approx 30mins in unit due to ‘covid cleaning’
MSA-DCS | WA3648009 | Unit 4A, near 53 Kitchen - urn leaking, tripping electrics may require require replacement | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 13:36:11 | 2020-09-24 14:00:00 | Fail | Complete
MSA-DCS | WA3648018 | front of prison sallyport frozen shut but is not locked | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 23 Sep 2020 | 2020-09-23 17:42:19 | 2020-09-23 18:00:00 | Fail | 23/09/20Adjusted motor limits.Broken actuator found. Replaced actuator for locking pins.Reset clutch on outer doors.
MSA-DCS | WA3648032 | Unit 1, corridor & yard Camera have frozen | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Sep 2020 | 2020-09-23 17:52:40 | 2020-09-23 16:30:00 | Pass | Rectified and fixed the fault from unit 1 ws, job completed.
MSA-DCS | WA3648063 | unit 4 C wing grill Lock is loose | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 14:10:58 | 2020-09-23 15:00:00 | Pass | On Site - Supply and fit nutsert into door to allow Jackson Grill Lock to be re-secured.
MSA-DCS | WA3648070 | Unit 3, PA System not working in prisoner acccommodation | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2021-05-06 15:00:00 | Fail | Inspected PCB for track damage, non evident strapped PA Amp output to House C pA speaker feed and tested. PA operating now in house C, but with excessive Hum. Strapped house B output to House C, staff confirmed PA operation without Hum. Advised Tony Vavier ASSIEM of situation. He responded if it is working, sign it off.
MSA-DCS | WA3648078 | Unit 3, B wing yard door lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 14:38:55 | 2020-09-30 08:15:00 | Fail | 24/09/2020. Attended site. Determined beyond repair. Replacement needed.30/09/2020. On site. Supplied and fitted replacement lock.
MSA-DCS | WA3648081 | Official visits- Staff toilet floor drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 14:42:13 | 2020-09-24 08:05:00 | Pass | 500mlof acid down drain pipe after cleaning hair and gunk from pipe to plunge to clear
MSA-DCS | WA3648133 | industries gate inbetween industies and external lock hard to double lock | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 15:56:46 | 2020-09-24 09:40:00 | Pass | adjusted gate frame locking strike and serviced Gate Lock
MSA-DCS | WA3648146 | admin building ICF PC is unable to except indigo vision | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 19:00:00 | Pass | Found Indigo Command Centre was unable to access the database, correct database error then reloaded Security access. Programmed Workstation to autologous and bring up Command Centre login panel.
MSA-DFES | WA3647745 | ground office all globes & light covers be checked & covers fixed/globes replaced were required | O'Connor Fleet Storage | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-10-14 14:45:00 | Fail | Installed 3 x Downlights Repaired 1 x Globe in Hallway Fixed 5 x Fluro lights in Office
MSA-DFES | WA3647940 | Ground level, training tower - Broken key pad lock on tower gate. | CFRS Perth | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 13:40:00 | Pass | Replaced mortice lock in gate
MSA-DFES | WA3647956 | L1 ktichen Water cooler tap broken off, | DFES Rescue Helicopter Base | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 14:33:00 | Pass | Replaced tap to cooler A40191056F
MSA-DFES | WA3648055 | Security door in kitchen – lock is faulty | Armadale Regional Office | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 10:55:00 | Pass | Gain entry & service lock kitchen sliding screen door
MSA-DTAG | WA3647802 | Lvl 3, Female Public Toilets, Hay Street end- lock on the first toilet is very loose | Central Law Courts | WSM-BR-SITE | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-24 12:00:00 | Pass | resecured loose lock
MSA-DTAG | WA3648048 | ground registry rear door Access card reader faulty | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 10:15:00 | Pass | 24/9/20 - Dean Simpson, Joshua ParkElectric strike loose on rear registry door.Replaced top holding plate on strike, now screwed tight and secure.Tested ok.
MSA-DTWD | WA3647536 | A block, level 2 -Power tripped to computers in Library A250 | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 23 Sep 2020 | 2020-09-23 17:00:00 | 2020-09-23 15:30:00 | Pass | Job complete
MSA-DTWD | WA3647667 | Level 2, Library, Lights are blown | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-26 08:35:00 | Fail | Replaced faulty lamps as per list supplied by site.job completed
MSA-DTWD | WA3647685 | Q block - Circuit W26 has tripped. Circuit wont re set. Main overload on board has tripped | Joondalup McLarty Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 12:21:00 | Pass | Investigated power tripped out. Tested circuit and appliances and found no faults. Fault being a broken gpo shorting out. Replaced gpo and plug to appliance
MSA-DTWD | WA3647696 | M block ground CCTV system fault (DVR beeping) - see notes | Balga Campus | GMP-BR | Security | CCTV Surveillance (SE) | Casa Security Pty Ltd | 1 | CLOSE | 23 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 14:00:00 | Pass | Rectified faulty monitor
MSA-DTWD | WA3647773 | South Wing, Level 1- Female toilets are blocked & overflowing | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 23 Sep 2020 | 2020-09-23 14:46:54 | 2020-12-04 11:30:00 | Fail | Job completed
MSA-DTWD | WA3648003 | B006.2, Female staff toilet - Faulty lights (high ladder required) | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 11:30:00 | Pass | Job complete
MSA-DTWD | WA3648074 | A block, level 1, control room - Repair Purge function on BMS for A and B Block | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Building Automation & Electrical Services Pty Ltd | 1 | COMPFIN | 23 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-23 18:00:00 | Pass | Steve Kinslow has programmed night purge.Work order closed out at $0 cost
MSA-DTWD | WA3648141 | B block BG25 W/S Broken Emergency Stop Switch - see notes | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Sep 2020 | 2020-09-29 17:00:00 | 2020-10-05 15:30:00 | Fail | Arrived on site, signed in, spoke to fm about job, completed jsa, located stop button , prepped stop button for fast install as could only shut off power for short period of time, isolated power, removed old stop button , replaced with new stop button with fitted shroud , cleaned up work area , completed paperwork, signed out *** job completed ***
MSA-MRWA | WA3648021 | Illuminated Exit Sign not working (not illuminating) | Materials Engineering Branch-Asphalt Lab-Ground Floor-Corridor-From courtyard to Metrology Building | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-25 11:00:00 | Pass | Replaced faulty fluro light. All now working.
MSA-MRWA | WA3648023 | Emergency light admin courtyard not illuminating (tagged out) | Materials Engineering Branch-External Area-Ground Floor-Courtyard | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 3 | CLOSE | 23 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-25 10:30:00 | Pass | Replaced faulty em light. Tested and tagged all now working
MSA-DCA | WA3648492 | distribution board circuit Whlite 3 is tripping | PICA-Main Building-Level 1 | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 13:01:00 | Pass | Located faulty circuit, identified all lights on circuit, isolated until fault was clear , repaired all ok
MSA-DCS | WA3648248 | Unit 1, B3 - Main lock on cell door faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 07:23:01 | 2020-09-24 11:45:00 | Pass | On site. Repaired door and replaced main lock. Normal function restored.
MSA-DCS | WA3648252 | Kitchen - Combitherm oven not working suspected pump malfunction | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 07:27:23 | 2020-10-01 12:45:00 | Fail | Returned to site and replaced electrode and tested ok.
MSA-DCS | WA3648257 | unit 3 - control room switch board making loud buzzing noise | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 11:30:00 | Pass | Noisey contactor
MSA-DCS | WA3648264 | Unit 3, control room has major cockroach issues | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 24 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 09:20:00 | Pass | German Cockroach infestation in the control room at Hakea Prison treated.
MSA-DCS | WA3648267 | Unit 5, A Wing, Cleaning Cupboard - cleaning cupboard drain seeping water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 24 Sep 2020 | 2020-09-24 11:37:40 | 2020-09-25 13:30:00 | Fail | Nill
MSA-DCS | WA3648269 | Unit 1, B wing - store room door lock faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 07:40:51 | 2020-09-24 11:30:00 | Pass | Replaced door lock barrel on Unit 1 / b wing storeroom door
MSA-DCS | WA3648299 | Unit 4, A & C - Only one shower working, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-25 08:30:00 | Pass | Nill
MSA-DCS | WA3648306 | Unit 2, B & D Dayroom - 56SO520 Switch socket smashed in 20 AMP, possibility of exposed wiring | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 08:05:55 | 2020-09-24 10:30:00 | Pass | Investigate and replace unit 2 b&d dayroom three phase outlet.
MSA-DCS | WA3648335 | Unit 14, Cell A9- shower is blocked, plunger has not fixed the problem | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 13:00:00 | Pass | Nill
MSA-DCS | WA3648348 | Admin, Changeroom- Flush buttons are continuously getting stuck | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-29 15:00:00 | Pass | Nill
MSA-DCS | WA3648351 | Unit 2, Cell 56 - light switch broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-25 13:30:00 | Pass | Investigate and replace unit 2 cell 56 light switch
MSA-DCS | WA3648353 | Unit 3, cell A7- TV wall socket not working after lightning strike | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-25 09:30:00 | Pass | Job completed - Attended site. Removed plate, re-crimped connections and TV working perfect.Job completed.
MSA-DCS | WA3648357 | Unit 2, PA system not working after lighting strike | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-11-09 12:54:00 | Fail | Replaced PA amplifier removed excess cabling and tested fully operational.
MSA-DCS | WA3648426 | Gate House - Office - Security require SEME to download CCTV footage from gatehouse on 16 July 2020 | Casuarina Prison | WSM-MW-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-25 09:00:00 | Pass | Attended site and checked camera recordings for gatehouse cameras. Found recordings only backdated to early September as the earliest recordings. No other recordings further back. Advised site and made aware. Job complete
MSA-DCS | WA3648459 | Library Office - Our Middle bank of lights are out. with 3 out of our top row are still out. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-25 08:30:00 | Pass | Restored power to library lights
MSA-DCS | WA3648511 | Unit 8, SO Office - ceiling leakng above fax machine when air con is on. | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 10:15:22 | 2020-09-24 13:30:00 | Pass | Found leak to be inside roof space in the supply water to evap from boiler inlet. Isolated water to stop leak and informed site to get plumber to repair line. Plumber was on site and carried out repairs on same day.
MSA-DCS | WA3648517 | Medical Centre Mental Health Area No cool air blowing | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 10:19:24 | 2020-09-25 10:30:00 | Fail | Schedule timer faulty. Replaced timer and programmed schedule. Operational at time of departure.
MSA-DCS | WA3648547 | Unit 6, A wing yard - 2ft fluorescent light broken needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 10:44:27 | 2020-09-24 13:30:00 | Pass | Replaced light
MSA-DCS | WA3648591 | cleaning cupboard store room - light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-25 14:30:00 | Pass | Found fault sensor in cleaners cupboard, left site to collect new sensors returned and replaced. Set and tested
MSA-DCS | WA3648602 | internal Sallyport door, pins were not dropping would only open half way | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 08:30:00 | 2020-09-24 14:00:00 | Pass | 24/09/20Inner doors - adjust stops, adjust limits.Take bottom lock pin plate for adjustment at AFD Workshop. Modify base plate at AFD Workshop.Return to site with base plate and reinstall.
MSA-DCS | WA3648613 | CCU control pod Computer Screen for electronic door opener is Blank | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 11:54:03 | 2020-09-24 13:45:00 | Pass | Attended site checked and found CCU EBI workstation not working properly, staff can’t control the electronics doors. Reboot EBI workstation and bring all functions back on line.
MSA-DCS | WA3648627 | Visits Area - Lobby Area visits non contact booths not working - see notes | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 12:16:37 | 2020-10-07 08:33:00 | Fail | Invoice raised for costs to date as advised
MSA-DCS | WA3648631 | Unit 4 C5 tongue of the lock is jammed as the sliding mechanism has snapped | Hakea Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 12:20:39 | 2020-09-29 16:15:00 | Fail | Attended 24/09/2020. Attempted repair, replacement required.On site 29/09/2020. Supplied and fitted replacement lock.
MSA-DCS | WA3648714 | Control - camera 91 & 173 are not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 13:25:51 | 2020-09-25 15:30:00 | Fail | Rectified and fixed camera fault no video, job completed.
MSA-DCS | WA3648737 | Academy Accommodation Wing - blown lights and electrical cabling for smoke detector loose | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-01 11:00:00 | Fail | Repaired lights
MSA-DCS | WA3648758 | unit 4 F 21 exhaust fan faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-25 15:00:00 | Pass | Investigate and replace unit 4 F22 exhaust fan
MSA-DCS | WA3648767 | Unit 9, A wing - Window glass smashed (no glass) | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 14:22:44 | 2020-09-25 12:00:00 | Pass | Glass had been removed, we located the glass and installed
MSA-DCS | WA3648771 | Unit 7 - D Wing oven not working properly and keeps tripping the power | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 14:40:00 | 2020-10-07 08:55:00 | Fail | Returned 7/10 and replaced element, fitted and tested ok.
MSA-DCS | WA3648772 | Unit 1 & 2- Heat control switch faulty | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2021-05-04 13:00:00 | Fail | Attended container today checked to see if supplied smoke detector had been change from a fire panel (two wire) to security panel type (4-wire power and alarm) had been corrected. It hadn't. nothing further we could do. Closed job.
MSA-DCS | WA3648781 | unit 1 A11 and A12 Toilets are Blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 15:04:17 | 2020-09-25 12:20:00 | Pass | Plunged x2 cells lots off poo
MSA-DFES | WA3648237 | Reception Ground floor - security computer not connecting to server | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 24 Sep 2020 | 2020-09-24 17:00:00 | 2020-09-24 11:00:00 | Pass | 24/9/20 - Dylan Parslow, Ryan VestyFound network device on Pc not connected.Pc on wrong IP range. Reset Pc to DHCP and tested, Pacom online.Recommend Pacom computers to be upgraded as windows 7 no longer supported.
MSA-DFES | WA3648417 | engine room door No3 rear left not opening when pushing button need to manually raise | CFRS Armadale | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-11-11 11:27:00 | Fail | Following our service call on 25/09/2020 to the Engine Room Door, W22529 located at the above site, it has been reported that the existing remotes are damaged and will require replacement to restore and maintain safe and reliable door operation. Technician attended the site of Armadale Fire Station on 25/09/2020 and completed quoted works. Full test and inspection of door function completed prior to leaving site. This quote includes:"Supply and installation of 5 x new replacement remotes "Test and check door operation."The above work is to be carried out during normal business hoursBreakdown of cost: First callout and labour = $390.00Labour = $650.00Parts = $882.47
MSA-DFES | WA3648469 | Bathroom lights - RCD keeps tripping out | CFRS Malaga | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-10-12 09:30:00 | Fail | CompleteCollected ladder and Attended site and found that the tubes in s the sign out front were burnt out causing it to trip, replaced fluros and tested all in working order
MSA-DFES | WA3648472 | Dorm 3 - Air Con is not working | CFRS Malaga | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 12:31:00 | Pass | Attended site and inspected air con in dorm room.Found multi head split system feeding both dorm rooms.Found condenser unit isolated at isolator.Turned isolator on and ran up both systems.Found aircon system operating correctly.Reported findings and completed paperwork.
MSA-DFES | WA3648475 | Dorm 4 - Air Con is not working | CFRS Malaga | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 12:28:00 | Pass | Attended site and inspected air con in dorm room.Found multi head split system feeding both dorm rooms.Found condenser unit isolated at isolator.Turned isolator on and ran up both systems.Found aircon system operating correctly.Reported findings and completed paperwork.
MSA-DFES | WA3648826 | ICT help desk L1 no power | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 17:15:00 | Pass | COMPLETED
MSA-DTAG | WA3648343 | 2A, Lift 3 - Lift 3 not responding - | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 13:50:00 | Pass | Some components of the car door operator were worn out. Following our attendance, the equipment was left in service. To be closed out at $0
MSA-DTAG | WA3648666 | ground court 1 Duress alarm in Court 1 is faulty and going off. Can’t reset it. | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 14:00:00 | Pass | Fix druress and move map graphics to match duress location
MSA-DTAG | WA3648768 | 1903 external Water leaking from reticulation sprinklers – outside Sheriff’s Office | Supreme Court | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-25 15:30:00 | Pass | Labour & Retic Parts
MSA-DTWD | WA3648292 | T block Male student toilets G.F adjacent café and hairdressing - 2 x W.C. pans blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 24 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-24 10:00:00 | Pass | Unblock various toilets
MSA-DTWD | WA3648327 | K Block, Ground floor - Kitchen alarm panel showing tamper error on arming. Area isolated | Midland Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 1 | CLOSE | 24 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-24 10:10:00 | Pass | Investigated sensor trouble on zone 7. Found to be sensor in rear kitchen foyer. Found cover to this sensor damaged. Replaced with new and retested.
MSA-DTWD | WA3648496 | Level 2, D block, Administration area - 20 blown flouro tubes in area | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 09:00:00 | Pass | Replace 22 x tubes and starters throughout level 2 receptionReplace 20 x tubes and starters throughout level 2 reception
MSA-DTWD | WA3648575 | AMEP Hot Water System (message: Error DetecteED) LEAK FROM TAP-see notes | Perth Campus B1 | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-11-12 14:48:00 | Fail | Installed new boiler
MSA-DTWD | WA3648596 | L3 north mens student toilet, toilet seat broken. | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-25 11:06:00 | Pass | New toilet seat
MSA-DTWD | WA3648669 | tower block L4 male toilet broken toilet seat | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-25 15:15:00 | Pass | Complete
MSA-DTWD | WA3648798 | rear carpark caged area Dust extractor full at Number 12 | Perth Campus B5 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 24 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-28 15:39:00 | Fail | BRAF works have been completed. Dust extraction unit restored to normal operation.
MSA-DTWD | WA3650255 | RETROSPECTIVE D block D3 – Faulty tap set is leaking badly | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 0 | CLOSE | 24 Sep 2020 | 2020-09-24 16:42:00 | 2020-09-24 15:25:00 | Pass | Repaired leaking taps
MSA-DCA | WA3649161 | lower ground lift unresponsive stuck on basement floor | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 25 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 11:45:00 | Pass | Lift 2 Art-Geared :Found lift as reported, found lift rope brake pulled in, fault 11 showing ( accleration with out energy) reset and tested ,left lift running
MSA-DCA | WA3650310 | leak in the plantroom - Craig is aware of fault | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 20:17:03 | 2020-09-25 18:30:00 | Pass | Attended call logged.Steam Boiler 1 water leak from Auto Blow down valve and actuator assembly. Steam Boiler slight leak from same area. Faults with parts already noted in PM. DAS submitted. Approval for repairs received. Awaiting parts arrival. Removed, cleaned, tried adjusting alignment. Leak reduced to a drip but water still passing through valve when closed both Steam Boilers 1 & 2 blows own lines until repairs are carried out.Cleaned immediate area of water spillage.Closed job.
MSA-DCS | WA3648867 | Kitchen- CPB brat pan side ignition is failing | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 25 Sep 2020 | 2020-09-25 09:15:08 | 2020-09-25 12:30:00 | Fail | 25/09/20Attended kitchen Issue - Bratt pan side ignition is failing.Found dirty ignition probes and burners.Looks like there was a spillage and it contaminated the probs and burners.Cleaned ignition probes, burners and burner jets.Checked gas working pressure at 2nd stage regulator that controls the gas pressure to all kitchen appliances. The pressure was adequate.The appliance lit, stayed on and heated up to temperature.Problem rectified.
MSA-DCS | WA3648931 | CCU - Tap in cell C2 in CCU is leaking coming from the top, down the wall and onto the floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-30 09:30:00 | Pass | Nill
MSA-DCS | WA3648938 | Unit 14, C6 - Tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 12:00:00 | Pass | Nill
MSA-DCS | WA3648941 | Unit 14, C wing, C6 - main light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 08:30:00 | Pass | Repaired faulty lights in unit 14 c6
MSA-DCS | WA3648950 | Unit 7, B wing - Fly zapper globe faulty/blown | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 10:00:00 | Pass | Checked faulty bug zapper in unit 7. Picked up replacement parts and installed and tested
MSA-DCS | WA3648960 | Jeelia, A3 - shower drain block | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-02 08:30:00 | Fail | Clear blockage to shower waste
MSA-DCS | WA3648970 | Jeelia, C6 - Badly blocked toilet | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-02 09:15:00 | Fail | Inspect drains all water and waste running free
MSA-DCS | WA3648974 | Assessments, Security Door - Door will not unlock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 07:42:21 | 2020-09-30 10:30:00 | Fail | 25/09/2020. Attended site. Opened door and made safe. Replacement lock required - parts needed. 30/09/2020. On site. Supplied and fitted replacement sliding door lock.
MSA-DCS | WA3648980 | Canteen east - Roof leaking above store room shelf | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 07:45:32 | 2020-12-17 14:00:00 | Fail | roof repaired to rectify leaking
MSA-DCS | WA3649005 | Unit 2, A-B 11 & 12 - fire alarm panel showing fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 08:14:36 | 2020-09-26 08:14:00 | Pass | Attended at 0830, unable to access due to lock down, instructed to return at 1200A/C 11/12 in fault on arrival. Pipe 1 stuck in closed position. Rectified. All clearWhilst on site rectified the following in unit 1 as faults present on arrival;A/C 11/12 zone fault. Too many scans. Adjusted thresholds marginally and reset. All clearC/D 15/16 suspected high airflow. Investigated pipe work and connections. All okay.
MSA-DCS | WA3649009 | Unit 2, A-B 15 & 16 - fire alarm panel showing fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 08:18:06 | 2020-09-26 08:18:00 | Pass | Attended at 0930, unable to access due to lock down, instructed to return at 1300Upon arrival found low airflow fault. Pipe 3 D16 blocked from lint build up. Cleaned sample point. All clear.
MSA-DCS | WA3649012 | Unit 2, C-D 15 & 16 - fire alarm panel showing fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 08:19:21 | 2020-09-26 08:00:00 | Pass | Found vesda unit powered off on arrival. PSU and batteries failed. Removed batteries and regained power to PSU.
MSA-DCS | WA3649027 | Main Kitchen - Back oven is showing fault 25 | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-02 12:20:00 | Fail | Replaced new hook clip to baffle cage.
MSA-DCS | WA3649031 | Main Kitchen - Freezer is going into E1 fault alarm | Bandyup Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 08:29:27 | 2020-09-25 13:30:00 | Pass | Gained access to kitchen and inspected systems.Controller in warning alarm regarding P2 coil probe, faulty.Picked up new.Tested.Alarms now cleared.Systems working as normal.Chef advised of works.
MSA-DCS | WA3649033 | Staff Carpark, Disability car parks - repair damaged bollards | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-11-06 11:00:00 | Fail | Attended site and removed damaged bollard.Sourced new bollard and picked up concrete and asphalt.Re-Attended site and installed new bollard
MSA-DCS | WA3649035 | Control Room - air conditioning no working in control room | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-30 09:00:00 | Fail | Replaced motor and board. Test ran operation. Operational at time of departure.
MSA-DCS | WA3649128 | Visits Indigo system has failed | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 17:33:36 | 2020-09-30 16:00:00 | Fail | Powered down connected equipment, removed existing UPS and installed replacement Powershield RT1100 UPS. Restarted Indigo workstation and confirmed correct operation.
MSA-DCS | WA3649184 | Jasper C wing Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-25 15:00:00 | Pass | Replaced faulty light switch in jasper c1-1
MSA-DCS | WA3649188 | Reception, Office - 2x doors damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-06 14:30:00 | Fail | Supply and install new 600mm x 600mm glass vision panels to reception office doors
MSA-DCS | WA3649273 | Lennard B wing - no hot water | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 11:21:07 | 2020-10-02 14:55:00 | Fail | Replaced faulty electrical box
MSA-DCS | WA3649277 | Unit 2, A1 - Water Seeping up from the floor drain | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-09-30 14:25:00 | Pass | Drain rod used to unblock floor waste
MSA-DCS | WA3649286 | Unit 3 control room Control room broken tiles | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-08 11:30:00 | Fail | LOCATION INSPECTED - NO EVIDENCE OF BROKEN TILES FOUND
MSA-DCS | WA3649292 | Unit 5 A13 and A28 Taps are still dripping needs plumbers attention | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-01 11:30:00 | Pass | Turned off water supply reseating and replacing tap washers valves and orings
MSA-DCS | WA3649350 | Unit 3 - B & D wing showers drains are draining slowly. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-29 08:30:00 | Pass | no issue found
MSA-DCS | WA3649474 | Unit 8 Store Behind SO. office 2nd water leak behind SO. Office up in roof space needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Sep 2020 | 2020-09-26 13:36:23 | 2020-09-30 10:50:00 | Fail | Replaced length off 15mm copper for aircon feed in roof space up and down across x2 man holes
MSA-DCS | WA3649484 | Bakery BREAD SLICER KEEPS STOPPING. | Casuarina Prison | WSM-GR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-11-06 13:15:00 | Fail | 29/9/20Check bread slicerFound RH side not locking blades on Fault find Found overload tripped Clean internals of electrical box and slicer Test slicer, working ok Found RH slides at top of slicer worn and require replacing Parts required2 x Shuttle Bushes23/10/2020Shannon Remove covers Attempt to remove slide Found not and bolt threads and unable to remove without cutting off Advise staff and advised to put back together to be used and order parts5/11/2020Sign in Escorted to site Isolated bread slicer Remove and replace right side shuttle guidesRear guide rightWear in guide Adjust unit for minimum noiseReassemble and test heavily Ok.6/11/2020Sign in Get escorted to sight Found RH side not moving but motor operating Found rear slide melted onto shaftRemove shaft and check with part and slide would not move freely.Machine shaft down in maintenance workshop Install with new part Test unit by hand to make sure running freely Test machine for 10 minut
MSA-DCS | WA3650195 | Unit 2 duress comunication fail | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 18:18:52 | 2020-10-23 09:28:00 | Fail | Unit 2 communication failure.Modified fibre network routing after fibre replacement between Admin and Unit 2.Tested OK.Job Complete
MSA-DCS | WA3650225 | Stores - Loading Dock repair damaged tap and pipe in front stores and secure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-14 12:30:00 | Fail | Nill
MSA-DCS | WA3650236 | back door staff entry/exit alarm not arming correctly - see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 11:45:00 | Pass | 2 x PIRS false alarming 88, 89. Checked PIRs and found dead insects and spiders in both. Clean and spray poison. Tested relays on PIRs and all is OK. Tested voltage and 12.4VDC at PIR. Checked terminations t panel and pir all is OK. Getting 10KR seal and 20kr alarm. Operation of PIRs all OK.
MSA-DCS | WA3650244 | perimeter fence zone 8 internal continues to alarm | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 18:58:30 | 2020-09-25 17:15:00 | Pass | Attended site checked and found Zone 8 Internal microwave keeps alarming. Checked on field found a lot of weeds blocking the sensors. Cleanup the weeds and tested alarm activated and reset correctly.
MSA-DFES | WA3649279 | Retrospective W/Order - STORE REAR ROLLER DOOR - SINGLE HIT - refer 35041911 | DFES Regional Office - Belmont | GMP-BR | Building | Doors (BU) | Securex Security Systems & Services | 1 | CLOSE | 25 Sep 2020 | 2020-09-25 17:00:00 | 2020-09-25 07:43:00 | Pass | INTERNAL AND EXTERNAL CHECK, ALL APPEARS SECURE, STAFF ON SITE NAMED BELLA MADY SCHARFENSTEIN, LICENCE NUMBER 1981699,CLEARED BY OPS
MSA-DFES | WA3649364 | ground floor Emergency Light not working – leading to the bin storage area | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 09:00:00 | Pass | Replaced faulty exit sign with a new exit sign adjacent to reception desk.
MSA-DFES | WA3650243 | Lunch room - Fridge power points not working, unable to reset. | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 18:55:09 | 2020-09-25 16:15:00 | Pass | Arrived on site and Investigated tripping RCD on R2. Reset RCD and it stayed energised even after we had plugged back in all appliances that were on the R2 circuit. There is multiple fridges, a water cooler and potentially other electrical appliances which have been plugged in on R2 circuit, giving a probable cause for nuisance tripping. Have advised staff not to put too many things on the same circuit and to move the fridges around so that they’re not on R2.
MSA-DTAG | WA3649130 | Lift - Schindler technician required to attend site afterhours to assist Sapio technicians | State Administrative Tribunal (SAT) | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-09-25 22:00:00 | Pass | Repairs to lift
MSA-DTAG | WA3649202 | Ground, Public mens toilet - Appears to be a leak when flushed. | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 14:25:00 | Pass | COMPLETED
MSA-DTAG | WA3649241 | 1903 Lower Gnd Lvl - Infrared safety beam preventing roller door from closing when blocked | Supreme Court | GMP-BR-HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-27 12:07:00 | Fail | Ryan Nicholson (29/09/2020) - Work NoteTravel to site. Inspect and found that the same problem is happening due to the controller having issue. Tested access system and found that the access has normally closed contacts and that the contol board takes priority of which one is still latched after button is open for either open or closed button. Simulated operation with access disconnected and found the door will still go down if PE beam is broken prior to moving down. Spoke to manufacturer who has recommended replacing the control board.
MSA-DTAG | WA3649253 | Level 4, Disabled public toilet (across from custody) - Disabled toilet, is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 14:00:00 | Pass | Complete
MSA-DTAG | WA3649265 | Level 4, Male public toilets (Hay Street end) - Toilet blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 13:30:00 | Pass | Complete
MSA-DTAG | WA3649478 | Basement 1 - inside building, card reader faulty and unable to secure door - | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 17:38:57 | 2020-09-25 15:30:00 | Pass | Found SAT upper & lower basement unable to open doors. 485 Star Coupler offline with controller.Reload controller configuration and door controller back on line. Replaced break glass insert on lower basement.Job completed.
MSA-DTAG | WA3650229 | ground court 1 Internet port on the side of court room 1 not working, - see notes | Armadale Courthouse | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 08:30:00 | Pass | Job complete
MSA-DTAG | WA3650276 | cell 4 Peeled paint needs either repairing eg. sanded. Prisoner used peel paint to cut wrist. | Rockingham Justice Complex | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 25 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 09:20:00 | Pass | REPAIRS TO DAMAGED WALL COMPLETED
MSA-DTWD | WA3649051 | B Block B015 & B019 have faulty fluro fittings | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 13:30:00 | Pass | Job complete
MSA-DTWD | WA3649084 | A Block Conference room A19 - Daiken cassette air con not working | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 25 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-29 14:00:00 | Pass | Attended site and signed in, checked the aircon at room A19. Found a fuse on the outdoor board blown,picked up new fuse from supplier's. Fitted the new fuse and test ran all ok , rang Daikin tech support and checked with them of any other problems. Working ok.
MSA-DTWD | WA3649125 | A block, 003 - faulty fluro fitting | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-29 15:30:00 | Pass | Job complete
MSA-DTWD | WA3649180 | F block, FG23 Workshop - Emergency Exhaust Fan Push button not starting the fan at the Northern end | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-12 13:01:00 | Fail | Control fault identified. Alternative replacement required as existing component is obsolete - Stock ordered Replaced faulty component, bms requires re configuration, will be organised by facilities management
MSA-DTWD | WA3649192 | next to B block high security light on pole not working | Balga Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 16:30:00 | Pass | Job complete
MSA-DTWD | WA3649246 | E block kitchen E74 door is jammed on the combi oven | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 25 Sep 2020 | 2020-09-29 17:00:00 | 2020-09-25 13:45:00 | Pass | COMPLETED
MSA-DTWD | WA3649260 | H block kitchen prep area exhaust hood light faulty | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-29 16:30:00 | Pass | Job complete
MSA-DTWD | WA3649264 | H block H001 Bain Marie heat lamps faulty | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 13:30:00 | Pass | Job complete
MSA-DTWD | WA3649270 | H block H001 canteen servery front counter sandwich cabinet lights loose on existing brackets | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 16:30:00 | Pass | Job complete
MSA-DTWD | WA3649272 | H block H002 kitchen prep area air con vent missing | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-29 16:00:00 | Pass | Attended site , completed relevant sign in procedures, inspected missing grille in back kitchen area , purchased replacement grille from metaflex and replaced as required, all working ok
MSA-DTWD | WA3650306 | E block E37 walk in freezer not cooling properly | Bentley Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 0 | CLOSE | 25 Sep 2020 | 2020-09-25 20:04:49 | 2020-09-25 19:30:00 | Pass | Defrosted and cleared iced up evap coil
MSA-MRWA | WA3649303 | L2 RTTO desk 14 Sit stand desk not working please remediate | Road Network Operation Centre (RNOC) | GMP-BR | Furniture | Office Furniture (FU) | SCHIAVELLO SYSTEMS (WA) PTY LTD | 2 | CLOSE | 25 Sep 2020 | 2020-10-01 17:00:00 | 2020-12-01 09:30:00 | Fail | to be closed out at $0
MSA-DCS | WA3654214 | Camera 47 is stuck no pan on the camera | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Sep 2020 | 2020-09-27 08:02:53 | 2020-09-30 17:45:00 | Fail | Located camera equipment and reset camera power and tested all functions and checked for any faulty equipment. All reset and PTZ functions all working ok. Job complete
MSA-DCS | WA3654235 | Adminstration door lock is faulty | Wooroloo Prison Farm-Administration Centre | GMP-BR- HO | Building | Doors (BU) | ACE LOCK & SAFE | 2 | CLOSE | 26 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-29 11:30:00 | Pass | Replaced Mortice lock on Admin Building Unit 2 side ) lock faulty /Worn )
MSA-DCS | WA3654238 | unit 4 A- cell 4 Door lock barrel is broken cannot secure cell | Wooroloo Prison Farm | GMP-BR- HO | Building | Doors (BU) | ACE LOCK & SAFE | 2 | CLOSE | 26 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-29 10:30:00 | Pass | replaced broken cell lock on Unit 4A / Cell 4
MSA-DCS | WA3654249 | Securty system perimeter-zone 6 receiver 11 microwave has gone into fault will not reset | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Sep 2020 | 2020-09-27 11:38:01 | 2020-09-27 11:00:00 | Pass | Contacted site and found zone 6 in alarm, reset logic block from programming via phone support and retested. All tested and working ok. Job complete
MSA-DCS | WA3654293 | Hakea Prison- CCU Unit - Cell H-9- The celll call system is not working | Hakea Prison-Administration Block East | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Sep 2020 | 2020-09-26 18:32:38 | 2020-09-29 10:00:00 | Fail | Attended site checked and found CCU H9 cell call stuck on remote display but not on control panel. From H9 can’t make cell call to control. Reboot control panel and tried to make cell call connection from control to H9 successfully. Tested cell call from H9 to control and confirm all working ok after work.
MSA-DFES | WA3654276 | water leak from the pot hole underground, on the drive way behind the main gate | VFRS Secret Harbour- TO BE DECOMMISSIONED Secret Harbour Vols-RA and CP | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 26 Sep 2020 | 2020-09-27 13:36:12 | 2020-10-14 11:55:00 | Fail | Replaced damaged part of water line tested and holding
MSA-DCS | WA3654464 | Zone 14 - perimeter fence is constantly alarming,4 zone presets needs to be adjusted | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Sep 2020 | 2020-09-28 06:04:40 | 2020-09-27 10:00:00 | Pass | Afterhours callout, travelled to site and checked zone14 fence alarm. Checked for correct end of line resistor and all tested ok, replaced zone with cable ties and retested zone. All tested and reset ok. Re-adjusted several camera presets as requested on job description. All set ok. Job complete
MSA-DCS | WA3654470 | Unit 3- Transmit failure with the cell call. Indicating node 83 | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Sep 2020 | 2020-09-28 08:24:00 | 2020-09-27 10:00:00 | Pass | Afterhours phone support, contacted site and got site to reset 3210 unit in unit 3. Cleared through all alarms and tested all unit cell calls. All tested and working ok, no alarms present. Job complete
MSA-DCS | WA3654478 | Fence not alarming | West Kimberley Regional Prison | GMP-BR- HO | Building | External Walls (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Sep 2020 | 2020-09-28 08:48:04 | 2020-09-29 12:00:00 | Fail | Contacted site and reset fence logic block from programming, advised site to reset fence zones, contacted site and had advised that all fence alarms activated ok. Job complete
MSA-DCA | WA3654747 | Plant room Level4 -Multiple BMS alarms going on | Art Gallery of WA - James St - Main Building (Block B)-Level 4 - Roof Ventilator Plant | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 28 Sep 2020 | 2020-09-28 12:10:17 | 2020-09-28 12:15:00 | Fail | Arrived on site. Fault finding. Found steam plant boiler 1 and 2 tripped low gas prssure safety.Reset the boilers and ran. Running ok but further investigation is needed.0915 AM - 1215PM on 28/09/2020No need for further investigation.
MSA-DCA | WA3655121 | Control room - Admin - Fire panel is in fault - Fire Brigade attended last night - needs resetting | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-AG.26 - Foyer | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 28 Sep 2020 | 2020-09-28 22:15:33 | 2020-09-28 20:00:00 | Pass | 28/9/20 GAArt galleryCallout due to faults and false alarm on fip found the following -Loop 3 in over current fault and unable to reset investigated and found there is a water leak in the ladies toilet on level 3 and water got into thermal detector l3 s72, bypassed detector and left isolated until leak is rectified, Loop tested loop to clear over current fault.False alarm on smoke detector l2 s10 l2 gallery 2, fire brigade attended on the 28/9/20 at 150am and reset alarm but left detector isolated. Located detector in gallery and requires 12 foot+ ladder to replace. Site advised to leave detector isolated and possibly replace at same time as above detector once ceiling is fixed.
MSA-DCS | WA3654587 | Banksia Hill Control Room - Controller 118 has failed | Banksia Hill Detention Centre-Administration | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Sep 2020 | 2020-09-29 05:57:17 | 2020-09-28 09:30:00 | Pass | Attended site and investigated the fault.Found that FlexPS processor in EC8 is offline.Reseted power to processor and conducted test.All ok at departure.
MSA-DCS | WA3654600 | Self care Serpentine room Camera 131 fault | Banksia Hill Detention Centre-Block Q Self Care Unit | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 11:25:00 | Pass | Escort organised for 8Escort was late,Checked camera footage, when no lights are on image is dark.Checked camera, panasonic SD5 dome, camera has no IR capabilities.Checked other cameras all the same.No fault with camera
MSA-DCS | WA3654698 | Control room - Camera 188 is out | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Sep 2020 | 2020-09-29 07:44:57 | 2020-09-28 11:30:00 | Pass | Attended site and investigated the fault.Found that there is no video on camera 188 PTZ 23.Reseted power to PTZ camera 23 (located in Sallyport Equipment Room in Melaleuca Prison).Tested.All ok at departure
MSA-DCS | WA3654742 | Expansion Project - Unit 16 toilet is overflowing | Casuarina Prison-Prisoner Accommodation Unit 14 | WSM-MW-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 28 Sep 2020 | 2020-09-28 12:17:44 | 2020-11-16 15:00:00 | Fail | Unblocked but needs camera to inspect drain. Camera inspection being done under job
MSA-DCS | WA3654758 | Cell # C3 - In operable cell lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 0 | CLOSE | 28 Sep 2020 | 2020-09-28 12:34:30 | 2020-09-28 10:10:00 | Pass | Attended site after hours (Public Holiday). Repaired cell lock. Normal function restored.
MSA-DCS | WA3655068 | Unit 1 - cell D09 - locksmith to fix door to the cell | Melaleuca Prison | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 0 | CLOSE | 28 Sep 2020 | 2020-09-28 17:42:58 | 2020-09-28 16:15:00 | Pass | Attended site after hours (Public Holiday). Adjusted and refastened hinges to restore normal function.
MSA-DCA | WA3655412 | lower ground kitchen lift s not working, stopped on lower ground. -see notes | Art Gallery of WA - James St - Main Building (Block B) | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-29 12:50:00 | Pass | No completion notes
MSA-DCA | WA3655653 | Loading dock area, large graffiti on wall needs to be removed | State Library of WA-Main Building-External Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 10:45:00 | Pass | job completed - Graffiti Removal
MSA-DCA | WA3655841 | Air pressure sensor low limit | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Mechanical Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-30 09:30:00 | Pass | Air pressure low limit alarm cleared 20min after being raised on the 29-09-20. No longer alarmed. Probably due to contractor works. TEF 9A in program fault. Reset. Only alarms active are AHU 4 related and being ignored.
MSA-DCA | WA3655904 | Adjacent front car park entry - under ground water leak | Sunset Hospital Heritage Precinct-External Area | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-30 14:18:00 | Pass | Locate expose and repair burst water pipe re enstate surrounds
MSA-DCS | WA3655135 | Gatehouse - cannot open doors in gatehouse - security system issue | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Sep 2020 | 2020-09-29 05:18:22 | 2020-09-29 02:30:00 | Pass | Contacted site and spoke with officer Roberts - problem with doors is retrieved and don’t require attendance (Gatehouse can control doors remotely)
MSA-DCS | WA3655184 | Cell call in the MPC Area cell 3.09 is not working/activating.-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-07 18:00:00 | Fail | Job complete Part from Perth
MSA-DCS | WA3655218 | Bakery electric rotel oven not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 07:30:02 | 2020-09-29 10:20:00 | Pass | 29/09/2020Sign in Get escorted to siteFound power going to oven but not heating Found breaker inside cabinet tripped.Reset and found loose connection on outgoing wire.Tighten Heat machine and test heavily Clean insulation off contactor's and relays Test steam, ok.
MSA-DCS | WA3655241 | ice build up on the back of the evap freezer | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Kitchen | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 07:52:34 | 2021-02-01 15:16:00 | Fail | Access to be scheduled January 2021
MSA-DCS | WA3655248 | Unit 6, B2 - sink blocked, plunger was used with no effect | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-09-30 11:30:00 | Pass | Nill
MSA-DCS | WA3655249 | Unit 4, C wing - low shower pressure in C wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-09-29 10:30:00 | Pass | Nill
MSA-DCS | WA3655250 | Unit 4 - Furthest shower tap in C WING not working, tap keeps spinning with no water coming out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-09-29 09:30:00 | Pass | Nill
MSA-DCS | WA3655251 | Unit 3, A4 - floor drain is flooding when they drain water from cell sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-02 09:30:00 | Pass | Nill
MSA-DCS | WA3655254 | Unit 6, B-D day room sink, hot water tap dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-09-30 10:30:00 | Pass | Nill
MSA-DCS | WA3655260 | MPU 8, east, MPU punishment cell M 18 - The cistern will not fill, although the water is on. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-09-30 08:30:00 | Pass | Nill
MSA-DCS | WA3655261 | unit 2 control pod CCTV camera's not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Sep 2020 | 2020-09-29 12:20:31 | 2020-09-29 11:00:00 | Pass | Travelled to site and checked CCTV monitors for unit 2. All had frozen, reset CCTV workstation and reloaded camera layouts . All loaded and working ok. Job complete
MSA-DCS | WA3655262 | Unit 5, A wing - shower drains are blocked. unable to use showers | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-06 10:30:00 | Pass | Nill
MSA-DCS | WA3655267 | Unit 5 - Office air con not working if another air con is on | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-05 09:30:00 | Pass | User fault. System fully operational
MSA-DCS | WA3655269 | Unit 13, A11 - shower seal is leaking | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-11-11 12:00:00 | Fail | RE sealed shower screen
MSA-DCS | WA3655275 | Unit 14, A & C - water urn is lekaing at over 1 cup minuter | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 10:39:00 | Pass | System leaking badly from the tap. Had to isolate power and water. Drained unit and changed rheem tap. Tap was still leaking. Needed to return to car for parts. Returned to unit. Drained system and isolated power and water again. Used tape on the tread of tap. Fixed leak. Waited for unit to get hot. Normal operation
MSA-DCS | WA3655278 | Unit 4 - B Wing Plastic light cover broken on light near window at the end of wing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-02 10:30:00 | Pass | Investigate and replace unit 4 b wing diffuser (stock on site)
MSA-DCS | WA3655282 | Unit 14, C13 - door striker lock isnt catching properly | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-11-02 12:45:00 | Fail | Replace mortise lock, requires custom strike.Replace worn strike plate with oversized strike.
MSA-DCS | WA3655283 | Zone control 2 Baine Marie faulty continually trips circuit breaker, needs repair | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 08:41:44 | 2020-09-30 09:30:00 | Fail | Repaired baine marie
MSA-DCS | WA3655285 | Unit 14, C6 - cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-05 08:30:00 | Pass | Repaired faulty lights in unit 14 c6
MSA-DCS | WA3655290 | Unit 14, A6 - Shower pressure is minimal & water is cold | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-06 14:00:00 | Pass | Nill
MSA-DCS | WA3655301 | Reception, toilets - Toilet Cistern overflowing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 08:54:09 | 2020-09-29 11:41:00 | Pass | Replaced fualty inlet valve and bellows. Waited 50min for escort
MSA-DCS | WA3655306 | unit 4 E18 Leaking shower rose | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3655311 | Unit 1 day room Urn not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 13:22:00 | Pass | Unit off on arrival and missing extension cord. Replaced cord and unit powered up correctly and working correctly. Advised was an issue with old power cord and was causing power to trip. Unit now working ok
MSA-DCS | WA3655312 | Relocate old X-ray machine from Albany back to PFM stores in Hakea Prison | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-06 08:45:00 | Pass | 02/10/20pickup x-ray machine from Albany RP, building water proof box and transport back to Perth05/10/20Deliver to stores at Hakea Prison. Keys not available, return tomorrow.06/10/20Deliver to stores at Hakea Prison.
MSA-DCS | WA3655314 | Unit 2 top landing blocked urinal | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 12:30:00 | Pass | COMPLETED
MSA-DCS | WA3655321 | Unit 1, C11 - Viewing hatch cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 09:08:40 | 2020-09-29 14:30:00 | Pass | viewing hatch re glazed
MSA-DCS | WA3655338 | Unit 17 - A & C cleaning cupboards have been ripped and lock damaged | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-11-09 14:30:00 | Fail | REPAIR AND REPLACE NEW LOCKS TO CUPBOARDS
MSA-DCS | WA3655392 | Unit 2, B-5 - Prisoners lock jammed in door | Melaleuca Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 09:57:56 | 2020-09-29 15:00:00 | Pass | Attended site. Replaced personal lock.
MSA-DCS | WA3655417 | oven not heating could be element | Boronia Pre-release-AP21 - Prisoner Accommodation House 12 and 13-Ground Floor-House 12 - Kitchen Area | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-05 15:15:00 | Fail | Replaced failed oven elements
MSA-DCS | WA3655428 | Vegetable Preparation - cold water tap, cant turn it on | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 13:00:00 | Pass | Nill
MSA-DCS | WA3655499 | Bakery, workshop - bun rounder pin has sheared | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-09-29 12:20:00 | Pass | 29/09/20Client broke divider/rounder while on site Asked to repair while on site Found split pin broken Site supplied 8mm roll pin Install and test unit, ok.
MSA-DCS | WA3655503 | Unit 1 - Rack is overheating | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 10:52:13 | 2020-09-30 11:00:00 | Fail | Rack side panel removed, taken offsite to fabricate and install twin fan cooling system and reinstalled back on site. Fully populated rack now has cooling.
MSA-DCS | WA3655507 | Main Prison MDAS - alarm 56 is in constant alarm - dropped in water | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 10:54:20 | 2020-10-27 10:00:00 | Fail | Replace,reprogram and test PDA 056. Deliver cover for disinfecting prior to use.
MSA-DCS | WA3655539 | Hotham Laundry power point to w/machine does not work | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 10:55:07 | 2020-09-29 14:30:00 | Pass | Replaced suspect gpo in Laundry with a new one.Tested gpo and rcd ok. Test ran washing machine ok.
MSA-DCS | WA3655614 | Gate house - upstairs computer download fault | Greenough Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 11:30:36 | 2020-09-30 14:30:00 | Fail | Travelled to site and logged into Indigo on control room PC, downloaded correct footage for security and uploaded to USB device as requested. Created a Security login for Indigo to view and download footage and advised security on how to do this. Awaiting approval for Indigo workstation for downloading footage.
MSA-DCS | WA3655619 | admin kitchen Water leak under sink | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-29 14:49:00 | Pass | Replaced leaking trap and ministop.Struggled to find isolation valve for the admin block
MSA-DCS | WA3655702 | Unit 5, house 3 - bathroom GPO is cracked | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 13:30:00 | Pass | Replaced cracked power outlet in bathroom
MSA-DCS | WA3655703 | Unit 6, Cell 7 - bathroom exhaust fan not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 14:30:00 | Pass | Replaced exhaust fan
MSA-DCS | WA3655705 | Unit 4, LB oven not working, electrical fault | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-06 12:00:00 | Fail | Replaced oven element
MSA-DCS | WA3655707 | Reset building outside - 1 row of fans not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 12:00:00 | Pass | Replaced faulty fan controller
MSA-DCS | WA3655711 | Unit 6, Cell 16 - prisoner lock is binding on the key | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 12:33:58 | 2020-09-30 11:15:00 | Pass | Adjusted prisoners privacy Lock on Cell 16 Unit 6 Bandyup Womens Prison
MSA-DCS | WA3655716 | Unit 1, B13 - sink has no water pressure | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-13 16:20:00 | Fail | Removed stanless basin from wall checking for kinks and blockages ordered new tap det603
MSA-DCS | WA3655723 | unit 2 D10 toilet broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 12:40:21 | 2020-09-29 18:00:00 | Pass | Unable to get escort on arrival.Replaced broken toilet.
MSA-DCS | WA3655740 | unit 10 A & B. Shower rooms Left hand shower door won’t open faulty lock needs repair | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 12:56:22 | 2020-10-02 09:30:00 | Fail | 29/09/2020. On site. Assessed issue. Parts required.02/10/2020. Attended site. Supplied and fitted new handle.
MSA-DCS | WA3655747 | unit 10 cell C14 light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 13:00:50 | 2020-09-30 14:00:00 | Fail | Repaired light
MSA-DCS | WA3655796 | Reception- Hot water urn not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 13:30:58 | 2020-09-30 14:05:00 | Fail | COMPLETED
MSA-DCS | WA3655798 | visits centre child activity area water leaking in ceiling 3 mtrs from west wall | Wooroloo Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-12-17 14:00:00 | Fail | roof repaired to rectify leaking
MSA-DCS | WA3655800 | External stand pipe near fence is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 13:35:29 | 2020-09-30 14:40:00 | Fail | COMPLETED
MSA-DCS | WA3655804 | stores air con not working | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 13:36:51 | 2020-10-12 08:28:00 | Fail | COMPLETED
MSA-DCS | WA3655831 | Kitchen - bad roof leak (roof looks like it wants to cave in) | Karnet Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 13:54:10 | 2020-11-12 18:20:00 | Fail | ROOF HAS BEEN REPAIRED
MSA-DCS | WA3655849 | EC3-Zone 11 constantly alarming | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-19 17:54:00 | Fail | Checked Programming for zone 11 and adjusted.performed walk test and monitored, still alarming but not as frequently.calibrated and monitored.confirmed false activations have stopped.zone still activates when breached
MSA-DCS | WA3655857 | unit 4 A Wing Dayroom Door lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 14:11:23 | 2020-09-30 09:45:00 | Pass | Attended site. Repaired door furniture to restore normal function.
MSA-DCS | WA3655860 | Unit 3, D15 - Basin Tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 09:40:00 | Pass | Removed basin replacing pillar tap
MSA-DCS | WA3655911 | Unit 3 Cell 1 lock is faulty | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 14:30:00 | Pass | Replaced Lock on cell 1 Unit 3 and top door hinge
MSA-DCS | WA3655912 | Squash courts main door lock is faulty | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 12:45:00 | Pass | Replaced lock deadlatch mechanism and refitted door frame strike
MSA-DCS | WA3655952 | Zone 2 mircro receiver 6 will not reset may be out of alignment due to contact with vehicle. | Greenough Regional Prison-Security | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:42:05 | 2020-09-30 16:45:00 | Pass | Attended site and re-aligned and reset beamset for zone 2. Cleared all alarms and retested. all tested and working ok. Job complete
MSA-DCS | WA3655963 | Gatehouse/Canteen/Gate control - Multiple alarms going off, cannot isolate | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 22:14:24 | 2020-09-30 11:46:00 | Pass | Officers unable to clear alarms, checked activity report.No alarms between 1830 to 0600.
MSA-DFES | WA3655207 | front auto doors not opening | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 29 Sep 2020 | 2020-09-29 11:07:43 | 2020-09-29 10:15:00 | Pass | Technician attended the site of Cockburn Emergency Services Centre to the main entry external auto door on 29/09/2020. Following a full test and inspection of door components found that the door is working as it should. Technician has gone through and tested all of the inputs and found all to be working fine. He suspect that the issue may have been coming from the access system. After having security reset a few times door is now working. He also tested door multiple times in all modes without any issue and spoke with sontec to let them know that he suspect issue to be on their end. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3655336 | Front gate - Electric entry gate to station not closing automatically. | CFRS Belmont | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-29 15:30:00 | Pass | Technician attended the site of Belmont Fire Station, Auto Gate on 29/09/2020. Following a full test and inspection of door components found fault to be gate not operating. Technician noted gate in manual. Restored to auto operation and tested. Required to adjust slow down distance, checked time clock operation, and adjusted safetybeam. Tested all ok. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3655383 | FF dorms old section flyscreens on windows in affected areas are not sealed- see notes | CFRS Maddington | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-06 14:45:00 | Pass | Gaps around the edges of ill fitting screens sealed
MSA-DFES | WA3655631 | ground water line opp space shuttle to feed drink fountain needs to be capped off no longer in use | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 13:00:00 | Pass | Cap off water
MSA-DFES | WA3655656 | Various lights throughout the building require replacing - see list below | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-23 11:00:00 | Fail | CompleteAttended site and replaced faulty sensors and pe cell, tested and all in working order. Notified staff and signed out
MSA-DFES | WA3655937 | Bush Fire Management Risk area passage way - light is out | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-05 15:00:00 | Pass | CompleteReplaced faulty lights in hallway all in working order
MSA-DTAG | WA3655399 | 1903 L1 Registrars’ not cooling down to temp set on thermostat | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-06 17:05:00 | Fail | Pick up new fan and motor from supplier. Attend site. Take sll parts and tooling to roof. Isolate unit and tag out. Attempt to remove fan guard screws but found all seized. Dismantle unit roof to access seized screws. Remove all screws. Dissconnect motor wiring. Remove fan guard motor mount assembly. Remove motor and fan, fit new motor and fan. Replace fan guard mount assembly and connect motor wiring. Install new screws to fan guard. Fit new capacitor. Deisolate and test operation. Found new fan to work as normal, motor amps normal. Unit is now operation as normal. Clean up area and dispose of old motor.
MSA-DTAG | WA3655418 | L3 room 3.04 unable to secure room fault with card reader | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-29 14:00:00 | Pass | found strike faulty. Replaced strike (supplied by site), checked all functions, OK.
MSA-DTAG | WA3655443 | Ground Floor - Registry Office - building alarm back up is running low & keeps going off | Armadale Courthouse | GMP-BR-HO | Security | Security Management System (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 11:50:00 | Pass | 30/9/20 - Dylan Parslow, Joshua ParkFound Ademco panel powered up. Panel is obsolete.Disconnected.No call out fee as already onsite.
MSA-DTAG | WA3655693 | New pendant alarm installed is activating numerous times by itself | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 Sep 2020 | 2020-09-29 16:17:06 | 2020-10-16 11:30:00 | Fail | Replaced expander module. Monitored and tested Inputs and no more intermittent faults. All working ok.Job completed
MSA-DTAG | WA3655700 | Basement - Cell 1 - Custody require BOI clean as Prisoner has vomited in cell | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-29 18:30:00 | Pass | Job carried out as per work order
MSA-DTAG | WA3655910 | Ground, registry, rear door - Access card reader faulty | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-09-30 11:15:00 | Pass | 30/9/20 - Dylan Parslow, Joshua ParkInvestigated issues with registry rear door.Found blue terminal block for the lock power in panel faulty. Replaced and tested, all working.
MSA-DTWD | WA3655324 | L1 Back of beauty clinic Remove Graffiti (high priority Offensive graffiti) | Perth Campus B2 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 1 | CLOSE | 29 Sep 2020 | 2020-09-30 17:00:00 | 2020-10-01 09:30:00 | Fail | REMOVAL OF GRAFFITI FROM VARIOUS LOCATIONS AROUND THE L1 BEAUTY CLINIC
MSA-DTWD | WA3655341 | 838 kitchen - hot water system faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Lane's Plumbing | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 14:30:00 | Pass | Check HWS to building 838 kitchen not repairable. Return with new HWS and Replace
MSA-DTWD | WA3655359 | E block E65 Bentley Pines Restaurant – Faulty sensor in aircon | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 2 | COMPFIN | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 00:00:00 | Pass | Works completed-Work order closed out at $0 cost
MSA-DTWD | WA3655364 | Block, Building 1 - Repair Fire operation mode in conjunction with Critical Fire | Perth Campus B1 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2021-06-11 12:12:00 | Fail | Current works have been completed. Critical Fire are working on the Fire system programing and control. Once completed they will notify the campus and a new job will be raised for further testing work.
MSA-DTWD | WA3655367 | centre block L 0-8 Fire Escape Stair Repair Stair Pressurization fan controls | Perth Campus B1 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 29 Sep 2020 | 2020-10-06 17:00:00 | 2020-11-09 13:48:00 | Fail | Returned to site and completed fault finding / cable tracing after previous inspection with critical fire tech. Cable traced to control essential services pannel within the the level 1 chiller plant room. I/L safty on/off switch found in the off position preventing power to reach 240-24v control transformer required to drive relief air actuator/damper. Control was reset and power was restored to contacts and switching. Put fan into operation test mod and confirmed relief air damper operation. Checked amp draw at control transformer and confirmed that it was below safty trip setting. It is unclear if control had been left off or tripped had occured. Pannel would not have been able to be located without previous assist form critical fire when tracing cable. All equipment has been left in auto position. Damper operation restored. Work area left tidy.
MSA-DTWD | WA3655372 | Block, Building 1 - Repair Fire operation mode in conjunction with Engie | Perth Campus B1 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | FLDCOMP | 29 Sep 2020 | 2020-10-06 17:00:00 | 2021-10-27 13:26:00 | Fail | Repairs
MSA-DTWD | WA3655390 | C block ground C24 Light issues, lights flash on and off , suspect black box controller | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 14:30:00 | Pass | Replaced tubes in classroom. Parts supplied by site. Job completed
MSA-DTWD | WA3655490 | D block D3 damaged ceilng outside of room needs repair and painted | Murdoch Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 13:00:00 | Pass | Toby Bindon (30/09/2020) - Work NoteArrived at site, signed in and set up work area. Stripped back damaged plaster and prepared surface. Mixed up some patching compound and layered on. Waited untill partly dry before doing another coat. Will require a sand and final coat before painting. Please re-book for another 3 hours.Toby Bindon (01/10/2020) - Work NoteArrived at site, signed in and set up work area. Sanded back and patched over a final coat. Waited untill dry, gave another light sand and painted x2 coats. Tidy area and packed away tools.
MSA-DTWD | WA3655568 | T block ground male toilet leaking | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 13:08:00 | Pass | REctify toilet issues
MSA-DTWD | WA3655574 | A block disable toilet is blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 13:09:00 | Pass | unblocked toilet
MSA-DTWD | WA3655665 | 818 - electrical mains box faulty | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 13:45:00 | Pass | Job completed - replaced faulty mains box
MSA-DTWD | WA3655782 | A block, Ground, Corridoor AF26 - Wooden floor boards cracked in front of AF26 | Fremantle Campus (formerly WA Maritime) | GMP-BR | Flooring | Timber (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-02 10:45:00 | Pass | Repaired floor boards
MSA-DTWD | WA3655930 | BLD 832 - level 1, Hallway - faulty fluro light | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 12:45:00 | Pass | Job completed - repair faulty light
MSA-DTWD | WA3655934 | Homestead BLD 833, Kitchen - faulty tap | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 29 Sep 2020 | 2020-10-02 17:00:00 | 2020-09-30 13:00:00 | Pass | Job completed - Repair faulty taps to Home stead Kitchen
MSA-DCA | WA3656304 | Beauford street wall graffiti needs to be removed | Art Gallery of WA - James St - Administration Block (Block A) External North | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-01 14:45:00 | Pass | job completed - Graffiti Removal
MSA-DCA | WA3656311 | Reticulation leak | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Materials (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 15:00:00 | Pass | job completed - Identified leak location and cause- Fix broken sprinkler riser that was cracked- Test zone after and it was in full working order.
MSA-DCA | WA3657340 | Low steam generator alarm | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Package (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 16:30:00 | Pass | Common low steam pressure alarm. Low steam pressure steam boiler 1, low steam pressure steam boiler 2. All pneumatic plant in operation. No faults. Steam Boilers 1 and 2 tripped on low gas pressure safety. Fire alarm was activated during demolition works prior to alarms on steam boilers. Too many individual alarms being caused by different problems to identify mains gas pressure as the cause. Will be monitoring further to see if mains gas pressure is the cause or if these individual issues from works causing faults.Closed job.
MSA-DCA | WA3657566 | Fire panel on ground floor continuous faults relating to current building works. | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Foyer | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 13:45:00 | Pass | Attended site and found the following.1: 91 alarms/isolated across loops 1,2,3,& 42: Perth fire had fitted a new loop card to loops 3&4 yesterday to see if causing alarms.3: Checked panel earth monitoring found turned off, re enabled and found panel to have earth fault.Traced earth fault to loop 3. Earth faults will generate false alarms.Loop three covers level 1,2,3 & lift motor room.Checked and found readings to earth on loop.4: Panel has 522 isolated devices.5: Found one Vesda in fault on network Level 4 Conservation has been disconnected due to building works.6: Collections acquisition store has Vesda detector missing in new building works area.Worked through loop 3 to try and trace earth fault note legal 1 had a water leak in the area.While tracing fault it cleared.Possible due to water leaking into detectors on level 1.Site to sort out 522 isolated.As instructed by PFM de isolated all devices and left Gallery security to isolate what is requiredIsolated Level 3 mal
MSA-DCS | WA3656064 | SOG senior officers office light globes blown not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 10:00:00 | Pass | Repaired light
MSA-DCS | WA3656073 | Abattoir faulty electric sheep stunner | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 09:00:00 | Pass | Investigate and repair abattoir sheep stunner
MSA-DCS | WA3656075 | gate house cell call has a fault and cannot clear | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Sep 2020 | 2020-09-30 15:45:18 | 2020-09-30 09:00:00 | Pass | Contacted Control officer who advised cell call constantly going into alarm, asked if they could answer cell call or cancel, officer advised that they couldn't. Asked them read entire description on Ci3210.Duress alarm MPC.Advised this officer this is a fixed duress button along the MPC corridor, asked if they could reset this. Advised it had already been done.Contacted security and askes them to reset, button had been pressed and reset cleared alarm.No further action required
MSA-DCS | WA3656083 | Amenities - Male Changeroom missing floor tile in front of shower | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 3 | CLOSE | 30 Sep 2020 | 2020-10-06 17:00:00 | 2020-10-09 14:45:00 | Fail | NEW TILES LAID
MSA-DCS | WA3656087 | Abattoir elements on smoke oven not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Sep 2020 | 2020-10-02 17:00:00 | 2020-10-01 11:30:00 | Pass | Investigate and repair abattoir smoke oven not working.
MSA-DCS | WA3656094 | Jasper, A05 - Cracked cell window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-06 12:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3656095 | keywatcher light broken needs to be replaced as is dark | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 08:04:39 | 2020-09-30 15:00:00 | Pass | Replaced LED light fitting
MSA-DCS | WA3656127 | Kitchen stores - shattered window | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 08:26:51 | 2020-09-30 13:30:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3656155 | Unit 8, C5 - Drain Blocked, over flowing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 08:51:11 | 2020-09-30 15:30:00 | Pass | Drain rod used to unblock floor waste
MSA-DCS | WA3656171 | Unit 4 C13 main broken light. | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 12:00:00 | Pass | Replace broke light U4
MSA-DCS | WA3656176 | HR and Security offices Air Conditioner controller not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 15:00:00 | Pass | Repaired faulty connection to wall controller. Ran unit up in all modes successfully. Operational at time of departure.
MSA-DCS | WA3656251 | Laundry washing machine No4 Steam Leak Internally | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 09:45:42 | 2020-10-02 09:50:00 | Fail | AMS701572 WA3656251 - Hakea -No 4 WM - Steam leaking inside.1/10 - Inspect and test machine, steam hose split.Order new hose and fittings.2/10 - Return to site supply and fit new steam hose and fittings.Test washing machine operation, tests ok
MSA-DCS | WA3656268 | Level 4, store room door - self closer faulty, not self closer | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-09-30 12:00:00 | Pass | Attended site and carried out repairs to the hydraulic closer on the store room door.
MSA-DCS | WA3656316 | Unit 4 A4 Personal light cover is broken - see notes | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-02 12:00:00 | Pass | Investigate and replace unit 4 A4 bed light & cover.Light Cover used stock on site
MSA-DCS | WA3656373 | Unit 2 D10 Cell Call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 10:59:56 | 2020-09-30 15:30:00 | Pass | No activation when call button pressed. Removed intercom and found speaker/switch plug loose. Repaired plug. Stripped and cleaned intercom of toothpaste. Secured and tested ok loud and clear in cell and in the control room. Parts used:Consumables
MSA-DCS | WA3656379 | kitchen Rational Oven No1 Not Working fault showing as NO FUNCTION on screen | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 11:03:30 | 2020-10-01 11:45:00 | Fail | Returned and replaced fan motor & tested ok.
MSA-DCS | WA3656384 | unit 1 A wing cell A16 GPO and light switch faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 15:30:00 | Pass | Replaced cracked light switch and power point
MSA-DCS | WA3656388 | Main Laundry middle dryer not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-11-25 13:55:00 | Fail | Found overload tripped - reset - test motor, loose, motor spinning on rubbers. Suggest replace motor - BRA forwarded 13/10/20 no reply as of 29/10/20
MSA-DCS | WA3656417 | CCU (11) - D4 sprinker needs to be reinstated following transfer of prisoner housed in cell. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-05 15:15:00 | Pass | drain system - reinstated 2 sprinkler heads as requested - refill system
MSA-DCS | WA3656419 | Pre Release Unit 4 - double side gates the stopper has been damaged | Bunbury Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 11:13:06 | 2020-10-01 12:00:00 | Fail | 01/10/20Replace damaged gate stop.Repair concrete.
MSA-DCS | WA3656741 | Master Control Pod - Computer Alarm Screen Not Working Blank | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 11:25:41 | 2020-09-30 16:00:00 | Pass | Attended site checked and found access and security Control workstation 02 right hand side monitor is showing blank. Located problem to be workstation itself. Restart workstation and EBI programme and tested all ok after.
MSA-DCS | WA3656768 | unit 1 A2 Vinyl flooring lifting | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-22 14:45:00 | Fail | DAMAGED VINYL REPLACED
MSA-DCS | WA3657330 | Towards rear of building 4 cupbards doors need to be re-hung after falling off | East Perth-Main Building-Level 4 | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-07 13:00:00 | Pass | Attended site and carried out repairs to the damaged hinges on cupboard doors.
MSA-DCS | WA3657333 | Meeting room - rear of building Rubber strip has come off the window | East Perth-Main Building-Level 4 | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-07 11:00:00 | Pass | Attended site and carried out repairs to the insertion rubber in aluminium frame that was falling out
MSA-DCS | WA3657336 | Meeting room - clock has fallen off the wall - please re-hang | East Perth-Main Building-Level 4 | WSM-BR-SITE | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-07 12:00:00 | Pass | Attended site and installed digital clock to the meeting room wall.
MSA-DCS | WA3657355 | ktichen robo coupe the blades damaged | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-16 12:30:00 | Fail | Kitchen robo coupe (CL50) blades damaged. Check slicer & blades. Order replacement blades & screw. Pickup new blades & return to kitchen staff.
MSA-DCS | WA3657377 | Reception - Sally Port Security require CCTV footage to be downloaded by SEME from Recept sallyport | Casuarina Prison | WSM-MW-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-05 09:30:00 | Pass | Attended security office to get details of video required. Attended Gatehouse Equipment room to review video required. Unable to locate video on Gate Control DVR as “Recorded Monitor” was not displaying video from the Sally Port. No video available. Advised Security Manager.
MSA-DCS | WA3657401 | Administration - Staff toilet leaking-contractor on site | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2021-09-16 12:30:00 | Fail | 27/11/20 : organised with maintenance to have shelving removed so we can gain access to duct to complete works for 1/12/201/12/20: shelving has not been removed, cannot get access to duct , try again for tomorrow 2/12/20: 8am , shelving still up, job has been rescheduled for 7/12/20 as we have organised other works for 2/12.16/12/20: shelving still up in cleaners cupboard in front of duct, unable to access, maintenance asked to remove shelving on 27/11/20 in order for us to complete work, have asked more than once so they are aware it needs to be taken down.17/12/20: still no access, shelving still up in cleaners cupboard blocking access to plumbing duct 21/12/20: shelving still up , no access22/12/20: shelving has not been removed, no access23/12/20: works can’t be completed today as we have multiple priority 1 jobs around the prison to compete today and shelving is still up so there is still no access anyway.5/1/21: shelving still up , no access7/4/21 : shelving sti
MSA-DCS | WA3657423 | unit 1 cell call in cell 5 goes to control room but cannot hear but can in gate control | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 12:14:00 | Pass | Tested cell call, no fault found. Checked handset and confirmed cables are connected correctly and no loose cabling.Checked multiple cell in unit 1.All working correctly.Cleared all faults on Cell call system
MSA-DCS | WA3657431 | Unit 9, A & B wing Dayroom - Hot water urn faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 13:59:29 | 2020-11-11 09:25:00 | Fail | Replaced, commissioned and tested unit.Installed New Capex Asset Rheem BWU WM 40L 70240S-AU Serial N 142 Prog Number A401889226Lclient did not want Maxiflow System installed due to safety issue as can be accessed.
MSA-DCS | WA3657482 | Kitchen - Faulty BRAT Pan | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 14:36:42 | 2020-11-25 17:00:00 | Fail | 01/10/20Called as requested to the unit pan not lifting. Found the what appears to an air pocket or the release solenoid not closing off correctly so will order a new solenoid valves and new oil. Parts Required:1 x Solenoid valve 1 x Hydraulic Oil 25/11/20Attended kitchen. Removed oil tank and solenoid. Found the oil was contaminated, cleaned out tank and replaced solenoid. Filled old tank and primed pump. Checked for leaks and operation of the unit.
MSA-DCS | WA3657506 | Unit 1, B wing - ablutions block closet to control - no hot water to the showers | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 15:15:06 | 2020-10-01 14:00:00 | Pass | Job complete
MSA-DCS | WA3657528 | Image flickering across all CCTV monitors | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-12-02 16:00:00 | Fail | Adjusted screens and installed 2x monitor desk mount for all security monitors installed cable management for security cables adjusted indigo rights and mover 3 video wall monitors on to one workstation (running at 94% CPU)
MSA-DCS | WA3657534 | Excess water on driveway, blocked storm water drainage | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-11-18 14:30:00 | Fail | SEE ATTACHED SUPPORTING DOCUMENTS
MSA-DCS | WA3657563 | SOG - Fire alarm panel has gone into fault and won't reset. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Sep 2020 | 2020-09-30 21:12:56 | 2020-09-30 21:10:00 | Pass | 30/9/20 JN - Hakea SOG (Tyco MX)Conventional zone 10 went into fault on 29/9. No block plan and no location description on panel. Old paperwork shows Z10 could possibly be plant room zone. Zone reset on arrival and did not come back into fault monitored for half an hour to make sure. If fault returns will have to verify where Z10 detection is and fault find further. Panel currently in normal condition
MSA-DFES | WA3657419 | Station, ground TV/training room - light switch not working | CFRS Osborne Park | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-05 15:00:00 | Pass | laced faulty switch mech and dimmer nob.
MSA-DFES | WA3657427 | ground kitchen/courtyard-roller duel mesh security doors worn out - see notes | CFRS Kiara | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-01 15:00:00 | Pass | Toby Bindon (01/10/2020) - Work NoteArrived at site, took measurements for rollers on door. Picked up materials. Returned to site, the guys had been calledout no sender at door or phone. Returned later in the day, removed doors and removed hook bar on the the right handdoor so I could get it off the track. Removed old rollers x4 in total. Installed x4 new rollers. Riveted into place. Reinstalled doors and lock bar. Stop strip on the outer of each door where loose. Replaced fixings in strips to tighten upand stop rattling. Adjust door height so lock bar lined up with latch. Works smoothly now. Tidy area and packed away
MSA-DFES | WA3657442 | Main building, ground floor - Fluoro light above Craig Scott’s desk (see att) is not working. | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-11-20 10:00:00 | Fail | Attended site and located non working lights on ground floor, replaced various globes all in working order. Will need to order parts and a light in training room 2Attended site and replaced faulty downlight. Tested and all in working order notified staff
MSA-DFES | WA3657520 | Applied training ground - Charging lead for Golf Buggy has become detached from connection point. | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 14:30:00 | Pass | Continued on site at 13:30 to repair golf cart charger. Found cable had been pulled out of roof. Refitted off outlet tested and continued on site at14:30
MSA-DTAG | WA3657323 | Ground, Security admin - Battery back-up did appears to have not activated (see long description) | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 16:00:00 | Pass | Checked UPS and tested operation. Both passed test with mains fail. But with one UPS 60% load showing 32 mins and other with 25% load showing 3 hours. Possible batteries require replacing.
MSA-DTAG | WA3657362 | Court 2, ground level - Air con in court is too cold. Occupants would like it slightly warmer | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 16:00:00 | Pass | Attend site. Access court 2 and check temps. Found court to be 21.8 degrees with a setpoint of 22. Check operation of ac unit and found to work as normal. There is a manual setpoint adjustment in court 2. Change setpoint to 23 degrees. Monitor temp and found to rise. Leave note for judge about setpoint adjustment on wall behind judges chair.
MSA-DTAG | WA3657474 | 1903 Ground, 1987 levels 2 & 3 - Isolate FIP Saturday 3 Oct from 7.00am - 17.00 hours- see notes | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-03 17:30:00 | Pass | 03/10/200700Isolated zones 7-11, 12-14 and zone 19 on main FIP. Isolated zones 3-4 and 7-8 on building 87 SIP.1730Deisolated all zones panels back to normal
MSA-DTWD | WA3656068 | D block security panel will not arm up | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 0 | CLOSE | 30 Sep 2020 | 2020-09-30 11:34:12 | 2020-09-30 09:45:00 | Pass | Attend site to investigate fault on D Block, upon visiting site found the campus doing a full network upgrade and the system is down currently and won’t be up for a day or two. Unable to proceed with getting our system online while theirs is offline. TAFE has also requested a wiring diagram
MSA-DTWD | WA3656099 | campus master key broken B13 keys (5) | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-06 07:30:00 | Fail | Job completed - keys crushed bent
MSA-DTWD | WA3656111 | A block, Level 2, Plant room - AHU 2 has stopped working | Leederville Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Precise Air Group | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 14:00:00 | Pass | Attended site and found a public holiday scheduled for today. Cleared the holiday schedule and the AHU and RAF started
MSA-DTWD | WA3656239 | block 10 ground male toilets Ceiling needs water damage repair. | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-16 13:00:00 | Fail | Ceiling damaged by leaking from the toilet on the floor above. Removed damaged section of ceiling, replaced with new and patch painted
MSA-DTWD | WA3656263 | Main Entry off Aberdeen St, Doors making noises when closing | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-23 10:14:00 | Fail | Inspected and tested door and found gear is noisy while operating, quotation required for new belt drive gear box only.Programmed IP no A402133259Returned to site and replaced faulty belt drive gearbox as per quote, tested all ok
MSA-DTWD | WA3656309 | L1 25 Ab carpark bay 17 Pipe leaking in carpark | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-05 14:00:00 | Pass | Repair burst pipe
MSA-DTWD | WA3656314 | Block D Level 1 - Fire panel - Zone 1 in alarm, needs to be cleared but isolated | East Perth Campus | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-09-30 15:30:00 | Pass | False alarm from beam device recommend revoming or fixing device
MSA-DTWD | WA3656358 | Block 8 ground Main power switch in main switchboard tripping | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-11-30 19:28:00 | Fail | BRAF Declined invoice costs to date
MSA-DTWD | WA3656439 | Level 4, plant room - Hot water system not working properly | Perth Campus B6 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-02 12:18:00 | Pass | Attended site gained access and carried out inspection of BMS and reported heating water system. Please note that reported equipment is for domestic hot water system and not linked to BMS or base building plant. The equipment is located in the L4 plant room. Site facilities have been advised.
MSA-DTWD | WA3657356 | blocks T, U and V cannot access the BMS | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Icon Logic Pty Ltd | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-06 11:15:00 | Fail | job completed - replaced CAT 6 lead to p
MSA-DTWD | WA3657375 | Front Toilet next to AT202 (Program managers office)(blocked, out of service tag) - Blocked toilet | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 11:19:00 | Pass | Unblocked toilets
MSA-DTWD | WA3657408 | B block B2417 damaged GPO | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-09-30 15:20:00 | Pass | Repalced faulty gpo in room. Job completed
MSA-DTWD | WA3657448 | main office and entrance fire panel ews problem please investigate | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-12-18 10:30:00 | Fail | Main ewis cpu board replaced in Tower Ewis system
MSA-DTWD | WA3657449 | G block - boiler for G block faulty over heating | Rockingham Campus | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 10:20:00 | Pass | Attended site, checked boiler operation, no faults found on the boiler.The problem is the temperature control within the building.This looks like a BMS problem.
MSA-DTWD | WA3657451 | B block ground B10 Room "E" Stop box damaged and switch not operating correctly | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-10-02 15:00:00 | Pass | Replaced faulty e stop and tested
MSA-DTWD | WA3657470 | L1 S block S123 Repair Pin lock broken - See Steve Meyer for details | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-01 16:05:00 | Pass | Remove and replace faulty mortice lock, lever handles and key barrel to door S123
MSA-DTWD | WA3657510 | D Block Ground Floor D3 - faulty sensor - false alarms from this room | Bentley Campus | GMP-BR | Security | Monitoring (SE) | CONNECT SECURITY SYSTEMS | 3 | CLOSE | 30 Sep 2020 | 2020-10-07 17:00:00 | 2020-10-06 11:16:00 | Pass | Found sensor to be zone 3 located in Room D1, not D3. 23 year old PIR at end of working life. Replaced with new dual tech and retested. Plan updated off site to show correct layout and sent to DoE Security and Bentley Campus Manager.
MSA-MRWA | WA3656284 | amenities Instant Boiling Water Unit is not working properly - see notes | Materials Engineering Branch-Admin Building-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 30 Sep 2020 | 2020-10-05 17:00:00 | 2020-09-30 16:27:00 | Pass | System off on arrival and not getting hot. Element seems fine, filter not blocked. Solenoid needed replacing. Replaced solenoid and waited for system to fill up and get to temperature. Normal operation
MSA-MRWA | WA3657265 | water logged lights | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-812-Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 30 Sep 2020 | 2020-10-01 17:00:00 | 2020-10-01 17:30:00 | Fail | Attended site and replaced water damaged light fittings and motion sensor.Tested and everything is working correctly now.
MSA-DCA | WA3660628 | issue with the steam boilers gas supply | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-02 13:00:00 | Pass | Steam Boilers 1 and 2 faulted on low gas pressure alarm. Reset and monitored cycles. Alarms cleared. Contractors on site the previous night were carrying out works to fire monitoring sytem due to various alarms. During works they had 4 individual fire alarms activate over the time span that we had the Steam Boiler faults. Boilertronics to attend site and confirm or adjust if required supply gas pressure and safety.On going.Boilertronics found no issues with gas pressure or settings.Closed job.
MSA-DCS | WA3660068 | Bakery prover door had dropped - Please attend today | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 07:53:56 | 2020-10-01 15:00:00 | Pass | completed 1/10
MSA-DCS | WA3660076 | Unit 4 - C1 mortace lock is very hard to engage with unit keys | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 13:30:00 | Pass | Requires lock rebuilt.Remove edge capping and lock, rebuild lock in workshop, re install lock and edge capping with new fixings.
MSA-DCS | WA3660078 | Unit 5, C wing, C1 - C8 - ceiling lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-26 15:00:00 | Fail | Investigated faulty lights circuit in unit 5. Found faulty contactor. Made temporary repair. Ordered replacement, picked up and installed in switchboard
MSA-DCS | WA3660089 | Unit 7, A wing - alarm on freezer keeps sounding | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-27 14:37:00 | Fail | Isolated freezer,remove faulty pc board,fit new pc board,turn power back on and tested all running ok at present.
MSA-DCS | WA3660095 | Unit 1, A wing - Wing office dooor lock striker is stiff and not retracting | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 08:14:49 | 2020-10-01 09:50:00 | Pass | Replaced faulty / broken lock on Unit 1 a wing office door
MSA-DCS | WA3660101 | Unit 5 - Control Room air con covers are falling apart held together by sticky tape | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-05 10:00:00 | Pass | New cover no longer available. Secured cover using screws. All ok.
MSA-DCS | WA3660247 | Kitchen, opposite ovens - push sink tap wont turn off (tap is isolated) | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 08:31:55 | 2020-10-01 14:10:00 | Pass | Adjusted and modified bent push button tap
MSA-DCS | WA3660544 | Ground level, Main Hall, female toilet at rear of Hall - Water leaking from female toilet - at joint | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 14:50:00 | Pass | COMPLETED
MSA-DCS | WA3660545 | kitchen small combi oven not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 08:49:41 | 2020-10-01 15:25:00 | Pass | Clean level electrode ok, drain & refill ok. check diagnostics, found b5 sensor max at 180c. Reset ok.
MSA-DCS | WA3660547 | kitchen bakers oven turning off at 270c and not coming back on | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 08:51:23 | 2020-10-14 16:00:00 | Fail | Completed 14/10/20
MSA-DCS | WA3660602 | Main Kitchen, Bain-Marie - faulty water level swtich. Beeping sound when unit is turn on | Nyandi Training Academy | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 11:00:00 | Pass | 02/10/20Arrived at site liaise with reception, identify Bain Marie, isolate remove panels test/fault find diagnose and found the water level sensor was alarming while the unit as full of water, tested and found calcium build up all over float switch attempted to clean calcium off to free up float but will still require replacement, Will also require a 2nd technician for assistance with replacing the float mechanism. And needs to be on a Friday at 2pm so that the silicone can dry over the weekend 1x float mechanism switch Arrived at site liaise with kitchen, identify Bain Marie (completed on job # 18570)
MSA-DCS | WA3660636 | Crisis care unit cell H9 Cell call not working needs repair | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 07:59:46 | 2020-10-01 09:00:00 | Pass | Tested and working as normal, job completed.
MSA-DCS | WA3660648 | Gatehouse - Key watch not working. | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 06:39:53 | 2020-10-01 11:00:00 | Pass | Job complete
MSA-DCS | WA3660650 | zone 10 mircowave been in alarm all morning -see notes | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-01 14:30:00 | Pass | Job complete
MSA-DCS | WA3660699 | Unit 13 - B & D-leaver on urn broken off - see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 10:33:54 | 2020-10-02 09:48:00 | Pass | Tap broken and no water on arrival, had to isolate power and drain existing water. Fixed screen that had fallen down. Replaced tap and waited for unit to fill and get to temperature. Normal operation
MSA-DCS | WA3660708 | Unit 14 - D Wing shower leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 08:30:00 | Fail | Nill
MSA-DCS | WA3660721 | Unit 2 C7 shower tap leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-01 15:12:00 | Pass | Turned off water and Replaced qutar turn tap
MSA-DCS | WA3660725 | front gate fire panel Showing Faults N-1 L3M81 & N-1 2053 Holding Cell | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 11:06:56 | 2020-10-02 11:03:00 | Pass | vesda fault - cleared sampling point - all ok on departure
MSA-DCS | WA3660729 | Health - Toilet & sink block solid again | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-02 10:30:00 | Pass | Clear blockage to sewer line
MSA-DCS | WA3660744 | Unit 2 D1 Sink Taps Leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-01 16:05:00 | Pass | Turned off water replacing qutar turn tap on cold
MSA-DCS | WA3660813 | Unit 2, Lower landing - GPO faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-01 15:00:00 | Pass | Investigate and replace faulty gpo in unit 2 lower landing
MSA-DCS | WA3660860 | unit 10, A5 - sink leaking underneath U bend | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 12:21:22 | 2020-10-02 07:40:00 | Pass | Removed outlet on basin replacing orings and retightend outlet
MSA-DCS | WA3660862 | Unit 1 - A9 Putty around the footing of the bed and wall fixing has been picked out | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 13:15:00 | Fail | NEW SEALANT ADDED
MSA-DCS | WA3660870 | Unit 10, C6 - Porcelain sink Broken Smashed, sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 12:25:42 | 2020-10-02 10:17:00 | Pass | Removed old sink replacing with new and new one
MSA-DCS | WA3660875 | Unit 3 PA system is not working | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 12:26:44 | 2020-10-01 14:15:00 | Pass | Actual job start time is 10:45am. Checked and found Unit 3 PA not working at all. Located problem to be speaker line fault. Rectified the fault and tested all ok. Leave spare amplifier got from office on site as site spare. ZA-6120
MSA-DCS | WA3660879 | Unit 1, B11 - Broken Window wire, Holding wire on the window has been pulled out of the frame | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 10:30:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3660882 | Unit 1 - B8 Both the main and inspection lights are not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 09:00:00 | Pass | Investigate and repair unit 1 cell b8 lights
MSA-DCS | WA3660885 | Uni 10, Day room - sink U bend broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 12:34:14 | 2020-10-02 08:33:00 | Pass | Replaced plug and waste and 50mm trap on kitchen
MSA-DCS | WA3660890 | U7 S Wing cleaning cupboard Handle on tap snapped off needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 12:37:25 | 2020-10-02 13:15:00 | Fail | Shit off water and rewasherd x2 taps with new valves and orings
MSA-DCS | WA3660900 | Unit 1 - B1 door seal has been bent out of the frame leaving exposed metal and screws. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 11:00:00 | Fail | SEAL REMOVED, LOOSE METAL AND SCREWS REMOVED AS WELL. NO NEW SEAL REQUIRED
MSA-DCS | WA3660906 | laundry eye wash station not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 12:51:28 | 2020-10-02 14:30:00 | Fail | Pulled apart eye wash station cleaning all air rader and adjusting flow
MSA-DCS | WA3660916 | Unit 4 B1 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 10:30:00 | Pass | Replace broken light Unit 4 B1
MSA-DCS | WA3660919 | unit 4 B5 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 09:00:00 | Pass | Picked up new light and replaced broken light U14 B5
MSA-DCS | WA3660942 | Unit 9, C16 - Cell call no volume | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 13:15:46 | 2020-10-01 16:00:00 | Pass | Clean the cell call front plate, test the cell call ok back to normal operations.
MSA-DCS | WA3660947 | Unit 9, D1 - Cell call no volume | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 13:18:09 | 2020-10-01 17:30:00 | Pass | Cell call unit was vandalised, replaced with new and tested ok. Job completed.
MSA-DCS | WA3660954 | 2A kitchen fridge over heating | Wooroloo Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 13:21:14 | 2020-10-02 12:00:00 | Pass | Compleated
MSA-DCS | WA3661077 | Investigate sudden increase in water usage | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-01 18:35:00 | Pass | Boiler valve not shutting off. Boiler guys ok site
MSA-DCS | WA3661100 | Unit 1, B wing b9 & b30 - cracked windows panes | Bandyup Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-07 10:30:00 | Fail | REPLACED 2 WINDOW PANES
MSA-DCS | WA3661130 | Transponder 7 perimeter - constantly activating. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-02 10:38:00 | Pass | Job complete.Used Seme stock .Part#: EA102A-304. Bosch receiver .
MSA-DCS | WA3663577 | Investigate sudden increase in water usage | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 3 | CLOSE | 01 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-01 20:45:00 | Pass | Investigate valve not closing on drain line, trace out and check water, remove tubing clean out water blockage to getwater flowing to close valve, button up and return to service.
MSA-DFES | WA3660756 | Grounds in front of Administration Building - Glass on in ground flood light broken. | FESA RHQ - Forrestfield | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-21 09:42:00 | Fail | Made safe light glass fitting... SPOKE WITH MICHELLE BRANCH FROM PROGRAMMED AND SHE HAS REQUESTED US TO CLOSE OF WORKS AND CHARGE OUT COST TO DATE AS GLASS PANEL COULD NOT BE SOURCED****ATTENDED SITEMADE SAFE BROKEN GLASS TO LIGHT6.38 CLEAR LAMINATED SAFETY GLASS 1-196 mm DIAMETER4MM CLEAR 1-178 mm DIAMETERPLUS SAFETY FILM AND SILICONE
MSA-DFES | WA3660787 | L1 ladies bathroom door broken | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-02 08:00:00 | Pass | Door closer arm fitting had come loose. Re-tightened, now operating correctly
MSA-DFES | WA3660951 | Hot water system on roof - has sprung a leak, water running the roof into gutters into the drain | CFRS Maddington | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-01 15:05:00 | Pass | Inspecting the leak on solar hot water system.
MSA-DFES | WA3661145 | North East Region CESM Office, - Crackling sound heard from the wall light switch when turning on/of | DFES Regional Office - Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 15:30:00 | Pass | CompleteReplaced faulty switch in end room on the right
MSA-DTAG | WA3660694 | Level 5, Disabled public toilet (opposite courts 53 & 54) - has loose taps on the hand basin | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 13:50:00 | Pass | COMPLETED
MSA-DTAG | WA3661081 | Assist in user privilege and access assignment for level 31 | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-02 10:30:00 | Pass | Assist in Users privilege and access groups for Level 31
MSA-DTAG | WA3661095 | L4 Interview room 4.2 Check A/C air flow – temperature is not consistant | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 12:45:00 | Pass | Attend site. Access level 4 and check temps. Found temps to be inconsistent between area served by VAV box. Found to be airflow issue. Carry out airbalance to even flows between rooms. Check sensor calibration and found to be ok. Monitor operation after adjustment and found temps to now be even. Ac working as normal.
MSA-DTWD | WA3660024 | D block L1 plant room Repair tripped fuse to Black Water Treatment plant | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 01 Oct 2020 | 2020-10-01 17:00:00 | 2020-10-01 14:08:00 | Pass | Haddow Electrical Repaired tripped fuse whilst on site - Charged hourly Instrument Technician rate $180.00 x 4 Actual hours + $23.00 parts - NO TRAVEL CHARGED already at
MSA-DTWD | WA3660608 | A block, 1st floor, A49 - Water is leaking all over the bench and running onto the floor in the | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-13 11:37:00 | Fail | Installed new hot water urn
MSA-DTWD | WA3660758 | T block L1 T114 same damaged lagging on the hot water pipes to the air conditioning unit | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-06 11:30:00 | Pass | Redfern industries attended site and replaced section of pipe insulation
MSA-DTWD | WA3660768 | Building 7,Main entrances student lunch room - Weather / insect plastic curtains damaged and missing | Thornlie Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-20 15:30:00 | Fail | Replaced insect doorway screen with new
MSA-DTWD | WA3660845 | Level 4, plant room - Hot water system not working properly | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-15 09:39:00 | Fail | Hot water investigation.
MSA-DTWD | WA3660852 | Outside BLD 876 - Piggery water meter faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-08 17:00:00 | Fail | Replaced meter
MSA-DTWD | WA3661099 | A block Arming Panel to A144 and Student Services has comms error | Leederville Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 01 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-02 08:30:00 | Pass | Reset NESS GSM. Tested through to monitoring station. Signals received.
MSA-MRWA | WA3660820 | Wall port 64 does not connect to patch panel port 64 - see notes | Jandakot Depot-Main Building-Ground Floor-IT Server Room | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 15:30:00 | Pass | Arrived on site. Have been informed by staff that IT has been modifying patching in Comms room and as a result port 64 now does not have access to domain 2 server. Will have to return in after hours time to investigate further as port 64 is still patched in to network switch and may be mislabelled for a different port resulting in potential loss of internet for staff.
MSA-MRWA | WA3660835 | White Storage Shed - Remove and dispose of four (4) 1000L Bulktainers | Materials Engineering Branch-Sign Yard Shed-Ground Floor | GMP-BR | Waste Management | Waste Removal (WM) | Veolia Recycling and Recovery Pty Ltd | 3 | CLOSE | 01 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-13 10:30:00 | Fail | FIELD JOB COMPLETED
MSA-MRWA | WA3661142 | Room 510, power board need reattached to the wall. Kitchen area, light fitting not working. | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor-Open Office Area-West Side-Station 510 to 520 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 01 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 08:45:00 | Pass | Attended site and signed in. Located open area 510, checked out under all desks for damaged or broken outlets. Found 1 x data at Sam grant desk to have broken mounting block. Replaced mounting block. Found mounting block to Maria’s desk to be loose. Removed and refitted to skirting duct.All other desks okay. Inspected kitchen light and found light to be working okay. Checked operation and inspected tombstones for correct connections. All okay. Job complete
MSA-DCA | WA3661415 | main entrance fire panel needs to be isolated due to works - see notes | King Street Arts Centre-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-05 14:45:00 | Pass | 08:00Isolated zones 1 to 20 to allow full building spraying/cleaning to be carried out.13:45Check and de-isolate system after spraying works completed.Leave system in normal working order.
MSA-DCA | WA3661660 | high humity and low temp reader in stacks - Craig Hogan if Possible | State Library of WA-Main Building-Level 5-Office - Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Oct 2020 | 2020-10-05 17:00:00 | 2020-10-06 11:03:00 | Fail | COMPLETED
MSA-DCS | WA3661266 | Rear door to the gate house not operating electronically. | Karnet Prison Farm | GMP-BR- HO | Electrical | Materials (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Oct 2020 | 2020-10-02 09:46:46 | 2020-10-02 11:00:00 | Fail | Attended site checked and found sally port door not responding to Control. Further check found fuse for the power to door blown. Tried to replace fuse but it won’t last long. Checked with technician who worked on the lightening strike damage to site before and found sally port and monitor room door lock still need to be further check on existing job. Problem will be fixed on existing job, this job completed.
MSA-DCS | WA3661268 | Control Room - CCTV Indigo-2 not working | Albany Regional Prison-Administration and Visitor Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Oct 2020 | 2020-10-02 13:57:00 | 2020-10-02 09:30:00 | Pass | Attended Albany Prison control room, confirmed Indigo Workstation 2 PC not operating. Attended Equipment room, powered off the workstation, repowered and restarted workstation. Logged into IndigoVision and loaded CCTV images, configured monitors.
MSA-DCS | WA3661342 | Rational oven connot program not able to cook | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 02 Oct 2020 | 2020-10-03 07:24:03 | 2020-10-02 11:20:00 | Pass | Adjusted door and continued abort cleaning cycle. clean cycle failed last night due to this issue. Tested ok
MSA-DCS | WA3661383 | MPU (8) - M10 Obs light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 08:30:00 | Pass | Repaired faulty lights in mpu m10
MSA-DCS | WA3661388 | Unit 14 - C Wing shower constantly leaking down the wall, requires plumber to repair. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 09:30:00 | Fail | Nill
MSA-DCS | WA3661391 | Unit 13 - A & C oven in water drain in oven is blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-07 10:30:00 | Pass | Nikl
MSA-DCS | WA3661418 | Unit 10 - Water pipe leak | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Oct 2020 | 2020-10-03 08:32:43 | 2020-10-02 12:10:00 | Pass | Replaced section of burst pipe and reconnected with new
MSA-DCS | WA3661421 | Unit 10 A & B Storeroom - Water pipe leak | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Oct 2020 | 2020-10-03 08:35:55 | 2020-10-02 09:25:00 | Pass | Shut off hot water and replaced hot tap only
MSA-DCS | WA3661429 | gate house zone 13 omnitrax only activating from the far end (13/14 end) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-11-24 19:04:00 | Fail | Checked and adjusted calibration. Tested OKJob Complete
MSA-DCS | WA3661522 | education kitchen sink waste pipe leaking in the ground outside externa brick work | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Oct 2020 | 2020-10-03 09:49:24 | 2020-10-02 11:45:00 | Pass | Overflow relief gully at rear of education building full of sand creating a blockage on kitchen waste line. I removed the sand clearing drain. All working fine.
MSA-DCS | WA3661525 | Reception area - internet port has beeen pushed into wall | Rockingham Justice Complex | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-05 12:00:00 | Pass | Repaired data outlet and checked cable for continuity to data rack.
MSA-DCS | WA3661662 | Unit 1, Cell B22 - faulty lights | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 12:30:00 | Pass | Investigate and repair cell light unit 1 cell b22
MSA-DCS | WA3661663 | Unit 4, Cell K41 - Faulty fan | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 14:00:00 | Pass | Investigate and repair faulty fan unit 4 cell k41
MSA-DCS | WA3661666 | Unit 4, Cell L48 - Faulty fan | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 15:30:00 | Pass | Investigate and repair fan circuit unit 4 cell L48
MSA-DCS | WA3661699 | gatehouse sallyport constant alarm - see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-09 12:00:00 | Fail | Job complete
MSA-DCS | WA3661725 | Unit 3 - A & C Wing door handle requires replacement. Damaged | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-11-05 11:00:00 | Fail | NEW CUSTOM HANDLES INSTALLED
MSA-DCS | WA3661931 | Unit 4, D16 - Light switch Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-06 11:00:00 | Pass | Replaced light switch.
MSA-DCS | WA3661934 | Unit 4,Centralyard - fore hose reel box corroded away | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-11-20 11:29:00 | Fail | Repair FHR cabinet in Unit 4 and FHR in Unit 9
MSA-DCS | WA3661970 | Paint Shop, Workshop - fuse blown on spray booth paint shop/tripping | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 14:00:00 | Pass | Restored power to paint shop spray booth
MSA-DCS | WA3661977 | Gatehouse, visits - outer door not closing properly (door closer) | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-06 14:00:00 | Pass | NEW HEAVY DUTY HINGES FITTED AND SEAL RE IN STALLED
MSA-DCS | WA3662058 | Front Reception Interview Room 2 - 2 ceiling lights faulty | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-07 16:10:00 | Pass | Repaired lighting in interview room 2.
MSA-DFES | WA3661683 | facilities and contract office admin building power is out | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 02 Oct 2020 | 2020-10-02 15:07:35 | 2020-10-02 13:30:00 | Pass | Arrived on site at 11:30 to attend P0. Found 3 RCDs had tripped after power surge had tripped right back to driving simulator transportable. Reset RCDs and tested circuits. Found water in Transportables supply inlet. Left site at 12:30 to pick up plug, returned to site at 13:00 dried Inlet resealed inlet and swapped out 20A plug end. Tested and found faults had gone. Wall inlet needs to have a new base so water won’t leak into unit and trip RCD. Continued on site at 13:30.
MSA-DFES | WA3661941 | Roof above engine room - A timber barge board on front of station is coming away from the gable | CFRS Canning Vale | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-13 12:00:00 | Fail | Inspect barge board to front elevation , knuckle boom EWP is required to complete task- re-fixed barge board to the rafter with larger and longer fixings. Filled holes and touched up paint. Re-fixed TV Aerial bracket through the barge board and onto the rafter for greater fixing strength
MSA-DTAG | WA3661325 | ground staff female toilet Water not draining in the overflow drain that is above the sink | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Oct 2020 | 2020-10-02 17:00:00 | 2020-11-16 16:47:00 | Fail | job done
MSA-DTAG | WA3661823 | Ground, R111 - BMS will need to be reset due to power outage occurring on Saturday 3 October – HVAC | Supreme Court | GMP-BR-HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 02 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-05 09:00:00 | Pass | Attend site after weekend electrical shut down. Access BMS and found to be of. Turn on computer snd reboot. Log in and check schedule times and found to be ok. Check BMS tome and found to be correct. Check all plant operation and found to be working as normal.
MSA-DTAG | WA3661891 | Level 4, Disable public Opposite custody - clogged | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Oct 2020 | 2020-10-05 17:00:00 | 2020-10-02 14:00:00 | Pass | COMPLETED
MSA-DTAG | WA3661896 | Level 4, Female Public Toilets, Hay Street End - toilets are both out of order/clogged | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Oct 2020 | 2020-10-05 17:00:00 | 2020-10-02 14:15:00 | Pass | COMPLETED
MSA-DTAG | WA3661998 | Issue with Time Delay lock door in Court 2 (see notes) | Rockingham Justice Complex | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-05 14:00:00 | Pass | Checked door and electronic security working fine. Issue is with snib for mechanical lock. Requires locksmith to investigate.
MSA-DTAG | WA3662071 | Court Room 34 - Courtroom Gallery Door lock is loose | Central Law Courts-Main Building-Level 3 | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 02 Oct 2020 | 2020-10-05 17:00:00 | 2020-10-02 20:00:00 | Pass | Afterhours Attended site, tightened screws on lock to gallery door Court 34.Date on site: 02/10/2020Time on site: 07:20pm - 08:00pm
MSA-DTWD | WA3661358 | Ceiling Lights to staffroom and adjoining Toilets reset, but keep tripping out. | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 02 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-05 15:30:00 | Fail | Attended site and signed in. Removed old light fittings in female toilets. Replaced with new led fittings. Retested cabling and found no faults on circuit. Reinstated power and tested all light fittings to be working. Job complete
MSA-DTWD | WA3661364 | L block ground lift stuck on 1st floor - Swipe card activates but wont release lift to ground level | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 02 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-02 10:36:00 | Pass | Lift turned over to security on ground floor , turned back to normal operation
MSA-DTWD | WA3661722 | Building 6, Mezzanine floor, painting and decorating - light not working in 2 days | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-05 13:00:00 | Pass | Attended site and signed in. Located mezzanine floor. Found lights to be in non ideal location for painting booths. Relocated 2x light fittings and replaced 1 light fitting not working. Rewired light fittings. Tested all okay. Job complete
MSA-DTWD | WA3662064 | Creche - maytag dryer & flue lint clogging system | Perth Campus B1-Main Building-Level 2 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 02 Oct 2020 | 2020-10-09 17:00:00 | 2020-11-19 09:25:00 | Fail | Child Care Centre Cleaned all internal surfaces of the laundry exhaust system x 1 including the flue riser through to the atmosphere
MSA-MRWA | WA3661250 | Server Room CRAC Alarm + AC-1 Fault Basement Server Room | Don Aitken Centre MRWA Head Office-Main Building | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 02 Oct 2020 | 2020-10-02 17:00:00 | 2020-10-02 07:40:00 | Pass | Arrived on site. Checked ac units in the server room. Found alarm on ac 1 and 2 (Comms fault)Reset the alarm and test run. Monitored. Worked fine.A40483156K / A40483157L0440-0740 on 02/10/2020
MSA-DCA | WA3662247 | Lift is not working. | PICA-Main Building-Level 1-Lift Foyer | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 2 | CLOSE | 03 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-04 11:04:00 | Pass | Job completed - no notes
MSA-DCS | WA3662163 | Security section - The barrel is jiggly and the lock is sort of broken. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 03 Oct 2020 | 2020-10-03 11:16:55 | 2020-10-03 09:30:00 | Pass | After Hours Attendance. Repaired/realigned lock to restore normal function.
MSA-DCS | WA3662164 | issue with computer system in the control room | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Oct 2020 | 2020-10-03 11:49:35 | 2020-10-05 15:32:00 | Fail | Rectified and fixed he faulty ebi ws, job completed.
MSA-DCS | WA3662179 | Karnet Prison Farm- visit cameras in visitor centre is not accesible | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-07 17:00:00 | Pass | Checked Indigo Workstation, able to log in but no cameras,checked user privilege's and access.adjusted camera selection as visits could see all cameras.checked IP address and found IP had changed.reprogrammed and tested all cameras online
MSA-DCS | WA3662185 | Running tap in Lenard unit in the staff office. | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Oct 2020 | 2020-10-04 09:18:45 | 2020-10-04 09:04:00 | Pass | Repair spindal to kitchen sink
MSA-DCS | WA3662193 | Hakea Prison -sprinkler alarm room unable to reset | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Oct 2020 | 2020-10-04 08:25:27 | 2020-10-03 23:39:00 | Pass | flow switch alarm isolated - checked flow switch and had no issues, de-isolated and system all ok on departure
MSA-DCS | WA3662201 | 3 cameras in the perimeter are out. Cameras 44, 17 and 62 are out. | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Oct 2020 | 2020-10-04 10:44:40 | 2021-06-05 11:30:00 | Fail | Attended site.Replaced faulty camera 44 (end of life) with new Wisenet HCB-6001P and CCTV lens (supplied by SEME).Used EWP for access.Conducted test.All back to normal and operational
MSA-DCS | WA3662251 | Wooroloo Prison Farm - Gatehouse - Gallagher command centre has locked a workstation. | Wooroloo Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Oct 2020 | 2020-10-03 21:52:01 | 2020-10-03 19:00:00 | Pass | Contacted site and spoke with officer Caarooy - problem with Gallagher system is retrieved and system is back to normal and operational
MSA-DCS | WA3662253 | Exterior of Unit 9 - Burst water main | Hakea Prison-Unit 9 64 Cell Prison Living | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 03 Oct 2020 | 2020-10-04 00:50:49 | 2020-10-03 22:52:00 | Pass | Repaired burst pipe in store room unit 9 cold water supply.
MSA-DCS | WA3662255 | Both inner and outer premeiter fence in false - reset is not fixing. | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Oct 2020 | 2020-10-04 06:59:58 | 2020-10-05 11:00:00 | Fail | Attended site.Checked FlexPS processor for external zones 3 and 4 MF.Checked outer zone 3 MF cable for any damage.Checked splice kits and found one loose connection.Resecured and replaced splice kit (supplied by SEME)Tested.All ok at departure
MSA-DCS | WA3662276 | Banksia Hill Detention Centre-replacement of basin in Lenard unit staff office | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-21 14:10:00 | Fail | Replaced basin set
MSA-DCS | WA3662288 | Banksia Hill Detention Centre-In Karakin unit wing entry door lock is broken | Banksia Hill Detention Centre | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 0 | CLOSE | 04 Oct 2020 | 2020-10-04 14:37:39 | 2020-10-04 12:30:00 | Pass | After hours attendance. Replaced door lock to restore normal function.
MSA-DCS | WA3662300 | Hakea Prison - fire system earth fault is showing up | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 04 Oct 2020 | 2020-10-04 16:58:05 | 2020-10-04 15:33:00 | Pass | intermittent fault - carried out some checks and not present when left site
MSA-DCS | WA3662309 | HEALTH CENTRE- Cell 8- Intercom has stopped working. | Hakea Prison-Health Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Oct 2020 | 2020-10-04 17:32:04 | 2020-10-07 12:30:00 | Fail | Site CONFIG program checked. No further issues with CCU cell intercoms. All tested ok.
MSA-DCA | WA3662499 | ground fire panel FIP fault – area 39 in fault, power fault light is on. | Maritime Museum Victoria Quay-Main Building-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 10:10:00 | Pass | Callout - Investigated fault zone 39. Sub FIP in engineering stated power fault/battery.Opened door and terminal and wire off of battery. Resecured. Door touching wire and terminal disconnected. Adjusted batteries and resecured all terminals. Fault removed.
MSA-DCA | WA3662964 | wall facing culteral centre has graffiti | The Blue Room-Main Building-External Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 09:00:00 | Pass | Removed graffiti
MSA-DCS | WA3662349 | Kitchen - Freezer is not holding it's temperature. | Karnet Prison Farm-Stores | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 05:03:48 | 2020-10-05 11:30:00 | Pass | System short of refrigerant , carry out leak check and repair leak on TXV
MSA-DCS | WA3662413 | Karnet Prison Kitchens The 3 stack moffat oven is not working - not heating up | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 05 Oct 2020 | 2020-10-05 10:34:04 | 2020-10-05 12:20:00 | Fail | Replaced 2 simmerstats to top deck which were not regulating . Test all elements ok. Test other two decks regulating ok. Left unit operating.
MSA-DCS | WA3662461 | Unit 2 - Cell A09 long piece of metal has come out causing the bottom window to be loose | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-14 13:00:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3662464 | Unit 13 -Cell C16 hot water tap on sink to hard to turn. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-07 09:30:00 | Pass | Nikl
MSA-DCS | WA3662468 | Level 4 towards rear building - internal blind has fallen down | East Perth | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-11-20 08:30:00 | Fail | Attended site and picked up damaged blind.Carried out repairs to blind and replaced broken parts.Reattended site and fitted blind to window.
MSA-DCS | WA3662475 | oval grounds Broken Retic Valve | Melaleuca Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-22 10:00:00 | Fail | repairs to the station "grounds on oval"
MSA-DCS | WA3662477 | Unit 1 - Cell C2 Faulty window stays | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-12 14:00:00 | Fail | RE NEW SPIRAL BALANCES AND REPAIR FRAME
MSA-DCS | WA3662479 | U9 C15 No water pressure from hot tap needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 07:59:23 | 2020-10-05 14:40:00 | Pass | Renew spindles to basin hot and cold
MSA-DCS | WA3662485 | Eyre C wing Aircon not blowing cold air | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 08:47:00 | Pass | Checked found the evaporative cooler switch in vent pisition, turned to cool and checked the operation found OK.
MSA-DCS | WA3662490 | Jeelia A wing Drains blocked A1 & A4 | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 09:25:00 | Pass | Clear blockage to shower A1Clear blockage to basin A4
MSA-DCS | WA3662491 | Gymnasium - Mezanine Floor - Hot Water system failure tank leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-11-13 10:30:00 | Fail | Nill
MSA-DCS | WA3662494 | Unit 1 - Office Tap in the officer's tea room is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-07 08:14:00 | Pass | Nikl
MSA-DCS | WA3662495 | Unit 1 CCTV monitors have frozen | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Oct 2020 | 2020-10-05 11:49:50 | 2020-10-05 09:00:00 | Pass | Work station 1 ok. Both workstation 2 monitors frozen. Shut down PC. Removed and cleaned internal parts of the pc. Reconnected and tested ok.
MSA-DCS | WA3662496 | Unit 1 - Cell B1 Faulty window stays | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 12:00:00 | Pass | RE NEW SPIRAL BALANCES AND REPAIR FRAME
MSA-DCS | WA3662498 | Unit 4 - Cell B13 Drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-07 16:00:00 | Pass | Nill
MSA-DCS | WA3662506 | kitchen Blast Chiller No 2 Controller Broken | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-16 15:30:00 | Fail | Replaced controller and sensors as quoted. Test ran unit. All operational at time of departure.
MSA-DCS | WA3662513 | Unit 4 D4Toilet Pipe Leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 08:36:01 | 2020-10-05 16:00:00 | Pass | Replaced flush cone to cistern
MSA-DCS | WA3662515 | U7 H wing shower L/H side shower leaking needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 08:40:31 | 2020-10-05 15:40:00 | Pass | Reseat and rewasher shower hot and cold
MSA-DCS | WA3662521 | Unit 7 E wing Tap leaking can’t be turned off needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 08:43:13 | 2020-10-05 16:40:00 | Pass | Reseat and rewasher shower hot and cold
MSA-DCS | WA3662560 | Unit 14 - A3 Cell A03 has a badly leaking sink tap. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 15:00:00 | Fail | Nill
MSA-DCS | WA3662571 | Unit 1 - Office Air Conditioner in the officer's tea room is not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-15 15:45:00 | Fail | Replaced fan motor and PCB. All operational at time of departure.
MSA-DCS | WA3662574 | Unit 1, D7 - srews missing in door hinge | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-15 11:30:00 | Fail | Replace hinge screws
MSA-DCS | WA3662579 | Unit 1, D1 - the following cell door hinges missing screws | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-15 10:30:00 | Fail | Replace hinge screws, latch and weld on strike
MSA-DCS | WA3662588 | Unit 1, B4 - the following cell door hinges missing screws | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-23 11:00:00 | Fail | Require parts and awaiting access.Replace hinge screws, door plate, lock, strike and barrerl.
MSA-DCS | WA3662608 | Sewer treatment plant Cholrine injection no working | Karnet Prison Farm | GMP-BR- HO | Waste Management | Waste Removal (WM) | MAK Industrial Water Solutions Pty Ltd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-12 08:30:00 | Fail | Inspected, found to be working. No charge
MSA-DCS | WA3662611 | Unit 1 Toilet block fans faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 11:00:00 | Pass | Investigate and repair unit 1 toilet block exhaust fan
MSA-DCS | WA3662614 | Vistors toilet block fans faulty in male toilets | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 09:30:00 | Pass | Investigate and repair visitors toilet block exhaust fan
MSA-DCS | WA3662659 | Unit 7, D wing - Leaking from below sink in kitchen Unit 7 D wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-15 09:30:00 | Fail | Nill
MSA-DCS | WA3662677 | Unit 1, D wing - grill motor failed to open for a short period of time but eventually started itself | Casuarina Prison | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 09:30:00 | Pass | Ryan Nicholson (08/10/2020) - Work NoteTravel to site. Inspect Unit 1 D wing grill. Found to be operational and working fine so investigated. Found clutch was loose, so tightened. Found limit plate fixings were loose, re-tighended. Found closing limit plate end was bent so bent back straight as limit was almost off in closed position. Tested several times, all fine.
MSA-DCS | WA3662691 | Unit 1, D2 - External Arial point problem | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 11:00:00 | Pass | Installed TV Point plate. Redone connectors in Unit 1 D2. Tested signal, OK.Replaced coax cable to D3, site to raise new job for D3 requiring mounting plate & TV Point.
MSA-DCS | WA3662705 | Unit 13 - B12 cell call faulty | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-05 15:30:00 | Pass | Attended cell 13B12, drilled out cell call retaining Rivets, found damaged pushbutton and pcb connection plug. Replaced cell call components, tested cell call to local control, God audio both ways. Reriveted Cell call into position.
MSA-DCS | WA3662709 | U13, Cell A13 - BLOCKED DRAIN REQUIRES MAINTENANCE. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 08:30:00 | Pass | Nill
MSA-DCS | WA3662712 | Unit 6 - A12 no power | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 12:30:00 | Pass | Restored power to cell a12 unit 6
MSA-DCS | WA3662714 | Unit 1, B7 - floor drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 13:55:00 | Pass | Unblcoked basin drains
MSA-DCS | WA3662716 | Unit 13 - D6 CELL CALL NOT WORKING | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-05 13:45:00 | Pass | Attended unit 13, cell D6. Drilled out cell call retaining Rivets. Found cell call PCB damaged. Replaced cell call unit, tested cell call to local control. Good audio both ways, riveted Cell call unit back in place.
MSA-DCS | WA3662717 | Unit 1, C15 - Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-06 10:00:00 | Pass | Replaced broken light switch and repaired light
MSA-DCS | WA3662720 | Unit 1, C6 - light broken in cell | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-05 15:00:00 | Pass | Repaired light
MSA-DCS | WA3662728 | Unit 1, Foyer - 2x light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 10:53:25 | 2020-10-05 14:00:00 | Pass | Repaired lights
MSA-DCS | WA3662729 | MPU (8) - M10 vinyl is damaged | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2021-02-08 12:00:00 | Fail | new vinyl installed to damaged areas
MSA-DCS | WA3662757 | Abbs - Stat valve faulty on ring man | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-11-09 14:00:00 | Fail | COMPLETED
MSA-DCS | WA3662760 | Abbs - temp valves faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-11-27 12:00:00 | Fail | COMPLETED
MSA-DCS | WA3662766 | Education - Faulty urn | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 13:00:00 | Pass | Removed old urn and installed new Zip urn
MSA-DCS | WA3662773 | Letuce shed, nursery, pump room - power faulty GPOS broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 08:30:00 | Pass | Investigate and repair lettuce shed gpo’s
MSA-DCS | WA3662779 | Amenities - Office We have no heating again | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-03 09:15:00 | Fail | Unit has not tripped in a month, checked over again, all ok
MSA-DCS | WA3662780 | U7, Cell E10 - Cell call not working correctly needs repair | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 11:30:43 | 2020-10-05 13:30:00 | Pass | Active call message stuck on overhead display. No active call on the officer station. Intercom LED stuck on but intercom not activating when pressed. Reset power to CI8 boards. Tested ok with spare intercom directly into the CI8 board. Tested loud and clear from cell.
MSA-DCS | WA3662802 | Security Area - Office duress alarm self activating | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-13 10:30:00 | Fail | tested pda 312 duress alarm. cleaned button contacts, tested buttons. unable to reproduce fault carried pda all day no alarm.
MSA-DCS | WA3662806 | business manager officer light flickering | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 14:15:00 | Pass | Repaired lights
MSA-DCS | WA3662807 | Cleaning - Workshop Polisher control box broken (unit 4) in the cleaning workshop. | Casuarina Prison | WSM-MW-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-19 13:00:00 | Fail | Checked damaged polisher, ordered replacement parts picked up and repaired.
MSA-DCS | WA3662810 | SB1 - Office between units 15-16 Unable to open door with key. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 12:10:51 | 2020-10-06 11:30:00 | Pass | Require parts.Replace mortise lock due to face plate had been modified, causing lock tongue to jamb.
MSA-DCS | WA3662816 | perimeter internal zone 23 MW constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 12:15:57 | 2020-10-06 09:00:00 | Pass | Located power source for TX microwave in Melaleuca. Tested cabling between the microwave in Hakea’s perimeter and the Sennet module in Melaleuca. Repaired power issue. Tested ok back to the gatehouse. Parts used:Consumables
MSA-DCS | WA3662835 | Unit 13, D15 - middle shower glass shattered still in place .cell not useable till it is repaired | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-27 13:30:00 | Fail | SHOWER SCREEN RE GLAZED
MSA-DCS | WA3662836 | Reset Centre - Toilet light in the toilet hallway is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-06 08:30:00 | Pass | Repaired faulty lights in outcare passage
MSA-DCS | WA3662841 | Unit 3, D7 window needs repair as stays are broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-14 14:15:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3662842 | MPU Cell M1 SPU personal key lock latch is not servicable. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-11-10 09:00:00 | Fail | Require parts.Replace mortise lock, cams and install offset strike.
MSA-DCS | WA3662843 | Unit 3, D8 window needs repair as stays are broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-14 15:00:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3662848 | Unit 3, D11 window needs repair as stays are broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-19 09:45:00 | Fail | NEW WINDOW BALANCERS FITTED
MSA-DCS | WA3662851 | Unit 14 - A Wing Suspected leaking pipework leading down to sink in A Wing cleaning cupboard, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-16 10:30:00 | Fail | No leak found
MSA-DCS | WA3662852 | Unit 3, B1 window needs repair as stays are broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-19 11:00:00 | Fail | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3662856 | Unit 14, A8 - Shower screen needs resealing as water is leaking onto beds | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-11 10:00:00 | Fail | RE sealed shower screen
MSA-DCS | WA3662862 | INF (10) - B8 CELL CALL ALARM IN CELL B8 IN THE INFIRMARY IS NOT WORKING. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-13 12:30:00 | Fail | 13/10/2020 Drilled out existing creatinine Rivets, removed cell call from wall, connected replacement cell call with wireless Receiver connected. Unable to trigger cell call from wireless due to lack of suitable continuous 12v supply inside cell call. Removed receiver and tested cell call. Good audio both ways to local control.
MSA-DCS | WA3662871 | Turner outside toilet broken | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 10:35:00 | Pass | Replaced cracked toilet and cistern
MSA-DCS | WA3662909 | Reception Laundry - Simpson tumble dryer door broken | Hakea Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 14:03:46 | 2020-10-23 11:30:00 | Fail | AMS703463 WA3662909 Hakea -Simpson tumble dryer door broken7/10 - Attend site to pick up dryer and take back to workshop for repairWorkshop - supply & fit new inner doorReturn Dryer to site
MSA-DCS | WA3662922 | admin barista damaged ceiling fan barista area --electrical fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 14:00:00 | Pass | Replaced damaged fans and secure properly
MSA-DCS | WA3662940 | Boiler House - Boiler start-up & shut off until further notice | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 14:40:49 | 2020-11-02 17:00:00 | Fail | Start up & Shut Down 3 X Steam Boilers for Monday 2/11/2020
MSA-DCS | WA3662956 | Ground floor admin office 1 x flickering fluro light | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 14:51:46 | 2020-10-06 09:45:00 | Pass | Replaced failed lamps and starters. Cleaned diffuser.
MSA-DCS | WA3662961 | kitchen main work area Rational Ovens have low water pressure | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2021-02-15 13:30:00 | Fail | 28/10/20Arrive at site to check oven low water pressure, oven is tagged out as has comms error. Showing: service 34-2, internal data communication defective scc-07.00.08.5Will need to gather information from tech support if we are going to repair. Would recommend to replace 3 x water filters and test water pressure issue when oven is working again.Parts required:3 x water filters 15/02/21Arrive at site to fit parts, fit all and test all ok. Left side oven is still out of service but water pressure is good.
MSA-DCS | WA3662966 | kitchen main work area Mobil Hot Boxes Not Heating Up | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-28 12:00:00 | Fail | 28/10/20Arrive at site to check hot box's not working, found various issues acroll 4 hot box's. Reset some of the overtemps, some had fans not running, found faulty power cord. Will need to gather information to assess parts. Kitchen staff advised they are possibly looking at new hot box's. I suggested we take 1 away to workshop to repair when time suits.Parts required (parts are no longer available)1 x Fan1 x Element1 x Over temp1 x Power cord
MSA-DCS | WA3663009 | Inner & outer perimeter fence zone 7 to 14 - continually going into alarm and will not reset | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Oct 2020 | 2020-10-05 23:53:14 | 2020-10-06 12:00:00 | Fail | Reset microphonics processor, check & test ok.
MSA-DCS | WA3663033 | Zone 7-14 Inner and outer fence will not reset going into alarm constantly. | Greenough Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Oct 2020 | 2020-10-06 04:35:47 | 2021-08-04 10:30:00 | Fail | Inner MF has been upgraded to gallagher electric fence, check and test nodes Flex PS nodes for zone 7 to 14 outer MF. Visually inspected any loose cable and rectified. Job completed.
MSA-DFES | WA3662392 | Belmont FS - Burst pipe in the under ground at rear of the engine room. | CFRS Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 05 Oct 2020 | 2020-10-05 09:55:26 | 2020-10-05 09:29:00 | Pass | Repair burst
MSA-DFES | WA3662552 | field analises door ground door has been hit by car and will not open | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-06 09:00:00 | Pass | Attended site, assessed damage and took photos. Will require inspection and report by a structural engineer to assess the extent of the damage.Claim discounted to keep within approved limit. Work order closed off before BRAF could be submitted.
MSA-DFES | WA3662556 | Front career side, front shutter door - Not coming down automatically | CFRS Rockingham | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-11-23 11:30:00 | Fail | Technician attended the site of Rockingham Fire Station to the Front Door No. W20573 on 06/10/2020. Following a full test and inspection of door components found fault to be new beams out of alignment so tech has adjusted. This is due the fact this is a new install unfortunately reflective safety Beams are the issue easily go out of alignment. Recommended replace reflective type for send receive type. Technician returned on site on 23/11/2020 to remove existing reflective type safety beams. Replaced it with a send receive Photo beam test all ok. Full test and inspection of door function completed prior to leaving site.Breakdown of cost: Labour = $715.00Parts = $1,655.30
MSA-DFES | WA3662561 | Workshop entry - the alarm panel has gone blank & is unable to be set from this location | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | COMP | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 16:30:00 | Pass | 5/10/20 - Dylan ParslowFound main power point for workshop panel disconnected.Reconnected and tested, all working.No charge on this job.
MSA-DFES | WA3662570 | North East Entry - new handle keeps scraping the side of the door as it attempts to close causing | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 11:20:00 | Pass | Reposition electric strike. Adjust to door closer and reposition door handlesDoor was scraping on electric strike as it was not lush. Increased door closer strength and moved handles over slightly to create more space.
MSA-DFES | WA3662662 | Applied training ground - Electric fence insulators are broken caused by debris fallen on them | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 05 Oct 2020 | 2020-10-05 14:15:25 | 2020-10-05 12:00:00 | Pass | CompleteAttended site and replaced broken insulators on electric fence
MSA-DFES | WA3662751 | tech area ground metal fab bay Exposed wiring identified in the metal - see ntoes | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 13:45:00 | Pass | CompleteLocated exposed cables and made safe all in working order
MSA-DFES | WA3662997 | L2 disable toilet door not opening on egress push-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-06 16:15:00 | Pass | Technician attended the site of Cockburn Emergency Services Centre to the Level 2 Disabled Toilet Auto Door on 06/10/2020. Following a full test and inspection of door components found fault to be power to door tripped reset power. Unfortunately the circuit for the swing is on the cleaners cupboard cleaner must trip it so require door be on the auto door circuit. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3663008 | Admin building lawn broken sprinklers - see notes | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-07 17:30:00 | Pass | B Coniglio & K Skulley (1 Hr x 2 employees) & $25 Retic Parts
MSA-DTAG | WA3662793 | Ground FIP Tech required to assist HVAC on Saturday 10 October from 08.00am until 16.00pm | Perth Children's Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-10 12:00:00 | Pass | ..
MSA-DTAG | WA3662907 | 1987 L2 FIP Retrospective work order for a tech to isolate FIP on Sat19/9/20 & de-isolate - see note | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-05 14:14:00 | Pass | 19/09/20 Isolate at 07:0019/09/20 De-isolate at 16:0020/09/20 Isolate at 07:0020/09/20 De-isolate at 16:00
MSA-DTAG | WA3662913 | 1987 L2 FIP Retrospective work order for a tech to isolate FIP on Sat26/9/20 & de-isolate - see note | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-05 14:27:00 | Pass | 26/09/20 Isolate at 07:0026/09/20 De-isolate at 16:0027/09/20 Isolate at 07:0027/09/20 De-isolate at 16:00
MSA-DTAG | WA3662974 | court 2 entrance door faulty lock | Rockingham Justice Complex | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 16:05:00 | Pass | Attend site and change function on mortice lock.
MSA-DTAG | WA3663434 | Retrospective WO - technician to isolate FIP on Monday 5/10/20 and de-isolate (4 hours in total) | Supreme Court | WSM-BR-SITE | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-06 12:10:00 | Pass | Isolated courts 10+11 for drilling worksDeisolated @ 2345 all okay
MSA-DTWD | WA3662603 | Q block - power loss to class rooms | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 14:54:00 | Pass | Repalced blown fuse to red phase. Tested power all working properly
MSA-DTWD | WA3662607 | A block, level 3 - Replace broken tap L3 A Block Male toilet | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 12:45:00 | Pass | replaced fibre washer and jumper washer in hot tap
MSA-DTWD | WA3662628 | building 6, Ground, Painting & Decorating - 2 drop single phase power points not working. Remainder | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-26 11:47:00 | Fail | BRAF declined, invoice costs to date
MSA-DTWD | WA3662730 | Have an RCD in the Staffroom that is tripping out and will not reset. | Jandakot Campus - Annex | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 11:00:00 | Pass | Attended site, signed in, spoke to staff about problem, completed jsa, located gpos that weren’t working , identified gpos on the circuit , opened up board and tested rcds, found rcd in on position with 1v on load side , reset rcd and voltage was at 240 on the Load side , went back and tested gpo , gpo operational , screwed back gpo , spoke to site and they said they will plug all computers and move desk back , completed paperwork, signed out *** job completed ***
MSA-DTWD | WA3662777 | North, F Block & West, U Block Auto doors not working; | Rockingham Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-05 15:10:00 | Pass | Found that the door has failed, cpu fault, I have reset the controller and it seems to be operating correctly now.Checked over door for Programmed barcode - could not find one so unable to provide.Whilst onsite, check sensor not working. Found that the external sensor has failed, replaced faulty sensor, tested and adjusted, all ok.
MSA-DTWD | WA3662788 | Level 5, faulty lights - replace lights as required | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-07 15:45:00 | Pass | Attended site, signed in, spoke to fm about job, completed jsa, located lighting, replaced various tubes and starters as per list given by fm (fm said not to worry about the diffuser) , cleaned up work area, completed paperwork, signed out , site happy ***job complete***
MSA-DTWD | WA3662794 | LEvel 5, corridor west block - drinking fountain is blocked | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-06 10:10:00 | Pass | Fix fountain
MSA-DTWD | WA3662796 | A block, A20 - GPO faulty x2 | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-06 12:15:00 | Pass | Attended site, signed in, spoke to fm about job, completed jsa , located gpos that were faulty , isolated power and replaced both gpos , tested gpos and both working as intended, cleaned up work area, completed paperwork,signed out ***job completed ***
MSA-DTWD | WA3662805 | G block, G20 - Blocked wash basin drain | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 11:42:00 | Pass | UNblcoked line Root infested
MSA-DTWD | WA3662808 | Level 1, Chalk and cheese - kitchen tiles have fallen off the wall - retiles | Perth Campus B2 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-13 14:30:00 | Fail | Arrived at site, signed in and set up work area. Sealed all boarders of tiles with silicone. Sealed grout with grout sealer. Tidy area, packed away tools. Complete.
MSA-DTWD | WA3662820 | H block, nursery - retic control box is not functioning correctly | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 05 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-05 15:00:00 | Pass | Liaised with onsite contact, checked operation of irrigation controller, the controller is work normally with no fault found.
MSA-DTWD | WA3662824 | West block, Level 1, Kitchen - replace/repair faulty lock on cupboard | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 11:25:00 | Pass | 05/10/2020 3.40pm-4pm - need to return with parts12/10/2020 11am-11.25am - replace faulty cupboard lock
MSA-DTWD | WA3662854 | FT15/FG17 - Electrical fault – FT15 Supply Air Fan 1 contactor won’t disengage. | Carlisle Campus-Block F | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 15:23:00 | Pass | Located faulty system found bms control keeping system on , will require bms company to repair. Facilities management are sorting all ok
MSA-DTWD | WA3662951 | S block L1 S109 13sq metres of carpet damaged | Mount Lawley Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 05 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 10:30:00 | Pass | Replace damaged carpet as requested by site
MSA-DTWD | WA3663028 | A block, Lift - not working has broken down. | Leederville Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | COMP | 05 Oct 2020 | 2020-10-05 20:51:30 | 2020-10-06 11:00:00 | Fail | On investigation found lift fataled with error 10(FC fault) with preceding 146(Safety T3A) errors. Further investigation foundcontact block on JRH switch intermittently dropping T3A. Check contact block connections and resecure block on back of switch. RTo be closed out at $0
MSA-DTWD | WA3730955 | Centre Block, Fire Pump Room- Drain line is leaking | Perth Campus B1 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 05 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-05 09:00:00 | Pass | Replaced leaking section of drain line
MSA-DCA | WA3663169 | Ground - Security Control Room - multiple BMS alarms throughout building due to testing of CEP. | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Entrance - Security | GMP-BR | Security | Security Management System (SE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 06 Oct 2020 | 2020-10-06 17:00:00 | 2020-10-06 11:00:00 | Pass | Scheduled shutdown works carried out by contractors caused multiple alarms on site. Works completed. Steam Boilers and Pneumatic Plant in fault. Reset and monitored. AC 3 gallery 3 low humidity alarm. Alarm cleared 11:14.Closed job.Further scheduled works to follow this week.
MSA-DCA | WA3663329 | lift No 3 going up and down but doors not opening | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-06 12:45:00 | Pass | Job completed - Lift 3 Art (glass)-Hydraulic :Found lift as reported, checked door contactor 443:1 , reset door control board, checked all connection, cleaned and lubed all movinv parts on door skate, clean andlubed door plunger, tested couldn't duplicate fault left lift running
MSA-DCA | WA3663840 | Loading dock doors will not open - vehicle stuck inside | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Loading Bay and Loading Bay Drive | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | ASSGN | 06 Oct 2020 | 2020-10-07 17:00:00 |  | Overdue
MSA-DCS | WA3663151 | Unit 1 Cell A11 Main lock not working | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 07:16:23 | 2020-10-06 12:40:00 | Pass | Attended site. Repaired lock by replacing faulty component. Normal function restored.
MSA-DCS | WA3663197 | Unit 16 - C Wing Cell light in C7 has not been working for the last few days. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-19 13:00:00 | Fail | Checked light. Ordered replacement parts, repaired faulty lights in c7
MSA-DCS | WA3663209 | Bakery WEIGHT WELDED TO THE BREAD SLICER ARM HAS SNAPPED | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-23 14:30:00 | Fail | 09/10/2020Check bread slicer and found LH guide comb completely torn away. Advise manager could weld temporarily but they just want replacement.Parts required: 1 x Pusher Arm LH 1 x Pusher Roller 1 x End Cap23/10/2020Remove and replace arm and bearing Found adjuster rod bent preventing correct position of arm Remove and straighten Reassemble unit and test ok
MSA-DCS | WA3663220 | stores yard Rubbish Wash Down Drain blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-12 09:15:00 | Fail | Pumped out overflow tank in stores yard
MSA-DCS | WA3663260 | U7 Cell H13 No TV signal to aerial point needs repair | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 08:18:25 | 2020-10-14 16:00:00 | Fail | Replaced U7 H13 TV Point. Checked, signal has improved. Found TV with intermittent fault. Tested by using TV from next cell, tested OK. Officer to replace TV in H13.Job completed.
MSA-DCS | WA3663302 | unit 10 plant room behind A and B wing water is coming spraying of pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 06 Oct 2020 | 2020-10-06 12:52:44 | 2020-10-06 12:25:00 | Pass | Repair burst water pipe u10 plant room
MSA-DCS | WA3663314 | SITE COSTED Stop and start of boilers for next 3 days | Hakea Prison | WSM-GR-SITE | Mechanical Services | Boilers (MS) | Boilertronics | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-09 09:28:00 | Pass | Start up & Shut down of Steam Boilers5/10/2020 - 9/10/2020
MSA-DCS | WA3663317 | Amenities, shower block - Mens shower block lighting is faulty. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-06 15:00:00 | Pass | Repaired faulty lights in amenities male change rooms
MSA-DCS | WA3663321 | Unit 3 - D4 sink tap leaking from under sink. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 12:30:00 | Pass | Nill
MSA-DCS | WA3663338 | Unit 1, C11 - Toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 08:30:00 | Pass | Nill
MSA-DCS | WA3663340 | Administration, Court Yard - Admin External lights keep tripping | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-11-23 12:30:00 | Fail | Repaired multiple faulty light circuits and repaired external lights around admin visits centre
MSA-DCS | WA3663352 | E section 2 of the camera's are very grainy and distorted | Albany Regional Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 09:25:30 | 2021-07-30 17:30:00 | Fail | Installed new CAT6 cable between camera locations and network switch. Replaced existing analogue cameras with IP cameras, Reprogrammed equipment.
MSA-DCS | WA3663411 | outside gym Locker change room Lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 13:30:00 | Pass | Repaired lights
MSA-DCS | WA3663421 | Unit 5 A19 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-07 12:00:00 | Pass | Repaired light
MSA-DCS | WA3663441 | Unit 17, A wing, Cell A12 - Outside light switches damaged/vandalism | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-09 08:30:00 | Pass | Replaced damaged cell switch in unit 17 a12
MSA-DCS | WA3663470 | kitchen 2 ovens the waste water pipe are blocked | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 10:30:06 | 2020-10-06 12:30:00 | Pass | Unblocked and ran hot water through to clear the drain.
MSA-DCS | WA3663532 | Visits - CCTV cameras not working | Bandyup Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Oct 2020 | 2020-10-06 15:02:27 | 2020-10-06 16:42:00 | Fail | Diverted from Melaleuca job to Bandyup.Repaired Visits CCTV cameras and control room workstation.Tested OKJob Complete
MSA-DCS | WA3663548 | Turner A wing fire stobe damaged | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 11:10:40 | 2020-10-12 11:45:00 | Fail | 7/10/20 EIAttended site but no access due to lockdown & escort availability at time of attendance.BG EI 12/10/20Picked up stock from office.Manufactured strobe mount and bracket. Installed new bracket. Performed alarm test and verified strobe operationNote - Additional time on site due to working at heights protocol and requiring a 2nd man
MSA-DCS | WA3663570 | B wing cell B19 toilet not working - contractor on site | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-19 12:30:00 | Fail | COMPLETED
MSA-DCS | WA3663572 | Turner A wing Aerial antenna damaged | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | COMPFIN | 06 Oct 2020 | 2020-10-07 11:16:36 | 2020-10-13 11:00:00 | Fail | Checked MAW in Turner A Wing. Requires new TV Aerial Antenna set. Cell B5 requires new TV Point & re-cabling of coax cable to comms cabinet.
MSA-DCS | WA3663597 | Turner B wing B05 cell has been damaged will need clean | Banksia Hill Detention Centre | GMP-BR- HO | Cleaning | Emergency Cleans (CL) | DUNBAR SERVICES (WA) PTY LTD | 1 | COMPFIN | 06 Oct 2020 | 2020-10-07 11:31:42 | 2020-10-14 13:00:00 | Fail | Clean under the direction of site escort Luke Cliff
MSA-DCS | WA3663655 | Unit 8, Cell 10 - Broken porcelain sink & broken waste pipe needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 12:06:04 | 2020-10-06 15:30:00 | Pass | Removed broken basin and waste replaced with new
MSA-DCS | WA3663676 | unit 1 C10 Toilet Bowl Leaking Sewerage Water from the base into the Shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-12 16:10:00 | Fail | Removed old broken toilet replacing with new one
MSA-DCS | WA3663689 | unit 1 D13 Cell Light not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 10:00:00 | Pass | Repaired faulty lights in unit 1 d13
MSA-DCS | WA3663695 | Unit 1 cell B11 Light switch broken | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 11:00:00 | Pass | Replaced damaged cell switch in unit 1 b11
MSA-DCS | WA3663696 | Unit 9, staff room - Hot & Cold water unit underneath sink lights flashing on taps, not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 12:16:35 | 2020-10-09 10:42:00 | Fail | Replaced inlet solenoid JG fittings kit tap handle and spring ass
MSA-DCS | WA3663706 | Turner A wing plant room HWU pulled of wall multiple pipes damaged- see notes | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | COMPFIN | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-09 10:33:00 | Pass | Replaced damaged flue and fixed hwu back to the wall
MSA-DCS | WA3663708 | Unit 1, C6 - shower taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 10:10:00 | Pass | Replaced leaking quator turn tap cold side only on shower
MSA-DCS | WA3663713 | Unit 1 cell D7 Shower Tiles Broken and shower frame leaking water | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2021-01-12 15:30:00 | Fail | removed damaged tiles in shower recess and replaced. resealed shower screen.
MSA-DCS | WA3663717 | Unit 1, C6 - Shower Tiles Broken and shower frame leaking water | Melaleuca Prison | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-12-22 12:30:00 | Fail | replaced damaged tiles in shower recess and cell floor resealed.
MSA-DCS | WA3663768 | education office lost power to all work stations | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 13:14:18 | 2020-10-06 16:05:00 | Pass | Restored power to education room.
MSA-DCS | WA3663813 | main kitchen Evidence of water damage to corner of freezer wall | Melaleuca Prison | GMP-BR- HO | Building | External Walls (BU) | Schlager Construction Group | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-27 10:00:00 | Fail | Carry out repairs to damaged walls supply and fit stainless steel plate to wall.
MSA-DCS | WA3663815 | Unit 3, C3 - toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-07 14:43:00 | Pass | Unblcoked toilet
MSA-DCS | WA3663817 | Unit 3 cell D5 Smoke Detector Burn’t | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 13:56:00 | 2020-10-07 10:22:00 | Pass | replaced sampling point and cleared sampling points
MSA-DCS | WA3663836 | Library east office Air Con Vent in office blows Hot air only | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-11-02 14:33:00 | Fail | Completed leak check as quoted.
MSA-DCS | WA3663841 | Unit 8, C & D wing - Fire sensors at the entry of C & D wings look to be cracked or broken | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 14:28:06 | 2020-10-09 08:01:00 | Fail | sampling points broken - replaced and reset with extension ladder and second man
MSA-DCS | WA3663857 | Upstairs large room Ceiling divider hanging down - see notes | Midland (North East Metro) | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-07 15:30:00 | Pass | Attended site and carried out repairs to the T bar in the ceiling grid system that was hanging down.
MSA-DCS | WA3663864 | Unit 1 B12 Cell Door Dropped jamming on the floor | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 10:00:00 | Pass | Attended site and carried out repairs to the door that was not closing properly.
MSA-DCS | WA3663900 | Unit 1, B24 - leak from shower | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-19 10:30:00 | Fail | COMPLETED
MSA-DCS | WA3664178 | Turner A, B and C wing - B wing B06 damaged light switch - all wings damaged exhaust fans- see note | Banksia Hill Detention Centre | GMP-BR-RC | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 08:30:00 | 2020-12-02 15:00:00 | Fail | Repaired cell vent units turner.
MSA-DCS | WA3664191 | Turner A, B and C wings multiple flu's and window smashed, 17 in B wing - see notes | Banksia Hill Detention Centre | GMP-BR-RC | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 08:30:00 | 2020-12-10 09:00:00 | Fail | RIOT REPAIRS COMPLETED
MSA-DCS | WA3664237 | Unit 5, Cell D12 - The keys provided to the personal lock(prisoner lock) don’t work | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 10:30:00 | Pass | Replace barrel, lock and weld on strike.
MSA-DCS | WA3664239 | Metal shop lock on the security gate is faulty Key gets stuck, cannot lock gate sometimes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-11-04 10:00:00 | Fail | Service lock, replace bolt throw and temp. repair lever pack.Replace worn lever pack.
MSA-DFES | WA3663359 | engine bay door 3 perspecs viewing window fallen out | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 17:00:00 | 2020-11-06 12:45:00 | Fail | Technician attended the site of Welshpool Fire Station to the Engine Room on 06/10/2020. Following a full test and inspection of door components found fault to be perspex viewing window had fallen out, attempted to reinstate into position but found strip clips were missing. Quote was declined. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3663892 | ground admin building Exhaust Fan in Male & Female toilets, near Reception not working - see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-23 14:00:00 | Fail | Arrived on site at 10:30 to inspect exhaust fan. Found 2 broken fan belts and one fan with no 415V supply. Traced cables back as far as possible. Ordered gear for fan and signed out at 12:15.Completen site and started work at 1200, replaced fan belts in non working toilet exhaust fans all in working order. Notified staff and signed out
MSA-DFES | WA3663904 | Engine room roof tiles cross-bar bend, causing tile to bow and broken ceiling tile near the light in | CFRS Daglish | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-16 11:00:00 | Fail | Arrived on site to assess the job unable to complete as ceiling hight is about 5 mtrs and the cracked ceiling panel has a fluorescent light attached to it.x2 men needed WAH and OH & S ReasonsReplace Ceiling Tiles
MSA-DTAG | WA3663789 | St Georges Terrace end L10 meeting room Long wall shelf has become detached - see notes | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 06 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-08 11:30:00 | Pass | SHEL REPAIRED AND P[ATCHED
MSA-DTWD | WA3663273 | Whole of campus Multiple Access and Security panel failures. | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-08 17:30:00 | Fail | Dang Nguyen (06/10/2020) - Work NoteAttend site to investigate fault on Gallagher system due to network upgrade that transpired last week on the TAFE. Issues connecting to network from data points assigned, found issues sending data down but receiving was fine. Talked to IT and they’ve added a rule to now receive and send data back and forth through old infrastructure network system. Still unable to connect to system. Barry has requested us to return ASAP to rectify this issue. All controllers working are on the locations that were not upgraded during last week. Continue network testing with IT to get controllers back online required. D Block no alarm found, no dial tone on phone line. Getting 4G module installedMauro Caputi (07/10/2020) - Work NoteReplaced 4G GSM dialler on D Block. Now dialler is ok. Alarm is sending signals to Education SecurityMarcus Chan (08/10/2020) - Work NoteChecked all existing TCP connections from the server. Unable to see any attempted connections to
MSA-DTWD | WA3663445 | E block canteen Auto door not working properly | Rockingham Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-06 14:13:00 | Pass | No Program Serial number on unit.On inspection, found internal sensor faulty causing door to stay open.Replaced faulty sensor as approved by management (Frank).Tested and adjusted, all ok.
MSA-DTWD | WA3663455 | classroom F2 Lighting CB continuously dropping out, suspected short | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-07 12:45:00 | Pass | Attended site and signed in. Located F2 and found lights tripping. Investigated to find faulty fluro in middle of room. All fans okay. Supply and replace with new led light. Tested all okay. Job complete
MSA-DTWD | WA3663457 | Court yard entry Western side - Back timber gates are damaged | Rockingham Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-11-02 12:00:00 | Fail | Remove old timber gate and replace with new colourbond gate and fit hardware
MSA-DTWD | WA3663474 | Canteen kitchen (E Block) - Several flouro light fittings are faulty | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-07 14:45:00 | Pass | Attended site and signed in. Located canteen and checked out all light in kitchen not working, found 4 x faulty light fittings. Supply and replace with new led lights. Tested all okay. Job complete
MSA-DTWD | WA3663715 | Between B and T block - roots lifting bitumen on road | Munster Campus (ACEPT) | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 2 | CLOSE | 06 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-13 13:30:00 | Fail | Cut bitumen, lift, remove root, reinstate new bitumen
MSA-DTWD | WA3663883 | Server room Re-bolt safe to floor in new location - see notes | Armadale Campus - 40 Commerce Ave | GMP-BR | Security | Safes (SE) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 06 Oct 2020 | 2020-10-07 17:00:00 | 2020-10-07 14:15:00 | Pass | Relocated safe as requested by site
MSA-MRWA | WA3663163 | Lift 3 is in operable at basement level | Don Aitken Centre MRWA Head Office-Main Building-Basement-Lift Car 3 | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 06 Oct 2020 | 2020-10-06 11:32:50 | 2020-10-06 10:49:00 | Pass | Job completed - Checked for voltage, found voltage going into rope brake board but not coming out of board. Did further investigation, found compressor circuit breaker and motor overload tripped. Reset and tested. Lift back on service.
MSA-DCA | WA3664161 | Lift 5 One of the in-car display screens is blank | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMP | 07 Oct 2020 | 2020-10-14 17:00:00 | 2021-10-07 13:29:00 | Fail | job completed - no charge
MSA-DCA | WA3664436 | far side CPP carpark entrance stairwell leaking tap | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 0 | CLOSE | 07 Oct 2020 | 2020-10-07 15:46:14 | 2020-10-07 13:30:00 | Pass | Replace faulty tap in orchard garden with new tap
MSA-DCA | WA3664597 | Graffiti on the left side of the PICA tower | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 10:15:00 | Pass | Job completed - Graffiti due to vandalism
MSA-DCS | WA3664011 | Lenard - Fire alarm system is not activating | Banksia Hill Detention Centre | WSM-BR-SITE | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 07 Oct 2020 | 2020-10-07 11:12:14 | 2020-10-07 09:59:00 | Pass | BG 7/10/20Attended site to investigate Lenard wing fire alarms not activating. Pod officer informed that staff attempted to set off fire alarm by burningtoast in all wings. Upon investigation found all detection to be thermal, hence no activation. Tested thermal detection, all worked okay. Lenardshowing O/C fault and detection stuck in alarm. Unable to reattend Lenard wing due to site shut down. Will require return visit to investigatefurther.BG EI 12/10/20Reset loop in field, alarm cleared.
MSA-DCS | WA3664053 | Zone 6 B Microphonics not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 07:46:26 | 2020-10-07 09:30:00 | Pass | Reterminated the cables in the Sensitive/Non-sensitive Splice kit join. Replaced cable ties. Calibrated and tested back to the gatehouse ok. Parts used:Consumables
MSA-DCS | WA3664065 | Unit 14 - A & C cell C06 shower screen is leaking | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 07 Oct 2020 | 2020-10-13 17:00:00 | 2020-11-11 11:00:00 | Fail | RE sealed shower screen
MSA-DCS | WA3664068 | Double 10 amp GPO in kitchen damaged & requires replacing-see notes | Boronia Pre-release-AM08 - Prisoner Accommodation House 3-Ground Floor-Kitchen Area | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 10:30:00 | Pass | Replaced cracked power outlet in house 3 kitchen.
MSA-DCS | WA3664082 | Abattoir 2 broken switches in abattoir packing area | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 09:30:00 | Pass | Investigate and replace broken switches in abattoir packing area
MSA-DCS | WA3664160 | Unit 2, D7 - Main Door Lock Jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 09:06:10 | 2020-10-07 13:15:00 | Pass | Attended site. Repaired main door lock by replacing faulty component. Normal function restored.
MSA-DCS | WA3664166 | Crisis Care unit - cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 09:13:51 | 2020-10-07 10:30:00 | Pass | Staff in the CCU and Health centre unaware of a fault or who called it in. All intercoms in CCU tested back to CCU control. All ok.
MSA-DCS | WA3664211 | Reset centre female toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 09:49:48 | 2020-10-07 13:05:00 | Pass | Unblcoekd drain
MSA-DCS | WA3664223 | unit 3 C wing day room window smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 09:59:01 | 2020-10-08 11:00:00 | Fail | day room window replaced
MSA-DCS | WA3664224 | Unit 2, A&C - Drawers are all falling off runners | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-11 13:15:00 | Fail | RE NEWED DRAWER RUNNERS TO KITCHEN UNIT
MSA-DCS | WA3664235 | Unit 2, C2 - Cell call unclear | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 10:08:53 | 2020-10-07 16:58:00 | Pass | Removed intercom from bed head. Used new PCB and speaker with the cleaned original plate due to the odd size of the bed head cutout. Secured and tested. Loud and clear in cell and in control. Parts used:CellGuard intercom CI-CCConsumables
MSA-DCS | WA3664241 | Unit 1, control room - cell call handset damaged cord and sticky button | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 10:13:18 | 2020-10-07 15:00:00 | Pass | Removed CI-OH handset and replaced with CG-OH. Replaced cabling from hand set to officer station. Tested multiple cell intercoms and PA. Tested ok. Parts used CellGuard CG-OHConsumables
MSA-DCS | WA3664244 | MPU (8) - M10 Lock is damaged. Cannot turn. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 10:17:33 | 2020-10-08 15:15:00 | Fail | Remove main lock for repairs in workshop, rebuild lock in workshop. Re install lock with new fixings.
MSA-DCS | WA3664247 | Electrical Service Duct - Small explosion from Electrical service duct on roof | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 10:20:32 | 2020-10-07 15:00:00 | Pass | Duct explosion investigated
MSA-DCS | WA3664296 | obs post 4 corner of perimeter bee hives - see notes | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 13:30:00 | Pass | Carried out a service for bees at Hakea Prison. Here were reports of bees located at obs tower 3 and the sogs armory. Upon further inspection bees were located in both areas. Due to entering the cavity of both areas the bees could not be safely removed and had to be treated. Thoroughly dusted all entrance points of the cavity in both areas.
MSA-DCS | WA3664301 | Reset Centre Hakea grounds Broken down pipe that runs of the front veranda | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-14 09:00:00 | Fail | Removed remainder off x2 broken down pipes and installed x2 new ones
MSA-DCS | WA3664358 | gate control main prison, no access to unit 6 site map-SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-07 14:30:00 | Pass | Noted that there were no “Quick Links” on Medium Prison Main Site plan to connect to Unit 6 Site plans. Programed quick links on Main Medium Prison Site map and on the perimeter site map. Programmed return links to Perimeter and overall site plans on Unit 6 Main page. Programmed quick links from Unit 6 wing pages to Unit 6 main page.
MSA-DCS | WA3664362 | unit 6 auto arming timing incorrect-Seme on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2021-01-21 16:00:00 | Fail | Install NTP server, GPS antenna and associated cabling
MSA-DCS | WA3664365 | unit 6 multiple alarms to gate control for no reason programming issue- Seme on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-18 12:05:00 | Fail | Incorrect programming from unit 6 build (by others) amended.
MSA-DCS | WA3664419 | Kerry Building - main sewer pipe is blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 11:40:27 | 2020-10-08 12:30:00 | Fail | COMPLETED
MSA-DCS | WA3664448 | Visits - Table 1 for E- Visits Microphone not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-07 17:00:00 | Pass | Job to be referred to DCS IT branch. Appears to be table 2 with the issue not table 1.
MSA-DCS | WA3664452 | Unit 8, B wing - The film of the sensor at the top of B wing by the common room grill, has been push | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-04 09:30:00 | Fail | Replaced damaged PIR with new and tested ok, job completed.
MSA-DCS | WA3664467 | Staff room east - Two fluorescent lights need repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-13 09:30:00 | Fail | Repaired flouros in staffroom East
MSA-DCS | WA3664478 | Unit 2 - B5 Door latch has broken off and needs relacing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 15:30:00 | Pass | Replace door plate, lock, repair door frame and weld on strike plate.
MSA-DCS | WA3664483 | unit 7 H21 The cell light only works from outside & not inside | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 09:30:00 | Pass | Repaired light
MSA-DCS | WA3664486 | Unit 7, E wing showers - The far R/H shower Continuously running can’t be turned off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-14 10:00:00 | Fail | Turned off water rewashering x2 taps
MSA-DCS | WA3664491 | unit 6 D8 Sink slow drain When plunger used water comes out of the floor drain beneath sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-14 11:50:00 | Fail | Drain machine used to unblock drain removing sponge cloth
MSA-DCS | WA3664512 | Mitchell House - blocked sewer line - sewage backing up | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 07 Oct 2020 | 2020-10-07 16:51:36 | 2020-10-21 12:50:00 | Fail | COMPLETED
MSA-DCS | WA3664527 | Bakery belt on dough sheeter is becoming tattered and freyed | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-16 16:30:00 | Fail | 09/10/2020Check dough sheeter Customer would like both sheets replaced Parts and labour require investigating. 16/11/2020Sign in and get escorted to site Carry out replacement of sheets Test unit ok.Put back in storage
MSA-DCS | WA3664543 | Kitchen Drainage pipe snapped off wall outside loading fridge (coolroom 5) bottom L/H side of door | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 14:59:00 | Pass | Repaired PVC drain for cool room. All ok.
MSA-DCS | WA3664545 | public toilet is blocked | Mandurah | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 13:38:29 | 2020-10-09 12:00:00 | Fail | Used drain camera and water jetter to remove wipes from main sewer line.
MSA-DCS | WA3664618 | Inner perimeter microphonics damaged | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 14:46:46 | 2020-10-21 15:17:00 | Fail | Travelled to site and replaced 20 metres of intelliflex cabling from seme stock, replaced with 2 x splice kits seme stock. All connected cable tied and retested and working ok. Job complete
MSA-DCS | WA3664650 | Unit 1 A13 Double GPO broken out of the wall | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 15:10:54 | 2020-10-08 08:30:00 | Pass | Replaced damaged cell switch and gpo in unit 1 a13
MSA-DCS | WA3664697 | Gate house, security camera is not working properly | Pardelup Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 17:10:18 | 2020-10-07 19:00:00 | Pass | Contacted Pardelup Operations Officer Paul, who explained the Monitor started playing up when they used a handheld radio beside the monitor (base radio had a Fault). Paul had power reset the monitor which appears to have resolve the issue. I recommended that hand held radios should be at least a metre away from the monitor before using.
MSA-DCS | WA3664709 | External perimeter from zones 1 - 11 are down on security system after a lightning strike | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Oct 2020 | 2020-10-08 03:11:04 | 2021-03-12 16:23:00 | Fail | Repaired multiple perimeter faults and tested OK.Job Complete
MSA-DFES | WA3664417 | L2 room Nancy Appleby door latch mech faulty - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 12:45:00 | Pass | Reinstalled striker plate. Mechanism now working correctly
MSA-DTAG | WA3664147 | 1987 L3 Skirting carpet tile has become detached – corridor adjacent to Court 11 | Supreme Court | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 09:30:00 | Pass | Restuck skirting carpet tile l3 corridor
MSA-DTAG | WA3664151 | L5 Skirting near Magistrates lift is missing | Central Law Courts | GMP-BR-HO | Flooring | Timber (FL) | Midolo Building Services | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-08 13:45:00 | Pass | NEW ALI SKIRTING INSTALED
MSA-DTAG | WA3664157 | L5 court 52 Skirting carpet tile behind Magistrates bench is peeling off | Central Law Courts | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 07:45:00 | Pass | Restuck skirting carpet tiles l5 court 52 behind magistrates bench
MSA-DTAG | WA3664159 | St Georges Terrace end - Interview room 5.4 - replace approximately 9 stained carpet tiles | Central Law Courts | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 08:30:00 | Pass | Replaced stained carpet tiles
MSA-DTAG | WA3664449 | External light globe & bulb have been smashed | Joondalup Courthouse | GMP-BR-HO | Electrical | Lighting, External (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-16 11:30:00 | Fail | Replaced pole light and tested working
MSA-DTAG | WA3664454 | 1987 L2 sherriff's office Several A/C ceiling outlets are not sitting correctly - affecting the air | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-27 08:21:00 | Fail | 1st run 2x spigots in front of #1 #8 blanked off with silver tap and cable ties flex removed from ceiling. Reattached #1 troffer to flexible duct cable tied and silver taped, reinstalled correctly into light fittings. #2 #4 #5 reinstalled correctly into light fittings and repositioned into nearest correct places. #6 modified troffer to allow it to fit into light fitting above false wall. Reattached #7 troffer to flexible duct cable tied and silver taped, reinstalled correctly into light fittings. #8 #9 reinstalled correctly into light fittings and repositioned into nearest correct places. # 11 replaced troffer with correct 150 spiggot size and modifed to allow fitting over false wall. #13 replaced troffer with correct spiggot size and double troffer a single troffer was installed incorrectly. 2nd run #4 #2 #1 #7 reinstalled correctly into light fittings and repositioned into nearest correct places. #25 new spiggot cut into main run fastened, glued and reinsulated. New flexible duct ins
MSA-DTAG | WA3664456 | 1987 L2 sheriff's office Several supply air troffers are not connected or blocked | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-27 08:46:00 | Fail | 1st run 2x spigots in front of #1 #8 blanked off with silver tap and cable ties flex removed from ceiling. Reattached #1 troffer to flexible duct cable tied and silver taped, reinstalled correctly into light fittings. #2 #4 #5 reinstalled correctly into light fittings and repositioned into nearest correct places. #6 modified troffer to allow it to fit into light fitting above false wall. Reattached #7 troffer to flexible duct cable tied and silver taped, reinstalled correctly into light fittings. #8 #9 reinstalled correctly into light fittings and repositioned into nearest correct places. # 11 replaced troffer with correct 150 spiggot size and modifed to allow fitting over false wall. #13 replaced troffer with correct spiggot size and double troffer a single troffer was installed incorrectly. 2nd run #4 #2 #1 #7 reinstalled correctly into light fittings and repositioned into nearest correct places. #25 new spiggot cut into main run fastened, glued and reinsulated. New flexible duct ins
MSA-DTAG | WA3664466 | L2 sheriffs office Fault description A/C flexible ductwork above administration area is broken | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-27 08:39:00 | Fail | 1st run 2x spigots in front of #1 #8 blanked off with silver tap and cable ties flex removed from ceiling. Reattached #1 troffer to flexible duct cable tied and silver taped, reinstalled correctly into light fittings. #2 #4 #5 reinstalled correctly into light fittings and repositioned into nearest correct places. #6 modified troffer to allow it to fit into light fitting above false wall. Reattached #7 troffer to flexible duct cable tied and silver taped, reinstalled correctly into light fittings. #8 #9 reinstalled correctly into light fittings and repositioned into nearest correct places. # 11 replaced troffer with correct 150 spiggot size and modifed to allow fitting over false wall. #13 replaced troffer with correct spiggot size and double troffer a single troffer was installed incorrectly. 2nd run #4 #2 #1 #7 reinstalled correctly into light fittings and repositioned into nearest correct places. #25 new spiggot cut into main run fastened, glued and reinsulated. New flexible duct ins
MSA-DTAG | WA3664474 | 1987 L2 sheriff's office Several temperature sensors require to be re-located | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-12-14 14:41:00 | Fail | Icon logic installed additional averaging sensors as per quote. Commission operation, working ok.
MSA-DTAG | WA3664645 | Basement server room door Door isn’t locking Pacom isn’t registering a fault | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 09:30:00 | Pass | Door handle found unlocked - relocked and lubricated lock retested ok.
MSA-DTAG | WA3664684 | ground court 6 waiting room Light switch not turning any lights on or off-see notes | Perth Children's Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 10:00:00 | Pass | Attended site and signed in. Located waiting room for court 6. Found switch panel behind door. 2 x switches were faulty and not working. Removed panel and switch mechs and replaced 2 x switches. Realigned and adjusted the switch mech panel and re instate cover correctly. Tested all okay. Job complete
MSA-DTWD | WA3664074 | A block L1 A132 female toilet 3rd toilet pan is leaking.(Middle cubicle) | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 16:45:00 | Pass | installed new pan collat and pipework in pan line
MSA-DTWD | WA3664174 | Building 2, ground, Support Staff lunchroom - Boiling water unit won’t stop boiling and overflowing | Thornlie Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 15:00:00 | Pass | Replaced solenoid valve, level sensor and main PCB board
MSA-DTWD | WA3664177 | F block, FG04 - leaking tap | Carlisle Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 14:58:00 | Pass | Replaced taps
MSA-DTWD | WA3664250 | L4 tower block light flickering on the west side-please check canteen lights | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 14:48:00 | Pass | Repaired faulty lighting . Job completed
MSA-DTWD | WA3664374 | A block ground AF13 Wilson water unit no hot water - see notes | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 11:45:00 | Pass | REPLACED ALL 3 SOLENOIDS ON WILSON REPLACED MULTIPLE FITTINGS, RETUBED AND REPLACED PRESSURE RELIEF VALVE ON UNIT TESTED OK
MSA-DTWD | WA3664389 | D block L1 plant room- 2x sprinkler monitor valve faulty | East Perth Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-22 14:51:00 | Fail | Investigate monitor valve issue Short circuiting and requires replacing to return to site22/10/20Repaired and replaced x2monitored valves
MSA-DTWD | WA3664397 | D block L1 DBA switch faulty | East Perth Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-22 14:52:00 | Fail | Replaced time delay pressure switch and checked for operation
MSA-DTWD | WA3664399 | E block L1 fire bell faulty | Mount Lawley Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-15 15:00:00 | Fail | Bell replaced
MSA-DTWD | WA3664427 | L1 fire pump room Module to Electric pump faulty | Leederville Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-23 14:00:00 | Fail | 1 issued resolved, further time required to investigate faulty loop 1.
MSA-DTWD | WA3664462 | S block lift has stopped working | Mount Lawley Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-07 13:30:00 | Pass | NON CHARGEABLE
MSA-DTWD | WA3664476 | G block, Gas storage facility - Acetylene gauge not working | Mandurah Campus (formerly Peel) | GMP-BR | Mechanical Services | Storage Tanks (MS) | BOC | 1 | CLOSE | 07 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 09:00:00 | Pass | job completed - Replace Acetylene manifold contents gauge.Attach all info & pics to GeoOp
MSA-DTWD | WA3664480 | L1 beauty clinic Blinds fell off the wall | Perth Campus B2 | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-27 11:27:00 | Fail | completed & Invoiced
MSA-DTWD | WA3664481 | Level 3, Staff male toilet - Dripping water tap | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-07 16:00:00 | Pass | Repair leaking tap
MSA-DTWD | WA3664547 | Building 10, 10G74 - 4 faulty lights | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-22 08:15:00 | Fail | Attended site and signed in. Got keys from facilities. Accessed room 10g74. Isolated light fittings and dismantled to access ballasts. Disconnect and removed ballasts. Supply and replace 2 x 58w ballasts. Re assembled light fitting parts. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3664548 | Building 10, 10G75 - faulty lights 3 not working 1 flickering | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-08 15:30:00 | Pass | Attended site, signed in, spoke to fm,located lighting, changed various tubes,starters and lampholders(client supplied lampholders) , tested and all working , cleaned up work area, completed paperwork, signed out ***job completed ***
MSA-DTWD | WA3664583 | L4 workshop Several high level ceiling lights not working. | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 15:30:00 | Pass | Attended site and signed in. Located L 4 workshop. Found faulty light fittings over work bench. Removed old fittings. Supply and replace with new led battens. Replaced switch with 2 gang. Tested all okay. Job complete
MSA-DTWD | WA3664629 | block 9 Broken skylight panels of roof of covered area – north side of library | Thornlie Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 07 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-22 14:30:00 | Fail | Replaced aged skylight sheeting as requested by site
MSA-DTWD | WA3664685 | F-Block Room FG31 - Faulty Pendant power point, may need replacing &new chain | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 12:45:00 | Pass | Attended site, signed in, spoke to fm, located pendant gpo that needed replacing, completed jsa, went to wholesaler to pick up materials, isolated ircuit , removed old gpo , replaced with new, pushed cable back into ceiling rose to rectify exposed cables , tested gpo , working as intended, cleaned up work area , completed paperwork, signed out ***job complete***
MSA-DCA | WA3665169 | Steam room Boiler 1 & 2 have gone into alarm | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 08 Oct 2020 | 2020-10-08 17:00:00 | 2020-10-08 08:00:00 | Pass | AGWA Call-out.Fire alarm activated over night. Steam Boilers 1 and 2 faulted on Low Gas Pressure. Manual reset. Monitored start-up and cycling to SP.Alarms cleared.Closed job.
MSA-DCA | WA3665549 | Access toilet Single flush button does not work. Full flush button not working very well.-see notes | Swan Bell Tower-Main Building-Level 1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-09 12:00:00 | Pass | Relaced rubber on the button and bellows
MSA-DCS | WA3664834 | Gatehouse Camera 24, 94 & 137 have no pictures | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 11:12:16 | 2020-10-08 14:25:00 | Fail | Repaired faults with cameras after lightning strike.Tested OKJob Complete
MSA-DCS | WA3664848 | master control room - cant access perimeter or alarms on PC | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 11:22:57 | 2020-10-08 09:30:00 | Pass | Travelled to site and reset KVM extender and workstation located in upstairs comms room. Reconnected to Gallagher and tested PC functions. All tested and working ok. Job complete
MSA-DCS | WA3664864 | Control cant arm the fence - Zone 8. 9, 11 & 12 constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 11:31:49 | 2020-10-08 16:15:00 | Fail | Repaired controller fault which was causing Zones 8 and 9 faults. Tested Ok.zones 11 and 12 being repaired on job WA3664618
MSA-DCS | WA3664879 | Various perimeter faults caused by lightning | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 07:34:55 | 2020-12-17 11:20:00 | Fail | Repaired multiple faults across prison after lightning storm.Tested OKJob Complete
MSA-DCS | WA3664892 | Unit 1 - B10 toilet water running overtime. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 12:44:00 | Pass | Nill
MSA-DCS | WA3664928 | Gatehouse - Key control CCTV not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 08:08:33 | 2020-10-08 17:15:00 | Pass | CCTV monitor-restarted Maxpro keyboard and logged into it. Setup monitor with the correct display setting. MDAS monitor-repaired issue with KVM extender in key control. Tested ok.
MSA-DCS | WA3664929 | control office A few carpet tiles coming up have lifted, been taped down, trip hazard needs repair | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2021-01-06 11:00:00 | Fail | DAMAGED CARPET TILES REPLACED WITH NEW
MSA-DCS | WA3664962 | pump house Issue with Controller to pump, pump not engaging, working intermittantly | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-14 10:15:00 | Fail | Fixed the issue but additional work required and further work orders to be raised to fix additional issues.
MSA-DCS | WA3665128 | Gatehouse - Senstar network fault | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 14:22:49 | 2020-10-08 12:00:00 | Pass | X and Y faults on all Senstar Modules.traced fault to EC12, Intelliflex module has 48vdc but no LED to indicate if online.power-cycled, LED's showing online.Cleared faults on Senstar system and tested various zones.all activated
MSA-DCS | WA3665134 | Gatehouse - Visits camera offline | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 10:25:19 | 2020-10-08 11:30:00 | Pass | Network dropping offline intermittently,checked network switch settings in Visits, power-cycled and checked network switch in Comms room.tested different SFPs and restored linkreplaced MGB-SX (LC-550m) 1000base-SXmultimode DDM 850nm1.25Gbps in both from Seme stock.Visits Workstation unable to connect to server.re-terminated RJ45 connections and confirmed ok
MSA-DCS | WA3665202 | Karakin wing B – Replace 8 smashed windows | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 14:30:00 | Pass | ALL SMASHED WINDOWS RE GLAZED
MSA-DCS | WA3665245 | Unit 4 - D Wing window seal/surround is broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 12:00:00 | Pass | CELL D13 WINDOW NEW BALANCERS FITTED & RE SEALED
MSA-DCS | WA3665251 | Health store room tap leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-12 13:42:00 | Pass | Reseat and rewasher kitchen taps
MSA-DCS | WA3665299 | Swipe access door Door is not closing properly - see notes | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-15 12:30:00 | Fail | Attended site and carried out repairs to the swipe access door that was not closing properly.
MSA-DCS | WA3665314 | Abattoir switch board in skin shed damaged | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-16 12:30:00 | Fail | Investigate abattoir skin shed control board.Source parts.Repair abattoir skin shed board.
MSA-DCS | WA3665333 | gate house camera 1 has failed - SEME on site | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 12:14:30 | 2020-10-08 14:27:00 | Pass | Power cycled gatehouse camera.Replaced 5vdc power supply from PFM site stock For camera 5-1 and 10-1
MSA-DCS | WA3665335 | gate house network fault zone 76 - SEME on site | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 12:16:54 | 2020-12-15 14:30:00 | Fail | Found and corrected issue with redundant loop and network setup. standardised network switch IP address and camera network protocols. found and removed old stp programming in EC switch’s. standardised Stp in all loop switch’s updated IP map. System now has reduced network load and faster response times camera glitches and drop out have reduced. Redundant loop back in operation.
MSA-DCS | WA3665351 | Unit 1, B16 - Cell Door Dropped jamming on the floor top hinge bolt heads stripped | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 12:26:48 | 2020-10-08 15:30:00 | Pass | Attended site and carried out repairs to the cell door that was jamminig and unabled to be closed.
MSA-DCS | WA3665359 | BA store west storeroom roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-12-17 14:00:00 | Fail | roof repaired to rectify leaking
MSA-DCS | WA3665379 | Stores, entrance - The Street lights in the carpark/Road (The really tall ones) are not coming on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-09 15:00:00 | Pass | Investigated tripping street lights circuits, split circuits in field, found and repaired damaged cable. Left order open to monitor lights. Re-checked all ok.
MSA-DCS | WA3665426 | Unit 2 C7 cell call faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 13:33:59 | 2020-10-08 15:45:00 | Pass | Attended site checked and found Unit 2 C7 cell call point LED stuck on red and can’t make cell call. Reboot cell call point and node in office. Connected cell call to C7 from office ok. Tested cell call from C7 to office and confirmed both sides loud and clear.
MSA-DCS | WA3665430 | kitchen dishwasher 3 Phase Electrical Conduit coming away from wall | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 13:39:30 | 2020-10-08 15:45:00 | Pass | Repaired exposed cable
MSA-DCS | WA3665432 | unit 4 B15 tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-14 13:30:00 | Fail | Removed basin replacing pillar tap
MSA-DCS | WA3665453 | Main Building & Gwynlea Building fluro's not working | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 12:00:00 | Pass | Repaired lighting in main building and Gwynlea.
MSA-DCS | WA3665467 | Perimter fence - G4 outer voltage outer defence | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 18:25:11 | 2020-10-09 14:00:00 | Fail | Attended site and found electric fence zone G4 connectors damaged causing fence to be in constant alarm. Technician re attended site and replaced 2 x fence zone Gallagher connectors. Seme stock used.All replaced and tested ok. Job complete
MSA-DCS | WA3665471 | Unit 10, C2 - 4 of the screw heads are snapped off on second hinge down from top on door frame, | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-13 09:45:00 | Pass | 12/10/2020. Attended site. Could not access job due to sudden operational issue.13/10/2020. On site. Drilled out broken screws, re-tapped threads in holes to M5. Supplied and fitted new security screws.
MSA-DCS | WA3665473 | unit 1 fire pump house bearings faulty | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-15 16:15:00 | Fail | Unit 1 Fire pump house bearings faulty. Check pump & controls, found to have faulty bearings. Remove to workshop. Dismantle motor, fit new bearings, tropic proof windings, clean all. Return to site, install, connect wiring. Assemble all & test. Set to auto.
MSA-DCS | WA3665576 | Education, rear of room 11 art center - serious water leak from burst water pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 20:36:44 | 2020-10-09 09:30:00 | Fail | Nikl
MSA-DFES | WA3664976 | applied training ground suction hose has blown off pump No2 at the bottom dam- notes | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 12:36:29 | 2020-10-29 15:00:00 | Fail | confirmed works complete by malcolm thompson pumps all ok
MSA-DFES | WA3664978 | Damaged/broken blinds throughout building | CFRS Welshpool | GMP-BR | Furniture | Indoor Furniture (FU) | AWB Co. | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-11-05 15:00:00 | Fail | Works completed as per quote/BRAF
MSA-DFES | WA3665353 | kitchen & training room 2x LED strip lights not working kitchen - 1x LED strip light in the training | CFRS Wangara | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 15:45:00 | Pass | Locate faulty lights. Staff advised the lights would be unplugged has it was too bright. Investigate why the lights were not working and found in the kitchen the lights are wired so they would not work. Require the lights so they would work. Once rewired the lights worked. In the training room the light was unplugged. Plugged the light back in and it worked. Discussed with staff on site and they advised they would like the light to remain off. I left the 3 lights unplugged.
MSA-DFES | WA3665544 | Lounge room - TV gives a message of poor reception or faulty aerial connection | CFRS Armadale | GMP-BR | ICT/Audiovisual | General AV works (AV) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 16:15:00 | Pass | Investigated signal issue with Channel 2 and 24. Located point and discovered it was connect via and old redundant saddle type connection.we installed a compression crimp and channels are working correctly. Notified staff and left site
MSA-DTAG | WA3665109 | L6 Lift 3 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMP | 08 Oct 2020 | 2020-10-15 17:00:00 | 2021-10-08 13:10:00 | Fail | When responding to the callback dated 08.10.2020, the Schindler Technician found a problem with your equipment. Some componentsof the car door operator were faulty. Following our attendance, the equipment was not put back into service. We are taking allthe necessary steps to return the unit to service as soon as possible.
MSA-DTAG | WA3665131 | Investigate core switch A dropping out | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-08 16:00:00 | Pass | job completed - Investigated Core Switch A, constantly failing and end of life. Recommend replacing switch. Works will be completed under WA3681890.
MSA-DTAG | WA3665286 | ground Garden bed facing McIver train station Sprinkler broken- water leaking freely | Perth Children's Court | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-17 12:00:00 | Fail | 14/10/20 Dom Coniglio - 1.25 Hrs Labour17/10/20 Rob Reynolds - 4 Hrs LabourRetic Parts $89.00
MSA-DTAG | WA3665309 | ground rear courtyard Sprinkler broken- instead of spraying at 180 degrees it’s spraying in a jet | Perth Children's Court | GMP-BR-HO | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 11:30:00 | Pass | Dom Coniglio Call Out & Labour & Parts
MSA-DTAG | WA3665438 | L10 front counter Light in Registrations area above Katarina has been flickering and needs replacing | Westralia Square | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-13 08:00:00 | Pass | Attended site and signed in with security. Got access to level 10 for security escort. Located katarinas desk and faulty light fitting. Replaced tubes and starters to light fitting and tested all okay. Signed out with security. Job complete
MSA-DTAG | WA3665475 | 1903 ground courts 1 & 3 isolation - see notes | Supreme Court | WSM-BR-SITE | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-10 19:00:00 | Pass | 9/10 16:30hrsAttended site and isolated vesda for courts 1 & 3 and Zones 1 ,3 , 12 & 13 for works in courts.20:45hrsAttended site and de isolated vesda for courts 1 & 3 and Zones 1 ,3 , 12 & 13 for works in courts.10/10 5:45hrsAttended site and isolated vesda for courts 1 & 3 and Zones 1 ,3 , 12 & 13 for works in courts.17:45hrsAttended site and de isolated vesda for courts 1 & 3 and Zones 1 ,3 , 12 & 13 for works in courts.Left system normalTold work completed and no isolations required on Sunday.
MSA-DTAG | WA3665553 | Check network failures, multiple outages between master and slave servers | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2021-05-17 16:00:00 | Fail | Reconfiguration of network switches for Vlan database and routing protocols and switch port interface configurations for all switches between DMJC and SAT
MSA-DTAG | WA3665579 | Basement, Security -Pacom System keeps logging out intermittently – contact Luke Asplin 9221 3141 | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-09 13:30:00 | Pass | Attended site. Work station time was out by approximately 2 minutes. Adjusted time to match the other work station. Pacom no longer logging off randomly.Job completed
MSA-DTWD | WA3664934 | block 6 ground cabinet making Power point broken in 6D27 work shop near lectures bench | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-08 13:30:00 | Pass | Attended site, signed in, spoke to fm about job, located gpo that needed replacing, completed jsa,located dB that circuit was powered from, isolated circuit, removed old gpo and mounting block, replaced with new , tested and working as intended, cleaned up work area, completed paperwork, signed out ***job complete ***
MSA-DTWD | WA3664940 | T Block – G.F female student rear of café.Toilet pan block x1 | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-08 15:16:00 | Pass | Unblocked toilet t block
MSA-DTWD | WA3664951 | West block L1 Sewerage smell near West Block link to North Block | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-13 13:00:00 | Pass | inspected issue , no issue present . Maintenance officer says issue has been resolved.
MSA-DTWD | WA3664981 | B block L1 B107 Male toilet near B107 has water leak in ceiling | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 11:45:00 | Pass | water damage to ceiling was caused by a leaking pan collar from the floor above. I exposed the back of the pan and cut out and replaced neccesary pipework/pan adaptor.
MSA-DTWD | WA3664999 | T Block Car Park Bin Bay retaining Damp patches on L shaped rendered bay retaining walls-see note | Murdoch Campus | GMP-BR | Building | External Walls (BU) | AWB Co. | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-11-30 12:15:00 | Fail | Supply and install new 7 metre flashing to enclose gap between wallSupply all accessories required to fix and seal in placeReseal any perished seals to capping of brickworkRemove all waste from site on completion of work
MSA-DTWD | WA3665041 | E block kitchen E30 roof leak over bench 2 and 3 | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-29 09:45:00 | Fail | Sealed leak with Storm seal silicone
MSA-DTWD | WA3665045 | E block kitchen E30 east end entrance door closer faulty | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 08:00:00 | Pass | Door closer replaced and now door in working order
MSA-DTWD | WA3665047 | E block kitchen E30 bench 13 leaking taps | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-13 13:27:00 | Fail | Replaced taps in commercial kitchen sink. Could not complete paperwork on time due to ProMAP app causing issues.
MSA-DTWD | WA3665052 | D block D1 kitchen cracked pendent GPO | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-09 08:15:00 | Pass | Attended site and signed in, repaired broken suspended gpo. Tested, job complete.
MSA-DTWD | WA3665221 | Old Murdoch C15 Disabled toilet Blocked pan blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-08 15:17:00 | Pass | unblocked toilet
MSA-DTWD | WA3665231 | C block female toilets 1st Floor Ladies toilet 1st cubicle blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-20 15:45:00 | Fail | COMPLETED
MSA-DTWD | WA3665274 | S block student services fire panel door cannot with key | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 08 Oct 2020 | 2020-10-08 15:24:47 | 2020-10-08 12:10:00 | Pass | Service lock on fire panel
MSA-DTWD | WA3665347 | S8 plant room Filter 5 , AHU1 Solenoid engaging and making a loud noise. | Murdoch Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-16 15:00:00 | Fail | Replaced ahu 1 return air damper actuator
MSA-DTWD | WA3665349 | south block L1 plant room AHU 6 not running | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-09 13:19:00 | Pass | Attended site gained access and carried out inspection of A/C 6. OAF and main AHU both found to have no control enable. Located control breakers and found A/C 6 tripped. Reset and placed equipment into operation test. Units started and coms enable re established placed back into auto operation. While in plant room noted A/C 7 and 9 has been left in the off position on MSSB. Confirmed with site FM David Gaff and placed back into Auto. A/C 5 was also noted not to be operating. Control braker located and found tripped. Reset but still would not come back online. Control fuse was located power isolated fuse removed tested and replaced with onsite spare. Restored power and equipment put into test mode. Operation restored. Unit moved into auto operation. Power fluction may have led to breaker trip. bMS control upgrade is currently occuring in site.
MSA-DTWD | WA3665361 | B-Block, Room BG16 - External door to BG16 needs hinges tightened & possibly reset. Door jamb may | Carlisle Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-16 14:30:00 | Fail | Repaired door frame and rehung door. Fitted new door closer as requested by site
MSA-DTWD | WA3665416 | S-Block room S009 entrance has a broken inspection cover drain lid | Joondalup McLarty Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-29 15:30:00 | Fail | Arrived at site, inspected faulty water cover. Has rusted out on the hinge. Requires a new Galvins 300mmx400mm concrete surround and lid. Please allow Liam or myself 2-3 hours to pick up materials and install.Picked up materials on way to site. Arrived at site, signed in and set up work area. Removed paving and dug up existing cover. Installed new cover and filled in. Leveled area and re layed pavers. Tidy area, packed away tools. Complete. Will get FM to sign on Monday,
MSA-DTWD | WA3665429 | L Block Lift is not working | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-10-09 13:15:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close work order
MSA-DTWD | WA3665448 | A & F Blocks Evap A/C water supply lines leaking | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-14 16:00:00 | Fail | Filled out roof access form , accessed the roof and welded up the main water line to the evap coolers on f block . Test ran all ok
MSA-DTWD | WA3665478 | O block, workshop - Sectional door not opening at the rear of the welding workshop | Balga Campus | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 08 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 10:30:00 | Pass | Program asset number is A40437444J our asset number 1091731Full service and safety check. All lubrications applied.Unable to repair manual release mechanism.Tested in operation and all ok!
MSA-DTWD | WA3666246 | B block BG6 spray booth Faulty Spray Booth Exhaust Stack Damper-see notes | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 08 Oct 2020 | 2020-10-09 17:00:00 | 2020-11-18 17:30:00 | Fail | Works complete
MSA-DCA | WA3666290 | fire exit for the bar, alarm cable has detatched from the wall and needs investigating | PICA-Main Building-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 11:00:00 | Pass | Please see images, job referred onwards. Completed
MSA-DCA | WA3666476 | make safe light in supply water is coming into toilet | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Male Toilet | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 12:30:00 | Pass | As requested make safe for roof repairs. Isolated at DB. New job required for reconnect
MSA-DCA | WA3666679 | Kitchen lift has stopped | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Lift Car | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 14:41:00 | Pass | job completed - Found rope brake engaged with fault 3 on display, informed supervisors, reset and Tested , left lift running
MSA-DCA | WA3666771 | ground staff kitchenette Dripping tap in the downstairs - see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Workshop | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 17:50:00 | Pass | Replaced leaking and coroded kitchen set
MSA-DCS | WA3666178 | Abbatiors - #4 freezer is not working | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 09 Oct 2020 | 2020-10-10 07:18:13 | 2020-10-14 13:00:00 | Fail | Attend site found freezer controller faulty , replace controller and test also found door switch and fan motor faulty and replace both , left system operational
MSA-DCS | WA3666198 | Zone 11, keeps activating | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Oct 2020 | 2020-10-10 07:27:47 | 2020-10-09 12:03:00 | Pass | Checked calibrations, found zone extremely sensitive. adjusted pot right back and calibrated monitored for 45minutes and confirmed no false activations
MSA-DCS | WA3666234 | Unit 2 - B8 strike plate snapped of frame | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 09 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-09 11:30:00 | Pass | Replace door plate lock and weld on strike.
MSA-DCS | WA3666236 | Kitchen - hot box has dropped an element | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 09 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-20 14:45:00 | Fail | Replaced faulty lower element foil pad & test ok.
MSA-DCS | WA3666301 | Unit 9 D16 When sink is being emptied water coming up through floor drain, blocked needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-23 10:35:00 | Fail | Removed floor grate removing rubbish and used plunger to clear blockage
MSA-DCS | WA3666303 | stores loading dock Water Cooler/ Drink fountain, has been unplugged keeps tripping circuit breaker | Hakea Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 14:00:00 | Pass | Repaired water fountain
MSA-DCS | WA3666310 | Boilerhouse Boiler 3 Leak in blowdown pipe | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-11-13 12:30:00 | Fail | Pre Fab pipework in Boilertronics workshopTravel to site, signed in on arrival and met with escort.Removed blowdown pipe work on Boiler # 3 and replace with new pipe work. Run boiler up to temp and test for leaks, no leaks were present so brought the boiler back online. Boiler had a fault which I reported to the Jim onsite, a work request has been raised to investigate the issue.Runs ok with low fire hold on but shuts down in the auto position.Left the boiler burner in the off positionRemoved all the old pipe work and rubbish from site and cleaned up work area prior to departure.
MSA-DCS | WA3666316 | Sallyport front gate pit grille Intermitantly stopping before closing | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 13:00:00 | Pass | 09/10/20Service sally port grille.Clean track, remove debris, lubricate track.Run through cycle 10 times - no issues.
MSA-DCS | WA3666339 | Electronic door lock is not working (ES2000 lock) | Boronia Pre-release-AH19 - Administration, Education Senior Officers and Programs-Ground Floor-Community Room 2 | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-15 09:30:00 | Fail | Lock replaced with ES2000 tested working ok.
MSA-DCS | WA3666487 | Unit 7, D Wing - Hot plate on the stove is not working. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-11-27 14:30:00 | Fail | 16/11/2020Turn hot plate on and found not heating at all Remove unit and test components Found unit now operating correctly Thermostat requires replacing Unit put back in place and advised manager. Parts required: 1 x Thermostat27/11/2020Sign in Wait for escort Remove and replace thermostat Heat to test ok
MSA-DCS | WA3666509 | Textiles, staff toilet - Continuing running water thru toilet system in officers toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-12 10:30:00 | Pass | Nill
MSA-DCS | WA3666544 | Unit 3, A wing - Window broken nearly falling out, metal at side broken | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 15:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3666563 | Unit 1, B12 - whole moveablew window pane has come out , its in one piece | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 09:30:00 | Pass | RE NEW SPIRAL BALANCES AND REPAIR PANE
MSA-DCS | WA3666570 | ground pilbura small kitchen No power to hydro tap unit possibly due to faulty power point on wall. | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 10:00:00 | Pass | Restored power to small kitchen auto-boil.
MSA-DCS | WA3666582 | Reception - Property Cage Door has dropped, and needs to be lifted back up. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 16:30:00 | Pass | Re install hinges with new fixings.
MSA-DCS | WA3666602 | Gate house - fire panel in fault, unable to clear - | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 09 Oct 2020 | 2020-10-09 15:34:21 | 2020-10-09 15:20:00 | Pass | Attended site and carried out the following works1: Found device 4012 Unit 1 bed 12 in missing faultDue to detector being removed from base. Re fitted and cleared fault.2: Unit 2 Side A Room 18 missing fault as detector removed from base re fitted and cleared fault.3: Unit 1 Bed 14 missing due to fault in room 12Found front main panel bell failed requires new 200mm bell to be fitted.Left panel normal14/10 KSAttended site and fitted new main bell and tested ok
MSA-DCS | WA3666633 | gym lights faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 09:00:00 | Pass | Investigate and repair lights in gym
MSA-DCS | WA3666682 | Unit 10, cells 01-08 - Lights cells 01 to 08 keep tripping circuit breaker when lights are turned of | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 10:30:00 | Pass | Lights tripping
MSA-DCS | WA3666697 | Unit 10, A05 - Sink leaking from underneath the middle spout has threaded nut split & stripped | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-23 12:20:00 | Fail | Replaced outlet and x2 quator turn taps on basin
MSA-DCS | WA3666714 | maintenance office internal store room door Lock Jamming in the door | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 09 Oct 2020 | 2020-10-10 12:12:53 | 2020-10-09 14:30:00 | Pass | Attended site. Replaced worn faceplate screws.
MSA-DCS | WA3666770 | Jeelia, A wing - bee infestation | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 09 Oct 2020 | 2020-10-10 13:00:41 | 2020-10-09 15:45:00 | Pass | Attended site and spray allethrin.
MSA-DCS | WA3666779 | kitchen Outside by the Service Road inside the Air-con Caged Area leaking tap | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-12 12:15:00 | Pass | Once located shut off valve for kitchen replaced hose Tap washer and valve
MSA-DCS | WA3666841 | Unit 1 - Control Room Unit control pannel is beeping continuously presenting follwing error-see note | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Oct 2020 | 2020-10-09 18:01:01 | 2020-10-10 09:00:00 | Fail | Cell call systems having with multiple errors from new units causing lots of issues with other controllers, advice maintenance dept. Test the cell call from unit and gatehouse control room, all back to normal operations.
MSA-DCS | WA3666847 | unit 3 cell 45 window frame and sash rotten | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2021-01-29 15:50:00 | Fail | replaced sashes
MSA-DCS | WA3666865 | Karakin, pedestrian gate lock - not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 09 Oct 2020 | 2020-10-10 14:34:28 | 2020-10-09 15:45:00 | Pass | Attended site. Realigned mortice lock and refastened. Locktite used to ensure normal function.
MSA-DFES | WA3666463 | Engine room door - faulty, securing cables have become detached, door not usable | CFRS Daglish | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 09 Oct 2020 | 2020-10-09 14:29:42 | 2020-10-09 11:45:00 | Pass | Attended site , found door had been lowered on something & cables had come out of position. Removes tangled cables , lowered door , reinstated cables into position, checked over doors for any other damage , tested operation several times, door operational but found cables had frayed, detailed for repairs.BRAF declined, job closed off.
MSA-DFES | WA3666751 | Hanger - Birds nesting in hangar and dropping faeces over aircraft engineering equipment | DFES Rescue Helicopter Base | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-19 15:15:00 | Fail | Carried out a service for birds nesting within the hangar. Used a cherry picker to safely reach the height in order to remove the birds nest. Once the nest was removed it was relocated offsite. Will be returning on Monday afternoon to mist deterrent internally in order to discourage birds from nesting in here in future. Bird spiking would not be cost efficient as there are multiple ledges that would need to be covered, and the sliding door is generally open for helicopters which provides birds easy access.Misted D-Ter around all ledges and walls of the hanger in order to attempt and prevent birds from roosting/nesting here in future due to bird spiking not being cost efficient as the sliding door is open most of the day.
MSA-DFES | WA3666793 | Breathing Apparatus Room door not closing | CFRS Hope Valley | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 14:15:00 | Pass | Latch not lining up with striker plate. Removed hinges and adjusted. Door now closing correctly
MSA-DFES | WA3666797 | whole of station various fluro lights need changing - see notes | CFRS Hope Valley | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-30 09:30:00 | Fail | Located 5 x Lights in Engine Room 1 x Light in Tunic Room and 1 downlight in the kitchen.
MSA-DFES | WA3666802 | fence in rear yard fence has collapsed - see notes | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-23 16:00:00 | Fail | Replaced corroded posts and damaged panels
MSA-DFES | WA3666922 | ground hanger door flashing has come away - see notes | DFES Rescue Helicopter Base | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-16 08:00:00 | Fail | Reattached flashing and secured
MSA-DTAG | WA3666858 | Ground, court 5 - JSO Duress Alarm going off without being touched | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-16 08:00:00 | Fail | Court 5 clerk desk button requires replacement. Button bypassed until new button can be sourced staff onsite advised button will not function but other duress is available in room. New button to be sourced.16/10/20Button replaced tested working ok.
MSA-DTAG | WA3666893 | Cell 4 - Custody - BIO clean person in Custody has been spitting & HEP-C | Joondalup Courthouse-Main Building-Ground Floor | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-10 14:00:00 | Pass | Job completed as per WO.
MSA-DTAG | WA3666949 | Main Kitchen in Judicial Corridor - Leaking Urn in Kitchen opposite Judicial Library | Supreme Court | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 15:49:00 | Pass | System leaking on arrival. Hard time finding power isolation. Called Ian for help to isolate. Have left power and water on as requested by Ian. Needs system replaced ASAP. Waiting for approval New system approved! Installed new system and added fittings!!! Commissioned, normal operation removed old to tip
MSA-DTAG | WA3666957 | Ground, cell 1 - Special Clean in Cell 1 – Accused urinated and spate on the cell floor | Midland Courthouse | WSM-BR-SITE | Cleaning | Cleaning (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 18:30:00 | Pass | P1 in cell 1 attended and cleaned spit and urine from cell.
MSA-DTWD | WA3666263 | Whole campus Multiple Access and Security panel failures. | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-11-03 12:45:00 | Fail | 09/10/2020 - E Block alarm dialler fault and unable to arm alarms. Multiple expanders and dialler had locked up due to overload alarms flooding the system from backlog of alarms continuously dialling out from controllers. Reset event database on controllers to clear backlog of alarms. E Block is now back to normal. Three other older version 3000 controllers also offline. Tested end-to-end connectivity from server. Connection seems to be getting dropped from within core network. Attempted to use a small hub switch connected between controller and the new FortiNet switches, as previous issue was a port-negotiation fault. This did not work. Narrowed down issue to the subnet configured on the controllers, as the core network was blocking the connection after the network upgrade. Michael from IT made some changes and got the connectivity working. All controllers are now back online. Older model 3000 controllers still need to be upgraded to prevent future issues29/10/2020 - Replaced FTC#03
MSA-DTWD | WA3666378 | Pay Station room - Broken/faulty power point | Armadale Campus - 40 Commerce Ave | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 15:30:00 | Pass | Attended site and signed in. Completed jsa. Investigated broken gpo. Found gpo and wall box cracked. Isolated and replaced with new. Reenergised and tested. all ok. Completed paperwork and informed staff of completion of job, job complete
MSA-DTWD | WA3666414 | Power building, Ground floor - lift not working, doors staying open | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 14:20:00 | Pass | job completed - DOOR OPERATOR - DOOR OPERATOR CONTROL BOX - RUNNING ON ARRIVAL
MSA-DTWD | WA3666435 | G block, wash bay - Power point in the outside wash bay, | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 11:01:00 | Pass | Attended site, attempted to sign in but digital system was down (I let fm know what time I arrived and that I was here ), located gpo, completed jsa, fm said that job was raised because there was something plastic in on of the pins of gpo , on inspection the plastic reported was actually a safety feature on the gpo , got the lecturer in the area and showed him what it is and explained how it works and why it’s there , tested gpo and all working as intended, had no problem putting plug into gpo , completed paperwork, signed out ***job complete ***
MSA-DTWD | WA3666462 | block 2 Faulty toilet exhaust fans | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 16:30:00 | Pass | Reprogrammed block 2 toilet exhaust fan time clock and replaced broken exhaust grille
MSA-DTWD | WA3666576 | Kitchen - Rec Centre Oven wont start | Muresk Institute | GMP-BR | Equipment | Catering Equipment (EQ) | Lane's Plumbing | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-09 15:30:00 | Pass | Job completed - Repairs to rec centre oven not lighting
MSA-DTWD | WA3666579 | L2 student kitchen faulty dishwasher | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-13 08:15:00 | Pass | Attended site , signed in ,spoke to fm about problem with the washer , completed jsa, found that washers on off button isn’t working ( washer still works but to turn it off and on you need to use the gpo which is located behind a cupboard in a hard spot to reach ) , will have to be replaced by someone that specialises in washers (manufacturer) , brand is wash tech gm, informed fm about this
MSA-DTWD | WA3666601 | Metal Fab 1 - Intermittent power in grinding bays | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 12:15:00 | Pass | Attended site and signed in. Located grinder bays in metal fab. Couldn’t find tech who logged fault. Spoke with various staff regarding issue and was believed that the pendant gpos are causing problems where hanging. Advised to mount the outlets to the booth wall to minimise potential to move and be pulled out. Removed suspended mounting gear and direct bolted all outlets in booths to wall. Tested all okay. Job complete
MSA-DTWD | WA3666678 | block 3 Window fallen out of frame in Heavy Auto classroom | Thornlie Campus | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-09 13:45:00 | Pass | Re- secure window hinges
MSA-DTWD | WA3666701 | AT220 the third toilet is continue to run | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 09 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 13:06:00 | Pass | Repaired leaking toielt
MSA-DTWD | WA3666704 | Building 6, level 3, classroom B325 - Split A/C unit not working | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-22 14:03:00 | Fail | Materials collected and brought to site signed in gained access to out door unit confirmed power isolation and lock out. Replaced fault weather proof isolator. New isolator has been fitted to wall behind unit. Put covers back in place and tested equipment operation. All ok. Work area has been left tidy.
MSA-DTWD | WA3666925 | level 1, 104 - Blockage in drain | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 09 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 13:13:00 | Pass | Installed sealed grate panel for dodgy installation
MSA-DCS | WA3666979 | PDA system has failed. It's not triggering this morning. | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Oct 2020 | 2020-10-10 11:18:12 | 2020-10-10 10:15:00 | Pass | Found mains comms for Melaleuca down, restart & test. all ok. job complete
MSA-DCS | WA3666980 | Hakea-perimeter transmitter for PDA alarm not working | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Oct 2020 | 2020-10-10 10:56:23 | 2020-10-10 10:30:00 | Pass | Rectified and fixed the MDAS master pc and test pda in different locations. Job completed
MSA-DCS | WA3667012 | UNIT 2- Electric burning smell coming from the roof of unit 2. | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 10 Oct 2020 | 2020-10-10 14:10:19 | 2020-10-12 11:00:00 | Fail | Investigate burning smell. Found light had hot joint. Disconnect light.Replace light.
MSA-DCS | WA3667019 | Cell call interface is in error in reader- Entire Yeeda unit | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Oct 2020 | 2020-10-11 11:39:17 | 2020-10-10 13:30:00 | Pass | Rectified and fixed the fault from 3210 controller, job completed.
MSA-DCS | WA3667059 | Bandyup Prison - Unit 4 - L Block - Front door lock - Officer lock is loose but secure. | Bandyup Prison | GMP-BR- HO | Carpentry | Materials (CA) | ACE LOCK & SAFE | 3 | CLOSE | 10 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 12:00:00 | Pass | Removed cylinders from entry door lock to Unit 4 / L Blockresecured cylinders and refitted
MSA-DCS | WA3667083 | EBI 1 moniitor has script errors | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-12 12:00:00 | Pass | Travelled to site and found EBI workstation had no full site plan image on detainee reception. Reset workstation and reloaded site plan, all tested and working ok. Tested camera functions and door control and all tested ok. Job complete
MSA-DCS | WA3667085 | High temp alarm in equipment room | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Oct 2020 | 2020-10-11 17:37:06 | 2020-10-11 14:00:00 | Pass | High temp alarm from equipment room , attended and rectified the fault. Job completed
MSA-DTAG | WA3667082 | On Fire panel- System Fault 1- | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 10 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-10 19:00:00 | Pass | Vesda low pressure fault will speak to ian (site supervisor on monday)
MSA-DCS | WA3671442 | Beeper on control panel not functioning | Casuarina Prison-Prisoner Accommodation Unit 3 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Oct 2020 | 2020-10-11 12:40:03 | 2020-10-11 12:30:00 | Pass | Rectified and fixed the unit 3 cell call, test cell call ok and working. Job completed.
MSA-DCS | WA3671444 | Gatehouse control room- Security Management system is basically cut from the server, unable to do an | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Oct 2020 | 2020-10-11 13:01:49 | 2020-10-11 11:30:00 | Pass | Rectified and fixed the EBI fault. Test and check the function on all ws ,ok and back to normal operations. Job completed.
MSA-DCS | WA3671517 | Burst pipe on 22 Driseel Drive Canning Vale | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 11 Oct 2020 | 2020-10-11 18:24:44 | 2020-10-11 16:48:00 | Pass | Temporary fix as water meter was damaged and couldn’t shut off to repair broken hose tap waters stoped but will need to get approval to replace water meter and replace hos tap
MSA-DTAG | WA3671529 | On Fire panel- System Fault 1- | Central Law Courts | BUG-MW | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 11 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-11 21:00:00 | Pass | Will contact ian to organise further investigation when access is available.
MSA-DCA | WA3677386 | Leak on HW pump in plant room. Leaking from glands - see notes | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - In Front of Lift | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-30 14:30:00 | Fail | Attended site 1130. Water leakage present in outside plant room. Applied tests and checks to find HWP leaking from gland seal coupling heavily. Isolated HWP and boiler system. Setup dehumidfiers in RA pathway of the Batavia gallery AHU system, applied applicable manual changed to HW and CHW valves to 0% via BMS. Removed HWP to be repaired. Job to be closed with a new work order to be raised for pump repairs. Left site 1430.
MSA-DCA | WA3677539 | Wall panel has come away, please refix. | Sunset Hospital Heritage Precinct-Building G-Two Storey Ward Block-Ground Floor-Disabled Toilet - New Toilet Block | GMP-BR | Building | Internal Walls (BU) | ICS Australia | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 11:00:00 | Pass | Fixed panel
MSA-DCA | WA3677783 | Ground level - FIP faults, light is on against the “run AC fan” button. FIP also displaying a system | Maritime Museum Victoria Quay | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 17:15:00 | Pass | Carried out fault finding/checks on system control, rotary dial working as intended, disconnected stop indicated to avoid confusion, run indicate working as intended,.
MSA-DCS | WA3677123 | Gate house control system issue "network link to the command centre server has failed" | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Oct 2020 | 2020-10-12 10:40:00 | 2020-10-12 09:30:00 | Pass | Travelled to site and checked system. Found no network connection, cat5e data cable had somehow been disconnected from PC in control room. Replaced connector with new cat5e connector due to wear and tear. All replaced and system tested ok. Job complete
MSA-DCS | WA3677138 | Unit 1, D9 - Camera lens scratched and damaged | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 07:11:38 | 2020-10-23 13:00:00 | Fail | Replaced damaged Flir camera cover CC-COVR-31, job completed.
MSA-DCS | WA3677159 | Dairy - power point faulty (was smoking) | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 07:33:24 | 2020-10-12 10:00:00 | Pass | Investigate and replace dairy gpo
MSA-DCS | WA3677171 | POD - camera play back issues on most CCTV | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-12 14:30:00 | Pass | Reprogrammed Indigo system security user account to have access to all new Gatehouse cameras and playback features. All tested and working ok, job complete
MSA-DCS | WA3677207 | Unit 14 - the bolt on eastern side (outside) gate needs adjusting. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 12:15:00 | Pass | Gate has been removed for construction purpose.
MSA-DCS | WA3677211 | Unit 14, D wing - Blocked drain pipe in shower. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-16 14:00:00 | Fail | Nill
MSA-DCS | WA3677214 | Unit 14, D wing - Shower tap is getting constantly bad leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 09:30:00 | Pass | Nill
MSA-DCS | WA3677221 | Unit 4, D13 - Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 14:00:00 | Pass | Nill
MSA-DCS | WA3677223 | Unit 4, D13 - Flush button is broken and can't flush toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 14:00:00 | Pass | Nill
MSA-DCS | WA3677225 | Unit 14, C9 - Shower floor drain outlet cap, screw has snapped | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 08:30:00 | Pass | Mill
MSA-DCS | WA3677229 | Unit 4, C wing - Tap constantly dripping in C wing cleaning cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-22 13:30:00 | Fail | Nill
MSA-DCS | WA3677241 | CCU (11), D wing, D7 - the water jets are blocked and spray horizontally rather than vertically | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 12:30:00 | Pass | Nikl
MSA-DCS | WA3677245 | Crisis care - staff toilet light switch damaged and does not work | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 08:34:46 | 2020-10-15 14:00:00 | Fail | Replaced cracked light switch
MSA-DCS | WA3677250 | Unit 16, C wing - cells C7 & C8 night observation lights not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 08:38:12 | 2020-10-19 11:00:00 | Fail | Checked lights in c8, ordered replacement parts, picked up and repaired cell light in c8
MSA-DCS | WA3677255 | unit 8, Control Doors and Wing Cameras - 10 second time delay on doors opening and cameras | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 08:42:13 | 2020-10-13 15:50:00 | Fail | Investigated door control fault, replaced faulty power supply and installed replacement hard drive in workstation.Monitored for correct operationTested OK.Job CompleteParts (SEME Stock):1 x 19V Power Supply1 x SSD Hard Drive
MSA-DCS | WA3677263 | Kitchen- Corridor between coldrooms 6/7/8- Fluro light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-12 14:00:00 | Pass | Repaired light
MSA-DCS | WA3677267 | Unit 6, Cell B6- Fluro light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 14:00:00 | Pass | Repaired Cell light U6 B6
MSA-DCS | WA3677269 | Unit 10, Cell B6- Fluro light is broken, Tripping RCD | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 08:48:49 | 2020-10-12 13:00:00 | Pass | Repaired light
MSA-DCS | WA3677273 | Unit 4, office - computer door lock is very stiff to open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-14 10:00:00 | Pass | Service and replace bolt throw
MSA-DCS | WA3677277 | Unit 5, C2 cell window springs in side of frame are broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-15 09:30:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3677280 | Unit 4, A & C Day Room- 1st big window near the oven is cracked | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-12-15 14:15:00 | Fail | WORK ORDER DOUBLE UP - JOB COMPLETED ON WA3751948
MSA-DCS | WA3677311 | visits center auto boil faulty water coming out over flow constantly | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 10:11:00 | Pass | Replaced inlet solenoid and level sensors
MSA-DCS | WA3677312 | Boilerhouse, Mezzanine Floor Holding Tank - Not Holding Pressure. Very Bad Leak | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 09:11:04 | 2020-11-01 13:00:00 | Fail | Make way to boiler room. Started draining the feed water tank. This took a couple hours so completed job in laundry and came back. Once drained Brendan hopped inside tank and removed bolts from top flange which have rusted away and gasket has blown out the bottom. Installed new gasket with new bolts and tightened up. Ran up one of the boilers to test for leaks with pressure. Found that the condensate line from other side of steam coil was not draining out any water therefor steam was not coming in properly and heat ring the tank. Looks to be the steam trap not working. Brendan has recorded details of steam trap recommend replacing. Boilers shut back down and everything back to normal and filled tank back up.
MSA-DCS | WA3677330 | MATV unable to stream from gatehouse | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-26 15:00:00 | Fail | Supply and Installation of 2x DVD players to be located in Main MAW Tack (Gatehouse Comms Room)- Supply and Installation of 2x HDMI to RF modulators to be located in Main MAW Rack (Gatehouse Comms Room)- RF modulators to be programmed into sites existing Main MAW distribution system located in Gatehouse to BroadcastDVD players over RF Channels throughout prison
MSA-DCS | WA3677332 | Reception bee infestation - may be nest in crawl space | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 09:29:55 | 2020-10-12 13:45:00 | Pass | Bees Treatment.
MSA-DCS | WA3677354 | Gatehouse electronic gate - intermittent failure of the electronic pedestrian gate t | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 09:46:47 | 2020-10-12 13:00:00 | Pass | Removed lock from gate. Traced fault to poor ground wire connection. Reterminated +V, GND and switch wires. Tested ok.Parts used:Consumables
MSA-DCS | WA3677380 | control room PTZ 5 a pre set needs to be done showing trees | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 17:00:00 | Pass | Checked Camera Preset locations on PTZ 5. Found Preset for Zones A & B were pointing toward sky. Corrected views and confirmed camera views by alarm activations during walk test.
MSA-DCS | WA3677387 | Bakery, workshop - Bread slicer side not working at all | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 10:13:52 | 2020-10-12 13:00:00 | Pass | 12/10/20Sign in Wait for escort Escorted to bakeryCheck bread and found right side not working at all Fault find and found stop button permanently stuck on as food built up insideRemove and clean button Reassemble and test, found. Emergency stop not working. Found base of emergency stop had come loose. Repair and reassemble unit, test. Ok
MSA-DCS | WA3677389 | Unit 6, A & C dayroom sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-16 08:30:00 | Pass | Nill
MSA-DCS | WA3677413 | Maintenance office - Light Diffusers are broken and require replacement | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-21 08:30:00 | Fail | Checked and measured missing light diffusers in maintenance. Ordered replacements, picked up and installed.
MSA-DCS | WA3677415 | House 9 - HWS, not heating water | Boronia Pre-release-AM26 - Prisoner Accommodation House 8 and 9-Ground Floor | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 11:00:00 | Pass | COMPLETED
MSA-DCS | WA3677419 | Canteen door frame is falling out, requires refixing to the wall. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 12:00:00 | Pass | RE NEWED ALI FRAME
MSA-DCS | WA3677438 | Investigate root damage in main line to industries (camera) and water meter on same line | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-23 09:00:00 | Fail | COMPLETED
MSA-DCS | WA3677451 | Unit 1, Cell A10- Judas hatch isnt able to be re-secured. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 10:00:00 | Pass | Repair hatch lock
MSA-DCS | WA3677462 | SOP, Cell A8- Window in cell does not remain in open position | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 15:00:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3677464 | Pot Wash room - Pre rinse spray swivel has been over extended & bent. Nozzle is not turning off | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-12-01 15:15:00 | Fail | COMPLETED
MSA-DCS | WA3677509 | Lenard, Cell C07- Shower solonoid will not shut off | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 12:40:00 | Pass | Replaced faulty solenoid and button
MSA-DCS | WA3677512 | Karakin, Cell C02- Toilet solonoid will not shut off | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 15:15:00 | Pass | Replaced faulty solenoid
MSA-DCS | WA3677524 | Roof truss – tail of top chord has rotted | Boronia Pre-release-AM26 - Prisoner Accommodation House 8 and 9-Ground Floor | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2021-08-04 10:30:00 | Fail | new rafters installed
MSA-DCS | WA3677553 | Gate fire panel is in error - see faults below | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 10:18:00 | Pass | Attended site and found panel had no earth fault present when arrived.Checked history found earth fault started on the 12/10 at 9:43hrs and was intermittent till 12/10 13:03hrs but nil alarms since.Not able to locate fault as not present at this time.
MSA-DCS | WA3677573 | Unit 14, Cell D16- Shower is flooding in cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-16 11:30:00 | Fail | Nill
MSA-DCS | WA3677583 | Unit 14, D16 - sink how water tap is hard to turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-16 12:30:00 | Pass | Nill
MSA-DCS | WA3677609 | Unit 6, Cell B1- Toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-23 13:48:00 | Fail | Refitted cistern wasn’t installed properly installed correctly and replaced outlet washer
MSA-DCS | WA3677623 | L3 female toilet blocked toilet | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 12:13:47 | 2020-10-12 16:00:00 | Pass | unblocked toilet
MSA-DCS | WA3677625 | Unit 1, Cell A8- toilet leaking onto floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-23 16:00:00 | Fail | Removed stanless toilet redoing flush pipe
MSA-DCS | WA3677634 | Unit 2, Cell A11- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 15:30:00 | Pass | Repaired Cell light Unit 2 A11
MSA-DCS | WA3677676 | Kitchen - Combi oven #4 - tension button broken snapped | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 14:30:00 | Pass | Fit new knob, test ok
MSA-DCS | WA3677763 | kitchen probe bent in oven closes to office | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-16 09:35:00 | Fail | Replaced meat probe & tested ok
MSA-DCS | WA3677769 | Gatehouse toilet (downstairs)- Light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 14:02:00 | Pass | Replaced 4 tombstones in bathroom light fittings, tubes and starters had been replaced by maintenance recently.
MSA-DCS | WA3677789 | Unit 1 - A9 Water isnt going down, the plug hole is blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 10:30:00 | Pass | Nill
MSA-DCS | WA3677794 | Unit 7, B wing oven hotplate is tripping its circuit breaker | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 10:05:00 | Pass | Tested all cook tops on each temp and oven with timer, all is working ok and wouldn't fault.
MSA-DCS | WA3677823 | New security office - fault with swipe card reader | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-12 15:30:00 | Pass | Re-programmed Gallagher system for 2 x doors to give access to only relevant security officers into security office and SGW doors. All programmed and tested ok. Job complete
MSA-DCS | WA3677836 | sewage plant dam pump house - pump & bleeder valve damaged | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Plant & Pumps (WM) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 14:56:23 | 2020-10-19 14:00:00 | Fail | Sewerage plant dam pump house - pump & bleeder valve damaged. Check sewerage plant. Pipework & pump damaged. Check pump pipe, remove broken pipework. Install new parts. Run, test pump, not making pressure & very noisy. check belt & suction lines. Found main suction line blocked with leaves & nuts. Repair all good.
MSA-DCS | WA3677876 | male toilet bowl continues to have more and more water everytime it is flushed | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-21 11:30:00 | Fail | Complete
MSA-DCS | WA3681643 | front cholrine plant cholrine gas detector faulty not working | Karnet Prison Farm | GMP-BR-RC | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-11-24 13:49:00 | Fail | Attended site and installed ESD
MSA-DFES | WA3677558 | ground gym door is damaged and in need of repairs - see notes | CFRS Duncraig | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-22 15:30:00 | Fail | COMPLETED
MSA-DFES | WA3677587 | Male Toilets (Near Gym)- flush button on the urinal is sticking causing the water to run constantly | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-29 15:30:00 | Fail | Replaced cicten due to broken
MSA-DFES | WA3677621 | Front Gate is chattering and will not close | DFES Rescue Helicopter Base-Car park | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | COMPFIN | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 11:42:00 | Pass | Requires motor replacement, setting off the circuit breaker. Also requires track for gate. Quote has been declined, closed off job.
MSA-DFES | WA3677751 | Storm water drain cover is cracked | CFRS Armadale | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-12-14 16:03:00 | Fail | Storm water grate reqd replacing
MSA-DFES | WA3677778 | L2 med editing room exit door green button is not working | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 15:57:00 | Pass | On inspection, found P2not working.On further inspection, found security access is not releasing the door.Advised Nick of issue found.Nick will organise Sontec to resolve this issue.No programmed asset number
MSA-DFES | WA3677797 | Engine room fluro's need replacing - see notes | CFRS Rockingham | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-29 14:30:00 | Fail | Located damaged lights in Engine room. Light has completely snapped and is no longer usable. Is currently in a safe condition. 2 lights are also faulty next to it and I suggest replacing all 3. Will need to seek approval for 3 x New LED replacements.Notified staff of works.Returned on the 29/10 and replaced 3 lights,
MSA-DFES | WA3677801 | rear yard - Lids to sewer pit are sitting proud of bitumen.EQUIRE FIXING TO ALLOW LID TO SIT INTO RE | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-26 10:00:00 | Fail | Cut down lid
MSA-DFES | WA3677862 | L2 media editing room exit door having issues | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-13 11:00:00 | Pass | 13/10/20 - Dylan ParslowFound door controller not responding to egress signal.Reset and tested, all working ok.
MSA-DTAG | WA3677324 | Level 5 - Seat outside Court 53 is loose, see notes below | Central Law Courts | GMP-BR-HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-12 13:00:00 | Pass | RE SECURED SEAT
MSA-DTAG | WA3677371 | The air conditioning for the Courts rooms and registry is currently not working. | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 13:00:00 | Pass | Attend site. AC not working in building Access BMS ans check operation of plant. Found all AC units operating. Check time schedules and found to be normal. Check temps throughout building and found court 2 and 3 to be slightly warn. Check operation of chilled water valves and found to work as normal. Make slight adjustment to setpoint and found chilled water valves to remain open and court rooms temperature is now dropping. Monitor operation of all Fan Coil units for correct operation. Working ok.Possible cause being the transitional period between winter and summer ambient temps, where the outside temp is the same as the inside temp.
MSA-DTAG | WA3677399 | ground front door of building are in constant state of alarm, sensors aren’t working - see notes | Perth Children's Court | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 13:00:00 | Pass | Found cable broken at point and point reed damaged. Remounted and fixed cable/resistor pack
MSA-DTAG | WA3677552 | Technician required to assist Australian HVAC on Sat 17th October from 07.00am until approx 16:00pm | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-17 15:00:00 | Pass | Assist with HVAC Testing
MSA-DTAG | WA3677563 | Lvl 2A, Storeroom- Aluminium skirting in office storeroom is loose | Central Law Courts | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo Building Services | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-12 15:00:00 | Pass | RE ATTACHED SKIRTING
MSA-DTAG | WA3677577 | Level 4 - Wall partition fixings are loose | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-12 14:30:00 | Pass | RE SECURED WALL PARTION
MSA-DTAG | WA3677744 | electronics and communication fire panel fault | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 15:30:00 | Pass | Will require further access putside of business hours to fix faults on zone 3. Client aware and will organise
MSA-DTWD | WA3677144 | All areas - alarm faults, cleaners unable to disarm alarm | Munster Campus (ACEPT) | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 12 Oct 2020 | 2020-10-12 17:00:00 | 2020-10-12 11:20:00 | Pass | 12/10/2020, 1050-1120Re enabled the cleaners code as the facilities manager voided the user after her card was lost
MSA-DTWD | WA3677298 | Fire Alarm Panel - Panel has fault sensor fault male toilet | Fremantle Campus (formerly WA Maritime) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-11-10 15:39:00 | Fail | Fire Alarm Panel - Panel has fault sensor fault male toilet, Replace faulty sensor with new-COMPLETEDREPAIR WORK COMPLETED ON WA3677298
MSA-DTWD | WA3677360 | B Block, Room B106- Tap is faulty | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-20 09:45:00 | Fail | Complete
MSA-DTWD | WA3677398 | house 8, kitchen - Faulty gas stove | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 15:30:00 | Pass | Job completed - Repair faulty burners to stove and replace ignitor and lead to oven house 8
MSA-DTWD | WA3677404 | house 8, kitchen - faulty HWS | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 13:00:00 | Pass | Job completed - Repair faulty hws to house 8
MSA-DTWD | WA3677427 | E block ground stores area fire alarm activation, replace faulty sensor | Joondalup Kendrew Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-12 14:40:00 | Pass | Call out - investigated alarm on FIP - zone 2 stores/amenities - no detector in alarm - found detector in male toilet with soft pastry on it - replaced.Also facilities asked me to change thermal detector in switch room - extra dirty - reset FIP and no alarms.
MSA-DTWD | WA3677594 | A block 2 east A009 FTC 06 controller not responding | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BJ SYSTEMS | 3 | CLOSE | 12 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-13 15:30:00 | Pass | Attend site to investigate fault on FTC#06, found the controller to be pinging back when directly plugged into laptop. Set laptop to same IP as controller plugged into switch to ping server and gateway with no success. IT to resolve issue
MSA-DTWD | WA3677666 | B Block Lift Persons stuck in lift | Bentley Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 0 | CLOSE | 12 Oct 2020 | 2020-10-12 16:31:10 | 2020-10-12 16:45:00 | Fail | Job completed - UNINTERRUPTABLE POWER SUPPLY - OVERLOAD - LOW VOLTAGEVendor to return to complete works
MSA-DTWD | WA3677759 | tail fin of the B737 Aircraft in the Hangar - Bee’s have made a nest | Jandakot Campus - Hangar | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-19 16:20:00 | Fail | Day 1- (15th October)Attended site at organised time to treat bees that are nesting within a gap of the tail fin on a plane. Although we attended with 2 technicians and a cherry picker, we deemed the job unsafe to carry out due to high amounts of people working within the Vicinity. As the bees would need to be dusted, they will get territorial and aggressive which will pose a risk to anybody working nearby. For this reason we have organised to attend on Monday afternoon around 4pm when staff and students go home.Used cherry picker to gain access to the entry hole that bees are using to enter their nest within the tail fin. As bees could not be removed/relocated, thoroughly dusted all entry ways to the best of our ability, must allow a few hours for bees to spread dust back to their queen to lead to colony elimination. Couldn't seal off gap as there is multiple other entry ways bees could possibly use and we want them to be able to pass the dust back to the queen.
MSA-DTWD | WA3677831 | A-Block, Level 2, 214 - has two faulty network ports | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 12 Oct 2020 | 2020-10-13 17:00:00 | 2020-10-13 10:33:00 | Pass | Replaced 2x data mechs in room 214 and 1x in library
MSA-DTWD | WA3677858 | K block K004 glass sliding door constantly jamming | Balga Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 12 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 15:15:00 | Pass | Removed existing flyscreen to access roller door. Changed rollers and re-fit flyscreen.
MSA-DCA | WA3681626 | Broken sprinkler | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Materials (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-15 12:00:00 | Fail | Job completed - one was thought to of been a broken sprinkler but was actually a busted sub main pipe that had been hit with a shovel- the other was a broken valve near the toilets that had possibly been kicked/ stepped on- used a ball valve and retro fitted the exsisting parts from the old one.-the other I used a slip fix to replace the broken section of pipe.- met wit Reese the site manager to sign off the work
MSA-DCA | WA3681630 | graffiti tag on large grey planter box | Perth Cultural Centre Precinct - Museum Plaza (James Street) | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 13:00:00 | Pass | Removed graffiti
MSA-DCA | WA3681674 | 2 Tall lights at the top of Amphitheater near Fiji room are out | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 09:33:00 | Pass | As requested attend site and investigate power loss to amphitheatre lights.found nuisance tripped cct in the events db and reset Kevin also notified me of 2 single lollipop lights that are out that have already been captured in Lighting inspection maintenance that is waiting for approval
MSA-DCA | WA3681691 | Art Gallery - loose gray Tactile | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Paving & Roadworks | Paving (PR) | ICS Australia | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-15 12:14:00 | Pass | Refined and secured tactile
MSA-DCA | WA3682088 | kitchen storage area external damaged kitchen window | Perth Concert Hall-Main Building-Ground Floor | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-20 10:30:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSMADE SAFE BROKEN WINDOW PANEL WITH SAFETY FILM 1-500 X 1000RETURNED LATER DATE TO REGLAZE OVERSIZE PANEL6MM CLEAR TOUGHENED SAFETY GLASS1-1702 X 20007.4 L/M OF RUBBER REPLACED PLUS SILICONE
MSA-DCA | WA3682104 | Level 2, Door 1 sound lock - 1 x down light fitting and globe have dislodged from the ceiling | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2 | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 11:48:00 | Pass | Attend site and investigate found loose and damaged gimble light. Sourced led equivalent as gimble halogens are now redundant itemscalled multiple wholesalers and found cnw to have a single colour gimble style
MSA-DCA | WA3682108 | Fire panel fault - EWIS speakers on level 4 & 5 | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 09:45:00 | Pass | Attended site & investigated EWIS EWS fault on EWS 4 “AGWA L4 & L5”.Checked EWIS panel OK.Checked & measured EWS 4 cable at EWIS & measured a short circuit on the EWS 4 cable.Inspected L4 & identified that the floor ceiling have been stripped out & all the in ceiling cabling is at height (4-5m).No authorised access to the construction site on L4, L5 to further fault find.Advised FM & advised no further fault finding to be conducted until construction works are complete.Placed information tags on both EWIS panels.
MSA-DCA | WA3682286 | Mechanical service required for Main building - A/C 2 High Humidity alarm | Art Gallery of WA - James St-Main Building (Block B)-External Area | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 03:00:00 | Pass | Attended after hours callout.Multiple humidity alarms on AC 3. Ambient humidity high. L4 open to elements. Opened return ChW butterfly valve on AC 3 and monitored SA temp. All reheats functioning correctly. All but 1 alarm cleared. Humidity dropping slowly. Following monitoring, all alarms cleared. Closed job.
MSA-DCS | WA3681497 | Unit 2, camera 29 - Blank with two vertical lines through screen. | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-19 17:00:00 | 2020-12-09 11:00:00 | Fail | Found faulty coax converter in cabinet, parts are obsolete, run new cat 6 cable, install new indigo vision camera, program and test, all ok.
MSA-DCS | WA3681510 | Unable to playback cell call audio in Arunta room | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-19 17:00:00 | 2021-12-09 08:42:00 | Fail | Engineer attended site from Perth to complete WA3729804 - MDAS Rectification, WA3967128 IndigoVision upgrade, WA4112478 and this job.Installed new monitor @Arunta room Cell Call PC with built in Speakers to allow Audio playback.Re-configured and tidied security racks as required (photo's sent to PFM).Living and accommodation costs related to the above mentioned work orders.Parts supplied: Patch leads and Rack Accessories
MSA-DCS | WA3681515 | ICF workstation lagging | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-19 17:00:00 | 2020-11-10 16:01:00 | Fail | Removed existing ICF workstation, installed new workstation and programmed.tested Indigo functions and confirmed correct operation
MSA-DCS | WA3681522 | Unit 14, D4 - prisoner lock is sticking (and the plate on the door frame is loose) Prisoners are una | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 13 Oct 2020 | 2020-10-15 17:00:00 | 2020-11-02 10:15:00 | Fail | Replace lock and temp. repair strike.Replace strike with oversize strike.
MSA-DCS | WA3681524 | Unit 1, B14 - Viewing glass smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 07:30:55 | 2020-10-13 12:30:00 | Pass | OBS PANEL REPLACED
MSA-DCS | WA3681612 | Visits Building - Evap Air Con Drive Belt Adjuster Rusted & Seized (unable to adjust drive belts) | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 08:17:58 | 2020-10-13 13:15:00 | Pass | Replaced 2x fan belts and treated corrosion on bolts
MSA-DCS | WA3681614 | Unit 10, Cell C11- Medical hatch will not facilitate being unlocked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 08:28:33 | 2020-10-21 11:00:00 | Fail | 13/10/2020. Attended site. Replacement hatch required. BRAF request lodged.21/10/2020. On site. Replacement hatch supplied and fitted.
MSA-DCS | WA3681625 | External security camera is not working- possible warranty issue | Welshpool | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 08:38:22 | 2020-10-13 12:00:00 | Pass | Camera 2 external not responding. Rebooted camera, all working OK.Job completed.
MSA-DCS | WA3681636 | Unit 9, Cell A16- Judas hatch can be opened by prisoners | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 08:46:55 | 2020-10-21 12:30:00 | Fail | 13/10/2020. On site. Performed temporary repair but replacement hatch required. BRAF request lodged.21/10/2020. On site. Replacement hatch supplied and fitted.
MSA-DCS | WA3681638 | Unit 8, Cell A9- Getting Electric shocks from touching basin taps | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 08:51:58 | 2020-10-14 08:00:00 | Pass | Unit 8 Cell A9 Tested and reported to Western Power
MSA-DCS | WA3681686 | Unit 7, E Wing Showers- L/H shower leaking into corridor floor, see notes below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 09:09:51 | 2020-10-13 14:20:00 | Pass | Replaced tap washers and valves to x2 shower cubicles
MSA-DCS | WA3681687 | Reception Rear Entrance HW Cylinder Cage HW circulation pumps not working | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 09:09:01 | 2020-10-21 13:30:00 | Fail | Attend and check out pumps, power all ok removed pumps and did a turn test pump 2 had a failed bearing and pump 1 is on its way out. Getting prices to replace. Have left pump 1 in manual so hot water is always available for now. Collect new pumps from APS in Belmont, replace both pumps and new seals, tested both working and back on duty cycle.
MSA-DCS | WA3681699 | Stat room computers not working, no power to that area - see notes | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 09:17:33 | 2020-10-13 11:00:00 | Pass | Restored power to stat area computers.
MSA-DCS | WA3681700 | Control room - FIP fault - SUBFIP Remand Z23 connection fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 09:25:18 | 2020-10-13 12:00:00 | Pass | Complete
MSA-DCS | WA3681726 | Control - PTZ Camera 18 & 10 not functioning | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 09:45:40 | 2020-10-13 16:03:00 | Pass | Worked between Hakea and Melaleuca to resolve multiple PTZ camera faults.Tested OKJob Complete
MSA-DCS | WA3681729 | Control - PX 3A & 4 not functioning | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 09:48:43 | 2020-10-14 16:33:00 | Fail | Repaired multiple perimeter detection and camera faults as per SOG Control.Tested OK.Job CompleteParts used:Consumables
MSA-DCS | WA3681880 | Sally port door lock is not operational | Karnet Prison Farm | GMP-BR-RC | Security | Locksmith (SE) | Bullant Security Pty Ltd | 0 | CLOSE | 13 Oct 2020 | 2020-10-13 15:32:52 | 2020-12-17 14:16:00 | Fail | Attended site, made Existing lock (trimec es8204) mechanically operational and Securable. Electrician (who was onsite, has stated that there is faulty wiring, and will need to replace the wiring on that door. Electrician checked electronics on lock, need to replace)Date on site: 13/10/2020Time on site: 12:44pm - 02:46pm Have emailed BRAF for additional works required.Returned to site to install new lock.
MSA-DCS | WA3681899 | Unit 3, C house - PA speaker is damaged, cover is missing and does not work | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2021-01-22 16:30:00 | Fail | Broken PA speaker replaced. C house PA line issues on different job.
MSA-DCS | WA3681900 | Unit 13, Cell D7- shower is blocking from time to time | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-22 09:30:00 | Fail | Nill
MSA-DCS | WA3681952 | Unit 4 house 4 cell 4 reed switch falling out - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-22 14:13:00 | Fail | Checked all reed switches in the house and re-secured all loose reed switches, tested all and confirmed correct operation on Gallagher
MSA-DCS | WA3681953 | Control PDS monitor no working - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-29 18:29:00 | Fail | Removed faulty monitor and cabling.installed new monitor and re-installed cable into desk cable cavity
MSA-DCS | WA3681954 | DCP control monitor 2 not working - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-29 18:30:00 | Fail | Removed faulty monitor and cabling.installed new monitor and re-installed cable into desk cable cavity
MSA-DCS | WA3681956 | Unit 7, Cell F10- Seal leaking where pipe goes into back of the toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-26 08:00:00 | Fail | Removed cistern and flush pipe to replace key seal then reinstalled
MSA-DCS | WA3681975 | Unit 8 B3 Both sink taps keep dripping in cell | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-26 09:32:00 | Fail | Turned off water reseating and replacing both hot and cold taps
MSA-DCS | WA3682031 | Stores - Fire panel (zone 2) in constant alarm and unable to reset | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-13 15:30:00 | Pass | Complete
MSA-DCS | WA3682034 | Gate house light faulty keeps flickering on and off | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 10:30:00 | Pass | Investigate and replace gatehouse light
MSA-DCS | WA3682037 | Green Water Meter Box (Mains) Leaking Water onto Driscoll Drive | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 13:38:11 | 2020-10-13 15:54:00 | Pass | Temp repair to water leak on water meter.Spokr to Dean about shitting the water supply off.He will advise when ready.
MSA-DCS | WA3682056 | Unit 4, Cell C5- Keeps tripping RCD | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 13:00:00 | Pass | Power tripping
MSA-DCS | WA3682057 | Unit 3, Control Room- Electrical Cabinet door falling off | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 09:30:00 | Pass | repaired door
MSA-DCS | WA3682058 | Unit 3, Senior Officers Office- Power keeps tripping out | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 12:00:00 | Pass | SO power tripping.
MSA-DCS | WA3682068 | Unit 2, Cell A06 - drain blocked. Not draining properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 09:30:00 | Pass | Nill
MSA-DCS | WA3682071 | Visits, Main hall - Evap Air Con Fan Blade Has Broken Off | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 14:21:41 | 2020-11-03 15:08:00 | Fail | Repaired Ec V1. Tested and all ok
MSA-DCS | WA3682074 | Unit 7, D Wing- Cooker top not working, see additional notes | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 14:22:15 | 2020-10-22 09:45:00 | Fail | Replaced both RHS elements.
MSA-DCS | WA3682136 | Sally port gate - hydraulics seem to not engaging correctly | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-15 14:25:00 | Pass | 15/10/20Inspect gate operation.Check limit switches.Inspect gate controller.No faults found.
MSA-DCS | WA3682166 | unit 1 intermittent cell call from cells | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Oct 2020 | 2020-10-14 00:37:28 | 2020-10-13 18:00:00 | Pass | Multiple NODE errors on multiple nodes. Restarted all nodes via site CONFIG program. Unit 1 did not restart. Powered down all of U1 Cell call and restarted. Cleared all errors. Tested ok in U1, U2 and U3. U5 errors cleared by U5 Officer.
MSA-DCS | WA3682280 | One of the key issue doors locking Mechanism failed | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 13 Oct 2020 | 2020-10-13 21:09:38 | 2020-10-13 18:50:00 | Pass | Attended site after hours. Not a lock issue, an electronic issue. Needs to be addressed by others.
MSA-DFES | WA3681608 | Workshop- Louvers mechanism on south eastern side not working correctly/faulty | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2021-01-11 09:00:00 | Fail | Technician attended the site of DFES Fleet & Equip Services, Louvers on 04/11/2020. Following a full test and inspection of door components found fault to be needs to have 12 handles made for louvers. Also all louvers are jammed and rusted and all need to be serviced and access is hard. Quote was submitted. Technician returned on site on 11/01/2021, service and repaired all 12 handles. Made and supply new handles for shutters as per quote. Full test and inspection of door function completed prior to leaving site.This quote includes: "Removal of the existing components."Supply and installation of new replacement handles and servicing of all louvers to get them working again, "Test and check door operation."Lifting equipment to be provided by Assa Abloy Entrance Systems"The above work is to be carried out during normal business hoursBreak down of cost: Labour = $1,475.00Parts = $ 2427.17
MSA-DFES | WA3682043 | main admin door is jamming- Protek on site | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-13 15:00:00 | Pass | Drill out aluminium door frame behind striker plate
MSA-DFES | WA3682046 | rear reception light pole cover on lower part has come off | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-13 15:30:00 | Pass | Replace missing bolt to light pole cover
MSA-DFES | WA3682047 | Exit door of fire isolated stairwell to Northeast of State Operations Centre slams close | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 08:45:00 | Pass | Resecure door closer arm and adjust door closer - door closer now operating correctly
MSA-DFES | WA3682111 | In hallway between BA Service Area and FDP Office- Light switch won’t turn off | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 11:25:00 | Pass | COMPLETED
MSA-DFES | WA3682131 | Firefighters Number 1 Shower - shower screen broken | CFRS Joondalup | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-29 16:30:00 | Fail | ATTENDED SITE, ASSESSED AND MEASURED DAMAGED SHOWER SCREENS RETURNED TO SITE AT LATER DATE, SUPPLIED AND INSTALL 2X NEW SHOWER SCREENS 1 - 2000 X 987/983 1 - 2003 X 980/975 BARLEY FRAME, GLAZED IN TRANSLUCENT LAMINATED SAFETY GLASSSCREWS, PLUGS AND SILICONE USEDAS PER APPROVED BRAF
MSA-DFES | WA3682168 | Main Driveway and Carpark A 5 pot holes check is required for cracks | FESA RHQ - Forrestfield | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-23 11:40:00 | Fail | Job completed -= Bitumen repairs
MSA-DFES | WA3719160 | RETROSPECTIVE WORK ORDER - external check carried out - DO NOT ATTEND | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-13 11:48:00 | Pass | Despatch Comments:BYPASS ZN 25 R/S WATCH ROOM DOORPatrol Resolution:EXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE. NO OFFENCE DETECTED. NO PERSONS FOUND ONSITE HOWEVER TRUCKS WERRE ARRIVING BACK AT SITE AS PATROL
MSA-DTAG | WA3681550 | Electrician required to disconnect HWU in Judges kitchen – please attend Tuesday 13 October at 13.30 | Supreme Court | WSM-BR-SITE | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 13 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-13 14:15:00 | Pass | Disconnected old hwu and reconnected new hwu
MSA-DTAG | WA3681891 | Cells 1 & 3 Special Clean - Unknown substance stains on the ceiling | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-14 17:30:00 | Pass | P3 Clean to Cells 1 and 3 Ceilings
MSA-DTAG | WA3681945 | ground security office No power circuit supply, lights are okay - see note | Armadale Courthouse | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 08:30:00 | Pass | Attended site and signed in. Located security office upstairs and investigated which power outlets don’t work. Found a 4 gang outlet in kitchen not working and outlet for microwave not working. Removed all appliances and went to switchboard. Found 2 x circuits tripped. R1 and R3. Spoke with site and was advised that R10 tripped also. Being that all these are in the same room an appliance is most likely to blame. Tested and checked out all appliances in room. Toaster had low IR. Removed parts and cleaned and brushed element and frame. Retested and load tested. No circuit faults. Tested cabling and all okay. No faults on site. Advised of findings and what’s been tested. Job complete
MSA-DTAG | WA3682169 | 1903 ground court 2 Flickering fluorescent light above witness box - see notes | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | COMPFIN | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 07:30:00 | Pass | Replaced blown tubes to court 2
MSA-DTWD | WA3681718 | Male toilets - graffiti on the toilet partitions Re paint antigraffiti paint | Perth Campus B5 | GMP-BR | Cleaning | Graffiti (CL) | AWB Co. | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 11:30:00 | Pass | Work completed
MSA-DTWD | WA3681725 | Lvl 2, Student Kitchen - Industrial dishwasher is faulty | Perth Campus B5 | GMP-BR | Equipment | Catering Equipment (EQ) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 13:55:00 | Pass | Investigated dishwasher. Dishwasher needs to be serviced. Attached photos of last service company to the job. Faulty on off bottom on dishwasher control panel.KCI: Replaced power switch, thermostat and solenoid with new. Client to purchase glass washing detergent. KCI quoting direct to client for new racks as per client request.
MSA-DTWD | WA3681850 | B block rooms B19 and B20 air con blowing hot air | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 11:00:00 | Pass | System working correctly on arrival. Comms error cleared itself
MSA-DTWD | WA3681909 | Lvl 2, Room B244- Faulty light switch - will not turn off | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-29 09:00:58 | Fail | Attended site and signed in, completed jsa, replaced faulty 3 gang light switch with new, tested lights to see if correct operation. **job complete**
MSA-DTWD | WA3681987 | Level 2, cleaner room - water fountain system is leaking | Perth Campus B4 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-14 13:17:00 | Pass | Rectify leaks on water supply for drink fountain
MSA-DTWD | WA3682003 | B310.2 no power to data projector | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 09:15:00 | Pass | Attended site, signed in, located projector, completed jsa, located dB 9 , found that there is a subboard in the classroom , subboard had circuit tripped , reset rcd and tested circuit, circuit tested good , tested projector, projector working as intended, completed paperwork, signed out **gjob complete***
MSA-DTWD | WA3682044 | Block 2, Outside disabled toilet- Water damage to ceiling | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-11-02 10:00:00 | Fail | Inspected damaged ceiling, removed damaged part and replaced with new, patched and painted. Job completed
MSA-DTWD | WA3682066 | BMS for block 9 showing conflicting readings on zones 1 & 2 of AH 3. Calling for heating and | Thornlie Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 09:30:00 | Pass | Nrp inspected and updated BMS program. Quote to follow
MSA-DTWD | WA3682073 | block 3 ground metal fab 1 Faulty on/off switch on post drill south wall.- | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 11:45:00 | Pass | Attended site and signed in. Located metal fab drill presses. Found all drills to operate correctly. 1 drill press had a spinning e stop. Isolated and dismantled control panel. Readjusted and connected e stop. Replaced control panel to drill. Tested operation. All okay. Job complete
MSA-DTWD | WA3682079 | Tower - alarm system keeps going into fault | West One Services | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 12:15:00 | Pass | 14/10/2020, 730-845Attended site, does not open til 8 so had to wait.When opened no staff available to guide us as we have no information on this site regarding mapsor monitoring.Walked 1st floor looking for smoke detector only saw 1 that is on Tecom the rest are all FIP.No known codes etc. waited in lobby for 45 mins staff kept saying someone should be here soon butno one showed up. No one wanted to sign programmed form either.14/10/2020, 1145-1215Returned later and still unable to get required information. Spoke to Matt Eade he wasn’t able toacquire details he will email Securex office directly with info and we return then19/10/2020 Approx 1130Michelle from Programmed called and advised to close this job, to not proceed any further
MSA-DTWD | WA3682081 | South Block, level 1, S102 - Remove broken sharpes container female toilet and dispose | Mount Lawley Campus | GMP-BR | Waste Management | Materials & Supplies (WM) | AWB Co. | 3 | CLOSE | 13 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 08:30:00 | Pass | Arrived at site, signed in and located sharpes container. Had to pry open to access screws and remove. Once removed I cut the anchors back and patched the plaster work. Relocated a sign to cover different paint colour. Tidy area, packed away tools.
MSA-DTWD | WA3682090 | Staff lunchroom, Kitchen Sink needs repair, see notes below | Rockingham Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 09:15:00 | Pass | Cleared old silicone out and rebeaded with silicone
MSA-DTWD | WA3682098 | B737 aircraft 3 phase portable air con Elec fault with the power lead, it keeps tripping breaker | Jandakot Campus - Hangar | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 13:30:00 | Pass | Attended site , signed in, spoke to staff onsite about the issue with the a/c , completed jsa , apparently Ac is tripping power , unplugged lead to Ac and tested it , test was all good (>999Mohm on all phase and neutral to earth ) , tested gpo and tested good and rcd was operational, tested Ac unit and there was a fault between neutral and earth (1 ohm ) , problem is in the a/c unit , refrigeration mechanic required to do the job , completed paperwork , signed out
MSA-DTWD | WA3682114 | tower server room L1 air con has stopped working sitting at 28 deg should be 21 | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 13 Oct 2020 | 2020-10-13 19:02:25 | 2020-10-29 18:00:00 | Fail | Found both units in server room to be in fault Unit 1 - indoor fan fault a6 - qrf submittedUnit 2 - L9 fault overcurrent on compressor - qrf submitted
MSA-DTWD | WA3682130 | E-Block Restaurant, the glass washer does not drain the water | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 12:00:00 | Pass | Completed 14/10/20
MSA-DTWD | WA3682150 | A block A49 staff lunch room faulty GPO | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 14:15:00 | Pass | Attended site and signed in. Located A49. Found sparking gpo to water urn on wall. Isolated and removed. Supply and replace with new double gpo. Tested all okay. Job complete
MSA-DTWD | WA3682159 | A block L1 Aircon in “A” Block Top Floor as it is not cooling. | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 13 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-20 16:00:00 | Fail | Found drive open had failed on chilled water valve, and fcu1 trying to use outside air but hu mmidity to high so manualed valves open to keep cooling . Quoted new valve and bms tech
MSA-DTWD | WA3682167 | C block C31 corridor Cold water drinking unit is leaking | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 16:50:00 | Pass | Repaired leaks to bubbler with new parts required REPLACED BUBBLER INTERNAL CARTRIDGE, TAP ADAPTORS/TUBING ON WATERWORKS REFRIG FOUNTAIN A404213126
MSA-MRWA | WA3681703 | Lift 4- is stuck on level 5 | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor-Lift Lobby | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 13 Oct 2020 | 2020-10-13 13:30:01 | 2020-10-13 14:00:00 | Fail | Job completed - compressor faults. Bypass compressor for lifts 3 and 4. Test emergency phone in lift. Test operation of lifts and return toservice
MSA-MRWA | WA3681940 | Disable toilet One of the disabled toilet is blocked with tissue paper - see notes | Heavy Vehicle Services-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-14 13:40:00 | Pass | unblocked toilet
MSA-MRWA | WA3681949 | tap in the outside area, right side near the exit door – is leaking. | Jandakot Depot-External Area | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-15 08:45:00 | Pass | Shut off water replacing broken tap with new the turning water back on
MSA-DCS | WA3684451 | Unit 1, C6 - Cell Call Light constantly on | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 07:08:35 | 2020-10-14 10:30:00 | Pass | Job complete New cell call installed office stock
MSA-DCS | WA3684456 | Unit 2, Control Room - Fire alarm constantly going off | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 07:14:31 | 2020-10-14 10:23:00 | Pass | Attended site and checked unit 2 and found system normal. No one in unit two knew anything about a fault. Possible due to sample points being blocked over night to allow smoking in cells.Left system normal.
MSA-DCS | WA3685380 | Unit 3, C10 - window is loose and wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 12:00:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3685713 | vegetable preparation - Coolroom compressor leaking severely | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 14 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 14:30:00 | Pass | Removed blockage and cleared drain. All ok
MSA-DCS | WA3688870 | Kitchen - oven 2, dash and steam flashing | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-14 15:15:00 | Pass | Replaced level electrode to repair water level issue. Reset Gas fixed by adjusting steam burner mixture . Also fit new dial knob.
MSA-DCS | WA3692730 | Education power has tripped and is unable to be reset | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 09:00:08 | 2020-10-14 15:30:00 | Pass | Restored power to education rooms, found faulty jug and removed from site
MSA-DCS | WA3693024 | Behind old Kitchen near Boiler house- Isolation valve is leaking | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-11-20 16:00:00 | Fail | Nill
MSA-DCS | WA3693241 | Unit 13, A & C - Regi oven seal is faulty | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-16 09:00:00 | Pass | Replaced door seal as it was damaged and adjusted door catch. test ok.
MSA-DCS | WA3694026 | gate house ENR4 disc fault | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 09:11:35 | 2020-10-14 16:30:00 | Pass | Attended site and investigated the fault.Found that disk 3 of NVR 4 failed - can not be found.Restarted NVR-AS 3000 and formatted raid arrey.All back to normal and operational.
MSA-DCS | WA3694398 | Front auto door is not operating correctly, see further notes below | Rockingham Justice Complex | GMP-BR- HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 14 Oct 2020 | 2020-10-14 13:06:32 | 2020-10-14 12:00:00 | Pass | Door is failing on electric locking, found door was upgrade by Assa Abloy and door is still in under warranty, notify the site to call out Assa Abloy.
MSA-DCS | WA3694879 | Camera 173 can not connect to server | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 16:27:00 | Pass | Repaired multiple camera faults and tested OK.Job Complete
MSA-DCS | WA3696032 | Lost non essential power to the gate house | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 10:08:00 | 2020-10-14 13:00:00 | Pass | Tested normal power and found all on at arrival
MSA-DCS | WA3696069 | Security alarm system faulty, unable to be armed | Rockingham Justice Complex | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Oct 2020 | 2020-10-14 14:30:35 | 2020-10-14 17:00:00 | Fail | Job complete
MSA-DCS | WA3696095 | Gatehouse, Stairwell- power unable to trip back in | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-14 14:00:00 | Pass | Replaced faulty gpo
MSA-DCS | WA3696114 | Unit 4, Cell D1- Window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 11:00:00 | Pass | NEW SPIRAL BALANCERS FITTED TO WINDOW
MSA-DCS | WA3696116 | Unit 2, Cell A Wing- Bathroom shower window runners broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 13:30:00 | Pass | NEW BALANCES FITTED TO MAKE WINDOW OPERATIONAL
MSA-DCS | WA3696122 | Unit 2, Cell B Wing- Bathroom shower window runners broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 14:45:00 | Pass | NEW WINDOW BALANCES FITTED TO MAKE WINDOW OPERATIONAL
MSA-DCS | WA3696126 | Unit 4, Cell D13- Sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 16:00:00 | Pass | Nill
MSA-DCS | WA3696129 | kitchen small hot box not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 11:10:50 | 2020-10-14 15:30:00 | Pass | Replaced damaged digital control thermostat as required.
MSA-DCS | WA3696139 | Visiting JP room - no power to a/c unit | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-21 11:30:00 | Pass | Investigate and repair power to visiting JP room air con
MSA-DCS | WA3696141 | Unit 1 - A Wing lock on the judas hatch A8 will not lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-15 13:00:00 | Pass | Replace barrel in hatch lock
MSA-DCS | WA3696149 | SOG - Admin section - female toilet is leaking from main value to the wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-16 13:05:00 | Pass | Removed broken flexi and inlet valve and leaking mini stop replaced with new
MSA-DCS | WA3696150 | Grounds - Common wire fault in controller, see notes below | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-11-06 10:30:00 | Fail | INSPECTED AND REPAIRED
MSA-DCS | WA3696178 | Unit 1, house 2, cell 1 - reed switch tampered | West Kimberley Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 14:12:00 | Fail | Checked all reed switches in house and replaced and secured into RS hole.1x 19mm door insert used from site stock
MSA-DCS | WA3696179 | Unit 2, House 5, Cell 5 and 6 - reed switches missing | West Kimberley Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 14:14:00 | Fail | Checked all reed switches in house and replaced and secured into RS hole.2x 19mm door insert used from site stock
MSA-DCS | WA3696190 | Front auto door is not operating correctly, see further notes below | Rockingham Justice Complex | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 14 Oct 2020 | 2020-10-14 16:09:14 | 2020-11-23 11:00:00 | Fail | Following our service call on 14/10/2020 to the entry automatic door, W28535 located at the above site, our technician reports that the existing hanger brackets are catching on the frame and will require replacement to restore and maintain safe and reliable door operation.Technician/s attended site of Rockingham Justice Complex to the Entry Auto Door No. WW28535 on 23/11/2020 and completed quoted works. Full test and inspection of door function completed prior to leaving site. This quote includes:" Removal of the existing components. " Supply and installation of new replacement hanger brackets "Test and check door operation."The above work is to be carried out during normal business hoursBreakdown of cost:Labour first visit $355.00Labour and parts $613.93
MSA-DCS | WA3696239 | Unit 1, Front Entrance- Gutter is rusted out | Casuarina Prison | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-11-26 10:30:00 | Fail | 15/10/20Inspect gutter and measure damaged section26/11/20removed and replaced rusted out gutter.12m colorbond gutter and 2 x 50mm spouts
MSA-DCS | WA3696245 | Unit 2, Water pipe leaking at the back of unit 2. may require capping off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 11:30:00 | Pass | Nill
MSA-DCS | WA3696301 | Unit 7, E Wing- Lino has lifted at the grille (creating a trip hazard) | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-11-25 10:00:00 | Fail | DAMAGED VINYL UPLIFTED & REPLACED WITH NEW
MSA-DCS | WA3696349 | Unit 14, B & D- disconnect and reconnect faulty urn | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-14 15:15:00 | Pass | Disconnected and reconnected urn in unit 14 b/d day room
MSA-DCS | WA3696353 | Kitchen work area Repair holes in tiles and walls | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 11:30:00 | Fail | Carried out repairs to damaged walls and replaced damaged tiles.
MSA-DCS | WA3696356 | Unit 2 air locks Repair Broken Door seals | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-11-05 11:30:00 | Fail | Attended site and measured opening for new airlock seals.Fabricated new airlock seals.Re attended site and installed new airlock seals.
MSA-DCS | WA3696358 | Unit 1, Air Locks - Broken Door seals | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-11-05 15:30:00 | Fail | Attended site and measured opening for new airlock seals.Fabricated new airlock seals.Re-attended site and installed new airlock seals.
MSA-DCS | WA3696363 | Garments, Workshop - Power cord to lightning cutter damaged | Casuarina Prison | WSM-BR-SITE | Equipment | Power Tools (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 08:30:00 | Pass | Repaired damaged lightning cutter in garments
MSA-DCS | WA3696366 | ISU S.O office air con not working (no power) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-15 09:30:00 | Pass | COMPLETED
MSA-DFES | WA3693459 | ground Rear Yard (Between tennis court and garden bed bitumen has lifted- see notes | CFRS Welshpool | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-29 07:40:00 | Fail | job completed - Asphalt repair at DFES 380 Welshpool Rd Welshpool
MSA-DFES | WA3696038 | ground, Wash pod - The power point at the wash point has burnt out | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 12:45:00 | Pass | Arrived to site , identified plug and socket outlet for washpump to be damaged and unsuitable for use. Replaced for new, tested for function and notified staff .
MSA-DFES | WA3696170 | ground staff lunch room exterior door handle is very loose | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 14:45:00 | Pass | Screws tightened on door handle. Tested. Now working correctly
MSA-DTAG | WA3688871 | Court 9, Isolate electrical circuit to Court 9 GPO “R1” to allow AV works to proceed | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-15 09:15:00 | Pass | Isolated r5 in court 9
MSA-DTAG | WA3689122 | Ground & Basement - FIP isolation, see notes below | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-17 17:13:00 | Pass | Isolated detection for works at 0700Returned and reinstated at 1700Sunday 18/10/20 cancelled as per Iain Johnston email 16/10/20
MSA-DTAG | WA3693003 | Basement, Secuirty - on Saturday 17 October at 07.00am, security functions may be affected due to | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-17 07:30:00 | Pass | Checked power / UPS for camera system due to power outage, not affected by power outage, all OK.
MSA-DTAG | WA3694356 | BMS to be reset due to weekend power outage – attendance required at 07.00am Monday 19 October | Supreme Court | GMP-BR-HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 09:30:00 | Pass | Attens site after power shutdown on the weekend. Reboot BMS and check operation of plant. Check all associated Airconditioning unit and found to work as normal.
MSA-DTAG | WA3696047 | Unable to operate the Sally Port roller door by remote | Midland Courthouse | GMP-BR-HO | Building | Security Doors (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 09:00:00 | Pass | Paul Cullum (15/10/2020) - Work NoteTravel to site. Inspect sally port roller door. Door runs dead man both directions, okay opening. Failing to close. Okay at time of visit. Suspect PE was not aligned, could move if touched. Align and secure PE. Checked limits, okay. Lubricated to silence while in motion. Left operational.
MSA-DTWD | WA3685349 | G block, Level 1, G124 - Broken lights needing reairs and some clips broken but check others in case | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 14 Oct 2020 | 2020-10-14 17:00:00 | 2020-10-14 15:00:00 | Pass | Replaced broken light fittings and dimmers to G block classroom.job complete
MSA-DTWD | WA3685378 | B block, level 2, B225 - flickering light | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 14 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 10:21:00 | Pass | Attended site and signed, flickering light in in b225. Couldn’t access room and it was occupied, willl return when room is free.will need big ladder to reach. **not complete**
MSA-DTWD | WA3695182 | unit 3 mezzanine floor 3CF2 Lights not working. Some of those that working are very noisy | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-20 13:30:00 | Fail | Attended site and signed in. Located class room in block 3 with faulty lights. Disconnected and removed old light fittings. Supply and replaced with new led panels. Tested all okay. Dispose rubbish. Signed out. Job complete
MSA-DTWD | WA3695986 | G block - toilets are blocked | Leederville Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 14 Oct 2020 | 2020-10-14 13:39:08 | 2020-10-16 09:30:00 | Fail | Complete
MSA-DTWD | WA3696015 | U011 faulty fluro fittings | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-21 10:45:00 | Fail | Repairs lights in U011 as shown by site.job completed
MSA-DTWD | WA3696049 | block 4 Blocked urinal male toilets | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 09:22:00 | Pass | Unblocked urinal
MSA-DTWD | WA3696133 | Lvl 5, Chiller deck- Chiller 2 in alarm | Perth Campus B2 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2021-02-02 08:47:00 | Fail | Return to site carried out isolation of chiller 2 and completed BRAaf repairs. Replacement of in line oil filter and repair of oil leak. Unit tested and run through restart sequence as per manufacturer manual. Unt has been placed back into auto function.
MSA-DTWD | WA3696147 | Sea Container- electrical lighting to be checked - see notes below | Naval Base | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 08:00:00 | Pass | Attended site and signed in. Spoke with staff on site about job. Got access to sea containers outside. Inspected light fittings in chemical area to be in good working condition. Ensure lights to be of explosive atmosphere rated fittings. Checked out connections and conduit. All okay. Advised site all safe. Tested all okay. Job complete
MSA-DTWD | WA3696173 | G block G9 student toilet are blocked | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 13:28:00 | Pass | Unblocked toilets
MSA-DTWD | WA3696183 | C-Block mens G/Floor & Ladies 2nd Floor & D-Block Library Female toilets blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-15 08:30:00 | Pass | Plunged 3 blocked toilets and checked for correct operation
MSA-DTWD | WA3696207 | Mclarty Grounds, repair broken re-tic sprinklers on station 1 and broken wiring | Joondalup McLarty Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-12-18 15:00:00 | Fail | 21-11-2020 - Provided a BRAF for completion of works onsite.Approval received 14-12-2020, repair works scheduled for the 18-12-2020.18-12-2020 carried out repairs as quote, system operating well.
MSA-DTWD | WA3696262 | C block, C003 - faulty hot water system | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-11-05 14:45:00 | Fail | Installed new hot water unit
MSA-DTWD | WA3696285 | Q Block, G/Floor, Room Q001B- sliding door has come off its sliders/ rollers | Joondalup McLarty Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 11:00:00 | Pass | Toby Bindon (19/10/2020) - Work NoteArrived at site, signed in and contacted David. Found door and set up work area. Removed pelmet, loosened off tension bolts. Lifted door back onto tracks. Once on, re tensioned lower bolts. Tried re hanging pelmet but wouldn’t go. Had to remove a small sign stuck on pelmet for it to sit in properly. Re fixed sign. Tidy area, packed away tools.
MSA-DTWD | WA3696367 | E block, outside/opposite EG20 - Nuisance tripping of RCD W1 in Switchboard E Block DB1 | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 09:30:00 | Pass | Attended site, signed in, completed jsa, investigated problem with circuit , circuit was live on arrival, switched all lights on circuit on , circuit didn’t trip, tested for voltage on load side of rcd and tested out all good , push button tested rcd and all operational, suspected moisture in board causing it to trip earlier in the week , no fault found , completed paperwork, signed out ***job complete ***
MSA-DTWD | WA3696516 | L7 center block Conference Room Split system a/c not running | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 13:59:00 | Fail | Attended site signed in and gained access. Carried out inspection of A/C. Wireless remote control found not to be sending signal to start A/C I . confrance room. Replace batteries with on site spares and rechecked for operation. A/C start as per setting on remote. Checked unit in through full operation range and is running correctly. No further action is required. Work area left tidy.
MSA-DTWD | WA3696517 | L2 male student toilet leaking tap | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-20 19:27:00 | Pass | Fix leaking taps
MSA-DTWD | WA3696519 | C block cafertia burning smell coming from evap Air con-poss burnt out motor | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 14 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-15 13:00:00 | Pass | Attended site, Filled out paperwork. Gained access to unit on roof. Isolated unit. Investigated and found motor hot and failing. Located parts. Picked up parts from suppliers and returned to site. Replaced fan motor, pulley and belt. Removed isolation and started unit. Checked operation. All ok. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-MRWA | WA3682485 | Fire alarm activation - reset and report on cause | Don Aitken Centre MRWA Head Office-Main Building-Basement-Foyer-South Entry | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 14 Oct 2020 | 2020-10-14 04:58:05 | 2020-10-14 10:29:00 | Fail | 14/10/20 - 01:15amZone 12 activated without known cause. Investigated level to unable to determine obvious reason for alarm. Left zone isolated to allow for monitoring of false alarms. Will call back during business hours. Left tag on panel14/10/20 - 09:30amRe-attended site, Zn 12 alarm did not re-occur. In consultation with with Brendan, removed isolation.Note: Zn 4 isolated 31/10/19 due to false alarm activations (reset but left isolated). Zn 30 isolated 9/8/20 due to fault constantly present.
MSA-MRWA | WA3696510 | west fluro light over desk not working | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-23 08:30:00 | Fail | Attended site, signed in, pre inspected ewp , completed jsa, took lift up to level 1 west office , set up work area, replaced tubes and starters , tested and all working , site happy , left ewp in spot it was dropped off , off hired ewp , spoke with programmed staff about barcode system as the barcode on the dB wasnt allocated to dB ***job complete***
MSA-MRWA | WA3696511 | Please not address below in notes-ground replace key tambour unit | Don Aitken Centre MRWA Head Office | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 14 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-15 15:00:00 | Pass | supply key and service lock on tambour unit
MSA-MRWA | WA3701478 | RETROSPECTIVE WORK ORDER-L1 stopped not responding - see notes | Don Aitken Centre MRWA Head Office-Main Building | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 14 Oct 2020 | 2020-10-15 17:00:00 | 2020-10-14 20:15:00 | Pass | job comleted - Switched key to off position, lift started running. Checked fault log, DTC fault was recorded. Made 100 run of lift , nofault recorded. Cleaned door sensor. Put lift back on service
MSA-DCA | WA3701347 | Male change room – near loading bay 7 light not working - see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Male Shower | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 07:14:00 | Pass | Replaced ballasts tubes and starters in faulty light
MSA-DCA | WA3701412 | Garden - retic system leak | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Water (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 11:15:00 | Pass | job completed - Irrigation technician Kody repaired 4 leaks in the Urban Orchard. Their cause is unknown as some were clean cuts and otherswere smaller damaged sections. All were cut out and replaced with new subsurface drip line.
MSA-DCS | WA3700833 | Unit 3, Cell D4 - Call cell faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 11:44:57 | 2020-10-26 08:48:00 | Fail | part returned to site stock, job will be completed under WA3717614
MSA-DCS | WA3700834 | Unit 6, Cell D8 - faulty cell call | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 11:48:32 | 2020-10-15 12:00:00 | Fail | Travelled to site and tested cell call, blocked sound. Removed cell call and cleared out toothpaste from cell call. All cleared out and retested ok. Job complete
MSA-DCS | WA3700841 | Microphonics, X internal zone 13 & 14 - Not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 11:50:08 | 2020-11-10 14:55:00 | Fail | Performed calibrations and tested OK.
MSA-DCS | WA3700864 | Unit 6, Cell A13 - Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 07:57:20 | 2020-10-15 09:45:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3700872 | Unit 6, Cell A24 - Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:00:29 | 2020-10-15 10:50:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3700874 | Unit 6, Cell A23 - Sink taps continually dripping | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:01:20 | 2020-10-15 11:50:00 | Pass | Turned off water rewashering tap
MSA-DCS | WA3700875 | Unit 6, Cell B4 - Toilet continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:02:18 | 2020-10-15 12:55:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3700881 | Unit 6, Cell D8 - Blocked drain, water coming up from drain underneath sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:03:18 | 2020-10-15 13:58:00 | Pass | Plunger used to unblock drain
MSA-DCS | WA3700883 | Kitchen Freezer sitting on -9 Degrees and should be 18 degress | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 11:58:48 | 2020-10-16 15:00:00 | Fail | Defrost was not working correctly. Tightened terminals on contact and freed up contact. Defrost ran as designed
MSA-DCS | WA3700885 | Unit 6, Cell A15- Toilet won’t flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:04:46 | 2020-10-15 15:00:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3700893 | Kitchen, Outside sink- water leaking from wall | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:08:02 | 2020-10-15 17:01:00 | Pass | Redirect water pipe as leaking in wall
MSA-DCS | WA3700903 | SHU, A6 - cell a6 obs lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 09:00:00 | Pass | Checked light in a6, all working fine. Waited for access
MSA-DCS | WA3700911 | CCU (11)- Cell D1- Viewing hatch window, bottom fitting ripped off, exposing glass. | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 08:12:43 | 2020-10-16 15:00:00 | Fail | GLASS FRAMEWORK REPAIRED
MSA-DCS | WA3700945 | Unit 2, Office - check and test air conditioner for air quality due possible Legionnaires' disease | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 12:20:55 | 2020-10-15 10:45:00 | Pass | Arrived to site.Met with Maintenance to discuss.Checked over system.Found unit in good working order.Sprayed anti bacterial coil cleaner through coil and fins.Wiped down unit.Tested on all modes and working okay.Discussed with Maintenance.
MSA-DCS | WA3700956 | Jasper, B Wing- Hot water unit not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-28 10:50:00 | Fail | Replace dflue damnper in jasper b wing
MSA-DCS | WA3700974 | Unit 2, Cell 68 - lighting fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-16 18:30:00 | Pass | Investigate and repair unit 2 cell 68 light fitting
MSA-DCS | WA3701101 | control - H3 camera not working | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 14:15:00 | Pass | Attended site and found camera not working , checked EC cabinet and found fuse blown to camera , replaced fuse and all tested ok. Job complete
MSA-DCS | WA3701108 | unit 2 cell B5 barrel on the hinges are broken on cell door | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 14:17:32 | 2020-10-15 12:30:00 | Pass | Replaced 2 Hinges on cell B5 Unit 2
MSA-DCS | WA3701113 | Unit 2 C and D fire exit cannot get key into lock | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 14:25:50 | 2020-10-15 13:15:00 | Pass | Adjusted escutcheon on Fire Exit Door Unit 2 C/D Wing
MSA-DCS | WA3701159 | Unit 4 - B1 Window in Cell B01 will not stay open. Drops back down. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 13:00:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3701162 | Unit 14, Cell B04- Prisoner cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 11:00:00 | Pass | Repaired faulty lights in unit 14 b4
MSA-DCS | WA3701171 | Unit 1 cell A1 Repair Broken Door Frames | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 16:30:00 | Pass | Welded hinges to metal frame to stop cell doors from dropping.
MSA-DCS | WA3701174 | Lenard, Cell C03- shower not working (intermittent) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-22 12:50:00 | Fail | Replaced faulty flowmatic control box
MSA-DCS | WA3701177 | Lenard, Cell B01- shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-22 11:20:00 | Fail | Replaced control box, 2x solenoids and 2x buttons
MSA-DCS | WA3701213 | NVR 5 Disk 0 has failed - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-30 13:28:00 | Fail | work order to be invoiced at cost to date.
MSA-DCS | WA3701215 | Unit 4 House 1 Living camera offline-SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 14:15:00 | Pass | Tested camera from Unit, image very poor.removed camera and found BNC corroded. replaced BNC and reinstalled image restored
MSA-DCS | WA3701219 | Unit 4 House 2 Entry camera offline - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 14:16:00 | Pass | Tested camera from Unit, image very poor.removed camera and found BNC corroded. replaced BNC and reinstalled image restored
MSA-DCS | WA3701221 | Unit 4 House 4 Corridor camera poor image - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 14:17:00 | Pass | Refocused camera, camera ok on test monitor but appears out of focus in control, swapped modems in house. fault with S700 T replaced with PFM stock.camera image clear
MSA-DCS | WA3701223 | Control room keyboards faulty - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-18 17:16:00 | Fail | Replaced MDAS, DCP and PDS Keyboards and mouse.had to remove cable management tray from under desk
MSA-DCS | WA3701225 | KVM extender in control intermittent - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-20 16:05:00 | Fail | Removed cable management tray under desk in control room,replaced HDMI extender for PDS.part from seme stock
MSA-DCS | WA3701228 | External visits controller Gbus Failed - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-16 13:26:00 | Pass | Controller Gbus has failed , tested Gbus 2 and confirmed ok.Replaced Gallagher 6000 controller from PFM stock. Programmed and tested. Gallagher 6000 controller to be ordered to replace site stock
MSA-DCS | WA3701290 | Unit 4, office - air con not working (Already attended) | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 11:00:00 | 2020-10-15 13:00:00 | Pass | Advised whilst onsite of another unit with similar issue.Inspected unit.No water holding or any risk of disease.Noted fan barrel dirty.Removed all covers and louvers and cleaned.Applied coil cleaner to coil and barrel.Awaited.Setup cleaning kit.Washed out system.Dried system.Covers returned.Tested.Airflow improved.Maintenance advised.
MSA-DCS | WA3701293 | Kitchen - bun divider timing - needs timing as faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 13:15:04 | 2020-10-19 16:30:00 | Fail | 19/10/20Arrived at site liaise with reception, walk to kitchen, identify bun rounder, isolate remove panels, test/fault find diagnose and found the motor drive belts were loose, tightened/adjusted motor bolt, reassemble all components and tested all components for correct function all okay.
MSA-DCS | WA3701318 | Unit 6, Cell 9- Exhaust fan hanging from ceiling | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 13:33:22 | 2020-10-15 15:00:00 | Pass | Replaced damaged exhaust fan
MSA-DCS | WA3701346 | Unit 5, C12 - Window will not stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 14:00:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3701350 | Offical Visits, Room 4- Roof Leaking | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-11-19 11:00:00 | Fail | SOURCE OF LEAK DETECTED & REPAIRED
MSA-DCS | WA3701354 | Unit 7 H8 - Light switch outside cell all pushed in needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 11:30:00 | Pass | Replaced damaged switch
MSA-DCS | WA3701357 | Unit 7, F12 - Light switch outside cell broken needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 13:30:00 | Pass | Replaced damaged switch
MSA-DCS | WA3701359 | Gatehouse, Key Control- Air Con not working. Gate 2 and Gate 4 | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 08:30:00 | Pass | Meet nrp on site,reprogram controller to rectify cooling issue and test.
MSA-DCS | WA3701367 | Control - Zone 23, External omnitrax not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 13:58:32 | 2020-11-03 13:16:00 | Fail | Performed calibrations. Tested okJob conplete
MSA-DCS | WA3701371 | Unit 7, Cell H6- Light switch outside cell all pushed in | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 12:30:00 | Pass | Replaced damaged switch
MSA-DCS | WA3701377 | Unit 7, S Wing cleaning cupboard - Tap continually dripping | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-26 11:05:00 | Fail | Turned off water replacing hot and cold taps
MSA-DCS | WA3701394 | Secure pedestrain inner door not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Oct 2020 | 2020-10-15 18:17:04 | 2020-10-15 18:30:00 | Fail | Lock found to be faulty, replaced with recommended replacement tested ok.
MSA-DCS | WA3701420 | Rec tower 7 PA System in tower 7 not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 14:33:44 | 2020-10-27 12:00:00 | Fail | Soldered 3 pin plug onto new hand held microphone. Installed in Obs post 7. Tested ok. Adjusted volume as required. Parts used:Redback C3055 PA microphone 3 pin plugConsumables
MSA-DCS | WA3701429 | SOP, Unit 12, all showers have blocked nozzles | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 13:30:00 | Pass | Nill
MSA-DCS | WA3701451 | Perimeter Fence Bottom rail & fittings need inspecting for rust strength & integrity around perimer | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2021-03-26 12:01:00 | Fail | 30/10/20Inspect rails on perimeter and document and damage / rust
MSA-DFES | WA3701314 | 2nd floor, Female toilet- last cubicle toilet wont flush | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 16:04:00 | Pass | Unblocked toilet and replaced inlet valve
MSA-DFES | WA3701335 | station officers dorm toilet not fllushing correctly | CFRS Maddington | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 10:02:00 | Pass | Unblocked the toilet using the drain machine
MSA-DFES | WA3701487 | ground FF toilet room 8 light not illuinating | CFRS Malaga | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 16:45:00 | Pass | Locate faulty light. Replaced faulty globe and starter with new. They also had issues with the sensors in the gear room. I found one faulty sensor however I have been on site in the past looking at the sensors. Replaced both sensors with new just in case of intermittent fault. Test both sensors and they are working correctly. Adjusted to time so the lights will stay on for around 10 minutes. Advised staff of work completed.
MSA-DFES | WA3719151 | RETROSPECTIVE WORK ORDER-External check carried out - DO NOT ATTEND | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-15 11:59:00 | Pass | Despatch Comments:BYPASS Z25 WATCH ROOM DOORPatrol Resolution:EXTERNAL CHECK CARRIED OUT. REAR STAFF KITCHEN SLIDING GLASS DOOR FOUND AJAR BUT EXTERNAL FLY SCREEN DOORS TO GLASS DOOR WAS SECURED, NO PERSONS FOUND ONSITE. NO OFFENCE DETECTED. ALL APPEARS SECURE.
MSA-DFES | WA3719156 | RETROSPECTIVE WORK ORDER - external check carried out - DO NOT ATTEND | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-15 11:17:00 | Pass | Despatch Comments:ISOLATION R/S ZN 18 BAY 1 FRONT DOORPatrol Resolution:EXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE. NO OFFENCE DETECTED. NO PERSONS FOUND ONSITE.
MSA-DTWD | WA3700844 | B Block, Room B106- exit light switch is faulty | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-16 12:14:00 | Pass | Rectified fault to exit sign and replaced 2x fluros in room. Tested, job complete.
MSA-DTWD | WA3700853 | B Block, Room B209 photocopy room- light tubes faulty | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-16 10:30:00 | Pass | Repalced multiple lamps out.job completed
MSA-DTWD | WA3700993 | JU21 classroom upper floor - Front ceiling Air con wall controller pad will not set to the set temp | Jandakot Campus - Hangar | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 12:30:00 | Pass | Replaced Daikin wall controller
MSA-DTWD | WA3701079 | Old building 819, ground - leaking sewerage | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-15 17:30:00 | Pass | Job completed - Clear blockage to sewer main near old building 819
MSA-DTWD | WA3701142 | Block 6, Toilet duct off cleaners room- light not working, see notes below | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 13:49:00 | Pass | Attended site and signed in. Replaced 2x Fluros to light in plumbing duct B6. Tested job complete.
MSA-DTWD | WA3701156 | Block 6, Lvl 4, Plant Room - Door lock faulty | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 15 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-15 16:00:00 | Pass | replace cylinder components and service to lock on level 4 plant room
MSA-DTWD | WA3701234 | A block L1 A141 faulty light switch doe not turn all the lights on | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-20 14:03:00 | Pass | Job incomplete due to need of extra wiring and materials. Booked in to return 20/10/20 Barry to confirm via email
MSA-DTWD | WA3701389 | D Block, Room D203- Aircon noisy fan | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 15:00:00 | Pass | Accessed d203.Test run reveals wall controller operates but when turned off noise still appears. Ceiling space accessed to inspect ducting, damper and fan operation.Investigation shows fan operates off bms time schedule and wall controller operates the cooling actuators. Bms operated fan deck and noise from fans within tolerance and consistant noise with other room fan operations
MSA-DTWD | WA3701481 | D Block Foyer - 4 x lights not working | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 15:30:00 | Pass | Attended site and signed in. Located d block foyer. Found 4 x lights not working. Advised to replace with site supplied led panel lights. Isolated and removed old light fittings. Retro fit new square panels into roof. Tested all okay. Job complete
MSA-DTWD | WA3720279 | E Block, Canteen- Door lock is faulty | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 15 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-16 15:10:00 | Pass | job completed - Security Screen Lockset
MSA-MRWA | WA3701512 | RTTO – Desk 14 Sit stand desk not working please remediate | Road Network Operation Centre (RNOC)-Main Building-Second Floor | GMP-BR | Furniture | Office Furniture (FU) | SCHIAVELLO SYSTEMS (WA) PTY LTD | 1 | CLOSE | 15 Oct 2020 | 2020-10-16 17:00:00 | 2020-10-16 09:30:00 | Pass | to be closed out at $0 cost
MSA-DCA | WA3703124 | Pica garden Bar - large leak, zone 11 | Perth Cultural Centre Precinct | GMP-BR | Plumbing & Drainage | Materials (PD) | Earth & Water Pty Ltd | 0 | CLOSE | 16 Oct 2020 | 2020-10-16 11:03:57 | 2020-10-16 10:00:00 | Pass | Completed items:- Located and identify leak- Repaired leak- Ran zone and tested for leaking
MSA-DCA | WA3703434 | Steam boiler has low steam alarm | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-20 09:18:00 | Fail | COMPLETED
MSA-DCA | WA3703507 | urinal constantly running | Sunset Hospital Heritage Precinct-Building G-Two Storey Ward Block-Ground Floor-Male Toilet - New Toilet Block | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 09:14:00 | Pass | Reconnect wire and adjust auto flow solenoid
MSA-DCA | WA3703737 | Leaking air con pipe in ceiling space | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2-S6 - Dressing Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 09:00:00 | Pass | Investigation completed, new work order being raised for plumbers to repair.
MSA-DCS | WA3703134 | Jeelia, A4 - light button jammed in | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-21 10:00:00 | Fail | Checked all switches and power points replaced faulty switch mech and plate. Installed screws to avoid being pushed in again
MSA-DCS | WA3703161 | Unit 10, 13 - Water coming up through floor underneath basin all blocked up | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 07:49:46 | 2020-10-16 12:10:00 | Pass | Drain machine used to clear blockage
MSA-DCS | WA3703166 | Old control - power lost | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 16 Oct 2020 | 2020-10-16 11:56:45 | 2020-10-16 15:00:00 | Fail | Investigated ups power circuits in old control room, found and upgraded circuit breakers. Tested and commissioned
MSA-DCS | WA3703169 | Old control - power lost, cameras down | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Oct 2020 | 2020-10-16 11:59:08 | 2020-10-16 12:00:00 | Fail | Attended site and found workstations all offline. Checked and found RCD had tripped in switchboard. Electrician present and replaced with replacement RCD with larger capacity. Retested and all workstations powered up ok. Reloaded camera layouts and all working ok job complete
MSA-DCS | WA3703178 | Unit 7, control office - Control office hot water urn ruptured tank | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-21 10:25:00 | Pass | Replaced faulty solenoid. Cleaned level probes and re configured install.
MSA-DCS | WA3703333 | Medical centre - hot water urn, boiling constantly, possible thermostat. 3 liter reem - 70303W/AU | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 09:25:32 | 2020-10-16 12:59:00 | Pass | Replaced solenoid, cleaned level sensor, to RheemBWU installed new capex asset to replace old fatigued Zip Global System - installed Maxiflow Scale System A40184148J.
MSA-DCS | WA3703389 | Reception button to release door not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-20 09:45:00 | Pass | Attended site and installed new push button underneath SO desk in gatehouse to release staff amenities door. All programmed and installed ok. Job complete
MSA-DCS | WA3703391 | No video signal in ICF room | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-12-03 16:00:00 | Fail | Installed new W/s supplied by PFM in ICF room.Supplied and installed Cat 6 cable for network link to ICF room Supplied and installed HDMI cables for connectivity to monitorsConfirmed correct functionality - works complete
MSA-DCS | WA3703494 | Unit 14, A Wing- Cold shower tap is hard to turn on & the shower head leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 11:30:00 | Fail | Nill
MSA-DCS | WA3703530 | Zone 7, Camera 1 has no video | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 11:52:57 | 2020-10-16 17:00:00 | Pass | Attended site and investigated the fault.Found that IndigoVision encoder is ant infested.Dismantled and cleaned unit.Tested.All ok at departure
MSA-DCS | WA3703612 | U6 D11 Hand basin dripping water from underneath plug hole maybe cracked needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-26 11:50:00 | Fail | Removed basin and waste then reinstalled resilcoing plug & waste
MSA-DCS | WA3703619 | Unit 6 D11 Toilet plunger sticking needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-26 13:00:00 | Fail | Removed cistern replacing flush button
MSA-DCS | WA3703717 | Voice recording not working for cell intercom | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Oct 2020 | 2020-10-16 21:45:45 | 2020-10-16 17:50:00 | Pass | Checked voice recordings and found recordings stopped recording after August.found voice recorder directory had become corrupt, archived all voice recordings into dates and reprogrammed new recordings. tested various cell calls and recording quality.
MSA-DCS | WA3703739 | Eyre courtyard bee infestation | Wandoo Rehabilitation Facility | WSM-MW-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 0 | CLOSE | 16 Oct 2020 | 2020-10-16 17:46:33 | 2020-10-16 16:25:00 | Pass | Removed beehive and bees in wooden box from courtyard in rehabilitation centre. Took entire hive from site for relocation.
MSA-DCS | WA3703774 | Garments - light in workshop not working (high bay light) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-11-03 14:00:00 | Fail | Replaced faulty lights in garments workshop using scissor lift
MSA-DCS | WA3703796 | Unit 1, Cell A2- Blocked toilet | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 15:36:33 | 2020-10-17 07:52:00 | Pass | unblocked toilet
MSA-DCS | WA3703798 | Unit 1, Cell B8- Blocked Sink and Showers | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 15:39:13 | 2020-10-17 08:28:00 | Pass | Unblocked basin and shower
MSA-DCS | WA3703799 | Unit 1, Cell B7- Blocked Sink and Showers | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 15:40:17 | 2020-10-17 09:05:00 | Pass | Unblocked basin and shower
MSA-DCS | WA3703803 | Unit 1 A 15 blocked sink and shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 15:43:42 | 2020-10-17 09:40:00 | Pass | Unblocked basin and shower
MSA-DCS | WA3703805 | Unit 1 A 16 blocked sink and shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Oct 2020 | 2020-10-17 15:45:48 | 2020-10-17 10:29:00 | Pass | Unblocked basin and shower. Checked pumps and macerator at the front
MSA-DCS | WA3718048 | **Retrospective order ** power surges throughout the building | Mandurah | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-16 22:30:00 | Pass | Power fluctuations due to failing neutral connection to site. Informed western power. Repairs made to aerial connection by western power staff. Power restored to building.
MSA-DFES | WA3703341 | Communications Centre - male toilets above cubicle light no longer working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-21 15:15:00 | Pass | Located 2 faulty light globes in communications centre Male toilet. We replaced with new and tested for function. Notified site and left site.
MSA-DFES | WA3703399 | Pump at bottom dam has lost prime & overheated | FESA RHQ - Forrestfield | GMP-BR | Mechanical Services | Pumps (MS) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-11-02 10:31:00 | Fail | Works completed by Malcolm Thompson pumps
MSA-DFES | WA3703429 | Dorm area west passage #57- Sliding door hard to close & open, see further notes below | Butler Career Fire Station | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-20 08:30:00 | Fail | Work completed
MSA-DFES | WA3703604 | First floor, lift lobby 1, east auto door - exit faulty button, delay when pressing buttton and have | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 15:30:00 | Pass | Technician attended the site of Cockburn Emergency Services Centre to the Level 1 lift lobby East Auto Door on 22/10/2020. Following a full test and inspection of door components found fault to be push button working ok, not faulty but slight delay and have to press and hold for a second. Technician checked connections and found has resistors fitted as it goes through the access system. Would need Access Company to investigate and see if can be sped up. Left door in working order and tested ok. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3703688 | DEMA Office - Air Con high temperature exceeds work conditions | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-29 14:00:00 | Fail | Pick up laptop to enable access to controls. Attend site. Meet with control technician. Access control and found BMS heating call to be 100% further investigation found that some how a heating setpoint had changed causing this issue. Reset the heating setpoint and remove it from access. Found heating call to disappear and system is working as normal.
MSA-DFES | WA3703752 | ground rear yard Wall around yard is falling apart. Trip Hazard - see notes | CFRS Welshpool | GMP-BR | Building | External Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-11-16 12:00:00 | Fail | Ground down raised concrete pathway's raised edges and mudded dislodged bricked back into position
MSA-DTAG | WA3703406 | Administration workstation unable to switch via KVM | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-11-03 14:00:00 | Fail | Installed KVM switcher for Pacom & Gallagher. Replaced old monitor with AOC monitor. Tested operation and all is in working order.
MSA-DTAG | WA3703416 | Courtroom 2 - Small area of carpet is lifting | Rockingham Justice Complex | GMP-BR-HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-16 14:45:00 | Pass | CARPET RE GLUED DOWN
MSA-DTAG | WA3703793 | 1903 ground Lift 4 Lift displaying “out of serv.” on LED panel | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-16 16:45:00 | Pass | job completed - Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA3703807 | old court house ground 6 globes require replacement. | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 13:30:00 | Fail | Replaced all blown and faulty lamps and tested working
MSA-DTWD | WA3703320 | Block 1 - Faulty VRV unit | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 16 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 16:30:00 | Pass | Works completed as per BRAF
MSA-DTWD | WA3703402 | A block ground AG3 Swipecard access not working - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 10:30:00 | Fail | 19/10/2020: AG3 door not opening on badge. Found door controller and checked cable. Possible reader or controller fault needs replacing22/10/2020: Reattended, replaced faulty door controller, now egress and access is working correctly on door
MSA-DTWD | WA3703549 | Nursery EVC 4 solenoid not opening fully to allow water though. | Murdoch Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 13:30:00 | Pass | Replaced evap cooler water inlet solenoid
MSA-DTWD | WA3703553 | C Block, Room C54- Water is leaking under the sink to the water filter. | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-20 15:04:00 | Pass | Replaced plv and tap adaptor fittings which was leaking. Water logic rental,
MSA-DTWD | WA3703720 | D Block, Room D16- Leaking tap on North Wall | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 12:45:00 | Pass | Serviced hot tap
MSA-DTWD | WA3703773 | Block 7 Leaking pipe from wall – male toilets | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 16 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 12:00:00 | Fail | Sealed leaking toilet pan had issues drying area for sealant
MSA-MRWA | WA3703410 | kitchenette zip heater tap leaver broken | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-16 13:33:00 | Pass | Replaced tap
MSA-MRWA | WA3703784 | Emergency light not working above stairs | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Boiler Room | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 16 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 15:30:00 | Pass | Attended site and signed in upstairs. Checked and inspected western stairwell. All lights and exits working. Checked out eastern stairwell and found 1 light on level 1 not working. Replaced fluro tubes to fitting. Tested all okay. All stair wells are illuminated. Identified barcode number for emergency circuit. Signed out and return keys. Job complete
MSA-DCS | WA3717263 | Perimeter Alarm G 1 and D3 for external is not working | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 14:51:30 | 2020-10-17 14:45:00 | Pass | Energised fence zones G1 and D3 tested fully operational, zones tested in multiple locations functioning correctly, zones should be reset during testing, having all zones in alarm at once can slow system.
MSA-DCS | WA3717344 | fire panel and sprinklers require reset, pump house | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 18:15:24 | 2020-10-17 18:14:00 | Pass | replaced damaged head using spares onsite
MSA-DCS | WA3717346 | broken pipes, smashed basins and toilets | Casuarina Prison | WSM-BR-RC | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 18:19:40 | 2020-12-11 15:00:00 | Fail | nil
MSA-DCS | WA3717348 | Unit 1- Cell D10 - Cell call unit not working | Hakea Prison-Unit 1 | GMP-BR- HO | Equipment | Building Equipment (EQ) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 11:00:00 | Pass | Rectified the fault, test cell call ok and working. Job completed.
MSA-DCS | WA3717350 | smashed cameras, broken security equipment, check electronics b and d wing | Casuarina Prison | GMP-BR-RC | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 18:21:07 | 2020-11-06 12:00:00 | Fail | Attended site and replaced 2 x PIRs and installed with new 360 Dome PIRs, all installed programmed and tested ok. Tested all alarm for correct operation with new PIRs and retested all cell call system. All systems checked and working ok. Job complete
MSA-DCS | WA3717353 | make safe for circuits - B and D wing - unit 1 | Casuarina Prison | WSM-BR-RC | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 18:18:36 | 2021-06-28 13:30:00 | Fail | Repairs to wing and dayroom lighting and replaced store lights. Damage switches. Isolated damaged oven and reconnected. Isolated damaged urn. Replaced damaged dayroom lights from scaffolding.
MSA-DCS | WA3717363 | unit 7 - F wing - multiple toilets blocked | Hakea Prison-Unit 1 | GMP-BR- HO | Equipment | Building Equipment (EQ) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 18:51:34 | 2020-10-18 09:00:00 | Fail | Cleared blocked drain caused by rugs,apples etc to F wing unit 7.
MSA-DCS | WA3717365 | Various windows smashed, control room affected | Casuarina Prison | WSM-BR-RC | Building | Materials (BU) | Midolo Building Services | 0 | CLOSE | 17 Oct 2020 | 2020-10-17 18:17:50 | 2020-12-10 15:00:00 | Fail | works completed
MSA-DCS | WA3717370 | control room gate house - D2, C1 external P.E. set faulty | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 18:00:00 | Pass | Issue investigated and report sent to PFM - Advised that PFM will attend site to assess issue - Further works to be quoted. No further the work to be carried out under this work order.
MSA-DCS | WA3717379 | Wooroloo Prison Farm - Main kitchen - Prover - steams the bread - float has touched the element. | Wooroloo Prison Farm | GMP-BR- HO | Catering | Catering Services (CT) | BAKE-QUIP PTY LTD | 2 | CLOSE | 17 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 12:30:00 | Pass | Completed 19/10/209/11 RESUBMITTED WITH SERVICE REPORT ATTACHES SIGND BY DAVE BROWN.
MSA-DCS | WA3717384 | Fire Pump is in alarm | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 18 Oct 2020 | 2020-10-18 06:24:22 | 2020-10-18 05:33:00 | Pass | pump running - fuel low
MSA-DCS | WA3717402 | Unit 1- No hot water- Boiler technician to attend. | Melaleuca Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 0 | CLOSE | 18 Oct 2020 | 2020-10-19 08:29:53 | 2020-10-18 12:45:00 | Pass | Travel to site sign in and carry out security checks. Make way to unit 1 investigate no hot water issues with boiler. Boiler has power from isolator but no power on LFL or anything else. Something else seems to be holding out boiler as pumps aren’t running either. Is all switched on on panel. Check fire alarm panel reset alarms there and cleared them all. Boiler and pumps started up made sure was operating ok. Informed staff boiler is operating packed up and left site.
MSA-DCS | WA3717417 | fence alarm is keep going off for zone 6 | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Oct 2020 | 2020-10-19 11:42:23 | 2020-10-18 15:45:00 | Pass | Checked cabling on zone 6 (both sections) reset controller and tested restored, both cases now registering 1Mohm, system restored
MSA-DCS | WA3717434 | Honeywell Computers - Cannot log back in - Screen went black. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Oct 2020 | 2020-10-18 23:21:13 | 2020-10-18 22:15:00 | Pass | System software restored, found software closed on main SMS computer. Restored and tested fully operational.
MSA-DFES | WA3719149 | RETROSPECTIVE WORK ORDER-External check completed-DO NOT ATTEND | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 18 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-18 02:47:00 | Pass | Despatch Comments:ZONE 36 TRAINING SINGLEPatrol Resolution:EXTERNALLY CHECK COMPLETED. ALL APPEARS CORRECT NO SIGNS OF FORCED ENTRY. INFORMED MONITOR CLEARED BY DAVID
MSA-DCA | WA3717737 | Leak in ceiling from sink waste floor above | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2-S6 - Dressing Room | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 17:05:00 | Pass | Reppaced section of leaking pipe
MSA-DCA | WA3717751 | Automatic toilet door closer is not responding | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2-Disabled Toilet - End of Corridor | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-11-03 13:30:00 | Fail | 1095913, removed existing operator and fitted new ED100 and rewired system to suit , commissioned and tested operation all ok.
MSA-DCA | WA3717800 | Half of Air con in Main theatre not working, see further notes below | Subiaco Arts Centre-Main Building-Level 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-30 09:14:00 | Fail | Complete Indoor fan motor replacement. Rewire and realignment of adjustable pulley. Found blown fuse on blue phase. Organise replacement. Found compressor faulty tripping circuit breaker. Notify Dan for quotation replacement. Quote was submitted to the client for approval on the 12/11.
MSA-DCA | WA3718154 | Harry Butler Centre, Cool Room in fault-outside parameters, please investigate | Collection and Research Centre Welshpool-Administration and Library Building-Roof Level-Roof Area - Adobe Laboratory | GMP-BR | Refrigeration | Coolroom (RE) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-19 16:30:00 | Pass | Attended site 19-10-20 1230. HBC downstairs coolroom to be in alarm sitting at 7c. Applied tests and checks to find system short cycling on LP safety. Carried out leak detection procedures. Investigation found leak present on liquid reciever bung plug. Pumped refrigerant down to compressor and condenser. Removed and resealed leaking bung plug. Leak checked system and added 2kg R134A. Adjusted dual pressure control and tested operation. System operating correctly cycling on 2c sp. Left site 19-10-20 1630.
MSA-DCA | WA3718297 | Steam boilers in fault, low steam alarm | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 17:30:00 | Pass | Low steam pressure and low gas pressure alarms. Reset gas pressure switch. Monitored cycles and supply pressure. Contractors carried out Fire Alarm testing in in the day.Closed job.
MSA-DCS | WA3717601 | Unit 4 control room Light switch on side of light above computer broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 10:30:00 | Pass | Replaced faulty switch
MSA-DCS | WA3717605 | Unit 1 A7-A15 All GPO’s tripping RCD | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-20 15:00:00 | Pass | Lead in GPOs, replaced 8 x GPOs
MSA-DCS | WA3717614 | Unit 3 D4 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-21 17:00:00 | 2020-11-19 09:30:00 | Fail | Reterminated water damaged cell call cable. Reinstalled cell call point and tested all ok.
MSA-DCS | WA3717620 | Unit 4 B14 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 15:30:00 | Pass | Replaced defective cell call, test ok and back to normal operations.
MSA-DCS | WA3717642 | Unit 2 B13 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-19 12:30:00 | Pass | Rectified and fixed the faulty connector, test cell ok and working. Job completed.
MSA-DCS | WA3717655 | Yeeda B07 shower,toilet,basin not working (intermittently) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-22 15:15:00 | Fail | Replaced fauly control box(2x installed), 3x buttons and faulty toilet solenoid
MSA-DCS | WA3717659 | Unit 2 Electrical Room Fire Panel Fault N3 L1M75 | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 07:44:13 | 2020-10-19 12:18:00 | Pass | BG 19/10/202x Faults on FIP on arrival;• Unit 2 A/B 1/2, pipe closed. Reset and rebooted. Fault cleared-Unit 2 A/B 5/6, pipe 4 blocked. Cleaned pipe and sample point. Fault clearedSystem normal at time of departure
MSA-DCS | WA3717661 | all security and duress alarms and has blown alarms-can hear batteries vibrating through walls | Mandurah | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Oct 2020 | 2020-10-19 11:46:08 | 2020-10-20 14:18:00 | Fail | Replaced power supply’s and worked with lock smith to fix door tested system and batteries all tested ok
MSA-DCS | WA3717703 | Outpatients Area Door can't be opened. Faulty lock. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 08:17:40 | 2020-10-19 10:00:00 | Pass | Adjust strikes on 2 x doors
MSA-DCS | WA3717740 | Unit 1 - C10 window broken. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 15:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3717750 | Unit 5 - A12 window mechanism broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 12:45:00 | Pass | RE NEW SPIRAL BALANCES & FRAME REPAIR
MSA-DCS | WA3717765 | Unit 9 - A9 Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-23 13:00:00 | Fail | Nill
MSA-DCS | WA3717769 | Unit 6 - B Wing window runners faulty small left and right middle | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2021-01-29 14:30:00 | Fail | Replaced damaged window window boxes
MSA-DCS | WA3717770 | SHU (9) - B4 Split pin broken on shower- shower not switching off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 08:50:36 | 2020-10-22 12:30:00 | Fail | Denied access at 2:00pm on 19/10/20, will go back on 21/10/20
MSA-DCS | WA3717779 | kitchen Freezer is not running at the correct temp, freezer alarm running at high temp | Casuarina Prison | WSM-MW-HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 08:54:24 | 2020-10-29 09:00:00 | Fail | Job signed as instructed as repairs to be carried out under warranty.
MSA-DCS | WA3717780 | Unit 14 - A16 shower drain is missing cover | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 10:30:00 | Pass | Nill
MSA-DCS | WA3717786 | Unit 7 - A8 door hinge needs adjusting as door has dropped | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 11:30:00 | Pass | Replace hinges, fixings, adjust strike and lubricate lock.
MSA-DCS | WA3717790 | kitchen water tap that is located in between the 2 brat pans in the Kitchen has fallen off. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 12:30:00 | Pass | nil
MSA-DCS | WA3717797 | server room gate house strong electrical smell coming through vents | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 19 Oct 2020 | 2020-10-19 13:08:56 | 2020-10-19 13:05:00 | Pass | Batteries in bank 2 are starting to fail and over heat causing them to leak and spray fluid on the cabinet doors, isolation carried out on bank 2 and battery replacement needed, Mario was informed and contacted there UPS NPS campany to get a technician Doug out to meet me and discuss next steps. Recommended installing some cooling fans on the top of the Battery bank enclosures to avoid this happening in the future.Tested batteries in 1st bank and 2nd bank, batteries are showing good voltage, Tested batteries for shorts to earth.
MSA-DCS | WA3717801 | Old control room monitor has no signal | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 09:12:04 | 2020-10-19 16:30:00 | Pass | Power loss occurred in area. System reset and connection restored to system database via login. Tested ok.
MSA-DCS | WA3717803 | Exp Project Bld 1 (Between U15-U16) - Office has a problem with the lock (prisoner waiting area) | Casuarina Prison | WSM-MW-HO | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 14:45:00 | Pass | Check lock function, no fault found. Discuss problem with officers, require replacement barrel.Obtain barrel from supplier, Install re[placement barrel.
MSA-DCS | WA3717830 | Unit 2, B Wing, PA system cant be heard | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-20 13:30:00 | Fail | Microphone replaced and new XLR 3 pin connector soldered on. Test ok.
MSA-DCS | WA3717833 | Gate Control- Cell Call hand set has a fault hard to hear | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 12:00:00 | Pass | Replaced the cell call handset with new CG-OH, tested ok and back to normal operations. Job completed.
MSA-DCS | WA3717837 | Unit 2, A Wing, Cell 17- Cell call going straight to gate control | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 10:30:00 | Pass | Rectified and fixed the cell call 17 , tested working ok. Job completed
MSA-DCS | WA3717842 | Unit 1, Cell B20 - Broken cell window | Bandyup Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 09:30:08 | 2020-10-19 15:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3717877 | control room camera server criticle and pre record reduced | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Oct 2020 | 2020-10-19 13:48:53 | 2020-10-19 15:45:00 | Fail | EBI showing HAKACAM1 CCTV with a low storage space error. Checked all cameras assigned to HAKACAM1. Removed footage more than 60 days old. Assigned cameras to different recording units to spread the footage more evenly.
MSA-DCS | WA3717886 | L4 conference room blind fallen down from the window | East Perth | WSM-BR-SITE | Building | Windows (BU) | Schlager Construction Group | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-11-20 11:00:00 | Fail | Attended site and picked up blind that was damaged.Re glued blind off site Re attended site and installed blind to window
MSA-DCS | WA3717895 | Unit 4A, Cell 11- bed light not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 16:00:00 | Pass | Replaced faulty bed light with led light
MSA-DCS | WA3717935 | Unit 3, Cell D4 -Window spring has come out | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 11:30:00 | Pass | RE NEWED SPIRAL BALANCES
MSA-DCS | WA3717945 | Bakery- 4x workshop roof light globes not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-11-03 10:00:00 | Fail | Repaired faulty lights in bakery using scissor lift
MSA-DCS | WA3717949 | UNit 6, A & C- Oven fan is not working | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 08:50:00 | Pass | Found that the fault is in the extraction fan and not the oven.
MSA-DCS | WA3717977 | Hard Drive in the Crypt has crashed. Hard Drive is the clock sync drive for the prison | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-31 11:17:00 | Fail | Installed replacement hard drive, intalled software and configured. Tested OKJob Complete
MSA-DCS | WA3717993 | ground ladies toilet cente toilet cistern is taking an extremely long time to fill up. | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 14:20:00 | Pass | Complete
MSA-DCS | WA3718012 | Amenities - no hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-28 12:00:00 | Fail | NOTE: further investigations found that the circulating pumps also tripping power, job requires a braff in order to replace both pumps
MSA-DCS | WA3718031 | Salon - External burst water pipe | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 11:20:40 | 2020-10-19 15:40:00 | Pass | COMPLETED
MSA-DCS | WA3718047 | interview room swipe card reader lock not working keeps shorting - see notes | Mandurah | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 0 | CLOSE | 19 Oct 2020 | 2020-10-19 15:25:46 | 2020-10-20 15:30:00 | Fail | Order received as a P0 BullAnt to coordinate with another trade and organise replacement stock. Calls made to SEME technician to confirm what we needed, photos sent from on site contact to confirm door hardware. Scope of works confirmed and stock ordered. BullAnt technician collected stock same day as order, for site visit to be completed the following day.Attend site the following day with available stock at appointment made by BullAnt with the site and SEME technician. Locksmith gained entry through damaged lock, installed new lock and ensured all locksmith scope was working correctly.
MSA-DCS | WA3718052 | Visits centre camera PTZ 4 not operating | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 08:30:00 | Pass | 22/10/2020 06:30. Power reset the camera to obtain its address (Pelco P Add 2) and connected handheld CCTV Tester. Confirmed was able to operate PTZ functions using tester. Checked programming of Indigo system. Loaded and saved the data and reconnected data feed to Indigo. PTZ functions now operating correctly from Visits Indigo Workstation.
MSA-DCS | WA3718056 | Unit 2, Cell 5.18- Cell call needs resecuring and intermittment function | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 16:00:00 | Pass | Attended site and removed and re-secured cell call with new rivets, all drilled and secured ok. Job complete
MSA-DCS | WA3718058 | Karakin, A wing (near ping pong table)- smashed sash window approx 600x350mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-12-10 12:30:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA3718067 | Jasper, Cell B01- Shower & basin not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-23 09:00:00 | Fail | Replaced custodian control smart box in jasper b1 and reset it.
MSA-DCS | WA3718070 | Kitchen - Billi hot water unit - orange light flashing | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 16:15:00 | Pass | Service required and done. Replaced filter and also replaced inlet solenoid dual solenoid and cold solenoid A40189280L Billi System
MSA-DCS | WA3718071 | Abattior - Hinges on freezer 4 door rusted and broken off | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-11-20 12:00:00 | Fail | make temporary repairs to keep door working.order parts ,return with replacement parts . install and test door hinges and latch , all operational.
MSA-DCS | WA3718075 | Market Grounds- 40mm to 25mm line cracked /leaking | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-23 09:30:00 | Pass | located broken pipe and fixed
MSA-DCS | WA3718080 | Unit 2, electrical room- RCD wont reset | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 11:55:15 | 2020-10-20 13:30:00 | Fail | Had to wait for escort, Located fault on rcd tripping, hot water system with blown element in plant room,Parts required, isolated and will return later date with parts. Pick up parts and replace hot water element, tested all working will take 30-40 mins to heat up
MSA-DCS | WA3718087 | Unit 1, Cell D9- Bunk bed light Switch broken | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 14:30:00 | Pass | Replaced faulty broken switch and switch plate in cell D9 unit 1 Had to wait for prisoners to go on rec before entering cells.
MSA-DCS | WA3718094 | Education, Demountable Office- Tap in the toilets does not turn itself off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 12:30:00 | Pass | Nill
MSA-DCS | WA3718103 | Kitchen, Office- Air con not running | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 12:13:29 | 2020-10-21 08:45:00 | Fail | Replaced isolator, ran up unit. All ok.
MSA-DCS | WA3718106 | Kitchen, Coms Room- Air con not running | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 12:17:10 | 2020-10-21 10:00:00 | Fail | Replaced isolator, ran up unit, all ok.
MSA-DCS | WA3718108 | Unit 1, Cell D14- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-11-19 12:30:00 | Fail | Removed broken floor tiles and replaced.Removed silicone and resealed.
MSA-DCS | WA3718115 | Main gatehouse UPS in fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | UPS System Maintenance (EL) | Sapio Pty Ltd | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-19 15:00:00 | Pass | Work performed by 3rd party contractor 19/10/2020:The techs have isolated the faulty string of batteries. There are 42 x 200Ah front terminal blocs on this string. Theyvaried in impedance between 6 and 20mOhms and voltage from 12.5 to 13Vdc. For comparison the other string was allaround 13.5Vdc and 6mOhm. The UPS is functioning correctly. These batteries have Powershield battery monitoring.
MSA-DCS | WA3718119 | Vegetable Prep- coolroom door frame has come away from panels | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-23 15:30:00 | Pass | Resecured and re shaped panels for cool room. All ok
MSA-DCS | WA3718196 | gate house cell call system coming up with network error node 1 transmit failure | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 13:28:27 | 2020-10-19 16:30:00 | Pass | checked unit 1 cell call, restarted 3210. tested to gatehouse all ok
MSA-DCS | WA3718220 | Amenities male changeroom no hot water electrical circuit problem - see note | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 09:30:00 | Pass | Investigated faulty hot water circuits, found and tagged out faulty circulation pump. Advised maintenance
MSA-DCS | WA3718221 | east side of prison Pump always on/running when controllers switch off - see notes | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 13:57:36 | 2020-11-04 10:30:00 | Fail | REPLACED DAMAGED RELAYS IN CONTROL CABINET
MSA-DCS | WA3718223 | Investigate damage in Driscoll Drive | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-19 18:30:00 | Pass | replaced 2 x water meters and neccesary pipework.
MSA-DCS | WA3718226 | Unit 7 F wing Toilets & sinks to these cells are not draining - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 14:03:35 | 2020-10-19 17:20:00 | Pass | Drain machine used up the main line removing what looked to be a phone with other bottles apple cores etc
MSA-DCS | WA3718232 | Aircon in main part of library doesn't appear to be on | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-19 15:15:00 | Pass | Checked over main area found it is fed by heating/ventilation ahu,no aircond to main area,turned on ahu and instructed operation of system.
MSA-DCS | WA3718236 | Unit 13, Room C14 - Vesda Fault, can not reset. Extra notes below | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 14:10:21 | 2020-10-20 08:48:00 | Pass | BG 20/10/20Unit 13 Cell C14 showing activated alarm. Isolated at SIP by prison staff. Vesda alarm cleared and all pipes normal at time of arrival.Performed local reset and removed isolation.Whilst on site, found Cell A16 causing urgent low airflow. Cleaned pipe and sample point. Flow returned to 100%.
MSA-DCS | WA3718237 | Unit 8 D wing servery Water cooler is leaking from bottom of tap, at mouth bladder area | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 14:09:05 | 2020-10-21 09:00:00 | Fail | Removed cartridge, cleaned and re lubed I ring. Tightened locking not. Checked intervals. All working ok how ever unit internal on bad rusty condition.
MSA-DCS | WA3718258 | Administration - air con not working (tripping) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-23 10:00:00 | Fail | Disconnected compressor and switch from system, stage 1 running and unit no longer tripping.
MSA-DCS | WA3718977 | In Unit 10 and Zone Control 2- Fire alarm is going on -Cant reset it | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 19 Oct 2020 | 2020-10-19 22:35:38 | 2020-10-19 19:45:00 | Pass | Reset system
MSA-DCS | WA3718984 | No power to the complete Unit 10 | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 19 Oct 2020 | 2020-10-20 19:08:47 | 2020-10-19 22:30:00 | Pass | Investigate and repair power to unit 10 cells
MSA-DFES | WA3717971 | north end of building latch screw missing from door will not allow door to auto close | DFES Regional Office - Belmont | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-20 12:00:00 | Pass | fixed lock on exit door and replace screw
MSA-DFES | WA3718092 | Engine room ground door knob controller spinning on itself | Kensington (old) | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 09:15:00 | Pass | Fault Found: Attended site as per work request and found push button loose causing button to spin pulling wire out Work Completed: Tightened push buttonRe wired push button Tested okPFM Door Barcode A40352245E
MSA-DFES | WA3718121 | ground rear yard - hydrent issues - please see notes | CFRS Welshpool | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 09:00:00 | Pass | Attend site and rectify hydrant
MSA-DFES | WA3718186 | appliance room sth east corner vehicle maintenance ladder bracket loose from wall | CFRS Armadale | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 14:15:00 | Pass | Refixed ladder bracket to the wall with larger fixings. Bracket now secure
MSA-DFES | WA3718306 | Grounds- Electrical board issue for the reticulation system | DFES Regional Office - Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 16:00:00 | Pass | CompleteAttended site and found no power to the Retic and bore pun in sim em basement. Found main switch to be turned off due to other electricians doing working that week. Reset and tested all in working order.
MSA-DFES | WA3722995 | **Retrospective work order ** Z33 Reed Switch store entry, External check | DFES Regional Office - Belmont | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 16:25:00 | Pass | EXTERNAL CHECK SHOWS ALL APPEARS SECURE AND CORRECT ON SITE AT STORES, NO CAUSE FOUND, NO PERSON SHOULD VISIBLY ACCESSIBLE ON SITE, CLEARED GRAHAME.
MSA-DTAG | WA3717793 | Registry/Special Witness waiting room- Emergency exit signs have fallen off the wall,needs reaffixed | Perth Children's Court | GMP-BR-HO | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-20 08:30:00 | Pass | Attended site and signed in. Spoke with staff regarding exit signs. Found emergency evacuations signs repetitively falling down. Screwed fixings to hold signs to walls. All okay. Signed out. Job complete
MSA-DTAG | WA3717898 | L3 public toilet Female toilet close to court 37 in public area has continuous running water | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-12-15 15:00:00 | Fail | Complete
MSA-DTAG | WA3717987 | server 2A Check Vesda pipes in server room for any blockages after nitrogen blow through | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 13:30:00 | Pass | Investigated VESDA on level 2A after nitrogen blowout - system all ok
MSA-DTAG | WA3718126 | Rear carpark Stormwater pipe cleaned & outfall pipe inspected/jetted | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2021-01-05 12:30:00 | Fail | jetted drain beyond boundary
MSA-DTAG | WA3718136 | DMJC and SAT as unable to lock or unlock doors remotely through unison | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 19 Oct 2020 | 2020-10-19 16:38:10 | 2020-10-19 15:30:00 | Pass | Attended site as unable to lock or unlock doors from Level 10 Unison Server. Restarted servers, checked all Floors, all OK.Job completed
MSA-DTAG | WA3718151 | 1903 & 1987- External light sensor timer needs to be reset due to power outage | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 10:00:00 | Pass | Reset times to external lighting and tested
MSA-DTWD | WA3717598 | S block L1 S102 block female toilet | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Oct 2020 | 2020-10-19 17:00:00 | 2020-10-19 10:30:00 | Pass | unblocked toilet
MSA-DTWD | WA3717702 | M block recycle water plant not working | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-06 16:15:00 | Fail | Replaced faulty pressure switch
MSA-DTWD | WA3717727 | O block sectional gararge door not working | Balga Campus | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-23 11:27:00 | Fail | Door has many motor faults and requires new motor , door is a sectional door 3450x2400 . Door is operating intermittently. Braf to be raised.Returned to site, remove old motor and replace with new. Job is complete and door tested working correctly
MSA-DTWD | WA3717764 | B block auto door not working | Balga Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-19 10:42:00 | Pass | Found that the doors were switched off, switched the doors back on, serviced and tested, all ok.Asset barcode number A40437127H
MSA-DTWD | WA3717766 | P019 faulty emergency stop button for isolating electrics | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 08:30:00 | Pass | Inspected e stops in classroom.all wokeimg fine.job completed
MSA-DTWD | WA3717845 | Tower block needs whiteboards & frames re-hung after painting | West One Services | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 19 Oct 2020 | 2020-10-26 17:00:00 | 2020-11-03 15:45:00 | Fail | Attend site after painters and hang Whiteboards & frames
MSA-DTWD | WA3718018 | Tower - alarm system keeps going into fault- Zone 85 smoke alarm | West One Services | GMP-BR | Security | Monitoring (SE) | Casa Security Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-19 15:35:00 | Pass | ATTENDED SITE AND PROGRAMMED OUT ZONE 85 FOR NOW.ZONE 85 IS A THERMOSTAT AND THE AIRCON IN THAT ROOM ISNT WORKING AT THE MOMENT.KIM WILL LET US KNOW WHEN ITS SORTED AND WE CAN PROGRAM IT BACK IN.STILL WAITING ON KIM TO ADVISE WHEN WE CAN RETURN
MSA-DTWD | WA3718062 | Block O, Room O005 - Air Con is faulty | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-27 16:00:00 | Fail | Attended site signed in and set up work front upon inspection and testing could not find breaker to isolate had to set up barricading and put on harness to access roof, isolated and locked out, removed covers to fan coil, tried disconnecting secondary wires from p1 and p2 control points but this resulted in no display to the units remote but unit still ran when tested, controller is showing master slave symbol which is not allowing temp to be adjusted below 28c, speaking with Dan we do not have access to the bms, Dave Jennings has been dealing with this issue previously, is on going, re fitted all covers and packed up work front
MSA-DTWD | WA3718082 | Eastern side of U017 - Faulty bin lifter | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 15:00:00 | Pass | Attend site and inspect bin lifter - provide BRAF for replacement, please note there are x 2 damaged on site
MSA-DTWD | WA3718165 | P Block, Machine room - GPO faulty | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 09:11:00 | Pass | Replaced faulty gpo.job completed
MSA-DTWD | WA3718289 | B Block, Room B2427- Sparks coming from ceiling fan | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-20 11:30:00 | Pass | Attended site and signed in. Located B block. Found room 2427 in use. Spoke with lecturer and was happy with us to proceed with works. Investigated to find no power to fans. Reset fan circuit R10 in switchboard. Tested all fans on low. Tested on high and fault appeared. Middle of room fan has high fault. Investigated internals to find not repairable. Removed old fan. Supply and replace with new 3 blade fan. Replaced 2 x tubes and starters to flickering light in classroom also. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3718293 | Campus Grounds- Loose branch hanging from tree opposite F Block maintenance area | Bentley Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-11-04 08:00:00 | Fail | variation order issued.tree not healthy.
MSA-DTWD | WA3718329 | K Blcok, Room K02- broken exhaust fan switch in the canteen kitchen | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-20 14:02:00 | Pass | Attended site,signed in , spoke with fm about about job , located switch in canteen area , switch was machine labelled, went back to liaise with fm and told him I could either special order one in or use the label maker on a standard switch , fm said he was happy with the label maker option , had to wait to isolate exhaust fan as staff were operating fryers , isolated circuit , removed old switch plate , fitted new one , labelled switch plate same as old switch plate was labelled (also put on old programmed barcode ) , re energised circuit, tested switch and operating as intended , cleaned up work area , completed paperwork, signed out ***job complete ***
MSA-DTWD | WA3718343 | F Block, F105 - right hand entry door to F Block Midland Campus is jamming badly | Midland Campus | GMP-BR | Glazing | Door Glass (GL) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 15:15:00 | Pass | ATTENDED SITEADJUSTED TOP & BOTTOM PIVOTS TO DOOR & TIGHTENED SCREWS.CUT DOWN BOTTOM SECTION TO STOP SCRAPING ON GROUND.JOB COMPLETE
MSA-DTWD | WA3718355 | E Block, Deli - Fridge door seal has broken | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 2 | CLOSE | 19 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-30 09:00:00 | Fail | Picked up required part,attended site, signed in located and isolated system in e block, removed and replaced door seal with new, tested system and left operational
MSA-MRWA | WA3718338 | Control cable broken please remediate | Road Network Operation Centre (RNOC)-Main Building-Second Floor-Real Time Traffic Operations | GMP-BR | Electrical | General Electrical (EL) | SCHIAVELLO SYSTEMS (WA) PTY LTD | 1 | CLOSE | 19 Oct 2020 | 2020-10-20 17:00:00 | 2020-10-21 14:30:00 | Fail | Repairs to cable
MSA-DCA | WA3719199 | floor waste blocked | Perth Concert Hall-Main Building-Ground Floor-Plant Office | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 14:00:00 | Pass | Clear blockage to floor waste
MSA-DCA | WA3719358 | Damaged sprinklers on Zones 11, 12 & 13 | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Landscaping & Gardening | Materials (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-20 17:50:00 | Pass | job completed - High water flow alerts caused by multiple breaks in sprinklers so four were replaced
MSA-DCA | WA3719510 | Leaking air con unit | King Street Arts Centre-Main Building-Ground Floor-Shop 5 - One Off (shoe shop) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-21 10:00:00 | Pass | Attended site signed in, waited for tennant to arrive,ivestigated water leak from wall split,found condensate pump internals to be dirty causing pump to not activate and overflow, cleaned pump and internals tested and left operational.
MSA-DCS | WA3719169 | Unit 6 - A9 Window runner broken. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 20 Oct 2020 | 2020-10-26 17:00:00 | 2020-11-02 14:15:00 | Fail | WINDOW BALANCES RENEWED & HANDLE RE FIXED
MSA-DCS | WA3719174 | kitchen 3 tier pizza oven not getting up to temp | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 07:39:23 | 2020-12-01 22:30:00 | Fail | 20/10/20Arrived at site liaise with reception, tool list, walk to kitchen, identify oven, isolate remove panels, test/fault find diagnose and found 1 faulty energy regulator, removed replaced regulator, reassemble all components and test all components for correct function all okay but I had a chat with the head chef about what was happening and from my understanding they didn't know how to use the energy regulators and were trying to heat up on the lower settings and wasn't cooking fast enough for them, have told them if they want it to heat up faster, is to put the energy regulators on setting 3 to achieve the higher heat then to lower the settings where required with a little trial and error. Tested the thermostat on all 3 decks over and over again the top deck is a little slower than the others but still tested okay at the time of testing, if fault still exists after they've adjusted the way they cook, maybe replacing the thermostats.01/12/20Arrive at site to check oven not
MSA-DCS | WA3719205 | Unit 6 B4 Toilet not functioning correctly needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:00:56 | 2020-10-20 17:58:00 | Pass | Replaced cisterna dn adjusted pipework to suit new cistern
MSA-DCS | WA3719207 | Unit 6 N wing showers running & leaking needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:03:32 | 2020-10-21 16:05:00 | Fail | Rewashed taps
MSA-DCS | WA3719219 | B wing day room smashed window | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:09:14 | 2020-10-20 13:15:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3719231 | control internal perimeter zone 8 internal MF A and B no activation | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Oct 2020 | 2020-10-20 12:15:49 | 2020-10-20 13:30:00 | Fail | Travelled to site and tested microfonics zone 8 with test device, all tested ok locally and working ok, unable to activate alarm back to control room. Reset controller and re-calibrated zone sensitivity with test device and retested , all tested ok, added cable ties to section of zone and all tested ok. Job complete
MSA-DCS | WA3719232 | Unit 10 C and D wing Power outlet behind C&D Wing Regi area is cracked needs repair | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:15:03 | 2020-10-20 10:00:00 | Pass | Investigate and replace unit 10 c & d kitchen gpo
MSA-DCS | WA3719234 | Unit 6 N12 Cell light faulty turns off after 20/30 seconds needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:21:05 | 2020-10-20 11:30:00 | Pass | Investigate and repair unit 6 cell N12 cell light
MSA-DCS | WA3719241 | Unit 9 D1 Cell call not registering on panel needs repair | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:23:18 | 2020-10-20 15:45:00 | Pass | Attended site and tested cell call, cell call faulty, replaced with 1 x new cell call from site spares cabinet and re-tested, all tested ok. Job complete
MSA-DCS | WA3719279 | unit 1 cell B 22 light fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-21 08:30:00 | Pass | Investigate and replace unit 1 cell B22 light fitting
MSA-DCS | WA3719302 | unit 6 control room Hot water urn not working needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 08:56:34 | 2020-10-21 11:00:00 | Fail | Replaced broken tap
MSA-DCS | WA3719339 | Clean-up of Unit 1 post incident | Casuarina Prison | WSM-BR-RC | Cleaning | Emergency Cleans (CL) | DUNBAR SERVICES (WA) PTY LTD | 0 | CLOSE | 20 Oct 2020 | 2020-10-20 13:16:09 | 2020-10-23 15:30:00 | Fail | Clean up post incident
MSA-DCS | WA3719359 | Unit 3 - B12 Cell B12 hatch frame broken off (the bottom piece).-see note | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 10:15:00 | Pass | HATCH REPAIRED
MSA-DCS | WA3719435 | Unit 4, Cell B7- exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-21 15:00:00 | Pass | Investigate and replace unit 4 cell b7 exhaust fan
MSA-DCS | WA3719439 | Unit 3, C Wing - Rangehood lights faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-21 13:00:00 | Pass | Investigate and replace unit 3 c wing range hood lights
MSA-DCS | WA3719441 | Unit 2 top landing blocked toilet | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-23 15:00:00 | Pass | COMPLETED
MSA-DCS | WA3719516 | detainee south sallyport gate of admissions stopped working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 20 Oct 2020 | 2020-10-20 15:07:13 | 2020-10-20 23:30:00 | Fail | 20/10/20Inspect gates.Faulty control board.Replace control board.
MSA-DCS | WA3719597 | Unit 5, B Wing, Shower window spring is faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 14:00:00 | Pass | SPIRAL BALANCES RE NEWED AND FRAME REPAIRED
MSA-DCS | WA3719603 | Unit 7, Cell D3- Shower tap not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 08:30:00 | Pass | Nill
MSA-DCS | WA3719656 | Kitchen, prover not heating | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-20 13:00:00 | Pass | Kitchen, prover not heating, no steam. Check water elements & controls, found element breaker off. Reset power run cycle on Humidity, good steam. Report to staff.
MSA-DCS | WA3719657 | unit 1 cameral 27 and 34 both camera's not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 12:43:19 | 2020-10-20 16:00:00 | Pass | Attended site, identified multiple camera and repaired network faults.Corrected faults and confirmed correct operation.Monitored and tested OK.Job Complete
MSA-DCS | WA3719743 | Jeelia A2 main light switch is sticking see notes | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-21 08:30:00 | Pass | Check all light switches and power points for sticking, all seem to be OK
MSA-DCS | WA3719751 | Jeelia A wing aircon not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-12-22 14:15:00 | Fail | Replaced motor, motor pully, belt, cntrolbix and wall controller.
MSA-DCS | WA3719753 | Jeelia, Cell A1- Main light not working, see further notes below | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-22 09:00:00 | Pass | Jeelia A-1 replaced blown tubes and starters and ballast in main bedroom light.
MSA-DCS | WA3719772 | Reset Centre - footpath between Reset Centre and the front gate has sunk | Casuarina Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | Midolo Building Services | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2021-01-05 14:30:00 | Fail | CONCRETE PATH GRINDED IN VARIOUS SPOTS TO LEVEL OUT.
MSA-DCS | WA3719775 | Unit 1, Cell C16- Viewing window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-29 14:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3719778 | kitchen middle blast chiller probe bent not reading correct temp. | Casuarina Prison | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-16 09:00:00 | Fail | Arrived on site and signed in, isolated power and removed faulty probe,fitted new probe,turned back on and tested all running ok at present.
MSA-DCS | WA3719779 | Unit 5, Cell B8- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 10:00:00 | Pass | Repaired light
MSA-DCS | WA3719781 | Unit 2, Senior Officers Office - GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 10:00:00 | Pass | Replaced gpo
MSA-DCS | WA3719784 | Health Admin- Air Con not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 13:45:00 | Pass | Found 2x compressors triped on multiple Actron air units. Reset and ran up both. All ok. Also found 1 actron air unit manually switched off from computer. All ok
MSA-DCS | WA3719786 | Education 1 admin air con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-23 08:30:00 | Pass | Complete
MSA-DCS | WA3719791 | Mechanics workshop - various lights faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-10 13:00:00 | Fail | Replaced 5x hibay lights in mechanics shop
MSA-DCS | WA3719996 | Indigo keyboard is not responding to the security system. | Roebourne Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Oct 2020 | 2020-10-21 04:41:24 | 2020-10-21 10:00:00 | Fail | Contacted site and had site reset keyboard from HDMI extender. Retested and all tested and working ok. Job complete
MSA-DFES | WA3719486 | gym rear security screen has become dislodge | VFRS Mandurah | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-21 11:15:00 | Pass | Re-fitted screen with screws to prevent it coming off again
MSA-DFES | WA3719926 | G Level, Dorm 7- Toilet seat is broken (seat has craccked all the way through) | CFRS Perth | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 14:03:00 | Pass | Fit new seat
MSA-DTAG | WA3719613 | Cathedral airkey - Duress is faulty , see below notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 20 Oct 2020 | 2020-10-20 16:02:02 | 2020-10-20 15:00:00 | Pass | Attended site, airkeys duress not sowing on Level 10. Airkey reader locked on program, restored airkey readers, programmed cameras to show on video wall.Job completed.
MSA-DTWD | WA3719345 | E block ground SK 1,2,3 blown lights in E71, E72 range hoods, E64 cool room light, ceiling lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-23 08:26:00 | Pass | Replace 8x tubes and starters 1x led batten and 12x cfls
MSA-DTWD | WA3719349 | B737 aircraft 3 phase portable air con is faulty | Jandakot Campus - Hangar | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 17:00:00 | 2020-12-02 15:00:00 | Fail | Picked up parts required, arrived on site signed in. Checked in with reception, gained access keys. Gathered tools and equipment started and removed Evaporative motor assisted by Dave installed new. Cleaned condenser coil, repaired insulation in Evaporative chamber. Repairs to unit for drain water flow, air ballanced system. Cleaned up and signed out. Dave removed waist and disposed.
MSA-DTWD | WA3719364 | Unit 9 ground Lift intermittently going into “Out of Order” mode | Thornlie Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 20 Oct 2020 | 2020-10-21 17:00:00 | 2020-10-20 12:45:00 | Pass | DOORS/ENTRANCES - CLOSER WEIGHT/SPIRATOR - COMPONENT OUT OF ADJUSTMENT
MSA-DTWD | WA3719409 | E block ground E772 the door closer mechanism does not keep the door open anymore. | Joondalup Kendrew Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 16:00:00 | Pass | Work completed
MSA-DTWD | WA3719445 | E Block, E72, SK2 tagged out oven, 3rd oven from left, not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-23 10:30:00 | Pass | COMPLETED
MSA-DTWD | WA3719471 | J Block 004 cracked timber decking at top of stairs | Balga Campus | GMP-BR | Carpentry | Timber (all types) (CA) | M Construction (WA) | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2021-02-08 08:40:00 | Fail | Job complete
MSA-DTWD | WA3719512 | Level 1, D Block - Aircon to D108 and D109 not working | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 12:30:00 | Pass | Rooms d108 and d108 accessed. test operation run shows no communication or power to indoor unit. Circuit break ok.Indoor unit shows blown inline fuses on both ac 1 and ac4. Replaced and test ran. Unit operation now operable by wall controller. Units tested on heat and cool. Operations now as needed
MSA-DTWD | WA3719590 | D Block, Room D109- Speaker coming out of wall | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 20 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-22 15:45:00 | Pass | Attended site and signed in. Located D block and found class 109. Investigated speaker hanging from wall. Moved desk in corner to get access with ladder. Dismantled speaker bracket. Re drilled and used larger wall plugs and screws to the bracket. Refixed to wall. Assembled speaker back to bracket. Replaced desk back into corner. Tested all okay. Signed out job complete
MSA-DTWD | WA3719617 | A Block, Room A140 Vent has fallen out of ceiling | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 16:35:00 | Pass | Accessed room and inspected fallen vent.Vent has removable section from frame which has come down. Factory design brackets, clips are all straight and not bent or dislodged. Frame also not showing any damage or unordinary assembly.Removed brackets and clips and proceeded to solidly attatch vent to frame by screwing two parts together.Tested for no movement. Solid.
MSA-DTWD | WA3719856 | Staff Room B16 - Zippy Hot water unit | Murdoch Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 12:00:00 | Pass | descaled and cleaned level sensor Rheem BWU A40190457J
MSA-DTWD | WA3719867 | D Block Staff Room- Zippy Hot water unit | Murdoch Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 12:35:00 | Pass | Replaced tap repairs to Rheem A401301509 Replaced Rheem Tap Assy
MSA-DTWD | WA3719967 | A Block, AT4A Male toilets- 1st cubicle toilet waste pipe leaking | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 15:04:00 | Pass | Replaced pan cone rubber
MSA-DTWD | WA3719971 | A Block, AAT9 Classroom- DGPO on skirting duct is broken | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 20 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-26 10:35:00 | Fail | Attended site and signed in. Got keys from facilities .Spoke with staff about jobs. Inspected fan in classroom to not be working correctly. Ran through it’s operation and found to be controlled on air con. Showed staff. Checked out data points in ET01 and found needs new plate and mechs installed. No parts on site need to order in. Found broken gpo in hallway controlling the water chiller. Supply and replaced with new double Checked out gpo in AT09 and found class in use and not out till 430pm and site advised us to return at another date next week. To be confirmed with site prior to attendance. Job not complete Attended site and signed in. Located classroom with broken data point. Replaced plates and mechs as required. Located class reported with broken gpo. Checked and tested all outlets and could not find broken outlet. Spoke with facilities and awaited them to check room out. Apparent wrong room. Awaited site find correct room. FT09 was room. Found broken gpo. Disconnect and remo
MSA-DCA | WA3720351 | blocked urinal and toilet | King Street Arts Centre-Main Building-Ground Floor-Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 09:25:00 | Pass | Cleared blocked toilet (1st left cubicle )and urinal to ground floor male toilet.Used drain cleaner to help clear blockage to urinal.
MSA-DCS | WA3720127 | Recovery west office Air Con Not Working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 07:00:25 | 2020-11-06 14:43:00 | Fail | Leak check and repair complete
MSA-DCS | WA3720134 | Western Courts Adjacent to Industries Cabinet Shop Drain overflowing grey water onto courts | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-26 15:28:00 | Fail | Removed tennis’s balls coke cans tuna cans and rubbish then installed new floor grate
MSA-DCS | WA3720135 | Unit 2 B wing day room gpo broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-21 11:00:00 | Pass | Replaced gpo
MSA-DCS | WA3720154 | kitchen door lock on rational oven is broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 07:28:17 | 2020-10-22 15:30:00 | Fail | Repaired door catch but adjust so it properly lines up with door lock. Test doorseal tightness ok. Left unit operational.
MSA-DCS | WA3720162 | Unit 3 - D4 leaking tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-29 10:30:00 | Fail | Nill
MSA-DCS | WA3720168 | Unit 3 A/C wing freezer is not freezing | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-23 11:15:00 | Pass | Duplicate job, closing.Report on job WA3721202
MSA-DCS | WA3720176 | Unit 14 - B13 Striker plate for personal lock is missing needs replacing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-02 14:00:00 | Fail | Require parts.replace missing strike plate with new oversize strike plate and replace mortise lock.
MSA-DCS | WA3720208 | Unit 8, Front entry door, electronic lock sticks out approx 3mm. beyond frame sometimes not allowing | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 08:03:02 | 2020-10-21 10:30:00 | Pass | Attended site. Adjusted mortice lock and electronic strike to restore normal function.
MSA-DCS | WA3720226 | main kitchen switch on hot box is broken | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 08:17:58 | 2020-10-21 14:55:00 | Pass | Replaced broken switch
MSA-DCS | WA3720241 | gate house front door No1 is not latching | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 08:33:01 | 2020-10-21 15:30:00 | Pass | Service lock, re install door stop, replace electric strike, mounting tabs and adjust door closer.
MSA-DCS | WA3720258 | Unit 9 A/B day room hot water system tripping out | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-11 09:00:00 | Fail | Disconnect and reconnected urn
MSA-DCS | WA3720288 | Unit 14, Cell C11- Sink blocked, tried unblocking it with the plunger and not sucessful. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-22 12:30:00 | Pass | Nill
MSA-DCS | WA3720290 | Unit 7, A Wing- Leaking tap at the round sink in the kitchen | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-29 12:30:00 | Fail | Nill
MSA-DCS | WA3720310 | Medical Centre- Floor underneath nurse’s desk in treatment room admin, ripped/torn | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-12-09 10:00:00 | Fail | INSTALL NEW VINYL FLOORING TO 5X AREAS
MSA-DCS | WA3720334 | Unit 6, Gate latch on the personal gate will not always release when activated from control room | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-21 11:45:00 | Pass | Attended site and checked personal gate in unit 6. All tested ok multiple times. Disconnected push button and tested contacts for correct operation and continuity and all tested working ok. No further issues found, staff are aware that gate is functioning correctly. Job complete
MSA-DCS | WA3720336 | PRU - perimeter fencing continually alarming F2 external & G1 external | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-21 13:00:00 | Pass | Rectified and fixed constant alarm on F2 MW and G1 MX, job completed.
MSA-DCS | WA3720337 | Unit 7 - A Wing cell 9 door has dropped | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-28 14:00:00 | Pass | Replace worn hinges
MSA-DCS | WA3720339 | Keywatcher 116 fault | West Kimberley Regional Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-23 09:38:00 | Pass | Reprogrammed key into new slot
MSA-DCS | WA3720340 | Keywatcher 128 fault | West Kimberley Regional Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-23 09:40:00 | Pass | Reprogrammed key
MSA-DCS | WA3720342 | Keywatcher 148 fault | West Kimberley Regional Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-23 09:41:00 | Pass | Reprogrammed key
MSA-DCS | WA3720349 | Unit 1 House 7 Cell 1 RS tampered | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-22 14:18:00 | Pass | Replaced 1x 19mm Door insert reed switch from PFM stock
MSA-DCS | WA3720350 | Unit 1 House 7 Cell 2 RS damaged and jammed in door | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-29 18:38:00 | Fail | Removed reed switch jammed in door frame.Repaired door frame and replaced magnet
MSA-DCS | WA3720356 | Main Kitchen- Combi oven showing error "32-2" | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 10:11:08 | 2020-10-21 16:35:00 | Pass | Replaced top & lower ignition modules after verbal approval from Mario on 21/10
MSA-DCS | WA3720374 | Horn speakers not working in below locations | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 10:28:25 | 2020-11-17 12:00:00 | Fail | Replaced four horn speakers C2053. Tested all ok after replacement.
MSA-DCS | WA3720379 | Unit 1, Cell B2- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-10 08:30:00 | Fail | Removed broken floor tiles and replaced.Removed silicone and revealed.
MSA-DCS | WA3720384 | Unit 1, Cell B3- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-19 11:00:00 | Fail | Removed broken floor tiles and replaced.Removed silicone and resealed.
MSA-DCS | WA3720386 | Unit 1, Cell B4- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-10 09:30:00 | Fail | no charges - closed off compfin
MSA-DCS | WA3720389 | Unit 1, Cell B5- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-10 10:30:00 | Fail | Removed broken floor tiles and replaced.Removed silicone and resealed
MSA-DCS | WA3720391 | Unit 1, Cell B6- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-12-04 09:30:00 | Fail | Replaced damaged floor tiles and resealed.
MSA-DCS | WA3720392 | Unit 1, Cell B7- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-12-04 11:30:00 | Fail | Replaced damaged floor tiles in shower recess and resealed.
MSA-DCS | WA3720393 | Unit 3 - B Wing Fluro light not working, tombstones are broken. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-22 13:30:00 | Pass | Repaired damaged lights in B/D wings unit 3
MSA-DCS | WA3720394 | Unit 1, Cell B8- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-12-04 13:30:00 | Fail | Replaced damaged floor tiles in shower recess and resealed.
MSA-DCS | WA3720396 | Unit 1, Cell B9- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-12-04 15:30:00 | Fail | Replaced damaged floor tiles in shower recess and resealed.
MSA-DCS | WA3720404 | Unit 4, Cell B13- Toilet only flushing for a few seconds & not filling up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 09:30:00 | Pass | Nill
MSA-DCS | WA3720421 | Unit 4, Cell B1- Cell light is not working, bunnk light switch has been smashed | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 10:00:00 | Pass | Replaced damaged cell switch in unit 4 b1
MSA-DCS | WA3720425 | Canteen - Officers toilet light broken. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-22 11:30:00 | Pass | Repaired faulty lights in canteen toilets
MSA-DCS | WA3720469 | Indigo vision system, monitor is not working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 19:28:39 | 2020-10-22 01:00:00 | Fail | Travelled to site, checked monitor and found loose connection between monitor and VGA extender. Removed all VGA extenders one by one, and removed any redundant cabling under desk. Tidied up remaining cabling and labelled HDMI and VGA extenders. All monitors tested and working ok. Job complete, travel back to PerthFight delayed from 1740 to 22:00
MSA-DCS | WA3720475 | Prisoner reception female staff PIR constantly active - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2021-01-14 09:00:00 | Fail | Faulty PIR in constant alarm. Replaced 360 PIR and terminated. Tested operation with Control and all is in working order.
MSA-DCS | WA3720477 | Camera 125 not working on Gallagher - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-22 14:20:00 | Pass | Camera working on Indigo but not visible on Gallagher,reprogrammed camera ONVIF profile and reprogrammed Gallagher External Services .camera image on Gallagher
MSA-DCS | WA3720485 | Camera 126 not working on Gallagher - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-22 14:24:00 | Pass | Reprogrammed onvif profile and program Gallagher external services Camera now visible from Gallagher
MSA-DCS | WA3720487 | Gallagher memory fault - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-23 09:37:00 | Pass | Gallagher creating mini dump file on workstation and using large amounts of space.Reprogrammed dump file and removed excess files
MSA-DCS | WA3720491 | OT triggered alarm constant - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-23 09:43:00 | Pass | Calibrated zone 4 OT
MSA-DCS | WA3720527 | Canteen- main door lock hard to lock & close | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-12-22 15:30:00 | Fail | Awaiting Access.Replace mortise lock and adjust strike box.Remove hinges to replace, require further parts.Replace hinges made to suit frame cut out and install frame support due to frame coming away from brick work.
MSA-DCS | WA3720554 | Gatehouse control room- multiple max pro cameras not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 16:29:18 | 2020-12-16 15:50:00 | Fail | Investigated multiple maxpro cameras which are not operational.Repaired maxpro trunk communication fault between gatehouse and unit 3. Corrected subrack fault in Visits.Tested OKJob Complete
MSA-DCS | WA3720852 | unit 4 intercome outside main control room not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-29 12:00:00 | Fail | Test cable and replace due to fault. Intercom functional10m CAT6 Cable used
MSA-DCS | WA3720878 | Sewerage treatment plant has a blockage | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 14:08:35 | 2020-10-21 14:55:00 | Pass | Priority 1 call out and after hours. Watercon employee found sewage pipe was blocked, unblocked tried using a rotating drill. Needed hi pressure blower, found lots of bricks in Pipe which when shattered cleared the blockage.Watercon had to call our a Plumbing contractor for Hi pressure blower. Attended site 21/10/2020.
MSA-DCS | WA3720888 | Camera to Front Entrance of the SHU has failed- see notes below | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 14:22:23 | 2020-10-23 09:49:00 | Fail | Investigated multiple faulty cameras in the SHU. Repaired data communication faults and tested OK.Found some cameras failed again. Returned with Indigo PSU, installed and tested ok.Job Complete1 x PSU (SEME Stock)
MSA-DCS | WA3720890 | control room, faulty MW zone 12 | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 18:23:44 | 2020-11-04 15:00:00 | Fail | Attended site and replaced zone 12 inner with new Ultrawave microwave set. All replaced, installed and tested ok. Job complete
MSA-DCS | WA3720987 | Crisis Care unit lost all cameras | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 20:23:49 | 2020-10-21 18:30:00 | Pass | Attended site checked and found CCU CCTV Monitor 1&2 are not showing cameras. Located problem to be the EBI workstation not working properly. Reboot the workstation and bring all cameras back online.
MSA-DCS | WA3720996 | Keywatcher is not logging transactions | Wooroloo Prison Farm | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 16:52:22 | 2020-11-04 11:30:00 | Fail | Keywatcher Cabinet missing logs in reports. Cabinet is working fine and the transactions collections. Cabinet can only hold up to 4000 events before you collect transactions. Tested key slots and all is ok. Also changed main battery (1x 12VDC 4.5A/h). Recommend a central server with software connected and running permanently to do daily transacrion collection. Currently users are collecting transactions and none of it is on a central database.
MSA-DFES | WA3720305 | West side path of Administration Building - Flood light is damaged | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2021-01-07 15:45:00 | Fail | Replaced ground light with new
MSA-DFES | WA3720309 | front sewer pump showing fault alarm going off and controller | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 11:14:00 | Pass | Clean pump pit probe
MSA-DFES | WA3720451 | L1 west end just near utility room, window leak - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-27 14:00:00 | Fail | Patched damaged wall at the base of the window. Sanded back and painted to match existing
MSA-DTAG | WA3720221 | Basement,Custody - Electrical switchboard contactor casing is old & cracked – new contactor required | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 12:30:00 | Pass | Inspected fault and replaced old and faulty contactor
MSA-DTAG | WA3720352 | Lvl 4, Plant Room - Chiller 1 high level interface is offline - see notes below | Supreme Court | GMP-BR-HO | Refrigeration | Chiller (RE) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-06 12:00:00 | Fail | Pick up new sensor and attend site. Access plantroom and isolate chiller. Disconnect supply water sensor and remove. Disconnect return water sensor and remove. Fit existing senso back in return water pipe and connect. Install new sensor with heat paste into supply water pipe. Follow wiring for sensor and connect. Deisolate chiller and check sensors. Found new sensor to be reading correctly. Start chiller and test operation, working ok.
MSA-DTAG | WA3720417 | Light globes not working throughout the building, see location list below | Rockingham Justice Complex | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-28 11:30:00 | Pass | Replaced faulty and blown lamps to court
MSA-DTAG | WA3720494 | Lvl 5, Male Public Toilets (Hay Street end) - Toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 10:30:00 | Pass | Complete
MSA-DTAG | WA3720503 | Ground court 2 Re-attach peep hole cover | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-05 13:15:00 | Fail | new door viewer installed
MSA-DTAG | WA3720891 | Lvl 2, Court 11- Electrical circuit (blue 7) keeps tripping | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 10:00:00 | Pass | Fault found to be incorrect connections, all now in working order
MSA-DTAG | WA3720904 | basement everytime an air key is used to open Pier st boom gate duress is activated in control room | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 12:00:00 | Pass | Changed programming on Gate, checked all functions, all OK.
MSA-DTAG | WA3720964 | Floor needs repairing - holes in concrete | Rockingham Justice Complex | GMP-BR-HO | Flooring | Concrete (FL) | Midolo Building Services | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-23 10:00:00 | Pass | FLOOR REPAIRS MADE & CARPET RESECURED
MSA-DTWD | WA3720218 | M block office area air con not working room M002.1 | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-12-11 11:30:00 | Fail | Found old centralised control in unit, this is now obsolete, so bypassed it and unit ran well
MSA-DTWD | WA3720271 | Glasshouse / Nursery – Evap 2 Solenoid not letting water through need replacement.-see notes | Murdoch Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 09:30:00 | Pass | attended site Replaced solenoid for evap cooler
MSA-DTWD | WA3720327 | G Floor, Gym- drinking Water fountain that will not switch off | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-21 13:01:00 | Pass | All working okay checked Zip Fountain - could not find any fault A40139053E
MSA-DTWD | WA3720366 | A Block Courtyard male toilets are blocked & bubbling | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 14:13:08 | 2020-10-21 14:00:00 | Pass | Complete
MSA-DTWD | WA3720537 | Wash Room - Lighting not working | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 11:15:00 | Pass | Attended site and signed in, completed JSA, inspected lights not working B6 lvl 3 wash room and various other areas, found fuse blown, replaced and blew again, left site to pick up another, took down covers and tested lights, found to be hard active was touching frame causing fuse to blow. Tested. Fault rectified. **job complete**
MSA-DTWD | WA3720549 | E Block E200 unable to lock door | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 16:23:27 | 2020-10-21 13:30:00 | Pass | Service lock to E200
MSA-DTWD | WA3720552 | Hot water urn – no water | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-23 21:30:00 | Pass | Attended as booked and arranged - on arrival could not get access and was then told that the system was not located at this address but rather it is at 145 Jull Street Site so tech left and waited for correct instructions..
MSA-DTWD | WA3720819 | E block tech area Electrical, needs florescent tube lights replaced. | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-23 10:00:00 | Pass | Attended site and signed in. Met with facilities, discussed lights not working. Went to G block and found 4 x lights not working. Removed diffusers and replaced tubes and starters, re-fitted diffusers. Went to E block tech office and found 3 lights not working. Removed diffusers and replaced tubes and starters, starters perished and crumbled on removal. Re-fitted diffusers. Tested all okay. Job complete
MSA-DTWD | WA3720900 | L2 corridor west Replace blown lights along the corridor | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 15:00:00 | Pass | Repalced multiple lamps out throughout hallway.all working properly.job completed
MSA-DTWD | WA3720906 | K Block, Room K02 - Kitchen entry door is faulty | Midland Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-12-02 15:10:00 | Fail | Works complete
MSA-DTWD | WA3720941 | Offices West Level 6, Staff Room- Lights blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 13:30:00 | Pass | Replaced various lights around B1 Level 6 according to instructions provided
MSA-DTWD | WA3720981 | Campus Grounds- Security lighting not working, tripping on red 3 | Bentley Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 2 | CLOSE | 21 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 14:30:00 | Pass | Fault on R3, tripping periodically, investigated each light pole and found nearly everyone to have corrosion on the joins causing degradation in the insulation resistance. Refitted off each pole, insulation resistance tests passing and circuit is good.
MSA-DTWD | WA3722531 | C Block, Room C31- Cold water drinking unit is leaking- see notes below | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 21 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-21 16:30:00 | Pass | replaced leaking tubing and fittings on disabled fountain C BLock A404213126
MSA-MRWA | WA3720458 | Billi boiler unit leaking please inspect/remediate | Road Network Operation Centre (RNOC)-Main Building-Second Floor-Kitchen | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 21 Oct 2020 | 2020-10-22 17:00:00 | 2020-11-10 14:55:00 | Fail | Replaced font kit drain tray with fittings.
MSA-MRWA | WA3720892 | ground breezway Investigate why Main FiP does not go into evacuation and remediate | Materials Engineering Branch-Admin Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 21 Oct 2020 | 2020-10-21 18:22:28 | 2020-10-21 16:30:00 | Pass | Attended site after a evac test was performed by 3rd party and found that tones weren’t changing over from alert to evac and tones were cutting in and out. Found redback tone generator part number (A4572) faulty and will need replacement.Quote to follow to Brendan Mitchell.
MSA-DCA | WA3721160 | two broken sprinklers | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-22 17:00:00 | 2020-10-22 15:05:00 | Pass | - met with Kevin and he showed me the broken sprinklers- all three were snapped off at the nozzle I'm assuming kicked off- replaced the 2 at the urban orchard (inner lawn)- the other was replaced in the south garden bed in front of pretzel.- rested after and videos attached- signed off with Kevin
MSA-DCA | WA3721551 | Dumb waiter not operating | Perth Concert Hall-Main Building-Ground Floor-Kitchenette | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 15:16:00 | Pass | job completed - ConH-DumbwaiterDoor lock on ground floor not making electrically. Secure wiring,clean and adjust contacts. Return to service. Bruce would like door locks and car gate switched to be upgraded
MSA-DCA | WA3721944 | near admin office 3 emergency exit light has gone out | PICA-Main Building-Level 1 | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 09:00:00 | Pass | Faulty exit sign rectified.
MSA-DCA | WA5681132 | RETROSPECTIVE WORK ORDER DO NOT ATTEND-Dumb waiter not operating | Perth Concert Hall-Main Building-Ground Floor-Kitchenette | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | COMPFIN | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-26 12:38:00 | Fail | Build up ground floor door lock arm to ensure full contact electrically. Test and return to service.
MSA-DCS | WA3721151 | Western oval station 15 Main Line Break In Retic | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 07:26:16 | 2020-10-22 12:00:00 | Pass | broken valve replaced.
MSA-DCS | WA3721155 | Unit 6 - A Wing lock on door is broken unable to be opened | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 22 Oct 2020 | 2020-10-22 11:42:15 | 2020-10-22 11:00:00 | Pass | Open jammed lock, obtain new lock and install
MSA-DCS | WA3721202 | Unit 3, A & C wing - Fridge in storeroom faulty, The fridge is not freezing properly, | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-10 13:52:00 | Fail | Job signed off as quote declined.
MSA-DCS | WA3721203 | Unit 2 - A & C water leak at the back of the unit | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 08:02:32 | 2020-11-04 11:30:00 | Fail | Nill
MSA-DCS | WA3721205 | signage w/s - auto boil constantly leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-23 11:48:00 | Pass | Replaced inlet solenoid and level sensors
MSA-DCS | WA3721206 | Unit 2 - D9 cell has water leaking from pipe under the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 11:30:00 | Pass | Nill
MSA-DCS | WA3721211 | SOP, unit 12 A12 - Vertical sliding external window drops, does not hold position. possible hazard | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-09 10:00:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3721240 | Unit 8, Cell B6 - Cell call faint & crackly, but no sound through to control room | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 08:40:24 | 2020-10-22 16:41:00 | Pass | Faulty and defective cell call replaced with new and tested ok. Job completed.
MSA-DCS | WA3721266 | Serpentine, Store room- Lock has broken | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 10:00:00 | Pass | Attended site. Replaced faulty lock.
MSA-DCS | WA3721269 | kitchen wash bay damaged power point - see notes | Casuarina Prison | WSM-MW-HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 13:30:00 | Pass | Investigated damaged wash bay gpo, picked up replacement parts, relocated and tested gpo.
MSA-DCS | WA3721285 | kitchen tap is falling off and leaking | Warminda Hostel | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 09:13:00 | 2020-10-23 09:00:00 | Pass | Complete
MSA-DCS | WA3721287 | admin office fluro light faulty | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-22 13:00:00 | Pass | Replaced tubes and starters in light fittings in main office area, had a walk around and checked all other light fittings,
MSA-DCS | WA3721291 | Camera in hall way not working- possible warranty issue | Maddington (South East Metro) | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 09:15:35 | 2020-10-22 16:30:00 | Pass | Job completed - Checked CCTV system. Camera 8 offline & Reception monitor has no camera view. Power cycled Camera 8 & restored Reception monitor. Instructed not to close Indigo in Server Room. Updated time on Server to correct time.
MSA-DCS | WA3721296 | unit 3 amenaties exteria door rotted through cannot be used | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-23 13:00:00 | Fail | Supplied andinstalled new 2060 x 820mm x 40mmSolid core door.Primed and painted new door colour to match exciting.
MSA-DCS | WA3721298 | HR block down pipes rusted and some are missing | Bandyup Prison | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-18 11:30:00 | Fail | 26/10/20Inspect and measure up downpipes to replace / gutter replacement18/11/20Remove down pipe and patch gutter. Remove and replace 2 down pipes
MSA-DCS | WA3721301 | entry building secure lock door alarm activating when not opening | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-23 10:00:00 | Pass | Rectified and fixed the faulty reed switch, job completed.
MSA-DCS | WA3721307 | No audio or video to let vehicles in from boom gate | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 09:33:05 | 2020-10-22 14:59:00 | Pass | Jacques intercom video system failing to display video and audio, intercom dropped off communications link, restored comms and tested fully operational. (Checked intercom has no history of failure)
MSA-DCS | WA3721434 | Unit 7 - Day Room Fly plastric screen entry to A,B,C and D wing fly flaps have dropped off | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 15:00:00 | Pass | MEASURED ONLY - PRISON TEXTILES/MAINTENACE WILL MAKE AND INSTALL
MSA-DCS | WA3721539 | Unit 1 - Control Room Control panel in control has died due to water ingress - SEME on site | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-24 11:11:00 | Pass | Attended site, found equipment issues due to contractors pressure cleaning, repaired faults and tested OK.Job Complete
MSA-DCS | WA3721614 | Unit 1 C12 cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 11:36:31 | 2020-10-22 16:44:00 | Pass | Faulty cell call , replaced and test ok. Job completed.
MSA-DCS | WA3721636 | Kitchen, Dishwasher is not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 11:34:24 | 2020-10-22 13:00:00 | Pass | Dishwasher tripped
MSA-DCS | WA3721804 | Unit 6 N7 Toilet cant flush needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 13:04:22 | 2020-10-23 08:00:00 | Pass | Removed broken button replacing with new on toilet
MSA-DCS | WA3721956 | Gate house- Burst Fire Main at the back off the Eastern Sally Port | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Oct 2020 | 2020-10-22 18:21:52 | 2020-10-23 00:00:00 | Fail | Nill
MSA-DCS | WA3721965 | unit 7 E wing showers water steeping into E wing floor - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 14:29:41 | 2020-10-23 09:00:00 | Pass | Have already replaced all washers in these showers all tiles are cracked and have no grout they need to be removed and water protection. Redone then tiles and grout
MSA-DCS | WA3721976 | control room ASU gate alarming during E section duress alarm | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-18 10:30:00 | Fail | Checked controller and inputs/outputs related to the Duress strip and gate alarm. No relationship between circuits, apart from common controller. Reset controller associated with both circuits and retested Duress Alarm. No corresponding gate alarm. Cause unknown.
MSA-DCS | WA3721977 | control External D1 zone in alarm mode | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-23 13:30:00 | Pass | PE Beam Set has ant infestitation. Cleaned ants from cover and stripped down PE Rx to clean ants from internal components. Reassembled and tested.
MSA-DCS | WA3722154 | EBI - Key Issue - Computer is frozen | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 21:00:48 | 2020-10-22 22:45:00 | Pass | Attended site checked and found Key Issue EBI workstation is not responding. Located problem to be the workstation itself. Restart workstation and EBI Station. Tested all ok after.
MSA-DFES | WA3721262 | KAT's office no power to the work station for the senior health and safety consultant- | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 10:05:00 | Pass | Complete
MSA-DFES | WA3721759 | Door # 6 pin has fallen and roller door has come crashing down-see notes | CFRS Welshpool | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2021-03-03 17:00:00 | Fail | Complete
MSA-DFES | WA3722016 | Yard - Bracket holding lights on tower has rusted away and lights are only held on by wiring | CFRS Fremantle | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-11 15:00:00 | Fail | Locate faulty light. The light bracket looks like it is damaged. The light is 8 - 9 meters high. Will require a sissor lift or boom lift to reach the light. Recommend replacing the light with a LED flood light.Collected parts from 6-6:30Arrived onsite and signed in at 1215Install new pole lights and tested for function.Notified staff of works and signed out and left at 1500
MSA-DTAG | WA3721265 | Technician required to isolate FIP at 06.30am Saturday 24 October & de-isolate FIP | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-24 17:00:00 | Pass | Isolated detection for works at 06:30Returned and reinstated at 17:00
MSA-DTAG | WA3721575 | ground cells 2 accused has Golden Staph | Midland Courthouse | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 19:30:00 | Pass | Completed P1 clean on the 22/10/2020
MSA-DTAG | WA3721772 | Level 4 room 4.08 push to exit button doesn't not work . | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-22 14:00:00 | Pass | Work performed by Ken Moore (22/10/2020):Attended site. Replaced faulty Push to Exit button on Level 4 Room 4.08.Tested, all OK.Job completed.
MSA-DTAG | WA3721981 | LINKS office- Wet Ceiling tile | Perth Children's Court | GMP-BR-HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 12:15:00 | Pass | CEILING TILE REPLACED
MSA-DTAG | WA3721986 | LINKS office- Smell of damp in the kitchen area | Perth Children's Court | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-03 09:30:00 | Fail | COULD DETECT NO OBVIOUS SMELL OF DAMP - TWICE ATTENDED
MSA-DTWD | WA3721180 | ground G block 3 phase power point in Welding bay 11 black and burnt | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 22 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-22 11:00:00 | Pass | Attended site and signed in. Spoke with staff on site regarding issue. Located G block. Checked out bay 11 and found outlets all okay. Checked other bays and found bay 12 with out of service tag. Burnt white phase on outlet. Disconnected and removed faulty outlet. Supply and replace with new switched 5 pin 32 amp outlet. Reinstalled ID markers. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3721280 | A Block, AG10C, Aroma Café Cool Room - Refrigerated cool room isn’t working | Carlisle Campus | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-23 12:30:00 | Pass | Replaced 2x condensor fan motors and blades on coolroom
MSA-DTWD | WA3721325 | E Block Restaurant Kitchen, under bench fridge on entree section not holding temp | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-26 12:00:00 | Fail | Attended site, signed in,located system, tested system and investigated, found system to have burnt out evaporator fan motor which was causing the ice up,removed fan motor and picked up new motor from supplier, re-attended site and fitted new fan motor assembly,connected electrical and tested, monitored system and left all operational
MSA-DTWD | WA3721439 | U block U011 dust extraction unit not working - electrical issue | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 09:30:00 | Pass | Inspected extraction fan not working outside U0011. Reset tripped thermal overload . Investigated why tripped lubed up chain and bearings . All working fine .job completed .
MSA-DTWD | WA3721442 | BLD822- Flat A- Faulty toilet, sewerage smell | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 12:30:00 | Pass | Job completed -
MSA-DTWD | WA3721476 | T Block, Level 1, end cubicle male student toilet- WC blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-23 10:05:00 | Pass | unblocked toilet
MSA-DTWD | WA3721480 | T block, Ground floor, Female student left cubicle W.C cistern continually flushing | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 22 Oct 2020 | 2020-10-23 17:00:00 | 2020-10-23 10:03:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3721577 | A Block, Fire Panel Fault Z4 28 smoke detector, 1st floor male toilets | Fremantle Campus (formerly WA Maritime) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-10 15:46:00 | Fail | A Block, Fire Panel Fault Z4 28 smoke detector, 1st floor male toilets.new detector replacedCOMPLETED
MSA-DTWD | WA3721594 | Workshops (listed below), 4 x Emergency lights not working above doors | Clarkson Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-23 11:00:00 | Pass | Attended site and took note of exit lights out and sourced replacements. Returned to site and replaced x4 exit lights
MSA-DTWD | WA3721639 | D block student male toilet several leaking basin taps | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-22 14:00:00 | Pass | Taps badly leaking wouldn’t shut off properly
MSA-DTWD | WA3721667 | Campus Ground, Trip hazard on path way outside G Block | Bentley Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-12 13:00:00 | Fail | Lifted and relayed numerous areas of uneven paving
MSA-DTWD | WA3721803 | Cafe, Kitchen- Broken tap | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-28 18:00:00 | Fail | Connect and run water for hot tap
MSA-DTWD | WA3721892 | S Block, Ground, External- Spray for millipedes around S block | Joondalup McLarty Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 09:30:00 | Pass | Sprayed all perimeter of S Block, walls and foliage.Please note that Millipedes live in bush land and after rain they seem to flourish for a few days.Spraying the perimeter of the building has limited affect on Millipedes due to their hard exo skeleton which slows the absorption of the chemical therfore making it hard to control this insect.
MSA-DTWD | WA3721934 | Block 3, Room 3D16- Door frame loose and preventing door from closing | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-02 13:30:00 | Fail | Re-secured and braced door frame to room 3D16
MSA-DTWD | WA3722003 | Chalk and cheese cafe - broken hose adapter in kitchen sink | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 22 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 13:30:00 | Pass | Install tap
MSA-DCA | WA3722954 | Black swan - Air Con is not working, temperature too hot | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 2-Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 23 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 11:00:00 | Pass | Issue resolved
MSA-DCS | WA3722396 | Unit 5 House 10 - holes in the decking. | Bandyup Prison-Administration | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 23 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-25 13:00:00 | Fail | NEW DECKING INSTALLED
MSA-DCS | WA3722427 | Unit 4 A3 lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 07:40:13 | 2020-10-23 11:05:00 | Pass | On Site. Replaced broken lock. Normal function restored.
MSA-DCS | WA3722436 | Murchison - Cell call not working correctly (Low or no sound) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-04 09:30:00 | Fail | Replaced faulty PA Amplifier in Murchison and installed new Redback Amplifier A 4043 60W (supplied by SEME).Conducted test.All ok at departure
MSA-DCS | WA3722444 | Unit 3, Cell D4 - Cell Call wet. Suspected roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 08:11:50 | 2020-12-10 14:15:00 | Fail | roof repairs complete to rectify leaking
MSA-DCS | WA3722445 | Unit 4, Control Room- Vesda System in Fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 08:13:43 | 2020-10-23 12:08:01 | Pass | Unit 4 vesda fault cleared sampling points levels 100% back to normal
MSA-DCS | WA3722460 | Please investigate reported of sudden increase of water usage onsite. Suspected leak | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-02 18:16:00 | Fail | Searched prison grounds for leaks no sign spoke with water Corp he advised to leave till Monday and just see what it does
MSA-DCS | WA3722475 | Kitchen, work area gas cook top - Gas Hose Leaking ( Has Been Isolated ) | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 08:40:23 | 2020-10-23 13:03:00 | Pass | Refitted gas hose in kitchen,checked and tested for leaks ok.
MSA-DCS | WA3722476 | Kitchen, Work Area on the end of fridge 1 - Hose Tap Leaking wont tighten into the | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 08:46:14 | 2020-10-23 13:50:00 | Pass | Repaired leaking hot water hose tap on the wall in the kitchen.
MSA-DCS | WA3722489 | control room unit 2 transponder alarm fault - SEME on site | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-23 13:30:00 | Pass | Alarm generated by MDAS Receiver 9.2.3 Unit 2 External Cell D9 (19). Contacted Maintenance to arrange access to the receiver. Noted when removing the cover the Tamper spring was low tension. Retensioned the spring and refixed the cover. Confirmed no further alarms from receiver.
MSA-DCS | WA3722494 | Please carry out the repairs to the kitchen billi unit - as per quote SOQ28704 | Clarkson | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 11:01:00 | Pass | Replaced element, main power board and pump. Calibrated hot water. Descaled tank.
MSA-DCS | WA3722509 | Unit 7, D Wing- Hot water tap is dripping/leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-02 12:30:00 | Fail | Nill
MSA-DCS | WA3722567 | Cell 5, 23 has exposed wires coming out of cell call. | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Oct 2020 | 2020-10-23 18:03:53 | 2020-10-23 12:00:00 | Pass | Contacted site and checked cell call and cell call all working ok, issue seems to be related to electrical fault and cell call is all ok. Job complete
MSA-DCS | WA3722628 | dairy glycol system is running to cold - please sub contract out to Essential Refrigeration | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 10:30:00 | Pass | attended site , ran system with a load .Temperatures are normal. left system to run over night and returned calibrate sensors and left operational.
MSA-DCS | WA3722681 | Education, Room 13- door lock is stuck in the 'unlocked' position, the room is unable to be secured. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 11:07:07 | 2020-10-23 12:30:00 | Pass | Service lock and replace bolt throw.
MSA-DCS | WA3722683 | Unit 4, B12 Toilet system not filling up. No water to flush toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-26 10:30:00 | Pass | Nill
MSA-DCS | WA3722736 | SB1 (Between U15-U16) - Room 1 Door lock to Health consult room 1 is broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 11:23:58 | 2020-10-23 15:45:00 | Pass | Lock barrel faulty, obtain replacement barrel from supplier and install
MSA-DCS | WA3722741 | Lvl 3, Female toilets- Blocked toilet | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 11:29:02 | 2020-10-23 14:00:00 | Pass | Complete
MSA-DCS | WA3722745 | Unit 3, Cell B1- Sink drain is blocked, cannot clear it | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-29 09:30:00 | Fail | Nill
MSA-DCS | WA3722754 | Unit 3 B1 toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-29 08:30:00 | Fail | Nill
MSA-DCS | WA3722792 | Bakery- Verstile moulder 3 phase plug short out | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 23 Oct 2020 | 2020-10-23 16:07:41 | 2020-10-23 15:00:00 | Pass | Repaired damaged verstile moulded in bakery
MSA-DCS | WA3722800 | Unit 7, G Wing Dayroom- Key snapped inside lock needs repair | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 12:15:57 | 2020-10-23 16:00:00 | Pass | Attend site. Remove broken key. Service/repair lock and replace damaged parts to restore normal function.
MSA-DCS | WA3722808 | Unit 6, Cell A25- Personal lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 12:19:25 | 2020-10-23 14:20:00 | Pass | On site. Replaced lock to restore normal function.
MSA-DCS | WA3722809 | U6 A1 - Door lock will not open needs repair | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Oct 2020 | 2020-10-24 12:22:21 | 2020-10-23 13:30:00 | Pass | Attended site. Forcibly opened faulty lock and replaced it.
MSA-DCS | WA3722820 | PTZ camera 16 unit 3.not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-12-21 13:49:00 | Fail | Job to be invoiced at cost to date.
MSA-DCS | WA3722821 | Unit 1 house 4 reed switch damaged | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 18:50:00 | Pass | Reed switch and cables have been damaged. Able to retrieve cable from door frame.Replaced reed swith and tested
MSA-DCS | WA3722823 | Zone 13 electric fence wire loose and dangling near the ground | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-18 17:18:00 | Fail | Replaced 100m of Gallagher electric fence wire,Adjusted various wires
MSA-DCS | WA3722829 | Unit 1, hut ablutions - blocked drains | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-26 15:45:00 | Pass | COMPLETED
MSA-DCS | WA3722831 | Broken sewage pipe behind construction shed | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 13:30:00 | Pass | COMPLETED
MSA-DCS | WA3722897 | unit 5 house 6 oven not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-11 14:30:00 | Fail | Replaced oven in unit 5 house 6
MSA-DCS | WA3722900 | Social visits area- cameras out of service on monitors | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Oct 2020 | 2020-10-23 17:51:42 | 2020-10-27 12:45:00 | Fail | Multiple IP cameras failed due to faulty network switch, replaced with new. Job completed.
MSA-DCS | WA3722917 | Control Room - Cameras are not recording | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Oct 2020 | 2020-10-23 18:28:35 | 2020-11-04 12:30:00 | Fail | Replaced hardrive for slot 5 in NVR 2. Rebuilt raid and retested camera recording schedules. All replaced and tested ok. Job complete
MSA-DCS | WA3723006 | Back door from kitchen is not locking- see notes below | Rockingham Justice Complex | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 10:43:00 | Pass | Attended site, replaced mortice lock on back door from kitchen, rehung door with existing hinges. recommend replacing hinges.
MSA-DCS | WA3723042 | Recall - Control room, faulty MW zone 12 | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Oct 2020 | 2020-10-23 21:58:05 | 2020-10-23 20:00:00 | Pass | Attended site checked and found Zone 12 Inner MW alarm input always on. Checked log file found faults since 21/10/20. Checked with security officer and office found there is a open job for the fault. Part has been ordered and will be back to site to replace early next week. Job will be completed under WA3720890. Job completed.
MSA-DCS | WA3795177 | CCU Cell HD4 TV cabinet causing blind sport on corner mount camera- see notes below | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 23 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-05 11:00:00 | Fail | WORKS COMPLETED - AS QUOTED
MSA-DFES | WA3722574 | FF1/FF2 Shower Room- Bracket which holds the shower head upright & in position is broken | CFRS Wangara | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-02 11:30:00 | Fail | Fit new shower rail and head
MSA-DFES | WA3722590 | lawn outside of main electric gate sprinkler head broken | CFRS Wangara | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 12:30:00 | Pass | Dom Coniglio & Retic Parts $84.00
MSA-DFES | WA3722984 | Engine room - Multiple leaks, roller doo leaking letting rain in causing extensive flooding on | VFES Karnup | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-16 09:45:00 | Fail | Repairs completed and leaks confirmed resolved after recent rain
MSA-DFES | WA3722997 | **Retrospective work order ** Z18 Reed Bay 1 front roller door bypass, External check | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 23 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-23 11:07:00 | Pass | NO SIGNS OF FORCED ENTRY OR DAMAGE . NO PERSON'S SIGHTED . STAFF CARS IN PARKING LOT
MSA-DTAG | WA3722449 | Court 31 public door squeaking – vinyl inner door panel needs additional screws | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 08:30:00 | Pass | LUBED AND SECURED
MSA-DTAG | WA3722883 | law museum Access hatch in Museum floor is jammed | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 10:45:00 | Pass | LUBED
MSA-DTWD | WA3722441 | Plant Room - Flow issues in domestic hot water pump system | Perth Campus B6 | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Equans Mechanical Services Australia | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-09 14:07:00 | Fail | Returned to site gained access to plant and checked equipment operation. Confirmed heat present on water line to eather side of pump. Work area left tidy. Site facilities to monitor for further signs of fault.
MSA-DTWD | WA3722452 | Several passage lights in G block west are inoperative. | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-28 11:45:00 | Pass | Attended site and signed in. Completed jsa. Found g block hallway lights that were faulty. Replaced hallway lights. Tested all ok. Completed paperwork and informed pfm of completion of works. Signed out. Job compete
MSA-DTWD | WA3722619 | A-Block Room A009 FUC in fault no airconditioning | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-11-03 11:00:00 | Fail | Picked up required parts attended site, set up and removed cieling panels,installed new motor into fcu,wired motor and tested,cleaned work area and left all operational
MSA-DTWD | WA3722722 | Jandakot hanger staff kitchen next to main entry door double GPO wall mounted | Jandakot Campus - Hangar | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 12:15:00 | Pass | Attended site and signed in. Got access from staff to staff room. Locate broken gpo and mounting block. Disconnect and removed faulty gpo. Supply and replace with new mounting block and gpo. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3722815 | J Block, Gazebo- Brick paving is uneven | Balga Campus | GMP-BR | Paving & Roadworks | Paving (PR) | M Construction (WA) | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2021-02-08 08:41:00 | Fail | Job complete
MSA-DTWD | WA3722818 | Block, 3, Metal Fab - Right hand grinding bay power point not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 10:45:00 | Pass | Attended site and signed in. Got keys from facilities. Located block 3 metal fab grinding bay. Investigated outlet in fault, found neutral pin to be sloppy and not biting the pins of appliances. Disconnect and removed faulty outlet. Supply and replace with new 3 pin outlet. Tested outlet and all okay. Signed out. Job complete
MSA-DTWD | WA3722822 | L block room L003 air con not working | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 23 Oct 2020 | 2020-10-26 17:00:00 | 2021-01-05 17:00:00 | Fail | Upon inspection found unit was out on fault, only runs on fan mode, isolated unit removed condenser covers to find multiple rodent droppings and urine on PC Board connections, fault code via remote displayed U4 com's fault, removed pipe covers to unit to check interconnected wires which were fine, belled wires to check for breaks all ok, quote required to replace indoor outdoor boards, then fit and test unit to see if there are any faulty components, refitted all covers and tagged out isolation switch at condenser.05/01/2021New unit installed
MSA-DTWD | WA3722855 | green skills building water bubling out of the ground | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Oct 2020 | 2020-10-26 17:00:00 | 2020-10-26 12:30:00 | Pass | Complete
MSA-DTWD | WA3722896 | Lvl 2, male toilet- Urinal leaking | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-26 15:30:00 | Pass | Fixed leaking urinal
MSA-MRWA | WA3722909 | East of staff carpark- bee hive | Materials Engineering Branch-External Area-Ground Floor-Car Park-Staff | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 23 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-27 06:05:00 | Pass | Dusted bee hive in base of tree east side of carpark
MSA-DCS | WA3723059 | Unit 2 -B10 -C13 -VESDA alarm is going on | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Oct 2020 | 2020-10-25 07:40:15 | 2020-10-24 15:44:00 | Pass | Melaleuca prison. Call out for alarm on vesda in unit 1.Once onsite found alarm latched on vesda in unit 1 cells C/D cells 5/6. Reset vesda and returned it to normal. Also found another vesda in unit 1 A/B Cells1/2 in minor airflow fault so cleaned pipework and returned vesda to correct operation.Kitchen defrost fridge missing fault. Requires new Coolroom notifier detector (FST 851) and 2 techs to replace (below and above ceiling) - being replaced under WA3730287
MSA-DCS | WA3723069 | between u3-u4 PE alarm is isolated ,Need to put back on action | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Oct 2020 | 2020-10-24 12:34:24 | 2020-10-24 10:45:00 | Pass | Attended site checked and found PE beam between U3&U4 has been isolated. Armed the PE beam then found it keep going to alarm. Checked on field found a lot of weeds blocking the bottom PE beam sets. Cleared all the weeds and tested alarm activated and reset correctly.
MSA-DCS | WA3723090 | Unit 4- J 10 - Personal lock of cell door is sticking- Difficulty in unlocking it | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 24 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 11:00:00 | Pass | Attend site. Replaced faulty lock to restore normal function.
MSA-DCS | WA3723115 | Greenough Regional Prison - Unit 1 - Cell 3 - Cell call system is not working. | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Oct 2020 | 2020-10-25 14:38:21 | 2020-11-05 14:15:00 | Fail | Traced fault to input 3 on CI8A 1 in unit 1 roof space. Replaced CI8A. Tested to control. Audio in cell and in control is loud and clear.
MSA-DCS | WA3723136 | Unit 1 cell11 B -Cell call not working | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Oct 2020 | 2020-10-25 16:18:34 | 2020-10-27 17:00:00 | Fail | Tested cell call, distorted audio/blocked sound.Cleared out toothpaste/dirt from cell call and re-tested. All tested and working ok. Job complete
MSA-DCS | WA3723143 | unit 1 - D5 - lock is faulty | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 2 | CLOSE | 24 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 13:10:00 | Pass | 26/10/2020. On site. Replacement lock required.27/10/2020. Attend site. Replacement lock fitted.
MSA-DCS | WA3728408 | gardens and control 1 area-bees swap pest removal | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 24 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 08:00:00 | Pass | Attended Hakea Prison for reported bees. Upon arrival no one at Hakea knew where the bees were located. Will have to return at a later date once more information is found out.Carried out a service for bees at Hakea Prison. There were reports of bees located around the zone 1 and gardens area. Upon further inspection no bees could be located and determined to be swarming on the day they were seen.
MSA-DCS | WA3723151 | SITE COSTED VISITS AREA inside prison- AC Fault. | Casuarina Prison-Prisoner Reception, Visitor Centre, Prisoner Accommodation | WSM-BR-SITE | Building | Materials (BU) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 25 Oct 2020 | 2020-10-25 11:23:33 | 2020-11-04 15:13:00 | Fail | Arrived on site and signed in, checked pressure test system held pressure overnight, released nitrogen and vac out system and recharge with R22, turned on and tested all running ok at present.
MSA-DCS | WA3723171 | Water tank is overflowing under neath the tennis court | Wooroloo Prison Farm-Prisoner Gymnasium | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-26 09:30:00 | Pass | COMPLETED
MSA-DCS | WA3723259 | Melaleuca Prison - Main gate - Visitor area - automatic door is not shutting | Melaleuca Prison | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 25 Oct 2020 | 2020-10-25 22:59:50 | 2020-10-25 20:30:00 | Pass | AFTER HOURS CALLOUTAnthony Calautti (25/10/2020) - Work NoteTravel to site. Inspect Visitors air lock door outer, (rear of guard house) Found lock not locking. Door is closing okay but not locking lock. Reset lock tabs, now okay. Test operation several times, all okay. Check interlock with inner door, all okay. Possible access system fault
MSA-DCA | WA3728402 | Broken reticulation sprinkler | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 14:45:00 | Pass | job completed - oFix the collector line by replacing it with 25mm LD poly pipe and bury it under the soil.oFix multiple drip leaks by joining it back to the other drips.
MSA-DCA | WA3728575 | emergency exit light out | His Majesty's Theatre-Theatre Building-Level 2-Upper Circle Seating | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-28 09:30:00 | Pass | Failed exit replaced with new
MSA-DCS | WA3728260 | Transmitter number 73, low battery warning | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 11:05:53 | 2020-10-26 16:02:00 | Fail | Replaced duress transmitter batteries and tested OK.Job CompleteParts (SEME Stock):2 x CR-2 Lithium Batteries
MSA-DCS | WA3728264 | Fire Control Panel- can not clear alarm | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 11:08:23 | 2020-10-26 08:38:00 | Pass | Unit 4 L Block Cell 48 thermal detector missing fault in toilets. Replaced 1x XP95 thermal detector. Fault cleared. System normal at time of departure
MSA-DCS | WA3728278 | Admin business manager office - Light fitting falling away from ceiling | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 13:30:00 | Pass | Investigate and repair admin business manager office light
MSA-DCS | WA3728283 | Signage w/s - GPO broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 12:00:00 | Pass | Investigate and repair/replace gpo’s in signage workshop
MSA-DCS | WA3728309 | Transitional Manager- Door lock not latching on external door | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 26 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 09:30:00 | Pass | Attend site. Serviced lock and door closer to restore normal function.
MSA-DCS | WA3728324 | Network controller number 1 - alarm | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 11:47:00 | 2020-10-26 17:00:00 | Fail | Attended site and repaired fault on sennet network 1. Tested OKJob Complete
MSA-DCS | WA3728348 | Unit 2, Cell A12 - Key broken off in Medical Hatch Lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 08:01:27 | 2020-10-27 13:55:00 | Fail | 26/10/2020. On site. Assessed lock - replacement required.27/10/2020. On site. Replacement lock fitted.
MSA-DCS | WA3728349 | laundry Door behind entrance grill Door is damaged hard to close | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 26 Oct 2020 | 2020-10-28 17:00:00 | 2021-01-13 13:30:00 | Fail | door repaired
MSA-DCS | WA3728350 | Unit 1, Cell D8- Broken Medical Hatch Lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 08:02:55 | 2020-10-26 13:45:00 | Pass | Attend site. Serviced lock and hatch to restore normal function.
MSA-DCS | WA3728353 | Unit 5, B & C Dayroom - Ceiling fan faulty possibly bearing fault | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-04 12:00:00 | Fail | Replaced ceiling fan
MSA-DCS | WA3728360 | kitchen Rational Combi oven (Gas) – keeps aborting on cleaning cycle-see notes | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Staff Kitchen and Dining Area | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 13:05:00 | Pass | Test all components, run unit through clean cycle successfully. Left oven operational .
MSA-DCS | WA3728371 | kitchen freezer no8 Limit switch faulty freezer motor do not start when door closed | Hakea Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 08:16:44 | 2020-10-26 14:30:00 | Pass | Resecured door switch and replaced controller due to faulty internal relay. All operational at time of departure.
MSA-DCS | WA3728374 | Unit 5, Cell D5- Toilet will not flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-30 10:30:00 | Fail | Nill
MSA-DCS | WA3728376 | Unit 2 cell call 5.12 Will not alarm and connect in the Unit Control room.-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 16:21:15 | 2020-10-27 22:15:00 | Fail | Travelled to site, waited for car hire in Karratha airport as non availableTravelled to site, replaced cell call with new seme stock cell call for unit 2 cell 12 as was worn and speaker was faulty, all replaced ok. Checked functions and still not working ok, checked port and swapped with working cell call, all working ok. Located spare input on C1-8 board No 1, re-termnated and retested, all working ok. Re-programmed labelling of cell to match correct cell number. All tested and working ok. Job completeTravel to Perth
MSA-DCS | WA3728377 | Unit 5, B Wing shower tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 10:30:00 | Pass | Nill
MSA-DCS | WA3728382 | Unit 4, C Wing- last shower tap just spins | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 09:30:00 | Pass | Nill
MSA-DCS | WA3728385 | Unit 13- Plant Room- 3rd flange from P1 pump leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-02 10:30:00 | Fail | Nill
MSA-DCS | WA3728387 | Unit 2 cell call 5.22 Alarm activates however is cracking, not clear.-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-27 15:30:00 | Pass | Collected parts and attended site, replaced cell call with new cell call and re-tested, all tested and working ok. Job complete
MSA-DCS | WA3728390 | INF (10), Cell B7- Broken basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-06 11:30:00 | Fail | Nill
MSA-DCS | WA3728394 | Bakery- Bread slicer cable sparked and shorted out. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 11:00:00 | Pass | Repaired damaged cable in bread slicer machine in bakery.
MSA-DCS | WA3728396 | Unit 6, A & C- power point on the sink area behind the toaster has been damaged. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-27 08:00:00 | Pass | Replaced damaged toaster gpo in unit 6
MSA-DCS | WA3728415 | INF (10, Cell B7 - 2x broken windows | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2021-02-17 13:15:00 | Fail | 2X WINDOWS total RE GLAZE AND DOOR PANEL
MSA-DCS | WA3728419 | Unit 14, Cell B1- Personal lock has something jammed in it | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-28 11:00:00 | Pass | Require parts.Replace worn/damaged barrel
MSA-DCS | WA3728432 | SB2 (Between U17-U18) - Control Room lock on the "Vocational Training" key lock box is faulty. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 14:00:00 | Pass | Open jammed key lock box, To many keys stored in box, causing lock to jamb under pressure.
MSA-DCS | WA3728433 | Kitchen, Dishwasher jets not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 08:50:55 | 2020-10-27 15:00:00 | Fail | 26/10/20Called as requested to the dishwasher not working correctly the pre wash pump not pumping and breaker tripping. Found the pre wash pump working but poorly will require new. Parts required 1x pre wash pump27/10/20Arrive at site to fit parts, fit new pump and test all ok. Water still less pressure at top jets, notice leak at jet arm at top inside also hose to pump collapsing, if problem persists would need to replace pump inlet hose and mount pump in better position so doesn't put more pressure on hose, this would mean drilling out the bracket 10-12mm hole. Test unit all working ok as is an old machine
MSA-DCS | WA3728468 | Abattior skins shed - fencing posts rusted and require repairs to secure area | Karnet Prison Farm | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Midolo Building Services | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2021-01-12 11:00:00 | Fail | NEW FENCE POSTS INSTALLED
MSA-DCS | WA3728502 | Unit 3, Cell A7- Window drops and wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 10:00:00 | Pass | SPIRAL BALANCES & FEET RENEWED
MSA-DCS | WA3728509 | Unit 14, B & D- terrible smell coming from waste pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-11 19:49:00 | Fail | Nill
MSA-DCS | WA3728518 | freezer hight temp - refer to Derek Man | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Staff Kitchen and Dining Area | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-12-02 13:01:00 | Fail | Quotation C20-11-02 BRA Issued Freezer Room Controls Upgrade.
MSA-DCS | WA3728581 | Reprogram required for door alarm & unattended switch - new Prisoner Reception Door-see notes | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-05 15:30:00 | Fail | Installed and tested new key switch in ax system
MSA-DCS | WA3728761 | Unit 2 courts area outside the unit- Water cooler tap faulty | Hakea Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 13:00:00 | Pass | replaced bottle filter on arcus fountain
MSA-DCS | WA3728769 | kitchen freezer Not Cooling below 2 C | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 11:47:51 | 2020-12-14 15:30:00 | Fail | Replaced heaters, re commissioned freezer. Operational at time of departure
MSA-DCS | WA3728776 | Gardens eastern oval Station 19 solenoid stays on affecting recreation | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 11:57:24 | 2020-10-26 15:30:00 | Pass | REPROGRAMMED CONGTROLLER TO ALLEVIATE FUTURE ISSUES.
MSA-DCS | WA3728818 | Jeelia block camera's are not recording and disappearing | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 12:24:30 | 2020-11-20 10:30:00 | Fail | Replaced power supply for new, restored cameras and tested operational, checked recordings ok.
MSA-DCS | WA3728906 | Unit 5, Cell 13- Window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 11:45:00 | Pass | SPIRAL BALANCES TO WINDOW REPLACED
MSA-DCS | WA3728914 | Unit 5, Cell A9 - Window unable to stay open. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 13:30:00 | Pass | NEW SPIRAL BALANCES FITTED & FRAME REPAIRS CARRIED OUT
MSA-DCS | WA3728919 | reset family centre Air con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 13:02:28 | 2020-10-27 10:30:00 | Pass | Replaced pump and float valve, unit now operating as designed
MSA-DCS | WA3728953 | Unit 1, Cell D3- Toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 17:28:27 | 2020-10-26 16:25:00 | Pass | Plunger used to unblock toilet
MSA-DCS | WA3728994 | Visit centre - Water cooler is noisy | Wooroloo Prison Farm | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-25 10:36:00 | Fail | attended diagnosed issues advised we recommend replacing quoted 2 options client did not respond.A40191160B Arcus Visitors Centre
MSA-DCS | WA3728995 | ground alarm system SEME to setup auto-arming and fix alarm trigger issues (warranty)-see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-26 15:00:00 | Pass | reprogrammed exit delay and entry points. Tested operation and all working. Programmed autoarm weekdays 19.30 and weekends 17.00 and tested. All is OK.
MSA-DCS | WA3728996 | Kitchen 4D- Fluro light is not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 12:30:00 | Pass | Replaced light fitting in kitchen area
MSA-DCS | WA3729016 | INF (10)- disabled toilet shower head is leaking water. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 08:30:00 | Pass | Nill
MSA-DCS | WA3729033 | ground staffroom/kitchen double doors hinges deteriorated - see notes | Rockingham Justice Complex | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-28 14:00:00 | Pass | New hinges installed
MSA-DCS | WA3729046 | ground staff ladies toilet Broken Toilet Roll Holder in Stall 1 of Staff Female Toilets - see notes | Rockingham Justice Complex | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 16:30:00 | Pass | Complete
MSA-DCS | WA3729114 | Gatehouse - inner sally port roller door is not working - will not open when button is pushed | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 20:52:00 | 2020-10-26 19:30:00 | Pass | 26/10/20Inspect inner roller door.Works with manual over ride buttons, therefore EBI issue, call SEME
MSA-DCS | WA3729124 | Gate house - M-DAS- Duress alarm system location accuracy has to be updated | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-12 12:00:00 | Fail | Travelled to site, checked duress system and funtions. Performed test on duress system multiple times around init 1 area and skills building, found a few duress recievers description incorrect but duress point was accurate when activated. re labelled duress reciever description and retested multiple times. All tested and working correctly. All tests complete, job complete
MSA-DCS | WA3729126 | Gatehouse - Sally port inner roller door access control needs fixing. | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 22:05:44 | 2020-11-02 12:09:00 | Fail | Repaired sallyport fault
MSA-DFES | WA3728680 | ground dorm 3 Toilet cistern broken.Cracked lid of cistern - see notes | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 09:28:00 | Pass | Servicing toilet cistern
MSA-DFES | WA3728723 | ground POD shed Damage to colourbond flashing vehicle bay- see notes | CFRS Canning Vale | GMP-BR | Building | General Building (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-03 14:30:00 | Fail | Remove damaged door flashing and replace with new
MSA-DFES | WA3728968 | Reticulation not working- see notes below | CFRS Vincent | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-23 13:00:00 | Fail | Site attended several times as BRAF have been raised for further works.All works are now complete
MSA-DFES | WA3728976 | Ground- plumbing issues, see locations & issues below | CFRS Ellen Brook | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-12-21 14:45:00 | Fail | Investigate damaged toilet seats located room 8,11,14 and leaking kitchen sink spoutRoom 11 needs new toilet seat will need to order and returnRoom 8 and 14 remove seat and re-install off issue persists replacement seats will be needed Remove old kitchen sink spout and replace with new spout, test operationRemove costern parts to replace inlet and outlet washers and test operationPack up and clean up Remove existing damaged toilet seat Ssupply and install new caroma cube toilet seatPack up and clean up worksite
MSA-DFES | WA3728978 | Rm14 – Shower screen leaks at the bottom side rail when showering | CFRS Ellen Brook | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 14:15:00 | Pass | Work completed
MSA-DFES | WA3728982 | Doors 9/10 , 12/13 & 24/25 and 3 external door issues - see notes | CFRS Ellen Brook | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-18 12:00:00 | Fail | Replace worn door closers with new
MSA-DFES | WA3729103 | Engine room door - faulty, securing cables have become detached, door not usable | CFRS Daglish | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 13:15:00 | Pass | ATTENDED SITE ON THE 27.10.2020. AT 12:15. DOOR CABLE ADJUSTED AND THE DOOR IS NOW WORKING WELL. DOOR IS NO LONGER TAGGED OUT.THANK YOU
MSA-DTAG | WA3728511 | basement custody centre - Air conditioner in custody centre does not appear to be working properly | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 12:00:00 | Pass | Attend site. Check operation of AC serving detention area. Found unit to be running. Adjust setpoint and check operation. Found to ne suppling 13 degree air to area. Access detention and chevk temps in unoccupied cell, found to be working as normal. Access BMS and adjust time schedule for AC unit to start earlier as staff say it is a bit warm first thing in the morning. Adjust setpoint from 23 to 22.5. AC unit is working as normal.
MSA-DTAG | WA3728604 | Sheriffs office - Flashing light in men’s bathroom | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 08:45:00 | Pass | No Fault Found
MSA-DTAG | WA3728605 | 1903 building - Airconditioning in Courtroom 1 too hot or not on | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 17:00:00 | Pass | Attend site with icon logic. Access BMS and check schedule issue. Found there to be two types of schedule, AHU schedule and the building master schedule. Further investigation found the building master schedule to be empty and the AHU schedule is normal. Found that the schedule was set to look at the building schedule that was missing. Icon logic changed the schedule setting so it looked at the AHU schedule and not the building schedule. Found all AHUs to start and work as normal. schedules issue now rectified.
MSA-DTAG | WA3728900 | Time and Date out on the custodial CCTV equipment. | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 14:00:00 | Pass | Checked PC and unable to get system to synchronise. Logged in as admin and repgrammed time server as file was being rejected by server. Setup screens for custodial and recreated layout.
MSA-DTAG | WA3729017 | Lvl 22 - Passage door between kitchen & office – door release fault | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Building | Doors (BU) | Sapio Pty Ltd | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-12-30 15:00:00 | Fail | replaced lock on Level 22 door. All up and running ok.Job completed.
MSA-DTWD | WA3728319 | Chiller 1 is not starting | Leederville Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 0 | CLOSE | 26 Oct 2020 | 2020-10-26 11:42:24 | 2020-10-26 13:30:00 | Fail | Accessed chiller and bms . No errors showing for chiller 1 or 2. Demand for cooling at 100 percent but no unit operation.Inspected physically chillers in plantroom.Found chiller 2 has end plates off condenser vessel by others and valves turn off.Chiller, pumps etc no2 isolated and tagged out.Chiller 1 showing flow innop evap side.Found incorrect duty as lead/lag chillers and causing chw2 pump to enable but no operation of chillers.Can Get duty to no1. Enabled chw pump and cow pumps. Chiller 1 into operation.Ensured pumps on auto and not manually as to be correctly run via chiller/water system settings.Both cooling towers operating for ccw.Chiller cycling to set 7 degrees and demand via fcu and ahu,s decreasing. Cooling occuring.
MSA-DTWD | WA3728346 | B30-31 wall Stops- Emergency stop buttons Broken | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-30 10:30:00 | Fail | Attended site and signed in. Located all E stops in class roooms. Spoke with facilities about class in use and got authority to be in class. Isolated power to workshops. Disconnected and removed e stops from walls. Installed blanking plates in place and wrote behind cover isolated e stops. Removed reset button and rewired to be automatic after power failure to reinstate. Re-energised power circuits. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3728405 | L block, Repair/replace faulty door lock on the entry doors east end of L Block | Midland Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-27 16:15:00 | Pass | repaired oval cylinder on main entrance door to L block
MSA-DTWD | WA3728422 | BLD 834, Training room 1- Burst water pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 10:30:00 | Pass | repairs to burst water pipe
MSA-DTWD | WA3728446 | main ground L/H entrance door Lock faulty to entry door | Armadale Campus - 145 Jull Street | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-26 10:30:00 | Pass | Door lock faulty LH front main entry.Lock repaired. Damaged keys replaced.
MSA-DTWD | WA3728505 | building 8, ground level, 8G31 - 1 faulty row of lights tripping RCD | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 09:15:00 | Pass | Attended site and signed in. Got keys from facilities. Located room 8g31 and found 1 row of lights tripping. Investigated light fittings and found 1 x faulty ballast causing lights to trip. Disconnect and removed faulty ballast. Supply and replace with new ballast. Checked out row of lights and found 4 x light fittings not working properly. Replaced tubes and starters. Tested all okay. Class lights all working. Signed out. Job complete
MSA-DTWD | WA3728632 | K004 faulty door closer broken and leaking | Balga Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 11:00:00 | Pass | Supply and install new heavy duty door closer
MSA-DTWD | WA3728639 | K006.3 ants infestation crete area | Balga Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-28 13:50:00 | Pass | Sprayed all external perimeter for ants with Fipronil @ .6% and also with ant granules
MSA-DTWD | WA3728707 | Recetpion- Ladies toilet seat is damaged | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-02 12:30:00 | Fail | Complete
MSA-DTWD | WA3728715 | Tower block, carpet in both lifts is lifting & trip hazard | West One Services | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-12 13:00:00 | Fail | Supplied and installed carpet as requested by site
MSA-DTWD | WA3728754 | Grounds, Re-Tic Lawn sprinklers not spraying | Joondalup Kendrew Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-02 15:00:00 | Fail | Investigated faulty and found the solenoid wire for station 11 was faulty, located and used a spare wire to fix fault. Replaced a couple of broken sprinklers.
MSA-DTWD | WA3728808 | T, U and V Block - issue with air-con software (BMS) | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Icon Logic Pty Ltd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 13:00:00 | Pass | Directly connected to EC-BOS and found Web server and Daikin gateway online. Web graphics issue related to campus network. Resolved the issue with IT department. Implemented automatic Daikin gateway software reset in case of dropping offline.
MSA-DTWD | WA3728912 | Block F, Various locks faulty, see notes below | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-30 16:25:00 | Fail | job completed - replaced locks
MSA-DTWD | WA3728922 | Air con Plant room - no cooling, possible BMS issue | West One Services | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Precise Air Group | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 09:00:00 | Pass | Water pump siezed, previously quoted back in August now needs replacing as it is holding out 1 chiller
MSA-DTWD | WA3729018 | S Block Lab S1.- Fume Cupboard # 2 & 3 the GPO’S are not working. | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-30 08:30:00 | Fail | Attended site and signed in. Located S block, found 3 x fume units on back wall. Tested outlets on units and no power. Checked out switchboards and RCDs. All have power. Turned on fume systems and awaited the, to start up. Found unit 2 to not turn the outlets on when running. Pulled the control circuits apart and found connection terminal on the pcb and press buttons to have come off the board. Re attached and reset the unit. Awaited to restart and all outlets working correctly. Tested all okay. Put unit back together. Signed out. Job complete
MSA-DTWD | WA3729031 | S Block, Water fountain is cloudy | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-03 12:15:00 | Fail | Complete
MSA-DTWD | WA3729054 | Room F 59, F Block Ceiling mounted A/C control panel display white out | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-27 11:00:00 | Pass | Arrived on site signed in, checked in with Dennis. Gained access keys. Went Room F59, class in room. Located switch board. Gained authorisation from lecturer to access aircon. Gathered ladder and required tools. Checked controller found White screen, unattached controller found loose wiring. Isolated and locked out until. Refastened wiring retested all ok. Cleaned up Work area, completed toolbox and signed out.
MSA-DTWD | WA3729089 | Room Q016 - faulty GPO | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 11:00:00 | Pass | Attended site and signed in. Located q block and supposed faulty gpo. Found that rcd was tripped. Investigated further and found blown up aircon isolator. Replaced isolator with New and tested. All ok. Job complete
MSA-DTWD | WA3729104 | F block, FG11 workshop - AC3 Supply Air Fan is very noisy. Doesn’t sound good at all | Carlisle Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-11-23 11:55:00 | Fail | Travelled to site and signed in. Located Ahu 3 in the F block plant room. Found that bearings had failed causing damage the shaft. Bearings and shaft. Braf to be created.Ronleys visit 1 - remove n repositon and replace bearings on shaft.Ronleys visit 2 - fan bearings and pulley replaced.
MSA-DTWD | WA3729111 | M block, Tiling workshop - Exhaust fan not working in the tile cutting room. | Balga Campus | GMP-BR | Building | General Building (BU) | Ronley Holdings Pty Ltd | 2 | CLOSE | 26 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 11:30:00 | Pass | Exhaust fan and exhaust system inspected and found to be not suitable for the application. Defects Report to be submitted.
MSA-MRWA | WA3728954 | Investigate why DHWU 2 keeps going into lock out. | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 13:20:00 | Pass | Investigate/tested DHWU 2 that was locking out.No issues found at the moment.
MSA-MRWA | WA3728956 | Solar hot water pump not working please investigate and remediate. | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Oct 2020 | 2020-10-27 17:00:00 | 2020-10-27 12:30:00 | Pass | Checked and investigated solar pump not working.sensor leak faulty.This will be replaced on a different work order.
MSA-DCA | WA3729277 | Glass Auto Door is not responsive | King Street Arts Centre-Main Building-Ground Floor-Corridor - Murray Street Entrance | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 11:15:23 | 2020-10-27 10:11:00 | Pass | Checked door found no fault. Reset unit and tested all good. A400350203
MSA-DCS | WA3729221 | front door is not locking | East Perth-Main Building | GMP-BR- HO | Carpentry | Materials (CA) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 10:06:57 | 2020-10-27 09:45:00 | Pass | Tested Door Strike amd schedule. Everything is fine. Tested break glass. Needed to be reset. I bypassed schedule and door locked. I unbypassed schedule before leaving
MSA-DCS | WA3729243 | Hakea Prison Control Room - PDA System not working properly | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 06:24:05 | 2020-10-27 10:00:00 | Pass | Slow response and Comms errors on Slave. Fixed Comms issues and the lagging with the Master PC. Tested ok. Programmed 3 spare duress transmitters to replace faulty transmitters 068, 231 and 239.
MSA-DCS | WA3729281 | Unit 3, B & D Room- Program room door appears to be jammed | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 27 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-28 15:00:00 | Fail | Service, replace bolt throw and spindle.
MSA-DCS | WA3729290 | CCU, Cell H9- Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 07:31:40 | 2020-10-27 14:45:00 | Pass | Replaced the faulty cell call with new, job completed
MSA-DCS | WA3729291 | Unit 6, Cell A18- Main lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 07:33:45 | 2020-10-27 12:00:00 | Pass | Attend site. Repaired lock by replacing worn component. Normal function restored.
MSA-DCS | WA3729301 | Unit 6, N Wing - Ventilation System not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 27 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-02 15:00:00 | Fail | Replaced belts and tested operation. All ok
MSA-DCS | WA3729309 | Bakery - Alarm going off in freezer tempertaure up to 4.7 degree | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 11:47:09 | 2020-10-27 12:00:00 | Fail | Checked over freezer found indoor coil iced up, manual on defrost heaters and check if working ok all ok,found drain blocked cleaned out drain and drip tray, after system deiced started up and tested all running ok at present.
MSA-DCS | WA3729354 | Door 1 at the gate house is unable to be opened without the button been pressed in pod | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 12:28:45 | 2021-01-12 10:30:00 | Fail | Gatehouse Door 1, Custodial electric strike replaced by Prison officer locksmiths. Replacement Electric strike obtained from site critical Spares Cupboard. New strike delivered to site today.
MSA-DCS | WA3729394 | External gardens CVP tripping & making noise - see notes | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 08:55:06 | 2021-01-19 14:00:00 | Fail | 28-10-2020, Technician checked fault and found irrigation storage tank control floats were faulty, both new irrigation pumps are working well.A BRAF to be provided for the replacement of the faulty floats.
MSA-DCS | WA3729410 | MPU (8) - M20 cell has no water supply. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 09:00:49 | 2020-10-28 15:00:00 | Fail | Nill
MSA-DCS | WA3729581 | Please hang curtains in rooms where they're left & labelled | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Midolo Building Services | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 14:30:39 | 2020-10-27 14:30:00 | Pass | CURTAIN FITTINGS INSTALLED & CURTAINS HUNG
MSA-DCS | WA3729583 | gate control MDAS transponder 4 BUS3 faulty - SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2021-09-01 13:00:00 | Fail | Every link between transponder to first receiver, then receiver to receiver checked on bus 3 throughout the industries buildings, vegetable prep, maintenance and grounds keeping shed. The last leg of the link to ground keeping shed was tested as partial short circuit. Cable nearby the receiver in the ceiling of the grounds shed was found eaten in half by rodents. Cable repaired and re insulated. Bus 3 fault is no longer on system. PDA test conducted in industries carpentry and accuracy confirmed within 1 metre of accuracy.
MSA-DCS | WA3729590 | unit 1 kitchen doors flywire doors 4 locks are faulty and please check the rest | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 14:45:00 | Pass | replaced 4 x Security Screen door locks on Kitchen Doors Unit 1 - Pods 2,3,6 & 7Repaired strike on Pod 9 Checked remaining security screen door locks - will discuss further action regarding these .
MSA-DCS | WA3729597 | kitchen work area Dishwasher not working power is at machine - see notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 14:45:15 | 2020-10-27 14:00:00 | Pass | 27/10/20Arrive at site to check dishwasher not working, staff advise sometimes doesn't fill and they have to pour water in manually. Check over all components and clean up as much as possible. No signs wet equipment although unit quite old and signs of corrosion. Check all switches and safety limits, fill and test all ok. Possible pressure switches or door switches faulty but all working well at this time.
MSA-DCS | WA3729612 | Programs rooms 3/4- auto boil leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-29 10:00:00 | Pass | Replaced tap adaptor fittings/ retubed and replaced Zip filter
MSA-DCS | WA3729669 | A Wing, Cell 5- Water constantly running in toilet | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-04 10:00:00 | Fail | Complete
MSA-DCS | WA3729685 | main building ground heater in hall overheating & frame is distorted - see note | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-26 12:30:00 | Fail | Complete
MSA-DCS | WA3729700 | visits female visitors toilet leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-28 14:30:00 | Pass | COMPLETED
MSA-DCS | WA3729711 | Gascoyne, Kitchen 1 - stainless steel drawers are broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-09 10:00:00 | Fail | Attended site and assessed what repairs where required.Removed damaged drawer runners and sourced new ones.Re attended site and installed new drawer runners.
MSA-DCS | WA3729763 | Investigate Gymnasium Floor for Termites | Casuarina Prison | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-03 08:35:00 | Pass | Treated Gymnasium Floor For Termites.
MSA-DCS | WA3729778 | Gascoyne, Main living area - aircon not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-28 16:00:00 | Pass | Investigated and repaired evap in Gascoyne
MSA-DCS | WA3729786 | Interview room 3 door sets off main alarm when opened | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-27 15:00:00 | Pass | Setup arming after 2hrs as 120 minutes. Setup autoarm.
MSA-DCS | WA3729827 | Provide concrete risers and lid with gatic inserts to pit at Unit 3 | Casuarina Prison | SPA-BR | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-29 10:46:00 | Pass | Provide concrete risers and lid with gatic inserts to pit at Unit 3
MSA-DCS | WA3729857 | Pathway way lights excavation and shoring works outside unit 3 | Casuarina Prison | SPA-BR | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2021-01-06 14:42:00 | Fail | Investigate faults in lights as quoted
MSA-DCS | WA3729860 | PTZ 12 has no pan or tilt | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 13:31:39 | 2020-10-27 16:00:00 | Pass | Rectified and fixed the issue from DVM, tested ok and working. Job completed.
MSA-DCS | WA3729861 | Unit 2, B wing corridor light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-29 15:00:00 | Pass | Investigate and replace unit 2 corridor light
MSA-DCS | WA3729916 | Medical Centre prisoners toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-30 09:00:00 | Pass | Unblocked drain and plunger to clear
MSA-DCS | WA3729917 | Crisis Care, kitchen- Regi oven not heating up | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-05 09:00:00 | Fail | Repaired regi oven
MSA-DCS | WA3729927 | Unit 5 D wing cell 3 Toilet won't flush. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 09:30:00 | Pass | Nill
MSA-DCS | WA3729928 | Fluro Light globe flickering above SO Visits desk | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 08:30:00 | Pass | Repaired faulty lights in SO visits office
MSA-DCS | WA3729931 | Unit 14 - A6 inspect / repair Cell A 6 main door lock. - see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 12:30:00 | Pass | Service main lock and adjust strike.Key Bunch 108 & 109 have worn key and require replacement via security.
MSA-DCS | WA3729950 | front gate master control pod Monitor screen Blank | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 12:00:00 | Pass | Rectified and fixed the fault on ebi ws monitor GH, job completed.
MSA-DCS | WA3730033 | Camera PTZ3 has lines across the monitor and goes on and off. | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Oct 2020 | 2020-10-28 17:57:12 | 2020-10-29 13:53:00 | Fail | Attended and test camera functions all back to normal. Job completed.
MSA-DCS | WA3730034 | Unit 6- Staff toilet area behind managers office is burst and flooding | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 21:57:41 | 2020-11-12 15:00:00 | Fail | 27,10,20 Plumber attended site, tempery fix cold water supply pipe work in duct.Waiting on access to replce pipe work
MSA-DCS | WA3730036 | Unit 2D has no power and keeps tripping. | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 27 Oct 2020 | 2020-10-27 22:09:08 | 2020-10-27 21:30:00 | Pass | Tested circuit, kitchen overloaded, educated and reset power
MSA-DFES | WA3729499 | ground 27-engine room Engine Room Bay 1 Exhaust Fan Baffles broken away from ducting - see notes | CFRS Midland | GMP-BR | Electrical | General Electrical (EL) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-27 15:30:00 | Pass | Repaired and re-attach engine room fan baffles
MSA-DFES | WA3729523 | Below ground water pipe has burst/leaking | CFRS Malaga | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 15:15:00 | Pass | remove damaged blue line tee, supply and install new blueline tee
MSA-DFES | WA3729897 | Lvl 1, Hallway near Reception - 1x light globe is not working | South Metro Regional Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 11:15:00 | Pass | Located 2 reportedly flickering lights in hallway. One light was out and damaged. We replaced all 4 globes to ensure the job is completed. Notified staff and left site.
MSA-DFES | WA3729925 | G Floor, Broken Retic. (Check all sprinklers and system timings) | DFES Cockburn Emergency Services Complex | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 06:30:00 | Pass | Dom Coniglio attended on 29th Oct and replaced retic fittings
MSA-DFES | WA3733240 | RETROSPECTIVE WORKORDER - BYPASS ON ZONE 18 APP BAY 1 FRONT ROLLER DOOR-DO NOT ATTEND | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 23:07:00 | Pass | Despatch Comments:*** INTRUDER ALARM ***BYPASS ON ZONE 18 APP BAY 1 FRONT ROLLER DOORPatrol Resolution:PYPASS ON ROLLER DOOR NO KEYS EVERYTHING IS SECURE CLEARED BY DARANSite Inspection / Departure:
MSA-DTAG | WA3729741 | 1903 ground Airconditioning in Associate to Justice Mitchell office not working | Supreme Court | WSM-BR-SITE | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-28 15:00:00 | Pass | Pick up fan motor assembly from supplierAttend site, bring all equipment and tools to roofTest for isolation.Dismantle unit and remove condeser fan and roof of unit to access indoor fan.Disconnect electrical wiring to motor.Unbolt fan assembly and remove.Install new fan assembly Connect electrical wiring Reassemble unit Deisolate and test operation, AC is working as normal.Check temp in room and found to be dropping.Clean up area and remove all gear from roof.
MSA-DTWD | WA3729325 | Hot water urn – no water, see notes below | Armadale Campus - 145 Jull Street | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-27 10:24:00 | Pass | Cleared scale build up Rheem A40191352E Staff Kitchen
MSA-DTWD | WA3729412 | A Block, Room A310- Fume cupboard 4 not working | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 10:00:00 | Pass | Accessed area.Found airflow fault to fume cupbrd 4 upon operation.Rooftop plantroom plant equiptment isolated. Protection cage removed and parts inspected. Found grub screws loosened causing misalignment of pulley on taper. Rectified threads hold. New drive belts installed, aligned and tensioned. Unit tested once rectified and fume cupbrd no fault downstairs. Unit exhausting fumes as req
MSA-DTWD | WA3729420 | Block 12, Room 12G1- Faulty DAIKIN cassette A/C | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-29 14:30:00 | Fail | Cleaned facier of casette
MSA-DTWD | WA3729453 | block 8, ground level, ladies toilet - Water leaking from rear of bowl | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-27 12:51:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3729460 | Block 10, 1st Floor, Male toilet- Water leaking from under sink | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-27 12:56:00 | Pass | Fix leak under sink
MSA-DTWD | WA3729553 | Block 6C, Bricklaying - Lights not working in Tiling room | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-30 15:30:00 | Pass | Attended site and signed in. Located tiling area in block 3. Found poor lighting and only some working. Disconnect and removed old lights. Supply and replace with new led fittings. Replaced lamps and starters in entry light fitting. clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3729585 | E Block, Kitchen E30- water leaking through ceiling | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-28 14:45:00 | Pass | Call back on roof leak
MSA-DTWD | WA3729625 | O block Reticulation bore pump is tripping out on low level | Balga Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-28 17:00:00 | Pass | Tested bore pump, found low level probes stuck in probe conduit, clean probe and reinstalled. Set discharge valve to provide the correct back pressure.
MSA-DTWD | WA3729628 | Student Services Offices- Air Con does not have air flow | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 15:00:00 | Pass | Adjusted thermostat setpoint and removed diffuser blockage
MSA-DTWD | WA3729636 | C Block, CG09 Technician’s Workshop- Broken plug on metal lathe | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 15:30:00 | Pass | Attended site and signed in, completed JSA, inspected cabling, replaced plug and socket. Tested to see if machine works. **job complete**
MSA-DTWD | WA3729643 | L1 north wing outside rear door to cafe Repair CCTV camera above canteen entry - North Wing external | Mount Lawley Campus | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 09:00:00 | Pass | 28/10/2020, 1400-1500There's a vent In front of the camera. Need to extend coax and relocate 1.5m to the right in conduit. Extension ladder 2techs because of traffic 1.5 hours approx30/10/2020, 730-900 (two techs)Reloacted camera 2m to the right with conduit
MSA-DTWD | WA3729684 | Lvl 2, Room A252- faulty electrical circuit | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-02 08:00:00 | Pass | Attended site, located room, inspected fault found to be nothing, got in contact with FM, said it was completed by insight electrical. Packed up and left **job complete**
MSA-DTWD | WA3729755 | E-Block restaurant kitchen basin spray hose from wall leaking | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 15:50:00 | Pass | COMPLETED
MSA-DTWD | WA3729765 | E-Block Room E71 the Combi oven will not come on, has a heat fault in the water jacket | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 11:30:00 | Pass | Completed 28/10
MSA-DTWD | WA3729772 | ground creche Temperature requires re setting - see notes | Armadale Campus - 145 Jull Street | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-05 14:45:00 | Fail | Reset hp trip on unit-landl9rd contractor will carry out other repairs
MSA-DTWD | WA3729789 | Bld 822, Flat D room 7 - Snapped window sash cord | Muresk Institute | GMP-BR | Building | Windows (BU) | Lee Carpentry | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-28 09:30:00 | Pass | Job completed - fixed top sash
MSA-DTWD | WA3729808 | Room F 61, F Block- Left side timer/light switch faulty, switching off after about 15 minutes | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 27 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 15:30:00 | Pass | Attended site and signed in. Got keys from site facilities. Located F block room 61. Found switches on wall. Indicator lights to opposite for a start. Turned lights on and awaited time out. Front lights turned off in approx 10 minutes. Removed switches from walls and checked out. Reprogrammed both switches to work the same at 2 hours from when pressed. Awaited to ensure they don’t turn off after short amount of time. All okay. Signed out. Job complete
MSA-DTWD | WA3729952 | E block E74 Kitchen – Loose Faucet on hand wash basin | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 27 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-28 12:00:00 | Pass | Fix taps e74
MSA-DTWD | WA3729959 | Level 3, Male toilet - Faulty detector 36, Zone 15 | Perth Campus B6 | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 17:10:00 | Pass | Level 3 Male Toilet Zone 15 D36 went into alarm from works being undertaken. Replaced dirty detector, reset panel. Fault did not reappear.
MSA-MRWA | WA3729940 | Main entry gate malfunctioning please investigate and remediate. | Western Vent Building-Main Building | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 17:47:00 | Pass | A40029457K - Inspected gate and found to be stuck open. Found R/H cable loop to ram broken. Replaced loop set up and tested all ok at time of test.
MSA-MRWA | WA3729954 | Remediate blown globes. | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 27 Oct 2020 | 2020-10-28 17:00:00 | 2020-10-27 15:30:00 | Pass | Attended site and signed in. Awaited facilities to give us access. Went to level 1 and counted up 10 x lamps out. Advised staff that these lamps have become hard to get a hold of and expensive. Site checked their stock cupboard and found they had a few left. Happy to use to get these lights going. Replaced 10 x lamps to foyer lights and got all lights working. Packed up and clean site. Dispose of lamps into recycle bin. Signed out. Job complete
MSA-DCA | WA3730533 | glass door on sign to be removed and made safe | King Street Arts Centre-Main Building-External Area-External Area - North - Murray Street | GMP-BR | Signage | General Signage (SI) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-28 16:15:00 | Pass | Remove rust damaged door & make frame safe
MSA-DCA | WA3730539 | front of Art Gallery loose paving out front of art gallery | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Paving & Roadworks | Paving (PR) | ICS Australia | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-03 08:00:00 | Pass | Two site visits to reinstate sand around loose pavers.
MSA-DCA | WA3730565 | right hand side of main door damaged water pipe has been pulled away from fixings -see note | PICA-Main Building-External Area | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-29 15:27:00 | Pass | Installed new valve and capped it off. Apparently that water pipe wasn’t feeding anything: therefore the pipe has not been reconnected to the original pipe. David ad.
MSA-DCS | WA3730239 | Attend site and eradicate spiders | Melaleuca Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 28 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-05 10:40:00 | Fail | Carried out a service for spiders at Melaleuca Prison. Residually Sprayed the full external perimeter of all admins andcommon buildings as well as spot treating all other spider activity. Could not spray around the units due to prisonersbeing out on recreation, etc. Its recommended that this treatment is carried out on a quarterly service. It's alsorecommended that the service takes place on a Friday when all prisoners are locked down.
MSA-DCS | WA3730242 | Near Zone one, Bee hive in bottle brush tree under drain- See notes below | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 07:26:47 | 2020-10-28 14:00:00 | Pass | Carried out a service for bees at Hakea Prison. There were reports of bees located in a drain around zone 1. Uponfurther inspection bees were located entering the drain through a stormwater pipe. Due to this the bees could not beremoved and had to be treated. Dusted the entrance point of the drain. It's highly recommended that the drain hassome form of mesh installed to avoid new bees returning in the future.
MSA-DCS | WA3730246 | Poultry- power keeps tripping | Karnet Prison Farm | SPA-BR | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Oct 2020 | 2020-10-30 17:00:00 | 2020-12-07 15:30:00 | Fail | Investigate poultry farm power fault. Found damaged cable underground. Requires replacement.Remove existing sub mains. Dig in and replace submarine. Upgrade switchboard.
MSA-DCS | WA3730255 | Assessments, Main Corridor- Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 28 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-02 09:29:00 | Fail | Found loose connection in wall switch which provides power to cooling stages. Repaired connection and test ran unit. All operational at time of departure
MSA-DCS | WA3730259 | Security Safe is making funny noise (have changed x2 on keypad) | Casuarina Prison | GMP-BR- HO | Security | Safes (SE) | Lock It Locksmiths | 2 | CLOSE | 28 Oct 2020 | 2020-10-30 17:00:00 | 2020-11-20 13:00:00 | Fail | Check safe keypad lock is slow to respond, Check with new batteries - Require parts.Replace lock and keypad
MSA-DCS | WA3730267 | Unit 10, Cells B4, B7, B11 & B13- Smoke detectors blocked | Hakea Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 28 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-30 13:42:00 | Pass | 30/10/20 BG MBAttended site for blocked smoke detectorsChecked vents reported to be blocked, found minor lint build up on grills but airflow satisfactory. Unit officers have instructed prisoners to clean vents in their relevant cells.
MSA-DCS | WA3730285 | Air Con is not cooling | Boronia Pre-release-AK19 - Library, Education Personal Development-Ground Floor | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-29 12:15:00 | Pass | Set the controller for 21*C and checked found OK.
MSA-DCS | WA3730287 | Front Gate, Fire Panel showing faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 08:14:47 | 2020-11-04 10:00:00 | Fail | Attended site and performed the following tasks;Waited 1 hour for escort-Unit 1 C/D 15/16 vesda fault latch after airflow fault. Reset fault as low airflow no longer present-Unit 1 B7 and B8 showing low airflow. Cleaned out pipes and sample points, fault cleared.-Unit 1 C15 showing low airflow, cleaned pipe and sample point, fault cleared-Unit 1 A/C 5/6 isolated fault. Removed isolation, fault cleared-Unit 1 C1 low airflow. Cleaned pipe and sample point. Fault cleared.-Unit 2 A/B cells 1/2 is showing a urgent fault valve closed on pipe 2. Unable to fix issue and believe the vesda unit is faulty. Recommendreplacement of unit as this model is obsolete. Have notified SO as to the issue.Kitchen defrost fridge missing fault. Requires new Coolroom notifier detector (FST 851) and 2 techs to replace (below and above ceiling)BG 29/10/20Picked up specialised cool room detector from officeKS BG 4/11Attended site and accessed roof space above cool room fitted and programmed new detect
MSA-DCS | WA3730301 | Unit 6, Cell 4- Exhaust fan in shower has dopped from ceiling | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 08:24:05 | 2020-10-28 11:00:00 | Pass | Replaced faulty exhaust fan
MSA-DCS | WA3730365 | Set up exclusion zone using temporary fencing & appropriate safety signage - see notes | Casuarina Prison | GMP-BR- HO | Signage | General Signage (SI) | Midolo Building Services | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 08:54:25 | 2020-10-28 11:00:00 | Pass | TEMPORY FENCING ERECTED
MSA-DCS | WA3730366 | Admin Office - Bad smell coming from Air Con system | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 08:58:03 | 2020-10-29 08:30:00 | Pass | Arrived on site and signed in, checked over aircond found no sign off any smell coming from systems,suspect may have come from fresh air coming in to airconds.
MSA-DCS | WA3730423 | Entry building Sally port door - gate not closing properly, not aligning at the bottom. | Bandyup Prison | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 09:40:50 | 2020-10-28 13:00:00 | Pass | 28/10/20Re-adjust limits
MSA-DCS | WA3730432 | Jeelia, Cell B2- Faulty light | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 10:30:00 | Pass | Replaced lamp and test ran ok. Test all lights in cell ok.
MSA-DCS | WA3730437 | Reception, VIP Cupboard- Faulty light | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 15:30:00 | Pass | Replaced blown lamps and test ran ok.
MSA-DCS | WA3730466 | Vesda faults on both A/C and B/D cells 15 and 16 both sides. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 10:04:44 | 2020-10-28 14:24:00 | Pass | 228/10/20 MBUnit 13 Vesda unit B/D cells 15/16 found to have low airflow on two pipes.Checked and vacuumed out pipework.Airflow levels returned to normal.Unit 13 Vesda unit A/C cells 15/16 found to have low airflow on pipe 4 and high airflow on pipe 3.Checked sampling points and vacuumed out pipework but Vesda still showing extremely low raw airflow on pipe 4 (less than 200).Have temporarily pushed out the airflow fault thresholds to keep unit from going in and out of fault.Will require two techs to return to site with spare sampling points. Recommend returning Vesda to factory settings, reprogramming,rebalancing airflow across all four pipes and normalising.22/1/21 MB JNInspect and clean all pipework and sampling points for Vesda serving unit 13 cells A/C 15/16.Good airflow readings for all pipes now established.Carry out ‘normalisation’ and returned system to normal working order.Also cleaned several other sampling points and pipework that were either dirty or deliberate
MSA-DCS | WA3730538 | A & C wing fan not working, have tried to turned on and off switch. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-13 12:30:00 | Fail | Replaced faulty ceiling fans in unit 4
MSA-DCS | WA3730542 | Gate house - hot water not working in Kitchen. | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 13:16:00 | Pass | Complete
MSA-DCS | WA3730553 | Unit 4, Cell D6 - No water in toilet, cistern has failed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 10:51:21 | 2020-10-28 13:00:00 | Pass | Replace spindle, and removed and washed out inlet valve due to sand debris
MSA-DCS | WA3730566 | Unit 1, Cell A12- Window is broken due to fire | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 10:56:33 | 2020-10-30 13:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3730571 | Unit 1, Cell A12- Bunk Stairs are burnt due to fire | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 11:01:00 | 2020-11-12 11:00:00 | Fail | DAMAGED STAIRS REMOVED & REPLACED WITN NEW
MSA-DCS | WA3730620 | Admin, Male Staff toilet- Right hand side basin, leaking tap - hot water. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-06 11:30:00 | Fail | Nill
MSA-DCS | WA3730666 | Administration - Staff toilet L/Hand toilet - cistern does not reseat. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-06 13:30:00 | Fail | Nill
MSA-DCS | WA3730698 | Gate house - Microwave D4 on out perimeter constant activating unable to clear | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Oct 2020 | 2020-10-28 16:12:39 | 2020-10-28 15:13:00 | Pass | Checked and repaired multiple microwave faults on perimeter.Found many nuance activation also caused by large amount of project activity.Tested OKJob Complete
MSA-DCS | WA3730707 | kitchen stove rear broken leg - See VSO Brennan when on site | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 12:15:00 | Pass | Found bottom plate and sides to be all badly rusted leaving it unrepairable.
MSA-DCS | WA3730711 | kitchen work area Sink tap damaged does not turn off - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 10:35:00 | Pass | Turned off water replacing top assembly
MSA-DCS | WA3730720 | Industries yard Wash dowe hose reel and hose leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 12:35:00 | Pass | Original hose was split In the middle replaced hose & reel with new
MSA-DCS | WA3730860 | Unit 1 House 2 day room reed switch missing | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-19 21:14:00 | Fail | Replaced missing reed switch
MSA-DCS | WA3730861 | Unit 1 House 5 Cell 1 reed switch missing | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-19 21:12:00 | Fail | Replaced missing reed switch
MSA-DCS | WA3730896 | Unit 4C, Pantry light is not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 13:30:00 | Pass | Replaced faulty pantry light
MSA-DCS | WA3730897 | Unit 4C, Toilet & Shower area, 5x exhaust fan | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 15:30:00 | Pass | Replaced 5x faulty exhaust fans
MSA-DCS | WA3730922 | Unit 2, A-B Wings Common Area - Water cooler not cooling | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-06 09:55:00 | Fail | Unit is chilling. Just not working efficiently. Thermostat is operating. Both initiating and turning off compressor. Heat exchange very dirty. May be causing long chilling period. Unit may also be undersized for up to 64 users.
MSA-DCS | WA3730923 | Unit 2 cell C10 leaking sink tap | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-09 15:03:00 | Fail | Replaced leaking cold water tap to basin( qtr turn).
MSA-DCS | WA3730924 | Kitchen, work area - oven is not working | Melaleuca Prison | SPA-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 15:20:35 | 2021-05-10 14:00:00 | Fail | Date - 30/10/20Make - RationalModel - SCC WE202Serial - E22SH14102427662Technician - PeteArrive at site to check oven not working coming up with comms error since being moved for floor works. Check all coms wires and seems ok. Take details to speak to tech support about a software update as next step before replacing circuit boards. Oven also takes a long time to boot up once power turned back on. Knobs also broken on all 3 ovens will require replacing.Barry would like an update on eta if not ready to come back early next week.Parts required1 x software update3 x dial knobsPC 20/11/20Arrive at site to fit parts and perform software update. Fit new knobs and test all ok. Attempt software update but still came up with coms error. Discuss with tech support over the phone and was advised to replace the main pcb and sd card and also obtain the repair file and instructions from techsupport@comcater.com.au - please email request with serial number. Parts requir
MSA-DCS | WA3730929 | kitchen work area Sink Waste pipes leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 12:10:00 | Pass | Replaced sink waste and refitted trap to kitchen sink.
MSA-DCS | WA3730980 | Entry building POD - main computer screens control has gone down | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Oct 2020 | 2020-10-28 20:17:35 | 2020-10-28 17:45:00 | Pass | Found pc turned off turned pc on and tested all ok
MSA-DCS | WA3746807 | RETROSPECTIVE WORK ORDER - Investigate and repair Urquhart D wing post incident - ATT 28/10/2020 | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Oct 2020 | 2020-11-03 17:00:00 | 2020-12-04 14:00:00 | Fail | Replaced instant hot water unit and replaced thermostat inside unit to be adjusted to 50-60 degrees
MSA-DCS | WA3746821 | RETROSPECTIVE WORK ORDER - Investigate and repair Urquhart D wing post incident - ATT 28/10/2020 | Banksia Hill Detention Centre | SPA-BR | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 28 Oct 2020 | 2020-11-03 17:00:00 | 2020-12-21 10:40:00 | Fail | 24 WINDOWS REGLAZED - SPIRAL BALANCES RE NEWED - CEILING REPAIRED & PAINTED - SEC FILM INSTALLED
MSA-DFES | WA3730850 | Repair Main Entry Cantilever Gate (as per quote #23927) | DFES Rescue Helicopter Base-Car park | GMP-BR | Security | Access Control (SE) | Go Doors | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-25 15:45:00 | Fail | COMPLETED
MSA-DFES | WA3730909 | Female Toilet in Change Room, Motion Sensor not working- further notes below | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-13 09:30:00 | Fail | Complete
MSA-DFES | WA3730917 | ground level, Locker room(hallway side)- light switch, the switch is loose & does not operate light | CFRS Perth | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 16:15:00 | Pass | CompleteAttended site and locked non working light switches in hallways and Coker room. Replaced and all in working order
MSA-DFES | WA3730928 | Garden - bore has stopped working | VFRS Mandurah | GMP-BR | Mechanical Services | Pumps (MS) | Dom's Total Grounds Maintenance | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 17:00:00 | 2020-11-03 16:00:00 | Fail | Work commenced 29/10/20.BRAF was then raised & approved & then works were completed on 3/11/20
MSA-DFES | WA3733243 | RETROSPECTIVE WORK ORDER - BYPASS ON ARMING Z18 REED SWITCH BAY 1 FRONT ROLLER DOOR - DO NOT ATTEND | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-28 13:33:00 | Pass | Despatch Comments:BYPASS ON ARMING Z18 REED SWITCH BAY 1 FRONT ROLLER DOORPatrol Resolution:EXTERNAL CHECK CARRIED OUT. STAFF CARS WERE PARKED ON SITE . PATROL DIDN'T FIND ANY STAFF PERSONS. ALL APPEARS SECURE. NO OFFENCE DETECTED.
MSA-DTAG | WA3730467 | Level 8 - Cameras not working,not connecting to server. | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 28 Oct 2020 | 2020-10-28 14:04:29 | 2020-10-28 13:30:00 | Pass | Cameras not working on Level 8. Switch in comms room non responsive. Hard reset on both switches and equipment, cameras are working again.
MSA-DTAG | WA3730500 | Rear car park fence has been tampered with to allow for access into car park. | Perth Children's Court | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 12:50:00 | Pass | job completed - Replace barbed wire from corner post. Remove old lacing wire from end post and re-tied.
MSA-DTAG | WA3730548 | Female Public staff toilet in custody control - toilet seat is broken, see futher notes below | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-28 15:24:00 | Pass | COMPLETED
MSA-DTWD | WA3730210 | C Block, Reception side- Disabled toilet is faulty | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 3 | CLOSE | 28 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-02 09:42:00 | Pass | Toilet leaking at inlet valve constantly running, when turned off at minitap that started to leak also. Replace inlet valve with new performa inlet and fit new minitap. Replaced flexi hose also as it was rusting (potential for burst hose and flooding).In order to change minitap had to locate isolation for bathroom, eventually found in the roof above the basin but there was no man hole for access.
MSA-DTWD | WA3730329 | G Block, Room GF23 Wall - Light switch broken | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 08:45:00 | Pass | Attended site, located access through staff doors. Signed in. Went to G block and doors all locked. Went back to A block and looked for cleaners. Got access from cleaners to G block. Found light switch tagged out. Disconnect and removed faulty light switch. Supply and replace with new light switch. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3730356 | Lvl 1, Room A101- Tap not working | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 13:32:00 | Pass | Installed new taps and modify pipework
MSA-DTWD | WA3730495 | E-Block, ground level, restaurant kitchen - trolley bay, to be re- painted | Joondalup Kendrew Campus | GMP-BR | Painting | Internal (PA) | AWB Co. | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 09:00:00 | Pass | No photos to provide, attend site, sign in, find location, start preparation and set up work area advised that works can not proceed Pack up work area and sign out
MSA-DTWD | WA3730563 | E002 - white ant activity requires attention | Balga Campus | GMP-BR | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-18 13:30:00 | Fail | Inspected termite bait bar - no activity.Topped up distilled water into bait bay.
MSA-DTWD | WA3730564 | C Block, Zip Unit - no hot water | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-28 16:35:00 | Pass | Replaced faulty hot pump
MSA-DTWD | WA3730572 | B block L3 female toilet burnt out hand dryer has been tagged out | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 14:45:00 | Pass | Replaced faulty handryer .job completed
MSA-DTWD | WA3730585 | A Block, Opposite A350.1 Male Toilet - Repair Tap | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-25 09:45:00 | Fail | Complete
MSA-DTWD | WA3730597 | A block L1 A115 Filter on Tap in student services requires changing | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 12:30:00 | Pass | Complete
MSA-DTWD | WA3730867 | A Block, Room A346- AHU 1 ..3..5 VSD communication error on BMS | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 3 | COMPFIN | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-04 00:00:00 | Pass | works completed - Work order closed out at $0 cost
MSA-DTWD | WA3730893 | B block L3 female toilet cistern constantly leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 15:37:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3730908 | S block fault with the RO Unit in Science | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | IBIS TECHNOLOGY | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 14:30:00 | Pass | Replaced exhausted RO membrane
MSA-DTWD | WA3730911 | Hall 831 - Gully trap leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 28 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-28 17:30:00 | Pass | Job completed - clear blockage to sewer main
MSA-DTWD | WA3730950 | Print Workshop, Level 1- Repair fallen drain grade | Perth Campus B4 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 28 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-30 11:00:00 | Pass | Found stormwater drain in front of roller door to be damaged - took measurements for replacement as will be unable to repair. Went back to PFM as best a plumber look after this.
MSA-MRWA | WA3730470 | Toilet is blocked | Heavy Vehicle Services-Main Building-Ground Floor-Toilet-Disabled-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 16:35:00 | Pass | Unblocked cubicle in the disabled toilet
MSA-MRWA | WA3730972 | Fire indication panel - false alarm please reset fire indication panel | Traffic Operations Centre-Main Building-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 28 Oct 2020 | 2020-10-28 20:04:12 | 2020-10-28 17:30:00 | Pass | Attended site & de-isolated VESDA in Conputer equipment room.Reset SIP in valve room zone 1.De-isolated zone 227 on MFIP OK.
MSA-DCA | WA3731213 | Electronic lock on door and door is not operating correctly | State Library of WA-Main Building-Ground Floor | GMP-BR | Building | Doors (BU) | Schneider Electric Australia Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-29 17:00:00 | 2020-10-29 14:00:00 | Pass | Repairs to door
MSA-DCA | WA3732524 | Latch on door between bar and bar store broken. | Subiaco Arts Centre-Main Building-Level 1-Bar Area | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-10-30 13:30:00 | Pass | Carried out repairs to door latch - Mechanism now operational;
MSA-DCA | WA3732539 | Aircon - not functional | Subiaco Arts Centre-Main Building-Ground Floor-Ticket Box Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-02 16:00:00 | Pass | Test unit. U2 fault. Found previously looked at and quoted for replacement of PCB cards. Recommend replacing the outdoor fan motor also.
MSA-DCA | WA3732584 | Door faulty - door seems to have dropped | Perth Cultural Centre Precinct - Cleaners Store and Distribution Room-Ground Floor | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-30 10:11:00 | Fail | Door repair was not completed due to BRAF declined.Technician visited site on first visit but was unable to repair door and so Glazing subcontractor scoped and priced works for a new door. These works have been declined and so problem has not been resolved.
MSA-DCA | WA3732683 | Studio Underground Auditorium - Emergency Exit signage light is out | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2 | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-03 11:00:00 | Pass | Faulty exit replaced with spare ken had in workshop.
MSA-DCS | WA3731144 | Kitchen, Rational Oven – Temperature probe broken | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 1 - Kitchen Area | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 29 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-03 13:05:00 | Pass | Replaced Meat Probe & tested ok.
MSA-DCS | WA3731160 | Admin, Visits- Aircon is not running - error code appears | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 29 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 12:00:00 | Pass | Investigated admin visits AC. Repaired AC, replaced cpntactor. Works good
MSA-DCS | WA3731180 | Admin, Male toilet- light is broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-30 13:30:00 | Pass | Replaced broken lights in toilet with new LED ones, test ran ok.
MSA-DCS | WA3731197 | Kitchen- Bromic freezer, Fan not working. | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 1 - Kitchen Area | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 29 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-29 15:30:00 | Pass | Replaced the condenser fan motor.
MSA-DCS | WA3731218 | Unit 2 - B & D Wing door for B/D in unit 2 is catching on the door frame as it closes. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 07:59:33 | 2020-10-29 10:30:00 | Pass | Re install and repair edge capping.
MSA-DCS | WA3731221 | Kitchen, Fridge Door No 4 is damaged | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2021-04-16 11:00:00 | Fail | Door replaced by sub contractors. All ok
MSA-DCS | WA3731226 | Kitchen- Rear grill supporting nib wall damaged as such grill door frame is loose | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2021-02-18 14:30:00 | Fail | NEW POLYCARBONATE PANLE FIRRTED TO REAR GRILL
MSA-DCS | WA3731231 | Outpatients Area pharmacy air con not working at all | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-10-29 10:14:00 | Pass | Checked over aircond found system running ok,checked setpoint, found set on 24.5 degrees, changed to 22 degress, both stages started up and all running ok at present.
MSA-DCS | WA3731240 | Unit 7 - C12 Shower tap broken and water running self care | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-10-30 16:00:00 | Pass | Nill
MSA-DCS | WA3731254 | Unit 2 - Court Yard Water tap has broken away from mount and is leaking Unit 2 courtyard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 08:10:45 | 2020-10-30 10:30:00 | Fail | Nill
MSA-DCS | WA3731280 | Zone 8, perimeter fence is activating | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Oct 2020 | 2020-10-29 12:31:07 | 2020-10-29 13:00:00 | Fail | Caliberate the microphonics fence zone 8 due to false alarms. Job completed.
MSA-DCS | WA3731286 | Unit 1, Staff Lunch room medical cabinet- top lock jamming wont lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 08:40:02 | 2020-10-29 12:15:00 | Pass | Attend site. Repaired and serviced lock to restored normal function.
MSA-DCS | WA3731291 | Unit 2, A-B Wing Air-Lock- Vinyl Floor lifting trip hazard, see notes below | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 08:44:13 | 2020-11-02 20:30:00 | Fail | DAMAGED FLOORING REPAIR - AFTER HOURS
MSA-DCS | WA3731296 | Unit 2, C-D Wing Air-Lock- Vinyl floor lifting | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-02 23:30:00 | Pass | DAMAGED FLOORING REPAIRED AFTER HOURS
MSA-DCS | WA3731321 | Dairy packing door broken glass window | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2021-03-25 10:20:00 | Fail | new door fitted & painted
MSA-DCS | WA3731405 | Cameras at gate house are not showing obs cells | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Oct 2020 | 2020-10-29 18:09:33 | 2020-10-29 13:00:00 | Pass | Job complete
MSA-DCS | WA3731410 | Cell 3.10 - Cell call system not working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 10:11:59 | 2020-10-30 12:30:00 | Fail | Call LED stuck on in cell. No call on system to try and clear, unable to make a new call. Replaced intercom, LED issue had cleared but still unable to make a call. Tested new intercom directly into the CI8A, call still not going through. Replaced CI8A. Tested cabling from cell to CI8A. Changed the name of the cell from 3-10 Punishment to 3-10 Transit cell as requested by U1 SO. Tested loud and clear in cell and in in control. Parts used:Austco CI8ACell Guard CI-CCRJ45 adapter AM-TB8RJ45Consumables
MSA-DCS | WA3731412 | PUR unit 4, - cable fault affecting PUR intercomms | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-29 17:00:00 | Pass | 44 connections related to intercom cabling not correct for required configuration. 22 devices removed for termination correction and reinstalled. Test ok
MSA-DCS | WA3731414 | intercom circuit board faulty (cell call TAG104) | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-10-29 12:00:00 | Pass | Identify and removed. Circuit board badly corroded and damaged. New unit sourced from MED prison stock. Replaced, programmed and tested as ok. IP conflict with server issue also resolved.
MSA-DCS | WA3731469 | F1 outter Perimeter sense - FAULT Fiber fault has changed to gate to open | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 10:42:22 | 2020-10-30 16:04:00 | Fail | Found outer perimeter would intermittently receive random comms faults. Monitored, cleaned fibres, traced fault to faulty fibre lead.Replaced lead and tested Ok.Job CompleteParts (SEME Stock):1 x 1M Fibre Lead.
MSA-DCS | WA3731526 | Kitchen, Back Passage - Back grill door lexan is damaged | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-12-04 13:30:00 | Fail | JOB ATTENDED ON ANOTHER WORK ORDER (WA3731226)- DOUBLE UP
MSA-DCS | WA3731550 | Unit 1, Cell C8- Judus hatch lock, key jams in lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 11:30:00 | Pass | Repair hatch lock and tighten cam screws.
MSA-DCS | WA3731590 | Bakery- D20 Dough divider, pin lock to the handle as the existing is heavily worn. | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2021-01-15 13:45:00 | Fail | 09/11/20Check divider Found handle pin worn and requires replacing as lid lifting.Power plug requires replacing as smashed and taped together Parts required:1 x sleeve 1 x rod1 x sleeve1 x handle12/01/2021Isolate unit Attempt to remove handle Top handle modified and screwed on Pin snapped off handle making constant turning able Requires new pin Cut old handle out and install new Unit still able to be used Requires pin and new plug tip Parts required: 1 x Pin (have sample) 1 x 4 pin 56 series plug15/1/2021Sign in Install roller back on mixer D20Found grub screw loose and handle wound upRemove asssmbly and calibrate height Drill into handle for grub screw to lock into position Drill through handle and install roll pin Insert roll pin through base of handle.Check with bakery manager, ok.
MSA-DCS | WA3731853 | Reset Centre- Sewerage smell in toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-06 16:00:00 | Fail | Nill
MSA-DCS | WA3732400 | Unit 5, external - faulty reticulation system requires repairs | Bandyup Prison | WSM-BR-SITE | Mechanical Services | Pumps (MS) | Pumps n Pipes | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-04 09:00:00 | Pass | VARIOUS BREAKS AND REPAIRS UNDERTAKEN
MSA-DCS | WA3732460 | Bakery- Berto Mixer Stabilization rollers are badly worn | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2021-02-12 15:00:00 | Fail | 05/11/20Check spiral mixerFound bowl rollers require replacing as seized and worn. Parts required:4 x bearings 2 x Thrust rollers2 x thrust roller pins4 x Hex pins11/02/2021Remove and replace rollers Adjust and calibrate Test unit ok.
MSA-DCS | WA3732471 | Bakery- Sortoriva 1 Mixer Stabilization rollers are badly worn | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2021-02-11 17:30:00 | Fail | 15/11/20Check spiral mixerFound bowl rollers require replacing as seized and worn. Parts required:2 x rollers2 x wheel pins2 x spacers11/02/2021Remove and replace rollers Adjust and test unit ok
MSA-DCS | WA3732475 | Bakery- Sortoriva 2 Mixer Stabilization rollers are badly worn | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2021-02-11 15:20:00 | Fail | 05/11/20Check spiral mixerFound bowl rollers require replacing as seized and worn. Parts required: 2 x rollers 2 x wheel pin2 x spacer11/2/2021Remove and replace bowl rollers Install and adjust Test unit ok
MSA-DCS | WA3732480 | perimeter number 15 and 25 not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 13:24:34 | 2020-11-11 13:30:00 | Fail | Replaced 3x perimeter lights
MSA-DCS | WA3732509 | unit 7 self care duress receiver is off line | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-13 15:00:00 | Fail | Job complete.Office stock used . (Bosch receiver )
MSA-DCS | WA3732521 | Unit 8, A11 & D3 - Cell calls not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 13:53:09 | 2020-10-29 15:30:00 | Pass | Fixed the fault from cell call point, tested working ok. Job completed.
MSA-DCS | WA3732530 | Stores Yard, Pot holes to be filled | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | AFD Contracting | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-02 10:30:00 | Pass | 02/11/20Repair pot holes
MSA-DCS | WA3732534 | Recreation- adjust timer for oval lights | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-10-29 16:30:00 | Pass | Reprogrammed timer for oval lighting
MSA-DCS | WA3732538 | Unit 9, A14 - Cell call faulty. Not receiving | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 14:08:22 | 2020-10-30 09:30:00 | Pass | Rectified the fault and replaced defective cell call, job completed.
MSA-DCS | WA3732551 | INF, Day Room- duress fault | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 14:30:50 | 2020-11-13 11:31:00 | Fail | Investigated multiple infirmary duress faults, traced cables, repaired faults and tested OK.Job Complete
MSA-DCS | WA3732564 | Karakin, C wing- Broken lower sash window Approx 450mm x 600mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-04 15:00:00 | Fail | SASH WINDOW RE GLAZED
MSA-DCS | WA3732565 | Visits Area, Visits-Non Contact area - Work Station failed - faulty | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-09 16:55:00 | Fail | Investigated and found existing workstation was obsolete and had aged. It was running Windows Vista 32bit. Obtained replacement workstation computer, display and other components. Installed, loaded software, configured and tested OK.Job CompleteParts (SEME Stock):HP Workstation24" DisplayConsumables
MSA-DCS | WA3732571 | Unit 14, Cell C11 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-02 12:08:00 | Pass | Nill
MSA-DCS | WA3732582 | 4D cell 3 light is damaged | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-02 10:00:00 | Pass | Replaced damaged light fitting with LED
MSA-DCS | WA3732600 | unit 6 control room Cell Call Display Not Illuminating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 15:07:16 | 2020-10-30 11:59:00 | Pass | Rectified and fixed the cell call LED display unit from officer pod Unit 6 and 7. Job completed.
MSA-DCS | WA3732628 | SOG base - admin female toilets is leaking and making noises | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 15:30:50 | 2020-10-30 07:20:00 | Pass | Replaced outlet washer
MSA-DCS | WA3732677 | Unit 2, rear service door, back of unit - timber door completely rotten | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 16:24:04 | 2020-11-24 12:00:00 | Fail | Supplied and installed new 2100mm x 820mm 40mm solid core door.Prime and paint new door colour to match existing
MSA-DCS | WA3732679 | Entry - hot water system for female staff showers is not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 16:26:38 | 2020-10-30 14:45:00 | Pass | COMPLETED
MSA-DCS | WA3732687 | : Electronic lock not functioning in Gatehouse – please meet SEME on site. | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-12-17 10:05:00 | Fail | Attended site, with electrician, removed locks on control room door and Sally port door for electrician to rewire. on removing the Control room lock discovered that the lock electronics are non functional, possibly due to the lightening strike which caused other issues. locks refitted as mechanically functioning.Returned to site to install new lock as per quotation.
MSA-DFES | WA3731306 | inbetween gym and kitchen male toilets urinal is overflowing | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 15:00:00 | Pass | Clear block urinal
MSA-DFES | WA3732379 | ground kitchen air con has stopped working, room gets overheated during meetings | Fleet Management Services - O'Connor Workshop | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-12-29 16:00:00 | Fail | Replaced all indoor pcb's and receiver. Ran and tested.
MSA-DFES | WA3732426 | Gym, Ground floor - Fluorescent lights in the gym have stopped working | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-11-03 11:30:00 | Pass | CompleteAttended site and located non working lights in gym and toilets found rcd to have tripped cause of faulty tubes and ballast replaced and all in working order
MSA-DFES | WA3732525 | lecture theatre exit ladies toilet basin is cracked around whole basin - see notes | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-26 11:00:00 | Fail | Replaced basin
MSA-DFES | WA3732553 | rear yard - Automatic sliding gate to rear yard u/s. | CFRS Wangara | GMP-BR | Building | Steel Fencing & Gates (BU) | Anvil Doors | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 14:45:00 | Pass | Attended Wangara Fire Station. Checked rear gate and found that the drive gear had come loose. Technician reinstalled the grub screw and refit the existing gear. The gate is now working correctly. Note- Service form was not signed off by client as they were called out on an emergency.
MSA-DTAG | WA3731333 | Lvl 11, Staff Kitchen- filter for cold water zip tap is faulty | Golden Square | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 14:20:00 | Pass | diagnosed and replaced filter checked system ok A40189279T
MSA-DTAG | WA3731334 | ground main entrance Auto switch controlling revolving door is not responding when keyed | Central Law Courts | WSM-BR-SITE | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-29 13:30:00 | Pass | Note IP number is 1002977 AGP revolver, arrived onsite and and checked the diagnostics LED’s which indicated the door was in remote lock mode , traced and found the BMS inputs to door and found all correct, checked operation of key switch through the PLC and found all ok. Further investigation and found lock micro switch faulty and repaired, carried out a full reset of the controller and tested operation, checked all safety’s and could not fault.Could not locate Programmed asset number
MSA-DTAG | WA3731354 | Courts 1 & 3 - Technician required to isolate FIP for vesda & smoke detectors - see notes below | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 29 Oct 2020 | 2020-11-05 17:00:00 | 2020-10-31 16:01:00 | Pass | Performed de-isolation of zones 1 & 3 for courts 1 & 3.System status displaying normal on departure.
MSA-DTWD | WA3731134 | A Block, Room A316- Fume Hood light needs replacing | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Precise Air Group | 3 | CLOSE | 29 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 14:00:00 | Pass | Accessed a316 lab.Test ran fume hood to show etc fan running but no lights to cabinet work area.Inspection and test shows lights to be of working condition.Operation of lights by switch shows no power to circuit but exh fan operating.Accessed rooftop plant area to inspect fume 5 hood parts.Mtr good and barrell.Control shows auto . All ok.Further fault finding shows control circuit fault to relays and contactor supply.Controller innop.Wiring fault rectified to per circuit.Isolator and switches now operating.Airflow lock out returned.Lights tested and airflow ok.
MSA-DTWD | WA3731190 | C Block East, Auto Door has a small proble with its keyed switch, see notes below | Mandurah Campus (formerly Peel) | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 29 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-29 10:15:00 | Pass | Inspected door and found key switch was faulty, replace Sk4 key switches, checked all fixings and sensors, tested door operation a number of times, all working fine.
MSA-DTWD | WA3731520 | E Block, Deli has a freezer that is not freezing | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-12-22 10:00:00 | Fail | Picked up required parts, attended site and signed in located system removed faulty controller and replaced with new, set parameters within controller and tested, left system all operational
MSA-DTWD | WA3732540 | BLD 834, Office- 2x faulty lights | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-02 15:00:00 | Pass | job completed - replace faulty lights
MSA-DTWD | WA3732560 | J block L1 dust extractor dust extractor has thrown the drive "V" belts - see notes | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-30 08:00:00 | Pass | J Block L1 dust extractor faulty. Check belts, found broken. Locate new belts. Return & install 4 x new belts. Refit covers, run system, all working correctly.
MSA-DTWD | WA3732570 | C block L2 C214 the aircon FCU not opening cooling valve | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-30 15:00:00 | Pass | Found the BacNet comms from the IG03 connected to the chiller and he IG03, connected to C block was down. It involved all Level 2 units not just FCU21. Checked through the live data points in the IG03 and found many faults. Power cycled the controller and found some faults cleared but some were intermittent still. Power cycled the chillers IG03 as well, also power cycled the L2 DDC. Re-built the devices and found that the comms came back online OK. Checked through all the logic in the config and found the units running OK, supply air temp for FCU21 reading at 11degrees. Turned unit back to Auto.
MSA-DTWD | WA3732585 | A block L2 corridor A214 Entry door swipe lock to A214 has failed | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Schneider Electric Australia Pty Ltd | 1 | CLOSE | 29 Oct 2020 | 2020-10-30 17:00:00 | 2020-10-30 14:30:00 | Pass | job completed - Attended site and inspected door fault.Found tha the door lock was faulty.Left site to collect new lock from supplier.Returned to site and installed new lock.Checked and tested door operstion.
MSA-DTWD | WA3732619 | A block, Level 1, A120 Cafe - Fault on alarm panel, Zone 20. Alarm is going off intermittently & | Leederville Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-30 11:00:00 | Pass | 30/10/2020, 930-1100Located device.Unable to locate expander device is connected to.Cable seems ok.Replaced sensor
MSA-DTWD | WA3732664 | level 2, Entry Foyer - Fire Panel in PreAlarm - will not cancel | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-03 12:00:00 | Pass | Re-Attendance requiredOn arrival detector in pre-alarm (optical Zone 20 Loop6 D107 “B307”)Would not clear pre-alarm. Inspected device for false alarm triggers- detector is high ceiling area and will require EWP.No visible cause for pre-alarm.Recommend replace detector as probable faulty detector (wireless optical)Spoke with client and they have informed me that on site EWP will be available tomorrow for access (may be possible with poles)Isolated device and set panel to normal- will require re-attending to replace detector and de-isolate. (Additional isolates on FIP due to false alarm from plumber works during the day- check with client if require de-isolation upon re-attendance)
MSA-MRWA | WA3731283 | Door is self-locking, when the door is closed | Jandakot Depot-Main Building-Ground Floor-Training Room 1-Kolbang | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 29 Oct 2020 | 2020-11-03 17:00:00 | 2020-10-29 10:30:00 | Pass | Replaced lever set
MSA-DCA | WA3732970 | External area- retic leak | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-03 12:30:00 | Fail | Check leak on Francis st garden beds (station 1). No leak to be found.
MSA-DCA | WA3733280 | Fire panel has comms & system fault, see note below | Shipwreck Galleries-Main Building-Ground Floor-Foyer | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 11:31:00 | Pass | Tech attended on 30th October at 11:40am to check out fault on panel showing comms and system faultElectricians required to attend on Monday 2nd November as fault could not be rectifiedThe EWIS at maritime has a faulty paging consoleTrusting/assume this is only issue quote sent to David de Villiers on 2nd November to supply and replace 1 x RPC, Labour, Test and commissionExclusive of any other system parts or labour that may be required if other cards are faulty
MSA-DCA | WA3733598 | Green Room AC not working, see note below | King Street Arts Centre-Main Building-Level 2-Green Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-12-03 11:55:00 | Fail | Works completed on WA3755735
MSA-DCA | WA3733720 | Art Gallery of WA - high temp alarm AC3 | Art Gallery of WA - James St | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 23:30:00 | Pass | After hours CALLOUT. Attended site. Contacted PROGRAMMED call centre for job start. AC 3 gallery 9 interior hi temp alarm. AHU controlling to BMS strategy. Reheat operating correctly. Heating and Chilled Water in ETS mode. Actual temp to sensor temp different. Sensor will need calibrating or replacement when controls tech in for next service.Alarm active but low priority. Gallery 9 not occupied or displaying any pieces.Closed job.
MSA-DCS | WA3732844 | Replace camera in gatehouse to key control | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 30 Oct 2020 | 2020-11-03 17:00:00 | 2020-11-02 16:00:00 | Pass | Attended site. Supplied and installed new camera in Gatehouse Side Exit Door. Updated license & commissioned camera, confirmed recording. Adjusted Gatehouse inner camera to Reception Area. Updated Gatehouse Salvo as requested.
MSA-DCS | WA3732979 | Unit 7, Cell E21- Faulty light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-03 11:00:00 | Pass | Repaired light
MSA-DCS | WA3732990 | Front Entrance, Kitchen- Hot Cold tap not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-10 16:00:00 | Fail | Leak fault - tray full of water.Dried unit and checked hottank, tubes and connections.Ran unit and monitored whilstin operation. All tests well. Ifproblem persists unit will needto be returned to workshop forfurther analysis.
MSA-DCS | WA3733180 | gate house monitor 4 is going blanks indigo vision has stopped working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Oct 2020 | 2020-10-30 16:52:42 | 2020-10-30 14:00:00 | Pass | Checked the power to the monitor and all the cable connections at the monitor and the PC. Restarted the workstation. Monitored through the day. Did not fail again.
MSA-DCS | WA3733184 | Concrete footpath between Reception & Obs Tower needs repair, trip hazard | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | Midolo Building Services | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2021-04-13 09:00:00 | Fail | ASSESMENT & ATTEMPT TO COMPLETE (LABOUR ONLY) - ADVISED TO CLOSE OFF - AS HIGH TRAFFIC AREA - IMPOSSIBLE TO COMPLETE - SEE ATTACHED
MSA-DCS | WA3733200 | Make safe light posts to front of Gatehouse in decking | Bandyup Prison | GMP-BR- HO | Building | External Walls (BU) | Schlager Construction Group | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-11-16 13:00:00 | Fail | Attended site and assessed works.Reattended site and secured external lights to the concrete underneath decking.
MSA-DCS | WA3733270 | INF (10) Disabled shower - Taps leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-10-30 12:00:00 | Pass | Nill
MSA-DCS | WA3733301 | Unit 4, tag #118 faulty intercom | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-11-19 09:27:00 | Fail | Cable was missing. Cable identified in ceiling and cavity and brought into intercom housing. Terminate, test and commission.
MSA-DCS | WA3733302 | Unit 4 - external zone E1 failed to alarm when hit | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2021-02-03 12:00:00 | Fail | Two tendedtechs attended site, tested fence sensivity and adjusted. Confirmed alarm activation on "Cut" perameter.
MSA-DCS | WA3733348 | zone 1 on the perimeter infrared beam coming up on monitor every 20 sec - SEME on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 10:56:42 | 2020-11-04 11:00:00 | Fail | Attended site and checked PE Beam for zone 1. Replaced zone 1 third stack from top. Reconnected new beam set and re-tested alarm activation. All tested and working ok. Job complete
MSA-DCS | WA3733354 | Unit 3, MMU- rear timber door to plumbing duct is warpped and unusable | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 10:59:45 | 2020-11-23 10:00:00 | Fail | Attended site and measured door to be replaced.Manufactured new 2140mm x 820mm x 40mm solid core door.Reattended site and fitted new door, painted to match existing colour.
MSA-DCS | WA3733360 | Unit 3, MMU- cell 3 - leaking spindle & stockcock is rusted | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 11:01:30 | 2020-11-02 09:00:00 | Fail | COMPLETED
MSA-DCS | WA3733365 | Unit 3, CCU, Cell 6- Plunger, washer and inlet valve faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 11:03:33 | 2020-11-02 10:00:00 | Fail | COMPLETED
MSA-DCS | WA3733366 | Unit 2, Cell A5- Tap spindles faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-16 11:30:00 | Fail | COMPLETED
MSA-DCS | WA3733368 | Unit 2, Cell D13- Tap spindles faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-16 09:45:00 | Fail | COMPLETED
MSA-DCS | WA3733369 | Unit 2, Cell D10- Bunk light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-19 07:30:00 | Fail | Replaced light switch in bed light
MSA-DCS | WA3733537 | Front Gate,Key control - Key Bunch 17 stuck in key watcher | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 12:40:07 | 2020-10-30 13:30:00 | Pass | Attend Site. Reset and service unit to restore normal function.
MSA-DCS | WA3733558 | Unit 1 maximum all camera's in ob cells not working- Seme on site | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 13:01:58 | 2020-10-30 15:30:00 | Pass | Confirm that power outage had exceeded UPS duration. Set up monitors and PC to desired configuration once power returned.
MSA-DCS | WA3733631 | Unit 6, A1 - Faulty light when activated from inside cell | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-04 10:00:00 | Pass | Repaired light
MSA-DCS | WA3733655 | ISU B desk - someone has received a eletric shock (desk is metal based) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 30 Oct 2020 | 2020-10-30 18:20:27 | 2020-11-03 13:30:00 | Fail | Carried out tests on the electrical system involved in the report of electric shock to staff member.
MSA-DCS | WA3733659 | DDU Hi Vis strips added to steps - see notes | Hakea Prison | WSM-GR-SITE | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-11-19 11:45:00 | Fail | HI VIS STRIPS INSTALLED
MSA-DCS | WA3733660 | Mircophonics network has a redunancy fault | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-12-12 14:57:00 | Fail | Investigated senstar servers, net controllers and fibre network.Traced fault to two fibre optic faults. Replaced patch lead which was causing some intermittent data faults. Found fibre broken between unit 4 and temporary sally port. Identified spare fibres and restored data communication.
MSA-DCS | WA3733663 | DDU two globes need replacing. | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-11-03 09:00:00 | Pass | Repaired lights
MSA-DCS | WA3733666 | DDU Slip resistant rubber matting on wooden steps is worn | Hakea Prison | WSM-GR-SITE | Flooring | Rubber (FL) | Midolo Building Services | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-11-20 09:45:00 | Fail | new hi vis stair treads installed
MSA-DCS | WA3733679 | DDU Carpet repairs - it has “rippled” slightly, creating a trip hazard. | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2021-01-05 11:27:00 | Fail | ADVISED BY STAFF JOB CANCELLED - FULL REPLACEMENT OF CARPETS APPROVED INSTEAD OF PLANNED REPAIR
MSA-DCS | WA3733704 | Medical center external entry door - will not lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-03 09:45:00 | Pass | Attend site. Repair lock to restore normal function.
MSA-DCS | WA3733706 | Unit 16 - Fire alarm fault not able to reset | Casuarina Prison | WSM-MW-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 15:45:57 | 2020-10-30 18:03:00 | Pass | System still displaying 22 x flow faults requiring DLP fire contractor to investigate
MSA-DCS | WA3733723 | Banksia Hill Detention Centre-Block M Stores - Cell call system not working. | Banksia Hill Detention Centre-Block M Stores | GMP-BR- HO | Building | General Building (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Oct 2020 | 2020-10-31 20:45:02 | 2020-11-03 16:00:00 | Fail | Attended site and investigated the fault.Checked connections and wiring on cell call station CI-3210.Replaced faulty unit with another (critical spare supplied by SEME)Upload ACM files to node 5.Conducted test in Murchison.All back to normal and operational
MSA-DFES | WA3733186 | outside the access gate is not opperating intemittently - please check remotes | CFRS Armadale | GMP-BR | Security | Access Control (SE) | Go Doors | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-13 16:37:00 | Fail | (30/10/2020) - Work NoteFault Found: Attended site as per work request and found ants inside gate motor and inverter had failed. Replacementcontroller & keypad requiredDate onsite: 13/11/2020Start time: 14:21Finish time: 16.37(13/11/2020) - Work NoteWork completed:Install new controller and keypad to gate onsiteTested operationAll tested ok
MSA-DFES | WA3733188 | station engine room remote has failed and there is no spare | CFRS Armadale | GMP-BR | Security | Access Control (SE) | Go Doors | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 14:13:00 | Pass | Supplied and programmed 2 additional remotes.
MSA-DTAG | WA3733581 | L10 Fire damper vent in office area is jammed open – adjacent to compactors | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-21 12:00:00 | Fail | Pick up new actuator. Attend site. Access lev 10. Isolate fire control voltage to damper. Remove wall grill. Disconnect failed actuator. Cut down drive shaft to accommodate new style actuator, fit actuator and stroke operation. Install new junction box, connect electrical wiring. Test operation, working ok.
MSA-DTWD | WA3733044 | D3 Staffroom - Several ceiling light not working and delay in coming on | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-30 12:00:00 | Pass | Attended site and signed in. Located faulty light fittings in d block. Removed old tubes and starters. Replaced with new. Light still not working. Supply and replace ballast to light fitting. Light operates fine. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3733194 | F Block, F206 Male toilet- toilet cistern is not flushing. Flush mech seems to have an issue | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 09:10:00 | Pass | Realigned dislodged flushing mechanism, flushing as normal.
MSA-DTWD | WA3733198 | E Block, Outside/Opposite EG20- Nuisance tripping of RCD W1 in Switchboard E Block DB1 | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 12:45:00 | Pass | Attended site and signed in, completed jsa, inspected fault on circuit w1 DB1, did I.R test A-E 631M ohm N-E 493 both readings are a pass, completed push button test (pass), completed ramp up test tripping at 22.5mA (pass) (also completed test on other rcd and were tripping at exact same 22.5) , completed rcd injection testing( 0-180 =28.20 180-0 =29.7) , did an amp test with clamp meter 1.73a, flicked everything on and nothing would trip the rcd. No faults found
MSA-DTWD | WA3733227 | D block, Level 1 - blocked toilet | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 13:30:00 | Pass | Complete
MSA-DTWD | WA3733239 | E block, E500 workshop - Three phase GPO hanging off the wall in welding BAY 11. | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 10:30:00 | Pass | Resecured loose gpo in welding bay.job complete
MSA-DTWD | WA3733242 | E block, E107 classroom - The light switch is intermittent and require replacing (large switch plate | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 11:00:00 | Pass | Replaced faulty light switch in classroom.job completed
MSA-DTWD | WA3733265 | Zone 3, fire panel in isolation at the moment | Mount Lawley Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 30 Oct 2020 | 2020-10-30 13:58:57 | 2020-10-30 12:30:00 | Pass | Investigated fire alarm. Panel all clear now
MSA-DTWD | WA3733268 | Jobs and skills Centre- Blown fluros | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 09:15:00 | Pass | Attended site and signed, completed jsa, inspected work area, replaced 14x Fluros to job skill centre, tested lights to make sure all working. **job completed**
MSA-DTWD | WA3733271 | E block E500 ground GPO issue in Sheetmetal workshop. - see notes | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-02 12:15:00 | Pass | Tested 3phase outlet , checked and tightened all terminals tested. All working properly.job completed,
MSA-DTWD | WA3733305 | Level 2, Male toilet - Urinal cistern running - Urinal overflowing | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 13:00:00 | Pass | Unblocked urinal was already on site when showed job
MSA-DTWD | WA3733312 | Cleaners room - Hot tap will not turn off | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-10-30 17:18:00 | Pass | Replace taps
MSA-DTWD | WA3733449 | All chillers have gone down | East Perth Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 0 | CLOSE | 30 Oct 2020 | 2020-10-30 15:58:16 | 2020-10-30 15:00:00 | Pass | Site accessed gained. Bms readings show no fault on main chilled water and chillers system.Physical inspection of plant equiptment show cooling tower on and water cascading and fan operation gd.Condensing water pump and chilled water pump operating at required vsd demand and pressures as required from pumps.No faults found on either chiller 1 or 2 local controll screen.Bms to reading of condenser to showing no flow.Further investigation shows the condensing water differential switch to have undone at the brass nut where it attatched via waterline to main condensing pipework.Ball valve assoc with to supply water was found in an off position. Do line reinstalled to waterline and ball valve opened to now supply water pressure to switch.Bms now confirming pressure reading and chiller able to begin start up proceedure.Chiller running and reducing water to set temps.Pumps on and cooling towers operating.Building temps reducing
MSA-DTWD | WA3733530 | K block - Lower pressure on bore | Rockingham Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-05 14:45:00 | Fail | Located and repaired two breaks on the mainline
MSA-DTWD | WA3733565 | J block vandalised bore more ajacent piping | Rockingham Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-09 10:10:00 | Fail | Repaired vandalized bore discharge pipe.
MSA-DTWD | WA3733619 | D block, D17 Lecture Theatre - The chilled water control valve is not operating on AHU2, | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-12-04 14:00:00 | Fail | Upon inspection accessed plant room, logged onto bms system, due to low ambient and no heat load in room valve was not calling for cooling, set up ladder and removed covers to valve actuator, changed set point on bms to open valve but valve would not function, check history for valve to find quote has been submitted for replacement. Refitted all covers.Traveled to site, isolated unit, removed faulty actuator, travelled to supplier pick up new chilled water valve travelled back to site, fitted and wired and tested valve function and operation via BMSAll ok Completed
MSA-DTWD | WA3733644 | Female Toilet- hot water system not working | Perth Campus B1 | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 30 Oct 2020 | 2020-11-06 17:00:00 | 2020-11-02 14:00:00 | Pass | Fix hot water issues
MSA-DTWD | WA3733715 | E block, large skal kitchen (main core sectoin) - fridge running at 20 degrees | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-11-02 10:00:00 | Pass | Reset hp switch and cleaned condenser coil
MSA-DTWD | WA3733722 | Sinks in commercial kitchen are blocked and need urgent attendance. | Joondalup Kendrew Campus-Block E | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 30 Oct 2020 | 2020-10-31 00:39:53 | 2020-10-31 08:44:00 | Fail | Attended site after hours,Investigate blocked grease lines to commercial kitchens at E block. Return the next morning to jet wash lines clear. Tested all sinks on completion and pressure washed areas clean.
MSA-MRWA | WA3733010 | ground toilet leaking tap | Traffic Operations Centre | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Oct 2020 | 2020-11-02 17:00:00 | 2020-10-30 15:27:00 | Pass | Reseat and rewasher basin hot and cold
MSA-MRWA | WA3733699 | One of the urinals seems to be blocked and nearly overflowing when flushed – require inspection. | Heavy Vehicle Services-Main Building-Ground Floor-Toilet-Male | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-03 13:30:00 | Pass | Clear blockage to urinal Inspect other fixtures all running free
MSA-MRWA | WA3733721 | High temp - Inspect and Report, Please call contact prior to arrival | Traffic Operations Centre-Main Building-Ground Floor-IT Server Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 30 Oct 2020 | 2020-10-31 00:14:53 | 2020-10-30 23:09:00 | Pass | Arrived to site.Accessed building with onsite staff.Located server room unit.Checked PC-2 unit running at setpoint.Checked over PC-1 found unit 2 degrees above setpoint.Stage 2 running.Stage 1 off.Searched for access into level 2 controller parameters.Found output status log with cooling 4 output energized with stage 2 running.Unknown mismatched bug in controls.Power reset whole system.System started in AUTO mode. Both compressors staged on within a minute of each other.Watched temperature fall to set point and compressor cycled off.All systems working okay.Client advised of findings.Keys returned and signed out of building.
MSA-DCS | WA3733753 | GATEHOUSE- Monitor is showing black screen. | Karnet Prison Farm | GMP-BR- HO | Building | Security Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Oct 2020 | 2020-10-31 13:28:33 | 2020-11-06 14:18:00 | Fail | Replaced monitor i with monitor provided
MSA-DCS | WA3733771 | Visits - non contact booth not working | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Oct 2020 | 2020-11-04 17:00:00 | 2020-11-19 12:36:00 | Fail | Invoice raised for costs to date.New work order WA3794642 was raised to complete the job
MSA-DCA | WA3736595 | 5th Floor mechanical room - Steam Generators In Fault | Art Gallery of WA - James St | GMP-BR | Plumbing & Drainage | Materials (PD) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 01 Nov 2020 | 2020-11-01 23:25:02 | 2020-11-09 08:25:00 | Fail | COMPLETED
MSA-DCS | WA3736552 | Unit 4 - Cell Call system does not sound in the control room, light only flashing | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Nov 2020 | 2020-11-02 11:35:48 | 2020-11-09 15:19:00 | Fail | Repaired comms fault and CI-3210 fault in Unit 4.Tested OKCell call now operating correctly.Job Complete
MSA-DCS | WA3736558 | KITCHEN- 2x kettles are not working. | Casuarina Prison-Kitchen | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 01 Nov 2020 | 2020-11-01 15:46:52 | 2020-11-16 17:00:00 | Fail | 01/11/20 - Arrive at site to check kettles not working, staff explain LHS unit not tilting and RHS not mixing. Check both units and both working ok at time of testing. Checked over LHS unit and found no obvious signs of issue other than knob on tilt controller worn. Would need to be replaced. Checked over RHS unit and found intermittent fault on mixing speed controller. Swapped the controller from the spare unit (in storage) and test all ok. Controller will need to be replaced along with a new knob.Test both units all working well at this timeParts required2 x knobs 1 x speed controller potentiometer 16/11/20 - Escorted to site. Found RH kettle potentiometer not working correctly. Replace potentiometer and knobs with ones supplied and will require replacement for spare unit at the back.
MSA-DCS | WA3736569 | fix camera presets for visits | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-02 15:00:00 | Pass | Checked camera settings, found camera automatically resets back to Preset 1 on each visits PTZ camera, logged into camera and checked settings, all settings checked ok. Removed presets on Indigo software and re-added presets. retested and found the same issue occurs. Called tech support and was advised that it is an issue he had not heard of before, checked model and software version of camera. Removed camera presets and tested twice with only one preset programmed and again with no presets associated with the cameras. Issue is rectified when presets are removed from visits camera, when camera preset is set up the camera moves to a different location than the one that is programmed to move to, removed all PTZ presets in visits as presets are not used during visits sessions. Re-tested all camera functions and all tested and working ok. Job complete, if site are wanting visits camera presets back then will need to re-programme and possibly upgrade firmware on all PTZ cameras
MSA-DCS | WA3736576 | Hakea Prison - SOG Hut - Automatic door - is not locking. | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 01 Nov 2020 | 2020-11-02 15:36:32 | 2020-11-01 17:00:00 | Pass | Urgent after hours attendance. Replaced battery to external door lock. Normal function restored.
MSA-DFES | WA3736526 | Water leaking through exhaust fan in kitchen- Exhaust fan has been made safe. Roof leak. | CFRS Maddington-Main Building | GMP-BR | Carpentry | Materials (CA) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 01 Nov 2020 | 2020-11-01 12:20:12 | 2020-11-02 14:30:00 | Fail | Removed old silicone sealer from the flashing and applied new
MSA-DCA | WA3736804 | Ground floor - FIRE PANEL faults due to ongoing project - please check | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 02 Nov 2020 | 2020-11-02 11:15:54 | 2020-11-02 10:00:00 | Pass | Attended site and found the following.1: EWIS system isolated2: 105 devices in alarm spread over loops 1,2 & 43: Code red in alarm state4: Loop 4 in over current state5: Loop 3 causing panel earth fault.Left panel with the following.1: 209 isolated2: earth fault3: Bell isolated4: Plant isolated5: Code Red isolated.6: EWIS in isolateLeft site as booked on other works.
MSA-DCA | WA3736826 | floor drain blocked | Perth Cultural Centre Precinct - Museum Plaza (James Street) | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 02 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-09 08:09:00 | Fail | Investigated blocked chanel grate between the cafe and the museum. Unable to jet washed stormwater drain during the day due to high pedestrian traffic. David agreed on carrying out the job early in the morning.
MSA-DCA | WA3736833 | exterior - Graffiti tag to be removed | The Blue Room-Main Building-External Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 3 | CLOSE | 02 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-04 08:30:00 | Pass | job completed - graffiti removed
MSA-DCA | WA3737130 | male & female toilets are running constantly. Both are the cubicle nearest the door - see notes | Maritime Museum Victoria Quay-Main Building-First Floor-Male Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-21 10:49:00 | Fail | Replaced flushing valve and inlet valve to induct toilet cistern 1st cubicle upstairs female toilet.
MSA-DCA | WA3737318 | FIP has a VESDA Collection Area 4 fault (attend today 2/11/20) | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-03 15:04:00 | Pass | Attend site and check VesdaFilters need to be replacedReplaced filters
MSA-DCS | WA3736666 | Zone 12 Activation - PTZ # 23 activates but not going to the zone | Roebourne Regional Prison | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 05:50:24 | 2020-12-11 07:00:00 | Fail | Test ptz going to correct zone, all working correctly, job was completed on different job already.
MSA-DCS | WA3736699 | Lights keep tripping out in the Dairy packing room. | Karnet Prison Farm-Dairy Cool Room | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 06:13:05 | 2020-11-02 15:00:00 | Pass | Investigate and repair tripping dairy lights.
MSA-DCS | WA3736842 | Lights not working for half the office - lights have been turned on from switch board and keep tripp | Maddington (South East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 07:37:23 | 2020-11-02 13:30:00 | Pass | Replaced submains supply cct breaker in site main switch board to Unit 2. Blue phase had gone open cct.. Test ran ok.
MSA-DCS | WA3736847 | Jeelia - drains blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 02 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-03 09:28:00 | Pass | Removed seized shower grates in Jeelia A3 & A4 .Cleared blocked showers caused by lots of hair.
MSA-DCS | WA3736875 | Unit 6, Cell A24- Toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-05 16:50:00 | Fail | Replaced outlet wahser, button mechanism
MSA-DCS | WA3736879 | Unit 8, Cell B4- Toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-05 18:25:00 | Fail | Replaced inlet vakve, outlet wahser and bellows
MSA-DCS | WA3736880 | Jeelia, A7 - No power to electrical sockets | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-11 07:02:00 | Fail | Tested power all working, carried out full electrical tests on rcd and power points, found an override panel for power in jeelia control room that had been isolated to room A-7 turned it back on tested all ok.returned to locate fault, found power reinstated to the power points, carried out a full electrical test, found a power isolation panel in the jeelia office turned power back on and tested all ok.
MSA-DCS | WA3736881 | Unit 9, Cell A14- Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 07:59:14 | 2020-11-02 10:30:00 | Pass | Attended and investigate the fault, test cell point ok and working as normal. Job completed.
MSA-DCS | WA3736884 | Unit 8, Cell B1- Cell Main light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-03 12:00:00 | Pass | Repaired light
MSA-DCS | WA3736887 | Medical Centre- Main prisoner entry door unable to lock door | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 08:03:16 | 2020-11-02 11:20:00 | Pass | Attend site. Operational issues required return (same visit). Repaired lock to restore normal function.
MSA-DCS | WA3736889 | Unit 8, Cell C3- Cell lock not working | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 08:05:18 | 2020-11-02 10:30:00 | Pass | On site. Repaired lock by replacing worn component. Normal function restored.
MSA-DCS | WA3736905 | Unit 16/17 Vehicle access gate Fault (Possible Electronic Fault) | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 02 Nov 2020 | 2020-11-02 12:02:46 | 2020-11-02 11:30:00 | Pass | 02/11/20Checked board.Checked wiring.Reset controller.Work ok.Tested locally and with master control.
MSA-DCS | WA3736917 | Unit 14, B & D - The black handle is broken on the B/D wing drinking fountain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-12-09 12:30:00 | Fail | Held up in unit due to short staff
MSA-DCS | WA3736929 | Unit 14, A9 -shower sewerage is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-02 15:00:00 | Pass | Nill
MSA-DCS | WA3736931 | Unit 14, Cell D14- Light switch panel is damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-04 10:00:00 | Pass | Replaced damaged cell switch in unit 14 d14
MSA-DCS | WA3736936 | Unit 14, D15 - Cell toilet blocks up sometimes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 08:30:00 | Pass | Nill
MSA-DCS | WA3736937 | Unit 14, B & D- Security camera (next to the grill)cover is scratched right in front of lens | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-03 12:00:00 | Pass | Job complete .Recommend replacing this camera as picture quality not perfect and rotating scratched cover to back side of camera.
MSA-DCS | WA3736938 | Unit 3, B5 - Window is jamming and not sliding properly. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 12:30:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3736939 | Unit 6, B Wing Yard- Under eaves water leak indicated by black arrows | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo Building Services | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 08:32:24 | 2021-04-08 09:00:00 | Fail | REPAIRS MADE TO BOX GUTTERS, ROOF SHEETING & OTHER AREAS OF PENETRATION
MSA-DCS | WA3736945 | Unit 12, Cell A12- toilet cistern constantly running even after adjusting float level | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 08:30:00 | Pass | nil
MSA-DCS | WA3736947 | Unit 14, Cell D1- Sink is leaking, Small amount of water leaks from the right side | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 16:00:00 | Pass | nil
MSA-DCS | WA3736952 | Unit 4 - D Wing- First shower on left has no water pressure. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 15:00:00 | Pass | Nill
MSA-DCS | WA3736959 | Unit 3, A wing - Auto boil faulty leaking from tap | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 14:14:00 | Pass | Replaced faulty tap. Was leaking. All ok.
MSA-DCS | WA3736968 | CCU(11), Cell D1- Constantly dripping/leaking shower- forms puddles on floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 11:30:00 | Pass | Nill
MSA-DCS | WA3736974 | Control room, Prison alarm system PDA 79 - it not reset, has been disabled | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-02 12:30:00 | Pass | Rectified and fixed the PDA, job completed.
MSA-DCS | WA3736980 | Unit 7, Cell B3- Door hinge faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 10:30:00 | Pass | Replace worn hinges and adjust strike
MSA-DCS | WA3736983 | Unit 13, Tearoom- Sink tap is extremely loose | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-02 12:17:00 | Pass | Nill
MSA-DCS | WA3737009 | Abattoir chlorine plant not dosing | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-27 16:23:00 | Fail | System now operational
MSA-DCS | WA3737017 | Unit 13 - A & C A/C oven faulty. Doesn’t heat over 150 degres. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 09:07:16 | 2020-11-11 11:00:00 | Fail | Replaced elements & gasket, fitted & tested ok
MSA-DCS | WA3737085 | YEEDA, C WING - Broken dayroom window Approx. 650mm x 550mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-12-10 10:30:00 | Fail | WINDOW REGLAZED AND SEC FILM APPLIED
MSA-DCS | WA3737122 | Unit 2, top landing toilets exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-04 08:30:00 | Pass | Investigate and replace unit 2 top landing toilet exhaust fan.
MSA-DCS | WA3737129 | Unit 2, top landing showers tap handles broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3737133 | unit 2 middle landing toilet ceiling falling down due to old age | Karnet Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-12-17 13:30:00 | Fail | Ceiling repaired, electrical completed, ceiling painted.
MSA-DCS | WA3737136 | Unit 2 middle landing toilets exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-24 09:30:00 | Fail | Investigate unit 2 middle landing toilet exhaust fan.Requires replacement.Source replacement fan.Waiting on midolo to replace ceiling.Replace exhaust fan
MSA-DCS | WA3737148 | unit 4 cell C15 Cell call speaker not clear needs repair | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 10:27:03 | 2020-11-03 09:00:00 | Pass | Replaced cell call with pcb board, tested working. Job completed.
MSA-DCS | WA3737166 | Crisis Care - Regitermic oven keeps tripping circuit breaker needs repair | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 10:37:26 | 2020-11-02 15:00:00 | Pass | repaired oven
MSA-DCS | WA3737170 | End of unit 9- window has been smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 0 | CLOSE | 02 Nov 2020 | 2020-11-02 14:41:34 | 2020-11-04 11:45:00 | Fail | END OF WING WINDOWS AND END OF CORRIDOR WINDOWS RE GLAZED
MSA-DCS | WA3737201 | Unit 1, urinal cistern broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3737205 | Unit 2, outside lower landing PA speaker not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-04 11:30:00 | Pass | Investigate and replace unit 2 lower landing pa speaker
MSA-DCS | WA3737211 | Visits, None contact room No. 3- High pitch buzzing noise coming into cell won’t turn off | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-02 15:00:00 | Pass | Attended and test all the non contact visits room, working as normal no defect found. Job completed.
MSA-DCS | WA3737226 | PTZ 30 showing blank screen | Banksia Hill Detention Centre | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2021-05-06 09:03:00 | Fail | Works complete as per BRAF
MSA-DCS | WA3737257 | Unit 4, B Wing- Shower keeps running. Won't turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 13:30:00 | Pass | Nill
MSA-DCS | WA3737284 | unit 1 B wing west ablusion block west toilets blocked- will need pump machine | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-12-10 09:00:00 | Fail | COMPLETED
MSA-DCS | WA3737303 | Reception, Sallyport- Fluro lights blown (Scissor Lift Required) | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-17 15:00:00 | Fail | Reception sally port lights, repaired multiple lights in reception using scissor lift
MSA-DCS | WA3737333 | Unit 6 - B Wing Light in shower not working tombstones have broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-04 08:30:00 | Pass | Repaired faulty lights in unit 6 shower
MSA-DCS | WA3737338 | Unit 4 - D5 Missing slats on bunk bed require relpacing | Casuarina Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Midolo Building Services | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 15:00:00 | Pass | NEW SLATS WELDED TO BUNK BED
MSA-DCS | WA3737340 | Unit 3, D5 - Door viewing hatch is broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 13:30:00 | Pass | new viewing hatch installed
MSA-DCS | WA3737349 | Unit 5, D wing - cell D04 Toilet cistern isnt refilling. We have checked and the water is still turn | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 12:30:00 | Pass | Inlet valve , 300mm Flexi hose, 15mm m/I from stock
MSA-DCS | WA3737368 | Unit 7, A wing - SCU stovetop faulty | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 09:40:00 | Pass | Tested for open/short circuits, tested all , reconnected and turned on. Stove is in full operation & tested ok.
MSA-DCS | WA3737381 | Medical Centre, Yeeda C Wing - Roof leaking outside medical staffroom | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 11:00:00 | Pass | sealed under flashings
MSA-DCS | WA3737395 | Assessments- Lights keep tripping circuit breaker | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 13:29:22 | 2020-11-02 16:30:00 | Pass | Investigate report of tripping power, nothing found, possible water leak when heavy rain.could not identify.
MSA-DCS | WA3737459 | Medical Centre, Dental Clinic - The sinks in the Dental clinic are still blocked, needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 14:20:35 | 2020-11-03 06:00:00 | Pass | Removed rubbish from dg used gully plunger to clear blockage
MSA-DCS | WA3737461 | Unit 5 - A11 Window won't hold up. Keeps sliding down. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 14:45:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3737470 | Unit 4, A & C- flooring badly bubbled in dayroom causing a severe trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 12:30:00 | Pass | DAMAGED SECTION OF FLOORING UPLIFTED & REPLACED WITH NEW.
MSA-DCS | WA3737477 | Gatehouse, toilet light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-03 11:30:00 | Pass | Replaced lamps,starters and lampholders as required, test ran ok.
MSA-DCS | WA3737478 | Murchison, Day room - Air con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 09:00:00 | Pass | Complete, no issues found.
MSA-DCS | WA3737486 | Perimeter fence - camera tamper fault | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-03 15:30:00 | Pass | Rectified and fault the camera tamper, cam 34 and 35 tamper works in progress.
MSA-DFES | WA3736961 | Top dam - pump has over heated and have lost prime | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-10 08:26:00 | Fail | attended site malcolm thompson pumps pump failed Braf submitted and declined
MSA-DFES | WA3737042 | Driveway - Side exit gate keypad does not work | CFRS Kiara | GMP-BR | Building | Steel Fencing & Gates (BU) | Anvil Doors | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-02 12:45:00 | Pass | Attended Kiara Fire Station. Checked keypad controller for drive way side gate. Upon inspection, it was found that the wiring gland that goes into the key pad was corroded. (this would be the probable cause of the key pad failure). Site technician cut/removed the corroded part of the wiring and reconnected to the key pad.The key pad is now working correctly.
MSA-DFES | WA3737313 | kitchen area toaster has electricuted FF please investigate | CFRS Claremont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 02 Nov 2020 | 2020-11-02 16:21:02 | 2020-11-02 13:30:00 | Pass | Complete
MSA-DTAG | WA3737203 | Basement, Custody Control - PTZ 99 Camera has colour distortion, not displaying/transmitting full co | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-12-04 10:30:00 | Fail | Job completed - camera replaced
MSA-DTAG | WA3737270 | Accused has released excrement in various location - please see notes | Joondalup Courthouse | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-02 22:30:00 | Pass | Job carried out as per WO.
MSA-DTWD | WA3736859 | C block Automatic door - not communicating | Munster Campus (ACEPT) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 02 Nov 2020 | 2020-11-02 17:00:00 | 2020-11-02 12:25:00 | Pass | 02/11/2020, 1135-1225Alarm was ok reset power to auto door motor. Tested ok
MSA-DTWD | WA3736994 | E Block, Training Bar - hot water unit tripping RCD | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-03 11:30:00 | Pass | COMPLETED
MSA-DTWD | WA3736996 | E Block, SK3 the Lecturers sink, Flick Mixer broken | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-02 14:30:00 | Pass | COMPLETED
MSA-DTWD | WA3737018 | F Block, Rm F4- Lighting motion sensor faulty and needs to be by passed | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 12:17:00 | Pass | Attended site and signed in. Located F block. Class 4. Found sensor in classroom. Disconnect and isolate from use. Bypass wiring for sensor and made to only operate on switch as requested by site. Tested all okay. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3737033 | D Block, D01 Library Lights- Damaged tombstones in light fitting | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-02 13:15:00 | Pass | Replaced broken tombstones in library.job completed
MSA-DTWD | WA3737055 | Comms room - lost the combination to safe | Naval Base | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-02 11:30:00 | Pass | Code was lost too the safe, x2, gain entry and change codes.
MSA-DTWD | WA3737057 | L Block - lift not working | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-02 14:53:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close work order
MSA-DTWD | WA3737058 | E Block, E19- Lock on the door difficult to unlock and lock | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-02 11:25:00 | Pass | job completed - serviced lock
MSA-DTWD | WA3737103 | E Block, E63 Bistro – Milk fridge not cooling | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 14:45:00 | Pass | Client did not want to go ahead with braf to repair
MSA-DTWD | WA3737232 | Entry Foyer- Auto door not working | Perth Campus B6 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-02 13:54:00 | Pass | Inspected door and found fire relay cables was disconnected, connected back the cables, also found batteries were out of date, replaced 2x batteries, realigned the door, checked all fixings, tested door operation a number of times, all working fine.
MSA-DTWD | WA3737243 | Boundary fence is damaged, see notes below | Murdoch Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-23 13:00:00 | Fail | Attended site on Monday and completed works
MSA-DTWD | WA3737287 | E block E63 Bistro – Store room - Faulty door lock | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 12:15:00 | Pass | E BLock - E36 Bistro store room faulty door lock.Locks repaired - damaged keys replaced.
MSA-DTWD | WA3737316 | A block L3 A346 - Rheem hot water unit is not working -see notes | Leederville Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-04 13:00:00 | Pass | Complete
MSA-DTWD | WA3737361 | L1 room 106 Faulty electrical circuit - Please attend first thing in the morning (7:00) | Perth Campus B2 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-03 10:00:00 | Pass | Attended site , signed in , completed jsa, spoke to fm about faulty circuit , fm said circuit was tripping once a day but would reset , tested all appliances and were ok , circuit was being overload , advised fm and lecturer in the classroom that all appliances needed to be plugged in to different gpos across all 3 circuits that were on the wall , started investigating circuit , circuit was tripping and wouldn’t reset, tested appliances and found 1 was faulty (dead short between a-e and n-e ) , tagged out appliance, reset circuit and it was operating as intended, replaced faulty gpo , tested and was working as intended, cleaned up work area, completed paperwork ***job complete***
MSA-DTWD | WA3737393 | A block, female toilets- not flushing at all | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Materials (PD) | Techworks Plumbing | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 09:22:00 | Pass | Attended siteLocated and inspected toilet buttonsToilet flush buttons not pressing in far enough to activate flush.Installed some spacers at the back of the buttons to allow for deeper recess for buttonsToilets flush nowJob Complete
MSA-DTWD | WA3737437 | S Block Level 2, Corridor - Trough Taps issuing white milky water | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-03 11:30:00 | Pass | Complete
MSA-DTWD | WA3737440 | D block L3 D307 Lock to D307 Kitchen is missing screws | East Perth Campus | GMP-BR | Furniture | Domestic Furniture (FU) | ADVANCED LOCK & KEY | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-03 10:20:00 | Pass | repair lock to Kitchen D307
MSA-DTWD | WA3737451 | E block ET02 smoke coming out of air con duct | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 0 | CLOSE | 02 Nov 2020 | 2020-11-02 18:10:56 | 2020-11-27 12:00:00 | Fail | Travelled to suppliers to pick up parts. Travelled to site and signed in. Accessed roof and isolated and removed old faulty fan motor and installed new fan motor. Wired up and yes ran unit all ok. To dispose of parts offsite.
MSA-DTWD | WA3737464 | outside of C block grease arrester trap lid is damaged | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2021-03-16 09:30:00 | Fail | Placed new concrete lid on top of old grease trap.
MSA-DTWD | WA3737473 | B Block chiller failed and tripped off line last Friday it couldn't handle the heat loading | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 02 Nov 2020 | 2020-11-03 17:00:00 | 2020-11-04 11:31:00 | Fail | Travelled to site, signed in and obtained keys, Upon inspection of Chiller B removed covers to access LCD screen and going through alarms found unit had tripped on VSD high temp, this was due to a high ambient temp and the system currently only running on 1 stage (50%). There is a outstanding fault on stage 1 which needs to be investigated, spoke with Daniel Wales from Vision Air, a quote has been submitted awaiting approval for these works.A PO was raised to have Vision Air to attend to investigate the VSD fault
MSA-DTWD | WA3737505 | BLD 834 - Faulty Switchboard | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 10:00:00 | Pass | Job completed - identification of Switchboard
MSA-DTWD | WA3737531 | west wing L1 W108 male toilets 2x Cisterns keep on running when flushed | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-03 13:00:00 | Pass | Complete
MSA-DCA | WA3738028 | exit doors - doors not closing properly banging in the middle | The Blue Room-Main Building | GMP-BR | Building | Doors (BU) | ICS Australia | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-06 13:54:00 | Pass | Plained, sanded to match existing and painted to allow for proper closure.Replaced one hinge
MSA-DCS | WA3737696 | Gatehouse foyer door - glass panel falling out | Karnet Prison Farm | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 2 | CLOSE | 03 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-09 15:00:00 | Fail | RE-ASSEMBLE GLASS PANEL BACK INTO DOOR
MSA-DCS | WA3737711 | Bulk stores expander failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-03 13:00:00 | Pass | Contacted site and had facilities manager reset contriller and reprogrammed contriller GBUS port and retested . All tested and working ok. Job complete
MSA-DCS | WA3737718 | Jeelia, C wing lounge - door lock not working properly | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 03 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-17 10:00:00 | Fail | 09/11/2020 - Attended Site. Although attendance was booked in advance, turned away due to operational (staffing) issues.17/11/2020 - On site. Adjusted hinges and strike until normal function restored.
MSA-DCS | WA3737720 | Jeelia, A wing laundry - door lock not working properly | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 03 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-17 11:00:00 | Fail | 09/11/2020 - On Site. Although attendance was booked in advance, turned away due to operational (staffing) issues.17/11/2020 - Attended site. Adjusted hinges and strike until normal function restored.
MSA-DCS | WA3737733 | Secuirty Office - CCTV monitor appears to be faulty | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 07:43:07 | 2020-11-03 14:00:00 | Pass | Job complete
MSA-DCS | WA3737737 | Unit 10,control room - The cell call showing on the remote monitor, but nothing comes up on cell con | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 07:48:02 | 2020-11-03 11:00:00 | Pass | Rectified and fixed the cell call diplay fault, job completed.
MSA-DCS | WA3737743 | Unit 9, A2 - S bend under sink is broken and leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 07:53:35 | 2020-11-04 11:30:00 | Fail | Removed Broken toilet and basin then reinstall new basin and pipe work and new toilet
MSA-DCS | WA3737747 | Kitchen workshop - Fault description Robot Coupe MP stick blended broken (this commercial equipment) | Hakea Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 03 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-20 10:30:00 | Fail | Kitchen Robo Coupe Stick mixer broken in half. Check mixer, remove for repairs. Dismantle, replace blade and foot assembly. Assemble & test. Return to Hakea Store.
MSA-DCS | WA3737752 | Kitchen, Dish wash area tap - tap/valve broken dishwash area | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 08:00:56 | 2020-11-03 14:19:00 | Pass | Replaced leaking tap in the kitchen
MSA-DCS | WA3737777 | Education -Main hallway light switch faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-19 08:00:00 | Fail | Replaced cracked light switch
MSA-DCS | WA3737778 | Unit 1 B Wing Cell B8 tap spindle faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-25 07:39:00 | Fail | Started job but was unable to complete due to no escort available.
MSA-DCS | WA3737779 | Unit 1 B Wing Ablutions Block West taps leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-12-10 11:00:00 | Fail | COMPLETED
MSA-DCS | WA3737783 | Unit 1 B Wing Water fountain constantly dripping, may need new spout | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-06 13:30:00 | Pass | Removed damaged tap and replaced with new . All tested Zip Chillmaster Fountain
MSA-DCS | WA3737830 | unit 4 PRU camera's keep dropping out of pane | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-12-07 08:02:00 | Fail | Relocate modem racks to bottom of rack. Replace all MM patchleads and secure neatly on tray and cable management. Generate labelling schedule for robots. Remove redundant fibre and coaxial patch leads from 10 CH rack relocation.
MSA-DCS | WA3737934 | ISU B wing blocked staff toilet and basin laundry trof | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 10:14:21 | 2020-11-03 21:47:00 | Pass | Unable to find sewer line outside, no drawings available. Uninstalled toiet pan, unblocked sewer line and reinstalled toilet pan.
MSA-DCS | WA3737968 | Murchison A05 cell call intercom very hard to hear | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 10:42:47 | 2020-11-13 09:30:00 | Fail | Replaced faulty unit with new Cell Guard intercom (supplied by SEME).Conducted test locally and to master control.All ok at departure
MSA-DCS | WA3737972 | ISU D11 light switch broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-04 11:15:00 | Pass | Replaced faulty light switch isu cell d11
MSA-DCS | WA3737984 | ISU B wing entry (near S.O) smashed door window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-26 11:00:00 | Fail | ISU - B WING ENTRY DOOR WINDOW REGLAZED
MSA-DCS | WA3737991 | unit 4 J block kitchen tap washer is needed bring in freeze spray | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-25 15:15:00 | Fail | Attended site,Isolated hot and cold water supply lines to kitchen, supply and Install spindle service kit to hot and cold taps to repair as required. Tested works on completion
MSA-DCS | WA3737997 | Unit 4 L block kitche double GPO is cracked and needs attention - not just mechanisms | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-19 09:00:00 | Fail | Replaced 3x power points in kitchen
MSA-DCS | WA3738035 | DDU kennels blocked gutter build up of leaves | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-04 12:00:00 | Pass | 04/11/20cleaned gutters
MSA-DCS | WA3738044 | unit 1 B9 Stainless toilet pan leaking from the back onto the cell floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 11:43:13 | 2020-11-04 10:25:00 | Pass | Replace leaking pan adapter and adjusted pipework to suit
MSA-DCS | WA3738048 | gate house sallyport doors not opening and locking | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 03 Nov 2020 | 2020-11-03 15:48:12 | 2020-11-13 19:30:00 | Fail | 03/11/2020Remove arm, cut and reweld straight. Replace limit sensors.Re-calibrate and test.Ordered parts from East Coast, expected to arrive by 20/11/20.13/11/2020Replace taper bush on drive arm. Replace proximity sensors.
MSA-DCS | WA3738068 | C wing dayroom door to yard Top hinge broken door is off resecure other two hinges - see notes | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 12:16:09 | 2020-11-03 15:30:00 | Pass | HINGES ON DAY ROOM DOOR REPLACED
MSA-DCS | WA3738072 | Unit 1 Huts no TV reception | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-06 13:00:00 | Pass | job completed - Attended site. Traced TV cable in Unit 1 Hut. Found underground feed cable joint connectors faulty. Replaced andducted. Tested TV signal, OK.
MSA-DCS | WA3738081 | Unit 2, A wing Yard - material in razor wire | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-11 08:30:00 | Fail | 11/11/20Clean balls off roof and razor wire.
MSA-DCS | WA3738085 | 2B cell 8 sliding window not closing clip broken on bottom of window | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-04 13:00:00 | Pass | WINDOW ADJUSTED
MSA-DCS | WA3738086 | Health Admin Building - sitting at 13 degrees | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 12:35:15 | 2020-11-05 08:30:00 | Fail | Arrived on site and signed in, isolated aircond,removed faulty motor,fitted new motor,turned back on and tested all running ok at present.
MSA-DCS | WA3738105 | Gascoyne A wing Laundry drain is blocked solid and A wing boiler leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 12:50:30 | 2020-11-04 14:16:00 | Fail | Repair water line to hwuMachine laundry waste
MSA-DCS | WA3738109 | Unit 7, E6 - Fault description Pipe leaking from bottom of cistern. water turned off to toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 12:54:52 | 2020-11-04 12:20:00 | Pass | Replace fuslty inlet valve and adjusted pipework to suit
MSA-DCS | WA3738110 | Unit 7 E22 Toilet flusher needs repair will not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 12:55:06 | 2020-11-04 13:55:00 | Fail | Replaced faulty inlet valve and adjusted pipe work to suit. Replaced faulty mechanics in the cistern
MSA-DCS | WA3738118 | Entry Pod - fire alarm set off in unit 5 didnt show in POD | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 03 Nov 2020 | 2020-11-03 17:04:23 | 2020-11-03 14:25:00 | Pass | Attended site and found panel normal checked history log and found device 11097 Az 35 Passage outside toilets had alarmed and indicated in pod panel normally. Zone description list to right of panel indicates where zone is located. System could benefit from a tactical fire plan near fip to assist in locating zones. Left system normal. Descriptions could be changed to include house numbers if required but would require software change.
MSA-DCS | WA3738157 | CCU (11) - C Wing no hot water in cell C4 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 10:30:00 | Pass | Nill
MSA-DCS | WA3738171 | Unit 1, rear - sewage leak (near large water & gas tanks) | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-06 16:30:00 | Pass | Complete
MSA-DCS | WA3738178 | shared facility 3 lights not working 2 in gym & 1 in training room | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 15:00:00 | Pass | Investigate lights in gym and shared facilities. Repaired some lights. Source more parts. Repair remaining lights.
MSA-DCS | WA3738212 | Kitchen - Lunch Room Tap loose in sink in diets room due to prisoner damage. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-11 19:51:00 | Fail | Nill
MSA-DCS | WA3738228 | front gate front door is flapping in the wind not opeing or shutting | Hakea Prison | GMP-BR- HO | Building | Security Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 03 Nov 2020 | 2020-11-03 18:44:48 | 2020-11-03 15:20:00 | Pass | Attend Site. Removed and inspected lock. No fault found. Re-installed and tested several times. Working Normally. Possible electrical issue?
MSA-DFES | WA3737814 | Roller Door 1 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737816 | Roller Door 2 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737819 | Roller Door 3 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737823 | Roller Door 4 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door
MSA-DFES | WA3737824 | Roller Door 5 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737831 | Roller Door 6 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737833 | Roller Door 7 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737835 | Roller Door 8 Rubber seals on the bottom of door are torn/missing/worn out | DFES Baldivis | GMP-BR | Building | Doors (BU) | Go Doors | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-16 16:15:00 | Fail | Date onsite: 16/11/2020Start time: 10:00amFinish time: 16:30pm(16/11/2020) - Work NoteWork Completed: Completed works as quoted.Bottom seal replaced on roller door.
MSA-DFES | WA3737927 | ground whole station Hot water from taps is excessive temperature, its coming out scalding | CFRS Duncraig | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-11 08:30:00 | Fail | Hot water at the station was to hot so adjusted the temp valves to working temperature
MSA-DFES | WA3737948 | ground lecture room 4 Panel has fallen off Lecture Room 4 – Exterior. | FESA RHQ - Forrestfield | GMP-BR | Building | General Building (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-04 14:00:00 | Pass | Re-attached loose cover plate between windows
MSA-DFES | WA3738198 | Engine room, ground - Screws have fallen out from electrical charging plug for the Light Tanker | Butler Career Fire Station | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 14:15:00 | Pass | Arrived onsite and signed in at 1345Site advised me they were worried about screws missing on a 12v charging outlet. We installed 2 screws to stop the outlet from being loose.Signed out and left site at 1415
MSA-DFES | WA3738267 | Engine room door Roller door bent.Please check over for any internal damage | VFRS Mundaring | GMP-BR | Building | Doors (BU) | Go Doors | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-04 10:30:00 | Pass | Inspected impact damage to roller shutter.Tested door operationRecommend replacement of damaged slats
MSA-DTAG | WA3737922 | 1987 Sheriff's Office Dishwasher intermittently stops working | Supreme Court | WSM-BR-SITE | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-06 07:30:00 | Pass | Inspected dishwasher and tested supply no fault found - possible appilance fault under warranty
MSA-DTAG | WA3738067 | Family Violence Services Client Lounge door is warped | Central Law Courts-Main Building-Level 5 | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-04 09:00:00 | Pass | door repaired
MSA-DTAG | WA3738255 | ground cell 3 Special Clean in Cell 3 – Accused spat on the cell floor | Midland Courthouse | WSM-BR-SITE | Cleaning | Cleaning (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-03 18:20:00 | Pass | Ground Cell 3 Special Clean in Cell 3
MSA-DTWD | WA3737795 | G block, ground floor, Ladies toilet - Key lock would not rotate to secure | Mandurah Campus (formerly Peel) | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-03 10:15:00 | Pass | job completed - lock serviced
MSA-DTWD | WA3737908 | Lift car hits something travelling between levels 2 & 3 | Perth Campus B6 | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-03 13:30:00 | Pass | REPAIRED AND RE-SECURED LEVEL 3 LANDING TOE GUARD. CONFIRMED APON DEPARTURENO charges
MSA-DTWD | WA3737938 | C block L2 Staff Kitchen the door handle is broken needs replacing | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-03 11:35:00 | Pass | job completed - serviced lock
MSA-DTWD | WA3737977 | building 8, ground floor, 8G37 - lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-04 13:45:00 | Pass | Attended site , signed in , completed jsa, removed old light and switch replaced with new lights and switch , tested lights , lights working as intended, cleaned up work area, completed paperwork, signed out *** job complete***
MSA-DTWD | WA3737978 | block 6 ground Bricklaying workshops Water leak over roller door between inner and outer workshops | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-30 06:05:00 | Fail | Leak was due to a rusted box gutter. Box gutter was measured up and quoted for replacement.BRAF was declined for works.
MSA-DTWD | WA3737985 | building 8, first floor, 8F60 - water leaking next to lecturers desk | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2021-02-26 11:07:00 | Fail | BRAF Declined, repair works not completed
MSA-DTWD | WA3737989 | A,B & C block - extraction fans not coming on | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-25 11:29:00 | Fail | VISIT 1 Arrived on site, signed in, then was taken to DB board were 3 DEC cards were fitted, unable to run exhaust fansfrom ITM, checked ITM, found no DIO for fans, removed covers on DEC cards, checked wiring, they wereconnected to D3 network, but unable to determine how they were trying to control the fans, they were using manualswitch on the board, as auto not working, due to ITM not connected to cards to control them, spoke with Adam, hetold me that he explained this to them when he updated the ITM, but no further action has been taken betweenthen and now. Referrer needs to find out how they are controlling the fans and the inputs that they are applying tothe DEC cards to turn them on and off, as no schedules are in the ITM for the extract fans, because they are notconnected to the ITM in the first place.VISIT 2Arrived on site, signed in, then went to C block ITM, could see exhaust fans on the ITM, unable to switch on,checked settings in the back ground of the ITM, were n
MSA-DTWD | WA3738001 | Southern Hall BLD 821 Flat C and Flat D Leaking showers | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-09 15:30:00 | Fail | Repair shower taps to Southern Hall units C and D
MSA-DTWD | WA3738002 | Male student toilet - blocked toilet | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-04 13:30:00 | Pass | Male student unblocked toilet
MSA-DTWD | WA3738053 | 1st floor, C block, Ladies toilet - ladies toilet blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-03 14:00:00 | Pass | COMPLETED
MSA-DTWD | WA3738147 | B16 staff room main entry north - Double timber doors banging closed with frequent high usage | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-18 13:03:00 | Fail | Works complete
MSA-DTWD | WA3738238 | D block L2 male toilet Repair urinals Green Skills . Leak onto floor | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-25 09:30:00 | Fail | Complete
MSA-DTWD | WA3738254 | ground floor 8G31 1 bank of lights tripping another 2 rows. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 03 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-04 10:00:00 | Pass | Attended site, signed in , located lighted , completed jsa, investigated fault, problem was faulty ballast, replaced ballast ,tubes and starters , tested and all working as intended , cleaned up work area , completed paperwork ***job complete ***
MSA-DTWD | WA3738257 | Centre block L4 female toilet Cistern not filling | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 03 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-05 13:37:00 | Pass | Inlet valve not working
MSA-DCA | WA3739002 | lift No2 stopped on the ground floor with doors open | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 13:30:00 | Pass | NON CHARGEABLE
MSA-DCS | WA3738480 | Main Driveway entrance - several pot holes | Karnet Prison Farm | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 3 | CLOSE | 04 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-12 12:30:00 | Fail | 12/11/20Repair pot holes to front entrance
MSA-DCS | WA3738483 | Unit 1, Last shower next to storeroom water leak from behind tiles | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Nov 2020 | 2020-11-10 17:00:00 | 2021-01-19 10:15:00 | Fail | COMPLETED
MSA-DCS | WA3738500 | Gatehouse, Microwaves Zone keeps falsely activating | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 07:18:36 | 2020-11-04 14:00:00 | Pass | Multiple mw zones are affected with the on going projects on site, rectified and fixed the G02MW. Job completed.
MSA-DCS | WA3738563 | Laundry, wash area - Washing machine number 5 showing low oil | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 07:56:21 | 2020-11-05 09:00:00 | Fail | AMS720626 WA3738563 - Hakea - WM number 5 showing low oilAttend site - supply additional lubrication oilTest machine - ok
MSA-DCS | WA3738579 | Jasper, Cell B01 - shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-09 12:00:00 | Fail | Inspected shower and contorl box. No issues found.
MSA-DCS | WA3738582 | Unit 4, L block, Cell L4 - bottom bunk light faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-19 10:00:00 | Fail | Replaced bed light fitting with LED
MSA-DCS | WA3738585 | Unit 14, cell A07- shower leaking onto bed, shower screen leak | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 09:00:00 | Pass | RE sealed shower screen
MSA-DCS | WA3738587 | Jasper Cell A02 - Shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 10:50:00 | Pass | Replaced shower solenoid, button and control box. Adjusted pipework to suit
MSA-DCS | WA3738588 | Unit 14, Cell C05 personal lock is faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-12-09 11:00:00 | Fail | Replace mortise lock.Replace worn barrel.
MSA-DCS | WA3738592 | CCU (11), C Wing- Hot water system not working properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 09:30:00 | Pass | Nill
MSA-DCS | WA3738607 | Unit 2, Cell B2 - Main lock hard to turn with key | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 08:28:33 | 2020-11-05 10:20:00 | Fail | 04/11/2020. Attend site. Serviced lock but cylinder requires replacement.05/11/2020. Replaced cylinder to restore normal function.
MSA-DCS | WA3738612 | Dairy hot water unit not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2021-03-09 16:12:00 | Fail | Works completed as far as practicable
MSA-DCS | WA3738677 | Rear of Amenities- 2 x Solenoids won't turn off. | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-06 09:30:00 | Pass | FAULTY COIL REPLACED VALVE WORKING OK
MSA-DCS | WA3738682 | Sterile Zone near Anzac memorial - Swarm of bees in bottle bushes check area thoroughly for bees | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 09:16:22 | 2020-11-05 11:45:00 | Fail | Carried out a service for bees at Hakea Prison. There were reports of bees located around the Anzac memorial, upon further inspection bees were located. Due to the location of the bees they could not be safely removed and had to be treated. Thoroughly dusted the bees.
MSA-DCS | WA3738701 | Karakin, C wing - Gas Heater is broken (falling apart & gas pipe needs fixing) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 15:10:00 | Pass | Replaced section of gas pipe at the gas heaterx secured cage to the wall.
MSA-DCS | WA3738717 | kitchen conduit wires exposed in yard - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 09:26:01 | 2020-11-05 15:00:00 | Fail | Repaired and replaced damaged conduits in kitchen
MSA-DCS | WA3738750 | Offical Visits, non contact room- Crackling noise coming from intercom | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 09:00:00 | Pass | Aiphone intercom is fitted with thick metal enclosure to protect from vadalism, but is creates feedback and unwanted noise from the speaker. Advice maintenance mngr. on site that they require a different type of standalone intercom with tamper and valdal proof specification.
MSA-DCS | WA3738751 | Make good damaged asbestos sheeting to Education Building | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 09:21:00 | Pass | ADVISED TO CLOSE OFF JOB cost to date- AS NEW LVM ISSUED (wa3741350)
MSA-DCS | WA3738911 | Unit 5 - B & D Water main burst behind Unit 5 B/D wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 04 Nov 2020 | 2020-11-04 14:59:43 | 2020-11-04 16:00:00 | Fail | Nill
MSA-DCS | WA3738920 | front gate sally port Camera not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 11:04:43 | 2020-11-23 12:30:00 | Fail | Replaced sally port camera, configured, aligned and focus. Job completed.
MSA-DCS | WA3738938 | Bakery large cake mixer hard to change gears keeps jamming | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 11:08:40 | 2020-11-04 14:30:00 | Pass | 04/11/20Arrive at site to check cake mixer hard to change gears/ jamming. Check over unit and run through all gears ok. Moved some more grease over moving parts. Checked operation all ok. Oil level looks ok from sight glass
MSA-DCS | WA3738978 | Jeelia A3 switch is faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 09:00:00 | Pass | Replaced faulty switch mech in jeelia A-3, replaced switch mech and switch plate.
MSA-DCS | WA3738979 | Unit 3, Cell D4 - Water in Cell call (roof leak) | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 11:26:31 | 2020-11-04 14:30:00 | Pass | Searched cell for signs off leaks searched roof space and roof no signs off mains water leaking possible roof plumbing leaking from weather
MSA-DCS | WA3738987 | York tower is overcooling & freezing the pipework | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 11:46:40 | 2020-11-18 12:00:00 | Fail | Attend site check chiller temp. too low, check and adjust set point and parameters .Monitor and return to confirm operation ok.
MSA-DCS | WA3738998 | Unit 16, A10 - Sink blocked, plunger inneffective. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-06 12:30:00 | Pass | nil
MSA-DCS | WA3739015 | Unit 4, Officer has key stuck in door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-05 13:15:00 | Pass | Remove jammed keys, open lock, remove foreign object from strike hole and test lock - OK
MSA-DCS | WA3739017 | Cooling fan in Indigo Vision Terminal (Security Office) noisy. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-04 15:30:00 | Pass | Check and clean the indigo ws pc, job completed.
MSA-DCS | WA3739055 | unit 2 cell C5 TV cable not working in the wall | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-19 10:30:00 | Fail | Replaced tv mechanism,
MSA-DCS | WA3739061 | Assessments - ladies toilet is blocking up again (water jet maybe required) | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-12 12:00:00 | Fail | COMPLETED
MSA-DCS | WA3739115 | Metal shop - Officer received large electrical shock from control panel in the office. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 04 Nov 2020 | 2020-11-04 17:45:52 | 2020-11-05 13:30:00 | Fail | Investigated tested and reported electrical shock in metal shop. Replaced switch involved
MSA-DCS | WA3739133 | Unit 3 - B5 Cell door plate broken off, requires welding back on | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-10 16:00:00 | Fail | Require parts.Replace hinges, door plate, lock and weld on strike plate.
MSA-DFES | WA3738639 | serveral bollards not working on site | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2021-01-19 10:00:00 | Fail | Identified issues with Bollard lights.The Pneumatic system on 3 Irwin street lights does not work, and all of the lights on the 3 Bollards on Murray Street don’t work. Will be in contact with LEDA to fix the issue.
MSA-DFES | WA3738672 | Operational Delivery, Meeting room - fluro light making very loud humm | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 12:00:00 | Pass | Arrived on site at 11:35 to repair Fluro fitting in meeting room. Found tube had blown so we replaced the tubes and starters. Tested staff said they didn’t have a register so we signed out at 12:00.
MSA-DFES | WA3738681 | ground external car park serveral external lights not working - see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-19 09:45:00 | Fail | Already onsite and started works at 1100I identified the exterior lights causing the problem. There are 4 floodlights that are controlled via a pe cell which is located above a roller door. Site advised me that they work intermittently. I have proven that all 4 lights work correctly and I believe the issue is the PE cell. I spoke to site and will have to re attend to use a scissor lift. Site also advised me that they would like minimum 2 days notice before works are undertaken. I am confident swapping the PE cell will fix the issue, however can’t be definite without further investigation using the scissor. Signed out and left site at 1145Picked up scissor lift at 0700, arrived onsite at 0800. Replaced faulty PE cell from previous visit. Conducted several tests to confirm the functionality of the new PE cell, all in working order.
MSA-DFES | WA3739123 | Engine Bay Door 3 Perspex window falling out | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-12-22 13:15:00 | Fail | COMPLETED
MSA-DFES | WA3739156 | Office, Outside front and back- lights not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 08:45:00 | Pass | Arrived on site at 8:00 to repair lights around the academy. Found 3 fittings with lights out, 1 in the oxygen store room office and 2 fittings outside. Repaired the 3 fittings and tested units. Continued on site at 8:45.
MSA-DFES | WA3739167 | ground bathroom Toilet is continually leaking water into bowl - see notes | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-06 13:15:00 | Pass | Located to main officer toilet to see why the cistern is leaking into bowl continuously tested multiple times and cannot see an issue but had to replace the Flexi hose due to it was rusted and could bedamaged.
MSA-DFES | WA3739168 | Engine Room - FIP has power fault, Zone 4 still activating (fault) | VFRS Mandurah | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 09:45:00 | Pass | Electricians attended for ongoing issueRecommended panel is replaced with newQuote submitted to Steve Cassie by email on 13th November
MSA-DTAG | WA3738623 | revolving door vertical brush has detached from the glass panel | Central Law Courts | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 11:14:00 | Pass | Re attached door seal on revolving door. Ps no program asset no.
MSA-DTAG | WA3738654 | All water pipes are rattling. Noise stops when you run hot water but continues once tap is off | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 14:35:00 | Pass | New water meter installed causing water hammer.Watercorp coming to replace the water meter
MSA-DTAG | WA3738809 | Bollard needs repairing - photo to follow in email | Rockingham Justice Complex | GMP-BR-HO | Building | Steel Work (BU) | Midolo Building Services | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 14:30:00 | Pass | RE SECURED TO FLOOR USING NEW SCREWS AND NYLON ANCHORS
MSA-DTAG | WA3738904 | ground male public toilet Graffitti on roof of male public toilets | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 12:00:00 | Pass | Removed graffiti from male public toilet ceiling
MSA-DTAG | WA3739056 | Mag Chambers 2 & pa - A fluorescent in FV office and a globe in the JP waiting area faulty | Midland Courthouse | WSM-BR-SITE | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 09:30:00 | Pass | REPLACED TUBES AND GLOBES
MSA-DTAG | WA3739063 | Sally port - Fault description - A fluorescent in the Sally Port faulty | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 08:00:00 | Pass | Replaced 4x tubes and starters in the sally port
MSA-DTAG | WA3739070 | Level 1,A fluorescent in Magistrate’s Chamber 2 and 4 fluorescents in a unit faulty | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 15:51:00 | Pass | Replaced 4x tubes and starters
MSA-DTAG | WA3739153 | 1903, Lvl 1 - Technician required to isolate FIP - see notes below | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-07 17:00:00 | Pass | GA 7amAttended site and isolated zones at fip for building works5pmDeisolated the above zones
MSA-DTAG | WA3739230 | ground custody Bio Clean required in Custody Cell 4, spit on the floor and walls | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 20:00:00 | Pass | Custody Cell 4 spit on the floor and walls
MSA-DTWD | WA3738541 | A block, level 1, link door - repair lock to south side link door A Block | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 04 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-05 15:00:00 | Pass | adjust strike plate on A Block, level 1, link door
MSA-DTWD | WA3738546 | A block, level 3 A318 - Sink Blocked in A318 | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Nov 2020 | 2020-11-04 17:00:00 | 2020-11-04 14:30:00 | Pass | Complete
MSA-DTWD | WA3738554 | E block, Level 2, E202 - Hot water unit in E202 is leaking from overflow drain | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-25 12:15:00 | Fail | Please read work log
MSA-DTWD | WA3738557 | U008 - faulty GPO (hanging pendant GPO) | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 04 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-04 15:20:00 | Pass | Replaced faulty gpo.job completed,
MSA-DTWD | WA3738771 | AF11 - Ice Machine not producing ice, (filter previous replaced) | Mandurah Campus (formerly Peel) | GMP-BR | Refrigeration | Ice machine (RE) | Water2water Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 13:14:00 | Pass | Cleaned air filter. Replaced filter and change to more appropriate filter. To reduce scale and chlorine. Waiting for unit to produce two harvest. Ice produced both clear and fully developed.
MSA-DTWD | WA3738782 | E block, E28 Store room – Faulty light fitting | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 10:30:00 | Pass | Work completed
MSA-DTWD | WA3738790 | G block - G9 External door – Faulty push button at wheelchair access point | Bentley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 04 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-04 13:40:00 | Pass | Inspected door and found external push buttons was faulty and door was hitting on the wall when opening, replace faulty push buttons and adjusted opening distance, checked all fixings, tested door operation a number of times, all working fine.Programmed IP No. A40313920B
MSA-DTWD | WA3738805 | Corridors on level 4 - Replace lights as required | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-06 15:00:00 | Pass | Attended site, signed in, spoke to fm about job , completed jsa, repaired 2 lights (level 7 staff room and level 4 staff room ) , lights now working , cleaned up work area, completed paperwork,signed out ***job completed ***
MSA-DTWD | WA3738925 | Car park, Repair shade sail | Perth Campus B5 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-12-11 13:59:00 | Fail | Works complete
MSA-DTWD | WA3738968 | L1 Creche back yard Repair Shade sail | Perth Campus B1 | GMP-BR | Building | General Building (BU) | AWB Co. | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-12-08 13:05:00 | Fail | Works complete
MSA-DTWD | WA3738972 | M Block, Male Student toilets- urinal cistern button is not working | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-18 14:30:00 | Fail | KPI review: 2Replaced cistern buttons x2
MSA-DTWD | WA3738975 | Print Workshop, Level 1- Repair fallen drain grate | Perth Campus B4 | GMP-BR | Building | Materials (BU) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-18 11:37:00 | Fail | Install new drain after removing broken drain
MSA-DTWD | WA3738993 | E Restaurant & A Block 2nd Floor passageway- lights not working, see notes below | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-17 08:31:00 | Fail | Fixed lights in E block restaurant.Fixed lights in A block 2nd floor end hallway and foyer.
MSA-DTWD | WA3739081 | T Block, South side- Air con keeps tripping off | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2021-01-08 12:00:00 | Fail | Replace master unit inverter compressor and associated PCBs and reinstated unit back to master status.
MSA-DTWD | WA3739100 | A block, level 1, A116 - Odour coming from kitchen drain in student services. | Leederville Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-25 13:00:00 | Fail | Complete
MSA-DTWD | WA3739119 | Chem Store door has rotted at the bottom | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-12-07 15:49:00 | Fail | Complete
MSA-DTWD | WA3739137 | E Block, E16 Female Student Toilet – Leaking cubicle toilet | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 04 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-05 11:45:00 | Pass | Replaced 2x pan cones
MSA-DCA | WA3739408 | Ground floor fire alarm is activated twice. | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Security Office | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 05 Nov 2020 | 2020-11-05 17:00:00 | 2020-11-05 09:30:00 | Pass | Attended site due to false alarms on detectors L3 S46,11,28 throughout last night. History of this site is due to construction water has gottenthrough from level 4 to level 3 which loop 3 covers and caused earth faults and shorts on loop in past, earth fault not present whilst onsite butafter speaking with client no one was working or any reason to cause false alarms. Recommend loop card to be changed to 500ma typepossibly damaged from previous faults due to no short circuit isolators and 2 techs to fault find through loop to find any visible cable damageor water ingress. One man scissor lift required to access some detectors at high level.Detectors left isolated as requested by client which went into false alarm.Also recommend loop base short circuit isolator to be installed into loop 3Quoted works approved on WA3740546, attending Monday 09/11/20
MSA-DCA | WA3739752 | Female toilets in education offices-Flush button is not working and water is leaking into pan | Shipwreck Galleries-Main Building-Ground Floor-Female Toilet | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-05 15:55:00 | Pass | Replaced faulty flushing valve,inlet valve,flush pipe cone and Flexi to female toilet in education.
MSA-DCA | WA3739760 | Polly Café, blocked drain outside Polly café next to tables. | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 06:00:00 | Pass | Jetwash and cleared blocked storm drain.
MSA-DCA | WA3739772 | BMS has lost remote access please investigate (Alerton to attend) | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-05 16:00:00 | Pass | Attended site 5-11-20. BMS remote connection offline. Applied tests and checks, attempted to reset router/modem/server (unsuccessful). Raised PO for Alerton to attend. Alerton to have restored BMS online remote connection. Please refer to attached Alerton service report for works carried out an in depth analysis.
MSA-DCA | WA3739853 | LEL system has gone into fault | Collection and Research Centre Welshpool-Bulk Wet Store | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-25 16:30:00 | Fail | Works completed. Please refer to work logs and gastech service reporting.
MSA-DCA | WA3740087 | caged storage fire sprinkler broken | His Majesty's Theatre-Theatre Building-Basement | GMP-BR | Fire Protection Services | Sprinkler Systems (FP) | Critical Fire Protection & Training | 0 | CLOSE | 05 Nov 2020 | 2020-11-05 20:40:48 | 2020-11-05 19:45:00 | Pass | Call out - arrived and investigated sprinkler system - Fire Personnel attached new sprinkler head to pipes - main water to sprinkler shut off - system to "0" - isolated FIP and Code RedSlowly refill sprinkler system - purged air - waited 20 minutesJacked up pressure to 800waited no leaks locatedDeisolated FIP no leaks with new sprinkler headNew Protective cage required
MSA-DCS | WA3739538 | Unit 1, D9 - CCTV camera has a new cover on it but the vision is blurry and not clear enough to see | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 07:59:38 | 2020-11-05 11:30:00 | Pass | Trace fault ,blurred image on the camera . Adjust focus and clean the camera front cover. Job completed.
MSA-DCS | WA3739547 | Unit 5, Cell A4- Toilet cistern rod broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-05 14:10:00 | Pass | Replaced cistern and adjusted pipework to suit
MSA-DCS | WA3739549 | Unit 7, C Wing, Cell C9- drains are blocked, see notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-13 10:30:00 | Fail | Nill
MSA-DCS | WA3739551 | Paint Shop - toilet leaking at bottom when toilet is flushed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-12-01 10:30:00 | Fail | Nill
MSA-DCS | WA3739554 | Unit 4, A3 - cant turn personal lock with key. door cannot be closed unless tongue is retracted | Hakea Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 08:16:13 | 2020-11-05 14:45:00 | Pass | 05/11/2020. Attend site. Serviced lock. Replacement cylinder required. 05/11/2020. On site. Replaced cylinder to restore normal function.
MSA-DCS | WA3739555 | Paint Shop -staff toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-18 14:00:00 | Fail | Nill
MSA-DCS | WA3739560 | Unit 14, B1 - - shower is blocked and has flooded the day room near the grill | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 08:19:26 | 2020-11-05 09:30:00 | Pass | Nill
MSA-DCS | WA3739635 | Grounds, Zone 3- Perimeter light not working, see notes below | Boronia Pre-release-External Area | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 10:00:00 | Pass | Repaired light
MSA-DCS | WA3739663 | Reception - Sliding door to disabled shower is very hard to slide open, runners need repair | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-12-04 14:30:00 | Fail | LUBRICANT APPLIED TO MAKE DOOR OPERATIONAL
MSA-DCS | WA3739699 | Outpatients Area, The Whole Unit - seized fan seized | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-05 12:30:00 | Pass | Found condenser fan motor siezed, isolated system,fitted new fan motor,turned back on and tested all running ok at present.
MSA-DCS | WA3739709 | Health Administration- Aircon extremely noisy | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-05 10:30:00 | Pass | Checked over aircond found, condensor fan motor bearings very noisy,picked up new and fitted,turned back on and tested all running ok at present.
MSA-DCS | WA3739714 | Unit 14, B & D, Cell B02- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-06 15:00:00 | Pass | nil
MSA-DCS | WA3739716 | Unit 15 - B & D Lock strike plate bent. (Prisoner damage) | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-12 12:30:00 | Pass | Require parts.Replace damaged weld in strike box with screw in strike box and strike.
MSA-DCS | WA3739754 | Unit 16, B Wing- Service Duct lock barrel came out with the key | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-05 12:00:00 | Pass | Attend site. Replace lock cylinder to restore normal function.
MSA-DCS | WA3739763 | Admin, kitchen - Zip boiler leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-06 11:55:00 | Pass | Replaced corroded johnnguest fitting. Replaced oring and collet where jg part connects. Replaced tube. Thisnrectified leak from top of unit. Still leaking from drain connect. Told by client that is ok. Just wanted top leak resolved.HAD ATTENED ON 2.11.2020 BUT NO ESCORT READY OR AVAILABLE ALTHOUGH BOOKED IN HAD TO RETURN
MSA-DCS | WA3739788 | Internal zones 13 & 14 mircowave is in constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-05 14:30:00 | Pass | Voltage drop on both MW power , trace fault and rectified. Job completed.
MSA-DCS | WA3739803 | Kaartdijin Mia, West - Ceiling access hatch missing requires replacement (North West Demountable) | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-12-08 12:00:00 | Fail | ACCESS HATCH REPLACED
MSA-DCS | WA3739826 | Unit E4 18 - fire alarm keeps activating | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Nov 2020 | 2020-11-05 15:23:10 | 2020-11-05 13:30:00 | Pass | Complete
MSA-DCS | WA3739836 | Unit 3, A & C Side - TV Cable is faulty | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-30 09:00:00 | Fail | Attended site. Checked Unit 3 A & C Dayroom TV, found TV lead damaged. Replaced TV lead & tested signal, OK.Job completed
MSA-DCS | WA3739840 | Metal Shop- grinder cable damaged , needs to be shortened and plug refitted | Casuarina Prison | WSM-BR-SITE | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 08:30:00 | Pass | Investigate and repaired metalwork grinder
MSA-DCS | WA3739845 | Visits Area - Toilet Male toilet in visits hallway leaking from seal onto floor. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-11 10:30:00 | Fail | Nill
MSA-DCS | WA3739846 | Inspect Unit 15 drains via camera and report on findings. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-12-22 14:00:00 | Fail | nil
MSA-DCS | WA3739870 | Unit 5 cell D2 TV plate (splitter type) broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-11 12:00:00 | Fail | Work performed by Lee Kiok (11/11/2020):Attended site. Replaced TV splitter 8, TV Points in Unit 5 Day Room. Tested signals, OK.Job completed.
MSA-DCS | WA3739872 | Abattior waste water shed broken filter housings | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-06 10:00:00 | Pass | COMPLETED
MSA-DCS | WA3739875 | Cue cell call not working node 5 - SEME on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 12:03:28 | 2020-11-05 15:15:00 | Pass | Attended site and investigated the fault.Found transmit failure message on CI - 3210 cell call station.Reseted power to unit and conducted test.All back to normal and operational
MSA-DCS | WA3739888 | Unit 5 Grill in passage outside unit 5 Main lock loose in grill | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 12:13:02 | 2020-11-05 14:00:00 | Pass | Attend site. Service grill lock to restore normal function.
MSA-DCS | WA3739900 | control external zone 2 PXT constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 12:19:05 | 2020-11-26 13:00:00 | Fail | Located replacement SM100-2 Senstar module and made some minor repairs. Replaced module in the RC. Ran plot graph. Walk tested and calibrated zone. Tested ok.
MSA-DCS | WA3739923 | main kitchen light in the pot wash globe has blown needs 4ft LED vandle resistant light | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 14:30:00 | Pass | Replaced led batten in pot wash area
MSA-DCS | WA3739936 | Unit 1 - A & C A Wing grille not working. Limit switch has snapped off | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 12:49:32 | 2020-11-06 15:30:00 | Fail | 05/11/20Pick up materials06/11/20Replace of limit switch. Test and okay.
MSA-DCS | WA3739949 | Reset Centre- Broken Fire alarm glass, alarm is constantly sounding | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Nov 2020 | 2020-11-05 17:10:14 | 2020-11-25 11:57:00 | Fail | Callout due to kids vandalising breakglass and strobe at outcare visits and activatIng alarm at fip. Bypassed breakglass and reset alarm at fip, breakglass will need to be replaced for newer conventional type and will require metal backing plate to be installed to fix mcp too. Strobe requires replacement aswell normal 24v dc type. (Photo attached)GAAttended site replaced BGA installed backing plate and left normal. Replaced external strobe left normal.
MSA-DCS | WA3739963 | Unit 9, A6 - Cell all smashed up, windows | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 13:16:30 | 2020-11-11 13:30:00 | Fail | WINDOWS REGLAZED & MIRROR REPLACED , REPAIRS MADE TO FRAME
MSA-DCS | WA3739970 | Unit 9, A6 - Cell all smashed up, sink/toilet needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 13:34:37 | 2020-11-06 13:15:00 | Pass | Job commenced later due to prisoners in the wing. The job had been stopped twice more during the morning due to the same reason.Installed new basin and new toilet. Pipework adjusted to suit
MSA-DCS | WA3739978 | Cabinet Shop - Workshop Water filter needs to be changed - see notes | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 12:00:00 | Pass | Replaced filter and flushed fountain as bad taste reported
MSA-DCS | WA3739982 | Kitchen, Back passage - Middle hinge broken on grill gate needs replacing/welding | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-12-01 09:00:00 | Fail | 01/12/20Re-welded middle hinge into place
MSA-DCS | WA3739983 | Unit 9, Cell D11- Inside switch for cell light faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-06 14:30:00 | Pass | Replaced light switch
MSA-DCS | WA3739987 | CCU (11), D4 - redundant wiring in cell from shelf being removed (wires requiring removal) | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-06 09:30:00 | Pass | Decommissioned cell d4 in ccu
MSA-DCS | WA3739991 | Unit 9, C16 - Bedside light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 13:53:52 | 2020-11-05 15:00:00 | Pass | Replaced light switch
MSA-DCS | WA3739992 | Unit 9, Cell C4- Tap dripping from underneath sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-18 08:20:00 | Fail | Renew spindle to basin cold
MSA-DCS | WA3739999 | Unit 2, Cell D1- Shelf metal frame bent away from wall | Hakea Prison | GMP-BR- HO | Building | Steel Work (BU) | Midolo Building Services | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 14:03:08 | 2020-11-10 14:00:00 | Fail | FLAT BAR RE WELDED TO BRACKETS AND SHELF RE ATTACHED STURDERLY
MSA-DCS | WA3740001 | Unit 9, Control office- Light is faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-06 13:00:00 | Pass | Repaired light
MSA-DCS | WA3740006 | Unit 2, Lower landing - 2 smashed glass panels | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 14:12:34 | 2020-11-09 14:30:00 | Fail | PANELS REPAIRED AND WINDOWS REGLAZED
MSA-DCS | WA3740011 | Unit 9, B4 - tap leaking badly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 14:19:12 | 2020-11-21 09:40:00 | Fail | Try to repair basin set Unable to repair due to corrosion order in new set from manufacture
MSA-DCS | WA3740013 | pump shed repair from transfer pump | Wooroloo Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-12-02 13:00:00 | Fail | Transfer pump faulty. Check pump, pipework & controls. Found partial blockage in big dam suction line & foot valve missing. Clear blockage. Fit new foot valve & fittings. Test all pumps.
MSA-DCS | WA3740077 | Sally port main internal door will not open can only open manually | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Nov 2020 | 2020-11-05 20:17:10 | 2020-11-06 19:30:00 | Fail | Reset door controld but to no avail. Checked doors and found right hand inner door not dropping. Contacted PFM to let them know to contact.
MSA-DCS | WA3740089 | ground staff ladies toilets - Toilet runs on in Stall 1 of Staff Female Toilets-see notes | Rockingham Justice Complex | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 15:30:00 | Pass | Complete
MSA-DCS | WA3740124 | Sally port main internal door will not open can only open manually | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 05 Nov 2020 | 2020-11-05 23:32:06 | 2020-11-06 11:00:00 | Fail | 06/11/20Adjusted limit switched with use of EWP.Test Fine.
MSA-DFES | WA3739864 | Light in ISFFT (Applied Training) Toilet Leftside not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 09:15:00 | Pass | Continued on site at 8:45 to repair light in toilets. Found blown tube, replaced tested and continued on site 9:15.
MSA-DFES | WA3739885 | Exhaust Fan in the male toilet behind Change Room 2 not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 14:15:00 | Pass | Continued on site at at 10:45 to fix toilet fan. Found fan motor had failed and unit needed replacement. Left site to pick up new toilet fan from Welshpool. Returned to site and replaced toilet fan, tested then signed out at 12:15
MSA-DFES | WA3740083 | cupboard vol side water leak - call Janine when arrive on site | VFRS Bassendean | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-09 16:02:00 | Fail | Repairing leak under the sink.
MSA-DTAG | WA3739638 | Level 1, FIP Cabinet housing - lower door is broken exposing electrical wiring | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-05 14:30:00 | Pass | PANEL INSTALLED TO REPAIR DAMAGED DOOR
MSA-DTAG | WA3739786 | Cell 3 - Special Clean - Cell 3 Prisoner has been picking her scabs & is now blood on the cell bench | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-05 18:30:00 | Pass | Job completed as per WO
MSA-DTAG | WA3739792 | Lvl 10 - Front Counter- Multiple light globes not working, see notes below | Westralia Square | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-05 14:30:00 | Pass | Repalced 2x faulty footage to corridors and 1x lamp to marriage rooms.job completed
MSA-DTAG | WA3740067 | ground custody Broken lock barrel in Custody kitchen door – Door locked - see notes | Midland Courthouse | GMP-BR-HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-06 08:10:00 | Pass | Attend site. Gain entry to to kitchen door. Replace lock, door handle/furniture and cylinder.
MSA-DTWD | WA3739542 | L Block, Drink fountain lever and extended tap is broken | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 14:37:00 | Pass | Replace broken off jug filler
MSA-DTWD | WA3739568 | G floor, Tower block, small kitchen - lights not working | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-05 12:01:00 | Pass | Replaced faulty fluros and tombstone.job completed
MSA-DTWD | WA3739604 | C block, CG13 - Replace smashed window from break in | Mandurah Campus (formerly Peel) | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-13 09:59:00 | Fail | ATTENDED SITEREMOVED BROKEN GLASSTEMP GLAZED OVERSIZE OPENING6.38 CLEAR LAMINATED SAFETY GLASS1-558 X 2140, 1-558 X 705 PLUS .5 SQM SAFETY FILMGLASS ORDERED AND TINT FILM APPLIED RETURNED TO SITE AND REGLAZED OVERSIZED PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-558 X 28372 MEN REQUIRED
MSA-DTWD | WA3739680 | B Block, Male student toilet- 1x middle male cubicle w.c pan blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 11:15:00 | Pass | unblocked toilet
MSA-DTWD | WA3739753 | T block L1 student male toilet auto urinal blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 12:45:00 | Pass | Unblock urinal
MSA-DTWD | WA3739795 | F Block, FG13- Fault showing on Fire panel | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-24 09:45:00 | Fail | On arrival found no fault, reset panel and test all ok, waiting for a week to see if fault returns,fault has not returned closing job off 24/11/20
MSA-DTWD | WA3739801 | Level 4, plant room - Replace broken SA fan belts | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 05 Nov 2020 | 2020-11-06 17:00:00 | 2020-11-09 14:11:00 | Fail | Recieved BRAF upgrade approval. Completed works and replacement of belts on SAF 1.1 and 1.2. Works area left tidy.
MSA-DTWD | WA3739869 | J Block, J4/5 door locks are faulty | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 11:45:00 | Pass | J Block - J4 & J5 - door locks are faulty.Damaged keys replaced.Locks repaired and replaced.
MSA-DTWD | WA3739876 | Lvl 2, Room B232- broken window | Perth Campus B6 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-20 11:04:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSMADE SAFE BROKEN WINDOW TO ROOF SAFETY FILM USED 1-600 X 1000RETURNED LATER DATE WITH 3 MEN AND HARNESSES TO ACCESS ROOFREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-1325 X 963PLUS SILICONE AND 4.6 L/M OF RUBBER REPLACED
MSA-DTWD | WA3739894 | H Block, H200 CNC Workshop- Lights not staying on White 2 RCD C/B tripping after being on for 10 sec | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-27 11:15:00 | Fail | Attended site and signed in. Completed jsa. Investigated lights tripping breaker. Found faulty tubes starters and ballast in one fluro fitting. Replaced parts with new. Fixed up all fittings with protective metal grate hanging down. Replaced 1 x faulty highbay globe. Tested all. All ok. Completed paperwork. Informed staff of completion of job and signed out. Job complete.
MSA-DTWD | WA3739898 | Centre Block, Room C316- Light switch is sparking | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-06 08:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located C316 staff room. Found switch arcing when turned on. Disconnect and removed old switch. Cabling behind switch was burnt and short. Made tricky to reterminate cabling into switch mech. Replaced switch and mechs. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3739942 | fuel store faulty light switch - Attention AJ | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2021-01-29 13:45:00 | Fail | Job complete
MSA-DTWD | WA3739974 | Lvl 1, male toilet - faulty exhaust fan | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-11 17:30:00 | Fail | Returned to site once weather had cleared. Gained access set work area up and replaced drive belts on central TEAF system. Second tech assist for working at hight. Work area left tidy. Confirmed fan operation.
MSA-DTWD | WA3740023 | A block west female toilet fly is damaged and needs replacing | Bentley Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 05 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 15:35:00 | Pass | ATTENDED SITEREWIRED FLY SCREEN1-110 X 13509 SCREWS USED
MSA-DCA | WA3740579 | Back of building - Plumbing pipe is leaking | Sunset Hospital Heritage Precinct-Building L-Master's Residence-Ground Floor-External | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 15:33:00 | Pass | Locate valve box Bee hive in box report to Phil who will get pest control to remove
MSA-DCS | WA3740147 | Block B - Administration door broken and came off the frame. | Banksia Hill Detention Centre-Administration | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Nov 2020 | 2020-11-06 09:13:49 | 2020-11-06 07:30:00 | Pass | Attended site and found that required locksmith to attend site and fix the door
MSA-DCS | WA3740232 | Kitchen Bratt pan will not tilt | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 06 Nov 2020 | 2020-11-12 17:00:00 | 2021-01-04 14:00:00 | Fail | 26/11/20Attended kitchen Issue - Bratt pan will not tilt.Found tilt motor had loose bolts, a intermittent fault in microswitch. Tightened loose bolts, cleaned cockroaches and Red backs out of control box.Checked tilt switches, no faults.Parts required 1 x Door microswitch04/01/21Fitted parts, tested all ok.
MSA-DCS | WA3740238 | Reception - sally port gate is not working | Melaleuca Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 06 Nov 2020 | 2020-11-06 11:17:05 | 2020-11-06 12:00:00 | Fail | 06/11/20Test and okay
MSA-DCS | WA3740247 | Kitchen rational oven probe broken | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 06 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-25 11:00:00 | Fail | 25/11/20Attended kitchen Issues - Oven temperature probe broken ovens.Removed existing probe and installed new probe in oven.
MSA-DCS | WA3740252 | Unit 3 -Water leaking from tap that is connected to copper pipe in service door | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 07:35:14 | 2020-11-06 10:30:00 | Pass | 25mm valve, 2x 25mm slip couplings, 25mm copper from stock
MSA-DCS | WA3740254 | Unit 13, B7 - shower blocked not clearing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-12 08:30:00 | Pass | Nill
MSA-DCS | WA3740260 | Psych Services -Ceiling Light panel appears to be coming loose from roof, looks like it might fall | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 07:43:31 | 2020-11-06 10:00:00 | Pass | Repaired lights
MSA-DCS | WA3740276 | Sally port - out locking mechanism on the outter doors - not engaging | Greenough Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 06 Nov 2020 | 2020-11-06 15:59:24 | 2020-11-10 07:30:00 | Fail | 06/11/20Inspect fault. Gas struts need to be replaced.Spent 2 hours in Geraldton trying to source parts - not available. Spent 1.5 hours in Perth collecting parts to ensure ready to ship to Geraldton.10/11/20Replaced gas struts in sally port door
MSA-DCS | WA3740285 | Kitchen- Rational Combi Oven (Gas) – keeps aborting on cleaning cycle | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 1 - Kitchen Area | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 14:10:00 | Pass | Could not fault unit, all components test ok and short clean cycle completed. Replaced suspected water solenoid single. Retest ok again. Will keep in touch for staff .
MSA-DCS | WA3740294 | Unit 8, control room - fire alarm continuely activated | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 08:16:09 | 2020-11-06 12:18:00 | Pass | Attended site found vesda isolated and vesda fault zone isolated at sfip. Checked vesda and found low airflow on pipe 2 wing A. Cleaned out all sampling points and left normal.
MSA-DCS | WA3740295 | Mulitple Cameras not working - Seme onsite | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 06:30:00 | 2020-11-06 10:15:00 | Pass | Zone6 camera 8, zone 7 camera 9, zone 8 camera 10 and zone 12 camera 14 all had poor images. Reset power to the camera, TX fiber modems and surge arrestors in the perimeter ECs. All cameras tested ok in the field and at the gatehouse. travel & accommodation on WA3723115
MSA-DCS | WA3740301 | unit 2, Control pod - CCTV monitors not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 08:22:15 | 2020-11-06 11:21:00 | Pass | Found cameras out reset machine and tested all ok
MSA-DCS | WA3740305 | Interview rooms - air-con blowing hot air into rooms | Maddington (South East Metro) | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 08:26:47 | 2020-11-06 15:21:00 | Pass | Replaced the Aircon no 6 Isolator.
MSA-DCS | WA3740309 | unit 9, leaking fire hydrant | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 08:29:50 | 2020-11-20 11:29:00 | Fail | carried out overhaul of leaking hydrant
MSA-DCS | WA3740316 | Control - internla zone 24, perimeter tracks continuously activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 08:42:22 | 2020-11-06 12:00:00 | Pass | Int. Zone 23/24 PXT constant alarming , re calibrate zone and walk test. Zone back to normal operations.
MSA-DCS | WA3740336 | Kaartdijin Mia - smoke detectors damaged x5 will not close - see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-12-13 07:54:00 | Fail | Attended site to complete and electrical contractors had already replaced
MSA-DCS | WA3740371 | Unit 7, B Wing- Tap in cleaning store has fallen off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-06 13:30:00 | Pass | nil
MSA-DCS | WA3740392 | Stores, toilet - light in male toilets at external stores is flickering on & off | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 08:30:00 | Pass | Repaired stores toilets lights
MSA-DCS | WA3740453 | Unit 1, End of unit- Yard Gate Lock is Jamming not double locking | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 10:24:01 | 2020-11-18 11:40:00 | Fail | 06/11/2020. On site. Assessed issue - replacement required. BRAF to be submitted18/11/2020. Attend site. Replace grille lock as per Approved BRAF.
MSA-DCS | WA3740480 | Main Kitchen- Brat Pan is not functioning | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 10:45:51 | 2021-02-09 14:30:00 | Fail | 06/11/20Arrived at site liaise with reception, sign in, walk to the kitchen, identify brat pan, isolate remove panels, test/fault find diagnose and found the hydraulic motor limit switch was sticking, pressed it up and down and seemed to rectified issue but the limit switch will require replacement.1 x limit switch30/12/20Arrived at site liaise with reception, sign in, walk to location, identify brat pan, isolate remove panels, remove faulty limit switch, supply and replace, reassemble all components and test all components for correct function all okay but while testing did notice the up/down rocker switch has a intermittent fault, remove panels and tested the rocker switch found that only 8vdc was passing through cleaned contacts on the switch reassemble all components and tested all components for correct function all okay but the rocker switch requires replacement,1 x tilt switch9/2/2021Sign in Carry out COVID tests Isolate unit Remove and replace switch Check operat
MSA-DCS | WA3740514 | Unit 13, Cell A7- Shower head has a small leak | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 08:30:00 | Pass | Nill
MSA-DCS | WA3740517 | Gascoyne, Blocked Drains | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-10 09:27:00 | Pass | Cleared blockage in the laundry
MSA-DCS | WA3740528 | Jeelia A wing toilet blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 11:12:14 | 2020-11-06 14:10:00 | Pass | Clear blockage to sewer line while on sir request to repair cistern Renew inlet valve Gascoyne A4
MSA-DCS | WA3740561 | Unit 7, C Wing- extractor fan is not working & switch is broken | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 11:00:00 | Pass | Repaired faulty extraction fan in unit 7 c wing
MSA-DCS | WA3740682 | Administration - Lunch Room demountable fly zapper not working | Casuarina Prison | WSM-GR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 13:30:00 | Pass | Investigate and repair admin lunch room bug zapper.
MSA-DCS | WA3740752 | Unit 2, Cell C1- Officer has reported getting a shock from cell door while unlocking | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 13:11:21 | 2020-11-06 17:00:00 | Pass | Investigate and test report of electric shock.All testing detected no fault.
MSA-DCS | WA3740762 | Unit 2, A-B wing - vinyl is lifting off stair treads | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-23 10:00:00 | Fail | NEW STAIR NOSING INSTALLED TO STEPS
MSA-DCS | WA3740817 | Unit 3, Cell B12- window metal wire runner broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 12:30:00 | Pass | RE NEW SPIRAL BALANCES AND REPAIR FRAME
MSA-DCS | WA3740818 | Unit 2, Cell D9- leak coming from under sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 13:00:00 | Pass | Nill
MSA-DCS | WA3740841 | UNit 1, B Wing- abultions block hot water unit not working closest to control | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Nov 2020 | 2020-11-07 15:19:16 | 2020-11-06 18:30:00 | Pass | Inspected hot water unit on roof, checked power supply Removed cold water supply to unit and found no water pressure.Found isolation valve in duct had been isolated.
MSA-DCS | WA3740849 | entry driveway scan under ground prior to excavation | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 17:00:00 | Pass | Scanned for underground services.
MSA-DCS | WA3740865 | Perimeter light not working 16A | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 16:30:00 | Pass | Replaced perimeter light with led
MSA-DCS | WA3740867 | Casuarina Prison - Unit 3 - C Wing - water gushing out of the showers. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Nov 2020 | 2020-11-06 22:41:34 | 2020-11-06 21:15:00 | Pass | Replaced 1x shower spindle in middle shower A-wing
MSA-DCS | WA3740869 | Unit 7 one of the cell shower - Burst pipe-Water flowing everywhere | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 06 Nov 2020 | 2020-11-06 22:57:54 | 2020-11-06 21:40:00 | Pass | Replaced wall top assembly in u7 e wing. Unable to locate isolation valve.
MSA-DFES | WA3740628 | Rear Yard Gate along outside of limestone wall - Retic head broken, squirting water straight up | CFRS Wangara | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-07 05:30:00 | Pass | Call Out & LabourRetic Parts - Large Hunter Gear Drive
MSA-DFES | WA3740828 | Admin, Lecture Room 4 - Emergency Evacuation Speaker in Lecture Room 4 making a loud buzzing noise. | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 10:45:00 | Pass | Continued on site at 9:45 to inspect confidence room speakers. Traced back cables to speaker control box and found speaker settings where allhigh. Adjusted speaker treble and computer output volume and tested found noise had been significantly reduced. Informed staff of issues andcontinued on site at 10:45.
MSA-DFES | WA3740839 | Amenity Room - 2x doors are falling apart, see notes below | VFRS Kwinana | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-12-14 11:30:00 | Fail | Doors have been replaced and painted using the existing door hardware
MSA-DFES | WA3740843 | rear engine room L1 yard protection grill on air con fallen off - see notes | CFRS Welshpool | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-17 14:00:00 | Fail | Investigated Hitachi AC grill fallen off. Repaired temporarily.
MSA-DFES | WA3740844 | Front Yard, near the verge, about half way down.- Sprinkler riser is faulty | CFRS Canning Vale | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 05:30:00 | Pass | Call Out & LabourRetic Parts - Small Hunter Gear Drive & Riser
MSA-DTAG | WA3740346 | Level 1, Sheriff’s Office - Wooden desk privacy screen is falling off | Supreme Court | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-06 14:15:00 | Pass | PRIVACY SCREEN RE SECURED
MSA-DTAG | WA3740661 | L4 Adult Community Corrections- Central Breach Unit lock broken - see notes | Central Law Courts | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 13:11:00 | Pass | No job done, requires electrician to complete works.
MSA-DTAG | WA3740758 | 1903 Building, Courts 2 & 3- Air Con is not working | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 06 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 15:00:00 | Pass | Check couts 2 and 3 and found temps to be high. Access Apac units serving courts and found fans running but no cooling. Check safety controls and found units tripped out on high pressure. Found condenser water to be quite warm. Access cooling tower on roof and check fans. Found fans to have no power. Return to lower ground plantroom and check circuit breaker serving fan. Found circuit breaker tripped. Reset breaker and return to the riif. Found both fans now running. Return to the AC units and reset high pressure cutout. Found compressors to now start and run as normal. Return to the roof and found chemical treatment circulation pump ti have failed and cause the fan circuit breaker to trip. There is already quote to replace the circ pump. Check court 2 and 3 temps. Found temp to now be ok.
MSA-DTAG | WA3740845 | Lvl 1, Tap in the disabled toilet water is constantly flowing | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 13:30:00 | Pass | Complete
MSA-DTAG | WA3740852 | 1987 L2 Chambers of Vaughan JA air con broken down | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 12:00:00 | Pass | Attend site. Investigate AC 3 serving 1987 lev 2 not working. Carry out fault finding of control. Found fan running. Found no call for compressor to start. Trace back to compressor start relay in switchboard and found power not coming through. Pull relay out and put back in. Found power to now go through relay. Found compressor to now start. Check over all electrical conections in unit. Found compressor 1 and 2 too have burnt wiring due to bad connection. Isolate power compressors and cut back burnt wiring. Fit new connectors to wiring and fit on compressor terminals. Deisolate compressor power and test operation. Found both compressors to start and operate as normal.Lev to area is now cooling down.
MSA-DTWD | WA3740361 | E-Cafe first TV from entrance, the digital box, bottom of TV has blown | Clarkson Campus | GMP-BR | ICT/Audiovisual | General AV works (AV) | Techworks Electrical | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 13:53:00 | Pass | Attended site and inspected digital box has melted components inside. I then tried turning the tv on and could not turn it on from the tv or with remote so i opened up the tv and checked the fuses inside and they were not blown so i presume there is a hardware issue within the tv. Recommend replacing the tv.
MSA-DTWD | WA3740422 | I Block, Door lock to front door is faulty and keys to be replaced | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-06 13:45:00 | Pass | Service to lock
MSA-DTWD | WA3740488 | B Block, South door to the Staff room B16 needs to be adjusted as it is not closing correctly | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 08:15:00 | Pass | Attended site, signed in, spoke to fm about problem with door, completed jsa, located problem with door , adjusted settings in door stopper , door now closes softer , cleaned up work area, completed paperwork,signed out ***job completed ***
MSA-DTWD | WA3740521 | E block restuarant kitchen has blocked drains | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Nov 2020 | 2020-11-06 15:07:22 | 2020-11-07 10:06:00 | Fail | Attended site,Jet washed grease lines to E block restaurant kitchen.Tested all lines on completion
MSA-DTWD | WA3740523 | A Block Chiller has a communication fault, will not start up | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 06 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 15:30:00 | Pass | Air Vision attended Friday 6th Nov and rectified issue with chiller in A Block. All up and running now
MSA-DTWD | WA3740569 | Block 2, Room 2G18 workshop- Light switches arcing when lights turned on | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 08:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located workshop in block 2. Found 2 gang switch plate arcing when turned on for about 3 seconds. Disconnect and removed faulty switches. Supply and replace with new 2 gang switch. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3740608 | Block 3, Fitting and Machining main store- Broken light fitting | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 10:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located fitting and machining. Found light in store not working. Tried to change tubes and starter and upon doing so the fitting fell to bits. Advised site to replace with new fitting. Disconnect and removed old light. Supply and replace with new led light. Clean and tidy site. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3740623 | A block AG23A staff toilet leaking - Possibly leaking at flush pipe pan cone | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 16:30:00 | Pass | Replaced toilet
MSA-DTWD | WA3740740 | B block ground B05 AC Plant room AHU8 drive belts badly worn and slipping (B60 Belt size) | Midland Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 06 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 15:30:00 | Pass | Isolated unit, obtained work order for repaires travelled to suppliers picked up parts, returned to site, locked out, carried out test for dead, removed fan gaurd removed belts, fitted new belts adjusted tension. Refitted all covers removed isolation and tested system
MSA-DTWD | WA3740793 | E Block,E200- floor flooding from floor wast drain causing interruptions to classes & safety hazard | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 06 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-09 15:19:00 | Pass | Cleared blockage partially. Need to quote further works to clear.
MSA-DTWD | WA3740811 | B Block, Plant Room- AHU 9 has ceased working | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-12-23 15:32:00 | Fail | Install and commission new Danfoss VSD to AHU 9
MSA-DTWD | WA3740825 | Block 2, Toilets- Exhaust fan not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 11:30:00 | Pass | ATTENDED SITE AND ACCESSED BLOCK 2 TOILET MSSB. FOUND TOILET EXHAUST FAN 1 NOT OPERATING DUE TO SNAPPED BELT. UNABLE TO ACCESS ROOF TODAY DUE TO WEATHER. WILL RETURN THIS WEEKreturned Located Toilet exhaust fan in block 2. Accessed roof and found belt had worn. Replaced 2 x A21 Vee belt from onsite spares. Tested operation and checked timer. All ok.
MSA-DTWD | WA3740826 | Block 3, 3D66 office- Broken light switch in RPL room | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 11:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located RPL room. Found light switch to be damaged and broken. Disconnect and removed faulty switch. Supply and replace with new switch. Tested all okay. Signed out. Job complete
MSA-MRWA | WA3740339 | 2x switch mech’s have failed please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 06 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-06 12:45:00 | Pass | Found two faulty light switches in tea room level 2. Isolated lights and replaced 2x switch mechs. Informed FM of job completion
MSA-MRWA | WA3740430 | LED light above pool table has failed | Materials Engineering Branch-Kitchen-Ground Floor-AE5-Kitchen | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Nov 2020 | 2020-11-13 17:00:00 | 2020-12-10 08:30:00 | Fail | Attended site and signed in. Located lunch room with pool table. Turned on lights and found 1 in back left corner not working. Pulled fitting down to get information on driver and fitting itself. Has power to the fitting all okay. Took photos and will source if we can this exact fitting and report back. Signed out. Job complete Attended site and awaited doors to allow us in for 8am then signed in. Disconnect and removed faulty light. Supply and replace with new led light. Tested all okay. Job complete
MSA-MRWA | WA3740846 | left hand side cubicle toilet cistern broken please replace | Don Aitken Centre MRWA Head Office-Main Building-First Floor-A1.02-Toilet and Shower-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 08:25:00 | Pass | Reppaced water wafer cistern with invisi. Adjusted pipework to suit. Replaced buttons too
MSA-DCA | WA3740954 | Art Gallery of WA - Administration Block (Block A)-Ground- Emergency warning fire panel not working. | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 07 Nov 2020 | 2020-11-09 17:00:00 | 2020-11-08 09:30:00 | Pass | Called out for fault on EWIS. When arrived no fault on panel, security panel switched to manual and PA zone L1+L2 admin block turned on. Cancelled PA zone and switched back to automatic. All ok
MSA-DCS | WA3740907 | unit 7 S-wing no water in the whole wing | Hakea Prison-Unit 5 | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 11:27:26 | 2020-11-07 10:47:00 | Pass | Fixed seized valve in u7Replaced broken cistern in u5
MSA-DCS | WA3740916 | Try to select the camera for different units but malfuntioning | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 13:06:01 | 2020-11-07 14:33:00 | Fail | CCTV keyboard non responsive unable to maneuver camera images, restored comms to keyboard and tested operational.
MSA-DCS | WA3740917 | security camera have gone blank.failed to reconnect | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 13:06:32 | 2020-11-07 14:15:00 | Fail | 30 plus cameras offline. Fiber switch displaying error. Checked all EC Cabinets and found EC14 Fiber switch faulty. 12VDC supply is not ok even power cycling switch always displaying error. Replaced PSU unit 48VDC but to no avail. Replaced Planet switch 1GS-10020MT and power cycled cameras that were not online. All cameras back online now.
MSA-DCS | WA3740919 | Cell call in security unit MSS B1 officers cannot hear conversation | Broome Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 17:33:01 | 2020-11-16 16:47:00 | Fail | Tested cable, found core 4 is damaged.Utilised spare cores and repaired cell call
MSA-DCS | WA3740934 | all cameras perimeter cell units are not working . | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 19:10:14 | 2020-11-09 07:54:00 | Fail | Phone support - contacted site at 1130am, site confirmed power outage due to western power street upgrade, site indicated attendance not required u until power restored. Site advised unit 1 to 4 CCTV is non operational, confirmed both perimeter CCTV and unit cell call restored when generator took over, however systems restarted, site contacted at 1800pm power has restored and unit 1 to 4 cameras restored.
MSA-DCS | WA3740948 | Hot water is not working in unit 1 & 2 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 17:58:13 | 2020-12-14 11:25:00 | Fail | Repaired hot water unit
MSA-DCS | WA3740949 | Waste water pipe behind Unit 4 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 07 Nov 2020 | 2020-11-07 17:56:11 | 2020-11-10 16:00:00 | Fail | 7,11,20Attended site anble to repair pipe need to cut up footpath with concrete saw.
MSA-DCS | WA3741016 | SITE COSTED Bakery- Container freezer not working | Casuarina Prison-Kitchen | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 08 Nov 2020 | 2020-11-08 12:17:06 | 2020-11-23 08:30:00 | Fail | After monitoring freezer over last week, carried out final checks all running ok at present.
MSA-DCS | WA3741030 | Bakery - baguette molder has a torn mat and the guard is damaged | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 08 Nov 2020 | 2020-11-09 09:35:21 | 2020-11-09 17:00:00 | Fail | 09/11/20Found rear belt ripped and cracked on left side due to plastic guard being broken. Trim so customer can still use and remove the rest of guard. Both belts require replacing and all guards as a minimum (some screws missing as well) Other works to unit required: pressure board and exit slide is moldy and should be replaced Bottom tray felt perished and moldy "Sheeting roller gap" knob missing Parts required:2 x Belts4 x Belt Guides1 x Knob 1 x Pressure board1 x ski felt1 x Screw1 x crumb felt Customer used Bakequip to replace parts
MSA-DCS | WA3741031 | The boilers in the provver not working. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 08 Nov 2020 | 2020-11-09 09:38:23 | 2021-02-11 11:45:00 | Fail | 09/11/2020Customer complaining on elements faulty Fault find Found front right tank wet element not heating Found solid state really not activating Replacement required Check all other elements and float valves working correctly, ok. Part required: 1 x Solid state relay 04/12/2020Isolate proover Remove and remove solid state relay Electrically test element to check not faulty ok Heat unit to test Found another solid state relay now faulty and requires replacing Parts required: 2 x Solid state relay11/2/2021Check unit Found unit has been rewired by another contractor as humidity sensor is faulty.Supply 2x solid states as ordered for when unit is repaired.
MSA-DCS | WA3741033 | Unit -2 control Panel -The door control monitor turned off ,Unable to restart | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Nov 2020 | 2020-11-08 14:09:29 | 2020-11-08 12:45:00 | Pass | Unit 2 Door Control computer not working. Windows logged in & operating but EBI software not running. Rebooted PC and all is ok now. Tested door control and all is in working order.
MSA-DCS | WA3741040 | CONTROL ROOM- Perimeter fence is showing offline. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Nov 2020 | 2020-11-08 14:44:55 | 2020-11-08 13:30:00 | Pass | Internal Perimeter offline. Since arriving onsite Perimeter back online. Checked server and Network Manager 2 temporary comms loss but since restored itself. Tested operation of zone and all is working.
MSA-DCS | WA3741113 | overflow pipe connected to waste pipe in gatehouse kitchen, leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Nov 2020 | 2020-11-09 17:31:18 | 2020-11-09 11:48:00 | Pass | Repair leak to condensation line
MSA-DCS | WA3741133 | Behind unit 14 (external) appears to be burst water main, geyser of water shooting up | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 08 Nov 2020 | 2020-11-09 00:21:37 | 2020-11-08 23:30:00 | Pass | isolated temporary blue line poly water service and made safe
MSA-DCS | WA3741134 | Kitchen Fridge No.3 is running at high temp | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Nov 2020 | 2020-11-09 20:27:41 | 2020-11-09 13:30:00 | Pass | Found system with 2 x faulty condenser fans collect parts , return and fit. Test system all operational
MSA-DFES | WA3741015 | The laundry sink tap is leaking. constantly running. | Butler Career Fire Station-Main Building | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 08 Nov 2020 | 2020-11-09 08:17:22 | 2020-11-08 12:15:00 | Pass | Attend site to investigate leaking tap. Found 2-1 laundry tap leaking through spout and leaking on spindle. Service tap and recut brass seat. Tested for leaks, all okay.
MSA-DCA | WA3741771 | Deluge System - Battery Charger Fail | Maritime Museum Victoria Quay-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 13:45:00 | Pass | Investigate pump charger fail. Standby pump isolated due to ongoing faults. Report being actioned to Programmed. Pey-Sue advised.
MSA-DCA | WA3742162 | L block -Bees on water Isolation valve | Sunset Hospital Heritage Precinct-Building L-Master?s Residence | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 09:23:00 | Pass | Completed on the 10/11/2020. All information located on the Technician Worksheet attached.
MSA-DCA | WA3742196 | Broken pole light outside livingstone cafe - see notes below | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 09:00:00 | Pass | Dome reattached to light pole.
MSA-DCS | WA3741339 | Unit 1 D wing showers Shower door hinge broken | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 07:31:33 | 2020-11-09 11:00:00 | Pass | HINGE DOOR REPAIRED AND REPLACE
MSA-DCS | WA3741366 | Turner B02 Light switch broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 14:00:00 | Pass | Replaced broken light switch.
MSA-DCS | WA3741372 | Turner A1 toilet not flushing | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-09 14:05:00 | Pass | Repaced tpilet solenoid and adjusted pipework to suit
MSA-DCS | WA3741381 | Unit 3 C wing shower door hinge broken | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 09 Nov 2020 | 2020-11-11 17:00:00 | 2020-12-23 09:00:00 | Fail | Replaced hinges
MSA-DCS | WA3741387 | B wing desk camera 56-57-26 not working (blank) | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-13 13:00:00 | Fail | Attended site and investigated the fault.Checked cameras 56 and 57 on CCTV tester - Ok.Checked monitor and found that picture is fuzzy - restarted DVR and tested.Cameras 56 and 57 are operational.Found that there is no video signal from camera 28 ( cam 26 is not part of ISU CCTV system).Checked power and connections - found loose connection - reconnected and tested.All ok at departure
MSA-DCS | WA3741390 | Unit 2 D wing showers Sink spout has come off tap set - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 14:55:00 | Pass | Replaced basin spout in the shower area(rhs basin).
MSA-DCS | WA3741410 | Unit 14 - D14 cold water tap hard to turn on. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 11:30:00 | Pass | Nill
MSA-DCS | WA3741430 | SOG board room fluro lights flickering | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-09 14:45:00 | Pass | Repaired lights
MSA-DCS | WA3741434 | Unit 2 Court water fountain (near unit 2 passage) has a power fault, trips C/B | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 09:40:00 | Pass | Unit not chiller. GPO tripper. Needs an electrician toDetermine if issue with GPO or unit itselfAs we don’t have access to controlBoard. If issue is with unit it will require replacement
MSA-DCS | WA3741442 | Bakery lighting breakers within the electrical room have tripped. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-17 11:00:00 | Fail | Repaired faulty lights in bakery using scissor lift
MSA-DCS | WA3741458 | Unit 4 - D Wing window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 14:00:00 | Pass | RE NEWED SPIRAL BALANCES
MSA-DCS | WA3741463 | Unit 4 - B & D spring at the side of cell window has come away and is exposed in Cell D10. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 15:00:00 | Pass | RE NEW SPIRAL BALANCES AND RE SECURE SASH TO WINDOW CELL
MSA-DCS | WA3741471 | Unit 2 - Court Yard side gate west side lock stiff and hard to use | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 10:30:00 | Pass | Service Lock
MSA-DCS | WA3741488 | Unit 4 - C Wing cleaning cupboard has a dripping tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-12 09:30:00 | Pass | Nill
MSA-DCS | WA3741510 | unit 7 E19 Toilet continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 12:35:00 | Pass | Replaced faulty oultet valve and washer
MSA-DCS | WA3741520 | Case Planning, Video Conference 2- Air Con temp unable to be adjusted | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-24 09:00:00 | Fail | Complete. Replaced wall controller with new.
MSA-DCS | WA3741528 | CCU (11) - D5 Smashed windows | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:09:16 | 2021-01-06 13:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3741538 | main kitchen HWS outside kitchen not hot water | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:15:33 | 2020-11-11 12:30:00 | Fail | Complete
MSA-DCS | WA3741557 | Administration, male toilet Urinal - Overflowing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:21:48 | 2020-11-09 12:30:00 | Pass | Nill
MSA-DCS | WA3741562 | CCU (11) - D5 Shelving is smashed and requires repair | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:22:32 | 2020-11-12 13:30:00 | Fail | shelving repaired
MSA-DCS | WA3741566 | Unit 5, B & D Wing(Common Room) - 7x fluro lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 08:30:00 | Pass | Quote to replace damaged dayroom lights.
MSA-DCS | WA3741579 | CCU (11),D5 - Security Camera smashed | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:31:27 | 2020-11-26 13:30:00 | Fail | Removed remanents of old camera from cell, installed new CAT6 cable from CCTV rack to cell location, and brought cable down thru roof slab. Programmed cameraand installed on IndigoVision System, Install new camera licence. Camera functioning correctly providing good picture.
MSA-DCS | WA3741599 | Block B - Administration door broken and came off the frame. | Banksia Hill Detention Centre-Administration | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:40:47 | 2020-11-10 08:45:00 | Pass | Two Locksmiths Required. Attend site. Remove door, adjust floor pivot and door closer, re-install door and test. Normal function restored.
MSA-DCS | WA3741638 | Unit 1, Cell D1- Tap leaking flooding floor | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-09 13:55:00 | Pass | Replaced leaking cold water tap to basin( qtr turn).
MSA-DCS | WA3741641 | Unit 1, Staff toilet is blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 09:59:36 | 2020-11-09 12:40:00 | Pass | Cleared blocked toilet caused by lots of paper.
MSA-DCS | WA3741645 | Unit 1, Cell B4- Broken light switch | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 10:01:28 | 2020-11-09 12:30:00 | Pass | Replace light switch
MSA-DCS | WA3741659 | Zone 11, Camera 1 is not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 10:14:18 | 2020-11-09 15:00:00 | Pass | Travelled to siteTested and found faulty Indigo encoderReplaced with new Indigo encoder from Seme Stock. All replaced and programmed ok.Tested camera recordings and all tested ok. Job complete
MSA-DCS | WA3741662 | SOG base computer training room ass superintendent office roof leaks | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 10:14:31 | 2020-11-09 14:00:00 | Pass | assess, eaves are asbestos, did not continue, sealed flashing as best he could
MSA-DCS | WA3741680 | ground Main Hallway & Computer area in A-wing water leak- see notes | Nyandi Training Academy | SPA-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 10:28:56 | 2021-02-25 09:00:00 | Fail | new box gutters installed - sealed penetration points - multiple locations/ visits
MSA-DCS | WA3741713 | assesments lights faulty x7 and 1x circuit breaker | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-09 15:40:00 | Pass | Replaced 6x lights and RCD on tripping circuit
MSA-DCS | WA3741728 | Unit 14, D3 - shower and sink have partial blockage Water takes a while to disperse | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 13:00:00 | Pass | Nill
MSA-DCS | WA3741789 | boiler house No2 boiler Boiler out on fault twice this morning - see notes | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 0 | CLOSE | 09 Nov 2020 | 2020-11-09 15:30:23 | 2020-11-09 14:45:00 | Pass | Went to site signed in did a tool check.Went to boiler house, found boiler no. 2 burner was turned off, I turned it back on and it ran.Jim onsite said he had turned it off because it had faulted twice.I could not see on the LFL were it had faulted, left burner running and could not get it to fault.I did remove the burner and there was dirt on the flame rod so I cleaned it up and put it back in and ran the burner and it still did not fault.Informed client that if it faults again to take a note of were it faults on the LFL as this will give us a better idea of where it is faulting if the fault returns.Packed up gear and signed out.
MSA-DCS | WA3741964 | Laundry roof leaking, appears to be a rusted valley tray just above the dayroom | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-12-18 19:13:00 | Fail | roof repaired to rectify leaking
MSA-DCS | WA3742044 | Gate house - Keybunch 572 will not release from the keywatcher cabinet | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-09 15:30:00 | Pass | Called to Gatehouse to remove keys from Keywatcher. Found keybunch not releasing. Used software to release solenoid lock which initially released for 1 second, though the pin did not sound as though it retracted. Requested release of key again again NC manulipated peg on slot to release key. Tested operation of key slot, issue resolved.
MSA-DCS | WA3742104 | Abattoir - hot water circulation pump leaking badly | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 13:36:17 | 2020-11-25 15:30:00 | Fail | COMPLETED
MSA-DCS | WA3742107 | Unit 5, B & D Wing- Kitchen sink is leaking, further notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-12 13:34:00 | Pass | Nill
MSA-DCS | WA3742141 | INF 10 Treatment room air con leaking water. | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-10 14:30:00 | Pass | Drain blocked , cut pipe higher and unblock, clean and flush.All operational
MSA-DCS | WA3742143 | Unit 3, C Wing toilet, cistern is broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-18 15:00:00 | Fail | COMPLETED
MSA-DCS | WA3742166 | Orientation Centre east side of prison Parts of lights & power tripping needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 14:38:19 | 2020-11-10 15:30:00 | Fail | Repaired lights
MSA-DCS | WA3742173 | unit 1 cell 13 cell call not working at all | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 14:45:27 | 2020-11-10 11:00:00 | Pass | Replaced defective cell call point with new and test cell call, working ok. Job completed.
MSA-DCS | WA3742193 | Gatehouse control- camera monitor & mouse is not working | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Nov 2020 | 2020-11-09 19:01:42 | 2020-11-09 15:54:00 | Pass | Phoned site, talked site through re-establishing connection between mouse and KVM extender mounted below monitor room desk, talked site staff through restoring images via indigo software. All restored ok.
MSA-DCS | WA3742198 | Kitchen, cool room 1 - handle is loose and not sealing | Bandyup Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 15:07:59 | 2020-11-10 12:00:00 | Pass | Arrived to site.Awaited sign in.Collected by kitchen staff.Checked over frame work.Found door latch broken and stripped.Removed and modified latch to pull in door to seal correctly again.Tested new position and now working okay.Advised chef of works.Noted top right hinge has cracked through the centre.Will replace both door hinges through a DAS repair on maintenance as this is not causing immediate issues and will need to plan time to replace.
MSA-DCS | WA3742207 | Unit 5, house 1 - toilet WC light is broken (LED) | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-19 11:30:00 | Fail | Replaced toilet light with LED
MSA-DCS | WA3742243 | Gate House - Control Room- no power to all computers at front gate | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-10 07:30:00 | Pass | Mains power supply for Western Power failed ( due to local MVA - car v lamp post) UPS in Gatehouse Equipment room failed. Loss of power to Gate Control Equipment until Generator started. Restarted servers, Workstations, monitors, reset tripped MCB on fibre rack and tested to confirm Cell Call, Security and CCTV systems operating. Requested Maintenance staff call UPS contractor to investigate.
MSA-DCS | WA3742246 | SITE COST Gatehouse, Lunch Room- smoke alarm nodes faulty in POD | Casuarina Prison | WSM-BR-SITE | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 09 Nov 2020 | 2020-11-09 20:32:35 | 2020-11-09 19:09:00 | Pass | 9/11/20 JN - Casuarina PrisonAttended site for ‘Simplex not working’. Pod advised that power pole down on Thomas Rd caused power outage to site earlier in the day, no monitoring systems were working afterwards. Since then generators kicked in and power back to site. Checked network talking to other nodes and all ok, graphics and menus working as normal. Pod system all ok left site.
MSA-DCS | WA3742248 | UPS has failed | Casuarina Prison | GMP-BR- HO | Electrical | UPS System Maintenance (EL) | Elec Power Technologies | 0 | CLOSE | 09 Nov 2020 | 2020-11-09 20:44:08 | 2020-11-12 11:15:00 | Fail | Reattendance to replace failed batteries under warranty
MSA-DCS | WA3742264 | External perimeter fence - ODF alarm system is highlighting as pink. | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Nov 2020 | 2020-11-10 01:13:34 | 2020-11-10 10:30:00 | Fail | Confirmed Perimeter was intact and alarming. Attended External Equipment Cabinets, found Modems in EC9 showing level loss. Reset these Modems and proceeded to EC8 and reset the Modems. Circuit indicators in both cabinets indicated full Comms restored. Returned to the Gate Control Room and cleared all alarms.
MSA-DFES | WA3741511 | first level, Conference room - SISCO conference station not working data cable out loose | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 11:00:00 | Pass | Arrived onsite and signed in at 0930Located faulty data outlet in Board room. We replaced faulty mech and patch cabling in comms room. Tested for function and was sighted by Mike at Dfes, all is working correctly. Stopped works at 1100
MSA-DFES | WA3741650 | Tunic Room - Middle fluro light not working effectively | CFRS Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 14:00:00 | Pass | Arrived on site at 13:30 to repair light in the tunic room. Found both tubes blown and starters. Replaced tubes and starters tested then signed out at 14:00
MSA-DFES | WA3741703 | Engine room door 2 not closing smoothly | CFRS Belmont | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2021-04-15 13:15:00 | Fail | COMPLETED
MSA-DFES | WA3741751 | ground PPC room - Evap A/C system in PPC room is constantly dumping water down the drain | CFRS Perth | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 14:30:00 | Pass | Attended service call, accessed roof , found evap cooler serving ppe room had excess bleed run off. Adjusted bleed valve to minimise waste water
MSA-DFES | WA3742088 | Faulty Blinds various locations - see notes | CFRS Hope Valley | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-17 13:16:00 | Fail | completed & Invoiced
MSA-DFES | WA3742124 | engine room - Soft close mechanism on exit door next at rear of engine room is not working | CFRS Belmont | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-13 14:09:00 | Fail | attended site and completed works.
MSA-DFES | WA3742133 | engine room - water leakng through roof in SE corner of Engine room | CFRS Daglish | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-12 10:30:00 | Pass | Repair roof leak se corner of engine room.
MSA-DFES | WA3742147 | Area Outside Mel Pexton’s Office - Lighting faulty at Grant Wilson’s desk tube may need replacing | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 07:30:00 | Pass | Arrived onsite and signed in at 0700Located reported fault with representative from Wilson security. Site advised that there is no fault and they got the lights disconnected due to aco worker getting glare from the fluros. No fault to be fixed.Notified staff and left site at 0730
MSA-DFES | WA3742177 | ground Lift 2 juttering on occasion when elevating/descending - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMPFIN | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-09 16:15:00 | Pass | Check car and landing door rollers, give the doors a learn run , check operation-To be closed out at $0
MSA-DTAG | WA3741482 | Ground - Hammering in water pipes near Presidents Chambers is very loud | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-09 12:20:00 | Pass | Vibration throw main water meter on water Corp side turned off meter undid meter and re done up turned back on slowly noise has stopped
MSA-DTAG | WA3741497 | custody control CCTV screens not working | Armadale Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 11:00:00 | Pass | 9/11/20 - Dylan ParslowFound top left monitor not responding.Reset monitor and cleaned hdmi plug connection.CCTV monitors all working.
MSA-DTAG | WA3742095 | L1 Isolate FIP (Zones 202 & Vesda 76) on Friday 13 November at 16.00pm - see notes | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 22:30:00 | Pass | Isolated performed as required
MSA-DTAG | WA3742113 | Lift 3- St George’s Terrace End flickering light - see notes | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 12:15:00 | Pass | Job completed - Replaced fluros and starters in lifts 2 and 3-To be closed out at $0
MSA-DTAG | WA3742215 | Lvl 3, Male Toilet, Hay Street End- Toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 18:00:00 | Pass | Complete
MSA-DTAG | WA3742217 | Lvl 2, Lift 2- Noisy doors (sounds like about to break). | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-09 19:15:00 | Pass | Car door hanger rollers worn out, replaced the two front rollers and tested. Doors back to normal - to be closed out $0
MSA-DTAG | WA3742220 | Lvl 8- Toilet is blocked in the judicial area and not flushing | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2021-07-02 11:00:00 | Fail | Replaced wall hung pan, new pneumatic cistern and flush buttons.
MSA-DTAG | WA3742381 | RETROSPECTIVE WORK ORDER - Check over security systems post HV shut down and auto reboot | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-09 10:00:00 | Pass | job completed - Attended site and checked all systems on site. All existing servers are running okay and no issues found on site.
MSA-DTWD | WA3741311 | A block L1 A147 Repair floor tiles in Prayer room - see notes | Leederville Campus | GMP-BR | Flooring | Tiling (FL) | AWB Co. | 3 | CLOSE | 09 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-25 16:50:00 | Fail | Works complete
MSA-DTWD | WA3741480 | A block L2 Repair Urinal flush button A Block Level 2 West End | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-26 17:00:00 | Fail | Complete
MSA-DTWD | WA3741586 | BLD 875 covered pen- Faulty light and pen blower | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-14 16:30:00 | Fail | job completed - Light repaired
MSA-DTWD | WA3741611 | BLD 875 Piggery- Burst water pipe in covered shed 1 | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 13:30:00 | Pass | job completed - Repair leaking water pipes to Piggery
MSA-DTWD | WA3741665 | S block, S008 - has a faulty PIR (166) alarm panel has been isolated | Joondalup McLarty Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 16:30:00 | Pass | Inspect PIR 166, no power. Fault and trace cabling issue, terminate cabling in panel. Test and check zones 173, 186, 185, 166, 174, 175 & 167. All ok. Sensor 166 working as normal
MSA-DTWD | WA3741686 | A block, first floor, AF04 - Water leaking again from ceiling | Mandurah Campus (formerly Peel) | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-12 11:30:00 | Fail | Sealed suspected source of leak
MSA-DTWD | WA3741698 | B block driveway retic pipe needs repair faulty - see notes | Balga Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-20 09:30:00 | Fail | 9-11-2020 - Technician exposed the broken pipe, cost to repair will exceed the $1000.00 limit, a BRAF will be provided with cost to date and costs to repair.19-11-2020 - Excavate and repair broken mainline under the asphalt.20-11-2020 - Reinstate asphalt and pavers and clean up site.
MSA-DTWD | WA3741700 | PEST issue in F12 F16 - F12 ants nests, F16 rats | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 10:05:00 | Pass | PEST issue in F12 F16 - F12 ants nests, F16 rats
MSA-DTWD | WA3741717 | A block, Behind the central stair case - Water leaking down the wall near big window down to floor | Mandurah Campus (formerly Peel) | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-12 10:30:00 | Fail | Cleaned old silicone around comms tower flashing and re applied new silicone seal
MSA-DTWD | WA3741741 | E Block , E75 Kitchen – Damaged GPO on south wall | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 13:30:00 | Pass | Attended site and signed in. Located E 75. Found broken vertical gpo on work bench post. Disconnect and removed faulty outlet. Supply and replace with new double vertical gpo. Clean up site. Signed out. Job complete.
MSA-DTWD | WA3741754 | Roof Leak - Main Corridor between C & D Block | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-24 14:00:00 | Fail | Remove and replace roof sheets and box gutter
MSA-DTWD | WA3741758 | D Block, D37 Meat Trades – Leaking waste pipe under basin | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-13 15:44:00 | Fail | Chrome waste was leaking due to blocked brand drain. Unblocked drain with kinetic ram and the re installed chrome waste.
MSA-DTWD | WA3741762 | Block 8, 8G37 and 8G36- Lights tripping RCD W2 | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-09 13:45:00 | Pass | Attended site and signed in. Got keys from facilities. Located 8g37. Found lights to be off. Went to switchboard and found breaker off. Tested out cabling and RCD function before turning back on RCD. Found no faults present. RCD passes. Reconnected and tested circuit live. Tested room by room and no faults were present. Found 3 x lights flickering and not lighting up. 1 x light was buzzing. Replaced tubes and starters and inspected ballasts to ensure no burnt out marks. Could not pin point fault to anything specific. Tested multiple times in all rooms to see if fault will appear. All lights okay on circuit. Possibly a suspect RCD. Notified staff on site of issue and if happens again that’s the path we will take if still no hard fault is found. Signed out. Job complete
MSA-DTWD | WA3741772 | D block ground security alarm panel has a system fault | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 11:15:00 | Pass | Attend site to investigate fault on D Block, found dialler to be overflowing causing issues with monitoring. Checked GSM unit, seems to be ok. Checked dialler, seems to be intermittent issue with buffer overflow, reset dialler, all working as per normal
MSA-DTWD | WA3741785 | G floor, Tower - Flickering fluro lights | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 15:11:00 | Pass | Repalced fualty fluro and starter to lights ground floor.job completed
MSA-DTWD | WA3741987 | Block 10, 10G66 Creche - Tap in toilet very loose on basin | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 14:29:00 | Pass | replAced tap, installed mini stop
MSA-DTWD | WA3742078 | north end of F block carpark pot holes | Rockingham Campus | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-12-07 17:00:00 | Fail | job completed - All repairs being: sweep repair areas / emulsion / infill and lay asphalt patches as flat as possible
MSA-DTWD | WA3742146 | L1 S100 passage Concealed Gutter S100 corridor leaks badly onto passage | Mount Lawley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-10 13:00:00 | Pass | repair box gutter that is congealed, lift sheets and repair timber work as required. if continues leaking will require new flashings to be ordered - however since we were told to close off old old/2020 roofing jobs and that we can't keep them open while we wait to see if it continues to leak. we just have to wait until site re-issue this job again BUT NOT AS A RECALL!!!
MSA-DTWD | WA3742155 | E Block, Water coming through light fitting in large scale kitchen | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-09 15:45:00 | Pass | Attended site and signed in. Met with staff on site. Located light with water coming out of them. Accessed light in large scale kitchen and removed from ceiling and isolated. Placed dead back into ceiling. Removed emergency light in hallway and placed in switchboard. Water coming out of ceiling tile. Site advised to leave isolated until further notice. All safe. Signed out. Job complete
MSA-DTWD | WA3742160 | E Block Canteen- Auto door continuously cycling | Rockingham Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 11:56:00 | Pass | Call to site. Attend to auto door. Find internal sensor self activating. Complete critical calibration due to environmental factors. Test operational and safety features- okay.Please note that there is no charge for this call out as it is covered under warranty from the previous call out.
MSA-DTWD | WA3742163 | J block ground J107 entrance Water in the entrance foyer of J Block | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-26 12:15:00 | Fail | J block - investigated are above leak, found 2x pairs of sheets to be rusted through on spots. made temp repair, measured pan inserts. Fitted custom pan flashings to area.
MSA-DTWD | WA3742171 | Lvl 2, Room W204- Swipe card reader not working | Perth Campus B1 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 09:30:00 | Pass | Restarted controller and confirmed that the device was online.
MSA-DTWD | WA3742189 | F Block, Room FT02 staff office- Roof leak coming through strip ceiling | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-10 13:30:00 | Pass | Sealed suspected source of leak. Confirmed by site leak has been resolved
MSA-MRWA | WA3742212 | Eastern fumehood.- Fume hood RCD to gpo’s fail, Reset button does not reset RCD light. | Materials Engineering Branch-Asphalt Lab-Ground Floor-Prep Area | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 09 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-11 16:05:00 | Fail | Inspected rcd gpo . Site advised they will get manufacturer to come and repair.job complete
MSA-MRWA | WA3742213 | concrete lab - MEB - external tap to Soils Lab coming loose from wall. Frequently used tap | Materials Engineering Branch | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 15:20:00 | Pass | Applied sealant/adhesive on outdoor tap spud.
MSA-DCA | WA3742565 | Reticulation leak in zone 13 | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Plumbing & Drainage | Materials (PD) | Earth & Water Pty Ltd | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-10 12:15:00 | Pass | Sprinkler heads were fine so the leak is likely come from a slow closing solenoid valve.
MSA-DCA | WA3742714 | Power socket out of the wall/ Broken (can be a Hazard) | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2-S5 - Dressing Room | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 12:30:00 | Pass | Remove existing gpo, replace with new gpo. Test and label gpo.
MSA-DCA | WA3742728 | isolate leaking pipe - Pest control have now removed bees | Sunset Hospital Heritage Precinct-Building L-Master's Residence-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 16:11:00 | Pass | Repaired burst pipe on the wall
MSA-DCA | WA3742744 | Facing left hand side tap dripping slowly | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 2-S5 - Dressing Room | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 12:21:00 | Pass | Service and rewasher basin set LHS.
MSA-DCS | WA3742347 | Sally port in the reception area is not closing. | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 10:27:13 | 2020-11-10 08:45:00 | Pass | Sallyport door fault. Reset controller and tested door functions, found door not opening or closing correctly. Issue with motor calibration as door has been hit by truck. Requires Marshall beatie to recalibrate
MSA-DCS | WA3742348 | front sally port door in gatehouse - not closing correctly | Melaleuca Prison | GMP-BR- HO | Building | Security Doors (BU) | AFD Contracting | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 10:11:24 | 2020-11-10 10:10:00 | Pass | 10/11/20re-aligned limit switches with EWP
MSA-DCS | WA3742364 | Lights tripping out again in the Dairy packing room | Karnet Prison Farm-Dairy Cool Room | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 06:24:23 | 2020-11-10 11:00:00 | Pass | Investigate tripping lights in dairy. Found moisture in some lights. Disconnected damaged lights.
MSA-DCS | WA3742376 | SITE COST Melaleuca Prison-xray machine at the gate house is malfuncition | Melaleuca Prison | WSM-BR-SITE | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 10:50:27 | 2020-11-10 09:45:00 | Pass | Attended site and reset Xray machine and ran full tests and retested xray machine. All tested and working ok. Job complete
MSA-DCS | WA3742389 | control camera 173 and 17 no connection | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 07:22:36 | 2020-11-12 15:55:00 | Fail | Repaired multiple camera faults in perimeter, zone zontrol 2 and obs posts.Tested okJob complete
MSA-DCS | WA3742399 | Unit 13 - C11 tap in sink constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 09:30:00 | Pass | Nill
MSA-DCS | WA3742405 | Western Gym Prisoner toilet door broken | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 10 Nov 2020 | 2020-11-16 17:00:00 | 2021-04-07 10:30:00 | Fail | Replaced cubicle door and hinges. Prison to Paint door
MSA-DCS | WA3742449 | Unit 9, B4 - Water leak in basin cracked pipe water leaking onto floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:05:07 | 2020-11-10 13:35:00 | Pass | Basin taps leaking replaced x 2 quator turn taps
MSA-DCS | WA3742454 | Unit 8, C10 - Cell floor leaking needs repair water coming up through pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:09:56 | 2020-11-10 14:35:00 | Pass | Removed rubbish from drain plunged to clear
MSA-DCS | WA3742495 | visits Hot Water unit in tea room needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:14:20 | 2020-11-11 10:45:00 | Fail | Filter due causing slow flow. Unit was reported as not working. But was operating correctly just over due for filter change also needed Zip PLV Kit changed + Filter
MSA-DCS | WA3742504 | Unit 8, Control office staff room - Hot water urn keeps tripping power needs repair | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:18:12 | 2020-11-10 12:00:00 | Pass | Repaired urn
MSA-DCS | WA3742516 | Abattoir faulty electric pump in smallgoods area | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-24 15:00:00 | Fail | Investigate pump in abattoir small goods area. Requires repair/replace. Remove pump from service.Collect repaired pump and reinstall
MSA-DCS | WA3742531 | visitors centre side wall light flickering LED light | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-18 16:57:00 | Fail | Unable to locate similar light fitting, spoke to site, happy to leave until other light fittings fail in the future and replace all at once.
MSA-DCS | WA3742535 | CCU, Control Pod - Camera Monitor Blank | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:31:04 | 2020-11-24 14:21:00 | Fail | Attended site and repaired multiple faults.Tested OK.Job Complete
MSA-DCS | WA3742540 | control monitor 2 one of the screens is purple | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-10 15:01:00 | Pass | Investigated and repaired display fault.Tested OK.Parts (SEME Stock):PSU / ConsumablesJob Complete
MSA-DCS | WA3742544 | Unit 2, A13 - Fire panel false alarming | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:35:05 | 2020-11-10 11:58:00 | Pass | 10/11/20 EIAttended site for unit 2 cell A13.On arrival VESDA reporting low flow on pipe 2.Cleared sample point in cell & blew out pipe 2.System status displaying normal on departure.
MSA-DCS | WA3742571 | Yeeda, Nicol - roof leak in tango S.O office | Banksia Hill Detention Centre | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-12-10 14:15:00 | Fail | roof repaired to rectify leaking
MSA-DCS | WA3742578 | east gate broken hydrolic ram ajacent to the admin building | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 08:58:08 | 2021-01-13 14:00:00 | Fail | 10/11/20Broken casing. New casing required. Arm taken off for manual mode. BRAF to be submitted and parts to be sourced then ordered.13/01/21Replace motor & controller
MSA-DCS | WA3742590 | Reception, Store room - Two fluorescent lights in store room between box area E & F need repair, | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 11:30:00 | Pass | Repaired lights
MSA-DCS | WA3742593 | Reception Hot Water unit in staff room not functioning needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 09:02:34 | 2020-11-11 10:05:00 | Fail | Unit completely. Blocked letting no water trough. Filter. All now ok
MSA-DCS | WA3742597 | Kitchen, dishwasher - not working | Melaleuca Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 09:06:53 | 2020-11-20 13:30:00 | Fail | 11/11/20Sign in Wait for escort as no staff available Escorted to kitchen Found dishwasher tripped at breaker Reset Fault find Found cable controlling door switch split and earthing out to frame. Repair and test Found contactor controlling wash tank elements stuck on mechanical and now not allow power through. Machine able to be used still Parts required: 1 x Contactor20/11/20Arrive at site to fit parts, fit and test all ok.
MSA-DCS | WA3742616 | Unit 7, H17 - faulty Toilet flush button needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 09:15:32 | 2020-11-10 15:38:00 | Pass | Flush button broken replaced with new
MSA-DCS | WA3742621 | Unit 5, Court yard windows - between cells A10 to 19 windows leaking when sprinklers are on | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-26 12:00:00 | Fail | all bottom of windows re sealed
MSA-DCS | WA3742629 | Recreation West, Staff office - Roof leak kitchen area above cup holder | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA3742643 | zone 1 gate not alarming when open | Boronia Pre-release-External Area | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 13:31:48 | 2020-11-10 12:00:00 | Pass | Travelled to site and rearmed alarm zone for zone 1 gate. Retested zone and all tested and working ok. Job complete
MSA-DCS | WA3742645 | Education, Classroom 1 & central lobby - 2 Roof leaking – See Alice Mcnulty when on site | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2021-04-08 09:00:00 | Fail | REPAIR & REPLACE BOX GUTTERS & ROOF SHEETING
MSA-DCS | WA3742654 | Unit 7, B wing -Hotplate in B wing not working. Has not tripped power on switchboard though. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-18 12:20:00 | Fail | Return to replace hot plate element
MSA-DCS | WA3742681 | Control - Cell call system computer time is not correct | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 09:49:21 | 2020-11-10 14:56:00 | Pass | Repaired faults with cell call and tacera equipment time syncronisation. Confirmed all officer stations, tacera computers and server are synchronised with GPS time. Job Complete
MSA-DCS | WA3742734 | Unit 2, Outside lower landing, hot water unit keeps shutting down | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-19 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3742736 | Unit 2, donga 77 - 80 no hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-20 14:45:00 | Fail | COMPLETED
MSA-DCS | WA3742785 | SHU Entry Door #22 can't close and its wide open | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-10 12:30:00 | Pass | Following site wide mains failure previous afternoon SHU doors PLC and workstation pc were no longer in sync. Reset both, tested and confirmed correct operation of doors.
MSA-DCS | WA3742822 | Farm chainsaw shed- no power to gpo | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-12-14 13:00:00 | Fail | Investigate power in chainsaw shed. Found fault with compressor. Requires parts to repair.
MSA-DCS | WA3742830 | dairy packing roof leaking over light fittings | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2021-04-08 09:00:00 | Fail | LEAKS LOCATED & REPAIRS MADE TO AREAS OF PENETRATION
MSA-DCS | WA3742848 | WWTP air activated valves faulty | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-12-03 09:30:00 | Fail | WWTP Air Activated Valves faulty, leaking. Remove faulty valve. Order new valve. Return to site for install. Report to staff.
MSA-DCS | WA3742851 | Yeeda - Cell Call system is not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 11:15:53 | 2020-11-10 15:42:00 | Pass | Yeeda cell call system indicating interface error, reset node with no change, removed CI3210 to find corrosion on interface card (Angela interface right side) cleaned and removed corrosion, repaired restored and tested fully operational.11/11/20 RESTART 3210 ,CHECKED CELL CALL FROM UNIT, ALL OK
MSA-DCS | WA3742872 | Unit 5, B Wing dayroom- Hopper window Grill left side of yard door damaged | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Midolo Building Services | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 15:00:00 | Pass | RE HUNG HOPPER WINDOW GRILL AND REPAIRED FRAME
MSA-DCS | WA3742875 | Unit 1 B8 Sink waste broken (remove sink to repair) | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-18 09:20:00 | Fail | Renew basin waste
MSA-DCS | WA3742876 | Karakin, Cell A07- Cell call system not working (unable to communicate) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-10 15:45:00 | Pass | Replaced cell call point in karakin block for new changed backing plate and cabling to suit new cell call point, tested operational.
MSA-DCS | WA3742878 | Karakin, Cell A05- Shower to hot & unable to adjust temp valve | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 10:35:00 | Pass | Replaced, tested fualty tmv. Adjusted pipework to suit
MSA-DCS | WA3742884 | Jasper, Cell C01- Smashed mirror | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 12:30:00 | Pass | SMASHED MIRROR REMOVED & REPLACED WITH NEW
MSA-DCS | WA3742947 | laundry wash house Washing machine 2 - major noise when spinning clockwise - see notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 11:57:10 | 2020-12-04 15:00:00 | Fail | No 2 WM very noisy when rotatin - motor mounting plate completely collapsed. Removal of motor mounting plate and rebuild of mounting plate
MSA-DCS | WA3742949 | Unit 1, Cell C2- Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-16 08:30:00 | Fail | Renew spindles to basin hot and cold
MSA-DCS | WA3742963 | Unit 1, Cell D9- Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-16 10:00:00 | Fail | Renew spindles to basin hot and cold
MSA-DCS | WA3742966 | Unit 2, Cell A6- Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-16 11:30:00 | Fail | Renew spindles to basin hot and cold
MSA-DCS | WA3742971 | Unit 2, Cell A12- Sink Smashed | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 12:07:39 | 2020-11-17 14:29:00 | Fail | Took photos off basin to order in correct one cleaned up broken basin and replaced toilet seat
MSA-DCS | WA3742977 | unit 1, Cell B10- Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 10:30:00 | Pass | Removed broken floor tiles in shower recess and replaced.Removed silicone and resealed.
MSA-DCS | WA3742989 | Unit 1, Cell B11- Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 10:30:00 | Pass | Removed broken floor tiles and replaced.Removed silicone anresealed.
MSA-DCS | WA3742997 | Unit 1, B16 - broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-19 12:30:00 | Fail | Removed broken floor tiles in shower recesses Removed silicone and resealed.
MSA-DCS | WA3742999 | Unit 1, Cell B12- Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-12 08:30:00 | Pass | Removed broken floor tiles in shower recess and replaced.Removed silicone and resealed.
MSA-DCS | WA3743000 | Unit 1, B15 - broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-19 15:00:00 | Fail | Removed broken floor tiles in shower recesses.Removed silicone andresealed.
MSA-DCS | WA3743001 | Unit 1, B14 - broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-12 11:30:00 | Pass | Removed broken floor tiles in shower recess and replaced.Removed silicone and resealed.
MSA-DCS | WA3743004 | Unit 1, B13 - broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 14:30:00 | Pass | Removed broken floor tiles and replaced.Removed silicone and resealed.
MSA-DCS | WA3743066 | skills house front door lock when shut cannot open from inside | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 12:51:54 | 2020-11-11 09:00:00 | Pass | Job cancelled when nearlt there Call out to be Charged ..
MSA-DCS | WA3743165 | Cleaning - Male plug top is not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-23 07:49:00 | Fail | Repaired faulty vacuum and polisher, picked up replacement parts, installed and tested
MSA-DCS | WA3743168 | Unit 14, cell C11- Sink is blocked, see notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 09:30:00 | Pass | Nill
MSA-DCS | WA3743185 | Unit 6 - Office carpet in the Senior Officer's office is wearing and buckling under the chair. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2021-02-23 13:30:00 | Fail | damaged carpet lifted & replaced with new
MSA-DCS | WA3743190 | Uquhart unit the middle hand rail unsteady and damaged a hazard | Banksia Hill Detention Centre | GMP-BR- HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Midolo Building Services | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 14:31:34 | 2020-11-17 10:30:00 | Fail | HANDRAIL RE SECURED- STEEL BRACKETS FABRICATED TO SECURE POSTS
MSA-DCS | WA3743203 | One of the cameras is not showing up on the other monitor screens | East Perth | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 14:30:00 | Pass | Camera 4 not displaying on monitor Located on Level 2 General Area after network issues. Installed multi display viewer on system and dragged camera 4 over to appropriate tile on monitor. All is in working order.
MSA-DCS | WA3743221 | Unit 14, B11 - faucet in sink in B11 is on and wont turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 10:30:00 | Pass | Nill
MSA-DCS | WA3743268 | Gate control- cardex manual camera selection not working | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 15:39:59 | 2020-11-16 12:00:00 | Fail | Confirmed Gate Control Officer was viewing incorrect monitor on workstation. Confirmed correct operation when viewing correct monitor. Provided instruction.
MSA-DCS | WA3743292 | SITE COST Unit 5, A Wing shower - Shower is constantly running with hot water, can not isolate | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 10 Nov 2020 | 2020-11-11 16:04:25 | 2020-11-10 20:51:00 | Pass | Located isolation valves turned off water replacing x2 quator turn taps
MSA-DFES | WA3742421 | breather app room vols side roof leak | CFRS Armadale | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 10 Nov 2020 | 2020-11-10 17:00:00 | 2020-11-10 15:00:00 | Pass | Sealed suspected leak and painted out water stain on ceiling panel with vin sealer
MSA-DFES | WA3742836 | front security gate not operating at al | CFRS Claremont | GMP-BR | Security | Access Control (SE) | Anvil Doors | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 13:30:00 | Pass | Attended P1 call out for non operational gate. Checked and found that safety beams to gate were flat so replaced all battery. The gate then functioned correctly. Issue resolved.
MSA-DFES | WA3743140 | L1 and L2 printer and wellness office leak in the window ledge on both levels | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2021-03-11 12:00:00 | Fail | New external seals have been installed to offending windows. Water test has been completed and no leaks are found
MSA-DTAG | WA3742818 | custody control - Custody are having problems with the security cameras | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Total Security Systems Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-13 11:45:00 | Fail | 10/11/2020 - Alan Marshall - 1.30pm to 3pmRestarted VSS camera and it is back online. Nvr Time was out of sync. Re synced times and camera times. Nvr 1 and 2 have hard drive issues. I have taken diagnostics and sent to tech support.13/11/2020 - Alan Marshall - 11am to 11.45amRestarted NVRs as advised from indigo and disk status is back to normal. I have tested burning of footage and all is ok. Adjusted camera times
MSA-DTAG | WA3742943 | G Floor, Filing Room - Roof leaking water all over the floor | Perth Children's Court | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2021-02-25 09:00:00 | Fail | MULTIPLE VISITS - SOURCE OF LEAKS ADDRESSED, REPAIRED
MSA-DTAG | WA3743062 | Lvl 3, Public toilet - Toilet roll holder in female toilet is broken, further notes below | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-19 09:45:00 | Fail | Toilet roll holder replaced
MSA-DTAG | WA3743082 | Special Clean in Cell 2 - Accused thrown coffee and food all over the cell floor and walls | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 19:00:00 | Pass | Special Clean in Cell 2
MSA-DTAG | WA3743262 | Unisex Public Toilet - Toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-10 17:30:00 | Pass | Complete
MSA-DTWD | WA3742410 | A block L1 A146 lights staying on in store | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 10 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 08:51:00 | Pass | Repalced faulty light switch and reconnected cabling .job completed
MSA-DTWD | WA3742478 | A block AM125 2x fluro tombstones broken | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-10 14:00:00 | Pass | Attended site, signed in,spoke to fm about job, fm said he wanted old lights replaced with led batons , went to wholesaler to pick up lighting, returned to site, completed jsa, isolated lighting circuit, removed old lights, replaced with new lights,reenergised lighting circuit, tested lights, working as intended, cleaned up work area, completed paperwork,signed out ***job completed ***
MSA-DTWD | WA3742561 | F block gastech alarm has been activated | Carlisle Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | GASTECH AUSTRALIA PTY LTD | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 11:30:00 | Pass | Job completed - replaced sensor
MSA-DTWD | WA3742647 | E Block, SK3 has two Blue Seal tagged out ovens not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-16 09:30:00 | Fail | completed 9.30am 16/11/20
MSA-DTWD | WA3742659 | E Block, SK3 2nd Student sink Left Hand Side of room is leaking at floor join | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 15:30:00 | Pass | Attended site,Investigate leaking sink, locate seals to trap failing. Supply and install new trap seals and test on completion.
MSA-DTWD | WA3742661 | E-Block Restaurant Kitchen has a water leak through a light fitting | Joondalup Kendrew Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-12 12:42:00 | Fail | Reconnected lights and checked for water ingress. All safe.job completed
MSA-DTWD | WA3742940 | E block ground E200 workshop We have two leaks in the F&M workshop. - see notes | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-10 14:25:00 | Pass | **Was shown leaks on site prior to WORK ORDER being raised - hence CSS times**Sourced leaks - sheets rusted out at joint in multiple spots - resealed perished seals.
MSA-DTWD | WA3742953 | E block, ground, Restaurant Kitchen - broken water main in ceiling | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 16:00:55 | 2020-11-10 16:00:00 | Pass | Repaired leak on aquatherm water service.
MSA-DTWD | WA3742956 | Main entry sliding doors to tower building are closed & will not open | West One Services | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 16:01:40 | 2020-11-30 16:27:00 | Fail | 1086344 (new number) upgraded door as per quote, tested all ok
MSA-DTWD | WA3743040 | F Block, Work shop F11- roof leak opposite main distrubition board | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-10 15:00:00 | Pass | Sealed suspected source of leak. Site confirmed leak has been resolved.
MSA-DTWD | WA3743095 | C block compound gate metal has been bent on the gate needs to be secured | East Perth Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 0 | CLOSE | 10 Nov 2020 | 2020-11-10 17:07:47 | 2020-11-11 14:20:00 | Fail | Repair latch and bend back metal for gate to close properly
MSA-DTWD | WA3743145 | Faulty light in hallway near entrance to Jobs & Skills. See notes below | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 09:30:00 | Pass | Attended site and signed in. Located hallway to job and skills centre. Couldn’t find any lights out. Or flickering. Rang facilities to get confirmation on the job. Light was flickering, replaced all tubes in half lights working. Upon replacing tubes and starters 2 x tombstones fell to bits. Replaced 8 x tubes and starters and 2 x starter end tombstones. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3743154 | A block male urinal - continually running urinal replace cistern, flush button | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 14:38:00 | Pass | Replace cistern button and flush pipe for urinal
MSA-DTWD | WA3743157 | Faulty light in hallway in front of toilets | Armadale Campus - 40 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 08:15:00 | Pass | Attended site and signed in. Spoke with staff regarding lights flickering. Checked out all of site for flickering lights. Replaced faulty lamps to downlights in rear hallway. Tested all okay. Signed out job complete
MSA-DTWD | WA3743170 | Block 8, 8G45/46 lunch room- Water leak | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-12-01 12:00:00 | Fail | Replaced 4 rusted out roof sheets and 4.5m of flashing to Block 8, 8G45/46 lunch room
MSA-DTWD | WA3743171 | Block 8, 8G19 staff lunch room- Water leak | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 13:00:00 | Pass | Sealed several areas suspected to be causing the leaks
MSA-DTWD | WA3743173 | Block 6, Painting & Decorating- Water leak | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 15:30:00 | Pass | Sealed around several suspected causes of the leak
MSA-DTWD | WA3743296 | A Block, Male toilet- End cubicle cistern is constantly running | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 16:00:00 | Pass | Fix issues with toilet
MSA-MRWA | WA3743298 | Blocked cubicle please attend and remediate | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor-A4.02-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 14:35:00 | Pass | Replaced inlet valve and outlet washer in cistern
MSA-MRWA | WA3743300 | Cubicle flush button damaged, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Nov 2020 | 2020-11-11 17:00:00 | 2020-11-11 15:16:00 | Pass | New seals kit and refitted button and water wafer kit in cistern
MSA-DCA | WA3746515 | broken glass on window small sqare | Sunset Hospital Heritage Precinct-Building L-Master?s Residence | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 12:00:00 | Pass | Siliconed clear perspex sheet over hole. Sign off on works approved by David De Villiers
MSA-DCA | WA3746516 | Rear of property fence has a hole in it | Sunset Hospital Heritage Precinct-Building L-Master?s Residence | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-12 12:30:00 | Pass | Replaced approximately 4m of damaged chain mesh fencing
MSA-DCA | WA3746649 | 2nd cubicle as one enters Full flush stuck inwards | State Library of WA-Main Building-Ground Floor-Female Toilets - Rear Entrance Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 12:30:00 | Pass | Renew inlet valve
MSA-DCA | WA3746665 | Full flush doesn’t work | State Library of WA-Main Building-Ground Floor-Male Toilet - Rear Entrance Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 09:15:00 | Pass | Replaced bellow and button rubber on the full flush(2nd cubicle)
MSA-DCA | WA3746674 | Staff ladies toilet – first cubicle Water continues to run after flushing unless pressed a few time | State Library of WA-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 08:20:00 | Pass | Replaced fualty inlet vakve and adjusted button
MSA-DCA | WA3746679 | Water runs continuously (has been switched off) | State Library of WA-Main Building-Level 3-3.97 - Staff Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 13:47:00 | Pass | Renew broken push button
MSA-DCS | WA3746309 | front gate house sally port not opening/closing on computer controls | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Nov 2020 | 2020-11-11 11:12:50 | 2020-11-11 08:45:00 | Pass | Mechanical issue not from EBI systems, advice SO gatehouse to raise a job from different contractor who deals with motorised gates.
MSA-DCS | WA3746313 | control room gate house Tacera has no connection | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Nov 2020 | 2020-11-11 11:15:45 | 2020-11-11 13:57:00 | Fail | Investigated faults, repaired multiple cell call faults, preformed backups and tested OK.Job Complete
MSA-DCS | WA3746346 | Patch/Seal/Paint numerous ceiling holes resulting from light replacements to main kitchen | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 07:35:05 | 2020-12-17 15:00:00 | Fail | Patched and painted numerous holes in ceiling
MSA-DCS | WA3746351 | Patch redundant electrical wiring x 2 positions - see notes | Bandyup Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 07:43:44 | 2020-12-17 03:30:00 | Fail | patch and paint all holes in walls and ceilings where electrical and plumbing fittings were previously fitted.
MSA-DCS | WA3746354 | Unit 4 control room Water leaking from ceiling mounted air con | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 11 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-11 12:15:00 | Pass | Found condensation forming on refrigerant pipe at insulation join. Taped up join to prevent further condensation. All ok
MSA-DCS | WA3746380 | front gate control pod Turn Stile not working | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 08:10:34 | 2020-11-11 15:02:00 | Pass | Rectified and fixed the turnstile fault and the lost of camera icons from site maps. Job completed
MSA-DCS | WA3746389 | main kitchen robo coupe stick wizz faulty wiring | Bandyup Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 08:18:26 | 2020-11-17 10:35:00 | Fail | Unit was repaired and returned to site.
MSA-DCS | WA3746394 | entry pod camera's 29,38,51 and 19 faulty freezing and skipping back | Bandyup Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Nov 2020 | 2020-11-11 12:20:21 | 2020-11-11 11:30:00 | Pass | Cam 19 bad image. PSU is measuring 22VAC after reset PSU is measuring 24VAC. Recommend PSU transformer be replaced as its old and obsolete.Cameras 29,38 and 51 were showing signs off lag earlier in the morning. Checked all cameras and could not find a lag issue. Checked camera statistics on live view and all is ok. No fault found with it freezing or lagging.
MSA-DCS | WA3746412 | SHU 9, Cell A8 - Observation light not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 15:00:00 | Pass | Investigate and repair shu cell a8 observation light.
MSA-DCS | WA3746421 | Bakery - baguette molder has a torn mat and the guard is damaged | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 08:32:55 | 2020-11-11 16:00:00 | Pass | COMPLETED 11/11/20
MSA-DCS | WA3746439 | Unit 6 C wing showers 1st. Shower is leaking needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-18 10:30:00 | Fail | Reseat and rewasher shower hot and cold
MSA-DCS | WA3746451 | Unit 7, H9 - Toilet will not flush needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-18 16:00:00 | Fail | Renew push button assembly to cistern renew inlet valve
MSA-DCS | WA3746474 | Kitchen roof leak over lights in extraction fan duct | Karnet Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2021-03-17 09:00:00 | Fail | INVESTIGATED ROOF FOR SOURCE OF LEAK. COULD NOT DETECT AN ENTRY POINT.
MSA-DCS | WA3746477 | gate house sally port is not opening or closing | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 11 Nov 2020 | 2020-11-11 13:07:05 | 2020-11-11 11:45:00 | Pass | 11/11/20Adjust height of drive arm.
MSA-DCS | WA3746478 | Unit 7, light switch damaged needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 11:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3746504 | Unit 7, G11 - Blocked toilet needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 09:24:33 | 2020-11-11 11:30:00 | Pass | Unblocked toilet and replaced flushing mechanism and installed new outlet washer
MSA-DCS | WA3746508 | Unit 7, G7 - Toilet seat & Flusher need repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 09:26:28 | 2020-11-11 13:30:00 | Pass | Replaced broken toilet seat and flush button installed new outlet washer
MSA-DCS | WA3746555 | Unit 3, D wing -Service door between D7 and D8 leaking toilet/toilet service area. Sounds like water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 11:30:00 | Pass | Nill
MSA-DCS | WA3746558 | Unit 4, C9 - sink is clogged and cant be cleared with plunger. sink not draining like it should be | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 10:30:00 | Pass | Nill
MSA-DCS | WA3746561 | unit 4, B12 - Toilet cistern either does'nt fill or runs continuously | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 11:30:00 | Pass | Nill
MSA-DCS | WA3746567 | Unit 3 - D Wing Cell D04 sink tap leaking - constant stream. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-18 10:30:00 | Fail | Nill
MSA-DCS | WA3746597 | laundry hot water tap faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 10:30:00 | Pass | COMPLETED
MSA-DCS | WA3746639 | Bakery power triping out tripping out all power points | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-11 15:00:00 | Pass | Investigate and repaired numerous tripping circuits in bakery
MSA-DCS | WA3746651 | Unit 4, A12 - Observation light not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 08:30:00 | Pass | Repaired faulty lights in unit 4 A12
MSA-DCS | WA3746697 | Unit 4, D wing - Light flickering | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 08:30:00 | Pass | Investigate and repair unit 4 d wing flickering light
MSA-DCS | WA3746718 | gym water chiller taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3746725 | Gym light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 08:30:00 | Pass | Investigate and replace gym light fitting.
MSA-DCS | WA3746727 | Unit 2, Middle landing water cooler isolation tap faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-19 14:00:00 | Fail | COMPLETED
MSA-DCS | WA3746756 | Unit 4 - A5 lock barrel faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 10:45:00 | Pass | Replace worn barrel.A wing lockdown no access.Replace door plate, lock, hinges and weld on door plate.
MSA-DCS | WA3746764 | Unit 4, D8 - Hatch frame broken, nay require new hingers | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 11:00:00 | Pass | Replace hinges and repair latch
MSA-DCS | WA3746782 | Unit 7 control room Control room door is moving out of alignment - see notes | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 12:59:27 | 2020-11-11 14:30:00 | Pass | On site. Service lock and replace worn part to restore normal function
MSA-DCS | WA3746805 | Unit 1, Control Pod - Cameras 5-7 are off line | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-12 10:30:00 | Pass | Rectified and fixed the encoder fault , cam 5 to 7 back online. Job completed.
MSA-DCS | WA3746812 | Unit 2, Control Pod - Cell call hand piece broken | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-12 08:30:00 | Pass | Replaced defective cell call handset and test functions, working ok.
MSA-DCS | WA3746822 | Gate house, Control room - main control panel fauity to power failure gatehouse | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 12:30:00 | Pass | Traced Fault of lack of video from Reception Sally Port to Maxpro SubRack. Reset sub rack controller and reconfigured monitor images in Reception. Returned to Gatehouse and confirmed Reception Sally Port Video now available
MSA-DCS | WA3746844 | Ramp outside Assessments Demountable rotting through | Bandyup Prison | GMP-BR- HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Schlager Construction Group | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-12-22 11:30:00 | Fail | Supplied and installed plates over rotten sections of flooring on ramp.
MSA-DCS | WA3746850 | Unit 2 Broken mains water pipe at the rear | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-12 11:30:00 | Pass | Job requires braff
MSA-DCS | WA3746859 | front gate sally port vehicle barrier - Barrier steel plates Jamming when Raising & Hydraulic Rams | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 14:47:10 | 2020-11-11 16:00:00 | Pass | 11/11/20Centre pins, move collars and grease pins.Pins damaged as well as collars.Temporary fix in place.Parts have been ordered as this was picked up in the last service.Parts coming from Melbourne.Repairs to be completed as part of LVM DAS WA3732535
MSA-DCS | WA3746865 | unit 14 office security camaras are not working | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 14:56:01 | 2020-11-12 11:00:00 | Pass | Following mains power interruption workstation was not able to see Indigo dB. Reset workstation, loaded and logged into program, configured monitors.
MSA-DCS | WA3746867 | Unit 6 - A & C dayroom sink requires repair, leaking underneath. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-23 13:30:00 | Fail | Nill
MSA-DCS | WA3746870 | Main Kitchen - bun divider, broken spring | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 15:06:03 | 2020-11-19 11:30:00 | Fail | 12/11/20Sign inFound RH spring broken off Modify spring as a temporary repair and installParts required. 2 x Head return springs19/11/20Sign in Isolate dividerRemove and replace return springs Test unit ok Advice manager
MSA-DCS | WA3746871 | Unit 14, D wing - D10 hot water tap on shower constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 15:00:00 | Pass | Nikl
MSA-DCS | WA3746873 | Unit 14, B wing - drain grate has been removed and needs rescuing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 16:00:00 | Pass | Nill
MSA-DCS | WA3746896 | Rear staff entry, alarm panel in controller 2 offline - power supply not working | Rockingham Justice Complex | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Nov 2020 | 2020-11-11 18:52:51 | 2020-11-11 15:30:00 | Pass | Found controller 2 offline. Client reported they had power issues. Power cycled and reset battery fail. Battery is all OK. tested operation and all is OK.
MSA-DCS | WA3746901 | cleaning -The edge of the wall in the bin area next to the staff lunch room has loose bricks coming | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2021-03-02 19:36:00 | Fail | REPAIRED/REPLACED DAMAGED BRICKS
MSA-DCS | WA3746903 | Unit 14, D9 - Cold tap is very hard to turn on/off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 11:00:00 | Pass | Nill
MSA-DCS | WA3746905 | Clean up post repair of Urquhart D wing post incident | Banksia Hill Detention Centre | GMP-BR- HO | Cleaning | Materials (CL) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 13:20:00 | Pass | Urquart D Wing Clean up in preparation for reopening
MSA-DCS | WA3747046 | Gatehouse - Sally port door in reception (in prison) is opening by itself, wont close at all now | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Nov 2020 | 2020-11-12 03:48:25 | 2020-11-12 06:15:00 | Fail | Contacted melalouca at 0030 site confirmed system restored, site made further contact at later stage indicating failing again, attended Melalouca to find safety beam setbintermittantly activating, reset and re aligned device that appeared out of range, restored and tested but very unstable, recommend gate be mechanically checked, temporarilly operational
MSA-DFES | WA3746713 | ground carpark Beb Side gate egress button not working - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-12 09:30:00 | Pass | 12/11/20 - Dylan ParslowReplaced normally closed contact and tested.All working.
MSA-DFES | WA3746775 | outside engine room fluro light needs changing deteriorated and rusted - see notes | CFRS Maddington | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 13:45:00 | Pass | Arrived onsite and signed in at 1415We repaired a bedside light in the SOs office. We also investigate a faulty with an exterior light. The light is damaged and us not longer Ingress protected and will need a new fitting. Will need to seek approval for works and will need a 10ft ladder. Signed out at 1445Arrived onsite and signed in at 1300Located faulty light and replaced with new. Site had to leave site for an emergency at 1315 and we could not collect a signature from site.Finished works and left site at 1345
MSA-DFES | WA3746788 | Lift 1 not working | DFES Cockburn Emergency Services Complex | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 18:28:00 | Pass | Lift overrun top floor,reset and tested, cause unknown .Had a SH drive error as well,left in service-To be closed out at $0
MSA-DFES | WA3746801 | Administration ground, computer store room - Wet and bowed ceiling panel in Computer Store Room. | FESA RHQ - Forrestfield | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-24 11:30:00 | Fail | Found leak - have sealed. Remove and replace damaged ceiling tiles. Job complete
MSA-DFES | WA3746869 | level 1, room 12 - Damaged toilet seat | CFRS Ellen Brook | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-12-24 08:00:00 | Fail | Replaced toilet seat in room 12
MSA-DTAG | WA3746520 | Sheriff’s Office, male toilets - Flashing light, Light above hand basin is flashing intermittently | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-30 08:00:00 | Fail | Returned to site with new ballast for Sheriffs Office male toilets. Replaced with new ballast which was causing the light to flicker. Check and tested male toilet lights. All in working order.
MSA-DTWD | WA3746299 | L2 main entrance Sensor on automatic door not working | Perth Campus B5 | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 11 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-11 13:38:00 | Pass | Found that the sensor has failed, replaced sensor and tested, all ok.
MSA-DTWD | WA3746433 | ground main auto door not opening, controller fault | Clarkson Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 14:00:00 | Pass | Attend site to investigate fault with auto door, checked relays, all working as per normal. Found auto door motor to be seized, rebooted the system, all working as per normal at time of testing
MSA-DTWD | WA3746466 | Block 7 ground canteen Chilled food display tripping RCD on sub board. | Thornlie Campus | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-13 12:00:00 | Fail | Attended site, Found condensate tray heater element failed causing main breaker to trip. Locating replacement part. Unit is made out of country and parts may need to come from New Zealand with long delay on parts arrival.Located replacement condensate tray locally.Picked up parts from suppliers. Returned to site. Gained access. Removed old tray and fitted new tray. Wired accordingly. Removed isolation and started unit. Checked operation. All ok cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA3746510 | G block Remove and replace damaged asbestos ceiling sheets above Trade entrance | Rockingham Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-12 15:00:00 | Pass | BRAF Declined
MSA-DTWD | WA3746541 | E block LSK warmer is not warming is needed for lunch today | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 0 | CLOSE | 11 Nov 2020 | 2020-11-11 14:01:09 | 2020-11-11 13:15:00 | Pass | COMPLETED 11/11/20
MSA-DTWD | WA3746672 | Level 2, car park roller door - Roller door not working | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 16:24:00 | Pass | Powered door on. Tested multiple times no fault detected. Tested safety beams etc. still no fault. Suspect when the power was left off. The control board reset itself. Ps programmed no A40574451J.
MSA-DTWD | WA3746708 | U block compresser in fault mode | Rockingham Campus | GMP-BR | Equipment Hire | Compressors, Generators (EH) | Equans Mechanical Services Australia | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2021-01-08 09:30:00 | Fail | Arrived on site signed in. Checked in with Dennis. Gained access keys, gathered tools and equipment started checks on controls and operation. Found Auto drain not operating correctly, also overdue for service. Drained water Checked operation all ok. Two inline filters also require replacing. Reported findings completed BRAF. Cleaned up and completed paperwork and signed out.all works now complete as per BRAF by subcontractors.
MSA-DTWD | WA3746742 | fault with the Irrigation Aerator in the lake at Murdoch Tafe | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | WESTERN IRRIGATION PTY LTD | 2 | COMPFIN | 11 Nov 2020 | 2020-11-16 17:00:00 | 2021-03-18 10:30:00 | Fail | 15-12-2020 The faulty aerator has been removed for offsite inspection, waiting on pricing on parts to repair.23-12-2020 BRAF emailed to wasc@programmed.com.au for approval.18-3-2021 Installed and commission new aerator and air compressor.
MSA-DTWD | WA3746765 | D block ground entrance security panel fault, not dialing to ed sec when arming up | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 14:45:00 | Pass | Attend site to replace faulty dialler. At time of testing signals are working as per normal. Advised TAFE that if this were to drop again to double check SIM card and if that’s all operational possibly a faulty serial port on controller but all seems to be working as per normal at time of testing
MSA-DTWD | WA3746793 | Level 2, Male student toilets - : Remove all drummy tiles from above urinal & save for future refit | Perth Campus B6 | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-20 16:30:00 | Fail | Assessed job, masking tape to tiles above urinal close to falling. Will be back tomorrow to remove tiles. Picked up ply to make shelf above urinal, to catch tiles as they fall. Removed drummy tiles over urinal and toilet. lost a few tiles which were very brittle, and others were stuck with adhesive. Clean up and take photos, and do paperwork.
MSA-DTWD | WA3746816 | Ground floor, 8G3 server room - RCD tripping shutting down server for campus | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-12 14:45:00 | Pass | Investigated faulty RCD. No fault was found. Site advised to close off job
MSA-DTWD | WA3746847 | A block, Level 2, A219 - Replace washers to basin taps A219 | Leederville Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-24 15:00:00 | Fail | Isolation valve in ground was faulty and could not isolate toilet block. Cut out old valve and brough ball valve up to ground level, then proceded to repair leaking taps which I ended up replacing all of them as they were well past their expiry date.
MSA-DTWD | WA3746853 | A block L1 ground Auto door A Block has stopped working | East Perth Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 11 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-11 16:04:00 | Pass | Attended the site and found controller power lead was not in properly, put back power lead into the controller, tested door operation a number of times, all working fine.
MSA-MRWA | WA3746843 | Level 1, Female toilet - Cubicle flush button damaged, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-First Floor-A1.03-Toilet and Shower-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Nov 2020 | 2020-11-12 17:00:00 | 2020-11-11 15:57:00 | Pass | Replaced inlet valve in cistern
MSA-DCA | WA3752304 | Mutliple purpose changerooms - Leaking Tap | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1 | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 13:50:00 | Pass | Replaced leaking and sezied mixer in the disabled toilet
MSA-DCS | WA3751923 | old front gate showers gym Left hand shower blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 07:38:31 | 2020-11-12 12:59:00 | Pass | Clear blockage to shower
MSA-DCS | WA3751929 | Unit 10 A3 Sink pipe leaking badly needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 07:43:02 | 2020-11-12 10:55:00 | Pass | Job delayed due to no escort available. Fixed leakingwaste in the basin
MSA-DCS | WA3751935 | unit 4 K Block front door lock jamming | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 11:47:44 | 2020-11-12 14:45:00 | Fail | Door Lock cylinder Jammimg ..Cylinder removed from door and checked may have had debris in cylinder Mortice Lock checked reassembled and tested with various keys all Ok if happens again - recommend cylinder be replaced Note - door frame / needs new hinges and frame is loose
MSA-DCS | WA3751939 | unit 1 B wing ablusions near WC control blocked will need machine-see notes | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 11:50:36 | 2020-11-12 10:30:00 | Pass | COMPLETED
MSA-DCS | WA3751942 | gate house camera 1 off line | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 11:52:54 | 2020-11-12 12:43:00 | Fail | Rectified and fixed the fault on Indigo encoder, camera 1 back on line.
MSA-DCS | WA3751948 | Unit 4, A & C - Day room window is all cracked and needs replacing | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:02:41 | 2020-12-15 14:15:00 | Fail | DAY ROOM WINDOW RE GLAZED & REPAIRED
MSA-DCS | WA3751961 | Unit 10, C2 - Hot water tap not working. | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:10:08 | 2020-11-12 11:45:00 | Pass | Job delayed due to no escort available. Adjusted valve and cleaned breech
MSA-DCS | WA3751964 | Unit 7, E7 & E8 - toilets continuously running needs repairs | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:14:05 | 2020-11-12 14:30:00 | Pass | Renew inlet valve and out let washer
MSA-DCS | WA3751970 | Unit 7, E wing - showers still leaking under floow into E wing corridor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:15:35 | 2020-11-12 16:30:00 | Pass | Inspect water leak Problem is grout and tiles leaking require tiler
MSA-DCS | WA3751972 | Unit 6, N5 & N6 - Cistern in duct between N5 & N6 leaking Needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:17:37 | 2020-11-12 13:10:00 | Pass | Replaced faulty inlet valve and flexi
MSA-DCS | WA3751974 | CCU (11) - Control Room - light opstructing cupboard from opening | Casuarina Prison | WSM-MW-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-12 12:00:00 | Pass | Investigated and relocated lights in CCU office
MSA-DCS | WA3751975 | Unit 6, A4 - Tap dripping badly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:19:08 | 2020-11-12 14:20:00 | Pass | Locked in the control room for 30mindue to no escort
MSA-DCS | WA3751983 | Unit 6, A6/7 - water running into toilet A6 & 7 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 08:22:15 | 2020-11-12 17:26:00 | Pass | eplaced fualty cistern. Moved pipes in the duct to suit new(bigger cistern). Water had been turned off to the wing.
MSA-DCS | WA3751988 | Control room - camera 85 has a grey screen and not responding | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 12:25:18 | 2020-11-12 12:30:00 | Fail | Job complete
MSA-DCS | WA3751991 | Structural Assessment on water tower | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-12-01 11:25:00 | Fail | COMPLETED
MSA-DCS | WA3751996 | Jasper B wing - Broken glass panel in laundry door | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-26 13:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3752001 | main kitchen 2x brat pans and 1x bell faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 12:36:15 | 2021-02-09 16:30:00 | Fail | 12/11/2020Found kettle not heating but indicator is on Found gas is being supplied to unit but not igniting Parts required:1x glow plug / ignitor09/2/2021Isolate unit Remove and replace ignition assembly Reassemble and heat to test, ok.
MSA-DCS | WA3752040 | Unit 1, D14 - Toilet leaking Sewage water from base into the shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 09:05:06 | 2020-11-12 17:30:00 | Pass | Inspect cause of water Basin tap left on causing water to run along basin onto shower floor turn off tap properly
MSA-DCS | WA3752041 | Unit 10, C15 - Toilet leaking badly needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 09:07:59 | 2020-11-12 14:30:00 | Pass | Renew inlet valve and outlet washer
MSA-DCS | WA3752081 | master control room outer defence G01 did not activate upon security test | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 13:44:12 | 2020-11-12 14:00:00 | Fail | Suspect as result of power failure this Zone restarted in “Access” Reprogrammed zone to change state via a schedule where the schedule checks status multiple times per day.
MSA-DCS | WA3752083 | Unit 1 near office area gutters are damaged and full - please contact Kevin for exact location | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-17 13:00:00 | Pass | 17/11/20Rectify leaks to box gutter Unit 1
MSA-DCS | WA3752150 | Outpatients Area air con to hot | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-12 11:30:00 | Pass | Checked over aircond found, adjusted setpoint and tested all running ok at present.
MSA-DCS | WA3752154 | Fire System has mulitple faults which will not clear | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 10:35:56 | 2021-04-13 08:45:00 | Fail | 12/11/20 JNAttended site for the following faults:Urqhart (node 20) - card faultMurchison (node 10) - battery low/disconnectedKitchen (node 4) - card faultLenard A wing - zone in alarm and open circuit.Harding A wing ceiling space - zone in alarmGym Zone 79 - open circuitCould not get access as no escort booked in. Will need to organise to return to site. Maintenance advised Thursday 19/11 they can provideaccess.19/11/20 EIAttended site to follow up on the reported multiple faults.Urqhart (node 20) - card faultCard 2 IDNET Class A fault present. Re-commenced fault finding.Further fault finding required.Recommend starting at M1-89 A Wing water closet plant room.Murchison (node 10) - battery low/disconnectedIs currently being resolved under task # 570301Kitchen (node 4) - card faultCard 4 PSU 24V side B output is in fault.Further fault finding required.Lenard A wing - zone 69 in alarm and open circuit.Resolved replacing faulty thermal detector & base in
MSA-DCS | WA3752173 | Unit 4 - A & C More broken skylights have been broken | Casuarina Prison | GMP-GR | Roofing | Rooflights and Skylights (RF) | Midolo Building Services | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-12-17 14:00:00 | Fail | 4X SKYLIGHTS REPLACED
MSA-DCS | WA3752181 | WWTP spirac mesh grill worn out requires replacement | Karnet Prison Farm | SPA-BR | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2021-07-19 14:19:00 | Fail | Arrived on site and signed inWent to inlet screen and inspected area.Isolated plant and equipment and removed existing screw screen also cleaned and hosed down container / screw.Inserted new screw screen and bolted into place.Deisolated plant and restarted the system in auto and check all functions working.Cleaned up and packed up and signed out.
MSA-DCS | WA3752198 | Unit 3, Cell B4- leaking tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-13 12:30:00 | Pass | Nill
MSA-DCS | WA3752215 | Kaartdijin Mia- Air conditioners in the classrooms at the back are not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-12 12:30:00 | Pass | Checked over aircond found both isolators turned off, no tags on them,turned on and tested all running ok at present.
MSA-DCS | WA3752243 | Master Control Room- Lost signal with PTZ camera 5 | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 15:21:08 | 2020-11-13 09:30:00 | Fail | Suspect that following power outage the fibre Modems did not restart correctly. Attended PTZ Camera Equip Cabinet, confirmed operation of camera (video and PTZ function) and reset modem. Still showing level loss. Returned to Gatehouse Equip Room reset fibre modem. Confirmed camera fully operational from Gate Control.
MSA-DCS | WA3752268 | Laundry - Toilet Blocked urinal | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-13 12:06:00 | Pass | Nill
MSA-DCS | WA3752321 | Unit 6, Cell A14- Toilet cistern is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 12:11:55 | 2020-11-13 09:21:00 | Pass | Job delayed due to no escort. Replaced leaking inlet valve
MSA-DCS | WA3752326 | Unit 10, Cell C16- Water leaking badly from drain thread under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 12:13:55 | 2020-11-13 11:10:00 | Pass | Job delayed due to no escort. Reppaced leaking spout and breech
MSA-DCS | WA3752370 | Gymnasium - Plant-Room disconnect and reconnect power to hot water unit so the plumbers can replace | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-13 09:00:00 | Pass | Disconnected and reconnected hws in gym plant room
MSA-DCS | WA3752380 | Control Room- PTZ 2 Camera is poor vision and focus and picture drops out | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2021-04-15 14:30:00 | Fail | Due to the proximity of the prison to the sea cameras at this site are regularly coated in salt. Camera housing window was cleaned, and bug spray applied to housing.
MSA-DCS | WA3752383 | Control Room- PTZ 8 has poor vision and blurred line | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-20 10:00:00 | Fail | Returned to site. Vacuumed dead ants from the base of the cabinet and around the Equipment on shelves in the cabinet. Spread ant bait around the base of the cabinet inside and outside. Spread bait around corner of shelves as ants still seen active in cabinet.
MSA-DCS | WA3752400 | Unit 6, B Wing laundry- Door lock does not operate correctly | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-16 11:45:00 | Pass | Service lock and replace bolt throw
MSA-DCS | WA3752426 | Old Front Gate House Staff external Gym Male toilet door hinges & door damaged | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Midolo Building Services | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2021-03-19 09:05:00 | Fail | NEW DOOR INSTALLED & PAINTED
MSA-DCS | WA3752451 | Abattoir hot water system in dayroom leaking and not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-18 13:30:00 | Fail | COMPLETED
MSA-DCS | WA3752539 | Main kitchen- handle/latch to main oven is catching | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-13 14:50:00 | Pass | Replaced door catch, align & test ok.
MSA-DCS | WA3752546 | Expansion Project Unit 15 - A & C - 9 alarm faults on fire panel which will not clear. - see notes | Casuarina Prison | WSM-MW-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 18:26:42 | 2020-11-12 17:11:00 | Pass | Attended site for no hot water in unit 15, found unit 15 FIP in normal condition. Checked history logs last alarm was sprinkler DBA on 4/11/20.No plant trip active on FIP. 9 missing faults on FIP all related to smoke detectors no modules missing. Advised maintenance that FIP side okwill need to get a plumber to check system.
MSA-DCS | WA3752559 | unit 2 whole unit no hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 14:38:27 | 2020-11-13 12:04:00 | Pass | Nill
MSA-DCS | WA3752568 | Perimeter Controller has failed possibly due to power outage. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-13 12:00:00 | Pass | Energised Fence Controller experiencing problems which first started following mains power restoration on Monday (09/11/2020). Controller would not reset or return on-line. Contacted tech support for advanced assistance, unable to resolve. Replaced failed controller and requested updated licence file. 13/11/2020. Loaded replacement licence file, confirmed alarms cleared.
MSA-DCS | WA3752596 | Medical Centre, Nurse Managers office- Safe wont open | Melaleuca Prison | GMP-BR- HO | Security | Safes (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 15:08:56 | 2020-11-13 10:00:00 | Pass | Attend site. Opened safe and replaced batteries. Reset combination to correct code. Normal Function restored.
MSA-DCS | WA3752606 | Unit 4, L Block- External garden tap leaking, see notes below | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-23 15:11:00 | Fail | Replaced bib tap, also had to replace copper feed to bub tap due to it being corroded. Had to leave prison for 1 hour whilst guards had lunch
MSA-DCS | WA3752638 | Cell window end piece coming away R/H Side of window, the window has been temporary screwed closed, | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 15:52:19 | 2020-11-13 11:00:00 | Pass | REAPAIRS MADE TO CELL WINDOW
MSA-DCS | WA3752666 | DVD recorder is not recording - used for CCTV cameras. | Banksia Hill Detention Centre-Special Purpose Unit Pod B | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 21:56:53 | 2020-11-26 18:29:00 | Fail | Investigated DVR recording issues, checked data communications and servers, confirmed cameras are recording in gatehouse server room. Confirmed cameras are being displayed and recording correctly.Job Complete
MSA-DCS | WA3752676 | PTZ 23 is not responding to zone 12 or 13 alarm activations. | Roebourne Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-13 23:59:00 | Pass | Job complete
MSA-DCS | WA3752677 | Gatehouse - Sally port door in reception is opening by itself, wont close at all | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 12 Nov 2020 | 2020-11-13 00:52:45 | 2020-11-13 00:00:00 | Pass | Broken sally port
MSA-DCS | WA3752679 | MIDAS Alarm Screen - Unable to reset alarms. | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 21:52:03 | 2020-11-13 11:00:00 | Pass | Attended site checked and found wireless keyboard and mouse of MDAS computer in control not responding correctly. Replaced batteries for keyboard and mouse. Also move the blue tooth transmitter of wireless keyboard and mouse as close as possible to keyboard and mouse. Tested it ok after. If problem still happens then hard wired keyboard and mouse need to be replaced.
MSA-DCS | WA3826217 | *Retrospective order* Gatehouse- Sallyport door in reception is opening by itself, wont close at all | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 3 | CLOSE | 12 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-14 13:00:00 | Pass | 13/11/20Issue discovered with PE beams, will need replacement14/11/20Collect PE beams from Malaga. Install new PE beams. Re-Configure controller. Test
MSA-DFES | WA3751986 | bathroom between dorm 4 and 5 cistern is running cannot be turned off | CFRS Hope Valley | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 13:15:00 | Pass | Servicing toilet cistern
MSA-DFES | WA3752032 | ground main front auto door mechanical issues not opening and closing correctly | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 11:10:00 | Pass | Work Completed: inspected all wiring and inputs- all okTidied up sensor wiring that was rubbing on belt, hard reset of unit, new learn cycle-tested all okProblem occurs early morning whilst door is locked by access control.
MSA-DFES | WA3752057 | Lift 1 not working | DFES Cockburn Emergency Services Complex | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-12 11:03:00 | Pass | Job completed - Lift stuck level bottom floor with brake errors, KB error, did harsh braking on lift for 30 minutes, no errors recorded , put lift back into service
MSA-DFES | WA3752609 | Pump 1 & 2, in bottom dam - has lost Prime and pump 2 is very hot | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-17 10:23:00 | Fail | SERVICE AND REPAIR PUMP 1 AND 2 IN BOTTOM DAM.
MSA-DTAG | WA3752362 | Ground, custody area - dust has triggered the fire alarm | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 12 Nov 2020 | 2020-11-12 16:27:14 | 2020-11-13 15:30:00 | Fail | Investigated alarm to find detectors in custody area had gone into alarm due to excess dust in area. Will leave isolated until Monday and replace when work is complete to prevent further false alarms
MSA-DTAG | WA3752565 | Lvl 1- Speaker fault shown on EWIS panel – level 3 Hay Street | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-24 07:30:00 | Fail | ...
MSA-DTWD | WA3752019 | alarm system in irrigation panel requires checking, the high & low pressure alarms. | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-12 12:30:00 | Pass | Reset modem and tested alarm system, now operating correctly.
MSA-DTWD | WA3752031 | Block 8, 1st Floor, Ladies toilet- Taps leaking in hand basin | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-13 15:01:00 | Pass | Issues with the water and isolation for the area
MSA-DTWD | WA3752036 | Block 8, 1st Floor, East end plant room- Light switch jammed & faulty lights, see notes below | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-13 15:00:00 | Pass | Attended site and signed in. Got keys from facilities. Checked out light switch and found to be jammed in off position. Disconnect and removed faulty switch. Supply and replace with new switch. Checked out lights in plant room and found only 1 fluro working out of 10. Using sites materials, replaced all tubes and starters to dead light fittings. All lights working. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3752055 | Paddock 1 - Trough reduction valves faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 15:30:00 | Pass | Replaced faulty reduction valve to stock trough
MSA-DTWD | WA3752073 | K Block, Power disconnected to bricksaw & pugmill | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-13 12:00:00 | Pass | Attended site and signed in. Spoke with staff regarding power works. Located K block. Found pugmill machine. Requires isolation. Someone has bricked up over the isolator to the unit. Unit also weighs way too much to manually move. Removed brick work to get access to isolator. Disconnect and made safe feed to pugmill. Located brick cutting area. Cutters have been removed. Was told by site to isolate the outlets in that area. Hung up 2 x pendants to roof. Isolated double gpo on wall. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3752120 | E Block, E26 Corridor - Roof leak | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-12 13:00:00 | Pass | Re-fixed several loose screws and sealed with roof and gutter silicone
MSA-DTWD | WA3752128 | Lvl 2, B Block, Room 209- Door closer not working | Leederville Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-17 15:30:00 | Pass | Found that door closer has been installed wrong, it has been adjusted so much.Refitted closer, adjusted closer as much as possible. Also the other doors are bent & twisted The door needs speed to latch to get over the bent & twisted doors.
MSA-DTWD | WA3752216 | Science- air gas bottle in the gas gage area is leaking badly - Please see notes | Murdoch Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-20 14:26:00 | Fail | aaa
MSA-DTWD | WA3752235 | E block LSK bistro extraction unit not working - F004 fault | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 09:30:00 | Pass | Travelled to site and signed in. Located LSK Room 58 found all extraction systems running with no faults. Client advises that filter cleaning contractors were carrying out works on the Extraction systems. Possible cause of the F004 power loss fault was due to the isolation of the Systems.
MSA-DTWD | WA3752314 | Under pathway next BBQ area - grout has come out from paving - re-grout | West One Services | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-20 14:30:00 | Fail | Attend site and investigate works, re attend with gear and re grout pavers
MSA-DTWD | WA3752316 | Tower block, level 3, male urinal not flushing | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 09:15:00 | Pass | reassembled urinal cistern to working order
MSA-DTWD | WA3752439 | BLD 875 - Faulty Fan | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-24 10:50:00 | Fail | Job completed - loose Capacitor in control box
MSA-DTWD | WA3752549 | Tower Block - re apply existing Picture frames and white boards to walls | West One Services | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 16:00:00 | Pass | Move TV and hang pictures
MSA-DTWD | WA3752649 | E Block, E58 LSK-Leaking Faucet & Loose Tap Set in south west corner kitchen, see notes below | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 12 Nov 2020 | 2020-11-13 17:00:00 | 2020-11-13 15:43:00 | Pass | Outlet spout was leaking, replaced o-rings and now sealing properly. Reinstalled coverokates as they had come loose.
MSA-MRWA | WA3752346 | Replace / Repair 2x shower heads in the bank of 3 showers, cubicle 1 and 3 | Don Aitken Centre MRWA Head Office-Main Building-Basement-AB.06.01-Toilet and Shower-Male | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 08:30:00 | Pass | Replaved lhs shower head and removed the flow restrictor from the rhs
MSA-MRWA | WA3752405 | Ice machine container area has potentially been contaminated - see notes below | Jandakot Depot-Main Building-Ground Floor-Entry Foyer | GMP-BR | Refrigeration | Ice machine (RE) | Water2water Pty Ltd | 2 | CLOSE | 12 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-13 16:17:00 | Pass | FULLY SANITISED ICE MACHINE + PROVIDED NEW ICE SCOOP
MSA-MRWA | WA3752411 | Lock to the roller Door has become disconnected, see notes below | Materials Engineering Branch-FWD Shed-Ground Floor | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 12 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-16 10:40:00 | Pass | repair to auto door lock to falling weight shed
MSA-DCA | WA3756856 | Boiler plant room, pressure tank valve is leaking | Collection and Research Centre Welshpool-External Area-Ground Floor-Boiler Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-17 16:30:00 | Pass | Completed repair works to leaking HW expansion/make-up tank. Please refer to works logs for in depth description of works carried out.
MSA-DCS | WA3755481 | Control room -PDA system alarm transponter is faulty and its like tampered alarm . | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Nov 2020 | 2020-11-13 09:52:51 | 2020-11-13 09:30:00 | Pass | Rectified and fixed tamper fault, job completed.
MSA-DCS | WA3755704 | metal shop 3 phase plugs are faulty and need checking | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-24 14:00:00 | Fail | Rewired socket outlets and plug tops on machinery
MSA-DCS | WA3755708 | admin area verandah pole split timber pole | Wooroloo Prison Farm | GMP-BR- HO | Carpentry | Timber (all types) (CA) | Midolo Building Services | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-12-07 12:30:00 | Fail | NEW VERADAH POLE AND STRUCTURE INSTALLED
MSA-DCS | WA3755716 | Unit 13 - B12 Shower screen leaking through to the bottom bed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Midolo Building Services | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-17 10:30:00 | Fail | SHOWER SCREEN RESEALED
MSA-DCS | WA3755876 | Kitchen - bain marie is tripping intermittent | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Nov 2020 | 2020-11-14 10:12:09 | 2020-11-16 11:30:00 | Fail | Investigate tripping kitchen Bain Marie. Found faulty element. Sourced replacement. Install new element.
MSA-DCS | WA3755889 | Unit 17, A15 - Prisoner lock has a broken key stuck in side as its not accessible from outside | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 13 Nov 2020 | 2020-11-13 14:17:03 | 2020-11-13 12:30:00 | Pass | Remove broken key stuck in lock.
MSA-DCS | WA3755904 | Unit 2, D7 - Sink blocked and there is no basin grate | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 09:30:00 | Pass | Nill
MSA-DCS | WA3756036 | front gate, gate- Blue light cannot be turned off | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Nov 2020 | 2020-11-14 11:16:39 | 2020-12-17 11:21:00 | Fail | Investigated fault and repaired blue light.Job Complete
MSA-DCS | WA3756053 | Bakery - Pinch Point Guards to be replaced to moulder, these were damaged due to the belt shredding | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2021-01-22 15:45:00 | Fail | finsihed 22/1/21
MSA-DCS | WA3756058 | Kaartdijin Mia - Smoke detectors are broken throughout the demountables | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-12-03 13:00:00 | Fail | Replaced failed smoke detectors in kaartdjin Mia transportable buildings.
MSA-DCS | WA3756435 | Unit 5 B2 Ceiling leak on ground floor cell | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 11:00:00 | Pass | Inspect tiles and grout require tiler
MSA-DCS | WA3756441 | boiler house boiler No3 Boiler goes out on fault on high fire | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-25 08:30:00 | Fail | Investigated the fault on Boiler #3 for failure to run on high fire.On investigation I found the lack of gas from the supply to be causing the problem.This was a valve outside the boiler room had been mostly closed
MSA-DCS | WA3756445 | SB1 (Between U15-U16) - Lunch Room - Tap in SB1 kitchen missing aerator. | Casuarina Prison | WSM-MW-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 11:30:00 | Pass | Nill
MSA-DCS | WA3756804 | Unit 7, C Wing - Bug Zapper in C Wing not working. Possible globe replacement. Please assess. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-16 12:30:00 | Pass | Replaced damaged gpo in scu c wing
MSA-DCS | WA3756812 | Unit 13, A13 - shower has minimal pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-16 15:00:00 | Pass | Nill
MSA-DCS | WA3756845 | kitchen floor work area slicing machine belt drive faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2021-01-25 12:00:00 | Fail | 24/11/20Sign in Escorted to kitchen Slicer has been removed to stores Escorted to storesFound slicer in storage and has been taken apartRemove from site for repairs at workshop as requested.27/11/20 - DONE IN WORKSHOP, NO SIGNED SLIPOpen unit in workshop Found drive belt snapped Unit requires cleaning and service Order parts Parts required: 2 x belts4/01/2021 - DONE IN WORKSHOP, NO SIGNED SLIPRemove slide assembly and install new belts Clean base of unit and lubricate morning partsReassemble unit Test and knife blade ok Unable to get carrier in correct position to automatic feed. More investigation required.25/1/2021Remove keypad and check conditionFound oxidising on board Clean board Install board and test unit heavily All ok Deliver to site
MSA-DCS | WA3756852 | SITE COST Main Kitchen- Brat pan keeps switching off and wont keep temperature | Wooroloo Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 0 | CLOSE | 13 Nov 2020 | 2020-11-13 18:38:56 | 2020-11-24 23:00:00 | Fail | Main kitchen Brat pan keeps switching off, won't keep temperature. Check pan & controls. Thermostat faulty beyond repair. Order new part ex east. Return & install, reset controls. Assemble & test. Report to staff.
MSA-DCS | WA3756877 | ISU Cell #C06 - shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-18 11:20:00 | Pass | Replaced faulty shower button
MSA-DCS | WA3756881 | ISU Cell # A02 - Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-16 12:30:00 | Pass | Replaced faulty broken light switch in ISU
MSA-DCS | WA3756887 | Zone 10 mircowave, receiver number 19 constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Nov 2020 | 2020-11-14 15:15:27 | 2020-11-17 14:00:00 | Fail | Traced fault to the fuse intermittently losing contact in the fuse holder. Repaired and checked input power and alignment. Removed tall weeds from the path between the RX and TX. Tested ok locally and back to control.
MSA-DCS | WA3756891 | Zone 7 omnitrax constant alarm | Greenough Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Nov 2020 | 2020-11-14 15:18:36 | 2021-02-18 07:15:00 | Fail | work order to be invoiced at cost to date.
MSA-DCS | WA3756892 | Omnitrax system, zone 2 to 14 is not operating correctly | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Nov 2020 | 2020-11-14 15:19:23 | 2020-11-19 16:45:00 | Fail | Zone alarms not caused by sensitivity issues but by Comms issues dropping off the EC NODES. Unable to log onto NODES 4-7 via Senstar UCM program. Found a fault with the cabling between EC3 and EC4. Downloaded a copy of UCM so I could log onto the modules out in the field. Restored Comms to NODES 4 - 7. Checked Omnitrax zone tuning. Zones ok except for zone 7. Zone 7 to be repaired under work order WA3756891.
MSA-DCS | WA3756942 | karakin, TV aerial on roof is damaged | Banksia Hill Detention Centre | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 0 | CLOSE | 13 Nov 2020 | 2020-11-13 20:47:07 | 2020-11-16 12:00:00 | Fail | job completed - Found antenna broken off bracket, temporarily re-attached antenna. All channels restored. To return and replace antenna
MSA-DCS | WA3756951 | Gatehouse - ELEC door lock unlocking and locking randomly. Pls inspect and repair | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Nov 2020 | 2020-11-14 03:47:59 | 2020-11-14 01:30:00 | Pass | Attended site checked and found Key Issue EBI workstation is not working correctly and keep unlocking the door from Key Issue into prison. Reboot the workstation and tested all functions back to normal.
MSA-DCS | WA3791311 | Attend with AFD and investigate multiple issues with sallyport doors | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-13 13:00:00 | Pass | Investigate and assess the fault on detainee reception motorised sliding gate. Fault combg from motor and safety IR beam. Job completed
MSA-DFES | WA3755803 | rear of the building externa wall nth/west leaking tap | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 09:49:00 | Pass | Serviced Leaking TAP.
MSA-DFES | WA3755829 | Retic will not turn off and there seems to be a fault with the system | DFES Baldivis | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 18:20:00 | Fail | Call out & LabourParts $47
MSA-DFES | WA3755845 | dorm 4 pest control check to see if there are bed bugs | CFRS Vincent | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-13 16:00:00 | Pass | Inspected dorm 4 for suspected bed bug activity. Searched amongst all linen, bed linings, seams of mattresses, chairsand other accessible harbourage areas. There were no signs of any blood spotting or bed bug eggs or adults at thetime of inspection. Only areas that couldn't be inspected were underneath the bed and around the caster wheels as itwas too heavy to lift. Have advised staff to hot wash all bed linen at above 60 degrees Celsius.
MSA-DFES | WA3755897 | room 34 - Rising damp is appearing in Dormitory 5. (see notes) | CFRS Perth | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-24 11:00:00 | Fail | Repair skirting boards
MSA-DFES | WA3755931 | Ground level - Painting and repairs please see notes for fault and description | Butler Career Fire Station | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-28 11:30:00 | Fail | 1. Dorm 4 kick board needs re attaching2. Dorm 5 Door frame has detached from the wall3. Entry door from hallway to rear hall needs painting4. Door to BA room needs painting
MSA-DFES | WA3755941 | First floor, Staff Area, Stairwell , Fire light torch - Small globe faulty/out | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 09:30:00 | Pass | CompleteReplaced faulty light
MSA-DFES | WA3755964 | Training yard fence along rail line - Colourbond fence posts are loose and move up to 40mm | CFRS Fremantle | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 3 | COMPFIN | 13 Nov 2020 | 2020-11-20 17:00:00 | 2021-11-04 12:15:00 | Fail | Supply and install 3x 100 x 100 hot dip galvanised powdercoated posts, concreted in 1600mm in depth, this requires a 450mm concrete core drill and lined with an aluminium duct. Supply and install new temp fence bays in lieu of damaged rails and sheets. There is no allowance for disposal or handling of PFAS. The preliminaries required for these works include a permit officer & PTA rail approved temp fencing (heavy duty temp fencing). Our recommendation would be to assess this whole fence line to be installed to the new engineered spec as we believe it is not currently done this way and susceptible to future issues as per the current works.
MSA-DFES | WA3755985 | Level 1, Kitchen - Hot water tap broken off, | DFES Rescue Helicopter Base | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-13 13:30:00 | Pass | Replaced tap
MSA-DFES | WA3756417 | ground engine bay external wall keypad not working - see notes | CFRS Maddington | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 13:25:00 | Pass | Work completed: Found no power on external keypad, opened keypad up and tested power to find 0v on white andyellow cable.Found power source and switched to red and black cable as cables tested to be working and power source had poweron it, keypad now all working.Source of problem was faulty cores on 6 core cable.
MSA-DFES | WA3756487 | ground Engine Room Change Rooms Urinal in Change Room 4 not flushing properly. | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-22 14:00:00 | Fail | Install new flush button
MSA-DFES | WA3756763 | Engine Room Change Rooms - Hand Dryers in Change rooms 3 & 4 not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-10 14:00:00 | Fail | Replaced lights and repaired as per quote.
MSA-DFES | WA3756777 | First Floor, Balcony - Two of the hand rail anchors have become loose from the limestone wall. | DFES Education and Heritage Centre | GMP-BR | Building | General Building (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-12-16 14:16:00 | Fail | Removed esisting bolts and installed new threaded rod and fixings to handrails
MSA-DFES | WA3756834 | 1st floor, programmed - Two lights require replacement faulty | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 10:45:00 | Pass | CompleteReplaced faulty fluro
MSA-DFES | WA3756848 | Reception toilets - exhaust fans in the toilets are on constantly, they don’t turn off with lights | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 11:45:00 | Pass | Investigated exhaust fans that weren’t turning off with lights and found that they were separately fed from the plant room on a timer clock so they run all the time during the day. There is no fault with the fans. Informed staff of findings.
MSA-DFES | WA3756857 | Main Entry Auto door not opening on occasion with swipe card, sensor & egress button. | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-16 13:20:00 | Pass | Checked the door and found a damaged cable from security to the relay.Cut the wire and re wired. Tested ok
MSA-DFES | WA3756869 | Soak wellfull of dirt & requires emptying of dirt to allow drainage system to work. | CFRS Fremantle | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-22 10:08:00 | Fail | Blockage caused by hazardous substance different contractor to be engaged.
MSA-DFES | WA3756899 | The seal around the overflow grate/drain under the urn in the main dining room is gone and | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-24 13:09:00 | Fail | Repairing the seal on the drain
MSA-DFES | WA3756915 | Administration, Main Dining Room - kitchen bench in the main dining room is loose, can be lifted up | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-16 12:45:00 | Pass | Resecured desktop as requested by site
MSA-DFES | WA3756945 | Bathroom tap zapped while firefighter was showering and resulted in no power. | CFRS Welshpool-Main Building | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 13 Nov 2020 | 2020-11-13 21:26:49 | 2020-11-13 21:30:00 | Fail | Western power fault, western power tested before reenergising. Tested earthing system, system tested fine, suggest replacing earth stake and power pole
MSA-DTAG | WA3756937 | Lvl 31, Security workstation unable to view CCTV, user Corbin Houzer | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 17:00:00 | Pass | Checked and adjusted user privileges and reset windows login for client.Provided client with training for system. The windows User Login now authenticates access to the Milestone Client and grants access for the DotAG Corporate CCTV Role. This Windows User Login does not authenticate access to Pacom Unison and will need to be manually logged in with the retrospective operator(s) carrying out changes on the system. Job completed.
MSA-DTWD | WA3755772 | AT251 - Water leak in main Automotive workshop from roof | Kwinana Automotive Centre | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2021-03-26 10:10:00 | Fail | Roofing has been pressure cleaned down and all joints have been sealed with new silicone. Flashing has been installed over edge of roofing edging to stop water leaking in to cavtity areas
MSA-DTWD | WA3755825 | E-Block stores coolroom No E60 has stopped working | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Coolroom (RE) | Precise Air Group | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2020-12-01 16:00:00 | Fail | Attended site signed in and investigated system,found condesor motor to be faulty and txv faulty,picked up new parts from supplier,re-attended site fitted new motor and installed new txv, tested, monitored and set superheat, left system all operational and meeting set point
MSA-DTWD | WA3755916 | Building 7, Cafeteria - Water leak next to north east evaporative A/C in student dining area | Thornlie Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-17 11:00:00 | Pass | Sealed around base of air conditioning unit
MSA-DTWD | WA3756103 | Building 3 - Water leak in passageway outside Heavy Plant under above display cabinet | Thornlie Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-17 09:30:00 | Pass | Sealed gaps in flashings and ducting associated with the Air Conditioning unit
MSA-DTWD | WA3756203 | D-Block 2nd Floor staff Kitchen, the Zip urn is leaking water from tap | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 10:50:00 | Pass | Replaced faulty tap.
MSA-DTWD | WA3756793 | B Block, BG25 Panel Workshop - Cable/Conduit Damage to foot pedal control | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 14:47:00 | Pass | Removed broken conduit and refitted. All safe now job complete
MSA-DTWD | WA3756886 | J Block - J004 roof is leaking | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-12-18 12:45:00 | Fail | Removed rusted outridge capping and fitted new cappings
MSA-DTWD | WA3756889 | P Block - The water cooler outside P block (west side) is continually tripping the RCD | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2021-02-19 13:00:00 | Fail | New water cooler installed outside of P block
MSA-DTWD | WA3756893 | U Block, Loss of power to AC9 in U022.6. Blue 4 circuit breaker requires checking | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2021-01-18 16:19:00 | Fail | Repalced faulty isolater and ran new cabling to evap unit U block. Job completed
MSA-DTWD | WA3756909 | E Block, E58 LSK – Food Trap is blocked | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 09:00:00 | Pass | Unblocked drains
MSA-DTWD | WA3756911 | D Block, D3 Pastry Lab – Handwash basin faucet is very loose | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-16 13:50:00 | Fail | Replaced spout
MSA-MRWA | WA3756884 | Failed light in female toilets possible damaged starter retainer. | Heavy Vehicle Services-Main Building-Ground Floor-Toilet-Female | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 13 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 10:00:00 | Pass | Attended site and signed in. Completed jsa. Found and investigated faulty light in ground floor woman’s bathroom. Found blown ballasts and wrong starters. Replaced whole fitting with new led batten. Tested all okay. Clean and tidy site. Looked for barcode assets and none on site to scan and enter. Job complete
MSA-MRWA | WA3756931 | Level 2, 232 - LED light failed please refurbish | Don Aitken Centre MRWA Head Office-Main Building-Second Floor-232-Meeting Room | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 13 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 09:41:00 | Pass | Good afternoon AJ,Please close this down now.Brendan Mitchell Facility Manager M 0438 149 652brendan.mitchell@programmed.com.au programmed.com.au 43-47 Burswood Road, Burswood, Western Australia 6100 By receiving this email, we require you to comply with our Code of Conduct and our Privacy Policy and accept our Email Usage Policy. From: AJ Abbasi <aj@awbco.com.au> Sent: Friday, 4 December 2020 8:12 AMTo: Brendan Mitchell <Brendan.Mitchell@programmed.com.au>Cc: Susan Bokas <susan@awbco.com.au>Subject: Don Aitken level 2 meeting room 242 Lts WA3756931EXTERNAL EMAIL: Please use caution when clicking links or opening attachments.Hi Brendan,We have this outstanding job at Don Aitken level 2Description of Workorder: Level 2, 232 - LED light failed please refurbishTech works note: Attended site and signed in. Located level 2 room 232. Checked lights and all are working. Read notes for job and states meeting room 232 which is
MSA-MRWA | WA3756933 | Replace mini light switch mounted on aluminium door frame | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor-E7.01-Electrical Equipment Riser | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 13 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 11:00:00 | Pass | Attended site and signed in. Went downstairs and met with facilities. Signed out keys. Went to level 7 and found room 7.02 faulty light switch. Disconnect and removed faulty switch. Supply and replace with new double architrave switch. Tested all okay. Signed out and returned keys. Job complete
MSA-DCA | WA3756952 | HVAC Fault - Alarm AC1 & 2 - High Humidity Alarm | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 14 Nov 2020 | 2020-11-14 04:19:13 | 2020-11-16 08:00:00 | Fail | Humidity levels dropping and system running as required.
MSA-DCA | WA3758870 | Faulty fire alarm activate in Plant room ,isolated by DSES at 1 am .Please investigate and repair | State Library of WA-Main Building-Ground Floor-Security Foyer | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 14 Nov 2020 | 2020-11-14 10:32:38 | 2020-11-14 10:30:00 | Pass | Attended site Saturday 14th November due to A/C RM1 duct probe in alarmorbis duct probe was found to be dirty and the detector needed to be replacedDue to being a Saturday no stock was availableTech clean on site to ensure the detector did not go into false alarm until we could return to replace on MondayTech return on Monday morning to replace the dirty damaged detector
MSA-DCS | WA3758881 | Main Kitchen- The exhaust fan in the kitchen canopy is not working. | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Nov 2020 | 2020-11-15 08:25:17 | 2020-11-16 14:00:00 | Fail | Investigate range hood fan not working. Found broken belts. Sourced replacements. Installed replacement belts.
MSA-DCS | WA3758928 | unit 2 - turnstile jammed | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 14 Nov 2020 | 2020-11-15 15:36:36 | 2020-11-15 09:15:00 | Pass | Ryan Nicholson (15/11/2020) - Work NoteTravel to site. Inspect Unit 2 turnstile and found not operational so investigated. Found error on controller.Could not find a problem with turnstile so reset controller and now turnstile works. Tested several times in all modes, all fine.
MSA-DCS | WA3758933 | Reset the fire pumps in front of the prison | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 14 Nov 2020 | 2020-11-14 20:35:15 | 2020-11-14 18:11:00 | Pass | Pump had been running, checked pumps, refuelled and reset - all ok
MSA-DFES | WA3765604 | ceiling panel has come loose in engine room | CFRS Daglish | GMP-BR | Building | Materials (BU) | AWB Co. | 1 | CLOSE | 14 Nov 2020 | 2020-11-15 14:51:00 | 2020-11-23 13:00:00 | Fail | Repair gutter and replace ceiling tiles
MSA-DTWD | WA3758950 | E Block - Unblock the kitchen sinks in the restaurant | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-16 11:30:00 | Pass | Jet washed all branch and main runs from the kitchen to grease trap.
MSA-DCS | WA3763086 | Unit 10 -Major leak in the Boiler room | Hakea Prison-Unit 9 64 Cell Prison Living | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 15 Nov 2020 | 2020-11-15 11:03:35 | 2020-11-15 11:00:00 | Pass | Replaced burst section off 50mm pipe
MSA-DCS | WA3763087 | PTZ CAMERA 2,5 AND 7 IS NOT WORKING | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Nov 2020 | 2020-11-15 11:25:27 | 2020-11-17 16:00:00 | Fail | PTZ camera 2 operational, picture is now visable, modem is temperamental but operational. Maxpro display restored however required temporary offline. All ok
MSA-DCS | WA3763111 | CONTROL ROOM- No footage coming onto screens. loss of cameras. | Boronia Pre-release | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Nov 2020 | 2020-11-15 16:49:51 | 2020-11-15 14:45:00 | Pass | Attended site checked and found two monitors of the monitor wall in controlnot showing any cameras. Located problem to be Indigovision workstation itself. Reboot Indigovision workstation and tested all ok.
MSA-DCS | WA3763115 | Fire alarm panel - vesda alarm fault - D wing - cell 2 | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Nov 2020 | 2020-11-16 14:13:27 | 2020-11-15 16:13:00 | Pass | Reset vesda - inspected for blockages all ok
MSA-DCA | WA3765210 | Lift 1 is making a clunking & screeching sound, but operational | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-AG.26 - Foyer | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 09:00:00 | Pass | Found guide rails dry, re-lubricated rail and tested all OK left in. Lift has excessive movement, further investigation needed into under car guide shoe's. Non Chargeable
MSA-DCA | WA3765523 | Chiller 2 in fault | Maritime Museum Victoria Quay-Robert Steele Marine Engineers Display-Ground Floor-Chiller Room | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-26 16:30:00 | Fail | Attended site. Wet store laboratory fume hood in fault. Applied tests and checks to find fume hood not in fault. Carried out shutdown operation (ok) reinstated fume hood and tested active operation (ok). Checked online extraction fan and vsd (ok). System operating correctly with no faults present.
MSA-DCA | WA3765687 | Broken retic sprinkler is leaking | Perth Cultural Centre Precinct-Urban Orchard-Ground Floor | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-16 12:15:00 | Pass | This was all caused by vandalism and someone kicking and snapping the nozzles.- Ran and flushed all fixed sprinklers before putting new nozzles on.- Added 5 mp rotator nozzles (mp 2000 90-210) and tested all.- Noticed that this zone is taking around 1 minute to turn off. This could cause problems on Hydrawise
MSA-DCA | WA3773916 | Toilet is constantly running | Sunset Hospital Heritage Precinct-Building G-Two Storey Ward Block-Ground Floor-Disabled Toilet - New Toilet Block | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 13:30:00 | Pass | Adjusted water flow in the cistern. Struggled to removed and reinstall wall panel.
MSA-DCS | WA3764314 | Master control room - One of the mains screens displaying no signal. | Casuarina Prison-Gatehouse | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Nov 2020 | 2020-11-16 09:06:30 | 2020-11-16 09:20:00 | Fail | Found workstation 2 access control monitor indicating no signal, restored input signal and tested operational, system fully restored.
MSA-DCS | WA3765110 | Abattair - Fridge number 7 is not working. | Karnet Prison Farm-Abattoir Change Rooms | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 06:15:17 | 2020-11-16 12:26:00 | Pass | check loading dock coolroom 7 , control circuit tripping , found junction box filled with water.clear and dried out box and re-seal . tested and left system operational
MSA-DCS | WA3765215 | Control Room - Microphonics zone 1 not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 08:30:00 | Pass | Rectified and fixed the fault on mx controller, job completed .
MSA-DCS | WA3765226 | Eduucation Room 12 burst water pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 16 Nov 2020 | 2020-11-16 11:36:00 | 2020-11-18 15:00:00 | Fail | nil
MSA-DCS | WA3765233 | Education Room 12 isolate power to make safe for plumber after flooding | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 16 Nov 2020 | 2020-11-16 11:40:18 | 2020-11-18 11:00:00 | Fail | Made circuits safe in education room 12 and adjacent rooms. Returned once water was removed. Restored power to classrooms
MSA-DCS | WA3765272 | Unit 9, Cel A8- Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:01:43 | 2020-11-17 12:30:00 | Fail | Rectified and fixed cell call faul. Test functions ok and back to normal operations.
MSA-DCS | WA3765274 | unit 3 office Unable to here control room from cell call | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:01:48 | 2020-11-16 10:15:00 | Pass | Rafresh unit 3 node due to fault on audio, tested working. Job completed.
MSA-DCS | WA3765281 | Unit 7, H Wing- Water dripping from roof light | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 15:00:00 | Pass | lift roof sheeting and installed new sarking under sheeting, water tested and did additional section due to water travelling
MSA-DCS | WA3765285 | entry pod L14S5.21ST analog faut unt 4 vesda | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Nov 2020 | 2020-11-16 12:04:23 | 2020-11-16 11:15:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3765294 | Unit 8, C/D Regi Oven- Timer not switching off | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 09:30:00 | Pass | repaired oven
MSA-DCS | WA3765295 | Zone Control 2, West side Grille- Lock not opening | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:10:24 | 2020-11-19 12:30:00 | Fail | Replaced defective electronic lock with new, job completed.
MSA-DCS | WA3765306 | Staff Support Room Roof leak near desk carpet wet | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:15:15 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA3765309 | Kitchen, Work Area -Rational oven No 3 Gas alarm | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:17:27 | 2020-11-16 12:45:00 | Pass | Rational oven with "reset gas" alarms. Working ok on arrival. Found top ignition module, flame currents too low. Replaced module & retest, flame currents acceptable now. Left oven operating ok.
MSA-DCS | WA3765314 | Unit 1, Cell D4- Toilet Blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:20:09 | 2020-11-16 13:55:00 | Pass | Clear blockage to pan line
MSA-DCS | WA3765323 | Unit 3, Cell C5- Cell call can’t be heard from control room | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:22:30 | 2020-11-16 10:45:00 | Pass | Clean the cell call face plate and test , ok and back to normal operations. Job completed.
MSA-DCS | WA3765325 | Unit 6 - B8 Toilet leaking onto cell floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 09:30:00 | Pass | Nill
MSA-DCS | WA3765334 | Unit 14 - A1 Faulty shower head clogged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-16 13:00:00 | Pass | Nill
MSA-DCS | WA3765351 | Cell D2 toilet/ water keeps running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 11:30:00 | Pass | Nill
MSA-DCS | WA3765359 | Toilet leaking in the service duct. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 08:30:00 | Pass | Nill
MSA-DCS | WA3765373 | Unit 4 - B13 Toilet water running non stop. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-16 11:30:00 | Pass | Nill
MSA-DCS | WA3765377 | Karakin, Cell B03- Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-16 11:30:00 | Pass | Replaced faulty light switch in karakin
MSA-DCS | WA3765381 | S O P - A13 Tap in basin is dripping. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 08:30:00 | Pass | Nill
MSA-DCS | WA3765382 | Unit 4, D landing - No hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3765387 | Shared Facility - No TV reception | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-17 10:15:00 | Pass | Replaced antenna amplifier, in line power injector and rejoined cable in roof.
MSA-DCS | WA3765391 | Control Room CCTV - Intermittent failures of cameras 26, 31 & 40 | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 08:48:05 | 2020-11-17 16:30:00 | Fail | Saw the cameras fail once while electrical work was being done on site. Shifted the cameras to a different power source. Tested ok. Monitored throughout the day.
MSA-DCS | WA3765430 | Unit 14 - B8 sink is leaking in cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-16 14:00:00 | Pass | Nill
MSA-DCS | WA3765444 | Unit 6 - C3 water running in C wing service duct | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-16 12:30:00 | Pass | Nill
MSA-DCS | WA3765454 | Unit 5 - A2 Toilet leaking and sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-16 13:30:00 | Pass | Nill
MSA-DCS | WA3765465 | Unit 5, B & D Wing- Urn not working, no water coming out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-12-03 11:30:00 | Fail | Replaced inlet solenoid and pcbCalibration hot and test all okay
MSA-DCS | WA3765475 | Unit 13 - B14 has a broken internal light switch. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 09:12:37 | 2020-11-16 14:00:00 | Pass | Replaced damaged switch in unit 13 b14
MSA-DCS | WA3765481 | Unit 6, D wing, cell D2 - door hinges may need to be replaced/door dropping jamming lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 12:15:00 | Pass | Require parts.Replace hinges, door plate, lock and weld on strike plate.
MSA-DCS | WA3765488 | Unit 7, D Wing dayroom- Light is flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-30 13:30:00 | Fail | Repaired multiple faulty lights in unit 7 using 12 foot ladder
MSA-DCS | WA3765497 | MPU (8), Cell M11- GPO has metal plug stuck inside, keeps tripping the power board | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 08:30:00 | Pass | Replaced damaged gpos in mpu m11
MSA-DCS | WA3765512 | Unit 1, A8 - The internal cell door viewing glass panel is smashed and requires replacing | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 09:17:01 | 2020-11-17 16:00:00 | Fail | OBS PANEL REGLAZED & FRAMEWORK REPAIRED
MSA-DCS | WA3765516 | Unit 1, A8 - top bunk side panel has been broken off | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 09:22:59 | 2020-12-22 13:45:00 | Fail | New side panel installed
MSA-DCS | WA3765535 | Karakin A, B & C wings - Gas heater flues ripped off | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-12-10 14:15:00 | Fail | ROOF/FLUE REPAIRS COMPLETE
MSA-DCS | WA3765583 | MPC- Drink Water fountain, water flow is too strong | Wooroloo Prison Farm | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-17 13:46:00 | Pass | Adjusted flow rate to bubblerdiagnosed issue with flow restrictor A40333076F adjusted flow tested ok
MSA-DCS | WA3765588 | Main Kitchen- Can opener is broken | Wooroloo Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 13:15:00 | Pass | Main Kitchen, can opener is broken. Check opener, beyond repair. Order replacement & return to Kitchen.
MSA-DCS | WA3765596 | kitchen sink taps on western side leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 09:00:00 | Pass | COMPLETED
MSA-DCS | WA3765637 | Unit 9, Cell B1- Lock is broken | Hakea Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 10:16:40 | 2020-11-16 16:30:00 | Pass | Attend site. Replaced broken personal lock.
MSA-DCS | WA3765650 | Gatehouse NVR Failure | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 10:21:31 | 2020-11-18 08:50:00 | Fail | NVR has fully restored, camera streams restored and fully operational. No further action is required.
MSA-DCS | WA3765727 | control CCTV need information downloaded | Hakea Prison | WSM-GR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 10:47:52 | 2020-11-16 13:00:00 | Pass | Downloaded footage from zone 6 ,16 and 17 cameras.
MSA-DCS | WA3765759 | Unit 14, Cell D8- Water constantly leaking from behing spout | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 16:00:00 | Pass | Nill
MSA-DCS | WA3765766 | Kitchen, small oven probe broken | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-25 13:00:00 | Fail | 25/11/20Attended kitchen Issues - Oven temperature probe broken ovens.Removed existing probe and installed new probe in oven.
MSA-DCS | WA3765768 | Unit 14 - D6 shower head is leaking constantly. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 13:00:00 | Pass | Nill
MSA-DCS | WA3765791 | Jasper, Cell B05- 2x smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-25 10:00:00 | Fail | RE SEALED TILE SURROUND, WELD GRILLS, RE GLAZED WINOWS
MSA-DCS | WA3765798 | Jasper, B05 - Smashed mirror | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-23 16:15:00 | Fail | NEW MIRROR INSTALLED
MSA-DCS | WA3765811 | kitchen kettle lid damaged | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-27 16:00:00 | Fail | 16/11/20Called as requested to the mixing kettle lid broken. Removed the lid from site for workshop repair. 24/11/20 (WORKSHOP REPAIRS - NO SIGNATURE SLIP)Welded the location pin back in position. 27/11/20Supply and install kettle lid
MSA-DCS | WA3765850 | Unit 14, Cell B6- Tap is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 11:30:00 | Pass | Nill
MSA-DCS | WA3765852 | Textiles- Rheem hot water system red tap handle is broken | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-17 11:46:00 | Pass | Old broken tap replaced with new. All tested
MSA-DCS | WA3765861 | Unit 2 B wind showers wall damaged | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 11:50:19 | 2020-11-17 14:45:00 | Fail | PANEL RE FIXED TO WALL
MSA-DCS | WA3765865 | Unit 14, Cell C6-Shower & basin tap are both leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 10:30:00 | Pass | Nill
MSA-DCS | WA3765895 | Unit 14 - A9 shower head barely any water coming out could be build up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 09:30:00 | Pass | Nill
MSA-DCS | WA3765955 | Industries driveway, outside of gardens - 1m2 sq asphalt that has been ripped up by forchlif tra | Bandyup Prison | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-12-04 09:45:00 | Fail | 04/12/20Repaired pothole on industries drive way
MSA-DCS | WA3766361 | Unit 2, Cell A6- Prisoners lock is Faulty | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-17 12:00:00 | Pass | Attended site. Turned away by front gate staff after SO in Unit 2 advised there is nothing wrong with the Prisoner's Lock in Cell A6.
MSA-DCS | WA3766657 | WWTP - Air conditoner not cooling | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-12-01 12:00:00 | Fail | Completed leak check and repair
MSA-DCS | WA3766847 | Admin staff toilets Toilets and Floor Drains Blocked and Overflowing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 13:33:30 | 2020-11-16 17:02:00 | Pass | Clear blockage to sewer line
MSA-DCS | WA3772185 | Amenities - Male Changeroom shower rose damaged 1st shower on right side | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 09:30:00 | Pass | Nill
MSA-DCS | WA3772454 | Unit 10, Hot water system at back of unit - Leaking, Pipe Ruptured | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 14:32:37 | 2020-11-19 15:10:00 | Fail | Replced section of leaking pipe in the plant room. Job delayed due to no escort available
MSA-DCS | WA3773458 | Urquhart, D wing Day Room- Broken lower window Approx 500mm x 350mm | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-26 16:45:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3773927 | Unit 10, Cell A3 requires a new lock and cylinder | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-16 17:30:00 | Pass | 11/11/2020. Attend site. Prisoner trapped in cell. Opened cell. New lock required.16/11/2020. On site. Supplied and fitted new lock.
MSA-DCS | WA3773942 | Medical Centre, treatment room 3- Air Con is leaking | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-17 09:00:00 | Pass | Arrived to site.Awaited guard.Access medical unit.Shown to leaking A/C.Found unit off.Removed fascia.Found condensate float stuck.Removed and freed up float.Tested.Pump running well.Tested with more water.Drained okay.Unit working okay.Note left on desk saying it has been attended to and okay to use.
MSA-DFES | WA3765346 | Work shop - Lathe has tripped out, have tried to reset but not working | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 14:45:00 | Pass | Investigated issue with Lathe. We identified he issue to be with the machine itself and have proven voltage to the machine. The integrity of the electrical system up until the lathe is good. Have notified staff to get into contact with the manufacturer.
MSA-DFES | WA3765758 | 1st floor, both computer rooms - environmental units (CRAC) have audible alarms | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 12:00:00 | Pass | Access data and comcen server rooms. Found units to be in alarm. This alarm does not effect operation, is just an event warning. There was a condenser water flow loss alarm that occurred over the weekend due to power loss. Clear alarm and test operation. Found crac unit to operate as normal.
MSA-DTAG | WA3765436 | Lvl 11,Coroners Court- Lights are out across the office | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-17 08:00:00 | Pass | Job complete
MSA-DTAG | WA3765730 | External - Remove graffiti from south elevation walls opposite train station (3 locations) | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 08:30:00 | Pass | Removed graffiti from externa walls
MSA-DTAG | WA3765765 | Level 1 - Lift 1 showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-16 16:18:00 | Pass | Error 203 door motor thermal. Inspected car doors and door drive. Error 3 code 44 value 46 off ssm tool. Could not get doors to drive. Obr for door drive replacement. Lift at top floor no charges $0
MSA-DTAG | WA3772120 | RETROSPECTIVE WORK ORDER Duress 209 in wrong location - ATT 15/7/20 | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-17 08:00:00 | Pass | Remove duress reinstalled when new desk installed
MSA-DTWD | WA3765152 | Level 1 W112A Aircon doesn't work | Mount Lawley Campus-Block A-West Wing | GMP-BR | Air Conditioning | Ducted Split System (AC) | Precise Air Group | 1 | CLOSE | 16 Nov 2020 | 2020-11-16 17:00:00 | 2020-11-16 10:30:00 | Pass | Attended site and accessed wall split serving room W112A. Asked customer what issue with unit was and they said it was switching off intermittently, turned on and test ran (pressed A/H run button to allow controller switch on). Ran for 30 mins and no issue with operation found.
MSA-DTWD | WA3765261 | Level 2, Art Gallery- Ceiling damaged | Perth Campus B5 | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 16 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-16 12:30:00 | Fail | As per BRAF
MSA-DTWD | WA3765266 | D Block, Main Panel - Repair Open Circuit on Loop 1 | Leederville Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 16 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-01 15:30:00 | Fail | 27/11/20Investigated open loop fault to find short circuit on cable between MCP and D21 - quote to be forwarded to replace cabling and conduit work 01/12/20Replaced damaged cabling between MCP and D21 with conduit work. Also contacted Steven Myer about Electric Pump fault on FIP and investigated to find 3 I/O module had the negative and positive loop terminal fused together. Was advised to replace part on the same job 1x AMPAC 3 I/O module used
MSA-DTWD | WA3765360 | A Block, Room A126, Staff area- Light tubes not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-17 08:45:00 | Pass | Attended site and signed in, completed jsa, inspected work area, went and grabbed materials from Ute, replaced 10x tubes and starters in A126 and replaced 2x tube and starters in B block lvl2 staff kitchen. Tested to make sure all correct operation. **job comple**
MSA-DTWD | WA3765403 | J Block male student toilet, over urinals- faulty circular ceiling light fitting with LED | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 15:45:00 | Pass | Attended site and signed in. Completed jsa. Investigated faulty light in male toilets. Replaced with new led downlight. Tested all ok. Fcompleted paperwork. Job complete.
MSA-DTWD | WA3765411 | Store room door in Meeting room - Door not working | Perth Campus B1 | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 15:18:00 | Pass | Works complete
MSA-DTWD | WA3765509 | Lvl 6, Cupboard next to W606 - Broken lockable door handle | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 10:50:00 | Pass | Fit nightlatch supplied by client to Level 6 cupboard
MSA-DTWD | WA3765529 | ground personal gate padlock will not unlock | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 10:15:00 | Pass | Padlock will not unlock on personal gate.Lock repaired.
MSA-DTWD | WA3765614 | Female level 2 & Male level 3- Door Handle broken | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-12-03 14:55:00 | Fail | 23/11/20 9.30am-10.10am Checked handles to public toilets. Need rto return with stock (three pairs of 1360/1361/70SC handles)
MSA-DTWD | WA3765634 | Lift car Lift not working - responds to calls but doors will not open automatically | Perth Campus B6 | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 14:25:00 | Pass | REPLACED TOP OF CAR BATTERY - No cost
MSA-DTWD | WA3765708 | Pool- Gate valve leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-16 13:30:00 | Pass | Replace faulty gate valve to pool
MSA-DTWD | WA3765817 | M Block - Zone 9 smoke detector has gone into alarm. | Balga Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 16 Nov 2020 | 2020-11-17 17:00:00 | 2020-11-17 15:30:00 | Pass | No further action required
MSA-DTWD | WA3774060 | Water leaking through windows south side of classroom. | Midland Campus | GMP-BR | Building | Windows (BU) | AWB Co. | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-12-16 09:45:00 | Fail | Works complete as per BRAF scope/CSS attached
MSA-MRWA | WA3765468 | Replace 2x downlight & refurbish 600x600 fluro panels – Must book before arriving | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-Electrical Equipment Riser | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-17 09:00:00 | Pass | Attended site and signed in. Got keys from facilities. Located director suite on level 8. Found 1 x panel light not working and 2 x downlights. Replaced lamps in all light fittings with site supplied materials. Clean and tidy site. Signed out. Job complete
MSA-MRWA | WA3766257 | Room 825- Faulty light that need replacement, lifting platform required. | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-Electrical Equipment Riser | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 16 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 08:15:00 | Pass | Attended site and signed in. Located man lift on site, pushed into building and took up to level 8. Checked out lights not working and which ones need the man lift. Used lift to access and replace lamps as required. Replaced all lights out in the open area. Tested all okay. Took man lift back outside and off hired machine. Clean and tidy site. Signed out. Job complete
MSA-DCA | WA3791047 | Level 1, Green Room- Complete decontamination clean due to positive E.Coli result | His Majesty's Theatre-Theatre Building-Level 1-Green Room - Staff Lunch Room | GMP-BR | Cleaning | Emergency Cleans (CL) | DUNBAR SERVICES (WA) PTY LTD | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 12:15:00 | Pass | Sink Decontamination
MSA-DCA | WA3792053 | Stairs on ground level from Murray street entry - plates on the face of stairs are coming loose and | King Street Arts Centre-Main Building-Ground Floor-Stair Landing Area - From Ground Entry Foyer | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 12:30:00 | Pass | Installed stainless sheet to the front of the stair tread
MSA-DCS | WA3787243 | Melaleuca Prison - Gatehouse - Since power upgrade not all cameras are connecting to the servers. | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Nov 2020 | 2020-11-17 07:51:09 | 2020-12-18 11:59:00 | Fail | Attended site and repaired multiple faults after power outage and UPS failure.Tested OK.Job Complete
MSA-DCS | WA3790793 | Zone 12 fence is in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Nov 2020 | 2020-11-17 09:56:13 | 2020-11-17 11:47:00 | Fail | Fence cabling heavily damaged by detainees on fence, replaced damaged section, replaced 3x splice kits and joins, cable ties added to entire zone, access to high section via extension ladder, tested zone now operational. Be advised cable had been stretched quite badly but appears operational and tested ok.
MSA-DCS | WA3790916 | Main access rood to Prison- Pot holes in road require repairing | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 2 | CLOSE | 17 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 09:00:00 | Pass | 18/11/2020Main road pot holes repaired.It was noted that the road way is in poor condition due to tree roots and excess water.
MSA-DCS | WA3790924 | Unit 5, Cell 5- Cold tap does not turn off, jumps thread | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 07:23:11 | 2020-11-18 15:00:00 | Fail | Renew spindles to basin hot and cold
MSA-DCS | WA3790985 | Unit 1, Cameras 26 & 41 not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 07:40:59 | 2020-11-17 13:33:00 | Pass | Rectified and fixed the monitors cctv on unit 1, check and test all cameras. Job completed.
MSA-DCS | WA3791017 | Kitchen, loading dock - Tap damaged & leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 17:30:00 | Pass | Renew outside tap to loading dock
MSA-DCS | WA3791146 | Gym - Termite investigation | Casuarina Prison | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-18 08:45:00 | Pass | Termite Activity Was Found.
MSA-DCS | WA3791151 | kitchen bakers oven is not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 08:48:40 | 2020-11-17 12:45:00 | Pass | completed 17/11/20
MSA-DCS | WA3791333 | gate house UPS has not holding | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Elec Power Technologies | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-17 15:30:00 | Pass | job completed - Site attendance to investigate UPS fault with Gatehouse
MSA-DCS | WA3791334 | Perimeter MW Zone 1 MW Beam set in Zone 1 hit by machinery, needs reallignment | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Nov 2020 | 2020-11-17 18:38:47 | 2020-11-17 12:34:00 | Pass | Phone Support:MW and pole have been hit by a crane and are now out of alignment. Contacted Andy Moar and Craig Eynon on site - security officers willing to carry out temporary alignment under SEME instruction - provided instruction on re-alignment of MW set - Site successfully re-aligned and restored operation of MW set - Site will arrange local civil contractor to address re-levelling of the pole and SEME can attend to carry out final alignment of MW set at a latter stage if needed. Site/ PFM to request attendance if required.
MSA-DCS | WA3791377 | PDA 301 has been reported lost, can SEME please attend to deactivate and replace with new device | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 11:23:38 | 2020-11-27 15:01:00 | Fail | PDA 301 missing, replaced PDA with site stock, replacement PDA has been ordered for site stock
MSA-DCS | WA3791380 | Admissions, Staff toilet- toilet light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-12-01 13:00:00 | Fail | Replaced sensor.
MSA-DCS | WA3791388 | Check diesel pumps showing fault post HV shutdown last night | Hakea Prison | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-18 12:48:00 | Fail | Fuel transfer system operating as expected, however should be replaced moving forward
MSA-DCS | WA3791396 | SHU (9) - Control Room has lost the ability to control electronic doors. | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Nov 2020 | 2020-11-17 15:38:24 | 2020-11-17 13:45:00 | Pass | SHU access control system failure, traced issue to system software, restored EBI A and checked operational, door control has been restored.
MSA-DCS | WA3791415 | unit 1 End of D-Wing & Outside Cell D-3 Damaged Rubber Flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Rubber (FL) | Midolo Building Services | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-01 13:30:00 | Fail | DAMAGED SECTION OF RUBBER FLOORING REMOVED & REPLACED WITH NEW.
MSA-DCS | WA3791421 | unit 2 End of A-Wing & Outside Cell Doors Damaged Rubber Flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Rubber (FL) | Midolo Building Services | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2021-01-15 15:15:00 | Fail | DAMAGED SECTIONS OF RUBBER FLOORING UPLIFTED & REPLACE WITH NEW - VARIOUS REPAIRS CARRIED OUT
MSA-DCS | WA3791433 | unit 1 C-D-Wing Common Area Damaged Rubber Flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Rubber (FL) | Midolo Building Services | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-14 15:00:00 | Fail | DAMAGED SECTION OF FLOORING UPLIFTED / REPLACED WITH NEW
MSA-DCS | WA3791454 | front gate, Fire Panel - Showing Fault N.1 202 | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 12:00:50 | 2020-11-18 09:01:00 | Pass | 1: Unit 2 Device 2005 plant room S/A smoke detector failed removed device and fitted new detector.2: 1.202 missing module fault traced to be mimic in CCU pod had been moved pulling cable out of unit. Corrected and re terminated ok.
MSA-DCS | WA3791547 | Switchboard has been water damaged | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | Distribution Board (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 17 Nov 2020 | 2020-11-17 17:07:20 | 2020-11-27 16:30:00 | Fail | Replaced water damaged switchboard
MSA-DCS | WA3792080 | Alarm are faulty in -self care unit -Murchison | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 16:51:00 | Pass | Repaired sensor faults in Murchason self care unit and tested all ok.
MSA-DCS | WA3792093 | internal security system is out and not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Nov 2020 | 2020-11-17 22:35:16 | 2020-11-17 20:30:00 | Pass | Power cycle networks controller SN2, senstar internal perimeter back on line. Job completed.
MSA-DFES | WA3791175 | Driveway and Car Park - 16 metres cracks in car park | FESA RHQ - Forrestfield | GMP-BR | Paving & Roadworks | Paving (PR) | MR POTHOLE | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 10:40:00 | Pass | job completed - Crack sealing
MSA-DFES | WA3791179 | Radio Comms - Faulty Fluorescent Tubes in office | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-17 13:15:00 | Pass | CompleteReplaced faulty fluros
MSA-DFES | WA3791210 | Ground - Asbestos ceiling sheeting dropping requires refixing corner of exit to carpark closest | CFRS Fremantle | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-18 14:30:00 | Pass | Replaced missing plastic angle between sheets. Edging was siliconed into place. No disturbance of material required
MSA-DFES | WA3791244 | office, male showers - Hot water Service not working properly. Unable to regulate the shower temp, | Jandakot Airport Hanger | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 12:20:00 | Pass | Quote Submitted - not approved.
MSA-DFES | WA3791521 | Boundary fence in north east corner is damaged | FESA RHQ - Forrestfield | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 12:30:00 | Pass | Repaired section of broken electric fence
MSA-DFES | WA3792028 | Lift 2 - is really when reaching a floor and doors really slow to open | DFES Cockburn Emergency Services Complex | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 17 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 15:05:00 | Pass | job completed - Found door lock on level 2 jamming, lubricated all locks and serviced - to be closed out at $0
MSA-DTAG | WA3790904 | Damaged timber skirting in Custody Interview room- see notes below | Supreme Court | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo Building Services | 3 | CLOSE | 17 Nov 2020 | 2020-11-23 17:00:00 | 2021-02-25 09:35:00 | Fail | TIMBER SKIRTING REPLACED
MSA-DTAG | WA3790932 | External - Repair cracks in wall above the entry to Judges underground car park | Supreme Court | GMP-BR-HO | Building | External Walls (BU) | Midolo Building Services | 3 | CLOSE | 17 Nov 2020 | 2020-11-23 17:00:00 | 2021-04-01 10:00:00 | Fail | brickwork repaired and painted
MSA-DTAG | WA3791042 | Public waiting area Several seats are loose - see notes | Armadale Courthouse | GMP-BR-HO | Furniture | Office Furniture (FU) | Midolo Building Services | 3 | CLOSE | 17 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 14:15:00 | Pass | NEW SCREWS AND WASHERS INSTALLED TO SECURE LOOSE SEATS IN PUBLIC AREA
MSA-DTAG | WA3791237 | 1903 L1 Jury deliberating room filter light is flashing - see notes | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-18 13:45:00 | Pass | Had to wait to find the correct system then had to return when the jury had deliberated. Filter was completely blocked. Changed filter, flushed and checked under pressure
MSA-DTAG | WA3791448 | 1903 roof Pump pipe split and leaking on roof-mounted cooling tower. | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-17 16:00:00 | Pass | Attend site. Access roof and check water pump. Found pvc fitting on suction of pump to have cracked and leaking water. Leave site and pick up new fitting and pipe. Return to site. Access roof water pump, disconnect pump from fittings. Cut out cracked fittings and and glue in new section of pipe and new fittings. Reconnect pump and test operation. No more leaks found, pump working as normal.
MSA-DTAG | WA3791651 | Public disable toilet seat is damaged | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 08:45:00 | Pass | Realigned and tightened toilet seat
MSA-DTAG | WA3792014 | custody control & registry cameras programmed system to enable date & time to reflect camera's- | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Total Security Systems Pty Ltd | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-19 16:15:00 | Pass | 19/11/2020 - Jose Pereira - 1.30pm to 4.15pmAdded the time and dates to all cameras on site.
MSA-DTWD | WA3790885 | Room B254- Projector pull down screen is damaged | Perth Campus B6 | GMP-BR | Equipment | Office Appliances (EQ) | AWB Co. | 3 | CLOSE | 17 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-26 10:00:00 | Fail | Supply new fixtures and brackets to hang projector
MSA-DTWD | WA3791117 | A Block, Room A363- Male toilet basin washer faulty | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-25 15:00:00 | Fail | Complete
MSA-DTWD | WA3791147 | T block ground T011 LED ceiling light blown | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-17 14:00:00 | Pass | Replced faulty downlight and checked for otther lights out. No other lights out
MSA-DTWD | WA3791188 | M block ground M03 Active termites. | Midland Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-18 10:50:00 | Pass | Broke open workings and applied 3 Litres Termidor @ .6% to cupboards near sluice
MSA-DTWD | WA3791426 | Gate 10 - Repair pothole at the Mirrabooka Drive entrance Gate 10 | Balga Campus | GMP-BR | Paving & Roadworks | Concreting (PR) | MR POTHOLE | 3 | CLOSE | 17 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-20 09:20:00 | Pass | Job completed - Pothole repaired
MSA-DTWD | WA3791458 | U block man hole cover on the storm water pit between U Block & T Block has severely rusted through | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 17 Nov 2020 | 2020-11-20 17:00:00 | 2021-06-03 17:09:00 | Fail | Installed new plates as per quote
MSA-DTWD | WA3792049 | E block male student toilet cistern in urinal not flushing | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-18 11:15:00 | Pass | Replaced broken cistern with new
MSA-MRWA | WA3792032 | bridge compound yard Egress gate non-functioning stuck in open position | Materials Engineering Branch | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 17 Nov 2020 | 2020-11-18 17:00:00 | 2020-11-17 16:50:00 | Pass | Inspected gate and found that safety photo beams had failed. Replaced as necessary with new faac photocell set as necessary, checked over and tested operation upon completion and left in good working order.
MSA-DCA | WA3792856 | toilet - blocked toilet (Please contact David to arrange access.) | State Archives Repository Dianella-Main Building | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 09:47:32 | Pass | Unblocked tpilet, replaced faulty inlet valve and ministop.
MSA-DCA | WA3794364 | Lift 5 stuck with someone inside and alarm is activating | State Library of WA-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 14:35:00 | Pass | Lift out of service from night before. Load weighing was beeping but lift counterweight was sitting on buffers. Reset lift backinto service and monitored going forward
MSA-DCS | WA3792143 | Zone 13 and tamper alarm in zone 8 | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 05:31:14 | 2020-11-18 13:45:00 | Pass | Attended site checked and found Zone 13 Fence alarm not activating. Further check located the problem to be the sensor cable. Rectified the sensor cable problem, reboot controller and tested alarm activated and reset correctly. Tested Zone 8 tamper alarm ok.
MSA-DCS | WA3792188 | Unit 4, Cell B8 - door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 18 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 12:15:00 | Pass | Attended site, serviced cylinder and tightened cam screws for correct operation.
MSA-DCS | WA3792200 | Gate house - Controllers are faulty. | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 10:38:58 | 2020-11-19 16:46:00 | Fail | Investigated and found Main-multiport Lantronix device failed. Retrieved replacement from PFM stores, installed onsite and programmed. Tested OK. Job Complete
MSA-DCS | WA3792226 | Abbaitors- electrical switch is faulty on hoist | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 09:00:00 | Pass | Investigate and replace damaged switch for hoist.
MSA-DCS | WA3792229 | SHU(9), Cell A6- Obs light not working, turn on switch but light wont turn on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 07:16:32 | 2020-11-25 13:30:00 | Fail | Attended SHU, unable to gain access to cell. Returned and repaired faulty lights in a6
MSA-DCS | WA3792279 | SITE COST unit 3 Cell B5 Tap will not shut off at sink (have isolated water to cell0 | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 11:58:11 | 2020-11-18 13:00:00 | Fail | Renew pillar tap to basin alter pipe work to suit
MSA-DCS | WA3792280 | Mutliple zones not activating on perimeter | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 11:59:14 | 2020-12-17 11:21:00 | Fail | Repaired multiple perimeter faults and tested OK.Job Complete
MSA-DCS | WA3792281 | Unable to activate cameras on EBI | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 12:01:53 | 2020-12-17 11:22:00 | Fail | Repaired camera faults and tested OK.Job Complete
MSA-DCS | WA3792282 | Cameras 61 & 52 not operating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 12:02:51 | 2020-11-18 10:15:00 | Pass | Reload the camera due to lost of communications from DVM systems, job completed.
MSA-DCS | WA3792283 | Zone 24 external perimeter trax constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 12:03:29 | 2020-11-19 10:30:00 | Fail | Recalibrate and reload settings due to constant alarming. Job completed.
MSA-DCS | WA3792294 | unit 3 Cell D4 Bed sides damaged by water, needs replacing- see notes | Hakea Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 08:15:38 | 2021-02-15 14:30:00 | Fail | DAMAGED BEDSIDES REPLACED
MSA-DCS | WA3792310 | unit 6 day room HW urn not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 09:30:00 | Pass | Hot water is fine . Thinking over use in morning time and just not recovering in time. Told by guards that the may use it for mop bucket
MSA-DCS | WA3792311 | main kitchen 1x 15 amp GPO 2x 10 amp GPO broken - please check all GPO as they are loose | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 13:00:00 | Pass | Replaced power outlets in kitchen
MSA-DCS | WA3792312 | main kitche 5 x lights damaged replace with LED's | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 15:00:00 | Pass | Replaced 5x LED fittings in kitchen
MSA-DCS | WA3792313 | unit 2 cell C16 light switch inside cell not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 15:30:00 | Pass | Replaced tubes and starters
MSA-DCS | WA3792316 | unit 2 cell D12 shower and sink spindles leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-10 16:30:00 | Fail | COMPLETED
MSA-DCS | WA3792320 | Unit 3, Cell D4- Cell call plate is missing | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 08:40:54 | 2020-11-19 09:30:00 | Fail | Job completed under job Wa3717614.
MSA-DCS | WA3792334 | Unit 7 - A11 toilet is leaking in cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-23 16:00:00 | Pass | Nill
MSA-DCS | WA3792335 | INF(10), Cell B2- Obs light switch will not operate from the outside of the cell | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 12:30:00 | Pass | Repaired faulty lights in infirmary b2
MSA-DCS | WA3792354 | Unit 7, E Wing Showers- Leaking Through back of tiles. Tiles cracked and broken. Grout removed | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2021-02-24 14:05:00 | Fail | IT WAS DETERMINED THAT THE WATER LEAKING FROM WALL IS A PLUMBERS ISSUE (BROKEN PIPE). NO DAMAGE OF TILES EVIDENT
MSA-DCS | WA3792358 | visits cleaning store - hot water unit leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-12-04 11:10:00 | Fail | Replace hot water unit, electrical needs to be wired by electrician
MSA-DCS | WA3792426 | unit 1 Cells 1 & 2 C & D Wings Vesda Faulty has stuck valves | Melaleuca Prison | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 09:44:31 | 2020-11-26 12:22:00 | Fail | Attended site and removed old faulty vesda Fitted new vesda programmed and tested and fitted new water splash cover. Left system normal.
MSA-DCS | WA3792506 | Gate House - Control Room eastern sally port not closing | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 14:24:12 | 2020-11-18 16:00:00 | Fail | 18/11/20Inspect fault.Remove, clean and re-assemble limits.Test all relays.Test correct operation of doors.Re-adjust limits.
MSA-DCS | WA3792527 | CCU- time delay with cameras | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 14:35:53 | 2020-11-19 18:20:00 | Fail | Rebooted ebi ws and reload the correct video pain. Job completed
MSA-DCS | WA3792569 | INF (10), Cell B2- Obs light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 08:05:00 | Pass | Repaired faulty lights in infirmary b2
MSA-DCS | WA3792580 | Unit 5, A & C- sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-19 13:30:00 | Pass | Nill
MSA-DCS | WA3792583 | Unit 2, Cell A12- Viewing hatch frame is missing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-23 09:00:00 | Pass | SLIDER FRAME TO CELL DOOR REFITTED
MSA-DCS | WA3792590 | Main Area, Back left hand end- Cockroaches are coming out holes in ceiling | Midland (North East Metro) | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 11:19:05 | 2020-11-19 07:50:00 | Pass | Cockroaches Treatment - Main Area, Back Left hand End.
MSA-DCS | WA3792592 | Unit 14, Cell D16 - washbasin is blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-26 08:30:00 | Fail | nil
MSA-DCS | WA3792600 | Unit 2, Cell A11 - Window frame vent stuck closed | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-23 11:00:00 | Pass | VENT REMOVED & REPAIRED, RE INSTALLED
MSA-DCS | WA3792610 | Unit 3, A4 - A04 powerpoint (closest to the window) has something stuck in it. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 08:30:00 | Pass | Replaced damaged gpos in unit 3 a4
MSA-DCS | WA3792631 | Official visits, Spine side Internal Airlock Door - Door lock body jamming in unlock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 10:45:00 | Pass | On site. Replaced faulty mortice lock and adjusted strike to restore normal function.
MSA-DCS | WA3792665 | Camera 17 Zone 16 is offline | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2021-05-05 14:51:00 | Fail | Job is complete.
MSA-DCS | WA3792666 | UVSS Monitor has failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-19 17:30:00 | Pass | Monitor has failed half the screen not working, Replaced with site stock Dahua 27" required to replace site stock
MSA-DCS | WA3792667 | Unit 1 House 4 Cell 1 Front door reed switch has been vandalised | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-19 21:09:00 | Pass | Reed switch has been cut, cables stuck in door frame,Remove lock to access cables, retrieved cables and installed new rs, reinstalled all dooe hardware Downloaded footage for security
MSA-DCS | WA3792668 | Keywatcher door 2 not locking | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-20 16:03:00 | Pass | Keywatcher door lock not working correctly,removed lock and repaired worn spring, utilized parts from lock that has failed.replaced fixings holding lock into Keywatcher frame and applied Loctite to prevent them from loosening.repositioned reed switch and removed bugs from enclosure
MSA-DCS | WA3792671 | Unit 5 entry cell call is not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-19 21:04:00 | Pass | Cell call has stopped two way communication.Removed faulty cell call and installed new CI CC from PFM stock
MSA-DCS | WA3792688 | Download footage from 17/11/20 zones 23 & 24 | Hakea Prison | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-17 11:22:00 | Fail | Searched and downloaded multiple recordings and extracted data. Provided data to Security.Job Complete
MSA-DCS | WA3792692 | Unit 4 PRU fibre rack top PSU battery low/mains low fault | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-18 15:30:00 | Pass | Remove redundant programming causing alarms at the PRU Rack.
MSA-DCS | WA3792704 | Unit 2, lower landing outside ablutions- GPO's no power | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-20 11:30:00 | Pass | Investigate and repair unit 2 ablutions power
MSA-DCS | WA3792781 | Unit 1 Cell B23, stainless steel shower base has broken down water is leaking into cell next door | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 13:41:02 | 2021-03-17 15:52:00 | Fail | Water leaking around broken tiles and around top of shower base due to damaged tiling needs water proofing and tiling
MSA-DCS | WA3792787 | Gate House- Inner fence perimeter door closer, see notes below | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-27 08:00:00 | Fail | 20/11/2020. On site. Technician shown wrong door by staff. No action taken as no evident fault.27/11/2020. Attend site. Adjusted door closer and lubricated hinges on correct door with issue. Tested as functional.
MSA-DCS | WA3792794 | Admin, door between corridoor and counceling rooms lock barrel faulty keys jamming | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 09:30:00 | Pass | On site. Serviced and lubricated lock. Functioning normally with keys available for testing.
MSA-DCS | WA3792804 | Unit 4, Cells 4,5,6,7,8- no power to cells, see notes below | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 17:58:48 | 2020-11-18 15:30:00 | Pass | Power tripping U4 replaced gpo
MSA-DCS | WA3792832 | Exp Project unit 16 - Vesda Faults on FIP which will not reset and are alarming on a regular basis. | Casuarina Prison | WSM-MW-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 18:22:21 | 2020-11-18 16:19:00 | Pass | Attended site to unit 16 and found the following 1: Multiple MASDS in intermittent flow separator fault. 2: Found that units exhaust is exiting into roof space and not in the same area as the sample point as this can cause flow problems. Attached picture of page in manual.See section on flow fault errors. 3: faults will need to be pushed back to the builder as it possible hasn’t been installed/setup correctly since installed. Or ARA could attend with Ampac to do check system setup.
MSA-DCS | WA3792835 | Unit 1, B Wing- Ablutions block closest to control- water leaking through walls | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 14:29:20 | 2021-03-17 15:54:00 | Fail | Pipework needs replacing in walls
MSA-DCS | WA3792837 | SHU, Cell B8 East Wing's- hot water is not working. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 14:33:28 | 2020-11-19 09:30:00 | Pass | Nill
MSA-DCS | WA3792894 | Unit 6 door 4 to be configured the same as the bolt hole door to the Unit 6 staff kitchen area. | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 11:50:00 | Pass | Door 4 in Unit 6 reconfigured, tested and commissioned with security infrastructure manager.
MSA-DCS | WA3792931 | control room - PTZ 24 wont swing to zone 14 when alarm goes off | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 08:00:00 | Pass | PTZ 24 won't swing to zone 14, reset background alarms, indigo software boot multiple cameras lagging, system fully restored. Tested working correctly
MSA-DFES | WA3792371 | electrical room power outlet to be capped as it is faulty | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 13:45:00 | Pass | CompleteAttended site and removed light and GPO in electrical room as it was in the way of new equipment and would be damaged.
MSA-DFES | WA3792602 | Ground floor stair 2 external door, handle is loose on external side | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Building | General Building (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 13:30:00 | Pass | Refitted loose screws
MSA-DFES | WA3792888 | Office, unisex toilets - not working | DFES Baldivis | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 10:30:00 | Pass | Replacing toilet cistern
MSA-DTAG | WA3792301 | Basement, Custody Cell 3- Toilet running constantly | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 08:05:00 | Pass | Replaced bellow and outlet washer
MSA-DTAG | WA3792343 | L30 SSO PACOM PC not working - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 10:30:00 | Pass | Attended site, met with Security. Rectified issues with the Security PC. All running correctly.Job completed
MSA-DTAG | WA3792352 | L1 room 1.11 when duress is activated the does not get unlocked | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 11:00:00 | Pass | Attended site. At the time of investigation, the meeting room was occupied and unable to test fault. Found misconfiguredmacro settings on the server that needs programming. Will sort upon server database upgrade works, week of 7thDecember.Job completed.
MSA-DTAG | WA3792706 | Level 5, public toilets (Hay Street end) - Female toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 16:00:00 | Pass | Complete
MSA-DTAG | WA3792708 | Level 2, public toilet - Unisex toilet is blocked opposite Caffisimo | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 15:30:00 | Pass | Complete
MSA-DTAG | WA3792859 | Children's Court Airlock - hole in wall (see notes) - photo viewable in ProMAP attachments | Rockingham Justice Complex | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-17 09:18:00 | Fail | Ceiling repaired and painted
MSA-DTWD | WA3792250 | A Block, Level 2, AC Duct - Sensor is faulty | Joondalup Kendrew Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 11:33:12 | 2020-11-18 12:20:00 | Fail | In ceiling detector activated in alarm, room A237 replaced base and detector head. While onsite, I was asked to look at FIP LED screen as it Is faulty (glitching).
MSA-DTWD | WA3792255 | A Block, Air Con needs to be reinstated after fire fault, see notes below | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 18 Nov 2020 | 2020-11-18 11:35:10 | 2020-11-18 11:00:00 | Pass | Investigate Block A level 2 West and found some isolated. No units running in Block due to isolation. Reset transformers and much services now operating. Critical fire to replace fire detector due to possible faulty sensor.
MSA-DTWD | WA3792296 | A Block, Cafe Area - Arming panel fault, see notes below | Leederville Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 11:30:00 | Pass | 19/11/2020, 1100-1130Zone 100 door is openClosed door zone sealed okAll zones ready to arm
MSA-DTWD | WA3792298 | L block first level Female Ambulant Toilet blocked | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-18 12:00:00 | Pass | unblocked toilet
MSA-DTWD | WA3792448 | Tower block, level 4, east, main meeting door - wont close properly | West One Services | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 18:00:00 | Pass | hang pictures as required
MSA-DTWD | WA3792452 | Tower block, level 4, east - faulty Fluro's replace/repair | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 10:00:00 | Pass | Attended site and signed in. Got keys from reception. Went up to level 4 in tower. Spoke with staff on floor about lights. Found a few out and flickering. Removed all dead and flashing tubes. Replaced with new tubes and starters. Refitted light cover to a light that was taken down. Tested all okay. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3792542 | B Block, Room B101- AHU 2 Actuator is faulty | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-07 15:00:00 | Fail | Ahu2 faulty c/w valve actuator replaced .Locking rings and shaft stem locator installed. Valve stem seal cleaned of debris. Insulated c/w attatchment and reinstalled flashing box. Rewired actuator to suit and adapted fittings to suit. Bms operation test gd. Valve restored to auto operation
MSA-DTWD | WA3792549 | B block, spray painting area - mechanical switch board fault (with fans and exhaust) | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 1 | CLOSE | 18 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 09:42:00 | Pass | replaced switchboard isolater
MSA-DTWD | WA3792613 | F Block, Room FF09- Buzzing noise coming from Alarm Speaker | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 10:00:00 | Pass | Buzzing noise coming from vents not from fire equipment, Checked EWIS & detector working well no problem.School maintenance is looking into the vents. call out to fault find two guys 1 hour.COMPLETED
MSA-DTWD | WA3792646 | B Block, Staffroom- Relief Valve for Rheem not working | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-19 11:30:00 | Pass | Replace relief valve not working
MSA-DTWD | WA3792820 | G floor- Jobs and Skills entry- Light switch faulty in entry, see notes below | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 12:00:00 | Pass | Attended site and signed in. Located jobs and skills. Found middle light switch faulty and non operational. Located switch room down stairs and isolated light circuit. Disconnect and removed faulty light switch. Supply and replace with new switch. Tested all okay. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3792852 | workshops far end roller door, the padlock will not pich closed. (Broken) | Clarkson Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 10:00:00 | Pass | Replace damaged padlock on end roller door of workshop
MSA-DTWD | WA3792877 | V block male & female toilets are blocked | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 09:19:00 | Pass | Cleared blockage using jetter
MSA-DTWD | WA3792945 | Block C -Main entry Auto door is faulty | Mandurah Campus (formerly Peel)-Block C-Ground Floor-Administration | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 18 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-19 10:48:00 | Pass | 1064271/601910. (No asset number).Call to site. Attend to auto door. Check manual door lock to find receptacle jammed. Free this and refit/test. Although this is now functional it feels that it may malfunction in the future. Recommend a locksmith to replace complete lock.
MSA-DTWD | WA3799392 | ** Retrospective work order ** Main office and entrance-Fire detector is faulty, see notes below | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 18 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-18 12:30:00 | Pass | ATTENDED SITE, FAULT DUE TO WATER IN DETECTOR. REMOVED DETECTOR (DETECTOR WAS CORRODED). CLIENT TO REPAIR WATER LEAK & CUT ACCESS HATCH INTO CEILING PRIOR TO RE-ATTENDANCE. NEW WORK ORDER TO BE RAISED ONCE CLIENT REPAIRS ARE COMPLETE
MSA-DCA | WA3794525 | FCU 2b condensate pump is noisy | Shipwreck Galleries-Main Building-Ground Floor | GMP-BR | Mechanical Services | Pumps (MS) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-23 08:57:00 | Pass | COMPLETED
MSA-DCA | WA3794931 | Disabled lift is making a loud screeching noise | His Majesty's Theatre-Theatre Building-Ground Floor-Lift Lobby | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 15:30:00 | Pass | Lift3 DisHoist HMT-Accessibility unit :lift making a noise.replace guides and clean rails and reapply lube to rails.make some adjustments to guides and test run.left in service
MSA-DCS | WA3792962 | Site Perimeter zone in Tamper | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 11:30:00 | Pass | Site perimeter zones found not in tamper but solid pink indicating communications error, restored network and tested fully operational.
MSA-DCS | WA3792963 | Site perimeter zones in Fault | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 09:30:00 | Pass | Restored inner defence microwave zones now operational.
MSA-DCS | WA3794236 | Fence Zone 8 tamper alarm in fault | Wooroloo Prison Farm-External Areas | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 05:23:20 | 2020-11-19 13:55:00 | Pass | Replaced and rectified
MSA-DCS | WA3794261 | Dairy Cool Room - is not cooling. | Karnet Prison Farm-Dairy Cool Room | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 19 Nov 2020 | 2020-11-19 10:01:41 | 2020-11-19 11:00:00 | Fail | attend site and check coolroom . found overload tripped , reset and carried out tests and cleaned condenser unit . left system operational.
MSA-DCS | WA3794290 | Kitchen large combi oven wash cycle not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 19 Nov 2020 | 2020-11-23 17:00:00 | 2021-01-04 15:30:00 | Fail | 01/12/20Arrive at site to check oven error when on cleaning cycle. Staff explain functions are ok but when on cleaning cycle it cuts out at some stage and tablets not dissolved. Check water connections all ok. RO tanks are full and good pressure to oven. Run on rinse cycle and find water leaking from hose at base connection to drain valve. Cut back and re attach, would recommend replacing as is worn in other areas also. Check function of drain valve and pumps in diagnostics all working well. Run on short cleaning cycle and all went through well. Parts required1 x Cleaning suction hose04/01/21Fitted parts and tested all ok
MSA-DCS | WA3794314 | Control Room- no audible alarms when areas are triggered | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Nov 2020 | 2020-11-19 11:12:38 | 2020-11-19 16:40:00 | Fail | Repaired multiple hardware faults and tested OK.Job Complete
MSA-DCS | WA3794345 | Jeelia, C Wing - Unit TV room unable to turn key to open door | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 19 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-27 08:15:00 | Fail | 20/11/2020. On site. Inspect lock. Replacement cylinders required.27/11/2020. On site. Replaced cylinders and tested. Normal function restored.
MSA-DCS | WA3794358 | Gascoyne, Cell A1- Sticky outside key barrel | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 19 Nov 2020 | 2020-11-23 17:00:00 | 2020-12-04 08:30:00 | Fail | 20/11/2020 Attend site. Inspect lock. Parts required.04/12/2020 Re-attend site. Fit new cylinder as required to restore normal function.
MSA-DCS | WA3794380 | Unit 2, Staff Lunch Room- Rear Exit Door Lock Jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 08:01:26 | 2020-11-19 09:45:00 | Pass | Attend site. Serviced/repaired door lock to restore normal function.
MSA-DCS | WA3794438 | Perimeter - external zone 6 MW2 constant alarm | Hakea Prison | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 08:35:12 | 2020-11-26 18:00:00 | Fail | Multiple faults with zone 6. Replaced faulty Southwest microwave with Senstar Ultrawave. Fix3 low voltage issue to transmitter. Repaired tamper issue. Checked zones 5 and 6 microwaves. Tested ok back to the gatehouse. Parts used:Senstar Ultrawave pair
MSA-DCS | WA3794450 | Unit 5 Cell B5 Tile grout damaged | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2021-01-11 12:30:00 | Fail | TILES & GROUT REPLACED
MSA-DCS | WA3794461 | Ext Zone 3 sprinkler damaged next to training cntr - this zone always on, suspect relay jammed on | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 08:43:14 | 2020-11-19 15:40:00 | Pass | several coils had failed and required replacing
MSA-DCS | WA3794469 | HR Mangers office & bathroom - 2 lights have electronic ballast faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 08:49:56 | 2020-11-19 14:30:00 | Pass | Repaired lights
MSA-DCS | WA3794481 | unit 7, H16 - toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 09:01:21 | 2020-11-19 16:31:00 | Pass | Unblocked badly blocked toilet
MSA-DCS | WA3794483 | unit 7, E3 - toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 09:03:30 | 2020-11-19 17:25:00 | Pass | Unblocked badly blocked toilet
MSA-DCS | WA3794486 | unit 7, E17 - Tap Broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 09:04:10 | 2020-11-19 18:45:00 | Pass | Fixed leaking tap in the basin
MSA-DCS | WA3794528 | Unit 7, Regis oven - Not reaching Temperature | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-24 15:05:00 | Pass | Checked both ovens ok, all elements working etc. Left both operational.
MSA-DCS | WA3794539 | Unit 2, Cell C11- toilet wont fill/flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-24 11:30:00 | Pass | nil
MSA-DCS | WA3794666 | Main outter perimeter Electric fence EC8 - in fault | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 11:09:48 | 2020-11-24 09:45:00 | Fail | Replaced defective tamper switch and clear alarm from the systems. Job completed.
MSA-DCS | WA3794681 | Front gate, sally port - Sally Port Pit - a truck drove over the mechanical grate & it will not move | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 19 Nov 2020 | 2020-11-19 15:18:12 | 2020-11-19 12:45:00 | Pass | 19/11/20Removed grate panels from inspection grill.Bent back to shape.Put back on and tested - OK.Note, new panels will eventually be required in the future. A separate quote will be submitted.
MSA-DCS | WA3794688 | Gatehouse control room - screens are blank for 3 obs cells & the kitchen Unit 2, female donga | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Nov 2020 | 2020-11-19 19:20:23 | 2020-12-07 13:30:00 | Fail | Tested power supply to encoder and nvr, could not find fault, check programming and cabling, all ok. Power must have been disconnected at time, now all ok.
MSA-DCS | WA3794763 | Unit 3, Cell D8- Mesh on window damaged | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-04 12:00:00 | Fail | DOUBLE UP OF JOB #WA3873543
MSA-DCS | WA3794765 | Multiple lights faulty/blown see long description for location | East Perth | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 10:45:00 | Pass | Repaired lighting on various levels
MSA-DCS | WA3794772 | Unit 2, A5 - sink waste leaking & grate missing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-24 14:25:00 | Pass | Checked A5 and A15 basin.The grate has been replaced by Jim.
MSA-DCS | WA3794774 | Interview room 1 & 4 & Reception staff line doors open too long buzzer not working | Mandurah | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 12:04:10 | 2020-11-19 16:30:00 | Pass | Adjusted dots time form 60 seconds to 10 as per site request
MSA-DCS | WA3794780 | Unit 5 Cell B2 TV Splitter in cell plate damaged | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-09 10:30:00 | Fail | Replaced TV Point in Unit 5 Cell 62, tested signal, OK.Job completed.
MSA-DCS | WA3794796 | Unit 1 Cell B1 stainless pan damaged- see additional notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-24 13:50:00 | Pass | Checked and tested toilet pan no fault found.
MSA-DCS | WA3794798 | CCU Control Pod Repair Damaged Carpet | Melaleuca Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2021-03-08 08:00:00 | Fail | WORN DAMAGED CARPET REMOVED, FLOORS PREPPED & NEW CARPET TILES LAID
MSA-DCS | WA3794807 | Unit 7, A wing - The pipe underneath the A wing kitchen sink is leaking (round sink) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 11:30:00 | Pass | Nill
MSA-DCS | WA3794820 | INF(10) , Power point outside cell HC2 is not currently working, | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-23 07:42:00 | Pass | Restored power to infirmary cell hc2
MSA-DCS | WA3794847 | Unit 14, D Wing- Personal key snapped in lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-09 10:00:00 | Fail | Remove broken key, require parts.replace worn barrel.
MSA-DCS | WA3794863 | Fire alarm panel fault "L9S7324 ST missing FLT" | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-24 11:25:00 | Pass | 25/11/20 JNReplaced L9 S73 in unit 3 shower block A due to corrosion on old detector. Panel normal.
MSA-DCS | WA3794912 | Gatehouse - secure lobby door is not opening without override | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 19 Nov 2020 | 2020-11-19 18:44:22 | 2020-11-19 15:30:00 | Pass | Attend site. Door is secure and lock functioning properly. Problem is with electronic custodial strike which is not registering that door is shut even when it is. Access control system issue.
MSA-DCS | WA3794915 | Lvl 1, Interview room- Whiteboard has fallen off the wall | East Perth | WSM-BR-SITE | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-20 10:30:00 | Pass | Attended site and carried out repairs to the whiteboard that had fallen of the wall
MSA-DCS | WA3794923 | Unit 10 C14 Cell light Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 11:30:00 | Pass | Repaired light
MSA-DCS | WA3794963 | Back of alley way and staff room (leading out to courtyard) - boiling water coming from ground | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 19 Nov 2020 | 2020-11-19 20:47:59 | 2020-11-25 07:34:00 | Fail | Found pinhole under tarmac road in 40mm ring main, repaired main and Re-instated tarmac, copper in very poor condition
MSA-DCS | WA3796052 | RETROSPECTIVE WORK ORDER-gate house UPS has not holding - Attended 19/11 | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 19 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-20 14:45:00 | Pass | Repairs to UPS
MSA-DFES | WA3794873 | Engine Room Door 2 Career side front, tagged out by Go Doors. | CFRS Armadale | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 17:30:00 | Pass | Fault Found: Attended site as per work request and found large amount of impact damage on bottom 3 panels. Panels are cracked and warped. Bottom rh roller out of track. Number 1 roller hinge lhs twisted, number 8 roller hinge rhs twisted. Number 1 roller hinge lhs twisted and cracked, Lh cable not spooling g correctly on hub. Motor over driving door causing cables to be loose and not spool correctly which was sending the door up on an angle.
MSA-DTAG | WA3794778 | Basement -Technician to isolate FIP21/11/20 & de-isolate 21/11/20 - see times in notes | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-21 17:00:00 | Pass | 21/11 KSAttended site after hours at 6:30 and isolated Az’s 10, 17 & 18.Returned to site after hours and de isolated zones and left system normal.
MSA-DTAG | WA3794859 | Custody - Light in custody corridor has failed | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-30 08:30:00 | Fail | Replaced faulty lighting in custody and sallyportWas waiting for access due to people being in custody.
MSA-DTAG | WA3794921 | level 4, Public toilet - Disabled toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-19 15:00:00 | Pass | Complete, please read work logs for correct times.
MSA-DTAG | WA3794925 | Leaking tap in VSS bathroom | Rockingham Justice Complex | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-24 15:00:00 | Pass | COMPLETED
MSA-DTWD | WA3794286 | E Block, E58 Large Scale Kitchen- Hisco under bench fridge not cooling, see notes below | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 19 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 14:04:00 | Pass | ATTENDED SITE AND SIGNED IN. CARRIED OUT LEAK TEST WITH ELECTRONIC LEAK DETECTOR.. FOUND GAS LEAK ON FLARE NUT. TIGHTENED NUT AND RECHARGED WITH REFRIGERANT. CARRIED OUT FURTHER CHECKS UNIT NOW WORKING CORRECTLY. CLEANED COIL JOB IS NOW COMPLETE
MSA-DTWD | WA3794291 | N Block, Room N205- Blocked Urinal | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Nov 2020 | 2020-11-19 17:00:00 | 2020-11-19 16:30:00 | Pass | Unblocked urinal with K-50 drain machine and 1x bottle of mo-flo
MSA-DTWD | WA3794512 | Turf Area- GPO light on pole does not work | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-20 10:47:00 | Pass | Attended site and signed, completed jsa, inspected fault to gpo and control boxes, walked around site board to board found to be fed from main switch board, RCD W2 was tripped, reset RCD and power was reinstated back to gpo and boxes. **job complete**
MSA-DTWD | WA3794522 | E block, room E40, E46, E47 aircon not working | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 09:30:00 | Pass | Travel to supplier and organise replacement 7 day timer. Return to site. Remove faulty timer and replace with new one. Set to run from 6am to 8pm as facility managers request. Test operation. All ok. Job complete.
MSA-DTWD | WA3794529 | S Block- Hand dryers in the toilets do not heat up, so they are not working | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 16:00:00 | Pass | Attended site and signed in. Located S block toilets. Found hand dryers in all toilets. Tested hand dryers for auto function and heat function. All hand dryers pump out heat as required. All dryers flow good air as required. All dryers turn on and off as required. No problem with hand dryers. Fully functional. Signed out. Job complete
MSA-DTWD | WA3794721 | C Block Main Entry door lock is faulty | Mandurah Campus (formerly Peel) | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 12:45:00 | Pass | repairs to lock
MSA-DTWD | WA3794783 | E block - Repair white ant damage to the wall in E002 | Balga Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2021-04-21 09:00:00 | Fail | Works completed as per BRAFBRAF 4 submitted 21/04 - BRAF Declined - invoice cost to date
MSA-DTWD | WA3794907 | Block 10, G Floor, Room 10G72- Key lock not working | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-20 16:15:00 | Pass | Block 10 - 10G72 lock not working.Lock repaired.
MSA-DTWD | WA3794911 | Block 8, G Floor, Room 8G36- External door lock not working | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 19 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-20 16:15:00 | Pass | Block 8 - 8G36 lock not workingLock repaired.
MSA-DTWD | WA3794918 | E Block, E30 SSK, Station 9 sink, tap constantly running | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-23 08:24:00 | Pass | Fix leak and broken spout
MSA-DTWD | WA3794938 | Plant room Chiller #2 seal is leaking | West One Services | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 3 | CLOSE | 19 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-20 16:00:00 | Pass | Accessed site completed relevant sign in procedures, replaced x2 seals on chiller 2 condenser vessel , reassembled chiller checked for water leaks , bled air from system , all working fine
MSA-MRWA | WA3794535 | Light in fume cabinet not working (cabinet in left of attached photo) | Materials Engineering Branch-Asphalt Lab-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 19 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-19 10:46:00 | Pass | Repalced faulty lamps to fume cupboard.job complete
MSA-DCA | WA3795444 | Lift is not responsive and has dropped below floor level | PICA-Main Building-Level 1-Lift Foyer | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 10:45:00 | Pass | to be closed out at not Chargable
MSA-DCA | WA3795936 | L2 door 2 /37 door security lights green but does not open- see notes | State Library of WA-Main Building | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-23 12:00:00 | Pass | Attended site and spoke to Ben.Investigated door fault and found that the DPU was off line. Tried to restart the controller but foundthat the controller was faulty.Replaced controller with a site spare controller and restored controller config.Checked and tested door operation and confirmed door transactions.
MSA-DCA | WA3795966 | Toilet lights of circuit breaker will not hold | PICA-Main Building-Level 2-Female Toilet | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 06:58:00 | Pass | Ivestigate tripping light cct. Replace faulty ballast and damaged cabling.
MSA-DCS | WA3795179 | Sand build up and debris in zones 10/11- see notes below | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 3 | CLOSE | 20 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-15 16:30:00 | Fail | to be closed out at $0
MSA-DCS | WA3795180 | CCU Cell (11) D5 TV cabinet causing blind sport on corner mount camera, please liaise with SEME | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 20 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 15:00:00 | Pass | MODIFIED TV CABINET TO ELIMINATE BLIND SPOT
MSA-DCS | WA3795215 | Unit 7, Cells H8 & H23- Light switches broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 10:30:00 | Pass | Replaced light switches.
MSA-DCS | WA3795235 | Controller number 20 has failed | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 11:43:55 | 2020-11-20 09:00:00 | Pass | Maxpro Controller has been decommissioned on site, disabled and clear alarm. Job completed.
MSA-DCS | WA3795255 | Unit 5 control room Oval MKH barrel in control room door hard to turn key catches | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Nov 2020 | 2020-11-21 08:07:47 | 2020-11-20 12:45:00 | Pass | Attend site. Replaced faulty component (cylinder).
MSA-DCS | WA3795347 | Boilerhouse, warehouse- Boiler number 2 will not fire up, no fault shown, see notes below | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 07:00:00 | Pass | Investigated the fault of failure to start on Boiler #2.Investigated the fault and found the low gas pressure switch was hold out the boiler.On investigation it was found that the restriction on the gas supply were causing this and confirmed the restriction was caused by a mostly closed valve outside the boiler room.
MSA-DCS | WA3795349 | Boiler house workshop Boiler number 1 flame failure fault - see notes | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 16:00:00 | Pass | Travelled to site and got checked in, got escorted to the boiler room.Boiler 1 was faulting on pilot.Checked the burner and gas valves & finally tracked it back to the regulator.Tested the other Boiler (#2) and found it also had the same problem.The escort did not know where the main gas valve was located and the person who does had gone home.Returning back to site tomorrow & will chase it up then which may sort out all 3 boilers.Found the cause of the gas supply problem being a mostly closed valve outside the boiler room.Recommend a drain be fitted to the pressure sensor line on the boiler to remove blockages.
MSA-DCS | WA3795392 | control emergency alarm system not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 12:59:08 | 2020-11-20 10:00:00 | Pass | Test the control emergency alarms on site and verified from the units. Job completed
MSA-DCS | WA3795399 | Investigate fault fuel pump (electrical) serving generator | Wooroloo Prison Farm | SPA-BR | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-30 21:00:00 | Fail | Repaired various faults with pump
MSA-DCS | WA3795580 | INF(10), Cell B6- Inlet valve on toilet leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-27 12:30:00 | Pass | Nill
MSA-DCS | WA3795672 | Education, Room 9- Investigate reoccuring issues with locks | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-20 14:30:00 | Pass | Service lock, replace bolt throw.Teachers keys are worn and causing lock issues, advised to have security replace worn keys.Door is high use and requires servicing more often.
MSA-DCS | WA3795698 | between unit 3 and 4 fence end leaking fire hydrant | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 14:36:06 | 2020-11-20 14:23:00 | Pass | hydrant found to have debris pulled from the tank on site
MSA-DCS | WA3795711 | Cardex System is not operating and is down | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 14:43:53 | 2020-11-20 14:15:00 | Pass | Gallagher systems restored after generator testing, temporary NUC workstations are not backup up by UPS.System restored in fully operational.
MSA-DCS | WA3795718 | abattior - chillers 6 is not working | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-04 11:00:00 | Fail | located faulty TX valve and system short of gas , replace valve and sensor recharge system and left operational
MSA-DCS | WA3795721 | CCU all camera's frozen | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 14:52:14 | 2020-11-20 16:30:00 | Fail | Replaced faulty 19.5VDC PSU EBI WS CCU, job completed.
MSA-DCS | WA3795799 | Jeelia unit PA is not going through all units as should be | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 12:30:00 | Pass | No further action at PFM request
MSA-DCS | WA3795808 | unit 2 whole unit No hot water to showers and taps across the unit | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 20 Nov 2020 | 2020-11-21 11:59:46 | 2020-11-20 12:30:00 | Pass | Nill
MSA-DCS | WA3795845 | Education male toilet blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 09:25:00 | Pass | Cleared blocked male toilet.
MSA-DCS | WA3795869 | asphalt, Outside main kitchen - hot water coming out of ground outside kitchen **new location** | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 16:47:54 | 2020-11-25 09:02:00 | Fail | Repaired burst 32mm copper hot ring main to kitchen, report to programmed to follow
MSA-DCS | WA3795929 | Control Room - D4 mircowave beam is constantly in alarm, unable to reset | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Nov 2020 | 2020-11-21 13:33:09 | 2020-11-20 15:31:00 | Pass | Microwave zone d4 latched in alarm, zone is now operational, tecom relay appeared to have latched, all ok
MSA-DCS | WA3795956 | WWTP security flood lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 13:00:00 | Pass | Investigate and repair/replace flood lights at wwtp
MSA-DCS | WA3795957 | Unit 2, middle landing toilets- light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 08:30:00 | Pass | Investigate and replace unit 2 toilet light
MSA-DCS | WA3795963 | ISU (Harding), B Wing Southern end- Broken top door panel Approx 1200mm x 800mm | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-26 10:30:00 | Fail | DOOR PANEL RE GLAZED
MSA-DCS | WA3795965 | Unit 4, B Wing, Cleaning storeroom- water leaking from under sink area | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-30 11:30:00 | Fail | Nill
MSA-DCS | WA3795970 | Jasper, C Wing Lounge Area- smashed window approx 1400x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-26 15:00:00 | Fail | WINDOW REPLACED
MSA-DCS | WA3795975 | Dairy - hot water system has gone down. | Karnet Prison Farm | SPA-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 20 Nov 2020 | 2020-11-20 18:28:56 | 2020-11-24 13:00:00 | Fail | COMPLETED
MSA-DFES | WA3795969 | Ground engine room roller door openers slow to open and close not always opening sticking | VFES Karnup | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-27 13:30:00 | Fail | (27/11/2020) - Work NoteFault Found: Attended site as per work request. Doors slow and jerky and catching. Not always openingWork Completed: ran doors multiple times no fault found. Lubricated doors and guides.Increased open and close speed on both doors.
MSA-DFES | WA3795973 | southern western roller doors issues - please see additional notes | DFES Baldivis | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 08:55:00 | Pass | (25/11/2020) - Work NoteFault Found: Attended site as per work request and found all doors to be operating without issues.Work Completed: to prevent any of the reported issues in the future, I lubricated all roller door guides and cleaned allPE beams. I ran each door multiple times and doors did not fault.Checked that Weathershield is not getting caught in door guides, all good.All safety beams work in good condition.
MSA-DFES | WA3795991 | Gym, Middle LED (Fluro style) light globe bracket broken | CFRS Fremantle | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 11:15:00 | Pass | Arrived onsite and signed in at 0930Located damaged light in gym area. The lights brackets had deteriorated and were not repairable. With replace the fitting with a more suitable led variant. Notified station of works. Signed out and left site at 1115
MSA-DFES | WA3796005 | Undercroft Carpark, HAZMAT Storeroom- Light is out | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 09:00:00 | Pass | Arrived onsite and signed in at 0830Located faulty located faulty light fitting in hazmat store. The tube had gone faulty and we repaired accordingly. Notified staff and left site at 0900
MSA-DFES | WA3796053 | Buliding 55, engine bays - A number of CCTV cameras are blurry | CFRS Perth | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-30 08:30:00 | Fail | 30/11/2020, 730-830 (two Techs)Cleaned and adjusted cameras.Disconnected faulty cameraGot 2 others operational.
MSA-DFES | WA3796093 | Engine Room door has failed open | CFRS Armadale- TO BE DECOMMISSIONED Armadale FS-Main Building | GMP-BR | Building | Doors (BU) | Go Doors | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 14:15:00 | Pass | (23/11/2020) - Work NoteFault Found: Attended site as per work request and foundWork Completed:Attended site a found 1x missing roller and 2x bent number 3 hingesWe replaced the roller and hingesWe adjusted the bottom limit so the cables aren't loose when the door is closed this was a new issue because theyweren't loose when we were here last
MSA-DTAG | WA3795297 | L7 office Reports of extreme heat on the floor. | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 12:00:00 | Pass | Travel to site. Investigate lev 7 too hot. Access level 6 BMS. Check temps on level 7 and found to be 23.7 degrees. Check boiler and found to be operating. Change ambient lockout setpoint to inhibit boiler operations. Check floor vav box setpoints and found to be 23 degrees accross floor. Adjust all setpoints to 22.5. Monitor operation and found temps accross floor to decrease. AC is now working ok.
MSA-DTAG | WA3795630 | Registry entry, carpark side - irrigation cover broken now presents as potential trip hazard | Joondalup Courthouse | WSM-BR-SITE | Landscaping & Gardening | Materials (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 09:00:00 | Pass | Call Out & Labour & Reticulation Box
MSA-DTAG | WA3795974 | ground cell 4 Special Clean in Cell 4 – Accused spat on the cell floor | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 19:00:00 | Pass | Ground Cell 4 Special Clean
MSA-DTAG | WA3796023 | L4 Staff toilets- Digilock door issues with door lock - see notes | Central Law Courts | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-26 13:15:00 | Fail | Attended site, viewed lock and will require replacing. Need to re-attend. Date on site: 24/11/2020Time on site: 11:30am - 12:00pmAttended site, fitted new digital lock on level 4 male toilet door.Date on site: 26/11/2020Time on site: 12:15pm - 1:30pm
MSA-DTAG | WA3796062 | ground security office HPWU 1 failed | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-26 12:00:00 | Fail | Return to site and check operation of HPWU, found unit to be running with now faults. Check operation pressures and found to be normal. Possibe cause water back to the exchanger in heating mode.
MSA-DTWD | WA3795181 | D Block, Room B308- Repair boiler unit in kitchen | East Perth Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-20 12:32:00 | Pass | Replaced hot pump on Zip Hydrotap A404211089 .
MSA-DTWD | WA3795232 | Entrance wall has graffiti to be removed | Leederville Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 1 | CLOSE | 20 Nov 2020 | 2020-11-20 17:00:00 | 2020-11-20 09:30:00 | Pass | removal of graffiti from front of campus
MSA-DTWD | WA3795575 | Level 3, 309 - Reglue carpet tiles | Perth Campus B2 | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-01 12:00:00 | Fail | Carpet contractor has visited site and re-glued carpet tiles back down
MSA-DTWD | WA3795619 | E Block, Kitchen E58- Combi oven is showing error code "fan error code" | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-27 15:15:00 | Fail | Completed 27/11/20
MSA-DTWD | WA3795650 | V block ground ladies toilets Ladies toilets the end cubicle has a broken toilet seat | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 12:31:00 | Pass | Had to replace seat fixing kit
MSA-DTWD | WA3795818 | test the Gallagher alarm panel in T Block at on Tuesday 24th November at 1.00pm | Murdoch Campus | GMP-BR | Security | Security Management System (SE) | Total Security Systems Pty Ltd | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 13:45:00 | Pass | 24/11/2020 - Jose Pereira - 1.15pm to 1.45pmTriggered input to test if monitoring are receiving alarms as per Mike Day's request.
MSA-DTWD | WA3795825 | Chalk & Cheese cafe intermittent fault on big white door release button William St | Perth Campus B2 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-23 16:00:00 | Pass | Checked and found that the door release button was faulty. Collected new button from supplier, replaced reales button and tested door function.Confirmed door transactions on site workstation
MSA-DTWD | WA3795831 | D block, 2nd floor room D248 - lights not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 08:00:00 | Pass | Returned to site and replaced tubes to lights
MSA-DTWD | WA3795834 | E block, deli & hallway - lights not working - please attended with WA3795831 | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-23 15:20:00 | Pass | Replaced various lights and components
MSA-DTWD | WA3795838 | Chalk & Cheese cafe rain water leaking into Chalk & Cheese Cafe down grey Pillar | Perth Campus B2 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 20 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-27 08:30:00 | Pass | BRAF decline. close job
MSA-DTWD | WA3795959 | T Block ,G.F, Café rear freezer - Defrost fault flashing on the freezer panel box | Murdoch Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 14:00:00 | Pass | ARRIVED ON SITE AND SIGHNED IN. DEICED UNIT AND RAN THROUGH MANUAL DEFROST. CHECKED DEFROST HEATER, CHECKED DEFROST PARAMETERS, ALL OK. FRIDGE DOOR LEFT OPEN JOB IS NOW COMPLETE
MSA-DTWD | WA3796074 | A block, AG11 ICT Office - Broken/Sticky Lock | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 20 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 13:00:00 | Pass | AG11 Lock not workingLock repaired.
MSA-MRWA | WA3795536 | Kitchen - Hot water system not working, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 20 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-20 11:30:00 | Pass | replaced filter as low percentage - unit needs major repairs is a 2014 unit so recommendation is to replace quoted for both repairs and replacement of unit
MSA-DCA | WA3796113 | Unable to reset A/C3 after power failure | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 21 Nov 2020 | 2020-11-22 08:04:33 | 2020-11-21 12:00:00 | Pass | After hours call out completed
MSA-DCS | WA3796107 | pod control room camera PTZ 5 camera 118 picture is blurry | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Nov 2020 | 2020-11-22 07:05:49 | 2020-11-23 20:17:00 | Fail | PTZ 5 camera 118 blurry image, advice officer on site that camera was already recommended for replacement. Works in progress.
MSA-DCS | WA3796114 | BOILER HOUSE- theres a pit in there that is filling up with water. | Hakea Prison-Sewer pump house, generator, transformers | GMP-BR- HO | Building | Materials (BU) | Boilertronics | 0 | CLOSE | 21 Nov 2020 | 2020-11-21 12:22:27 | 2020-12-09 15:30:00 | Fail | Start at workshop make up enclosure, install din rail and terminals, cut uni strut and gather parts,pack up and travel to site.Sign in complete tooling and parts register. Wait for escort.Set up isolate power, remove old float assembly, make bracket for floats and install glands on bracket install and set float lengths.Mount new enclosure on wall, remove piro from jbox bend up to new box the best possible,install and extend piro cores and terminate into terminals Bell out cores to switch board, wire new floats to enclosure gland and terminate.chech float functions, terminate mcc cores test run and make float adjustments. Return to service.Pack up and house keeping sign out and tooling register.
MSA-DCS | WA3796122 | Gas hot water is leaking into the service duct | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 21 Nov 2020 | 2020-11-21 13:25:58 | 2020-11-21 10:45:00 | Pass | Replaced leaking tap in plumbing duct
MSA-DCS | WA3796157 | Karnet Prison Farm -kitchen dishwasher not working, electrical fault | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 21 Nov 2020 | 2020-11-22 12:44:36 | 2020-11-22 10:30:00 | Pass | 22/11/20Arrive at site to check dishwasher stopped working. Staff explained unit had been stopping and starting and giving off an electrical burning smell. Found cycle control switch shorted out against frame and burning. Replaced and test all ok. Noticed cockroaches in base of dishwasher and over electrics so sprayed base of unit with fly spray and advised staff. Test unit all working well.
MSA-DCS | WA3796165 | telephone P.A system not working in unit 2 | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Nov 2020 | 2020-11-22 13:33:28 | 2020-11-24 09:49:00 | Fail | Contacted site, confirmed local PA system is function correctly (maintained by Seme), phone system PA is maintained by NEC and requires attention. No further action required by Seme.
MSA-DCS | WA3796169 | control room - various cameras offline | West Kimberley Regional Prison | WSM-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Nov 2020 | 2020-11-22 14:31:32 | 2021-05-05 15:06:00 | Fail | Job is complete
MSA-DCS | WA3796170 | GATEHOUSE- Video window monitor 2, is showing up blue on the left hand corner | Roebourne Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-11 09:00:00 | Fail | Checked all indigo systems at gate house and comms room, no fault found at time, indigo and all cameras are up and working at gate house. Advised system may have reset at time job logged but all ok now.
MSA-DCS | WA3796219 | UNIT 8- VESDA FAULT on the FIP | Hakea Prison | GMP-BR- HO | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 22 Nov 2020 | 2020-11-23 08:05:24 | 2020-11-22 10:09:00 | Pass | After hours call to Hakea Prison Unit 8 Vesda fault. Checked unit and found that vesda had been isolated for no know reason causing fault onlocal SIP. De isolated vesda and reset fault on local SIP and left system normal.
MSA-DCS | WA3796224 | BLOCK M-Fire alarm system has failed. | Banksia Hill Detention Centre-Block M Stores | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 22 Nov 2020 | 2020-11-22 13:17:15 | 2020-11-22 10:59:00 | Pass | After hours call to Banksia hill for fire alarm not heard. Panel all normal when arrived. System had multiple devices off line but all showing normal now.Left system normal
MSA-DCS | WA3796259 | Expansion Project UNIT 16- Fire alarm is activated. Multiple areas in unit. | Casuarina Prison-Prisoner Accommodation Unit 14 | WSM-MW-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 22 Nov 2020 | 2020-11-22 18:04:26 | 2020-11-22 18:11:00 | Fail | Found that units exhaust is exiting into roof space and not in the same area as the sample point as this can cause flow problems.Attached picture of page in manual.See section on flow fault errors.4: faults will need to be pushed back to the builder as it possible hasn’t been installed/setup correctly since installed.Or ARA could attend with Ampac to do check system setup.
MSA-DCA | WA3796606 | Front staff carpark - gate not operating, wont shut. | Shipwreck Galleries-Main Building-Ground Floor-Staff Car Park | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-23 17:00:00 | 2020-11-23 10:51:00 | Pass | Found gate had come off of track. Refitted gate and tested all ok at time of test.
MSA-DCA | WA3796744 | North garden - Broken sprinkler | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Materials (PD) | Earth & Water Pty Ltd | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-23 11:15:00 | Pass | Job Summary & Cause of Problem- Arrived on site and immediately found a pop up sprinkler out of the ground.- ran and flushed the middle lawn zone.- replaced the snapped nipple and re used the original sprinkler.
MSA-DCA | WA3796863 | main chiller making a lot of noise not normal noise - see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-BMS Office | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 16:30:00 | Pass | Attended site 23-11-20. Investigation found chiller 2 to have faulted via a loss of phase error. Applied tests and checks to system. Investigation found incoming power correct and no loss of phase present. Contacted Airvison, Airvison to be attending VQ during the week for Annual RM so a PO is not required. Airvison to have attended site. Applied tests and checks. Dismantled mech contactors and cleaned and checked integrity (ok). Reassembled contactors and checked switching (ok). Power cycled chiller and carried out tests and checks to system. System operating correctly with no signs of phase failure faults present.
MSA-DCA | WA3797083 | Cafe, glass bi-folding entry doors bracket is broken, unable to move doors | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor) | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-12-14 11:55:00 | Fail | Repairs have been made to the doors for operation of the doors.On inspection of the doors, there are components that are requiring replacement to minimise further damage and to ensure operation in the future.Protek are awaiting for a quote for replacement and repairs from the Glazier for these works and will submit a quote once received for these repairs.PFM agreed to close off work order
MSA-DCA | WA3797136 | Water fountain, plublic area - blocked | State Library of WA-Main Building-Level 2 | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 15:00:00 | Pass | Cleaned drinking fountain grate and drain
MSA-DCA | WA3969157 | RETROSPECTIVE WORK ORDER- L2 DW issues- Do not attend ref 575573 | Perth Concert Hall | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 14:45:00 | Pass | Job completed
MSA-DCS | WA3796534 | Abattoir - Hot water pressure pumps spray water, leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 07:32:06 | 2020-11-23 15:00:00 | Pass | Job being done under job number wa3742104
MSA-DCS | WA3796549 | unit 4, Lunch room - the air-conditioning unit in staff tea room has no cover & wires are exposed | Casuarina Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 23 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-23 10:00:00 | Pass | Check over aircond found section of the pipe cover missing,pick up new section returned and fitted.
MSA-DCS | WA3796559 | Unit 7, C wing - Prisoners in C Wing report that the hot water is only warm. Please assess. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 07:39:24 | 2020-11-23 09:30:00 | Pass | Nill
MSA-DCS | WA3796568 | Unit 14, A9 - shower pressure really low | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-26 10:30:00 | Fail | tap was dripping so tap was over tightened and rounded the thermospacer, easier to replace tap then track down and order in spare parts
MSA-DCS | WA3796586 | Unit 4, office - staff toilet needs replacing/repairing as its cracked and is getting worse | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-27 15:30:00 | Fail | nil
MSA-DCS | WA3796594 | Unit 3 - hot water system does not heat up on A/C B/D | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 15:30:00 | Pass | nil
MSA-DCS | WA3796610 | Unit 4, Cell A2- Water leaking from vent above mirror | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 13:30:00 | Pass | nil
MSA-DCS | WA3796612 | Unit 14, Cell A13- Toilet button doesnt working, toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 11:30:00 | Pass | nil
MSA-DCS | WA3796615 | Unit 6, B & D - cold tap for kitchen sink faulty, Makes loud hammering noise when in used. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 08:30:00 | Pass | nil
MSA-DCS | WA3796619 | Unit 4, C Wing- Lock for store room is bent | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-23 12:15:00 | Pass | Repair lock and service
MSA-DCS | WA3796631 | Unit 14, B & D Wing, Cells 13 & 14- Fault will not clear or reset "code displays F05." | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-24 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3796640 | UNit 14, Cell C1- Bottom bunk light is faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-23 08:30:00 | Pass | Repaired faulty lights in unit 14 c1
MSA-DCS | WA3796650 | Unit 3, D13 - window cam of hinges (Window is in tack in frame sitting in the unit) | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:12:39 | 2020-11-23 12:30:00 | Pass | SPIRAL BALANCES TO WINDOW REPLACED
MSA-DCS | WA3796661 | INF(10)- Laundry washing machine water will intermitently not turn water off after cycle & will floo | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-08 09:30:00 | Fail | Infirmary 10 Washing Machine faulty. Remove machine for relay. Dismantle, remove faulty water inlet valves & levelling feet. Run all, test with full load. Return to store.
MSA-DCS | WA3796666 | MPU, M19 - Light switch completely ripped off wall, light switch cover hanging off wall | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:18:29 | 2020-11-23 10:30:00 | Pass | Replaced damaged cell light switch and wall box in mpu m19
MSA-DCS | WA3796675 | Unit 10, B wing - water leaking from ceiling | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:20:32 | 2020-11-23 10:42:00 | Pass | Replaced leaking cold water pipe in the roof in unit 10 A/B wing.
MSA-DCS | WA3796683 | Unit 1, Cell D5- Cell call very faint | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:25:38 | 2020-11-23 15:27:00 | Pass | Dismantle the cell call unit and clean, cell call unit was vandalised. Job completed.
MSA-DCS | WA3796685 | Laundry, Dryer # 3 - dryer not working | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:26:35 | 2020-11-27 13:50:00 | Fail | 23/11/20 - 24v Transformer u/s, replacement required. Part to be sourced.27/11/20 - Supply and fit new part
MSA-DCS | WA3796686 | Unit 1 & 2, Control pods- Cell calls not working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:27:50 | 2020-11-27 15:23:00 | Fail | Attended site and repaired multiple cell call issues.Tested all cell call communication and function OK.Tested Voice Recording OK.Job Complete
MSA-DCS | WA3796690 | Unit 2, Cell A15- Sink tap will not turn off, see notes below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:29:47 | 2020-11-23 17:15:00 | Pass | Replaced pillar tap
MSA-DCS | WA3796696 | Unit 3, A7 - Door hinges have dropped and lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:29:59 | 2020-11-24 14:30:00 | Fail | Replace hinges, door plate, lock and weld on strike.Replace worn barrel.
MSA-DCS | WA3796697 | CCU, Cells 1-5- Cell call buttons stuck in | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:33:39 | 2020-11-23 13:54:00 | Pass | Attended site and repaired multiple cell call faults.Tested OK.Job Complete
MSA-DCS | WA3796699 | Unit 1, D11 - Main lock playing up | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:35:53 | 2020-11-23 10:45:00 | Pass | Attend site. Serviced lock and tested. Normal function restored.
MSA-DCS | WA3796709 | Unit 7, B Wing- Shade cloth missing on skylights | Casuarina Prison | GMP-BR- HO | Roofing | Rooflights and Skylights (RF) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2021-02-25 16:37:00 | Fail | new shadecloth installed over skylights
MSA-DCS | WA3796710 | kitchen, Work area - dishwasher keeps tripping power | Melaleuca Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:39:06 | 2020-12-16 15:00:00 | Fail | 23/11/20 - Arrived at site liaise with reception, sign in, walk to location, identify dishwasher, isolate remove panels, test/fault and found 1 of the wash elements is short circuiting to earth and requires replacement, disconnected the faulty element to stop the circuit breaker tripping, further testing found that the wash thermostat is faulty and requires replacement also found that the wash temperature gauge is faulty and requires replacement.1 x Wash Element1 x Rec Temperature Gauge1 x 110 Degree Thermostat16/12/20 - Arrive at site to fit parts, fit and test all ok.
MSA-DCS | WA3796720 | MPU (8), Cell M14- Broken window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:41:52 | 2020-11-24 13:00:00 | Fail | CELL WINDOW RE GLAZED
MSA-DCS | WA3796731 | SEME required to down load CCTV in MPU cell M17. | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 08:47:05 | 2020-11-23 12:48:00 | Pass | Downloaded footage, see security for details
MSA-DCS | WA3796755 | Jasper B08 Smashed Cell window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 13:00:00 | Pass | WELDED AND RE GLAZED WINDOW
MSA-DCS | WA3796799 | Jasper, B wing - Smashed window approximately 1200x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 14:15:00 | Pass | JASPER, B WING WINDOW RE GLAZED
MSA-DCS | WA3796902 | unit 5 rear yard entry pass camera screens are black | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 09:51:57 | 2020-11-24 09:30:00 | Pass | Checked four camera with no picture, no video out from cameras. Power supply to cameras 25.4vac. Power reset cameras, video restored. Checked and confirmed correct operation of IndigoVision system in unit 5.
MSA-DCS | WA3796906 | Main admin tea room- Hot water urn water is running slow | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 09:54:31 | 2020-11-24 10:22:00 | Fail | Unit reported toHave slow flow. On arrivalUnit working fine. Cleaned scale from tap. All ok.
MSA-DCS | WA3796937 | Admin air con no longer working | Banksia Hill Detention Centre | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-11 14:35:00 | Fail | Complete
MSA-DCS | WA3796983 | Karakin, B Wing (kitchen area)- smashed window approx 1200x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 12:30:00 | Pass | WINDOW SASH RE GLAZED
MSA-DCS | WA3797003 | Laundry- Number 2 dryer will not heat up & keeps shutting down | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 10:32:49 | 2020-11-24 09:30:00 | Pass | No ignition. Replaced faulty ignition controller and test OK
MSA-DCS | WA3797039 | Main control room - all cell calls not going to unit all coming to Gate | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 10:49:47 | 2020-11-23 13:00:00 | Pass | Contacted Albany Prison Gate Control. Spoke to officer Ross Boyd who advised that two of four units cell calls were going direct to Gatehouse, not to unit control. I instructed Ross to interrogate Cell call console Where we identified units 2 & 3 were still in “Unattended” mode. Instructed Ross on switching units to “Attended” mode.
MSA-DCS | WA3797111 | Unit 4, PTZ camera 57 in visits does not pan tilt or zoom | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-24 14:30:00 | Pass | Checked programming at Gatehouse Equipment room. Attended PRU, checked supply to camera, tested from Modem rack in PRU and able toPTZ Camera from that location. Returned to Med Gatehouse, traced cable from modem rack to adjacent Encoder rack. Close inspection revealed broken wire in plug termination. Repaired break reconnected and tested.
MSA-DCS | WA3797123 | Maintenance Void Tug CTX470-0850-9812KF,electrical cable to charger needs repair | Casuarina Prison | WSM-MW-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 11:19:43 | 2020-11-23 15:00:00 | Pass | Repaired damaged tug lead and charger in void transport
MSA-DCS | WA3797135 | Boiler house roof space investigate if there is a fire door- see notes | Casuarina Prison | GMP-GR | Building | Fire Door (BU) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2021-05-20 10:00:00 | Fail | NEW FIRE DOOR INSTALLED
MSA-DCS | WA3797178 | Unit 2, D Wing- Rubber flooring is damaged | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-14 13:00:00 | Fail | REPAIRS MADE TO LIFTING RUBBER & MISSING COVING X 2 REPLACED
MSA-DCS | WA3797188 | Unit 2, Cell A5- Bottom Bunk Light switch Mech is broken pushed in | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-30 09:30:00 | Fail | Replaced light switch
MSA-DCS | WA3797204 | Unit 2 A1 Cell Door Jamming in Frame | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-08 09:30:00 | Fail | Carried out repairs to cell door that was jamming
MSA-DCS | WA3797239 | Unit 3 - A Wing cleaning cupboard water leak - see notes | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-08 14:30:00 | Fail | FLASHING REPLACED IN CLEANERS STORE
MSA-DCS | WA3797273 | entry control - security fault between duress alarm transponder in fault Multiplex.26 | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Nov 2020 | 2020-11-23 16:23:23 | 2020-11-23 14:59:00 | Pass | Rectified issue, transponder 6 indicating tamper, repaired and restored alarms.
MSA-DCS | WA3797276 | Unit 13, Cell A8- Possible blown transformer for personal bed LED light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-25 10:00:00 | Pass | Repaired faulty lights in unit 13 a8
MSA-DCS | WA3797277 | MPU (8) - M1 Bed light when on is flickering. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 08:30:00 | Pass | Repaired faulty lights in mpu m1
MSA-DCS | WA3797282 | Abiattors - Broken 3 phase switch | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 12:28:29 | 2020-11-24 11:00:00 | Pass | Investigate and replace broken three phase outlet
MSA-DCS | WA3797315 | Gascoyne Cell B3 toilet constantly running | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-25 10:15:00 | Pass | Service and replaced outlet washer to toilet cistern in cell B3 & A4
MSA-DCS | WA3797326 | Gascoyne Cell B2 Light flashing when turned on | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 10:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3797327 | Work Kitchen, work area - R/H Brat-Pan Thermostat not working | Melaleuca Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2021-02-15 13:30:00 | Fail | 16/12/20Arrive at site to check RHS bratt pan overheating, thermostat is jammed on, also of moisture found in behind controls. Thermostat will need replacing and further testing once replaced to check other functions.Parts required:1 x electronic thermostat kit 1 x high limit Was also asked to look at LHS bratt pan (same model) as not tilting, found top tilt limit switch jamming, oiled and is now working but would recommend replacing as looks worn. Also would recommend to take can of oil to oil other limit switches.Parts required1 x high tilt limit switch06/01/21Arrive at site to fit parts. Fit tilt switch to left hand unit and test all ok.Fit thermostat to right hand unit and test but is intermittently cutting out at inconsistent temperatures, recommend replacing heat probe as seems to be giving false readings or investigating gas valve further. Also ran out of time to fit high limit as staff were starting to use kitchen again so will need to fit this on return.Parts
MSA-DCS | WA3797330 | Admin Foyer Light LHS in admin foyer flickering | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 09:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3797342 | Admin Foyer cleaners store - Vauum cleaner power cord insulation damaged needs repair | Wandoo Rehabilitation Facility | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 08:00:00 | Pass | Cut damaged lead and replaced plug
MSA-DCS | WA3797355 | Jeelia Cell A4 and B3 toilets keep running after filling | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 08:00:00 | Pass | Refitted toilet seat in cell B3 ,checked cell A4 toilet no fault found.
MSA-DCS | WA3797360 | Jeelia Cell A6 shower and sink draining away to slowly | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 08:50:00 | Pass | Cleared blocked shower and basin to cell A6.
MSA-DCS | WA3797434 | SHU (9) - B2 HW tap not working turns without connecting (possibily split pin) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 13:38:34 | 2020-11-25 10:30:00 | Fail | nil
MSA-DCS | WA3797460 | Houses: 1;3;10 & 17- Gas isolation valves have broken handles & cannot be turned off/on | Boronia Pre-release | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2021-02-25 11:15:00 | Fail | Attended site,Supplied and installed new gas isolation valves to houses 1, 3, 10, & 17.Tested works on completion
MSA-DCS | WA3797468 | education campus managers office air con not turning on | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 15:00:00 | Pass | Accessed ac in managers office of education unit not operating. Found unit locked out on comms error. Inspected wiring and both indoor and outdoor boards. Reset lockout. Test ran unit, system running well.
MSA-DCS | WA3797475 | Ground, Conference room - Drawers on the wall next to the door keep opening after being closed | Midland (North East Metro) | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-07 10:30:00 | Fail | Attended site and installed new locks to cabinets locks keyed alike.
MSA-DCS | WA3797487 | SHU (9) - B5 hot water tap in Cell B5 is turning without connecting (possibly split pin) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 14:17:46 | 2020-11-25 09:30:00 | Fail | nil
MSA-DCS | WA3797510 | L1 program room 1 2x legs broken off round conference table | East Perth | WSM-MW-SITE | Furniture | Office Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-27 11:00:00 | Pass | Supplied and installed new adjustable feet to the table legs that had broken.
MSA-DCS | WA3797555 | training room roller door lock jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 12:15:00 | Pass | Attend site. Supplied and fitted 2x Roller Door Anchors and Padlocks as required.
MSA-DCS | WA3797558 | Unit 2 C-D wing laundry Ex-Fan Switch Broken Mech pushed in | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-30 08:30:00 | Fail | Replaced switch mech and plate
MSA-DCS | WA3797607 | PTZ camera 29 on the gate is not working properly | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-11 19:00:00 | Fail | Travel to and from siteJob complete on WA3681497, AMS 707754
MSA-DFES | WA3796898 | G floor, Female toilets- Toilet seat broken | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 10:30:00 | Pass | Replace toilet seat in female ground floor toilet second toilet in from basins . Tested all ok
MSA-DFES | WA3796978 | G Floor, ladies toilets - 7 toilet tiles fallen off wall | CFRS Joondalup | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 14:30:00 | Pass | GROUT
MSA-DFES | WA3796987 | Outside Gym - Torn shade sail | CFRS Joondalup | GMP-BR | Building | External Walls (BU) | AWB Co. | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2021-01-21 14:20:00 | Fail | Torn sail - replace
MSA-DTAG | WA3796931 | Key Wall Safe needs repair/replacing as the keypad no longer works and unable to change the code. | Rockingham Justice Complex | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 11:50:00 | Pass | Attended site, changed combination on safe to make functional, needs replacement.
MSA-DTAG | WA3797056 | Lvl 10,Registry of Births, Deaths & Marriages- Light globe not working, see notes below | Westralia Square | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-24 08:00:00 | Pass | Attended site and signed in at security. Got issued keys at security. Went up to level 10. No access into offices. Awaited staff to allow us in. Located faulty lights. Found 3 x lights in reception faulty. Supply and replaced tubes and starters. Tested all okay. Signed out. Job complete
MSA-DTAG | WA3797528 | Hay Street end, Lvl 5, public toilet- Door closer in male toilet is leaking | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 14:30:00 | Pass | Door closer replaced
MSA-DTAG | WA3797533 | Lvl 8- Door closer in staff corridor between Courts 85 & 84 is leaking | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 12:45:00 | Pass | Door closer replaced
MSA-DTAG | WA3797539 | Lvl 5, Duty Lawyer office entry- Door closer in secure area needs adjusted | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 10:45:00 | Pass | Adjusted door closer
MSA-DTWD | WA3796501 | A block, level 1, Main entry - fault door to main entry A block requiring repairs | East Perth Campus | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 23 Nov 2020 | 2020-11-25 17:00:00 | 2020-12-03 10:20:00 | Fail | 23/11/20 - Inspected door and found door battery back up was faulty, replace 2x 12v 1.2ah batteries and door is working, also found track wheels are heavily damaged and LHS door floor guides is worn, recommended quotation for 4 sets of besam bogies and 1x floor guide (standard type-A) 2x technicians required for this task.3/12/20 - Programmer number A405745280. 1091064. Carried out quoted works and also replaced 2x faulty battery’s, tested door all ok
MSA-DTWD | WA3796624 | M block - aircon in lectures office M002.1 - freezing cold | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 16:00:00 | Pass | Setpoint required to be changed when bms is installed , no mechanical issues found
MSA-DTWD | WA3796667 | E Block, Main hallway and the Baytree deli- Blown globes | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 12:03:00 | Pass | Replaced various lights. Investigated lights humming in c16, found all to have issues lights humming due to old iron core ballast, Barry would like them replaced with LED panels so sent Luke email with details for quote to replace
MSA-DTWD | WA3796814 | L1 Paule Scantlebury store - no power on some power points | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-26 09:29:00 | Pass | Reset RCD for storeroom power . Checked and tested .all fine
MSA-DTWD | WA3796901 | C Block, Toilet isnt working | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-25 07:36:00 | Fail | Found isolation valve to toilet block had been isolated
MSA-DTWD | WA3797002 | F block Rose Garden tap Broken – Water continually flowing | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 13:35:00 | Pass | Repaired broken pipe
MSA-DTWD | WA3797062 | Block 1 ground East end entry auto door.External door lock not working | Thornlie Campus | GMP-BR | Building | Doors (BU) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-23 13:00:00 | Pass | Block 1 east end entry auto door lock faultyLock repaired.
MSA-DTWD | WA3797079 | Block 9 L1 9F3E no lights in office | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 13:30:00 | Pass | Attended site and signed in. Located light fault to be faulty light switch. Found all mechs to be in poor condition. Recommended to replace all mechs. Disconnect and removed faulty switches. Supply and replace with new switches. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3797196 | E Block, E11 Laundry - Split system air con leaking water & emitting odour | Bentley Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 11:30:00 | Pass | Job complete
MSA-DTWD | WA3797305 | M block M016 Ceiling fixing workshop 3 x high bay lights not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-09 14:05:00 | Fail | Repalced lighting to ceiling and roof fixing to LED, used old woekimg lights to swap out in other areas. Job completed
MSA-DTWD | WA3797362 | 6 Cabinetmaking, Room 6D28- Broken power pint | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-23 14:30:00 | Pass | Attended site and signed in. Located cabinet making in block 6. Found gpo in workshop tagged out damaged. Disconnect and removed faulty outlet. Supply and replace with new double gpo. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3797369 | Level 1, LG IT - Fire alarm activated by fault 7:50 21/11/20 (see long Description) | Perth Campus B2 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 09:00:00 | Pass | Callout - attended site & investigated - zone 16 isolated & in alarm. Preaction has "0" pressure - investigated further - air compressor turned off. Turned back on - System repressurized to 550 kpa. Deisolated zone 16. Panel to normal.
MSA-DTWD | WA3797482 | BLD 875 pen Burst Water Pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-23 17:15:00 | Pass | Repair burst water pipes to Piggery pen
MSA-DTWD | WA3797495 | Tower block, level 3, ladies toilets - 2 broken toilets seats | West One Services | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-01 09:40:00 | Fail | COMPLETED
MSA-DTWD | WA3797502 | C Block, Room CG10 workshop- Evap 1 & 2 not working properly, see notes below | Carlisle Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-27 13:30:00 | Fail | Diagnosed ec1 and ec2 at c block. Left site to source parts and to reattend tomorrow to complete repairs.
MSA-DTWD | WA3797563 | C block internal auto door switch is not working properly | Balga Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-24 09:33:00 | Pass | Found that the mode pad wasn’t working, also the loom was damaged, replaced mode pad and loom, tested all ok.No programmed number on the door.
MSA-DTWD | WA3797577 | G23 toilet door unisex has dropped and hard to close | Rockingham Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Nov 2020 | 2020-11-26 17:00:00 | 2021-02-11 15:39:00 | Fail | Client has work completed by another contractor locally.
MSA-MRWA | WA3797441 | Out of hours - possible water damaged, see notes below | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-804-Office | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 23 Nov 2020 | 2020-11-24 17:00:00 | 2020-11-24 07:00:00 | Pass | Repalced faulty tombstone and fluros to light lvl8. Cleaned marks off cover also.job completed
MSA-MRWA | WA3797603 | Investigate air handling unit fault | Don Aitken Centre MRWA Head Office-Main Building-First Floor-AHU Room-South | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 23 Nov 2020 | 2020-11-23 22:23:08 | 2020-11-23 20:30:00 | Pass | Attended site for PO after-hours call out. L1 AHU system to have triggered a fault via the BMS system. Applied tests and checks, investigation found VSD to not be in fault for AHU & current schedule showing plant to not be operational due to time click schedule. Investigation found a BMS mis match fault present with mechanical plant to be ok. Reset fault and left site.
MSA-DCA | WA3797960 | L1 admin AC temperature is very hot, fault light on AC unit - see notes | Collection and Research Centre Welshpool-Administration and Library Building-Roof Level-Rooftop Plant - Above Administration | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 12:00:00 | Pass | Attended site. Lv1 admin eastern side AC system in fault. Applied tests and checks to find system faulting on an A4 error code. Investigation found system locked out on HP safety. Carried out tests and checks. Investigation found HP pressure transducer not reading correctly (disparity in resistance/ohms ambient temo comparison). Removed transducer cleaned plug with contact cleaner and applied fresh silicone grease. Tested operation of system. System operating correctly with no HP faults present. Removed and cleaned remaining LP transducer and EXV transducers. Applied new silicone gel. System operating correctly.
MSA-DCA | WA3798409 | sprinkler coverage to be investigated on the new lawn | Perth Cultural Centre Precinct - Museum Plaza (James Street) | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 13:15:00 | Pass | Lawn irrigation is working perfectly.Problem could be initial watering before the new lawn was installed. The dry patches in some cases have not put any rootsdown and the piles are quiet thin 25mm. This would also contribute to drying out very quickly. All other lawn piles (green areas)have taken with root
MSA-DCA | WA3798564 | zone 5 smoke alarm fault alarm on the panel | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Mechanical Plant Room | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 07:30:00 | Pass | Attended site and found panel locked up with Level one reference detector Az 5 in alarm isolated.Also found Az 5 Reference detector isolated but normal.Reset and left normal.
MSA-DCS | WA3797787 | Kitchen - Middle bell not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 07:15:46 | 2020-11-24 14:25:00 | Pass | Replaced broken on/off switch, test ok.
MSA-DCS | WA3797792 | Unit 6, C wing - Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 12:30:00 | Pass | Repaired lights
MSA-DCS | WA3797795 | Unit 6, Lobby outside control room - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 09:30:00 | Pass | Repaired light
MSA-DCS | WA3797804 | ISU, D wing - Aircon leaking from roof | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 24 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 10:00:00 | Pass | Complete
MSA-DCS | WA3797808 | Unit 13, control rooms - Cell call alarms have not stopped since 0600hrs today | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 07:34:17 | 2020-11-24 10:30:00 | Pass | COMPLETED
MSA-DCS | WA3797836 | Master control room - Perimeter fault, Microwave D4 and Peritrack F3 in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Nov 2020 | 2020-11-24 11:58:09 | 2021-02-23 15:59:00 | Fail | Investigated fault on old Senstar system. Repaired faults with Sennet Module and sensors. Tested perimeter zones OK.Job Complete
MSA-DCS | WA3797841 | Kitchen - Number 2 oven saying "reset gas" | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 08:06:56 | 2020-12-09 15:10:00 | Fail | Replaced required parts to oven and tested ok.
MSA-DCS | WA3797843 | SHU, West - There is no Power in the West side cells of the West wing. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 08:06:39 | 2020-11-25 12:00:00 | Fail | Attended SHU, unable to gain access to wing. Returned and restored power to west wing
MSA-DCS | WA3797851 | Fault to lighting circuits at Gwynlea Building | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-24 16:00:00 | Pass | Traced out faults on security lights found lights needed re-wiring, sourced parts when returned to re-wire found there to be 6 lights not 4 as originally traced
MSA-DCS | WA3797852 | Unit 7, Shade cloth over B wing - Appears to have blown off to 1 side by high winds, possibly ripped | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 12:00:00 | Pass | THIS JOB IS A DOUBLE UP OF #WA3796709
MSA-DCS | WA3797855 | Unit 2, B2 - bedside light faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-30 09:00:00 | Fail | Replaced bed light
MSA-DCS | WA3797862 | Unit 2, D7 - cell call light not working | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 09:43:00 | Pass | Unit 2 cell call led remounted, checked led operating correctly, led is slightly recessed. Cell call tested operational.
MSA-DCS | WA3797896 | Gardens, main water tank outside prison - tank not filling | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 08:40:42 | 2020-12-01 10:00:00 | Fail | change 7 level probes in tanks
MSA-DCS | WA3797904 | Unit 2, Cell C13 - New cistern required parts not available for old cistern | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-04 14:26:00 | Fail | Replaced broken outlet mechanism
MSA-DCS | WA3797916 | Unit 2, Staff Lunch Room- Rear Exit Door Lock Jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 24 Nov 2020 | 2020-11-24 12:58:06 | 2020-11-24 11:30:00 | Pass | Attend site. Inspected/serviced rear door lock - appeared fine. Tested lock with all available unit keys and lockdown key (8 in total) and all worked normally. Suspect that issue is with another users key.
MSA-DCS | WA3797951 | Unit 5, A/C common room door latch isnt catching sometimes, see notes below | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-27 10:36:00 | Pass | Lock bouncing out and not locking, dismantle and calibrate. Tested working, job completed
MSA-DCS | WA3797955 | control internal MW zone 7 not activation | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 10:00:00 | Pass | Checked events log, fault with Perimitrax not microwave. Ran plot graph and walk tested zone. Reset module in Obs post 3. Calibrated zone. Perimitrax and microwave tested ok.
MSA-DCS | WA3797961 | A Wing scenario training room- Computer for PDA not working.No signal on monitor. | Nyandi Training Academy | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-27 16:00:00 | Pass | Installed new PC tested fully operational. No further action required
MSA-DCS | WA3797968 | gate house lobby door electronic opener faulty | Broome Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 09:29:33 | 2020-12-05 16:00:00 | Fail | Replaced buzzer for door and tested operation. All in working order now.
MSA-DCS | WA3798018 | Gatehouse - Door handle broken going into keywatcher room | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-27 08:45:00 | Pass | On site. Replaced failed door furniture to restore normal function.
MSA-DCS | WA3798043 | Kitchen - A side dinning room aircon not working | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 10:24:51 | 2021-01-18 11:38:00 | Fail | COMPLETED
MSA-DCS | WA3798045 | Unit 1, Ablution Pod 7 - ceiling fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 15:00:00 | Pass | Replaced exhaust fan
MSA-DCS | WA3798048 | Unit 2, C - ablution pod near cell 30 - broken glass window | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 10:27:52 | 2020-11-30 12:15:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3798091 | ISU B wing Harding air con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-01 12:30:00 | Fail | Complete
MSA-DCS | WA3798096 | ISU, B Wing (Harding), Cell D09- Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 08:30:00 | Pass | Investigate and replace isu d9 light switch
MSA-DCS | WA3798097 | ISU, B Wing (Harding), kitchen- Exhaust fan not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-01 10:30:00 | Fail | Replaced ex fan
MSA-DCS | WA3798099 | ISU Harding cleaning store room light not working (burnt ballast) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-01 12:00:00 | Fail | Replaced light
MSA-DCS | WA3798111 | Unit 5, A2 - Tap may needs replacement as can’t turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 24 Nov 2020 | 2020-11-24 14:55:14 | 2020-11-24 13:20:00 | Pass | Replaced pillar tap to basin.
MSA-DCS | WA3798118 | Unit 13 - Control Room Handset damaged on PDA/ | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 11:07:33 | 2020-11-24 14:45:00 | Pass | Replaced faulty cell call handset and test functions,ok and back to normal operations. Job completed.
MSA-DCS | WA3798135 | MPU (8), Shower Block - shower between M2 and M3 when cold water tap turned no water comes out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 12:31:00 | Pass | nil
MSA-DCS | WA3798141 | Bakery, Blade broken on bun rounder | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-02 11:20:00 | Fail | 27/11/2020Check unit Found blade broken Attempt to weld on site but advised unable to work past 3pm as site closes down.2/12/2020Reassemble unit Exposed blades Repair bent blade Clean unit Weld blade in place Wear part in and make sure blade is flush Test unit mechanically, ok. Requires moving back into prison Left in stores
MSA-DCS | WA3798142 | SHU (9) - Control Room cameral 143 faulty | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 11:18:09 | 2020-11-24 16:40:00 | Pass | Video lost trace fault and fixed. Job completed.
MSA-DCS | WA3798143 | MPU(8), Day Room- Aerial socket does not hold lead | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 10:30:00 | Pass | Attended site. Checked MPU 8 Dayroom TV point, found damaged. Replaced TV wall plate 8, TV point. Tested signal,OK.Job completed.
MSA-DCS | WA3798266 | main fridge high temp at 10 deg C | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 12:57:55 | 2020-11-26 13:48:00 | Fail | Replaced the TX valve Na drier and charged the refrigerant, checked found OK.
MSA-DCS | WA3798297 | Unit 1,, Cell C16- Inspection window broken in cell door | Hakea Prison | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-30 16:45:00 | Fail | window re glazed REPLACED SLIDING MECHANISM
MSA-DCS | WA3798300 | Unit 1, Cell B8- Sink waste grate missing, see notes below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-12-11 10:40:00 | Fail | Replaced broken waste
MSA-DCS | WA3798302 | Canteen - commercial type fridge not coming down to tempature | Bandyup Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 15:00:00 | Pass | See work logs
MSA-DCS | WA3798316 | Unit 1, Cell B2 - Toilet cistern faulty & toilet part blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 13:22:23 | 2020-11-24 15:45:00 | Pass | Service toilet cistern and cleared blockage to toilet pan.
MSA-DCS | WA3798394 | MPU(8), Cell M11- window has shattered. | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 14:21:31 | 2020-11-24 19:25:00 | Pass | CELL WINDOW RE GLAZED & repaired
MSA-DCS | WA3798395 | ISU A wing Harding Cell A06 fault top power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 10:00:00 | Pass | Investigate and replace isu a6 broken gpo
MSA-DCS | WA3798397 | Kitchen, Rational Combi Oven - abort on cleaning cycle. Showing code SERVICE10 | Boronia Pre-release | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-25 14:00:00 | Pass | Clear flush pump of scale piece. Test pump flushing ok. Reset error, reset oven. No Further errors on screen.
MSA-DCS | WA3798431 | Staff vehicle entry Pot hole on staff car park entry | Walcott Centre (Central West Metro ) | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 13:30:00 | Pass | 26/11/20pot holes filled and repaired
MSA-DCS | WA3798460 | Fan noisy on outdoor unit. Refer to Raj for details | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-25 13:15:00 | Pass | Replaced the condenser fan motor assembly.
MSA-DCS | WA3798492 | Unit 17 - C Wing Personal lock Cell C09 stuck inside lock latch, unable to use at all. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 11:00:00 | Pass | Require parts.Replace mortise lock and adjust strike lip.
MSA-DCS | WA3798571 | unit 17 lobby fire panel continuously faulting, - see notes | Casuarina Prison | WSM-MW-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 15:53:31 | 2020-11-24 17:52:00 | Pass | COMPLETED
MSA-DCS | WA3798572 | Download Footage- see notes below | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-25 14:11:00 | Pass | Unable to obtain for ty age as NVR has a current storage capacity of 37 days.
MSA-DFES | WA3798378 | Station officers room to bathroom - Fire Door holding magnet is faulty & requires repair/replacemen | CFRS Duncraig | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-30 13:30:00 | Fail | Fire Door had faulty magnet. Attended site to verify what type of magnet required. Collected new magnet and installed.
MSA-DFES | WA3798578 | out the back of workshop air conpressor | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 09:45:00 | Pass | Arrived on site at 9:20 to inspect air compressor. Spoke to staff and inspected compressor found that the air compressor was reaching its air limit switch max and then stopping itself from operating. Staff would then come and restart. Informed admin and staff and they will have air compressor technician come out to adjust the max limit level. Signed out at 9:43
MSA-DFES | WA3798584 | L1 data centre comsen needs electrician on site for connection of new hardware | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 12:00:00 | Pass | Monitored power when energising new servers to ensure no power loss to COMSEN
MSA-DTAG | WA3797840 | Ground - Metal exit sign on handrail is loose, adjacent to scanning machines | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 24 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 11:15:00 | Pass | RE-POSITIONED AND SECURED SIGNANGE
MSA-DTAG | WA3798216 | L 7 and 11 whole floor areas Air-conditioning does not appear to be working correctly - see notes | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 16:00:00 | Pass | Attend site. Investigate AC lev 7 and 11 too warm. Access BMS and check floor temps. Found temps to range from 23 in the interior to 25 at the perimeter. Found perimeter boxes to be at 100% cooling. Check AHU supply air temp and found to be 14 degrees. Adjust supply air low limit to to 11 degrees. Found chilled water valve to open. Found supply air to now drop to 12 degrees. Monitor temps on floors and found to start dropping. Will recheck temps next maintenance.
MSA-DTAG | WA3798559 | Lvl 3- Toilet is blocked in the female staff toile tin the JSO area. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-25 10:15:00 | Pass | Complete
MSA-DTAG | WA3798562 | ground male public toilet Soap dispenser in bathroom needs to be re-attached to wall | Perth Children's Court | WSM-BR-SITE | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-03 08:45:00 | Fail | New Soap dispenser fitted
MSA-DTAG | WA3798586 | ground Require a BIO clean for cell 4 as a Person in Custody has golden staff | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 20:30:00 | Pass | Job carried out as per WO.
MSA-DTWD | WA3797767 | front main car park - Gas smell possible leak due to a vehicle incident in the c/park | Murdoch Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 24 Nov 2020 | 2020-11-24 17:00:00 | 2021-01-31 16:00:00 | Fail | Carried out repairs necessary for sound test and ATCO meter reconnection
MSA-DTWD | WA3797839 | C block. C208 & C212. Several horizontal blinds require refixing & repair | Joondalup Kendrew Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2021-01-13 14:30:00 | Fail | completed & Invoiced
MSA-DTWD | WA3797901 | BLD 875, Piggery Pens- Copper water pipe leaks | Muresk Institute | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Lane's Plumbing | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-25 17:30:00 | Pass | job completed - Repairs to water leaks at Piggery
MSA-DTWD | WA3798030 | T block Range hood in the Café does not seem to be working correctly. | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 12:00:00 | Pass | Reterminated motor terminals and repaired damaged cable
MSA-DTWD | WA3798123 | U Block- Evap cooler eastside of U010 is not working. | Balga Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Precise Air Group | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 09:00:00 | Pass | Accessed site completed relevant sign in procedures, gained access to roof , found evaporative blower motor to be isolated , checked over unit operation after reinstating power, all working fine
MSA-DTWD | WA3798281 | Ground, C block, Admin - FESA Red Box showing Fault and beeping | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 14:16:00 | Pass | Call out to investigate fault in code red box, Reset fire panel all good needs new batteries:COMPLETEDPLEASE NOTE: DAS WAS SUBMITTED 29/07/2020 FOR NEW BATTERIES which has not yet been approved.
MSA-DTWD | WA3798339 | D block kitchen D3 cold filter water tap isolation broken | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 16:15:00 | Pass | Fix leaking taps and replace ministop
MSA-DTWD | WA3798384 | B112 media store aircon is leaking brown oily liquid | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2021-03-16 12:00:00 | Fail | Found the high wall split dripping water. Removed the covers cleaned the coil , restarted and test ran found the drain pan cracked and needs replacing. Unit is on R22 and is decaying and rusting, recommend it be replaced as parts are no longer available. Quote being submitted.
MSA-DTWD | WA3798396 | F block. external tap at the Eco Playgroup leaking. requires replacing like for like | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-25 12:29:00 | Pass | Replaced outside garden tap, could not find isolation so had to do live
MSA-DTWD | WA3798567 | Block B lift fault on 3rd floor up arrow is not working | Bentley Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | SSP | 24 Nov 2020 | 2020-11-25 17:00:00 |  | Overdue
MSA-DTWD | WA3798592 | flooding and blocked toilet | Muresk Institute-Unit 801 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 0 | CLOSE | 24 Nov 2020 | 2020-11-24 22:54:29 | 2020-11-24 20:50:00 | Pass | job completed - to clear blockage to sewer line
MSA-MRWA | WA3798033 | Safety shower eye wash alarm for asphalt lab has alarm only, see notes below | Materials Engineering Branch-Asphalt Lab-Ground Floor | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 24 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-24 13:30:00 | Pass | 24/11/20 - Dylan Parslow, Joshua ParkTested audio files on SD card, audio files ok.Tested shower alarm activation. Audio message working on activation.Advised on how to test message device in audio rack.
MSA-MRWA | WA3798234 | Cistern not flushing, water continually flowing, please investigate and remediate | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor-A7.0-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Nov 2020 | 2020-11-25 17:00:00 | 2020-11-24 15:50:00 | Pass | Damaged cistern needs replacing
MSA-DCS | WA3798786 | Potable water chlorine plants - not dosing chlorine | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | TRILITY Solutions Pty Ltd | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 07:09:33 | 2020-11-27 16:17:00 | Fail | System now operational
MSA-DCS | WA3798791 | Gatehouse - Tamper alarm in fence in fault wont reset | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Nov 2020 | 2020-11-25 11:13:56 | 2020-11-25 13:10:00 | Fail | Investigated tamper fault. Repaired faulty tamper switch on perimeter cabinet door.Tested OK.Job Complete
MSA-DCS | WA3798794 | Gatehouse - zone 10 camera 1 - is down, will not record, showing blank screen | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Nov 2020 | 2020-11-25 11:18:29 | 2020-11-25 13:09:00 | Fail | Investigated perimeter camera fault and traced to Power Supply Unit.Installed replacement PSU and tested OK.Job CompleteParts (SEME Stock):Power Supply Module
MSA-DCS | WA3798799 | Gatehouse - Duress system - wont acknowledge code to reset | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Nov 2020 | 2020-11-25 11:19:49 | 2020-11-25 13:11:00 | Fail | Attended site, investigated and found wireless keyboard and mouse have poor RF data communication link causing intermittent keystrokes to be missed while typing password.Modified KVM configuration and installed wired keyboard and mouse on duress computer in control room.Tested OK.Job CompleteParts (SEME Stock):Keyboard and Mouse
MSA-DCS | WA3798810 | education decking boards broken and flexing require repairs | Karnet Prison Farm | GMP-BR- HO | Flooring | Timber (FL) | Midolo Building Services | 3 | CLOSE | 25 Nov 2020 | 2020-12-01 17:00:00 | 2021-01-04 14:00:00 | Fail | NEW DECKING INSTALLED TO AREA
MSA-DCS | WA3798813 | Master control, Perimeter PTZ cameras 2 & 3 no picture | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Nov 2020 | 2020-11-25 11:36:21 | 2020-11-25 15:30:00 | Fail | Attended Equipment cabinets associated with two PRZ cameras. PTZ 2 Camera noted no lights on modem, rested fibre modem and video restored. Attended PT3 Equip Cabinet. No video from camera at Cabinet, confirmed power output from cabinet power supply. NOTE: PTZ 3 is inside a building site. Referred Fault to SO Matt Crocker for referral to construction techs. Advised by Mr Crocker Fault fixed damaged cable on site, confirmed service restored with control.
MSA-DCS | WA3798841 | Unit 7, A5 - windows will not stay up,Internal mechanisms (strut thingies) have stretched | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-30 10:00:00 | Pass | RE NEWED SPIRAL BALANCES
MSA-DCS | WA3798845 | Unit 13, A Wing, Cell A7- Sink is slow to drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-25 13:30:00 | Pass | nil
MSA-DCS | WA3798851 | Unit 7, D Wing Kitchen- cabinets & tops are damaged | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2021-05-26 11:57:00 | Fail | LABOUR/INSPECTION ONLY - ADVISED TO CLOSE OFF COST TO DATE
MSA-DCS | WA3798853 | Hotham office - tap is constantly running | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-25 11:25:00 | Pass | Service and rewasher basin taps
MSA-DCS | WA3798942 | Unit 6, B Wing shower - Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-25 11:00:00 | Pass | Repaired lights
MSA-DCS | WA3798986 | Kitchen- deep fryer not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-30 14:30:00 | Pass | 30/11/20Attended kitchen Issue - Deep Fryer not working.Found water had been sprayed underneath fryer, Causing electrics to short out and some corrosion on connections. Was able to dry out and cleaned electrical connections.
MSA-DCS | WA3799022 | Kitchen - 2 robot coupe falling off | Wooroloo Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 09:53:56 | 2020-12-08 12:00:00 | Fail | Kitchen 2 x CL50 Robo Coupes damaged. Pick up the 2 x slicers take to Agent. Open machines, replaced faulty parts. Return to kitchen. Awaiting parts for 2nd machine. Repair second machine, return 2nd machine to kitchen.
MSA-DCS | WA3799107 | NVR 5 Disk 3 failure | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 10:32:05 | 2020-11-26 13:34:00 | Fail | Raid failed, replaced 3x hard drives to bring NVR back onlineHard drives from PFM stock
MSA-DCS | WA3799175 | unit 1 block 6 kitchen exhaust fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-27 17:30:00 | Pass | Replaced exhaust fan
MSA-DCS | WA3799188 | Karakin, C02 - Toilet solenoid leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-26 08:25:00 | Pass | Replaced solenoid and adjusted pipework to suit
MSA-DCS | WA3799204 | Lost all camera control after power reset | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Nov 2020 | 2020-11-25 15:21:37 | 2020-11-27 15:25:00 | Fail | Multiple faults caused by generator testing while UPS was out of order. This caused power spikes and fluctuations through all Security equipment and computer servers. Investigated and repaired multiple faults on gatehouse servers, network switches, cell call system, duress system, CCTV systems, Door control Systems and Keywatcher.Repaired all faults and tested OK.Job Complete
MSA-DCS | WA3799218 | North/ West perimeter gate not working (BSD variable speed drive requiring replacing) | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | AFD Contracting | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 09:30:00 | 2020-11-25 13:00:00 | Pass | 25/11/20Replace VSD and adjust gate motor
MSA-DCS | WA3799250 | Unit 14, Cell D08- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-26 12:30:00 | Pass | nil
MSA-DCS | WA3799254 | Visits workstation is offline, no video signal | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-04 16:00:00 | Fail | Installed new W/s Supplied by PFM in Security office. Decommissioned old W/s and reconfigured network to access new system. Trained officers on operation.Complete.Installed new W/s Supplied by PFM in visits;Supplied and installed:1 x SFP module1 x Planet Media Converter2 x HDMI leads2 x fibre patch leads1 x Cat 6 patch leadConfigured and confirmed correct functionalityWorks complete
MSA-DCS | WA3799302 | Reception - 14x ceiling lights faulty - need to be replaced with LEDs | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 15:00:00 | Pass | Replaced 8x old style lights with LEDs
MSA-DCS | WA3799303 | Maintenance work shop - light tubes & igniters broken needing replacement | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 17:00:00 | Pass | Replaced various tubes and starters in maintenance
MSA-DCS | WA3799329 | Unit 14 - A9 shower pressure really low | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-26 11:30:00 | Pass | nil
MSA-DCS | WA3799348 | Unit 3, House 2 ,Cell 4 - cell call not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-26 13:34:00 | Pass | cell call had ben damaged,replaced with CI-CC from PFM stock
MSA-DCS | WA3799368 | Unit 1, Plumbing duct for Cell B18- steel IO lid is leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 13:33:17 | 2020-11-25 15:45:00 | Pass | Attended site,Access unit 1, cell b18 service duct. Remove and reseal inspection opening to sewer line to repair leak.
MSA-DCS | WA3799393 | Education, Admin office - AC pump blown | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 13:51:53 | 2020-11-26 12:30:00 | Pass | See work logs
MSA-DCS | WA3799405 | Unit 10, Cell C14- Main light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 11:00:00 | Pass | Repaired cell light
MSA-DCS | WA3799408 | Unit 6, B Wing Dayroom- Hot water tap leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-05 12:31:00 | Fail | Checked and tested hot water tap no fault found.
MSA-DCS | WA3799409 | Unit 6, A Wing Shower Block- Hand Basin Leaking, split pipe. Nearest to shower cubicle | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-03 15:00:00 | Fail | Replaced spout and fixed leaking fitting
MSA-DCS | WA3799422 | Unit 4, L Block- External garden tap & piping leaking, connection to tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-25 16:24:00 | Pass | Attended site,Supply and install new half inch brass T piece to bore line hose tap as existing had perished. Tested work on completion
MSA-DCS | WA3799443 | Unit 3 - C12 window does not opperate correctly | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-30 13:15:00 | Pass | RE NEWED SPIRAL BALANCES & REPAIRED FRAME
MSA-DCS | WA3799447 | Edvoc 2 class 5- Light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-02 13:00:00 | Pass | Replaced faulty lights
MSA-DCS | WA3799450 | Unit 13 - Plant-Room alarm in Rheem box going off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2021-05-04 12:30:00 | Fail | Work planner for 18/3, due to unit being vacated because of the new build we are unable to acces without an escort , request sent on 17/3 now waiting on a date to be booked in
MSA-DFES | WA3799211 | Lvl 1, Special Operations (Open Plan Office)- Fluro light not working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-02 09:00:00 | Pass | CompleteAttended site and replaced faulty fluros all in working order
MSA-DFES | WA3799265 | Damaged u bend on sink area 52 | CFRS Perth | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-02 13:30:00 | Pass | Investigate damages trap under sink located Area 51Remove trap, supply and install new 50mm s+p trap Test for leaks , pack up and clean up worksite
MSA-DFES | WA3799335 | Change Room 2, Towel rail is broken & on the floor | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-01 10:30:00 | Pass | Towel rail was reattached to wall
MSA-DFES | WA3799343 | Ground floor, engine room door - Door number 8 not operating properly, slow to open and close. | CFRS Perth | GMP-BR | Building | Doors (BU) | Anvil Doors | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-27 09:55:00 | Pass | ATTENDED PERTH FS. BI FOLD DOOR NUMBER 8 WAS OPERATING SLOWLY AS THE CLUTCH WAS SLIPPING ON THE MOTOR UNIT. THE CLUTCH UNIT WAS READJUSTED AND THE MOTOR UNIT AND DOOR WAS THEN FUNCTIONING CORRECTLY AGAIN. THE DOOR IS NOW OPERATING AT NORMAL SPEED.
MSA-DFES | WA3799364 | Admin, Reception- Air Con is not working & showing error code UF | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-26 11:30:00 | Pass | Investigated AC 18. No cause evident for error. Reset unit. Unit running.
MSA-DFES | WA3799903 | Kitchen - Zip hot water urn is not working | DFES - SWORD - State Wide Operational Response Div | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 11:01:00 | Pass | Replaced plv and inlet solenoid A404214329 Billi Eco
MSA-DTAG | WA3798864 | keypad for Hearing Room 2.07, door next to room 211- is not operating correcty, see notes below | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-25 10:30:00 | Pass | Attended site. Investigated keypad fault at Door 2.06 next to Room 2.11. Resecured Keypad and checked operation.Multiple tests conducted, all working okay.Job completed
MSA-DTAG | WA3799116 | Water isn't draining correctly in the water fountain in Cell 5 | Rockingham Justice Complex | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-26 15:50:00 | Pass | Cleaned p trap and checked unit drainage all ok. After clean dodnoperate better but still not great. Any further drainage issues will require a plumber and cleaned from unit to as far as the trap.
MSA-DTAG | WA3799147 | Interview room 1 call buzzer and light in control room does not light up | Rockingham Justice Complex | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-27 09:42:00 | Pass | Found wiring loose in back of panel, re wire, power cycle and re test, all ok
MSA-DTAG | WA3799417 | holding cells holes and paint peeling off causing walls to flake | Joondalup Courthouse | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-18 08:00:00 | Fail | HOLES IN CELL WALLS PATCHED
MSA-DTAG | WA3799434 | Custody holding cell - camera's have been scratched altering footage being recorded | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Total Security Systems Pty Ltd | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 17:00:00 | 2020-12-17 08:00:00 | Fail | Description of Service Provided:26/11/2020 - Tahni Macara - 2pm to 3pm Replaced scratched cell camera lenses and cover with a second hand camera lense and cover. The replacement lense has small scuff mark on it which impairs the cameras vision but it is an improvement on what it was prior. Will see what availability our supplier has for a replacement.Approved via BRAF to get a replacement camera as it is 3 to 4 month wait for a replacement cover.17/12/2020 - Jose Pereira - 7am to 8amReplaced the cover for cell 2 camera and left camera with site as they now have a spare camera on site.
MSA-DTAG | WA3800181 | front entry door has been kicked and cracked also come off hinges - see notes | Joondalup Courthouse | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 09:23:00 | Pass | Door had been vandalised and had a broken floor guide. Replaced the guide and re aligned both door leaves. Tested all good
MSA-DTAG | WA3800191 | L8 court 85 Flickering light in Court 85 please attend before court starts at 10am | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 25 Nov 2020 | 2020-11-26 17:00:00 | 2020-11-26 10:30:00 | Pass | Job complete
MSA-DTWD | WA3799023 | Bike locker pigeons nesting require bird spikes | Perth Campus B4 | GMP-BR | Building | General Building (BU) | AWB Co. | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2021-01-14 11:30:00 | Fail | PIGEON/BIRD MANAGEMENT SOLUTION INSTALLED
MSA-DTWD | WA3799202 | House 18 - Faulty Gas HWS | Muresk Institute | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Lane's Plumbing | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-26 12:00:00 | Pass | Check hws to House 18 not repairable. Supply and install new hws
MSA-DTWD | WA3799260 | H Block, Canteen- Kitchen drain is blocked | Balga Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-26 13:25:00 | Pass | Cleared blockages using jetter
MSA-DTWD | WA3799300 | Male toilet Light broken, not working - Photo to follow in email | Marine Vessel Centre | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-30 12:45:00 | Pass | Attended site and could not get access. Went over to maritime tafe and signed in. Picked up keys from maritime. Returned to vessel centre. Located male toilets and found light not working. Could not get exact same light. Disconnect and removed faulty light. Supply and replace with new led oyster. Tested all okay. Job complete
MSA-DTWD | WA3799386 | Admin, 1st Floor- Damaged man hole, see notes below | West One Services | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 13:15:00 | Pass | Repair man hole and fix carpet
MSA-DTWD | WA3799396 | Block 8, Room 8G36- Water leak above lecturers’ desk | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-26 15:15:00 | Pass | Seal around overflow pipe in box gutter and surrounding flashing
MSA-DTWD | WA3800131 | F Block, Cooling Tower - Fan VSD in fault 2x days in a row, see note belows | Carlisle Campus | GMP-BR | Air Conditioning | Cooling Tower (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 25 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-27 13:30:00 | Pass | Reattended Monday for further investigation to find no active faults. all ok. close down job. after rest VSD working fine
MSA-DCA | WA3810522 | close to neighbouring Dept of Mines building large hole cut into fence - see notes | State Archives Repository Dianella-Main Building-External Area | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-27 09:00:00 | Pass | Replaced damaged cyclone fence panel in front boundary fence line
MSA-DCA | WA3810530 | External front tap - Dripping tap, most likely needs a new washer. Please inspect and repair | State Archives Repository Dianella-Main Building-External Area | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 10:52:00 | Pass | Replace leaking and corroded tap
MSA-DCA | WA3810536 | Unisex toilets - Toilet is blocking up. Please inspect and repair | State Archives Repository Dianella-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 10:30:00 | Pass | Unblcoked sewer line full of roots(between tpilet and vent). Cut the vent to make the camera fit
MSA-DCA | WA3810552 | Wet lab fume hood alarm is off, Airflow & GPO/gas are off on the panel - see notes | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-P.02 - Fume Extraction | GMP-BR | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 12:30:00 | Pass | Attended site. Wet store laboratory fume hood in fault. Applied tests and checks to find fume hood not in fault. Carried out shutdown operation (ok) reinstated fume hood and tested active operation (ok). Checked online extraction fan and vsd (ok). System operating correctly with no faults present.
MSA-DCS | WA3804238 | ISU unit - All the monitors are frozen from yesterday | Banksia Hill Detention Centre | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Nov 2020 | 2020-11-26 09:46:37 | 2020-11-26 08:29:00 | Pass | CCTV monitor failure, rectified and fixed. Job completed.
MSA-DCS | WA3806022 | Level 2, Ladies toilet - toilet water keeps running | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 07:37:00 | Pass | Replaced inlet valve and Flexi hose out of van stock
MSA-DCS | WA3806503 | unit 1, B8 - copper water pipe to sink cracked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Nov 2020 | 2020-11-30 17:00:00 | 2020-12-10 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3806528 | front gate, Control pod - 1 of multiple group alarm monitors has been lost | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 26 Nov 2020 | 2020-11-26 11:47:20 | 2020-11-26 10:30:00 | Pass | Attended site. Restored Gatehouse Control Room CCTV screen of Visits & Perimeter.Job completed
MSA-DCS | WA3806556 | MPU(8), Cell M18- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 08:07:41 | 2020-11-26 13:30:00 | Pass | Nill
MSA-DCS | WA3806707 | Unit 6, A4 - Water dripping from pipe under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-04 15:20:00 | Fail | Rewashed tap and replaced nut
MSA-DCS | WA3807188 | Cool room out the back loading dock - Coving damaged around bottom edge of the room | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2021-03-29 14:30:00 | Fail | Repairs.completed by sub contractors
MSA-DCS | WA3807508 | Metal workshop - Workshop machine metal cabling damaged | Hakea Prison | GMP-BR- HO | Equipment | Power Tools (EQ) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 08:23:40 | 2020-12-03 14:30:00 | Fail | Repaired foot pedal
MSA-DCS | WA3807577 | Kitchen, Prisoner day room - Water cooler tap faulty | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-03 09:40:00 | Fail | Cleared blocked drain
MSA-DCS | WA3808244 | Unit 14, A5 - shower is blocked - plunger has not worked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 14:30:00 | Pass | Nill
MSA-DCS | WA3810537 | INF(10) Day Room- Rubber strip in dayroom coming up, see notes below | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 09:00:00 | Pass | NO EVIDENCE OF RUBBER STRIP COMING UP IN AREA - PRISON OFFICERS UN AWARE THERE EVEN WAS A TRIP HAZARD
MSA-DCS | WA3810970 | Urquhart D07 smashed mirror | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2021-01-27 10:45:00 | Fail | NEW MIRROR INSTALLED
MSA-DCS | WA3811057 | Unit Managers office light damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-26 12:00:00 | Pass | Replaced damaged light
MSA-DCS | WA3811536 | SHU (9) B5 - windows broken, rear cell window & observation window broken beyond repair | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 0 | CLOSE | 26 Nov 2020 | 2020-11-26 15:10:55 | 2020-11-27 16:30:00 | Fail | MULTIPLE WINDOWS RE GLAZED & FRAME REPAIRED
MSA-DCS | WA3811556 | SHU (9) B5 - Side of shelf stack is not attatched and requires to be refixed to wall and shelf sides | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 11:25:34 | 2020-11-27 14:00:00 | Fail | CUPBOARD & SHELVING/ BRACKETS REMOVED & WALLS PATCHED
MSA-DCS | WA3811933 | Between Unit 15 & 16 - Automatic gate, not working. Not opening from panel control | Casuarina Prison | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 26 Nov 2020 | 2020-11-26 15:16:46 | 2020-11-26 15:00:00 | Pass | 26/11/20carried out repairs to lock drive motor on gate 15/16
MSA-DCS | WA3812993 | Unit 7 - C6 Lock stuck on single lock - contractor on site | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-01 14:15:00 | Pass | Open jammed lock, remove edge capping and main lock, service lock and reinstall.
MSA-DCS | WA3814571 | unit 4B washing machine Maytage water not entering machine | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 13:30:00 | Pass | Unit 4B Maytag Washing Machine water not entering machine. Check machine, make temporary repairs to wiring. Order new valves. Return & install. Recalibrate control. Assemble & test.
MSA-DCS | WA3819538 | Kaartdijin Mia control room damaged carpet hole in carpet 20cm x 20 wide | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2021-03-08 08:00:00 | Fail | damaged carpet tiles replaced
MSA-DCS | WA3819540 | L block unit 4 round kitchen light faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 10:00:00 | Pass | Replaced kitchen downlight
MSA-DCS | WA3819564 | Kitchen- roller door JA1 key is broken inside lock & cannot be secured | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 26 Nov 2020 | 2020-11-26 19:07:07 | 2020-11-26 16:00:00 | Pass | Attend site. Remove broken key from door lock. Normal function restored. Broken key left with Key Control.
MSA-DCS | WA3819577 | main kitchen robo stick wizz broken | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 15:32:56 | 2021-01-05 11:30:00 | Fail | Returned to site with 3 repaired robo sticks.
MSA-DCS | WA3819579 | unit 6 cell 3 toilet running replace valve | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-16 09:30:00 | Fail | Attended site,Serviced toilet including supply and installation new inlet valve and outlet washer.Tested works on completion
MSA-DCS | WA3819581 | visits air con motor leaking water near kitchen | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-09 10:00:00 | Fail | Arrived to site.Awaited unit guard.Accessed room.Tested unit.Staff advised unit dripped water from RHS of unit.Noted indoor fan barrel dirty.Removed all covers.Soaked in cleaner.Deep cleaned coil and fan barrel.Removed all debris.Washed down all components.Returned covers and airflowing okay.Advised staff.
MSA-DCS | WA3857639 | ** Retrospective work order ** Kitchen- Kettle not working, see notes below | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-10 16:10:00 | Fail | Replace LH kettle potentiometer & knobsTest ok
MSA-DFES | WA3810541 | 1st Floor, Ladies bathroom- 1x light globe not working | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-01 08:30:00 | Pass | CompleteAttended site and located faulty globe in ladies toilets lvl 1 replaced and all in working order
MSA-DFES | WA3810678 | L1 rear right engine bay door outside signal green light stays flashing why door is open | Butler Career Fire Station | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-26 15:45:00 | Pass | ATTENDED CALL OUT AND INSPECTED REAR RIGHT HAND SIDE DOOR. THE GREEN LIGHT WAS FOUND TO BE FLASHING WHILE DOOR WAS OPEN. (THE GREEN LIGHT SHOULD HAVE BEEN CONTINUOUSLY ON). TECHNICIAN MADE ADJUSTMENTS TO LIGHT CONTROL, WHICH RESOLVED THE ISSUE.DOOR WAS TESTED AND GREEN LIGHT IS NOW WORKING AS IT SHOULD1.12.2020 NARELLE PROGRAMMED RANG IN - DOOR IS HAVING SAME ISSUES. TECH TO ATTEND SITE TODAY TO ASSESS/FIX.TECH HAS RE ATTENDED THE SITE AS PER NEW SERVICE REPORT ATTACHED
MSA-DFES | WA3810771 | ground engine room Door 4 (rear right) is inconsistent in operation - see notes | CFRS Armadale | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2021-01-08 16:30:00 | Fail | COMPLETED
MSA-DFES | WA3810882 | Security alarm exterior strobe light continually flashing after fault malfunction & activation | CFRS Daglish | GMP-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 08:20:00 | Pass | Found zone 5 kitchen alarm had been set off, system needed to be reset to clear alarms. Reset alarm, test, all ok. Recommend system have a full overhaul or even look at upgrading, as most of the sensors and smoke detectors would be around 10 years old.
MSA-DFES | WA3811287 | Outside Foundation Training Instructor’s Office- Broken retic cap, outside Instructor's Office | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | Dom's Total Grounds Maintenance | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-08 06:00:00 | Fail | Call out & Labour - no parts required
MSA-DFES | WA3811470 | PPC ROOM- Light is not working, see notes below | Metropolitan VFRS | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 14:00:00 | Pass | Located faulty tubes in PPC room. Replaced tubes. All working.
MSA-DFES | WA3811553 | Lecture room 9 right hand wall- Fill holes in plaster and repaint to match | FESA RHQ - Forrestfield | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-09 11:00:00 | Fail | Fill holes and patch with base coat and topping. Sand back patching and repaint walls with 2 coats of color.
MSA-DFES | WA3813347 | Zone 15, Kitchen- Urn (Hot water) is not working. It is displaying the sign – Error Detected J, L. | CFRS Perth | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-27 12:45:00 | Pass | Replaced solenoid bye to poor water flow and reset elements
MSA-DFES | WA3816948 | ground rear yard gate area # 34 mirror safety dish damaged - see notes | CFRS Midland | GMP-BR | Security | Monitoring (SE) | AWB Co. | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 12:30:00 | Pass | Install new mirror
MSA-DFES | WA3818109 | Multiple faulty lights in multiple location - see long description for locations | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-10 13:00:00 | Fail | Replaced lights and repaired as per quote.
MSA-DFES | WA3819484 | Ground information resources 4 Lights not working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 09:30:00 | Pass | CompletedOn site and replaced faulty fluros all in working order
MSA-DFES | WA3819542 | Administration Area & Dining Room- light switches faulty, see notes below | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-27 15:15:00 | Pass | Arrived on site at 13:30 to inspect lunch room lights and walk way lights. Found RCD tripped upstairs in DB and tube and starter blown on walk way light. Replaced Fluro tube and starter reset RCD and tested both circuits. Signed out at 15:15
MSA-DTAG | WA3811242 | Cell 74 bio clean required person in custody has VRE disease highly contagious | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 19:00:00 | Pass | Job carried out as per WO.
MSA-DTAG | WA3815860 | 1903 ground Toilets next to Mitchell JA Chambers/Court 2 door handle fault | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-03 12:30:00 | Fail | REPAIRS MADE TO DOOR HANDLE
MSA-DTAG | WA3819574 | ground Sally Port, outside Court 3, registry fluro faulty lights - see notes | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-27 08:00:00 | Pass | Replaced tubes and starters
MSA-DTAG | WA3819594 | Cell 1 blown strip light - see notes | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 08:30:00 | Pass | Attended site and signed in. Found Gilmore and jooste had already completed the job. Signed out job complete.
MSA-DTWD | WA3806430 | W block, Mortar control room - air conditioning keeps tripping out | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 26 Nov 2020 | 2020-11-26 17:00:00 | 2021-01-08 15:56:00 | Fail | New aircon installed
MSA-DTWD | WA3807170 | D Block, Room D106- Air Con is noisy | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2021-03-23 14:30:00 | Fail | Collected parts and attended site.Completed pre start paper work and signed in. Accessed class room set up equipment and removed relevant ceiling tiles/ lights to access equipment. Installed new blower. Wired up and test ran. Set maximum speed. Reinstalled ceiling tiles and lights. Cleaned up work area and left unit in good working order. Job complete
MSA-DTWD | WA3810569 | workshop, Metal fabrication area - Hydraulic bender Intermittent fault with footswitch | Clarkson Campus | GMP-BR | Equipment | Power Tools (EQ) | Techworks Electrical | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 13:30:00 | Pass | Attended site and inspected machine. The machine was working fine while i was on site but opened up the stop/start control box and to check connections and found no issue. I then opened up the machine control box and checked connections and everything seemed fine except some of relays were not completed pushed in which may of been the cause of the intimate fault.
MSA-DTWD | WA3810823 | block 9, Library - Lights not working in Equipment Storeroom of Library Workroom | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-26 13:00:00 | Pass | Repalced faulty lights in blood 9 equipment store.job complete
MSA-DTWD | WA3810873 | Block 9 ground library Light switch in control box for Quiet Study area arcing. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-26 14:00:00 | Pass | Repalced faulty switch mec to light panel in library.job complete
MSA-DTWD | WA3811190 | U Block - Workshop U015 2x Evap unit not cooling. | Balga Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Precise Air Group | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-26 15:00:00 | Pass | Gained access to site completed relevant sign in procedures, accessed roof , replaced 2x solenoid on uO15 evaporative coolers , all working fine
MSA-DTWD | WA3811402 | L block LG12B Left external door has dropped and won’t close or lock properly | Mandurah Campus (formerly Peel) | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 17:00:00 | 2020-11-26 13:15:00 | Pass | Attended site and refitted loose hinge
MSA-DTWD | WA3811429 | E Block, E300 Automotive- Chrome plated tape above the wash trough that cannot be turned off | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 15:50:00 | Pass | Replaced faulty spindle
MSA-DTWD | WA3811698 | Lvl 3, Room C305- Smell from plumbing | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-01 11:15:00 | Pass | Removal of hws under bench and sealed drain
MSA-DTWD | WA3817956 | Carpark south - sewage over flow | West One Services | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Nov 2020 | 2020-11-27 17:00:00 | 2021-02-15 08:21:00 | Fail | Unblocked main sewer line with jetter, inspected drain with camera to find it was all clear
MSA-DTWD | WA3818146 | Lvl 2, D Block - Burst plumbing pipe | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 26 Nov 2020 | 2020-11-26 17:06:38 | 2020-11-27 09:18:00 | Fail | repaired burst water pipe and installed 2x ministops in cupboard for future
MSA-DTWD | WA3819102 | S Block, AUH 5 it keeps tripping out | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-18 15:24:00 | Fail | Sub contractor attended site and completed quoted works to repair AHU5 job is now complete 18/12/20
MSA-DTWD | WA3819485 | A Block, Room A304 to A333- Lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 14:22:00 | Pass | Repalce multiple lights out throughout level 3 a block
MSA-DTWD | WA3819488 | A Block, Room A311- broken motion sensor | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 26 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-01 10:51:00 | Pass | Repalced faulty sensor in classroom.job completed
MSA-DTWD | WA3819584 | A Block, A30- Damp odour coming from split system air con | Bentley Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-04 10:59:00 | Fail | Cleaned evaporator coil and drain. Flushed drain and for that drain pipe has come apart in wall.Picked up parts from suppliers. Returned to site. Modified and repaired drain pipe. Checked operation. All ok
MSA-MRWA | WA3810066 | Disable toilet blocked - see notes | Heavy Vehicle Services-Main Building-Ground Floor-Toilet-Disabled-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-26 15:25:00 | Pass | Unblocked lhs disabled toilet on the gr floorPrevious blockages had occurred on rhs toilet, so these are separate issues
MSA-DCA | WA3820109 | external Security door - door not closing properly | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Entrance - Security | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 27 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-27 14:17:00 | Pass | Inspected door and found that the door closer arm had come loose, resecured as necessary, adjusted and tested operation. Please note that this door closer is very old and adjusted is very temperamental. If unit fails again, would recommend to replace with a ts83 en5-7.
MSA-DCA | WA3820311 | Plant Room, Pneumatic station return air hose is leaking, see notes below | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-03 10:38:00 | Pass | COMPLETED
MSA-DCS | WA3819898 | Security office second monitor cannot see cameras | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-18 12:03:00 | Fail | Attended site and installed replacement security workstation.Tested OKJob Complete
MSA-DCS | WA3819906 | INF (10) - air conditioning unit in infirmary cell not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 07:23:38 | 2020-11-27 08:30:00 | Pass | Arrived on site and signed in,checked over aircond found system short on refrigerant, to be repaired by subcontractor under warranty as new unit.
MSA-DCS | WA3819914 | Unit 3, A wing - shower water pipes have disconnected | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 07:27:02 | 2020-11-27 09:30:00 | Pass | Nill
MSA-DCS | WA3819947 | Unit 4, A Wing- Clothes & shoes in the razor wire needs removing | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 3 | CLOSE | 27 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-01 10:30:00 | Pass | 01/12/20Clean litter unit 4 roof razor wire
MSA-DCS | WA3819964 | unit 1, cell A7 - Hole in main window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 08:19:03 | 2020-11-27 15:00:00 | Pass | POLYCARB PANEL REPLACED
MSA-DCS | WA3819981 | Unit 5, B & D, Cell B12 has no water (approx 3 weeks now) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-11-27 11:30:00 | Pass | Nill
MSA-DCS | WA3819982 | Unit 3, C wing Showers - 2 shower doors damaged (Doors are in the control room with hot water system | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-30 11:30:00 | Fail | installed hinges to shower doors
MSA-DCS | WA3820014 | Unit 2, D5- Cell lock is sticking | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 27 Nov 2020 | 2020-11-27 13:04:00 | 2020-11-27 11:30:00 | Pass | Cell lock on Cell D5 / Unit 2 - was jammed Unjammed and removed from door Serviced Lock and reinstalled .
MSA-DCS | WA3820036 | Kitchen - leak under the sink | Rockingham Justice Complex | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 09:21:51 | 2020-11-27 15:10:00 | Pass | COMPLETED
MSA-DCS | WA3820100 | Admin- Strip light near ASO's office(HR Admin) is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-03 15:00:00 | Pass | Repaired multiple faulty lights in admin building
MSA-DCS | WA3820104 | External Zone 3 mircowave constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-27 15:00:00 | Pass | Rectified and repair power from MW Tx, job completed.
MSA-DCS | WA3820106 | Flickering light bulb in Administration corridoor outside HR Managers office | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-11-30 08:30:00 | Pass | Repaired faulty lights in in admin corridors
MSA-DCS | WA3820127 | Unit 5, B Wing- Shower has no water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-11-30 09:30:00 | Pass | Nill
MSA-DCS | WA3820131 | admin auto boil not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-08 10:16:00 | Fail | Replaced urn due to corrosion and then particles coming out of tap changed filter on Gac Filter System. removed old unit to tip installed rheem bwu 7.5 litre urn
MSA-DCS | WA3820136 | Visits- commercial double door fridge inside fan cover broken & drain pipe broken | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-11-30 11:00:00 | Pass | found cover, re-fit drain pipe test operation and put cover back
MSA-DCS | WA3820137 | Visits officer - toilet cistern broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-02 14:30:00 | Pass | COMPLETED
MSA-DCS | WA3820140 | Unit 4, Cell C10 - shower taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2021-01-19 11:45:00 | Fail | COMPLETED
MSA-DCS | WA3820154 | Unit 14, A Wing- Cell A3- Tap in cell constantly running & wont turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-01 12:30:00 | Pass | Nill
MSA-DCS | WA3820169 | Unit 14, A Wing- Cell A16- Tap constantly leaking, causing mould | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-01 14:17:00 | Pass | Nill
MSA-DCS | WA3820248 | Unit 4, Visits camera family north east- PTZ can not be moved, out of focus | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-03 08:00:00 | Fail | Fuse had become loose. Fuse resecured and test ok.
MSA-DCS | WA3820251 | Main prison, Security office- CCTV loss of video camera feed for unit 2, 5 & 6, see notes below | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Nov 2020 | 2020-11-27 20:04:39 | 2020-11-27 17:45:00 | Pass | Found cause of loss of CCTV images in security office of all but visits cameras due to link loss between Health Core switch and Admin Network Switch. Reset SFP’s at both ends restored service. Confirmed restoration of camera visibility on Security office CCTV workstation.
MSA-DCS | WA3820288 | Textile workshop - Workshop front door has dicky lock./jamming | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-11-30 14:00:00 | Pass | Service and repair lock
MSA-DCS | WA3820296 | Water Leak in prison (not Identified where)- Letter received from,watercorp losing 200 liters per hr | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-09 17:50:00 | Fail | replaced toilet cisterns to Hotham A5, Gascoyne A4,education female toilet, staff lunch room. Replace pressure reducing valve to plumbing duct in Hotham B4 and A4. Replaced taps to cleaners sink in Hotham. Service toilet cistern in Hotham A2 and B3
MSA-DCS | WA3820298 | CCU, H1 - Judas hatch lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 12:58:03 | 2020-11-27 14:30:00 | Pass | Attend site. Serviced lock to restore normal function.
MSA-DCS | WA3820329 | Unit 2, CCTV has a 25min delay from real time | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Nov 2020 | 2020-11-27 21:44:41 | 2020-11-27 18:45:00 | Pass | Attended unit 2 cctv IndigoVision workstation, confirmed time on workstation showing 25min fast. It appears that this workstation has not been set to synchronise time with site time-Server. Unable to correct as require Administrator login. Referred back to Tony Vavier for referral to Honeywell.
MSA-DCS | WA3820349 | Miant kitchen - leaking tap | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-17 09:15:00 | Fail | Attended site,Removed failed pre rinse tap assembly to kitchen and supplied and installed new as required. Tested works on completion
MSA-DCS | WA3820352 | Kitchen - Big Mixer machine not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-24 14:30:00 | Fail | Kitchen big mixer machine not working. Check mixer & controls. Dismantle & remove bowl guard safety switch. Order parts ex east. Pick parts up, return & install. Assemble & test, report to staff.
MSA-DCS | WA3820353 | Unit 1, CCTV indigo footage is frozen in safe cells & possible further cameras | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Nov 2020 | 2020-11-27 18:51:13 | 2020-11-27 15:30:00 | Pass | Frozen camera view ,refresh the video pane safe cells. Job completed.
MSA-DCS | WA3820372 | Unit 14, A/C 9/10 - Fault on smoke alarm | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 15:35:36 | 2020-11-27 19:57:00 | Pass | Complete
MSA-DCS | WA3820375 | INF(10)- Control Room- key safe on wall, barrell not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 27 Nov 2020 | 2020-11-28 15:38:21 | 2020-11-30 11:00:00 | Fail | Contact site, discuss lock with site, lock is worn and beyond repair, requires new lock. Advised site job will be completed on 30/11/2020Replace lock, keys are worn and require replacing. Check keys from Security safe and replace as required.
MSA-DCS | WA3820388 | Gatehouse - Duress alarm system activating in false area's | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-08 11:00:00 | Fail | Testing around the EDUCATION building showed inaccuracies. Recalibrated receivers and tested in multiple locations around the EDUCATION and PROGRAMS areas. Tested ok. Databases taken before and after calibration changes.
MSA-DFES | WA3820222 | Urinal in 1st floor mens toilet partial blockage | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-17 13:00:00 | Fail | Investigate blocked urinal on first floor men’s toilet far left urinalAttempt to plunge and use bowl guard to clear blockage, unsuccessful Remove urinal from wall and isolate water supply, remove urinal trap/waste Will need to source new trap/waste to urinal and return to install, re-install urinal with out of service sign Pack up and clean up worksite Investigate blocked urinal in men’s toilet 1st floor Remove urinal from wall and clean, remove old trap and sealsSupply and install new trap and seals to urinal, fasten and silicone back to wallRe-connect water supply and test operatio/check for leaks, attempt to plunge and use of bowl guard, still slight blockage in waste pipe may need small drain machine and raised job Pack up and clean up worksite Isolate water supply to urinal, remove urinal off wall, clean urinal and remove silicone from urinal and wallRemove urinal trap and use small drain machine to clear blockage, put urinal back to flush with water and bowl guard, r
MSA-DTAG | WA3820341 | Male Public Toilet - Light has blown | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-02 10:30:00 | Pass | Inspected faulty light in toilets and replaced blown blue tubes
MSA-DTWD | WA3819967 | 1st Floor, Staff lunch room - 2 switches stuck on triple light switch | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-27 16:00:00 | Pass | Attended site and signed in. Got keys from facilities. Located upper staff room light switches. Found fault to be within door frame. Cabling inside has issues. Pulled out cabling and found faulty cable. Advised to relocate to the wall. Ran surface duct and switch on wall and extended cabling to suit. Installed new 3 gang switch next to door entry. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3819972 | Block 8, Staff Room 8G28- both ceiling fans are not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-27 13:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located staff room. Found fans to be moving at a snail pace. Investigated to find faulty fan controller on wall. Disconnect and removed faulty switch. Supply and replace with new fan controller. Tested all okay. Signed out . Job complete
MSA-DTWD | WA3819975 | Courtyard Veranda - roof has given way - need to secure roof until can be repaired (make safe) | Leederville Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 27 Nov 2020 | 2020-11-30 17:00:00 | 2021-02-19 16:00:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3820246 | House 8, Kitchen- Leaking Tap | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 27 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 16:00:00 | Pass | Job completed - Check leaking water pipe to kitchen and repair
MSA-DTWD | WA3820333 | E Block, room E014- Boiling water (drinking) unit not working | Balga Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2021-02-19 11:00:00 | Fail | Replaced boiling water unit
MSA-DTWD | WA3820343 | L Block, Repair leaking air line in the Stonemasons workshop. | Balga Campus | GMP-BR | Equipment | Compressors, Generators (EQ) | CAPS AUSTRALIA PTY LTD | 2 | CLOSE | 27 Nov 2020 | 2020-12-02 17:00:00 | 2020-11-30 13:43:00 | Pass | job completed - replaced leaking pipe
MSA-DTWD | WA3820385 | Lvl 5, North Block Plant Room- fan belts cooling tower 2 faulty | Perth Campus B1 | GMP-BR | Air Conditioning | Cooling Tower (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 27 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-01 10:45:00 | Pass | Found the belts on cooling tower two needed replacing. Isolated and tagged out , removed the covers , used the spare belts and fitted. Picked up new belts.
MSA-DTWD | WA3820432 | Security Panel - unable to arm Building A and B | Murdoch Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 0 | CLOSE | 27 Nov 2020 | 2020-11-28 03:45:08 | 2020-12-02 11:00:00 | Fail | 28/11/2020, 930-1100Power supply blown up in Block A wet lab expander , replace x3 back up panel batteries . zone 29 constant unsealedcausing alarm . Zero zone out and change zn 26 as entry exit to return to investigate zn 29 further door reed . mark jobas incomplete02/12/2020, 1015-1100Door got some work done on it replacing the seals causing the door to not close all the way so the reeds weren't sealing. Replaced the reed got a seal re enabled ok
MSA-DCA | WA3820500 | main public lift (lift no.#1) out of service - making loud noise. | Art Gallery of WA - James St | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 28 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 10:57:00 | Pass | Arrived on site and found lift as reported. Noise apprentice with counterweight at top of shaft. Removed dry grease from rails and applied slip it. Checked motor room sheaves and cleared error log. Ran and tested lift, could not reproduce noise. Left lift in service. to be closed at not Chargeable
MSA-DCS | WA3820464 | Unit 10 CD wing- Door seal on the regitermic oven has broken cant use the oven | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 28 Nov 2020 | 2020-11-28 14:59:04 | 2020-11-28 17:20:00 | Fail | Found door hinges all loose. Tighten & adjust both door hinges to raise door up from Sag to proper position. Adjust & tighten doorlock catch ok. Leak stopped. Test all elements working ok and thermostat calibration accurate.Left Unit operational.
MSA-DCS | WA3820493 | Casuarina Prison - PTZ Camera no.3 - has no display/ no signal. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Nov 2020 | 2020-11-29 14:14:16 | 2020-11-30 13:00:00 | Fail | Building company damaged and they will fix the cable from PTZ 3
MSA-DCS | WA3820503 | Front gate-Air extraction in the toilet is not working-enclosed area | Bandyup Prison | GMP-BR- HO | Electrical | Materials (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 28 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-02 11:00:00 | Pass | Replaced toilet exhaust fan
MSA-DCA | WA3820568 | A/C is not working please check and fix | State Library of WA-Main Building | GMP-BR | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 29 Nov 2020 | 2020-11-29 15:43:51 | 2020-12-08 14:00:00 | Fail | Attended site on an after hours call out. Server room AC system in fault. Applied tests and checks investigation found system faulting on an E4 fault (activation of low pressure switch). Checked system with an electronic leak detector (unable to find leak). Isolated system to return tomorrow to remove residual refrigerant and pressure test. Returned to site, weighed out refrigerant (700grams from a charge of 3.7kg). Pressure tested System (unable to locate refrigerant leak). Submitted BRA for further time to investigate and seperate system to identify leak. BRA approved returned to site separated system and re pressure tested. Identified pin hole leak on condeser coil elbow. Soldered and repaired leak and left system on pressure test. Returned to site syste to have held pressure. Submitted BRA to evacuate and charge System (BRA approved) evacuated system and weighed in a charge of 3.7kg R410a. Tested operation. System operating correctly. Works completed.
MSA-DCS | WA3820522 | Camera screen for all the zones and PTZ are all blank, unable to see anything | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Nov 2020 | 2020-11-29 10:40:02 | 2020-11-29 10:30:00 | Pass | Attended site and found that two CCTV monitors are blank.Restarted IndigoVision Workstation located in equipment room.Tested.All ok at departure.
MSA-DCS | WA3820543 | UNIT 2- Cell 9,14 and 17- Cell call system is constantly alarming. | Bunbury Regional Prison-Gatehouse | SPA-BR | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Nov 2020 | 2020-11-29 17:06:52 | 2020-12-17 15:00:00 | Fail | Replaced water damaged CI-8 module at UNIT 2 A -Wing with new 3 x CI-8A, test cell call functions A and B wing. Test PA through cell call 3210 controller, all back to normal operations.
MSA-DCS | WA3820547 | Karnet Prison Farm- Water plant not injecting chlorine | Karnet Prison Farm | GMP-BR- HO | Hydraulics | Hydraulic Pump Pipework (HY) | TRILITY Solutions Pty Ltd | 1 | CLOSE | 29 Nov 2020 | 2020-11-30 09:15:07 | 2020-12-08 16:15:00 | Fail | Replaced battery
MSA-MRWA | WA3820578 | Access gates are not working- Big sliding electronic gates. are not operating. | Neerabup Depot | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 29 Nov 2020 | 2020-11-29 17:30:46 | 2020-11-29 16:45:00 | Pass | Gates were not responding due to a possible power surge. reset all the gates. Found gate three remote not working. arrange to have installer return as building was only four months old. also never put asset numbers on building as still under warranty with builder
MSA-MRWA | WA3820599 | Panel outside server room coming up with device fault - display message VESDA 1 Fault | Road Network Operation Centre (RNOC)-Main Building-Second Floor-Server Room | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 29 Nov 2020 | 2020-11-30 01:32:48 | 2020-11-29 23:59:00 | Pass | Call out due to fault on vesda in level 2 server room. Fault due to filter needing replacement, replaced filter and left system normal
MSA-DCA | WA3820939 | BMS is in fault | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 16:30:00 | Pass | COMPLETED
MSA-DCA | WA3820992 | damaged sprinkler causing water leak | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 14:30:00 | Pass | job completed - Turn the orchard drips and look for the leak.oFix the leak.-Noticed a sprinkler body on the ground.oFix broken sprinkler body.oReplace 1 other sprinkler and nozzle on the lawn areas.-Please check a leak Alert High water usage (leak) triggered for controller PCC-Also check Alert High water usage (leak) triggered for controller PCC
MSA-DCA | WA3821096 | Balcony Foyer - Smashed window | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1-Foyer | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2021-03-16 08:15:00 | Fail | ATTENDED SITEREMOVED REMAINING BROKEN GLASS AND TEMP GLAZED PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-1620 X 11252 MEN REQUIREDRETURNED LATER DATE SUPPLIED & FIT NEW PANEL TO WINDOWWITH 6MM VS GLASS LOW IRON CLEAR TOUGHENED SAFETY GLASS20% OPACITY AS CHOSEN BY REESE1-1715 X 11272 MEN REQUIRED
MSA-DCA | WA3821339 | toilets Floor drain is overflowing with bubbles, possible blockage - see notes | Short Street Theatre-Main Building | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 16:06:00 | Pass | Cleared blocked floor drain.
MSA-DCS | WA3820780 | Unit 6 - D Wing Can't get key in to lock to open door./lock damaged/cleaning stores | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 30 Nov 2020 | 2020-12-04 17:00:00 | 2020-12-03 09:30:00 | Pass | Service lock and replace bolt throw
MSA-DCS | WA3820862 | Gate house sliding automatic entry personnel door sensor faulty and hard to open | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 30 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-01 15:45:00 | Pass | Paul Cullum (01/12/2020) - Work NoteTravel to site. Inspection and testing of control and sensors. Both sensors activate but door is slow to react/open. Accessing control difficult due to bundle of cables, terminals and relay tied up in front. During inspection and fault finding several cables found loose, out of terminal. Have left door as found. Issue with detection is intermittent. Door left in operation. Suggest retrofit new control.**Quote to be submitted for upgrade
MSA-DCS | WA3820918 | Unit 9 A4 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 07:46:35 | 2020-11-30 13:00:00 | Pass | Attended site checked and found U9 A4 cell call point RED LED stuck on and not operational. Reset cell call point and tested cell call function correctly after work.
MSA-DCS | WA3820948 | Security Area Visit room NW camera not showing recorded footage on terminal in Security Office. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 08:12:14 | 2020-12-04 11:56:00 | Fail | Repairs to be completed under WA3871461- no further works under this W/O
MSA-DCS | WA3820954 | Unit 13, Plant room - Air conditioner in the Electrical Room is blowing hot air | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 13:15:00 | Pass | found unit in heating. Located remote and found batteries had been removed. Replaced batteries, switched to cooling and tested operation. All ok.
MSA-DCS | WA3820956 | Unit 7 - D Wing Window supports broken. Window not staying open. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-07 11:00:00 | Pass | SPIRAL BALANCES RE NEWED
MSA-DCS | WA3820960 | MPU (8), M10 - night observation ceiling light not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 08:18:57 | 2020-11-30 15:00:00 | Pass | Repaired faulty lights in mpu m10
MSA-DCS | WA3820963 | Unit 4 - D Wing floor shower tiles surrounding drain missing | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-14 12:30:00 | Fail | 06/09/21 - closing job cost to date as site not given us response on access - cost for labour only/inspection
MSA-DCS | WA3820969 | unit 1, A & C - wall power point not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 10:00:00 | Pass | Replaced damaged gpo in unit 1 A/C dayroom
MSA-DCS | WA3820975 | Unit 4 - D Wing wall vent shower block has rusted and broken away leaving large hole | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2021-03-02 13:00:00 | Fail | NEW VENTS FITTED
MSA-DCS | WA3820976 | Unit 1, A9 - Judas hatch lock is not locking all the time faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2021-02-23 11:00:00 | Fail | Repair barrel, require parts and approval.Replace hatch and barrel.
MSA-DCS | WA3820986 | Gate House - Control Room Outside Door 6 there is a light that keeps flickering.U shape globe | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 15:00:00 | Pass | Investigated faulty lights. Picked up replacements and installed off 12 foot ladder
MSA-DCS | WA3820988 | Unit 5, A wing - There is a leak in the Fire sprinkler control cupboard on the A wing landing, | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-04 11:43:00 | Fail | Arrived on site and inspected leaking pipe in valve room found the leak to be coming from the isolation valve on the suction side for the jacking pumpWent to office picked up new 25mm isolation valve, ,check valve and 25mm nipplesArrived back on site and isolated incoming combined main s supplyRemoved existing leaking isolation valve and fittingsInstalled new valves and fittingsTested operation of new valvesReinstated combined mains
MSA-DCS | WA3821003 | Unit 4, D8 - cell call Speaker still working but very faint | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 13:00:00 | Pass | Replaced damaged cell call unit with new, job completed.
MSA-DCS | WA3821014 | Unit 1, Office - Unit 1 PA system is not working unable to make announcements | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-01 08:42:00 | Pass | Attended and test PA in the unit, working as normal. Job completed.
MSA-DCS | WA3821016 | Uni t4, D9 - Cell Call Not Working | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 15:30:00 | Pass | Replaced defective cell call unit with new, tested working ok. Job completed.
MSA-DCS | WA3821026 | Unit 6, D11 - Hinges have dropped on Door causing the lock to jam | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-03 09:30:00 | Pass | Unable to complete due to security cell searches.replace hinges and weld on strike.Replace barrel, other cell keys working in barrel.
MSA-DCS | WA3821030 | Front Gate, staff toilet - keep flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 08:58:15 | 2020-11-30 14:10:00 | Pass | Lubricated outlet mechanics, replaced foam seal, flexi and fixed cistern to the wall.
MSA-DCS | WA3821034 | Unit 2, Regi ovem - problem with heating, heats top 160 & drops to 155 & stays there | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 09:03:14 | 2021-01-07 11:00:00 | Fail | 30/11/20Arrived at site liaise with kitchen, identify oven, was told that the oven cooking times have changed from something taking 2.5 hours to 4 hours cooking time, checked and tested elements and fans and found the top fan was rubbing on the metal and will require replacement, the other motors and elements tested all good, did also notice that all the fans would shut down for around 1 minute every now and then but I couldn't do further testing because the guards told me I had to pack up so that they could put the food back in, also did notice the door seal had a few chips in the edges but not enough to make much of a difference.The main PCB board the encoder and probe could be faulty Parts required:1 x Fan1 x Motor1 x Capacitor07/01/21Returned, pulled oven out, removed panels removed faulty motor, supply and replace motor, reassemble all components and test all components for correct function and was all good until the oven got up to temperature which then the oven proceed
MSA-DCS | WA3821036 | Unit 5,Control Room, B & D Side- Bolt broken on the window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2021-03-09 10:45:00 | Fail | SLIDING BOLT LATCH REPLACED
MSA-DCS | WA3821043 | Unit 1, Cell B4 - Hole burnt in window | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 14:00:00 | Pass | POLYCARBONATE WINDOW RE PLACED
MSA-DCS | WA3821048 | Unit 2, Cell A16 - damaged may need replacement | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 09:11:04 | 2020-11-30 15:45:00 | Pass | Job delayed due to no escort available. Cell A16 in u3 doesnt exists. Apparently it should have been A15 faulty taps, but it has already been fixed previously on the different work order. No action taken
MSA-DCS | WA3821078 | Unit 5 - C13 toilet cistern is leaking into the service duct. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 08:30:00 | Pass | Nill
MSA-DCS | WA3821138 | unit 1 control room cell call hand set not working SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 10:01:00 | 2020-12-07 11:14:00 | Fail | Handset replaced and tested on cell call 3210.
MSA-DCS | WA3821143 | Unit 5 - A2 sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 10:30:00 | Pass | Nill
MSA-DCS | WA3821162 | Unit 7, Cell C6- Hot water issues (Water is not staying hot, needs to be regualted) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 13:30:00 | Pass | Nill
MSA-DCS | WA3821183 | Unit 5, Cell B10- Window slider is not working, window does not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-07 10:00:00 | Pass | SPIRAL BALANCES RE NEWED
MSA-DCS | WA3821208 | Kitchen - Main combi oven faulty sensor/thermoset | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 10:39:33 | 2020-12-01 11:45:00 | Fail | Replaced Broken Meat Probe. Check & adjust diagnostics. Left oven operational.
MSA-DCS | WA3821220 | Unit 1 cell B14 Windows has hole in it. | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 10:44:46 | 2020-12-02 12:00:00 | Fail | POLYCARBONATE WINDOW RE PLACED
MSA-DCS | WA3821227 | Unit 5, A Wing- Cell ventilation not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 10:53:45 | 2020-12-24 11:00:00 | Fail | Repaired cell vent fans U5
MSA-DCS | WA3821236 | Reset, Main Area- lights faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 10:57:55 | 2020-12-03 10:00:00 | Fail | Repaired lights
MSA-DCS | WA3821237 | Unit 2 Cell D11 Toilet pan loose on floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 10:51:25 | 2020-11-30 17:50:00 | Pass | Uninstalled loose pan and reconcreted it. Replaced rubbers too
MSA-DCS | WA3821261 | unit 6 cleaning workshop polisher lead has a cut PV278253 | Casuarina Prison | WSM-MW-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-01 15:00:00 | Pass | Repaired faulty cleaning polisher in unit 6
MSA-DCS | WA3821277 | Jasper, Cell B03- Smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 14:00:00 | Pass | WELDED AND RE GLAZED WINDOW
MSA-DCS | WA3821293 | Unit 6, Cell B12- Light not working, see notes below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 13:00:00 | Pass | Repaired faulty lights in unit 6 b12
MSA-DCS | WA3821296 | Unit 4, Cell D6- Light tombstones not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 11:30:00 | Pass | Repaired faulty light in unit 4 d6
MSA-DCS | WA3821300 | Unit 1 - A Wing landing has one light flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-03 08:30:00 | Pass | Repaired faulty lights in unit 1 A wing
MSA-DCS | WA3821322 | Unit 6 - B & D Chains are broken on both windows at the end of both B & D wing landings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2021-01-29 12:30:00 | Fail | replaced broken chain winder boxes
MSA-DCS | WA3821326 | stores - Rollerdoor closed onto a trailer damaging the roller door and won't open or close. | Casuarina Prison | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 11:51:13 | 2020-11-30 15:15:00 | Pass | slats and rail replaced
MSA-DCS | WA3821336 | Unit 1, Cell B5- Toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 11:57:55 | 2020-12-01 08:20:00 | Pass | Job delayed due to no escort. Unblockrd toilet in b10. Nothing wrong witht the toilet in b5(maybe wrongly reported)
MSA-DCS | WA3821341 | Unit 1, C Wing Shower - Shower door damaged | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2021-04-14 09:30:00 | Fail | HINGES REPLACED ON SHOWER DOORS
MSA-DCS | WA3821355 | Perimeter fence, inner fence zone 14,15,16 & 17 - are not operational | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Nov 2020 | 2020-11-30 16:06:38 | 2020-12-09 13:00:00 | Fail | Repaired the damaged sensor cable and terminations of Zone 14,15,16&17. Tested all ok after repair.
MSA-DCS | WA3821369 | Level 4, monitoring room - Door handle has come off | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-07 12:00:00 | Pass | Attended site and carried out repairs to door handle.
MSA-DCS | WA3821410 | Boiler house workshop Pressure relief valve on main water line into laundry is passing water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 12:46:34 | 2020-12-01 09:05:00 | Pass | Plastic air/water pipe leaking in the boiler house. Job reported to the wrong contractor. Boilertronic issue.
MSA-DCS | WA3821425 | kitchen burners not lighting up pilot not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-09 15:30:00 | Fail | 6 Burner stove pilots & burners faulty. Check stove & burners. Dismantle all parts. Clean out blocked jet & burner. Return with new pilot jets. Clean out pilot. Assemble, found gas main turned 1/2 off on main line.
MSA-DCS | WA3821446 | Official visits - The light in Room 6 has started to flash on and off | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-01 08:30:00 | Pass | Repaired faulty lights in offical visits offices
MSA-DCS | WA3821559 | Canteen- Door between canteen & store office lock is damaged including handle | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 15:02:46 | 2020-12-01 09:20:00 | Pass | Replaced damaged Mortice Lock on Door between Canteen & Storeadded extra Thick Door frame strike , to secure .
MSA-DCS | WA3821560 | Unit 1, Cell D14- Toilet Pan from the base leaking Sewage Water into the shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 15:06:30 | 2020-12-01 12:00:00 | Pass | Replaced pan rubber and kee seal
MSA-DCS | WA3821571 | Unit 2, D13 - Sink Taps Leaking Won’t Turn Off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-01 13:10:00 | Pass | Hot and cold spindles in the basin replaced
MSA-DCS | WA3821590 | Unit 4C, Cell 11- door will not open, see notes below | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 15:36:40 | 2020-12-01 11:15:00 | Pass | Open Lock on Cell 11 Unit 4C - fault with mortice lockLocking mechanism was not retracting fully had to drill of external handle and replaced lock and handle.
MSA-DCS | WA3821663 | Unit 4 Fire Alarm, no fire but site staff cannot reset | Casuarina Prison-Prisoner Accommodation Unit 4 | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Nov 2020 | 2020-12-01 00:39:59 | 2020-11-30 23:20:00 | Pass | Callout due to fire alarm activating in unit 3, when arrived checked graphics system and found flow switch in unit 3 in latched alarm but sitting in normal state. Reset fire system and flow switch alarm cleared and left in normal.
MSA-DFES | WA3820949 | Engine room door in front of pump - is not working - not fully lifting in automatic mode | CFRS Osborne Park | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-12-03 14:30:00 | Fail | Attended Osborne Park Fire station. Replaced faulty Logic board and 8 relays on door # 2. Door 1,2,3,and 4 -- replaced all relays and modified strobe light to come on when door stops in any position between fully closed and fully open. On completion, all doors have been tested and are operating correctly in Auto mode.Please refer to the attached service reports and photos
MSA-DFES | WA3821101 | Security system is in fault - arm system is not working properly and access points not responding | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 12:30:00 | Pass | 30/11/20 - Dylan ParslowAdvised of bypass procedure.All ok.
MSA-DFES | WA3821554 | Vehicle Security Gate - External access keypads for security sliding gate isn't working | CFRS Daglish | GMP-BR | Building | Steel Fencing & Gates (BU) | Anvil Doors | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-15 10:45:00 | Fail | Attended call out to Daglish Fire station. Inspected the vehicle security gate external keypad controller. The key pad controller has water damage to the internal components. The key pad will need to be replaced to get the gate operational again.Please see attached BRAF and quotation for the replacement Keypad to gate for approval.Our technician has installed the new keypad today to the gate at Daglish fire station. The Key pad was installed and worked correctly and then stopped. Our technician has advised as follows to close out this issue-1.The access control contractor may need to attend to re-programme the control software for the gate (Anvil Doors are unable to carry out this work)2.If step one does not work—there may be damage to the underground cables to the key pad (water damage)Unfortunately—replacing the key pad, although required as the old one had water damage, has not closed out the defect.
MSA-DFES | WA3821556 | No Power to security alarm system key pad | CFRS Joondalup | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-03 12:15:00 | Pass | Arrived onsite and signed in at 1145Locates Reported alarm panel with station office and proved that there was no fault. After doing some investigative work we discovered that it had been called through the wrong Fire station. Have advised client that they will have to raise it again but for Butler FS instead.Stopped works at 1215 and stayed onsite for a quote.
MSA-DTAG | WA3820835 | No screen/video cameras are displaying | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 30 Nov 2020 | 2020-11-30 17:00:00 | 2020-11-30 17:00:00 | Pass | Attended site. Investigated fault concerning cameras down, found multiple cameras showing black screen, from serverable to ping all cameras with black screen. Web browsed into cameras, live view on web browser is online, error messagedisplaying for video stream. Adjusted programming and restarted cameras. Cameras back online and client able to viewcameras on CCTV system.Job completed.
MSA-DTAG | WA3821053 | Toilets next to Mazza JA Chambers/Court 1- Water running constantly from faucet of rightmost sink. | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-11-30 15:07:00 | Pass | Reseat and rewasher basin hot and cold
MSA-DTWD | WA3820826 | B block B block B209 kitchen urn not working | East Perth Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 30 Nov 2020 | 2020-12-02 17:00:00 | 2020-12-04 17:30:00 | Fail | Unit off on arrival due to a bad noise. Filter had not been changed, ever, so replaced filter and flushed. Thermal overload has triggered and unable to reset. Have tagged out unit until the part has arrived. Return when part arrives Replaced element
MSA-DTWD | WA3821070 | Lvl 2, Room A252- Broken window pane | Perth Campus B5 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-03 12:00:00 | Pass | ATTENDED SITEREGLAZED BROKEN WINDOW5.38 CLEAR LAMINATED SAFETY GLASS1-876 X 458PLUS SILICONE AND 2.7 L/M OF PUTTY USED
MSA-DTWD | WA3821074 | Lvl 2, Room B262- Blown lights (many lights in this room have issues) | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 11:00:00 | Pass | Attended site and signed in. Completed jsa. Completed replacing faulty tubes and starters. Replaced 10 x tombstones, 32 x tubes, 32x starters. Completed paperwork. Informed staff of completed job and signed out. Job complete.2/12/20 Replaced faulty ballast + fluros to lights in 262, lights all work *** job complete ***
MSA-DTWD | WA3821082 | E Block, intermittent leak on the isolation valve on the MIG gas manifold, see notes below | Midland Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-03 10:32:00 | Pass | Stem found to be leaking. Removed cleaned and replaced. No evidence of a leak
MSA-DTWD | WA3821112 | H block south - concrete besser blocks lose on to of a garden bed & require them concreted back | Midland Campus | GMP-BR | Building | General Building (BU) | AWB Co. | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 14:00:00 | Pass | FIX LOOSE BESSER BLOCKS TO GARDEN BED
MSA-DTWD | WA3821125 | Level 1, Lift 6 - Lift not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 15:00:00 | Pass | Wiring in controller was loose Found and re terminated Lift running - To be closed out at $0
MSA-DTWD | WA3821224 | E Block, LSK E58- Dough mixer not working | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 13:30:00 | Pass | COMPLETED 30/11
MSA-DTWD | WA3821360 | Tower, level 3, Men's Urinal overflowing | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Nov 2020 | 2020-12-01 17:00:00 | 2020-11-30 16:15:00 | Pass | Readjusted alignment of cistern and unblocked urinal.
MSA-DTWD | WA3821396 | Creche- Broken latch on toilet door | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-09 15:05:00 | Fail | Install cabin hook to Creche toilet door
MSA-DTWD | WA3821494 | L1 admin building F16 water leak with damaged ceiling tiles | West One Services | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-04 11:15:00 | Pass | Investigate roof and found splits, cleaned and sealed
MSA-DTWD | WA3821505 | L1 near Media Store, Room B013- backflow taps leaking | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2021-03-10 18:00:00 | Fail | re-assembled installation, 2x RPZD, 2xTMV, 2X hose taps, 10" filter, pipe labels etc
MSA-DTWD | WA3821508 | L2 server room light has blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-04 12:46:00 | Pass | Replaced multiple lamps throughout lvl 2 server room. All lights working properly now.job completed
MSA-DTWD | WA3821592 | Numerous water leaks around campus- Small tap and toilet water leaks | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-02 15:30:00 | Pass | Job completed - Repair numerous toilet and tap leaks on campus
MSA-DTWD | WA3821593 | House 15 - Water meter leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 30 Nov 2020 | 2020-12-03 17:00:00 | 2020-12-03 14:00:00 | Pass | Job completed - Replace leaking water meter to house 15
MSA-DTWD | WA3821601 | Lvl 1, Room B162-- backflow leaking | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-02 16:43:00 | Pass | Install double check valve
MSA-DTWD | WA3821637 | Lvl 2, store adjacent to server room- new battery swollen | Perth Campus B1 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 30 Nov 2020 | 2020-12-07 17:00:00 | 2020-12-07 15:00:00 | Pass | Replaced 2x 7AH batteries.Disconnected batteries due to heating up.FIP - fault zone 36 - electrician investigated. Recommend to be decommissioned and system wired to main FIP.
MSA-MRWA | WA3821662 | Vesda 1 fault on panel outside server room | Road Network Operation Centre (RNOC)-Main Building-Second Floor-Server Room | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Nov 2020 | 2020-11-30 23:43:22 | 2020-11-30 21:00:00 | Pass | Callout due to level 2 gas sip in fault liased with Brendan from programmed and got key access. Found vesda 2 different vesda from after hours callout on 29/11/20, which was vesda 1 had gone into fault and required filter to be replaced. Replaced filter and left system normal.
MSA-DCA | WA3825179 | plant room - low compressed air pressure (part of fire alarm/monitor system) | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Equipment | Compressors, Generators (EQ) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 17:00:00 | 2020-12-16 14:30:00 | Fail | Air Dryer on Pneumatic Plant iced up in vessel. Defrosted and opened bypass slightly to guarantee flow to Fire Pumps. In discussion with manufacturer regarding sizing and application. Pressure at Fire Pumps at acceptable levels. Alarms cleared.Monitoring.Replaced existing Thermostatic Controller with new controller.
MSA-DCS | WA3824776 | MPU (8) - M13 blocked toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-02 12:30:00 | Pass | 1/12/20: waited for access into MPU, told to come back tomorrow by unit S/O.2/12/20: held up in unit for 30mins before commencing work
MSA-DCS | WA3824828 | gatehouse pedestrian gate stentofon not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-01 11:36:00 | Pass | Faulty intercom pedestrian door external, swap the unit from control room ( intercom not being used ). Test the intercom,ok and back to normal operations.
MSA-DCS | WA3824836 | Unit 7 regi oven making a grinding sound | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 01 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-08 14:40:00 | Fail | Fitted new thermostat, test operation ok now.
MSA-DCS | WA3824839 | CCU (11) - C6 Cell C6 toilet cistern constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-11 10:30:00 | Fail | 10/12: planned to compete works but a few priority 1 jobs came through in MPU (punishment unit) , going back on 11/12 to complete this work
MSA-DCS | WA3824877 | medical centre safe will not open | Banksia Hill Detention Centre | GMP-BR- HO | Security | Safes (SE) | AAA Ability Locksmiths | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 08:22:20 | 2020-12-01 10:15:00 | Pass | Attend site. Gain entry and power cycle to re-set. Tested ok and functioning normally.
MSA-DCS | WA3824888 | Staff Gym, Old Front Gate- Male toilet leaking from base, male showers & basins blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 08:28:10 | 2020-12-01 15:15:00 | Pass | Replaced kee seal, flexi And leakinf inlet valve in the rhs cubicle. Shower and basin drains draining properly
MSA-DCS | WA3824892 | Unit 1, Cell 9- TV point damaged | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-07 14:00:00 | Fail | Attended site and replaced Unit 1 Cell 9 with 1 x MATV point. All tested and replaced and working ok.Job completed
MSA-DCS | WA3824990 | laundry No2 washing machine does not spin | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 09:33:52 | 2020-12-08 14:00:00 | Fail | Attended site found cold water valve faulty on washer #2, returned to replace valve
MSA-DCS | WA3825073 | ISU C wing near table smashed sash window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2021-01-27 12:45:00 | Fail | BROKEN WINDOW RE GLAZED
MSA-DCS | WA3825135 | Unit 8, Back of D Wing Yard- Burst pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 11:10:17 | 2020-12-02 23:00:00 | Fail | Turned the water off to the whole site. Dug up and exposed leaking pipe. Fixed the leaking pipe and installed new valve.
MSA-DCS | WA3825184 | Kitchen, Hot water system - red top of tap is broken, tap dripping, see notes below | Rockingham Justice Complex | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-03 10:53:00 | Pass | Replaced broken tap to RHeem BWU .
MSA-DCS | WA3825201 | Unit 1, Cell 9- Cisten outlet valve is damaged where outlet rubber is attached | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-04 16:20:00 | Pass | Replaced outlet valve and wahser
MSA-DCS | WA3825209 | stores , camera 1 - not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-04 15:33:00 | Pass | Re established communications between switch and camera, changed camera IP gateway as dropping out, monitored for 24 hours with no further dropouts.
MSA-DCS | WA3825270 | Unit 1, Control Pod passage wall- Officer Security Emergency Push Button Broken | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 13:08:16 | 2020-12-03 09:49:00 | Fail | Replaced damage duress button with new and test ok. Job completed
MSA-DCS | WA3825286 | unit 2A cell 5 bedside light faulty not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 14:00:00 | Pass | Replaced light fitting
MSA-DCS | WA3825304 | unit 2B pod 1 kitchen HW urn tripping out - white zip 5LT | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 13:39:10 | 2020-12-22 09:10:00 | Fail | 2.12.2020 replaced element and filter, power went out so ordered in new pcb on arrival once part had come in unit was working ok.. so did not need to change the PCB ...A40184149K Zip Autoboil Unit Unit working okay. Spoke with unit manager and site contact who reported defect.
MSA-DCS | WA3825320 | Bootshop, workshop- Fire sprinkler is badly rusted and is leaking. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-04 15:57:00 | Pass | Attended site and identified leaking pipework Spoke to maintenance supervisor and wanted to remove pipe completely as stairs were getting deleteDrained system and removed pipework. Plugged off from elbow. Refilled system and deisolated FIPWhile refilling had other issues as another contractor had hit a fire main
MSA-DCS | WA3825330 | Unit 2, Cell A4- Broken & Cracked light switch | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 13:54:38 | 2020-12-02 11:30:00 | Pass | Replaced light switch cell a4 unit 2
MSA-DCS | WA3825452 | Infirmary CCU dayroom- INF Q2-Dayroom Duress false alarm is active needs to be reset | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 15:00:00 | Pass | Rectified and fixed damage cable, replaced faulty EOL. Job completed
MSA-DCS | WA3825461 | Gatehouse - control for doors: Gate Senior Officer cannot open any doors on system | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Dec 2020 | 2020-12-01 23:41:00 | 2020-12-02 11:45:00 | Fail | Attended site checked and found Gallagher workstation in front entry command Center can’t be login. Located problem to be software issue. Reinstalled Gallagher command Center and tested all ok after.
MSA-DFES | WA3824880 | FF/Disabled Toilet (Room 4)- Toilet Cistern slow to fill after flush and slight leak into bowl | CFRS Malaga | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-03 08:00:00 | Pass | Investigate slow filling toilet/leaking toilet located disabled toilet Malaga FSIsolate water supply and remove outlet valve, supply and install new outlet washerRemove old inlet valve, supply and install new performa inlet valveReinstall all parts and test operation, checking thoroughly for leaksPack up and clean up worksite
MSA-DFES | WA3824909 | Compressor & Rear Air Cond Room- 4 x external doors rotting from water damage, see notes below | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-15 11:15:00 | Fail | New external rebated double doors have been fit on to the compressor building. 2 x sets of double doors have been installed with colour match paint to existing paint colour.Doors were installed using existing door hardware.
MSA-DFES | WA3825046 | Rear store room, Garden tool store- Door is hard to open and even harder, see notes below | CFRS Claremont | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 14:30:00 | Pass | Eased sticking door
MSA-DFES | WA3825217 | Applied Training Ground. - Leaking hydrant | FESA RHQ - Forrestfield | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-03 10:00:00 | Pass | Attend site and rectify leaking hydrant
MSA-DTAG | WA3824818 | 1987 L3 Technician to isolate FIP at 07.00am Saturday 5/12/20 & de-isolate at 17.00pm - see notes | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 01 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-05 17:30:00 | Pass | Isolated at 07:00De-isolated at 17:00
MSA-DTAG | WA3824931 | Level 3 Hay Street- Fault displayed on EWS panel | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 12:30:00 | Pass | Checked EWIS system fault. Could not determine. Require 2x technicians after hours to investigate further and clarify fault
MSA-DTAG | WA3825107 | 1903 lower ground level Lights out in Court 3 Holding Cell. Very low visibility. | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 0 | CLOSE | 01 Dec 2020 | 2020-12-01 14:51:30 | 2020-12-01 12:00:00 | Pass | Repaired 1x light fitting in court 3 holding room
MSA-DTAG | WA3825164 | Male & Female Public Toilets,Hay Street End- Male Urinal Blocked & Female toilet flush not working | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 17:00:00 | 2020-12-02 09:00:00 | Pass | COMPLETED
MSA-DTAG | WA3825168 | Lvl 4- Disabled & Female Public Toilets, Hay Street End- Toilets blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 17:00:00 | 2020-12-02 09:30:00 | Pass | COMPLETED
MSA-DTAG | WA3825171 | Lvl 5, Male Public Toilets, St Georges Tce End- Toilet blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 17:00:00 | 2020-12-02 10:07:00 | Pass | COMPLETED
MSA-DTAG | WA3825423 | Custody Toilet- Duress alarm is sticking when reset. | Armadale Courthouse | GMP-BR-HO | Security | Monitoring (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 14:30:00 | Pass | 2/12/20 - Ryan Vesty, Joshua ParkChecked duress in custody male toilet.Device operating correctly.Reset and checked signals, all ok.
MSA-DTAG | WA3825436 | Old Court House Grd Lvl Electrical Panel opposite the kitchen - key required | Supreme Court | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-08 13:36:00 | Fail | Attended site, Anna not on site, and security didnt know location they walked me around for awhile trying to find, finally shown location by Natalie, viewed lock and will need to return with new lock. Date on site: 02/12/2020 Time on site: 14:25 - 15:25 Attended site and replace electrical panel lock as required for correct operation Date on site: 08/12/2020 Time on site: 10:45am - 11:15am
MSA-DTAG | WA3825466 | No power to site, buildings in area have power | Supreme Court-Supreme Court Building | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 0 | CLOSE | 01 Dec 2020 | 2020-12-02 00:04:06 | 2020-12-03 05:30:00 | Fail | Fault rectified all in working order
MSA-DTWD | WA3824760 | L1 B101 Zip Boiler won’t stop boiling, currently turned off | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-07 14:20:00 | Fail | System continuesly boiling on arrival. Opened unit to examine. Solenoid failed but unable to change as main isolation broken. Will return to unit after solenoid fixed. Steve has put a P1 for the plumber and will call us ASAP to return to fix tomorrow Replaced inlet solenoid run and test
MSA-DTWD | WA3824788 | A block L3 damaged ceiling tiles A305.A325.A333 | East Perth Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 01 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-03 11:00:00 | Pass | install new ceiling tiles to affected areas
MSA-DTWD | WA3824948 | BLD 839, toilet- Faulty power point | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-14 00:00:00 | Fail | completed dat before according to Damian - repaired faulty power point
MSA-DTWD | WA3824984 | Alarm continually reporting to Ed. Sec. from system 1501 | Rockingham Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 13:30:00 | Pass | 02/12/2020Looped out old siren in old tecom panel A block
MSA-DTWD | WA3825026 | Lift not working properly (front buttons are out of service) | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMP | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-01 13:15:00 | Pass | Buttons all working. Lift runningTo be closed out at $0
MSA-DTWD | WA3825033 | Plant room air con ceased condenser water pump | West One Services | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-16 16:30:00 | Fail | Attended site and completed pre-start paperwork. Spoke to Kim the FM who informed me chiller 1 CHW pump had been intermittently tripping on its contactor OL. Inspected and check amp draw, pulling 13.5amps and not pulling excessive inductive amps on start up. OL set to 23 amps. Suspect the contactor and OL are faulty and require replacement.
MSA-DTWD | WA3825038 | William St entry - Inner Auto door not working | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 12:05:00 | Pass | Inspected door and found sensors board was heavily corroded, replaced 1x PIB yellow board and rewired the new sensors cables, reset the door, checked all fixings, tested door operation a number of times, all working fine.
MSA-DTWD | WA3825116 | Lift 5 - Main panel not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-01 13:29:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3825118 | Lift 6 - Main panel not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-01 13:29:00 | Pass | Buttons now working correctly Waiting for ups to be approved
MSA-DTWD | WA3825120 | Lift 7 - Main panel not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-01 13:29:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3825131 | House 18 - Faulty outside waterproof powerpoint | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-03 00:00:00 | Pass | completed a day early according to Damian - faulty cable & GPO replaced
MSA-DTWD | WA3825204 | Air con plant room - faulty chilled water pump | West One Services | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-11 12:30:00 | Fail | Re-install Chilled water pump 1 laser align new motor & test
MSA-DTWD | WA3825264 | Training Room 4 - overhead projector issue, possible globe failure | West One Services | GMP-BR | ICT/Audiovisual | General AV works (AV) | K2 Audiovisual Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-07 10:57:00 | Fail | Attended Department of Training and Workplace Development on the afternoon of 07/12/20 in order to investigate issues with projector in Training Room 4.Upon inspection several faults were identified;1.Projector severely out of alignment with respect to fixed pull-down screen.2.Video input signal tracking significantly offset.3.Video feed from resident PC displaying colour incorrectly (pink tinge).4.Video feed from laptop fly-lead displaying colour incorrectly (magenta tinge).5.Laptop fly-lead lacking audio connectivity.6.Speakers cramped together in confined cabinet space (left and right channels not being utilised separately).7.VGA signal switcher not functioning as intended.The following actions were undertaken to resolve these issues;1.Screen lowered slightly to facilitate correct alignment and aspect ratio (now protrudes slightly below whiteboard pen-tray but original location did not allow for top of image to be displayed properly due to projection impeded by l
MSA-DTWD | WA3825276 | Creche - Lights have blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-02 10:30:00 | Pass | Replaced faulty PL lamps throughout crèche, lights all working *** job complete ***
MSA-DTWD | WA3825297 | Tower block, level 1 - zone 85 in fault (reset required ) - server room | West One Services | GMP-BR | Security | Security Management System (SE) | Casa Security Pty Ltd | 3 | CLOSE | 01 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 11:45:00 | Pass | REPLACED BATTERIES TO ZONE 19 SMOKE ALARM IN ECU BLOCK.
MSA-DTWD | WA3825301 | B Block, BG21 (Staff Room in Beauty)- Intermittent tapping noise coming from ceiling, see notes belo | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 17:00:00 | 2020-12-02 10:00:00 | Pass | Signed in and booked out the keys, accessed the fresh air louvers in the ceiling space of the office. Lubricated the fresh air vains, they were creaking when opening and closing.
MSA-DTWD | WA3825315 | light on parts-washer has disconnected itself exposing wires | Kwinana Automotive Centre | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 01 Dec 2020 | 2020-12-02 17:00:00 | 2020-12-02 10:15:00 | Pass | Attended site and signed in. Located parts washer. Found broken light fitting on end. Removed parts and reterminate light fitting. Replaced shorted onto light. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3825354 | Lecture theatre, G Block- Faulty centre bank light switch | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 16:00:00 | Pass | Attended site and signed in. Located g block lecture theatre. Found light switch at desk. Turned on lights and found to flicker. Dimmer on the circuit and fluros are not dimmable. Put dimmer to max as it’s always been and lights work fine. Showed site. All lights okay. Job complete
MSA-DTWD | WA3825367 | 6 Painting and Decorating, Office / Store- Water leaking onto ceiling | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2021-02-26 11:15:00 | Fail | BRAF declined, no repair works completed.
MSA-DTWD | WA3825374 | D Block - Leak from pump in Black Water treatment plant room | East Perth Campus | GMP-BR | Mechanical Services | Pumps (MS) | Daniel Chrisp Pty Ltd | 2 | CLOSE | 01 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-02 15:12:00 | Pass | Attended site 02/12/2020 called in Plumber for special equipment to complete work.
MSA-DCA | WA3825786 | Tap in maintenance room is leaking | Swan Bell Tower-Main Building-Level 3 | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-02 13:10:00 | Pass | Rewashed hot and cold tap
MSA-DCA | WA3825797 | Men’s toilet tap is leaking quote a bit. Tap has been turned off under basin for now. | Swan Bell Tower-Main Building-Level 1 - Disabled toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-02 14:00:00 | Pass | Rewshed cold tap
MSA-DCA | WA3825836 | Crew and King cafe broken light fitting to be replaced/repaird - Ken Thomas has originonal | His Majesty's Theatre-Theatre Building-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-29 10:24:00 | Fail | Instruced to close breakdown and provide quote for repair on 24/12/20
MSA-DCA | WA3827884 | retic stuck solenoid valve | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-04 12:15:00 | Pass | fixed and tested all replaced sprinklers
MSA-DCS | WA3825637 | INF (10) - Day Room red fire door requires key to pull door open scrapes on bottom of floor | Casuarina Prison | GMP-BR- HO | Building | Fire Door (BU) | Midolo Building Services | 3 | CLOSE | 02 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-17 14:00:00 | Fail | DOOR PLANED DOWN & RE FITTED
MSA-DCS | WA3825746 | Unit 2, Cell 59- broken glass window | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-14 13:15:00 | Fail | CELL WINDOW RE GLAZED
MSA-DCS | WA3825763 | Unit 2, outside lower landing- toilets leaking around base | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2021-01-19 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3825810 | Unit 1 cell D11 Cell D11 plumbing, toilet and sink blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Dec 2020 | 2020-12-03 08:59:42 | 2020-12-02 17:55:00 | Pass | Unblcoked toilet and basin. Job delayed due to no escort
MSA-DCS | WA3825814 | Unit 14, A & C- Filter in A/C dayroom drinking fountain | Casuarina Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-03 12:01:00 | Pass | No filter here Chiller working okay ATTENDED TO ARCUS CHILLER - CHECKED UNIT (NOT FILTERED) ALL WORKING AND CHILLING OK A40191350C
MSA-DCS | WA3826047 | Unit 6, Cell D6- Door hinges are worn | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-03 12:00:00 | Pass | Replace hinges, door plate, lock, and weld on strike.
MSA-DCS | WA3826054 | Unit 6- Front glass door bottom drop bolt lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Dec 2020 | 2020-12-03 11:26:04 | 2020-12-03 09:45:00 | Pass | 02/12/2020 Attend site. Faulty lock already removed by site. Replacement parts required.03/12/2020 On site. Replaced lock and cylinder as required.
MSA-DCS | WA3826161 | External Stores - Dryer making a squealing sound | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-17 08:30:00 | Fail | pick up dryer and transport to the CLS workshop. Strip and trace fault to pulley, belt and bearing assembly. Replace all, reassemble and test, tests ok.
MSA-DCS | WA3826244 | outside fence sewerage line blocked in the polly pipe at the tanks | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 17:24:36 | 2020-12-03 12:15:00 | Fail | Attended site,Investigate blockage to sewer system at sewage farm.Dismantle sections of pipe and used jet wash to clear gravel from sewer lines. Reassembled pipework and restored system function. Cleaned up and tested works on completion
MSA-DCS | WA3826266 | laundry - faulty GPO | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 10:30:00 | Pass | Replaced 3x RCDs in laundry area
MSA-DCS | WA3826268 | Admin - Bug Zapper in staff luch room not working. | Casuarina Prison | WSM-BR-SITE | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-04 09:00:00 | Pass | Picked up replacement parts. Repaired faulty bug zapper in admin lunch room
MSA-DCS | WA3826275 | MPU(8), Day Room- door ways, weather strips (Fly Flaps) are damaged/have large gaps, see notes below | Casuarina Prison | WSM-BR-SITE | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-16 15:00:00 | Fail | MEASURMENTS TAKEN AND GIVEN TO TEXTILES IN INDUSTRIES TO MANUFACTUREPRISON MAINTENANCE TO FIT ONCE MADE
MSA-DCS | WA3826279 | Unit 5, Cell A1- Toilet not flushing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-07 10:30:00 | Pass | Nill
MSA-DCS | WA3826303 | Unit 10, main entry door - lower hinge is nearly off | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 19:09:33 | 2020-12-16 10:30:00 | Fail | 02/12/2020 Attend site. Door made safe but additional parts needed to completely restore normal function. 16/12/2020 On site. Fit new nutserts, re-fix hinges and realign door. Normal function restored.
MSA-DCS | WA3826319 | Front desk PC not displaying | Rockingham Justice Complex | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 17:30:00 | Fail | Moved Gallagher PC to new location. Cabled to new location. Restored PC.Showed client basic operation.Job completed
MSA-DCS | WA3826323 | System frequently false alarms | Rockingham Justice Complex | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 15:00:00 | Pass | Job completed - Attended site. Checked Gallagher system, found Controller 2 offline. Restored Controller 2, reviewed report for any falsealarming devices. No identifiable faulty device. Advised to get information from Monitoring for any false alarms
MSA-DFES | WA3826021 | Front entrance doors not opening properly first thing in the morning. May be a program issue | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 09:30:00 | Pass | 4/12/20 - Dylan ParslowUnable to find any fault. Recommend revisit to watch door switch over.7/12/20 - Dylan ParslowFault appears to be with auto door hardware.Day/night and open signal relays working correctly.Swapped relay as requested.
MSA-DFES | WA3826070 | Toilet is continually leaking water into the bowl & not properly shutting off on operation of button | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 11:00:00 | Pass | Replaced cistern with new.
MSA-DFES | WA3826339 | Front Engine Room Door - on career side- jammed half open or closed | CFRS Armadale | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 20:09:43 | 2020-12-07 18:00:00 | Fail | (02/12/2020) - Work NoteFault Found: Attended site as per work request and found 3rd hinge bent and roller wheel bent and out of track on RHtrack (front of building LH automatic sectional overhead door viewed from inside )removed Non finger safe hinge No3and replaced with new hinge and new roller wheel , checked all other hinges and roller wheels all working , straightenedup bent lip on RH track . cables stretched and making door run out of level , relevel door on RH cable to allow door torun level in tracks.Realigned top LH bend , tried and tested door several times working ok .Parts used: steel sterling No3 hinge and roller wheel .(07/12/2020) - Work NoteDoor has bent #3 hinges againThis issue will keep happening until the door is replacedI have isolated and tagged out the door
MSA-DTAG | WA3825647 | Security cameras down after the power outage for the whole building | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 11:29:52 | 2020-12-02 13:00:00 | Fail | job completed - Main Custodial Security workstation appears to be giving persistent faults with the graphics displays dropping off. Ireconfigured Quadro P400 graphics ports and restored monitor setup to correct functionality, however I would highlysuggest upgrading this client machine to a simpler Dell Z2 Mini desktop at the user end, as suppose to the currentHDMI/USB extension leading back to client desktop in the rack
MSA-DTAG | WA3825930 | All the rooms on the graphics are flashing pink or purple in colour | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 13:58:50 | 2020-12-02 15:30:00 | Fail | Attended site. Met with Peter Sermon and discussed alarm screen issue. Adjusted Broadspectrum Operator Group privilege and tested with Level 10 Security at DMJC Building. Alarms all sorted and OK. Job completed.
MSA-DTAG | WA3825959 | Irwin St - Magistrates external swipe entry door frame is loose – door next to underground car park | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-03 10:00:00 | Pass | DOOR FRAME - RESECURED
MSA-DTAG | WA3826286 | 1987- Electrician to attend at 18.00pm Wednesday 2 Dec to assist Western Power high voltage techs | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 02 Dec 2020 | 2020-12-03 17:00:00 | 2020-12-02 21:30:00 | Pass | Met western power on site and stayed onsite till fault was found- fault was found to be cable on barrack street
MSA-DTAG | WA3826328 | 1987, Lvl 1, Sheriff’s Office- Carpark near Governors residence. The pavement has sunk. | Supreme Court | GMP-BR-HO | Paving & Roadworks | Paving (PR) | Midolo Building Services | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-14 13:00:00 | Fail | PAVING REPAIRED TO PROPER LEVEL
MSA-DTWD | WA3825753 | Lvl 2, Student services Staff Room- Tap is leaking | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-03 16:27:00 | Pass | Fix tap and replace filter
MSA-DTWD | WA3825825 | A Block, Toilets- Exhaust fan not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-07 10:15:00 | Pass | Attended site and signed in. Got keys from office. Checked all switchboards inside for fan control. Located roof access. Put on harness to go on roof. Found fan controls on roof. Ran through system and found all system to be running. Located fan on roof and removed covers. Found motor running but no belts attached. Replaced with new belts on motor 1 and 2. Reinstalled cover to fan. Tested all systems go. Checked for ventilation downstairs. All okay. Signed out. Job complete
MSA-DTWD | WA3825980 | Room T052- External rubber vertical glazing beads randomly falling out 2x to date. | Murdoch Campus | GMP-BR | Glazing | Window Glass (GL) | WELLARD GLASS | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-02 14:00:00 | Pass | re silicone 2 windows and ends of some windowds
MSA-DTWD | WA3826057 | Block 7 - Hand basin in male toilet cubical has cracks | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2021-01-11 16:00:00 | Fail | Had to wait to holidays to isolate water and remove sink install new sink drain and mini stops and mixer
MSA-DTWD | WA3826089 | garage one of the roller door has rolled off tracks and damaged | Perth Campus B1 | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 15:49:06 | 2021-01-15 13:33:00 | Fail | 2/12/20 - Damaged door IP is 1091911. Door requires new curtain due to damage, managed to get curtain back into guides and straightened as must as possible. Door is now secure.BRAF to be raised for curtain replacement.See attached images for details.15/1/21 - Remove damaged Curtain and replace with new, reset motor and limits , door tested working well
MSA-DTWD | WA3826113 | 2 Perspex sheets that have fallen from the roof of the Glass House | Murdoch Campus | GMP-BR | Roofing | Polycarbonate (RF) | ARGOSEE GREENHOUSE TECHNOLOGY PTY LTD | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-08 11:30:00 | Fail | Job completed - replace 2 vent panels
MSA-DTWD | WA3826201 | A block cold water fountain dispencing warm water | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-03 12:20:00 | Pass | Unit not cold on arrival. Power had tripped at main power board. Reset and allowed unit to power up. Was all ok. Got to temperature and then stopped as should. Issue may be from different appliance. Old electrical and could possibly be multiple things on that circuit. If unit does trip again. Replacement recomMended
MSA-DTWD | WA3826316 | Art Gallery - Air Conditioning not working | Perth Campus B5 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-03 15:00:00 | Pass | Found the gallery to warm , adjusted the thermostat for aircon 2 , temperature coming down. Will monitor over next few days while doing other work.
MSA-DTWD | WA3826346 | Level 1 - 111 beauty change area - leaking toilet | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-03 16:29:00 | Pass | Replace outlet valve that was broken and leaking.
MSA-DTWD | WA3826349 | Level 5 - Main plant room has a roof leak | Perth Campus B2 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 02 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-04 13:15:00 | Pass | Investigated area, found gap in cladding joints. Found silicone seal to flashing perished, Found pipes penetrating cladding. Carried out repairs
MSA-MRWA | WA3826039 | power points out back in the warehouse office have fallen out of the wall. | Jandakot Depot-Warehouse-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-04 14:15:00 | Pass | Attended site and signed in. Completed jsa. Found Workshop office. Found gpos hanging out of wall and additional data outlet due to inappropriate fixings. Installed 3x c clips and re fixed gpos and data outlets to wall. Looked for barcode number. Could not add to system on asset. No door frame location or barcode to add. Added in images. Signed out. Job complete
MSA-MRWA | WA3826263 | Roller door not functional, please investigate and remediate.- See notes below | Western Vent Building-Main Building | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 02 Dec 2020 | 2020-12-02 17:38:39 | 2020-12-02 16:56:00 | Pass | job completed - Safety beams have failed.new like for like beams installed.
MSA-DCA | WA3827141 | Large mechanical stage doors unresponsive | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Storage Water Tanks Room - Access via Loading Bay | GMP-BR | Building | Automatic Doors (BU) | Barclay Engineering | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-04 16:30:00 | Pass | Burnt out hydraulic pump motor
MSA-DCA | WA3827691 | Graffiti to be removed from stone table | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-16 10:00:00 | Fail | Graffiti removed
MSA-DCS | WA3826943 | West Kimberley Prison Perimeter cameras 18/20/21/22 down | West Kimberley Regional Prison | WSM-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Dec 2020 | 2020-12-03 12:02:06 | 2021-08-31 09:30:00 | Fail | cameras has stayed online for more than 30days. job complete.
MSA-DCS | WA3827067 | unit 4 B wing Intercom; buzzing noise from speaker | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 07:26:31 | 2020-12-03 12:45:00 | Pass | Calibrate amplifier unit 4 and test all wings PA, job completed.
MSA-DCS | WA3827069 | unit 1 C14 Prisoner used cell call system and the whole conversation came over the PA for the unit | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 07:29:12 | 2020-12-03 10:45:00 | Pass | Attended and test the celll call systems at Unit 1 C14, systems work as normal. Job completed.
MSA-DCS | WA3827074 | unit 2 cell 29 light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-08 11:00:00 | Pass | Replace light fitting
MSA-DCS | WA3827078 | stores light fitting not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 08:30:00 | Pass | Investigate and repair faulty stores light fitting
MSA-DCS | WA3827081 | Unit 1 D4 toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 07:40:47 | 2020-12-03 13:10:00 | Pass | unblocked toilet
MSA-DCS | WA3827084 | Unit 3 B11 toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 07:43:08 | 2020-12-03 14:10:00 | Pass | Unblcoked toiler, replaced inlet valve, flexi, washer
MSA-DCS | WA3827092 | abattoir officers toilet window exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-11 12:30:00 | Fail | Replace toilet exhaust
MSA-DCS | WA3827094 | unit 3 b wing dayroom ceiling fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 08:30:00 | Pass | Repair Unit 3 dayroom ceiling fan
MSA-DCS | WA3827097 | unit 3 c wing toilet exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-22 11:00:00 | Fail | Replace exhaust fan Unit 3, C Wing
MSA-DCS | WA3827107 | New canteen Repair concrete in entrance door way | Hakea Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo Building Services | 2 | CLOSE | 03 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-15 13:30:00 | Fail | CONCRETE REPAIRS MADE, NEW THRESHOLD FITTED
MSA-DCS | WA3827114 | CCU (11) D4 - door broken,Service door to Cell D4 (in infirmary garden) is damaged from being left | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2021-05-20 09:30:00 | Fail | NEW DOOR INSTALLED
MSA-DCS | WA3827115 | CCU (11) - Cell D4 toilet is constantly running. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-14 14:00:00 | Fail | Nill
MSA-DCS | WA3827123 | CCU (11) D5 - toilet cistern constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-14 12:30:00 | Fail | Nill
MSA-DCS | WA3827128 | SOG Base, senior officers desk - indigo vision control center frozen | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | COMPFIN | 03 Dec 2020 | 2020-12-03 12:13:09 | 2020-12-03 10:30:00 | Pass | Work performed by Cian O'Halloran 03/12/2020:Attended site. CCTV system frozen. Carry out hard reset of hardware. Rebooted system. All working ok.Job completed.to be closed off at $0Work completed under Warranty.
MSA-DCS | WA3827137 | Lobby and Corridoor Door near non contact visits room Latch gets stuck when using Fob | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-14 10:45:00 | Fail | Replaced faulty electric strike with new and tested ok. Job completed.
MSA-DCS | WA3827147 | Unit 1, Cell B1, B3, B5 & B6 - toilets blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 08:33:31 | 2020-12-03 12:15:00 | Pass | Unblocked lhs of B wing.
MSA-DCS | WA3827189 | The reticulation for the entire Prison is not working and the reason is unknown. | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 09:02:20 | 2020-12-03 12:30:00 | Pass | RESET AND TEST RAN FOR PERIOD OF TIME AND SYSTEM OK
MSA-DCS | WA3827211 | L1 reception L4 open area 2 x lights out | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-04 10:30:00 | Pass | Fixed 3 x faulty lights
MSA-DCS | WA3827229 | SITE COST Laundry- Hot water unit is not working | Wooroloo Prison Farm | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Dec 2020 | 2020-12-03 13:41:51 | 2020-12-03 12:11:00 | Pass | Attended site,Investigated hot water system failure to laundry. Identified gas regulator shut out and reset to restore gas flow to units. Restarted hot water systems and restored hot water.
MSA-DCS | WA3827295 | Gate house - Sliding Door sensor is not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 10:15:14 | 2020-12-03 15:25:00 | Pass | Sliding door sensor fault issue belongs to other contractor, advice officer on site.
MSA-DCS | WA3827308 | Interview room 2 door - unable to unlock from outside (doesn't lock from the inside) | Maddington (South East Metro) | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 10:20:46 | 2020-12-03 13:40:00 | Pass | Attended site, no job done, advised that they need to ring parker black for their system
MSA-DCS | WA3827320 | Gatehouse - door 1 does not close properly (door switch) | Albany Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Dec 2020 | 2020-12-03 18:26:42 | 2021-01-12 10:30:00 | Fail | Lock replaced by Prison officer locksmiths. Replacement lock (Custodial Strike FES112) obtained from site critical Spares Cupboard.12/01/2021 10:30. New FES112 electric strike delivered to site critical Spares Cupboard today.
MSA-DCS | WA3827328 | Unit 2, Cell B10- blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 11:30:00 | Pass | Nill
MSA-DCS | WA3827364 | SITE COST kitchen side entry door leaver handle is ready to snap off - see notes | Wooroloo Prison Farm | WSM-BR-SITE | Building | Doors (BU) | ACE LOCK & SAFE | 0 | CLOSE | 03 Dec 2020 | 2020-12-03 14:45:36 | 2020-12-03 13:15:00 | Pass | Replaced external handle on entry door to Kitchen
MSA-DCS | WA3827367 | unit 2C and 2A verandah lights not turning off | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 12:30:00 | Pass | Replaced faulty PE cell and re-wired auto switch
MSA-DCS | WA3827371 | Health Admin- Air Con is switched on but not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 09:19:00 | Pass | Carried out checks on airconditioning still running ok at present.
MSA-DCS | WA3827411 | SITE COST SHU (9) - East Staff key won't unlock the Yard Door for prisoners recreation. | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 03 Dec 2020 | 2020-12-03 15:04:31 | 2020-12-03 13:45:00 | Pass | Open jammed door, service lock, replace bolt throw, replace hinges.
MSA-DCS | WA3827415 | Unit 6 A19 Toilet leaking badly needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 11:09:46 | 2020-12-04 08:21:00 | Pass | Fixed leaking toilet
MSA-DCS | WA3827418 | Unit 6 A wing day room Tap centre spout leaking when tap is turned on needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 11:13:23 | 2020-12-04 09:05:00 | Pass | Replace spout
MSA-DCS | WA3827491 | SITE COST CCU- monitors for unit 1 & unit 6 not working | Hakea Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Dec 2020 | 2020-12-03 15:47:49 | 2020-12-03 14:43:00 | Pass | Rectified and fixed fault on monitor 1 CCU, job completed.
MSA-DCS | WA3827497 | Boilerhouse, Workshop - Main water line pressure valve is passing water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 11:44:21 | 2020-12-11 14:30:00 | Fail | COMPLETED
MSA-DCS | WA3827590 | Amenities - Air Con is not working (very hot in area) | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 12:54:04 | 2020-12-07 08:30:00 | Fail | Carried out checks on airconditioning, system still running ok at present.
MSA-DCS | WA3827614 | Unit 7, S2 - Viewing hatch, (Judas hatch) window broken needs repair | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 13:09:23 | 2020-12-04 10:30:00 | Pass | VEIWING HATCH GLASS REPLACED
MSA-DCS | WA3827639 | Gate control - M-DAS server computer issues | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 13:34:37 | 2020-12-03 17:48:00 | Pass | Repair peripherals driver issues on master and reboot. Slave server comms error required reboot for fix. All tested ok and alarms cleared.
MSA-DCS | WA3827642 | unit 2B self care urinal continues to run | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 13:38:21 | 2021-01-18 15:00:00 | Fail | Installed new urinal solenoid and sensor
MSA-DCS | WA3827656 | Unit 3, C2 - toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 13:58:06 | 2020-12-03 16:20:00 | Pass | unblocked toilet
MSA-DCS | WA3827657 | Unit 1, Cell C2- C/breaker W14 will not reset, see notes below | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 13:57:56 | 2020-12-03 16:00:00 | Pass | Repaired cell power
MSA-DCS | WA3827660 | Gate house, control room carpet worn out | Karnet Prison Farm | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2021-05-21 13:30:00 | Fail | OLD CARPET TILES LIFTED, SUPPLY & INSTALL NEW CARPET TILES
MSA-DCS | WA3827688 | kitchen potato peeling machine faulty | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-14 14:30:00 | Fail | Kitchen Potato Peeling Machine faulty. Check peeler, remove seized grinder plate. Motor not running. Remove to workshop. Dismantle, repair motor & VSD. Assemble & test. Return to kitchen.
MSA-DCS | WA3827690 | kitchen mixer wisk bladed faulty | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-21 15:00:00 | Fail | Kitchen mixer whisk blade faulty. Order new whisk. Pick up & return.
MSA-DCS | WA3827698 | Gate house, Entry to reception door - (glass sliding doors) door intermittently fails to open/ fails | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 15:12:47 | 2020-12-04 12:24:00 | Pass | Anthony Calautti (04/12/2020) - Work NoteTravel to site. Inspect entry to reception door. Found door operational but intermittently not responding to sensors. Trace wiring through cable bundle and test access system. Also not locking. Access company already on site, Liase and found new system is now controlling lock mode.Test, all okay. Open not responding to command. Rewire, now okay. Bridge auto mode. Test operation, all okay. Still recommend replacing operator due to age and condition of existing (fitted 1996)
MSA-DCS | WA3827701 | Education- controller offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 15:19:53 | 2020-12-05 11:30:00 | Fail | Education Controller offline. Found IEC lead faulty from UPS to all devices. Devices work when switched over to Bypass mode. Replaced IEC lead, switched to UPS supply and powered all devices individually to prevent spike. All controllers and transponders back online communicating. Tested operation and all is in working order.
MSA-DCS | WA3827703 | Gym recreation- Controller off line . | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 15:21:55 | 2020-12-05 13:30:00 | Fail | Gym Controller offline & EC7. Checked and found no power to GPOs. Circuit Breakers all on in EC Cabinet and at GYM Controller. Found UPS Breaker back at Gate House was tripped. Switched breaker on and all equipment back online. Software download and config push to EC7 Gallagher Controller as EC7-EXP46.03 was still offline. Tested all equipment and all is in working order.
MSA-DCS | WA3827706 | MDAS Faults. MDAS is sending false readings across the whole site, see notes below | West Kimberley Regional Prison | WSM-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 15:22:39 | 2021-04-20 11:50:00 | Fail | All faults rectified - replacement parts delivered to site.SEME Goods Transmittal 90237498 GT 07.04.21Works complete - report to be submitted.
MSA-DCS | WA3827716 | Unit 5, pre-release perimeter fence (barbwire fence) has some stapped/rusted poles at ground level. | Bunbury Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 12:15:00 | Pass | 07/12/20 - CompleteInspect fence. Source material. Dig and install brace posts and bottom rail to support bottom of post.Posts completely rusted out bottom.
MSA-DCS | WA3827737 | Unit b Wing - B28 Blocked & B27 Leaking. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 22:02:00 | 2020-12-04 10:05:00 | Pass | Removed 20+ tampons in sewer line with drain machine
MSA-DFES | WA3827524 | Passageway, long side station officers ensuite - water leak through the wall, skirting damaged | CFRS Claremont | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-21 15:00:00 | Fail | Repair plumbingRepair tilingRepair skirting
MSA-DFES | WA3827578 | No Power to security alarm system key pad | Butler Career Fire Station | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 14:30:00 | Pass | Arrived on site at 13:45 to inspect security system. Found no faults and station knows nothing about job. Tracked job with Janine mcCombe. Found that there had been a mistake and some how the job is at Daglish FS. Signed out at 14:30
MSA-DTAG | WA3827423 | L3 JSO office billi tap isn't working, no lights turning on and no water coming out of tap | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 12:20:00 | Pass | Issue was rectified prior to arrival. However job was left open so we could check unit over. Unit working correctly. Fault log clearedAll ok
MSA-DTAG | WA3827533 | Lower G Level - Weather strips on doors to Court 8 are peeling away | Supreme Court | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-07 08:15:00 | Pass | RE SECURED STRIPS TO DOORS
MSA-DTAG | WA3827582 | Lower G Level, Custody area- Intermittent sound from alarms in custody area | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-03 17:30:00 | Pass | Attended site. Found Server and Workstations offline. Security advised Western Power cable fault and been on UPSsince 4am. Restored Workstations and Server and configured to auto restart once power was restored. Performedcomputer health check on all Workstations and Servers. Checked UPS and found no errors on display. Reconfiguredmonitors for Control Room, checked all cameras for live view and recordings all working correctly.Job completed.
MSA-DTAG | WA3827715 | Few sprinkler heads are damaged & 1 has popped off, see notes below | Rockingham Justice Complex | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-04 18:30:00 | Pass | Call out & Labour & Retic Parts
MSA-DTWD | WA3827054 | L1 carpark exterior rectify tree issues from Westernpower report 341563 -see notes | Leederville Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-15 08:00:00 | Fail | POWER LINE CLEARANCES COMPLETED.
MSA-DTWD | WA3827063 | Level 1 - William street entry & beauty - two card readers cracked & dislodged on wall | Perth Campus B2 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 03 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-03 15:00:00 | Pass | Replaced reader to 114 William St.Used reader backing from 114 to repaie the reader on 104 William St.Checked andctested both readers and confirmed mounting is still secure for both readers.Checked and conformed doorctransactions for both readers
MSA-DTWD | WA3827144 | B block B019 damaged GPO | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-04 14:15:00 | Pass | Replaced broken mounting block
MSA-DTWD | WA3827173 | Level 5, E528 - door handle tongue jammed | Perth Campus B1 | GMP-BR | Building | Doors (BU) | ADVANCED LOCK & KEY | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 15:25:00 | Pass | Repair handle to lock on E528
MSA-DTWD | WA3827182 | T block female toilet blocked ground floor near library | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 16:29:00 | Pass | unblocked toilet
MSA-DTWD | WA3827299 | Level 2, Male showers - Shower valve in male toilet is broken | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-03 16:31:00 | Pass | Replace broken taps
MSA-DTWD | WA3827337 | L1 room 105 return air grille broken | Perth Campus B2 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 03 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-04 11:30:00 | Pass | Picked up new egg crate grill, returned to site and removed the ceiling tile and cut down to size, refitted the grill and ceiling tile
MSA-DTWD | WA3827520 | Farm Yards- Various troughs leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-09 18:30:00 | Fail | job completed - Repair leaking troughs to farm paddocks
MSA-DTWD | WA3827531 | D block, Level 2, AMT area.- Multiple blown lighting | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-04 18:00:00 | Pass | Replace multiple tubes and starters in D Block
MSA-DTWD | WA3827542 | S8 Plant Room, AHU -1 activator tripping | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 03 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-09 12:00:00 | Fail | Arrived on site signed in. Checked in with facility. Gained access keys, and gathered tools and equipment, completed fault find on AHU 1 found actuator failing. Ordered and picked up new fitted and tested all ok. Cleaned up and completed paperwork and Signed out.
MSA-DTWD | WA3827564 | B Block, B101- Isolation tap to Zip Boiler that won’t turn off | East Perth Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-03 15:00:00 | Pass | replaced faulty isolation valve.
MSA-DCA | WA3827882 | retic zone 11 retic system | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 04 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-04 10:30:00 | Pass | Both garden beds at pica bar were flushed and working.
MSA-DCA | WA3827953 | multiple lights out with in square please investigate | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 04 Dec 2020 | 2020-12-04 17:00:00 | 2020-12-04 08:36:00 | Pass | Garden DB had a tripped RCBO that was controlling lights down toward james st. last weeks weather ingress i believe to be the cause. AGWA DB had a fuse cartridge with no fuse, this was replaced an all lights were on and working.
MSA-DCA | WA3828083 | Leak on urinal, coming from seal that joins the cistern down pipe to the inlet of the urinal | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Men's Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-08 12:55:00 | Pass | Replaced faulty rubbers on the urinal and on the flush pipe
MSA-DCS | WA3827915 | Unit 7 Cell S8 cracked window | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 07:05:24 | 2020-12-04 16:30:00 | Pass | CRACKED WINDOW REPLACED
MSA-DCS | WA3827918 | unit 8 C/D Dayroom light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-16 15:00:00 | Fail | Replaced broken lights in Unit 8 C/D dayroom
MSA-DCS | WA3827928 | Unit 9 C4 Sink Leaking from copper pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 07:23:13 | 2020-12-04 11:45:00 | Pass | Replaced broken nut on basine set
MSA-DCS | WA3827930 | Unit 13 - A & C A/C oven fan not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 07:26:20 | 2020-12-04 10:25:00 | Pass | Check both side units ovens to be working ok. check maintenance log, Unit A/C reported no fan, re-check ok.
MSA-DCS | WA3827957 | freezer room controller display constantly flashing | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 07:55:59 | 2020-12-04 14:00:00 | Pass | Complete
MSA-DCS | WA3827974 | Kitchen - Rational Combi Oven – displaying fault ‘SERVICE 110’ & ‘UNIT NOT IN OPERATION’ | Boronia Pre-release | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-04 12:30:00 | Pass | Replaced suspect boiler drain pump, retest ok.
MSA-DCS | WA3828006 | Entrance road- Cables damaged in ground | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 08:31:59 | 2020-12-04 16:00:00 | Pass | Repaired damaged conduit
MSA-DCS | WA3828036 | gatehouse coms room cell server computer is has ceased working-see notes | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2021-01-20 11:00:00 | Fail | Edit ACM, generate node files, downloaded ad confit from new server to nodes in the field. Walk to each not to clear alarms and test
MSA-DCS | WA3828064 | Unit 1, Plant Room- Boiler Water Pipe Work Has leaking Flange Seals & broken Pressure Gauges | Melaleuca Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-11 16:00:00 | Fail | Travelled to site and signed in.Completed tool check.Isolated the water heater and all 3 pumps.Closed valves on water line and drained the sections of pipework.Separated flanges and removed rubber gaskets and replaced with graphite gaskets.Some bolts work almost seized from rust.Cleaned up bolts.Bolted up all flanges.Replaced damaged gauges.Opened up water inlet valves.Bled the air out at highest point.Opened up the rest of the valves.Turned on the pumps and the water heater.Went to unit 2 and installed new gauges.Signed out on site and completed tool check.
MSA-DCS | WA3828142 | Electronic door lock malfunctioning at Gatehouse | Albany Regional Prison-Gatehouse | GMP-BR- HO | Security | Locksmith (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Dec 2020 | 2020-12-04 18:31:43 | 2020-12-04 14:00:00 | Pass | Gatehouse front door not closing correctly. Contacted Security Manager who advised that the door was out of alignment and they would arrange for local repair.
MSA-DCS | WA3828153 | Lock on Multi-purpose cell # 1 is faulty, see notes below | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 10:47:20 | 2020-12-04 14:15:00 | Pass | Attend site. Service lock and adjusted strike plate. Normal function restored.
MSA-DCS | WA3828178 | Faulty wiring to fuel system control panel and fit relays | Wooroloo Prison Farm | SPA-BR | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2021-02-03 14:56:00 | Fail | Trace out controls and found original wiring and diagram incorrect.Modified drawing and then changed panel wiring to match.Test ran bulk fuel pump OK Returned to service.
MSA-DCS | WA3828198 | Front Gate, Metakl Detector- gatehouse entry metal detector continues to sound alarm. | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 11:28:09 | 2020-12-16 08:33:00 | Fail | metal detector is being replaced by PFM, work order to be invoiced at cost to date.
MSA-DCS | WA3828199 | security office CCTV to business office is problem with monitor | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-21 16:00:00 | Fail | Second hand CCTV workstation installed in video link room and VMS installed and configured. second hand switch installed in security office. New user groups and accounts created for vlinknoffice.
MSA-DCS | WA3828210 | Officers Gym (Old front gate outside the prison)- Left shower blocked (male) & urinal running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 11:37:53 | 2020-12-04 12:20:00 | Pass | Replayed inlet valve lh shower
MSA-DCS | WA3828224 | perimeter zones alarms are activating - SEME on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Dec 2020 | 2020-12-04 15:53:49 | 2020-12-09 15:00:00 | Fail | Repaired the damaged sensor cable and terminations of Zone 13. Tested all ok after repair.
MSA-DCS | WA3828314 | Kitchen- Centre prep area table taps; water can be heard running but no water visible | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 13:04:15 | 2020-12-14 17:32:00 | Fail | Leak detection for water leak under the kitchen floor.Jack hammer concrete flooring and repaired burst hot water pipe.Make good concrete.
MSA-DCS | WA3828333 | Unit 14 Emergency shutdown button in the POD needs reset | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-04 16:00:00 | Pass | Attended Gate Control, accessed the Control GUI for Unit 14 and activated the power reset. Attended unit 14 and restored the over-ride switch on the Electrical SwitchBoard to the “Auto” position. Confirmed systems operating correctly in unit control room.
MSA-DCS | WA3828362 | Social Visits, Camera number 2 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 14:01:18 | 2020-12-04 16:30:00 | Pass | Lost communication, refresh the camera and check the live view. Check recording, ok. Job completed.
MSA-DCS | WA3828365 | Unit 2, Cell D14- Sink is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 14:03:52 | 2020-12-05 10:50:00 | Pass | Replaced smashed basin.
MSA-DCS | WA3828370 | Unit 1, C Wing- 2 shower doors damaged | Hakea Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-23 14:00:00 | Fail | replaced hinges rehung doors
MSA-DCS | WA3828378 | Unit 3, C Wing Showers- Sink loose on wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 13:25:00 | Pass | Replacednut in the spout and fixed leakig tap
MSA-DCS | WA3828391 | Gatehouse control room - zone 5 & 7 faulty activation of alarm | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-18 15:30:00 | Fail | replace150mts cable & 5 splice kits in zones 5 & 7. tested ok. job complete.
MSA-DCS | WA3828449 | P.I.R for all units need to be moved and relabeled on Gallagher system, | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2021-04-01 09:50:00 | Fail | Modified graphics as required.Tested OKJob Complete
MSA-DCS | WA3828465 | Zone 11, Camera 1 is not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Dec 2020 | 2020-12-05 18:34:38 | 2020-12-09 10:00:00 | Fail | Replaced 5v 3 a psu and tested camera all ok
MSA-DFES | WA3828394 | Front entrance doors not opening properly | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-16 17:40:00 | Fail | COMPLETED
MSA-DFES | WA3828412 | Tap in Changeroom 1 is hammering and is leaking from the base | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-11 16:45:00 | Pass | 11.12.2020Attend site to investigate water Hame issue and leak on basin mixer located change room one. Isolate water main shut off and install stops underneath basin for future service. Replace old basin mixerand test. No hammer present. Cleaned up site.
MSA-DFES | WA3828417 | Main living area - aircon system for front half of station not working - | Butler Career Fire Station | GMP-BR | Air Conditioning | Ducted Split System (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 04 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-07 09:30:00 | Pass | Found ac 1 out on hard lock faut on main bms panel. Reset fault, ran and tested.
MSA-DFES | WA3828420 | 7x Plain trees have low lying branches hanging over main driveway & are causing a hazard | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-14 13:44:00 | Fail | BRAF raised 15/12/20Tree lopping don Thursday 14th January 2021
MSA-DFES | WA3828451 | Armadale FS-Main Building - External - Volunteer Side - Main lead in pipe is gushing water. | CFRS Armadale- TO BE DECOMMISSIONED Armadale FS-Main Building | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 04 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-04 19:30:00 | Pass | 04.12.2020Attend site to investigate burst and low water pressure to facility. Found burst in garden, dig up and expose burst. Found burst on 20 mm copper main. Found that tree roots had pushed up underneath20 mm copper line, which was the cause of burst. Cut out section and replace. Also cut and remove root causing issue. Test for leaks all okay and flush lines. Backfill and cleanup site.
MSA-DTAG | WA3828084 | ground holding cell walls have hardened accused picking at wall causing holes - see notes | Joondalup Courthouse | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 1 | CLOSE | 04 Dec 2020 | 2020-12-07 17:00:00 | 2021-02-15 10:01:00 | Fail | WALL REPAIRED IN HOLDING CELL 1
MSA-DTAG | WA3828122 | 1903 custody centre camera 116 fault - Sapio on site with scissor lift | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 04 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-21 12:30:00 | Fail | job comleted - Attended site. Replaced Camera 116 on Pole 7, overlooking Sherriffs Office.Tested with Security, all ok.
MSA-DTAG | WA3828424 | Lvl 1, Public waiting area- A tap in the public drinking water fountain is dripping | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-08 13:00:00 | Pass | Complete for AHS, further work required by “Water2Water”Appliance asset bar code in images.
MSA-DTAG | WA3828444 | Ground level - The soap dispenser in female public toilet is broken and requires replacement | Joondalup Courthouse | GMP-BR-HO | Equipment | Cleaning Equipment (EQ) | Midolo Building Services | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-07 12:45:00 | Pass | New soap dispenser installed
MSA-DTWD | WA3827923 | T block roof penetration duct. Tiles with staining indicating water ingress. | Joondalup McLarty Campus | GMP-BR | Roofing | Tiled Roofing (RF) | AWB Co. | 2 | CLOSE | 04 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-08 10:00:00 | Pass | Removed damaged ceiling tile and found extraction unit above, Accessed roof and inspected. Found no signs of water ingress, found windows flashing to be split and possibly cause of the leak/water damage. Sealed flashing.
MSA-DTWD | WA3828000 | Block 2- Broken light fitting in passageway outside first aid room | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 03:45:00 | Pass | Attended site and signed in. Located dead light. Disconnect and removed faulty light. Supply and replace with new led fitting. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3828081 | B Block, Room B50- Bank of light not working near the window as well as soft light switch | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 10:45:00 | Pass | Attended site and signed in. Got keys from facilities. Located room B50. Found back row of lights not working. No power to lights. Found 2 light switch mechs very average condition. Replaced with new. Back row still no power. Found old black box controller in last fitting we opened. Disconnect and removed box and bypassed cabling. 1 tube out of all 6 lights came on. Using site supplied parts. Replaced all tubes to back row. All lights now working correctly. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3828104 | Multiple locations on campus- Alarm system malfunctioning. | Carlisle Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 0 | CLOSE | 04 Dec 2020 | 2020-12-04 14:00:21 | 2020-12-04 14:00:00 | Pass | Job completed - checked alarms
MSA-DTWD | WA3828117 | M Block, foyer near the female toilets- broken hinge on the aluminium/glass door | Balga Campus | GMP-BR | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2021-01-22 09:30:00 | Fail | ATTENDED SITE AND ASSESSED, RETURNED TO SITE AT LATER DATE, REPLACED BOTTOM PIVOT TO HINGED DOOR REALIGNED, HEEL AND TOE DOOR 2 MEN REQUIRED
MSA-DTWD | WA3828121 | D Block,Room D002- privacy latch & door hinge on cubicle door damaged | Balga Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-08 15:00:00 | Pass | Work completed
MSA-DTWD | WA3828220 | Child care Centre ( C block) - roof leak over laundry please investigate | Rockingham Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2021-03-08 14:00:00 | Fail | new dry pan flashing has been installed over the laundry area. No works to repair internal ceiling have been completed as this was not included in the BRAF.
MSA-DTWD | WA3828223 | Child care Centre ( C block) - Gutters full of debris | Rockingham Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 08:37:00 | Pass | Clean out blocked box gutters.
MSA-DTWD | WA3828322 | B Block, Room BG25- Damaged workshop light fittings | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 14:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located panel beating and found lights not working. Disconnect and removed faulty light fittings from roof. Replaced with new led hi bays. Relocated 1 x light to spread the light in workshop. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3828433 | B Block, Library – Several light fittings aren’t working | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-07 16:30:00 | Pass | Attended site and signed in. Located library and found tubes out in numerous lights. Replaced tubes and starters as required. All lights okay. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3828448 | Level 1, printer - Replace faulty lighting | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 04 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-13 14:00:00 | Fail | Attend site. Inspected all areas as provided on list by site. Replaced faulty pl lamps to above lvl 1 printer and lvl2 podBRAF Submitted and declined 13/01
MSA-MRWA | WA3828300 | Lvl 2, Desk L2.111- Desk making continual clicking sound, please investigate and remediate | Road Network Operation Centre (RNOC)-Main Building-Second Floor | GMP-BR | Furniture | Office Furniture (FU) | SCHIAVELLO SYSTEMS (WA) PTY LTD | 2 | CLOSE | 04 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 09:30:00 | Pass | to be closed out at $0 cost
MSA-DCS | WA3828484 | Outdoor Area -Zone 6-Internal -Camera 7 is not facing in right direction unable to Adjust | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Dec 2020 | 2020-12-06 06:00:00 | 2020-12-05 13:45:00 | Pass | Trace camera location and adjust alignment, confirmed correct location with gatehouse control room officer.
MSA-DCS | WA3828498 | One of the Monitor is keep on flashing -Alarm monitor | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Dec 2020 | 2020-12-05 12:41:21 | 2021-10-13 14:25:00 | Fail | Replaced monitor, job completed.
MSA-DCS | WA3828516 | gatehouse - sally port traffic lights out | Banksia Hill Detention Centre | SPA-BR | Building | Materials (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 05 Dec 2020 | 2020-12-06 10:57:08 | 2021-02-11 08:01:00 | Fail | Ryan Nicholson (05/12/2020) - Work NoteTravel to site. Inspect sally port door. Found roller door green light not working so investigated. Tested voltage output and there was none. Found that both the middle and inner roller door green lights do not work (a total of 4 ) Suspect that they were not connected when motors were changed over but need a scissor lift to investigate as the controller is high. Also limited amount of room for scissor in middle door. When door is fully up its 650mm to walk way. When door fully closed its 750mm. Tested everything else all fine.**Quote to be submitted for further investigationsFurther approved works scheduled for 30/03/2021.Ryan Nicholson (30/03/2021) - Work Note30/03/21Inspected operation of lights and found no voltage on green traffic lights for both doors so investigated.Found that at the contactor sets for motors that cables for lights had been disconnected.Will need 2x new brackets and arm limit switches to with power supplies to ma
MSA-DCS | WA3828539 | C WIng- Multiple cell power has tripped cant reset | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 05 Dec 2020 | 2020-12-05 20:53:04 | 2020-12-05 20:00:00 | Pass | Replace faulty circuit breaker, test all effected outlets all ok After hours
MSA-DCS | WA3963122 | Gate house sliding automatic entry personnel door sensor faulty and hard to open | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 05 Dec 2020 | 2020-12-06 11:00:00 | 2021-03-12 12:45:00 | Fail | Anthony Calautti (12/03/2021) - Work NoteReturn and program door operatorSet df =2, Ln=2, rN=-1, C1=1, C2=4, C3=10, C4=43, E1=40, bA=4Test door operation several times okTest via access control open ok , lock ok, (fire working but unable to test)master control says there should be open , exit, fire ,and lockdown modeTrace cabling and run tests with master control to find lockdown mode cabling, cannot findCheck outer door, only has 3 sets of cables connected open , fire, and lock mode, no exit mode connectedSet up inner door the same, if exit mode required will need to return with access control company and trace cablingTest operation several times okTest battery operation okAnthony Calautti (11/03/2021) - Work NoteRemove old BWN operator and retro fit new faac A1400 auto door operatorFabricate custom pickup brackets to suit new operatorMount new equipment, Test manuallyWire up new sensors and controlController starts but won't finish learn process, err light onWill nee
MSA-DTAG | WA3828494 | Public lift (opposite to Court 2) is showing out of service and making noise | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 05 Dec 2020 | 2020-12-07 17:00:00 | 2020-12-05 12:39:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA3828550 | Ground level facing Maceur Hotel Irwin St - Roller door is in alarm | Central Law Courts-Main Building-Level 1 | GMP-BR-HO | Building | Doors (BU) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 05 Dec 2020 | 2020-12-05 23:38:51 | 2020-12-05 21:15:00 | Pass | Anthony Calautti (05/12/2020) - Work NoteTravel to site. Inspect roller door. Found operational,but on an access system not changing state (always reading open).No fault on roller door, Test operation several times, all okay. Fault lies with magnetic reed switch at the bottom of thedoor. Tried to re-align but cannot.Tried to align with another magnet, still not working. Will need access company to fix.Contacted Programmed, Zohan.
MSA-DCS | WA3828554 | Cell call system is malfuntioning and calling the cell without instruction -Wing B | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Dec 2020 | 2020-12-06 07:43:43 | 2020-12-06 06:15:00 | Pass | Rectified the issue and clear the calls thats not being acknowledged, test cell call all working ok.
MSA-DCS | WA3834240 | Greenough Regional Prison- all the perimeter including gatehouse not working | Greenough Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Dec 2020 | 2020-12-06 15:10:48 | 2021-02-17 08:00:00 | Fail | Attended site, repaired software issue on senstar servers, tested fail-over system OK.Job Complete
MSA-DCS | WA3834278 | GATEHOUSE- CCTV key board and mouse are not working. | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Dec 2020 | 2020-12-06 11:11:54 | 2020-12-06 09:00:00 | Pass | Rectified and fixed the issue from WS1, job completed.
MSA-DCS | WA3834532 | Fire alarm fault on the FIP. unable to isolate. | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Dec 2020 | 2020-12-07 07:15:10 | 2020-12-06 10:22:00 | Pass | Call out for alarm on MCP in unit 4 day room south. Reset MCP and deisolated MCP at FIP and return system to normal.
MSA-DCS | WA3834534 | INTERNAL PERIMETER- ZONE 16- CCTV camera 17 not operating. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Dec 2020 | 2020-12-07 07:33:30 | 2020-12-06 13:30:00 | Pass | Rectified and fixed axis encoder issue, job completed.
MSA-DCS | WA3835282 | UNIT URQ ART- Locksmith to attend to a door that is not unlocking. | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 06 Dec 2020 | 2020-12-06 12:05:48 | 2020-12-06 10:30:00 | Pass | Attend site after hours. Gained entry and replaced lock as required.
MSA-DCS | WA3835955 | UNIT YEEDA- Call bell intercom is not working- | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Dec 2020 | 2020-12-06 12:13:03 | 2020-12-08 15:53:00 | Fail | Attended site, checked server and cabling in Yeeda, found call call faults intermittently approximately 3 hours after resetting. Checked CI-Hubs, checked cabling between equipment locations in Yeeda, traced fault to CI-HUB module. Installed replacement, configured and tested OK.Monitored for correct operation and verified audio recordings on Server.Job CompleteParts (SEME Stock):1 x CI-HUB (Dual Channel)Note:Some delays in fault finding caused by prison operations and difficulty moving around prison.
MSA-DCS | WA3853747 | 2x PTZ Cameras not responding to alarm zones | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Dec 2020 | 2020-12-07 05:05:25 | 2020-12-07 16:30:00 | Fail | Reprogram presents for alarm zone 2,3,4 on PTZ 21. Also presets for alarm zones 2,12,13 on PTZ 23, test with gatehouse, all ok.
MSA-DCA | WA3855161 | Glue to be removed from wall after flyer postering, see note below | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Cleaning | Cleaning (CL) | FCT SURFACE CLEANING | 3 | CLOSE | 07 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-16 19:30:00 | Fail | Glue removed
MSA-DCA | WA3855182 | Several lights are not working, see notes below | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 17:00:00 | Pass | Ivistigate fault on b3 circuit in pcc events db. Find 2x faults and rectify.
MSA-DCA | WA3856227 | Office Area - AC on level 1 is not working, see notes below | Swan Bell Tower-Main Building-Level 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 14:30:00 | Pass | Travel to site. Investigate A/C 3 which serves level 1 offices and found excessive oil around base of unit. Investigate and found system to be short of gas due to possible gas leak. Leave unit operational for ventilation purposes but no cooling as compressor will not run. QRF submitted for le ask check /repair and check operation for any further faults.
MSA-DCA | WA3857717 | Water leak on Zone 12 | Perth Cultural Centre Precinct - Museum Plaza (James Street) | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-08 13:00:00 | Pass | Fix leak on station 8,14& 15. Check zone 10,11 and 13, no leakShow Joanne how to use Hydrawlse.
MSA-DCS | WA3854589 | Unit 2, Cell B7- leak found under basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-07 14:30:00 | Pass | Nill
MSA-DCS | WA3854591 | Unit 14, Cell A15- Sink tap constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-15 08:30:00 | Fail | Nill
MSA-DCS | WA3854592 | Unit 14, Cell A1 & A2- Toilets constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-15 09:30:00 | Fail | Nill
MSA-DCS | WA3854601 | Unit 3, A & C Wing- Water in showers is warm | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 15:30:00 | Pass | Nill
MSA-DCS | WA3854620 | Kitchen- large chips out of floor (floor sealent damaged) | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 07 Dec 2020 | 2020-12-11 17:00:00 | 2021-06-16 12:00:00 | Fail | INSPECTION DETERMINED EPOXY TREATMENT NEEDED - ADVISED TO CLOSE OFF COST TO DATE - A NEW LVM WILL BE ISSUED IN THE FUTURE
MSA-DCS | WA3854622 | Unit 6, Cell A8- sewerage is coming up from drain | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 07 Dec 2020 | 2020-12-07 11:29:08 | 2020-12-07 12:40:00 | Fail | Unblcoked sewer line outside a wing. Major job as whole line was blocked and therefore work could not be all completed within the 2hr P0 timeframe. Towel had been put down sewer line from cell
MSA-DCS | WA3854674 | Zone 5, camera 2 no video | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Dec 2020 | 2020-12-07 11:37:16 | 2020-12-07 13:00:00 | Fail | tested power supply & found to be 12v av instead of 18vac. reset performed, camera back online live & recording video ok.
MSA-DCS | WA3855494 | Essential Medication, Electric Gate- Lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:22:53 | 2020-12-07 10:30:00 | Pass | Rectified and fixed electric strike mounting, tested ok. Job completed.
MSA-DCS | WA3855538 | Unit 1, Cell D10- Camera covering is damaged | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:24:55 | 2020-12-07 13:30:00 | Pass | Replaced damaged bosch camera window, job completed.
MSA-DCS | WA3855550 | Unit 9, Cell D15- Viewing Hatch window glass broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:27:03 | 2020-12-07 15:45:00 | Pass | VEIWING HATCH WINDOW RE GLAZED
MSA-DCS | WA3855553 | Unit 7, Unit S2- Broken cell window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:28:43 | 2020-12-07 13:00:00 | Pass | CELL WINDOW RE GLAZED AND WELDED REPAIRS
MSA-DCS | WA3855557 | Unit 3, Control room door- striker plate damaged | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:30:05 | 2020-12-08 13:30:00 | Fail | 07/12/2020 Attend site. Inspect door and make safe. Replacement Blocker Plate required.08/12/2020 Re-attend site. Replace Blocker Plate to restore normal function.
MSA-DCS | WA3855562 | Unit 3, Cell C11- Cell floor drain oveflowing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:32:45 | 2020-12-07 09:30:00 | Pass | Held up in unit prior to commencing work
MSA-DCS | WA3855587 | Pump House- Jacking pump non return valve is passing (has been isolated) | Casuarina Prison | GMP-BR- HO | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-15 13:30:00 | Fail | Repaired under warranty
MSA-DCS | WA3855973 | Outside of main kitchen- hot water boiling up from out of ground (burst pipe) | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:46:40 | 2020-12-14 10:23:00 | Fail | Sectional water service replacement completed. Bitumen repair/replacement completed
MSA-DCS | WA3856007 | Unit 2, Control Pod & Passage- Damaged carpet | Melaleuca Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-15 12:57:00 | Fail | braf declined - advised to close off cost to date - no costs
MSA-DCS | WA3856011 | Jelia C wing Air Conditioner Blowing Warm air | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2021-04-19 07:32:00 | Fail | Works completed by other contractors. No charge
MSA-DCS | WA3856018 | Unit 1, Control- Monitors not working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:57:48 | 2020-12-07 15:00:00 | Pass | Attended site checked and found Unit 1 Control CCTV Monitors not showing cameras correctly. Located problem to be EBI CCTV workstation frozen. Reboot workstation and reassigned cameras and tested ok.
MSA-DCS | WA3856021 | Front Gate, Control Zone B5- Internal Fence Sensors Faults Alarming | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:58:50 | 2020-12-18 13:46:00 | Fail | Attended site and repaired fence fault.Tested OKJob Complete
MSA-DCS | WA3856024 | zone 1 grill gate Problem with keys opening the grill | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 08:58:03 | 2020-12-07 11:00:00 | Pass | On site. Serviced lock. Tested - normal function restored
MSA-DCS | WA3856030 | Unit 2, Cell D12- Cell call hard to hear | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 09:00:38 | 2020-12-07 15:51:00 | Pass | Cell call vandalised with toothpaste, dismantled and clean. Re- mounted and tested ok. Job completed.
MSA-DCS | WA3856039 | Unit 7, A Wing- Laundry sink is leaking badly on the 50mm tap, see note below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 10:30:00 | Pass | Nill
MSA-DCS | WA3856085 | Unit 6, Staff toilet is leaking under the bowl | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 12:00:00 | Pass | Nill
MSA-DCS | WA3856089 | Unit 14, Cell B5- blocked shower & wash basin drains | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 12:30:00 | Pass | Nill
MSA-DCS | WA3856105 | investigate the condition of the macerator & provide advice | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-06 11:00:00 | Fail | Called out for blocked drains, found the macerator majorly blocked. Had to use jetter to clear
MSA-DCS | WA3856124 | defective ground surface surrounding service hatch at main entry building, see notes below | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 15:19:00 | Pass | Relayed paving grind concrete, cement filled.
MSA-DCS | WA3856182 | SB2 (Between U17-U18) - The Whole Unit Hot water system not working in SB2. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 10:40:30 | 2020-12-08 10:30:00 | Pass | Nill
MSA-DCS | WA3856184 | Reception, Tombstones on light fitting knackered | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 08:30:00 | Pass | Repaired faulty lights in reception
MSA-DCS | WA3856213 | gate house control sally DRRS has changed every 2/3 minutes | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-07 15:00:00 | Pass | Intermittent controller failure was causing issues with GH door controller. Controller was reset and monitored and problem resolved. This controller is pending upgrade from 3000 to 6000 on a project variation during a night shift.
MSA-DCS | WA3856216 | unit 4 cowling fault appearing | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-23 10:00:00 | Fail | Ran report on Gallagher toshow Excessive alarmsfrom Cowling in PRU. Noted excessive alarms from Cowling zones 7 & 11. Attended PRU EC 03 and adjusted threshold from 15 to16 for Zone 7, and same at EC05 for Zone 11. Monitored alarms in PRU control while writing sig Slip. No activations.
MSA-DCS | WA3856223 | PRU, PTZ 38 camera is not moving | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 09:01:00 | Pass | Diagnose and test PTZ data fault. Fibrevmodem 732-R was replaced in MED prison rack. All test ok.
MSA-DCS | WA3856366 | Reset building male toilet blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 11:06:21 | 2020-12-07 14:35:00 | Pass | Unblocked toilet and sewer line
MSA-DCS | WA3856446 | Front Gate, Disable Toilet - Toilet Blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 11:15:39 | 2020-12-07 16:10:00 | Pass | Unblocked toilet and sewer line
MSA-DCS | WA3856679 | Admin, visits bookings- Air Con producing a smell | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 12:00:00 | Pass | Arrived to site.Awaited unit guard.Accessed room.Tested unit.Staff advised unit smells occasionally.Picked up split cleaner.Removed all covers.Soaked in cleaner.Deep cleaned coil and fan barrel.Removed all debris.Washed down all components.Returned covers and airflowing okay.Advised staff.
MSA-DCS | WA3856683 | J block transponder 7 reciever external wall B wlng store fault coming up on PDA monitor | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 11:22:49 | 2020-12-07 16:15:00 | Pass | Investigate & found transponder offline, reset & tested ok.
MSA-DCS | WA3857024 | Karakin B wing living area smashed window approx 1200x450 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 11:00:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3857352 | Mechanical w/s - external GPO not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-11 15:00:00 | Pass | Repair Mechanical W/Shop external GPO circuit
MSA-DCS | WA3857471 | Lenard, B wing living area - smashed window approx 1200x450 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 15:00:00 | Pass | 2 WINDOW REPLACED
MSA-DCS | WA3857500 | Hotham office/cell door not opening at all | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 12:00:00 | Pass | On site. Service lock and adjust frame to restore normal function.
MSA-DCS | WA3857698 | Unit 5, House 7- Electrical fault at viewing hatch, causing electrical faults through whole house | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 13:20:31 | 2020-12-07 17:00:00 | Pass | Replaced faulty downlight and tested
MSA-DCS | WA3857720 | Unit 3, Cell A6 - bed light broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 10:30:00 | Pass | Replace bed light Unit 3 Cell A6
MSA-DCS | WA3857721 | Unit 1, B wing corridor - light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 15:00:00 | Pass | Repair B Wing Unit 1 lights
MSA-DCS | WA3857731 | WWTP transfer pump not working no power | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-04 15:00:00 | Fail | Investigate and disconnect wwtp transfer pump. Remove pump and source replacement.Collect and replace wwtp transfer pump.
MSA-DCS | WA3857762 | Unit 7, Cell E17- Toilet Broken and not secured to floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 09:20:00 | Pass | Fixed loose toilet.uninstalled and reinstalled toilet
MSA-DCS | WA3857765 | Assessments, Kitchen- Fluro lights broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 15:00:00 | Pass | Replaced lights
MSA-DCS | WA3857769 | Reception, Kitchen- Hot and Cold water dispensar not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-11 09:00:00 | Fail | Replaced tap head all okay
MSA-DCS | WA3857774 | Jeelia, C Wing C07- Bottom cell door lock difficult to lock, door has to be lifted to lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 14:30:08 | 2020-12-08 11:00:00 | Pass | Attend site. Replaced hinge on door to restore normal function
MSA-DCS | WA3857781 | Admin, Staff Lunch Room- Air con is not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 14:36:56 | 2020-12-07 16:10:00 | Pass | Arrived on site and signed in, checked over aircond found remote set for fan only,changed to cool and tested all running ok at present.
MSA-DCS | WA3857785 | Unit 14 - B Wing Fire alarm will not reset between cell 5 and 6 B wing | Casuarina Prison | GMP-GR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 14:38:52 | 2020-12-08 13:33:00 | Pass | Attended site to unit 14 wing B/D Cells 5/6 and found vesda unit no longer operational. Flow sensors failing as flow swinging from no flow to high flow will require unit to be replaced. Currently isolated and not operating
MSA-DFES | WA3856196 | Western Front Engine room Tilt door - Smashed glass to engine room tilt door | CFRS Belmont | GMP-BR | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-14 10:16:00 | Fail | Made safe with film both side need to return with 6.38 trani laminated 1-975x1690.Return to site repair glass panel complete
MSA-DFES | WA3856208 | ground kitchen Filtered drinking water tap leaking and requires repair on sink. | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 08:15:00 | Pass | Replaced faucet. THIS IS A RENTAL SYSTEM SO NO CHARGE FOR ANY WORKS
MSA-DFES | WA3856211 | Dorm (5) -Air con 1st dorm (left hand side) appears to have a white powder/scale coming from it | CFRS Malaga | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-14 03:30:00 | Fail | Perfromed split cleans on A/C 3 and 6 to remedy the white dust issue
MSA-DFES | WA3857479 | Outside Garden- Retic, hose attachement has been cut & stolen | Armadale Regional Office | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2021-01-08 13:00:00 | Fail | Dom attended site x 2 and Jim from JCS Plumbing attended today to finish the job 8/01/21
MSA-DFES | WA3857805 | driveway gate not closing/opening automaitcally only work manually | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | Go Doors | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 11:30:00 | Pass | (08/12/2020) - Work NoteIssue with existing safety sensor not lining upCheck automation and lined up sensors and works ok, check timer and seems ok..Recommend replacing sensor with FAAC XP30 to avoid misalignment caused by vibration and loose screw if problempersists
MSA-DTAG | WA3856212 | 1903, Court of appeal office - Interior handle of secure door is disconnected. | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-08 13:30:00 | Pass | NEW LEVER HANDLE FITTED
MSA-DTAG | WA3856689 | L1 public waiting room Chair that is bolted to the floor - Gas lift cylinder may need replacement | Midland Courthouse | WSM-BR-SITE | Furniture | Commercial Furniture (FU) | Midolo Building Services | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-15 11:00:00 | Fail | NEW GAS LIFT FITTED TO CHAIR
MSA-DTAG | WA3857512 | External - Sprinkler adjacent to Sheriff’s Office entry is broken | Supreme Court | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Dom's Total Grounds Maintenance | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-08 17:30:00 | Pass | Call Out & LabourReset, Check & Replace 1 x Riser & 3 x Nozzles
MSA-DTAG | WA3857756 | Ladies Toilet in Custody constantly running | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-08 07:55:00 | Pass | Replaced faulty inlet valve and outlet washer
MSA-DTAG | WA3857777 | L1 DPP kitchen Mixer tap in Kitchen – Has a leak on top | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 12:45:00 | Pass | Replaced mixer tap and tested
MSA-DTWD | WA3854923 | C Block , Disabled toilet- cistern lid has been smashed | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 2 | CLOSE | 07 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-08 16:33:00 | Pass | Cistern lid had been smashed,Replaced cistern with PVC cistern to minimise potential future damage.
MSA-DTWD | WA3855563 | - T Block café rear Freezer not reaching temp and audio alarm sounding | Murdoch Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-17 16:00:00 | Fail | Gathered tools and equipment. Isolated freezer and started defrosting ice up Evaporative coil, through the process the light fitting came down at one end and was full of water. Further inspection found wiring penertration not sealed. Complete light fitting iced up. Isolated Power to light and reported fault. Completed works cleaned up completed paperwork and logged out.
MSA-DTWD | WA3856047 | C block workshop security system alarm continues to activate | Munster Campus (ACEPT) | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 12:45:00 | Pass | 07/12/2020, 1200-1245Tested cable to zone 128 ok, replaced device.Also rick asked me to check zone 39 in constant alarm.Found reed switch a bit corroded so replaced and resistors.
MSA-DTWD | WA3856067 | O block Repair retic pipe leak near O Block | Balga Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-21 09:45:00 | Fail | Repair broken mainline, back filled and test irrigation system for leaks.
MSA-DTWD | WA3856068 | classroom F-61 - Check timer settings or replace faulty light switches | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 13:30:00 | Pass | Attended site and signed in. Located f61. Found light switches to be in sequence. Tested operational times and checked settings. Both are okay and functioning correctly. Notified staff. Signed out job complete
MSA-DTWD | WA3856093 | P Block, low battery fault on alarm system | Balga Campus | GMP-BR | Security | Security Management System (SE) | Casa Security Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-07 14:40:00 | Pass | job completed - BATTERY CR123A 3V LITHIUM
MSA-DTWD | WA3857486 | various locations faulty fluro's | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-08 15:15:00 | Pass | Attended site and signed in. Awaited staff to confirm what locations to repair lights. Checked out all of the lighting throughout. Counted up tubes and lamps needed. Replaced all tubes and starters that were out. Replaced lamps to other lights needed also. Dispose of rubbish. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3857492 | reception auto door needs adjusting as it is to slow when closing | West One Services | GMP-BR | Building | Security Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-07 14:40:00 | Pass | Programmed Ip-A40442513CInspected door and found security signal is latching of too long, tested the dwell time from our side which is 01 seconds, notified site manger to callout security company to reduce the dwell time, replaced out date batteries, cleaned off track and sensors.
MSA-DTWD | WA3857496 | Plant room - main air conditioner has dumped a lot oil | Perth Campus B4 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 0 | CLOSE | 07 Dec 2020 | 2020-12-07 16:02:24 | 2021-01-27 09:54:00 | Fail | BRAF repair have been completed on equipment. Chiller is now back up and fully operational. Work area has been left tidy. Oil spill has been cleaned up plant area and around equipment.
MSA-DTWD | WA3857718 | H Block, station 3C in nursery is not working properly, see notes below | Mandurah Campus (formerly Peel) | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-08 09:15:00 | Pass | Investigate low pressure issue on station 3c, found inline filter has been install backward. Reinstall filter the correct way and test system, irrigation pressure back to normal.
MSA-DTWD | WA3857763 | B15 classroom- roof mounted A/C not operating | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 14:30:00 | Pass | Attended site checked in , checked the aircon in B15 class room. The electrician on site had turned the circuit breaker off then back on , this reset the aircon which is running ok. Will return later with a second person to access the roof as the package unit is on the roof.Found the unit not working, reset circuit breaker. Accessed the roof and all ok possible power surge. Assisted by Murray Biddle
MSA-DTWD | WA3857810 | Level 3, female toilets - broken door lock | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 07 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 14:40:00 | Pass | Replace mortice lock, turn knob & privacy indicator
MSA-DTWD | WA3857813 | Faulty pin pad code to front door - (Sentinel to attend 09/12/20) | Armadale Campus? 45 Commerce Ave | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 07 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 09:30:00 | Pass | Faulty digital lock to front door.Lock repaired.
MSA-MRWA | WA3857650 | North Hallway - Water fountain not working P2 error, please investigate and remediate | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor-Water Fountain Area | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 07 Dec 2020 | 2020-12-08 17:00:00 | 2020-12-07 15:18:00 | Pass | Fountain not working at allChecked power and water all okayMay need Arcus to attend
MSA-DCA | WA3869707 | ajacent public toilet block water coming up from ground- Please call Phil Golder prior to attendance | Sunset Hospital Heritage Precinct-External Area | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-08 17:25:00 | Pass | Tightened loose poly fitting underground
MSA-DCA | WA3869720 | AC in the clean lab (Molecular) is not function properly. Warmer than usual - see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Molecular Lab | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-08 17:30:00 | Pass | Attended site. Molecular lab AC system to be warm. Applied tests and checks (no faults present with in Temperzone Package AC system.). Carried out tests and checks to BMS control system (no errors present). Reset package AC system and power cycled BMS field controller. Tested operation of system and checked RA and SA TD's (23c / 11.9c) system operating correctly. Left site.
MSA-DCS | WA3857873 | In the ISU, have lost the monitor functions. Can see the cameras from control room but not from ISU | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 08:46:01 | 2020-12-08 12:24:00 | Fail | Phoned to notify attendance, travelled to Banksia hill, found ISU monitors indicating No signal, reset USB/KVM extender which restored images, no further action required.
MSA-DCS | WA3858010 | Front Gate, Sally Port- Sliding mesh not retracting over the pit | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 07:08:34 | 2020-12-08 10:45:00 | Pass | 08/12/20Inspect anti-ram, jammed when shutting. Officer pulled grate - starting working again. Inspected tracks and wheels, a lot of rubber debris from tyres and timber debris from most likely pallets, causing the wheels to jam. Cleaned out tracks of debris.
MSA-DCS | WA3858026 | Dairy packing room light fitting not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 09:00:00 | Pass | Replace Dairy packing light
MSA-DCS | WA3858038 | Unit 2, Cell C14- Tap is damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 10:10:00 | Pass | Rewashed and fixed leaking tap
MSA-DCS | WA3858046 | Unit 1, A Wing Dayroom- Sink waste broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 11:20:00 | Pass | Replaced 50mm plug in waste
MSA-DCS | WA3858057 | Unit 13, Cell A11- Shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 09:30:00 | Pass | Held up in unit , short staff due to escorts because crane was on site
MSA-DCS | WA3858058 | CCU(11), Cell C2- Sink is leaking water onto cell floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 15:30:00 | Pass | Nill
MSA-DCS | WA3858065 | Unit 7, Regi Area- Hot water tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-11 11:52:00 | Fail | Replaced leaking spindle
MSA-DCS | WA3858075 | industries gardens deadlock faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 12:03:32 | 2020-12-10 09:00:00 | Fail | made temporary repairs to gardens Deadbolt new lock being built will fit once ready ...Returned to site ( 10/12 ) fitted new deadbolt keyed to Prison system and cover plates also replaced top door Hinge .
MSA-DCS | WA3858079 | entry building sallyport door not running on the guids needs adjustment | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 08:05:22 | 2021-03-16 11:30:00 | Fail | 08/12/20Inspect door operation16/03/21repair door guides
MSA-DCS | WA3858082 | Unit 7, Cell H14 & H22- GPO broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-08 12:00:00 | Pass | Replaced broken light switch and gpo
MSA-DCS | WA3858375 | Unit 7, Cell E6- Exposed wires in cell. GPO smashed | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 08:25:04 | 2020-12-08 10:30:00 | Pass | Replaced gpo
MSA-DCS | WA3858718 | Vege Prep shipping container coolroom sitting above safe temp, see notes below | Casuarina Prison | WSM-BR-SITE | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 12:29:00 | 2020-12-15 12:12:00 | Fail | Rectify fault with wiring and reset contoller, monitor operation,all running ok at present.
MSA-DCS | WA3860720 | Gym, Hole in ceiling | Banksia Hill Detention Centre | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 09:00:00 | Pass | GYM CEILING REPAIRED
MSA-DCS | WA3861170 | unit 1 pod 5 ablusions fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-08 12:30:00 | Pass | Replaced 6x old exhaust fans with new fans
MSA-DCS | WA3861873 | External fire pump house- 8x fluro tubes not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-10 10:30:00 | Pass | Repaired numerous waterlogged lights in pump house
MSA-DCS | WA3862003 | Gatehouse- Omnitrax 17 & mircowave 6 constantly alarming | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 09:12:25 | 2020-12-08 16:00:00 | Pass | Re calibrate OT zone 17 and MW zone 6 and walktest. Job completed.
MSA-DCS | WA3863148 | SHU, control room - Red circuit breaker number 43 ( BWU) in SHU control will not reset. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 09:20:06 | 2020-12-08 14:00:00 | Pass | Investigate and repair SHU tripping circuit.
MSA-DCS | WA3866214 | education prisoners toilet is blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-11 10:15:00 | Pass | Attended site,Cleared an unknown blockage to education prisoners toilet by plunging toilets. Tested on completion
MSA-DCS | WA3869495 | Social visits center - Audible sound that can be heard by everyone in the center | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-15 13:15:00 | Fail | Re attend the socialist visits area to check for the buzzing sounds, all security systems in the area are still working ok. No defect or faulty equipment found.
MSA-DCS | WA3869517 | Outside gymnasium corner light pole damaged/perished. Bulb exposed to weather. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-18 11:30:00 | Fail | Replaced damaged pole light outside gym
MSA-DCS | WA3869537 | PRU PTZ 38 static on screen, SEME on site | Bunbury Regional Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-07-01 12:00:00 | Fail | New digital network links and hardware installed. Camera replaced with Interceptor. Program, test and commission.
MSA-DCS | WA3869541 | PRU programmes room camera static on screen, SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-22 09:00:00 | Fail | Identify camera and job is a duplicate.
MSA-DCS | WA3869564 | control room house 8 and 9 controller blowing fuses-att Carl | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-11 13:39:00 | Pass | Rectified issue causing fuses to blow, replaced fuses and tested fully operational.
MSA-DCS | WA3869570 | Bakery Berto mixer appears to have no power | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 15:23:28 | 2020-12-08 14:50:00 | Pass | Cover being replaced on WA4098821.
MSA-DCS | WA3869573 | Bakery Sortoriva mixer has stopped working under load | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 15:45:56 | 2020-12-08 14:50:00 | Pass | COMPLETED 8/12/20NOTE: PLEASE REVIEW SR DUE TO RISK OF COVER.
MSA-DCS | WA3869583 | Main Kitchen - Commercial Dishwasher not washing properly-crockery does look clean | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-19 14:45:00 | Fail | 09/12/2020Sign inWait for staff to finish in kitchen due to COVID restrictions. Check dishwasher Found end plug missing from top rinse arm. Clean wash arm Parts required: 2 x Rinse Arm End Bush19/1/2021Sign inInstall rinse arm end bush Fill and heat unit Tested ok
MSA-DCS | WA3869586 | unit 9 B12 Light switch smashed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 10:00:00 | Pass | Replaced light switch
MSA-DCS | WA3869602 | SOG Base, Administration wing - admin corridor aircon has failed | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 12:36:54 | 2020-12-08 16:00:00 | Pass | Replaced the control fuse
MSA-DCS | WA3869606 | Unit 9, Cell A7- Drain Blocked, water coming out onto floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 12:15:00 | Pass | Unblocked drain
MSA-DCS | WA3869607 | Unit 1, A2 - sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-17 08:00:00 | Fail | Replaced quarter turn spindles.
MSA-DCS | WA3869612 | Unit 2, B12 - sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-17 08:45:00 | Fail | Replace quarter turn spindles
MSA-DCS | WA3869626 | Front Gate Disabled Toilet is blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 12:06:51 | 2020-12-09 07:15:00 | Pass | Disabled toilet not blocked. Plunged and fluseh fixtures in it several times. Water draining properly.
MSA-DCS | WA3869629 | Unit 2, B7 - toilet pan seals leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-17 10:00:00 | Fail | Replace key seal on flush pipe to pan
MSA-DCS | WA3869632 | Unit 2, B3 - broken shower titles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-23 10:00:00 | Fail | replaced damaged tiles in shower recess and cell floor and resealed.
MSA-DCS | WA3869639 | Unit 9 - Cell A6 -Sink smashed on wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:00:18 | 2020-12-09 10:10:00 | Pass | Replaced smashed basin and adjusted pipe to suit new basin
MSA-DCS | WA3869640 | Unit 1, D14 - broken shower titles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2021-01-20 09:30:00 | Fail | Replace broken floor tiles.
MSA-DCS | WA3869648 | Unit 9 - Cell A6 -Toilet smashed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:26:54 | 2020-12-09 12:15:00 | Pass | Replaced smashed toilet, job delayed due to having no escort.
MSA-DCS | WA3869649 | Unit 9 - Cell A6 - Viewing glass smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:28:22 | 2020-12-09 10:30:00 | Pass | VEIWING WINDOW RE GLAZED
MSA-DCS | WA3869654 | Unit 9 - Cell A6 - Main cell window smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:31:21 | 2020-12-09 16:00:00 | Fail | REPLACED SMASHED WINDOW WITH POLY CARB WINDOW
MSA-DCS | WA3869655 | Unit 9 B16 Sink leaking from underneath | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 14:30:00 | Pass | Replaced leaking 1/4 turn cold spindle
MSA-DCS | WA3869660 | Kitchen, Work Area GPO's- Power tripping | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:32:34 | 2020-12-22 12:00:00 | Fail | Replaced gpos
MSA-DCS | WA3869661 | Officers Gym (old front gate outside the prison) kitchen water cooler not working-see notes | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-11 09:27:00 | Pass | No filter installed bad metallic taste from fountain bubblers and jug filler not working properly Client requests a new fountain and filter to be installed Original fountain had probably been there since the prison was builtRECEIVED ALL APPROVALS TO GO AHEAD AND INSTALL NEW FOUNTAIN - ORDERED IN STOCK HELD STOCK FOR A COUPLE OF MONTHS AND JOB IS NOT GOING AHEAD HAVE NOT INVOICED RESTOCKING FEE .
MSA-DCS | WA3869662 | Unit 5, Control Room- Vesda beeping – low flow warning | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:34:53 | 2021-02-22 10:44:00 | Fail | 9/12/20 MBAttended Site for Vesda faults in Unit 5.No faults on both Vesda’s on arrival.Check event logs and found that A wing Vesda has had intermittent low airflow fault on pipe 3.Checked all airflow levels and found low airflow on A wing pipes 1 and 3 and high airflow on A wing pipes 2 and 4. B/C wing Vesda showingnormal airflow levels.Temporarily adjusted airflow fault thresholds to prevent constant fault conditions and beeping.A wing will require all capillary pipes and sampling points to be checked and repaired/cleaned as required and Vesda to be adjusted/normalisedaccordingly.All A wing pipework and sampling points are located in roof void above wing (confined space) and will require 2 x techs for 4 hours.BG JG 22/2/21Cleaned out all sample points in a wing. Flows increased accordingly. Normalised flows to set new benchmark
MSA-DCS | WA3869663 | Transponder TR1 COMMUNICATIONS FAILURE | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-04-12 10:30:00 | Fail | Transponder 1 Comms failure tested area and checked MDAS all is ok. Replaced receiver and tested operation all is in working order. Fault has cleared parts from site stock.Completed under - WA3871543
MSA-DCS | WA3869669 | laundry washer area Washer 2 (75Kg) error 5, machine will not rotate | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 13:36:34 | 2020-12-11 14:00:00 | Fail | 11/12/20 - There was no water available to test the machine, Tim to contact us when readyNothing further heard, job completed.
MSA-DCS | WA3869672 | Unit 2, Stairwell Doors- Broken peep holes | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-09 15:00:00 | Pass | Source, supply and install new vision peep holes to stairwell doors.
MSA-DCS | WA3869674 | Unit 6, D Wing Cleaning Cupboard- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 14:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3869727 | Case Planning- L8 error air con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-08 15:54:00 | Fail | Complete. Replaced PCB's
MSA-DCS | WA3869755 | unit 3 cell 5 cell call is very hard to hear from cell but can be heard in the office | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 15:07:47 | 2021-03-11 16:00:00 | Fail | Distorted audio signal from the cell call unit, reset the unit and re test, ok and back to normal operations. Job completed.
MSA-DCS | WA3869781 | PRU sliding security doors opening/closing by them selves | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 23:44:21 | 2020-12-09 09:00:00 | Fail | Programming checked as ok, doors functioning.
MSA-DFES | WA3862858 | Eastern Side of Building, Radio communications area - Aircon not working | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 13:20:47 | 2020-12-08 11:30:00 | Pass | Attend site. Access radio comms area and found AC not working. Access AC and remove panels. Check faults and found lockout relay energized. Check all safety switches and found stage 1 & 2 high pressure switchs tripped. Reset high pressure switchs and lockout relay. Found unit to start. Check operating pressures and found to be normal. Check condenser fan motor amp draw and found to be normal.wash condenser coil with water. Monitor operation and found to work as normal. Unable to determine cause of high pressure fault. Possible printed circuit board intermittent signal loss to condenser fan. No other issues found.
MSA-DFES | WA3869738 | COMCEN, 2nd Floor, Men's Showers- Leaking shower head | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 13:30:00 | Pass | Investigate leaking shower located floor one comcen male shower Locate and Isolate water supply under basin, remove mixer parts to gain access to old cartridgeAttempt to source replacement cartridge, supply and install new cartridgeTurn water supply on and test operation/check for leaksPack up and clean up worksite
MSA-DTAG | WA3859880 | Lvl 3, Court 31- Cover over bolts on hand rail mounting leading to witness box have come off | Central Law Courts | GMP-BR-HO | Building | Steel Work (BU) | Midolo Building Services | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-08 14:15:00 | Pass | COVER PLATES RE SECURED
MSA-DTAG | WA3869533 | Level 6, “In Session” button not working on member’s door for Room 3.04.and 3.08 | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Keys & Access (SE) | Sapio Pty Ltd | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-10 10:00:00 | Pass | Job completed - Attended site. In Session buttons checked and tested after server upgrade works. All OK
MSA-DTAG | WA3869717 | Lvl 1, Public waiting area- A tap in the public drinking water fountain is dripping | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 15:50:00 | Pass | Replaced leaking bottle filler faucet. Required two people to lift fountain off the wall.
MSA-DTAG | WA3869797 | Level 1, court 4 - very humid & hot (adjusted the setpoint and didn’t make a difference) | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 17:00:00 | 2021-02-23 09:27:00 | Fail | Luke Crisp (03/02/2021) - Work NotePicked up parts Attended site.Located fcu 6Isolated chilled water pipes for unit on roof.Drained pipework.Removed stad valve Issues removing isolation valve Picked up rothenberger compression tool and purchased parts for use with tool.Returned to site.Completed installation of new stad and isolation valves.Unisolated system and turned fcu 6 onto full manual cooling.Tested system for leaks and conducted water balancing to original commissioning specifications.No leaks found.Reinsulated pipework to stop condensation issues later.Cleaned up work areaReported findings.Left site
MSA-DTWD | WA3858044 | N Block, Room N205- damaged ceiling tiles with Fire Detection sensors & speakers | Mount Lawley Campus | GMP-BR | Building | Ceiling (BU) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 08 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-10 10:30:00 | Pass | Installed new ceiling tile and wired EWIS speaker and smoke detector up in new tile.
MSA-DTWD | WA3858050 | T Block, Chiller units not coming on (no Air Con) | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 0 | CLOSE | 08 Dec 2020 | 2020-12-08 11:41:12 | 2020-12-17 12:05:00 | Fail | Lead lag change over issue identified with equipment. Controls tech was engaged for site to return and correct. Campus has reported no further issue with equipment.
MSA-DTWD | WA3858563 | Shed Vessel Centre- Shed door frame rusting and falling away | Marine Vessel Centre | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-17 14:30:00 | Fail | Remove surface rust and treat with rust converter. Applied primer and top coat
MSA-DTWD | WA3858880 | Canteen dining room- Ceiling fans broken | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-14 13:00:00 | Fail | Attended site and signed in. Located cafeteria. Found 2 fans not working. And 1 severely rusted and flaking and 1 with bent blades causing wobbles. Disconnect and removed faulty fans. Installed new fans in place. 4th fan has different mounting. Placed order for correct fan. Tested all okay. Signed out. Job not completeAttended site and signed in. Got new fan for remaining swap. Disconnect and removed fan. Supply and replace with new fan. Tested all fans working. Clean and tidy site. Dispose of rubbish. Signed out. Job complete
MSA-DTWD | WA3863238 | Block 3, Male Toilet- Broken toilet seat | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-08 15:47:00 | Pass | Toilet seat
MSA-DTWD | WA3864416 | C block, Level 1 - Repair water cooler Air conditioner | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-04-28 17:41:00 | Fail | BRAF declined for further works, closing out work order
MSA-DTWD | WA3865834 | A block, ladies toilets - 2x toilets not flushing | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-08 16:18:00 | Pass | Two toilets in female WC, users where not holding down flush button for long enough to flush toilet to clear.Have adjusted water level up to maximum,Toilet suites are water efficient 4/3L flush toilets if issue persist would recommend replacing cisterns with larger cisterns.
MSA-DTWD | WA3866002 | main office and entrance smoke alarms to be re-enstated | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-18 11:30:00 | Fail | Detector located from fip. New smoke head installed fault all clear
MSA-DTWD | WA3866158 | C block, Level 1, Access/staff toilet leaking | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-09 16:00:00 | Pass | Arrived on site and inspected found inlet valve and outlet washer faulty. Collected parts and returned to site. Changed parts and tested all working good.
MSA-DTWD | WA3867658 | Exterior- padlocks for Retic Control Box and Skip Compound keyed to 42886 are faulty | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-15 11:54:00 | Pass | Replace padlocks to skip compound & Retic controller box
MSA-DTWD | WA3869507 | Cleaners room- door lock is faulty | Naval Base | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-09 11:45:00 | Pass | Job completed - lock jammed cleaners room repaired
MSA-DTWD | WA3869527 | block 6 ground painting and decorating Blocked drain in workshop. | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-15 15:48:00 | Pass | Changed drain to avoid flooding
MSA-DTWD | WA3869676 | F Block - FG11 Workshop Emergency Stop Switch is faulty | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 12:30:00 | Pass | Attended site and signed in. Located fg11. Found 2 x e stops with no guards in walkways getting easily tapped and isolated. Disconnect and removed old e stops. Supply and replace with new guarded e stops. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3869691 | C block CG10 Workshop Evap 1 blowing hot air - see notes | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-17 10:00:00 | Fail | Travelled to site and signed in. Liased with client and Located faulty Evaporative unit Evap 1. Inspected unit and found that sump dump had split causing water to continuously run and not fill. Replaced sump dump also found that Low speed fan relay had burnt out. Travelled offsite to supplier to pick up parts. Travelled to site and installed new fan speed relay. After testing unit still not running on low speed. Possible problem with Bms card. Explained to client and they are happy to run unit only on high speed in the meantime.
MSA-DTWD | WA3869701 | D Block, Room 208- Daiken Air Con is tripping out, see notes below | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-06 16:25:00 | Fail | Attended site gained access and spoke with site facilities. Shown to room and braker location. During testing unit trip. On investigation braker was found to be under rated for the A/C unit. 10amp braker fitted. Units minium amp draw is 11.5A with max 19A when fully loaded would recommend having a 20Aamp breaker fitted. Tafe have advised to close job off as they will have an electrician upgrade the breaker. Work area left tidy.
MSA-DTWD | WA3869747 | Fire Exit Stairwell - Non slip strips damaged | Perth Campus B1 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 08 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-17 15:30:00 | Fail | Repair Fire Exit Stairwell - Non slip strips damaged
MSA-DTWD | WA3869770 | E block ET10 office Lock is sticking sometimes | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-11 11:15:00 | Pass | Room ET10 - locks sticking.Locks repaired.
MSA-DTWD | WA3869778 | A block room 0007.1 broken hinge on the aluminium/glass door. | Balga Campus | GMP-BR | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-22 15:18:00 | Fail | ATTENDED SITE AND ASSESSED DOOR, WILL NEED TO RETURN WITH 2 MEN TO ADJUST DOOR AND PLANE DOWN IF REQUIRED ***UPDATE***22 December 2020 3:18pm SPOKE WITH GEFRI HE SAID TO CLOSE THIS WORKS OFF AS COMPLETED AS THE DOOR IS NOW WORKING
MSA-DTWD | WA3869783 | Plant room Chiller tripped - see notes | Perth Campus B4 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-21 15:35:00 | Fail | Attended site gained access and carried out inspection. Chiller noted to have tripped due to flow switch interlock safty indicating no water flow. Checked for correct pump operation all ok reset chiller and cooling restored. Please note BRAF is currently awaiting approval for further equipment repairs on WA3696133.
MSA-DTWD | WA3869791 | Level 3, A wing, A354a staff kitchen - Condenser failure alarm on Billi Quadra drinking water unit | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-09 15:40:00 | Pass | Replaced faulty dual solenoid restricting flow to reforge causing compressor issues. All ok.
MSA-MRWA | WA3861305 | External entry gate not working, please investigate, remediate and report to site contact listed. | Western Vent Building-Main Building | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 08 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-08 12:01:00 | Pass | Gates were stuck open. Reset controller and serviced gate. Tested all good. Ps programmed no A40029457K
MSA-MRWA | WA3869705 | Hallway west - Water fountain not providing cold water only tap temperature. Please remediate. | Don Aitken Centre MRWA Head Office-External Area-Ground Floor-West | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-29 14:47:00 | Fail | have oncharged the arcus invoice as discussed with Brendan - they came to check as ongoing issues with these units since installed - they refuse to repair under warranty but will replace some parts and are quoting for further works - water2water have only charged what Arcus have invoiced for so far have not marked anything up. did not receive invoice from them until 29.12.2020 so could not upload invoicing till then. there is no sign slip.
MSA-DCA | WA3870247 | Winch room - Leaking air con unit DX0606 | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 6-Winch Room - West | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 11:30:00 | Pass | DX-06-06 dripping water in Tower Room. Unblocked using nitrogen.
MSA-DCA | WA3870542 | lawn damaged sprinkler water leak | Perth Cultural Centre Precinct-Museum Plaza (James Street)-Ground Floor | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-11 10:15:00 | Fail | Found that the tap timer valve opposite the Library has been tampered with (valve manual lever) was left in open position
MSA-DCA | WA3870557 | BMS fault VAV 5 and out side air fan | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 17:57:10 | 2020-12-10 11:00:00 | Fail | job completd - Full program/input/ outputtests were carried out. No faults were found, and the unit was reengaged to the VAV box.Test equipment in the kitchen proved the VAV unit was fully controlling to its full auto controlparameters. Kitchen space temp started to lower, but room temps on the day stayed higherthan set point due to the very high ambient weather.
MSA-DCA | WA3870614 | plantroom Chiller 1 having intermittent faults. Please arrange for Air Vision to attend and inspect | Collection and Research Centre Welshpool-Harry Butler Centre | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-16 16:30:00 | Fail | Attended site. Chiller 1 system in fault. Applied tests and checks. Investigation found system compressor circuit 1 to be faulting via an evaporator low pressure transducer lock out error. Carried out tests and checks via microtech controller. Investigation found discrepancys in transducer pressure readings. Removed LP pressure transducers and re siliconed greased and installed. Reset microtech controller. Tested system operation and monitored progress. System operating correctly and fault due to power interruption to building.
MSA-DCS | WA3869937 | Gatehouse - black gate is not closing flush properly. | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 06:51:08 | 2020-12-09 18:45:00 | Pass | 09/12/20Adjusted limits.Tested.Gate closes perfectly and microphonics switch engages.
MSA-DCS | WA3870004 | CCU, Holding Cells- Toilets are blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 07:44:53 | 2020-12-09 14:35:00 | Pass | Unblocked sewerline behind ccu
MSA-DCS | WA3870018 | Perimeter inner fence, zone 9 is constantly activating | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 11:55:44 | 2020-12-09 12:02:00 | Fail | Tested zone 9 for 40 minutes tested all ok
MSA-DCS | WA3870019 | Unit 17 - C9 blocked toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-15 13:30:00 | Fail | Nill
MSA-DCS | WA3870111 | Administration - Lunch Room Cold tap isnt working in Admin tearoom. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 09:02:43 | 2020-12-10 08:30:00 | Pass | Nill
MSA-DCS | WA3870144 | Stores, Ladies toilet- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-10 15:00:00 | Pass | Repaired light
MSA-DCS | WA3870147 | Prison Industries, Female toilet - toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-11 08:20:00 | Pass | Replace cone rubber
MSA-DCS | WA3870150 | Unit 7, Cell S11- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-10 12:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3870154 | Prison Industries, Male toilet - sink leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-11 09:30:00 | Pass | Replaced leaking rubbers
MSA-DCS | WA3870186 | Unit 7 - C Wing window winding system is faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 11:00:00 | Pass | WINDER REPAIRED
MSA-DCS | WA3870192 | social visits main hall evap air con fan is rubbing on cowling and water pump not working | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 09:53:26 | 2020-12-09 13:38:00 | Pass | Arrived on site and signed in, checked over evap cooler found pump working, no noise coming from unit, isolated power and inspected no sign of anything rubing or loose,turned back on and tested all running ok at present.
MSA-DCS | WA3870283 | control room gate house 1st 4 positions on monitors 3 and 4 frozen | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 10:58:24 | 2020-12-10 08:00:00 | Pass | VMS reset and second tech walk test while first tech confirm alarm switching.
MSA-DCS | WA3870290 | PRU camera 60 in programmed room picture is not very good | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-22 11:00:00 | Fail | Check camera on system and inspect and can confirm duplicate job. Camera replacement has already been ordered on another job.
MSA-DCS | WA3870315 | interview room 3 door handle not locking the way it is surpose to | Midland (North East Metro) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-11 10:00:00 | Pass | attended site and carried out repairs to the door lock
MSA-DCS | WA3870343 | Unit 7 - A5 split pin missing in shower. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 12:30:00 | Pass | Nill
MSA-DCS | WA3870364 | Dairy wash down pump leaking | Karnet Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-24 09:00:00 | Fail | Complete
MSA-DCS | WA3870368 | inside front gate turn styles not responding to computer screen | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 11:36:46 | 2020-12-09 15:18:00 | Pass | Turnstyle breaker found off, turned on and EC cabinet breaker popped, checked 24vdc at turnstyle and changing state, security equipment operating correctly. Further works via another contractor required.
MSA-DCS | WA3870391 | Education- leaking water pipe under kitchen sink | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-24 11:00:00 | Fail | Correct times 23/24:12:2020. 10:00-11:00
MSA-DCS | WA3870398 | Plater come away from wall in office | Warminda Hostel | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-17 14:00:00 | Fail | patched damaged render to walls in office.sealed walls.
MSA-DCS | WA3870467 | Security office - Honeywell system not connectong with front gate. | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 16:42:54 | 2020-12-18 11:47:00 | Fail | Investigated and repaired system faults and tested ok.Job Complete
MSA-DCS | WA3870488 | Unit 6, doors 1,2 & 3 are intermittently opening | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 12:51:22 | 2020-12-10 08:00:00 | Pass | Technicians test all doors in unit 6 and confirm function. Cause of fault was a server communication outtage
MSA-DCS | WA3870492 | Unit 1, Pod 7- loud speaker not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 15:00:00 | Pass | replaced damaged PA speaker
MSA-DCS | WA3870505 | Unit 3, B11 - Toilet keeps blocking there is something down the line | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 12:59:22 | 2020-12-09 16:10:00 | Pass | unblocked toilet
MSA-DCS | WA3870545 | WWTP chlorine dosing pump faulty | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-29 13:17:00 | Fail | works completed Chlorine dosing pump is fine but does not dose correctly due to probe being faulty.Chlorine probe requires replacement. Has not worked properly and cannot calibrate since power surge during lightningstorm months ago
MSA-DCS | WA3870546 | Kitchen- Evap on roof B side dining room is leaking water | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 13:46:40 | 2020-12-10 10:00:00 | Pass | COMPLETED
MSA-DCS | WA3870550 | WWTP final effluent meter faulty not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-08-18 14:14:00 | Fail | Took photos and spoke with Jacob Shaw about the meter.This works ok, there is no faults it just reduces with a blockage from time to time and reads incorrectly if not cleaned.
MSA-DCS | WA3870552 | wwtp anoxic tank mixer faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-29 12:13:00 | Fail | Works completed - Anoxic tank mixing pump is currently working as designed and does not require replacing.
MSA-DCS | WA3870576 | Unit 13, Cell alarms are activating | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 18:17:00 | 2020-12-09 17:31:00 | Pass | Unit 13 status displaying normal on departure
MSA-DCS | WA3870584 | Investigate dampness Unit 1 A wing | Bandyup Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-02-10 15:00:00 | Fail | Re point brick work outside ablution block.Supply and install vents to external brick wall.
MSA-DCS | WA3870589 | Unit 7, Cell H24- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-10 13:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3870623 | Main Spin walkway - Turnstile keeps tripping power | Melaleuca Prison | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 15:01:48 | 2020-12-09 20:00:00 | Pass | 09/12/20Inspect turnstile. Test numerous times.Working fine at turnstile, however not working from Access Control - SEME to resolve.
MSA-DCS | WA3870733 | Zone 1 & 2 - sense test failed/ faulty (offline) | Boronia Pre-release-Security Perimeter | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 19:57:57 | 2020-12-10 15:30:00 | Fail | Gallagher 6000 controller asset# A401302245 has been replaced for new and is now fully operational. RFI power supply suspected cause of issue, power supply did not recover correctly after being tested. Supply powered up and down quickly on its own multiple times before blowing fuse. Replaced RFI power supply with powerbox 12v 10ah supply and tested fully operational.
MSA-DCS | WA3870786 | Sally port outer gate - gate not automatically closing all the way. Latch already down on gate | Roebourne Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 09 Dec 2020 | 2020-12-10 00:20:24 | 2020-12-09 18:30:00 | Pass | 09/12/20Checked operation of door.Working OK.Possible explanation for fault as described was plunger on receiver end being stuck in.Lubricated plunger.Tested gate several times.Operating OK.
MSA-DCS | WA3870790 | Check Unit 7 E wing shower block for leaking pipes in the wall/ceiling spaces | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-11 13:00:00 | Pass | Rewashed leaking tap
MSA-DCS | WA3870866 | Gatehouse - turn style is not working. | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 19:53:01 | 2020-12-18 11:45:00 | Fail | Repaired turnstyle control faults and tested OK.Job Complete
MSA-DCS | WA3870869 | Key issue EBI is not operational | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 22:35:10 | 2020-12-10 09:30:00 | Pass | Attended site checked and found security officer has worked out the EBI workstation problem and all service back online. Late job cancellation.
MSA-DCS | WA3870870 | EPS is offline and 11 Omni trax offline as well due to lightning strike. | West Kimberley Regional Prison | WSM-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | COMPFIN | 09 Dec 2020 | 2020-12-10 06:39:55 | 2021-11-24 08:00:00 | Fail | 24/11/21 tested omnitrax 11 & checked ec9. all equipment online & alarms been received by control room
MSA-DCS | WA3870871 | Perimeter alarm fault Beam 1 TX Tamper has changed to open | Bandyup Prison-Entry Building | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 23:26:19 | 2020-12-10 09:45:00 | Pass | Cover found loose resecured retested working ok.
MSA-DFES | WA3870074 | Keycase can not be secured | CFRS Wangara | GMP-BR | Security | Keys & Access (SE) | Securex Security Systems & Services | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 10:25:00 | Pass | 09/12/2020, 1000-1025Reset ddl system. Got key locker secured and we tested it with a test call to ensure it will unlock and lock correctly
MSA-DFES | WA3870100 | Dorm 5 shower downlight dim, flickering when on and faulty/staying on when turned off | CFRS Kiara | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-05 15:30:00 | Fail | Arrived on site just after 1230. Staff arrived at 1250. Locate faulty light. The light globe was faulty investigate witch light globe is required. Swapped over the globe with a working one to confirm it was just the globe that is faulty witch it is. The hole cut out the the light is 70mm. The plug for the light is up on the beam and I could not reach it. Investigate if I could get in to the ceiling witch I can’t. The ceiling is suspended. Will need to order a replacement globe advised staff of work completed.
MSA-DFES | WA3870104 | Dorm 6 - Air Con has a fault "CH05" | CFRS Kiara | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2021-03-02 13:00:00 | Fail | Removed old pcb and installed new pcb
MSA-DFES | WA3870242 | Dorm 9 severe water hammer in shower | Butler Career Fire Station | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-12 09:27:00 | Fail | If water hammer in dorm 9 have Minimized the water hammer talked to the Senior officers and they are happy
MSA-DFES | WA3870255 | side of building roller door top part of the door has come out of housing | O'Connor Fleet Storage | GMP-BR | Building | Doors (BU) | Go Doors | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-09 14:45:00 | Pass | COMPLETED
MSA-DFES | WA3870338 | block 7 ground FF's new shower paint flaking on ceiling, cornice and light sensor - see notes | CFRS Claremont | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-12 10:30:00 | Pass | Work completed
MSA-DFES | WA3870383 | Kitchen- Flick mixer tap in sink is stiff to open | CFRS Osborne Park | GMP-BR | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 10:00:00 | Pass | Attended on 10.12.2020 no access given - returned on 14.12.2020 repaired system replaced mixer tap T2 Base and replaced Brass Mini stops - tested
MSA-DFES | WA3870472 | Engine room - Tiles broken in toilet and shower facilities | VFRS Mandurah | GMP-BR | Plastering | Plastering (PL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 12:00:00 | Pass | Re grout shower floor wastes remove and renew silicone to floor and walls
MSA-DFES | WA3870514 | GYM door - Aluminum frame - has pulled out from bricks (unable to secure door) | CFRS Osborne Park | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 10:00:00 | Pass | Attend site to report of P1 - Make door operational and make safeCosts to follow for BRAF and Remedial Works
MSA-DFES | WA3870515 | Blinds in Sth west Dorm fixing brackets not working correctly | VFRS Mandurah | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-21 10:18:00 | Fail | completed & Invoiced
MSA-DFES | WA3870541 | 21 Engine Room- Red LED strip warning lights on rear door 3 do not work.- see notes below | CFRS Wangara | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-02-17 15:00:00 | Fail | Locate faulty roller door lights. I found that door 3 lights on green is working fine but the internal light bar is a very faint red when the door is going up or down. Checked the connections and they seem fine. Will need a new light bar. It looks like some have already been replaced. The faulty light does not have a product sticker I have taken photos off the other light bars on site.
MSA-DFES | WA3870702 | driveway gate timer gate for shift change is not working - please see notes | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | Go Doors | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-08 10:30:00 | Fail | Complete
MSA-DFES | WA3870705 | Broken ceramic soap holder in Sth West toilet area, has sharp edges | VFRS Mandurah | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 10:00:00 | Pass | Replace damaged soap dish grouted to match Patch paint w/c wallRe grout shower floor wastes remove and renew silicone to floor and walls
MSA-DFES | WA3870759 | outside, especially around laundry trough area - Mosquito infestation, day and night. | CFRS Osborne Park | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 13:45:00 | Pass | Carried out treatment for mosquitoes. Applied residual insecticide spray around external perimeter, particularly around laundry trough areas.
MSA-DTAG | WA3870175 | Admin, registry - Several walls in office area indicate loose plaster/paint (patch & paint required) | Joondalup Courthouse | GMP-BR-HO | Painting | Internal (PA) | PPM Project Painting & Maintenance | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 14:00:00 | Pass | Repair & Paint damaged walls
MSA-DTAG | WA3870206 | Level 6 - The security PC has no power and we aren’t able to turn it on | State Administrative Tribunal (SAT) | GMP-BR-HO | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 13:57:40 | 2020-12-09 13:00:00 | Pass | Attended site. Found Workstation power supply faulty from power surge. Replaced power supply & restoredWorkstation. UPS system is electrical distribution. Electrician required for UPS checking.Job completed.
MSA-DTAG | WA3870231 | custody Repair cracks in custody cell bench seats | Midland Courthouse | GMP-BR-HO | Furniture | Commercial Furniture (FU) | Midolo Building Services | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-30 11:50:00 | Fail | repaired and painted bench seats
MSA-DTAG | WA3870323 | female public toilet, interview room 7 & court 2 light bulbs blown | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 15:14:00 | Pass | Replaced 12 x globes in courtroom 2Replaced 2 x fluoro tubes in interview room 7Replaced 2 x globes in female toilet
MSA-DTAG | WA3870548 | SAT security system has limited functionality- see notes below | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 09 Dec 2020 | 2020-12-09 17:43:25 | 2020-12-10 11:00:00 | Fail | Job completed - Attended site. Configured Operator SAT to log in under Admin Group privilege. Tested and showed working, all OK
MSA-DTWD | WA3870007 | A Block South, Auto door has stopped working | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 09 Dec 2020 | 2020-12-09 17:00:00 | 2020-12-09 22:55:00 | Fail | Inspected door and found external sensors were faulty, replaced 1x microhead sensors.After further inspection also found batteries were out of date, replaced 2x 12v 7ah batteries, reset the door.Tested door in all mode, tested door operation a number of times, all working fine.
MSA-DTWD | WA3870107 | front carpark Faulty car park light | Muresk Institute | GMP-BR | Electrical | Lighting, External (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 13:30:00 | Pass | job completed - replaced faulty light
MSA-DTWD | WA3870131 | BLD 826 bathroom middle toilet leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 14:00:00 | Pass | Job completed - Repair leaking toilet Building 826
MSA-DTWD | WA3870135 | A block, Main Entry, Level 1 - Repair controller to A Block inner entry Main Door | East Perth Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-09 12:24:00 | Pass | Attended site 8/12/20 Inspected door and found output charging volts of the controller is too high (34.7)tested power supply all ok, controller is faulty, please quote for 1xES 200 controller 2x 12v 1.7ah batteries and 1x battery fuses.
MSA-DTWD | WA3870137 | Vet Lab Toilet, Ladies toilet is leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 15:00:00 | Pass | job competed - Repair leaking ladies toilet at Vet Labs
MSA-DTWD | WA3870141 | Hughes Hall, Flat D, Kitchen - Tap is dripping | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 11:00:00 | Pass | Job completed - Repair leaking taps to kitchen Hughs Hall Flat D
MSA-DTWD | WA3870142 | Southern Hall A and C kitchen blocked sink | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-09 12:30:00 | Pass | job completed - Clear blockages to sinks Flat A and C Southern Hall
MSA-DTWD | WA3870211 | Gardeners staff room Tap dripping on wall near fan | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 13:30:00 | Pass | Repair leaking tap to gardeners staff room
MSA-DTWD | WA3870310 | G Block- Electronic keypad is faulty near room G23 | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-17 09:45:00 | Fail | Repairs to keypad
MSA-DTWD | WA3870334 | D block, level, plant room - Repair make up pump Green Skills Chilled water supply | East Perth Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2021-04-12 10:00:00 | Fail | Accessed level 4 plantroom. Removed air from system schw. Inspected pressure vessels and ok.Valves to water lines open and in good condition.Noise was found to be water movement past actuator to be occuring due to angle of valve.Not air noise as expected.Noise does disappear when valve fully open.Bms controls action, returned to auto.
MSA-DTWD | WA3870342 | R block, R014 - Passage entry light to class rooms, switch is broken and requires immediate repairs | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 08:48:00 | Pass | Repalced fualty light switch in roo14 corridor.job completed
MSA-DTWD | WA3870349 | A12 Conference room - Reverse cycle split A/C not operating; | Rockingham Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-18 10:59:00 | Fail | Gathered tools and equipment assisted by Dave with working at height. Isolated unit and locked out. Dismantled unit and Replaced new condenser fan motor and fan. Replaced new PC main board checked Op all ok reassembled unit, cleaned up and completed paperwork and signed out.
MSA-DTWD | WA3870432 | J Block, J111 - male urinal is backing up and requires looking at.. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-15 11:02:00 | Fail | Cleared blockage using plunger
MSA-DTWD | WA3870521 | Front of building- swimming pool at front of main entry needs repair, see notes below | Perth Campus B2 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-02-09 07:00:00 | Fail | Attend site, access pool using boom lift and core hole into base of pool at the lowest point to allow drainage as requested by site. Exclusionzones and barriers to be erected around work area for duration of works, liaise with council for permits if required, all works to take placeearly morning out of hours. Internal content if pool is unknown, we cannot accept responsibility for future performance of pool or ongoingdefects caused by drilling hole nor drainage capacity. boom lift to be delivered to the job location and driver to remain in the area to removemachine immediately after its use, allowance for obstruction permits and temporary barriers for duration of works
MSA-DTWD | WA3870528 | plant room - Network fault on BMS | Perth Campus B6 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 3 | COMPFIN | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 00:00:00 | Pass | completed-Work order cancelled close out at $0 cost
MSA-DTWD | WA3870536 | A block, Disable shower/toilet - Smoke sensors faulty in shower areas | Fremantle Campus (formerly WA Maritime) | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | SCAVENGER SUPPLIES PTY LTD | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-06 14:30:00 | Fail | A block, Disable shower/toilet - Smoke sensors faulty in shower areasSite:5101Location:South Metro TAFE-Fremantle Campus (formerly WA Maritime)Address 1:1 Fleet Street FREMANTLEAddress 2:WA 6160 Australia-COMPLETED
MSA-DTWD | WA3870551 | B block L1 male toilet ground floor blocked | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 10:30:00 | Pass | Complete
MSA-DTWD | WA3870586 | F block aged care 5x damaged locks | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 09 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-11 09:45:00 | Fail | repairs to lock
MSA-MRWA | WA3870683 | several data outlets require testing | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 09 Dec 2020 | 2020-12-10 17:00:00 | 2020-12-10 09:45:00 | Pass | Attended site and signed in. Spoke with staff regarding data testing. Can not test the specifics that site is requiring. Misunderstanding regarding the scope that was asked by facilities. Close job. Job complete
MSA-DCA | WA3871128 | Break glass not operating correctly | State Library of WA-Main Building-Level 4-Open Office Area - Next to Great Southern Room | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-11 13:00:00 | Pass | repairs to break glass
MSA-DCA | WA3871583 | Large crack in toilet contact Sue Murray for site access-photo to follow in email | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 13:05:00 | Pass | Replaced cracked toilet,cistern, toilet seat,leakinf ministop, and flexi
MSA-DCA | WA3871648 | High humidity alarms | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-16 09:22:00 | Fail | Attended site. Multiple hi humidity alarms. Chiller 2 refrigerant leak detection alarm enabled ChWP 2 which caused supply water temp to the building to rise to 11°c. Discussed issue with ENVAR. Isolated and tagged ChWP 2. Checked Chiller 2 for refrigerant leak, no leak found. Detector reading 1000ppm, out range, on BMS. Faulty detector likely. Monitored and adjusted zoning on AHU's to reduce hi humidity. All zones below 60%rh and some zones starting to clear at time of departure.
MSA-DCS | WA3870997 | MPU (8), Cell M15- No water, sink not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 07:11:25 | 2020-12-10 14:30:00 | Pass | Nill
MSA-DCS | WA3870999 | MPU(8) - Error code & alarm beeping on fridge next to oven,cooling fan looks blocked with dust etc | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 10 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-10 12:30:00 | Pass | Arrived on site and signed in, checked over fridge found coil blocked with dust,cleaned out and reset,turned back on and tested all running ok at present.
MSA-DCS | WA3871030 | Boot Shop- High Bay lights keep tripping out | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-12 13:00:00 | Fail | Isolated faulty lights. Replaced faulty hi bays in boot shop with scissor lift.
MSA-DCS | WA3871031 | Reception - Jacking Pump for the Fire sprinklers has died | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 07:54:45 | 2020-12-14 14:06:00 | Fail | Attended site to install new pumpAfter more investigation it was found there was no water to the valve room it looks like the in ground sluice valve has broken and isn’t openingPlumbers have been notified of this issue
MSA-DCS | WA3871057 | Kitchen, Maqimm Large freezer - Freezer not holding temperature | Hakea Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 10 Dec 2020 | 2020-12-10 12:09:52 | 2020-12-10 10:52:00 | Pass | Arrived on site and signed in, checked over freezeroom found room down to temperature, checked over all running ok, suspect was on defrost when they checked it.
MSA-DCS | WA3871078 | Visits- Irrigation valve not shutting off & no pressure | Wandoo Rehabilitation Facility | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 10 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 10:15:00 | Pass | Locate and replace faulty valve, tested system.
MSA-DCS | WA3871102 | Jasper, A Wing- Air con not working (flashing green light) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 09:56:00 | Pass | Complete. Parts for this unit already quoted on maintenance.
MSA-DCS | WA3871139 | Unit 2, lower landing light fitting not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-15 13:30:00 | Pass | Repaired light
MSA-DCS | WA3871214 | Zone 1 roller doors faulty will not operate | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 10 Dec 2020 | 2020-12-10 14:00:14 | 2020-12-10 11:00:00 | Pass | Unit 1 Industries roller door not working, found beam wasn't lined up.
MSA-DCS | WA3871232 | MPU (8), Cell M19- Toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 10:17:12 | 2020-12-10 15:30:00 | Pass | Nill
MSA-DCS | WA3871238 | Unit 1 - The Whole Unit Sprinkler Jacking pump has failed | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 10 Dec 2020 | 2020-12-10 14:21:58 | 2020-12-16 14:01:00 | Fail | Attended site and found that jacking pump was operating ok electrically but not generating pressure requires new pump.Pump switched off at this time.Pump details below.Winmax pumpCM6/410-50 L/min.75kwNote hard wired do will require electrician to attend also.11-12-20MH cVWent to repipe to pick up new jacking pumps and fittings, then went past alied pumps to get some 25mm flexible hosesArrived on site and inspected unit 1 jacking pumpFound the jacking pump pressure switch was isolated because the jacking pump wouldn’t switch off , after further investigation it was found the was no water pressure in the combined mains nor was there any in the sprinkler installation ,After more investigation it was found there was no water to the valve room it looks like the in ground sluice valve has broken and isn’t openingPlumbers have been notified of this issueHave left the main stop valve closed on the sprinkler installation , this will need to be reinstated once a water supply is p
MSA-DCS | WA3871246 | Download CCTV footage. Please contact Mario Kovac for additional information | Karnet Prison Farm | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-10 16:15:00 | Pass | Downloaded CCTV footage as per request from Security Officer Mark Cundell. Footage copied to portable 1TB hard drive and handed to MARK CUNDELL.
MSA-DCS | WA3871264 | MPU (8), Cell M18- Sink not working, no water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 14:30:00 | Pass | Nill
MSA-DCS | WA3871345 | Unit 13, Cell D2- Lights not working in cell, see notes below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-15 08:30:00 | Pass | Repaired faulty lights in unit 13 d2
MSA-DCS | WA3871357 | Admin- Air Con fault; 20 degree’s this morning 28 degree’s this afternoon and no setting changes | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 11:43:26 | 2020-12-11 10:15:00 | Pass | Arrived on site and signed in, checked over aircond found unit running,gas pressure ok, system running ok at present.
MSA-DCS | WA3871360 | OPS Post 7, Tower 7- Air Con is not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 11:45:30 | 2020-12-11 11:18:00 | Pass | Checked over aircond found remote set on heating,switched to cooling and tested all running ok at present.
MSA-DCS | WA3871394 | Unit 10 A3 floor drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 12:04:05 | 2020-12-10 16:10:00 | Pass | Unblocked sewer line
MSA-DCS | WA3871434 | Gate control- Alarms for NTCE CRIB light box TMP2 | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-10 14:00:00 | Pass | Tamper checked and found to be legitimate. All test ok.
MSA-DCS | WA3871437 | Bakery- Power points next to small cake bench mixer not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-10 15:00:00 | Pass | Investigated and restored power to bakery store circuits
MSA-DCS | WA3871453 | Canteen West, Lock problem with door- Key will not lock door most of the time | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 12:52:29 | 2020-12-10 15:15:00 | Pass | Attend site. Replaced lock to restore normal function.
MSA-DCS | WA3871457 | Grounds- Several stations not working suspected broken pipe, front of units 3,4,5 | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-15 10:00:00 | Pass | SERVICED VALVE AND RETURNED TO SERVICE
MSA-DCS | WA3871478 | SHU (9), West- Boiling water unit keeps tripping the power | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-17 12:10:00 | Fail | replaced Probe Level Sensor, Solenoid, Element, Controller Heatsink + flexihosing S/Steel to RHEEM removed to workshop as per client request to test before.. Reinstalled unit - Didn't connect water/power as requested by client.
MSA-DCS | WA3871486 | Reset Centre Toliet No 2 in reset center blocked.- paperwork at the Gatehouse | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 13:16:19 | 2020-12-11 08:30:00 | Pass | Nill
MSA-DCS | WA3871538 | EC8 and 9 damaged relays in electrical cupboards - photo emailed | West Kimberley Regional Prison | WSM-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:19:17 | 2021-05-31 21:26:50 | Fail
MSA-DCS | WA3871541 | Unit 4, Control Room- AC not working is not cold | Casuarina Prison | GMP-GR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2021-02-01 11:46:00 | Fail | Installed new Daikin unit
MSA-DCS | WA3871543 | TR2,4,5,6,7,8,9,commnications failure. MDAS down across site | West Kimberley Regional Prison | WSM-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:23:25 | 2021-04-20 11:53:00 | Fail | Repairs completed Parts from site stock replaced.90237498 GT 07.04.21
MSA-DCS | WA3871545 | Omnitrax off line | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:24:25 | 2020-12-11 18:00:00 | Fail | Omnitrax module 2 offline. Constant false alarms starting at Zone 11. Found faults with blown fuses in EC5 (OX Processor 3) and EC7 (OX processor 1). A and B side Comms ok. Omnitrax system stable. Zones tested ok.
MSA-DCS | WA3871546 | Laundry, washing area - 80kg showing low oil | Hakea Prison | GMP-BR- HO | Cleaning | Cleaning (CL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:21:29 | 2020-12-11 14:00:00 | Pass | Inspect and test machine, oil low.Supply and fill 1.1 litres of lube oil.Test machine, w/m tests ok.
MSA-DCS | WA3871549 | Unit 2 house5 expander Not responding | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:26:49 | 2020-12-22 08:42:00 | Fail | Transferred expanders to spare data point, brought equipment back online and tested.U2 H1 + U1H1Works complete
MSA-DCS | WA3871554 | Vegetable Prep- Power Point in the left coolroom hanging from the ceiling has some exposed wires. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:26:59 | 2020-12-11 08:30:00 | Pass | Repaired damaged pendant gpo in veggie prep coolroom
MSA-DCS | WA3871555 | Visitors centre UPS failed-By passed. | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 14:27:49 | 2021-01-15 08:00:00 | Fail | Checked UPS and its operating as per usual. Found AC Lead Faulty and replaced. Tested operation with AC Fail and HLI to Gallagher, all is in working order.
MSA-DCS | WA3871671 | Unit 9 - Cell call alarms are going off. | Hakea Prison-Unit 9 64 Cell Prison Living | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Dec 2020 | 2020-12-10 21:17:41 | 2020-12-18 15:57:00 | Fail | Job attended and completed through WA3871671.
MSA-DCS | WA3871991 | Hakea Prison - Unit 1 - Corridor Camera not working. | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Dec 2020 | 2020-12-10 20:33:44 | 2020-12-10 19:00:00 | Pass | Camera image has been restored and tested ok.
MSA-DFES | WA3871242 | Commissioner's Bathroom- Shower head is not spraying | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-21 09:00:00 | Fail | Investigate shower head not spraying, no pressureSupply and install new shower head, attempt to locate isolation in ceiling Caroma shower cartridge also leaking and will need to be replaced may need to try find extension for cartridge due to incorrect installation and mixer not opening fully Will need to return once sourced partsPack up and clean up worksite Isolate water to commissioners bathroom , isolation located ceiling in meeting room Remove tapeware and old mixer cartridge, supply and install new mixer cartridge, turn water on and check for leaks Test operation, pack up and clean up worksite
MSA-DFES | WA3871589 | Lecture room 10 - Air conditioning unit not functioning properly, doesn't stay at full cooling | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 11:30:00 | Pass | Aris Moulavasilis (17/12/2020) Arrived on site & signed in.Next I entered lecturer room 10 where AC is located.AC is 10 Kw wall mounted split..Turned AC on for testing. First I tested this AC on cooling.Cooling test.Supply Air 10cReturn Air 22c TD 12K Condensing unit is clean & appears to be in good working order.Next I turned AC on to hearing mode this will create heat load as ambient temp was 25c.AC was ran on heating for 20 mins.Supply Air 49cReturn Air 27cTD 22 KHeating & cooling appear to be working fine.Then turned AC back on full cooling whist I asked staff members for any more information on this AC. All staff that are based in lecturer room 10 are on annual leave.Next I completed a calculation to determine if A.c. was under sized this is not the case.But ideally having 2 Ac at 5 Kw each, at north & south of the lecture room, would distribute better conditioned Air through the room. (As distance is approx. 12M)( Room size 12M - 6M)Also it appears that office
MSA-DTAG | WA3871217 | Lvl 4, Kitchen, Adult Court Services- Leaking tap | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-14 11:00:00 | Pass | Complete
MSA-DTAG | WA3871417 | L1 male public toilet Vomit in the male public toilet | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 18:30:00 | Pass | Vomit Male Public Toilets
MSA-DTAG | WA3871446 | Lvl 11- Air Con in 3 Judicial Chambers has no air flow coming & extremely hot | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2021-01-23 11:00:00 | Fail | Attend site with icon logic. Access BMS and carry out operational testing of vav box 11.14. Hot side of box working but cold side un responsive. Icon carried out testing of bms and found lev 11 to become offline. Reset controller on level 12 and found level 11 to come back online. Further testing found VAV to keep driving to minium airflow, found vav not looking at AHU supply air temp causing this issue. Icon logic carried out program changes to allow communication between AHU and VAV. Also found this issue with other vav boxes throughout the building. Rectify all communication issues and found VAV boxes to start operating as normal. Check airflow through vav box and now reaching airflow max setpoint. Relocate temp sensor from ceiling to original location on wall. Test calibration of sensor, found to be reading correctly. Temperature in conditioned area now controlling correctly.
MSA-DTWD | WA3870990 | E block,Restaraunt kitchen- broken power point for the Combi steamer | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 10 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 11:27:00 | Pass | Attended site and inspected outlet. Found isolator to be cracked. Called various wholesalers for replacement and left site for new isolator. Returned to site and replaced
MSA-DTWD | WA3871129 | D block L1 D26 AC Plant room. AHU 4 motor is not running in AUTO or MANUAL-see notes | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-11 14:00:00 | Pass | Travelled to site, Signed in collected keys, accessed plant room, locked out unit, removed 3 phase hrc fuses and checked with meter, all ok, traced wiring to find contacts, found a overload had tripped, reset, and checked and tightened terminals to contactor and overload, checked motor belts and motor terminals, all ok.Notice motor is rated for 14amps but overload set at 13.8amps.Adjusted overload settings, removed isolation and ran system, checked phase current draw which was 11.5 - 12.3 amps per phase.Monitered unit all ok
MSA-DTWD | WA3871137 | L1 IT office Repairs to access control system subnets and IP addresses - see notes | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2021-03-31 15:30:00 | Fail | Attende site with Michael Beresford to assist with re locating all the access control devices onto thenew site network.Re addressed network controllers as required.
MSA-DTWD | WA3871158 | S block S106 Repair Sensor to Auto door S Block Main Entry | Mount Lawley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 11:11:00 | Pass | 1077682. Call to site. Attend to auto door. Locate to and replace failing external activation sensor and calibrate. Test operational and safety features- all okay.
MSA-DTWD | WA3871159 | Library & street air intakes blocked | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2021-01-27 12:19:00 | Fail | BRAF work has now been completed. RA vent within library and out side air intake at street level have been cleared and cleaned. Works are completed.
MSA-DTWD | WA3871308 | L2 mens toilet near main entry - urinals both blocked cleaners cannt fix | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-14 18:06:00 | Pass | Unblocked urinals
MSA-DTWD | WA3871351 | H Block, Room HG01- Split system air con not working, suspect filter needs changing. | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-16 09:30:00 | Fail | Arrived on site checked in with Marty, logged on site, gathered tools and equipment, started fault find on a/C in room. Located fault unit in heating mode, changed to cooling mode unit started monitored operation all ok. Cleaned up and completed paperwork.
MSA-DTWD | WA3871411 | L4 plant room Condensate trap has a blockage | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-21 15:33:00 | Fail | Recieved job and attended site gained access and carried out inspection due to water leakage noted at AHU UG-11. Shut down isolated and inspected. Blockage cleared from AHU condsation trap. Water line tested and drain pan flushed. Work area left tidy.
MSA-DTWD | WA3871571 | Block 10, Room 10G75- Door hinges dropped so door is hard to shut/lock | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 15:00:00 | Pass | Remove door from frame and re-secure frame on hinge side and rehang door adjust hinges and striker.
MSA-DTWD | WA3871633 | Block 7, student lunch area - Water running out of south end evaporative air conditioner | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2021-02-12 10:30:00 | Fail | Accessed the canteen roof , working at heights. Removed the old evap pads and fitted the new one's.
MSA-DTWD | WA3871638 | Block 2 ground External disabled toilet Switch for light and fan faulty.-see notes | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 10 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-18 15:30:00 | Fail | Attended site and signed in. Located disabled toilet. Isolated power. Disconnect and removed faulty switch. Supply and replace with new switch. Clean and tidy site. Job complete
MSA-DTWD | WA3871656 | E block, ET02 Classroom - AC blowing hot air | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 10 Dec 2020 | 2020-12-15 17:00:00 | 2021-01-13 11:30:00 | Fail | Found condenser fan motor failed. Picked up parts. Returned to site. Replaced failed fan assembly. Checked operation. All ok
MSA-MRWA | WA3871423 | test three ports 4.62, 4.68 and 4.69 as users are reporting degraded service - see notes | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor-Communication Equipment Riser | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 10 Dec 2020 | 2020-12-11 17:00:00 | 2020-12-10 15:50:00 | Pass | Complete
MSA-DCA | WA3872043 | RO plant fail alarm | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 11 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-16 09:30:00 | Fail | COMPLETED
MSA-DCA | WA3872170 | boiler in fault making loud screeming noise | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Precise Air Group | 1 | CLOSE | 11 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-17 08:00:00 | Fail | Investigate boilers and found no faults present. Precise Air to engage boiler contractors to meet on site to do further investigation.
MSA-DCA | WA3872261 | Plant room - BMS equipment in fault | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 1 | SSP | 11 Dec 2020 | 2020-12-14 17:00:00 |  | Overdue
MSA-DCA | WA3872530 | Beaufort street bollards - bollards have dropped and not going back up | Perth Cultural Centre Precinct | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 20:25:58 | 2020-12-11 19:35:00 | Pass | Attended site, Relay went out on Heat alarm, re set and all tested OK.
MSA-DCS | WA3871855 | Abattoir floor to floor - split down saw is not working. | Karnet Prison Farm-Abattoir Change Rooms | WSM-BR-SITE | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 06:34:16 | 2020-12-11 11:00:00 | Pass | Repair Abattoir split down saw
MSA-DCS | WA3871902 | Retic Pumps, Located near tank outside prison- Retic Pump pressure assessment | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 11 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 13:00:00 | Pass | RESET PUMPS AND RETESTED AND ALL IN WORKING ORDER.
MSA-DCS | WA3871919 | Grounds- Lock is Faulty on the grounds office door, barrel keeps spinning around | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 11 Dec 2020 | 2020-12-17 17:00:00 | 2021-01-20 12:15:00 | Fail | Service lock requires parts.Replace bolt throw and lever pack.
MSA-DCS | WA3871932 | Unit 7, Cell E21- toilet smashed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 07:48:30 | 2020-12-11 14:38:00 | Pass | Replaced smashed toilet, toilet seat and button
MSA-DCS | WA3871934 | Unit 7, Cell E21- Viewing hatch window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 07:49:59 | 2020-12-11 15:00:00 | Pass | VIEWING WINDOW RE GLAZED
MSA-DCS | WA3871935 | Unit 7, Cell E21- Cell window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 07:51:01 | 2020-12-11 15:00:00 | Pass | CELL WINDOW/FRAME REMOVED/REPAIRED AND RE GLAZED
MSA-DCS | WA3871940 | Unit 9, Control Room - Cell Call System constantly buzzing | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 07:52:46 | 2020-12-11 10:00:00 | Pass | Cleaned removed resecured connections, retested ok.
MSA-DCS | WA3871941 | Reception, Property Office- Air Con not cooling | Hakea Prison | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 07:54:10 | 2021-02-10 09:30:00 | Fail | Checked over aircond found unit running, checked gas pressures all ok, system running ok at present.
MSA-DCS | WA3871995 | Court services- front tamper sensor activated. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-13 09:30:00 | Pass | Cabinet secured ok. Reset controller from PC. Tamper alarm cleared.
MSA-DCS | WA3872001 | Laundry Air-conditioning blowing hot air | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-12 15:00:00 | Fail | Accessed Laundry area.Checked vent.Airflow ok.Checked over controller and found unit running fan only.Activated cooling.Unit shut down.Pre cooling pads.Fan started.Cooling okay.Advised staff in area of 'pre soak cycle'
MSA-DCS | WA3872006 | ISU- Cell call connect between ISU & Control is inaudiable | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-15 12:00:00 | Pass | Volume for cell call station found set to high level reduced retested multiple cell units test ok.
MSA-DCS | WA3872017 | Air Con is not working, unable to turn off isolator switch | Boronia Pre-release-AK19 - Library, Education Personal Development-Ground Floor-Kiosk | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 09:13:39 | 2021-01-19 15:25:00 | Fail | New cassette system installed & commissioned set to work
MSA-DCS | WA3872020 | Air ventilation system not working - C and D wing | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 13:14:51 | 2020-12-15 09:00:00 | Fail | COMPLETED
MSA-DCS | WA3872044 | unit 4 adjust door alarm of prisoner houses from 06.30 hrs to 06.00 hours SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 09:03:00 | Pass | Reprogram alarm zone schedule for unit 4 houses as per instruction from security.
MSA-DCS | WA3872045 | ISU, D10 - blocked toilet | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 09:30:53 | 2020-12-11 14:31:00 | Pass | Cleared blocked toilet in D10.There was a disposable cup stuck in the toilet pan.
MSA-DCS | WA3872046 | unit 5 control room CCTV camera not working - SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 09:32:16 | 2020-12-14 08:00:00 | Fail | Master power supply hard reset and camera views restored.
MSA-DCS | WA3872070 | Unit 1, C9 - Cistern large plastic nut on outlet valve broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 09:49:29 | 2020-12-11 14:38:00 | Pass | Unable to start job on time due to movement in the wing. Replaced broken nut
MSA-DCS | WA3872075 | Unit 1, D wing Shower - Both sinks waste’s waste damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 09:52:04 | 2020-12-11 17:10:00 | Pass | Replaced trap to LHS basin and replaced plug and waste and trap to basin on the RHS.
MSA-DCS | WA3872103 | Unit 7, H Wing- Hot water urn broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-21 14:25:00 | Fail | No escort available ON 15TH SEE EMAIL CHAINHAD TO REBOOK NEW DATES AND MOBILISE AND DRIVE OUT A 2ND TIME Replaced tap inlet solenoid and level sensors
MSA-DCS | WA3872106 | Unit 1, POD 5 Kitchen - hot water heater leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 10:37:43 | 2020-12-11 15:00:00 | Pass | Complete
MSA-DCS | WA3872112 | Monitors are frozen, zone 24 & 25 internal | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 14:45:00 | 2020-12-11 14:00:00 | Pass | repaired software fault & tested ok. job complete
MSA-DCS | WA3872122 | Unit 2 - A9 No water is running from the tap, when the tap is fully open. Tap is just dripping. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 10:36:59 | 2020-12-11 13:30:00 | Pass | Nill
MSA-DCS | WA3872189 | Security monitor is not clear and fuzzy | Maddington (South East Metro) | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 08:15:00 | Pass | Attended siteReplaced monitor as required - Dahua 27inch LCD Monitor Serial: PZO0AHJ00010051Advised site of the outcomeCompleted paperworkLeft site
MSA-DCS | WA3872217 | Gardens hot house fans not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-22 12:30:00 | Fail | Replace fan belt, repair cover, replace bearing, replace time of clock Hot House fans
MSA-DCS | WA3872220 | Unit 4, B & D - Windows in the shower blocks have metal strip missing from under the window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-15 14:30:00 | Pass | NEW SPIRAL BALANCES FITTED AND SLIDING SASH
MSA-DCS | WA3872221 | Unit 7, Cell C3- Toilet cistern is not filling completely, so not able to flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 13:30:00 | Pass | Nill
MSA-DCS | WA3872224 | Unit 4, A & C Sie- water pressure is poor throughut unit | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-15 15:30:00 | Pass | Nill
MSA-DCS | WA3872228 | Unit 4, Staff toilet is leaking water, see notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 13:30:00 | Pass | Nill
MSA-DCS | WA3872229 | Unit 4, C wing - cleaning cupboards lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2021-03-31 12:00:00 | Fail | Replace chubb mortise lockInstall custom made thickness strike plate
MSA-DCS | WA3872243 | Unit 4, D Wing - Light Fixture is falling off the roof | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 08:30:00 | Pass | Repaired damaged lights in unit 4
MSA-DCS | WA3872244 | control room, alarm screen not giving location | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 12:20:41 | 2020-12-11 15:40:00 | Pass | Restored alarm display issue, tested all fully operational
MSA-DCS | WA3872247 | Unit 2 - D1 hinges are damaged on the door and striker plate needs welding | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 09:45:00 | Pass | Replace hinges, repair lock and weld on strike.Replace barrel.
MSA-DCS | WA3872330 | CCU, Cell H1- Cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 13:19:40 | 2020-12-11 14:30:00 | Pass | Tested called from guard station reset retested from cell tested ok.
MSA-DCS | WA3872334 | Unit 4, Control Room Door Lock is faulty, see below notes | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 13:21:42 | 2020-12-11 15:45:00 | Pass | Attend site. Service/repair main door lock. Tested with several keys. Normal function restored.
MSA-DCS | WA3872355 | Fire valve broken in ground, no fire cover in unit 1 | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 17:31:50 | 2020-12-22 07:00:00 | Fail | Valve not broken valve had been isolated by contractor who damaged underground pipework.Underground valve not marked on the block plan so we had to search the grounds for it.Located and reinstated water to area.
MSA-DCS | WA3872426 | MPU (8) - West M13 Blocked Toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-21 11:30:00 | Fail | The last few blocked toilets in MPU have appeared to be blocked deliberately, finding full rolls of tiler paper in the bowl and some have had full plates of food
MSA-DCS | WA3872432 | MPU (8) - Light tube under the kitchen cupboard not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-21 11:30:00 | Fail | Checked damaged light in kitchen, picked up replacement fitting, installed installed and tested
MSA-DCS | WA3872443 | gate house fire alarm no audible alarm when hydrant system is set off | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 14:41:21 | 2020-12-12 10:32:00 | Pass | 12/12/20 EIAttended site & inspected FIP.Identified that the visual pump run leds Diesel pump 1 & Diesel pump 2 were blocked from direct line of sight of the gate house officer due to poorly placed signage on the front of the FIP’s clear perplex door.Found the FIP buzzer link removed from the back of the FIP PCB.Relocated the signage on the front of the FIP & re-fitted buzzer link.Performed a test & confirmed operation OK.
MSA-DCS | WA3872506 | unit 1 cell B1 blocked toilet over flowing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Dec 2020 | 2020-12-12 15:34:43 | 2020-12-11 17:29:00 | Pass | COMPLETED
MSA-DCS | WA3872516 | Gate house UPS no power to batteries.- SEME on site | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-22 10:31:00 | Fail | Restored UPS to normal operation and completed a Battery test with UPS controller, battery levels sufficient and test passed
MSA-DFES | WA3872047 | Outside front Garden -Retic needs fixing – water leaking at connection and unable to turn off water. | Armadale Regional Office | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-14 18:45:00 | Pass | Call Out & Labour
MSA-DFES | WA3872198 | Front entrance doors not opening properly - attend 16/12 llam to start with Go Doors | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 17:00:00 | Pass | Attend FIP for Go Door remedies
MSA-DFES | WA3872200 | Front entrance doors not opening properly - attend 16/12 llam to start with Go Doors | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 17:00:00 | Pass | 16/12/20 - Dylan ParslowDisconnected cables for auto door.Reconnected cables for auto door.
MSA-DTAG | WA3872021 | ground level, Buss P Chambers - Flickering Light in President’s Office | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 11 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-11 12:15:00 | Pass | Replaced blown lamps
MSA-DTAG | WA3872066 | Level 6 duress at counter desk 1 is faulty - not activating when pressed | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 13:45:00 | 2020-12-11 14:30:00 | Fail | Repairs to Duress
MSA-DTAG | WA3872089 | Custody, Outer Sallyport - Skirting board separating from the wall | Armadale Courthouse | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo Building Services | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-11 13:30:00 | Pass | SKIRTING RE SECURED TO WALL
MSA-DTAG | WA3872161 | Supreme Court, Stirling Gardens Complex - Lockwood contact sensor has fallen out of secure door | Supreme Court | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 15:22:26 | 2020-12-11 12:30:00 | Pass | Reed switch installed
MSA-DTAG | WA3872503 | Level 1 Room 210, Registrar Gilich’s Office - Water leaking from ceiling near light fitting | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 11 Dec 2020 | 2020-12-11 19:17:04 | 2020-12-14 09:00:00 | Fail | Return to site. Access roof and check water leak from previous friday. Found area to have dried up with no more visable leaks. Unit drain working ok.
MSA-DTWD | WA3872091 | Carpark 2 - Very large tree branch that has snapped off | Thornlie Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 11 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-14 07:50:00 | Pass | Tree works completed
MSA-DTWD | WA3872097 | E Block, Room EG08- Wall Mounted Split System AC leaking water down wall | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 14:30:00 | Pass | ATTENDED SITE SIGNED IN AND BOOKED OUT THE KEYS, FOUND THE EVAP RUNNING DOWN HILL , MOVED THE EVAP ON THE CORRECTANGLE AND LEVELLED THE DRAIN SO THE WATER RUNS DOWN HILL. FLUSHED OUT THE DRAINAGE SYSTEM AND REMOVED SOIL AND LEAF MATERIALS FROM AROUND THE DRAIN PIPE OUTSIDE. FOUND DRAIN FROM INDOOR UNIT SLIGHTLY RAISED. READJUSTED PIPE AND RECHECKED WATER FLOW. ALL OK.Cleaned out drain. Found bad install and drain running slightly up hill. Rectified issue as best as possible
MSA-DTWD | WA3872142 | Outside Southern Hall - Leaking Tap | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 12:30:00 | Pass | Replaced leaking tap
MSA-DTWD | WA3872146 | Tower building, left side lift is locked, doors stuck open & not functioning | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | SSP | 11 Dec 2020 | 2020-12-14 17:00:00 |  | Overdue
MSA-DTWD | WA3872168 | Lvl 3,Corridors Centre-East-West- Lights are blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-21 13:45:00 | Fail | Attended site and signed in. Located level 3. Found various lamps out. Replaced all tubes and starters out. All lights on floor corridors okay. Signed out job complete
MSA-DTWD | WA3872178 | Lvl 2, Room B209- Lock to exit door is faulty (See Steve Meyer for Details) | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 12:25:00 | Pass | Replace cylinder components to lock on B209
MSA-DTWD | WA3872222 | Block 7 ground kitchen Evaporative A/C does not appear to be working. | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 11 Dec 2020 | 2020-12-18 17:00:00 | 2021-02-12 13:00:00 | Fail | Accessed the canteen roof , working at heights. Removed the old evap pads and fitted the new one's.
MSA-DTWD | WA3872237 | U Block, U022 - Evap aircon continues dumping water | Balga Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Precise Air Group | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 16:00:00 | Pass | Attended site completed relevant sign in procedures, completed roof access permit , accessed evaporative units for room U022 , turned on and checked over operation, could not identify continuous dumping of water, identified small trickle from exterior drain , adjusted evaporative bleed off settings and monitored , all working as per spec , prior repairs completed by alternate company, turned units off , packed up site
MSA-DTWD | WA3872337 | Glasshouse major water leak on Evaporative cooler #2 | Murdoch Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 14:30:00 | Pass | Found the evap cooler on the greenhouse overfilling, the ball float was cracked and needs replacing. Picked up the parts from the supplier's, returned to site and fitted had to modify the pipe work a bit . Test ran all ok .
MSA-DTWD | WA3872450 | Outside BLD 830- Lights faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 16:30:00 | Pass | Job completed - replaced PLC lamps
MSA-DTWD | WA3872451 | D block D015 Staff toilets digital lock not working and replace faulty paddlock | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 11 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-14 11:30:00 | Pass | Job completed - replace digital lock on D015 & padlock on Q block
MSA-DCA | WA3872582 | room 3 ground floor leaking aircon unit | His Majesty's Theatre | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 12 Dec 2020 | 2020-12-14 17:00:00 | 2020-12-12 12:00:00 | Pass | Attended after-hours service call a requested. Accessed room 3 FCU and removed drain and spigot. Cleared and reassembled, tested drain with 5l of water. Reinstated power and test ran, found fan was drawing water of the top of the drip tray and leaking into roofspace. Lowered main drain run to improve fall which appeared to help with less water sitting in tray. Suspect there may be ongoing issues with the fall of the drain or have bio film build up causing it to de-rate and struggling to move enough water on humid days.
MSA-DCA | WA3872597 | Multiple high Humidity alarm going on-Level 4 Plant room | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Building | General Building (BU) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 12 Dec 2020 | 2020-12-12 14:33:44 | 2020-12-16 09:37:00 | Fail | COMPLETED
MSA-DCA | WA3872611 | both chillers in fault high temp in building | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Air Conditioning | Cooling Tower (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 12 Dec 2020 | 2020-12-12 17:56:21 | 2020-12-16 09:40:00 | Fail | COMPLETED
MSA-DCS | WA3872569 | Sally port man entry automatic door Faulty ,Keeps opening itself | Albany Regional Prison-External Area | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Dec 2020 | 2020-12-12 13:06:28 | 2020-12-12 06:30:00 | Pass | Phoned client & spoke to Dave Panton & when starting shift door had been working fine with no issues. did report 6000 controller was offline intermittently on Friday
MSA-DCS | WA3872576 | Zone 25 in A in constant alarm and PTZ12 not moving | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Dec 2020 | 2020-12-13 07:25:47 | 2020-12-14 17:00:00 | Fail | Rectified and fixed zone25a MW/PTZ12 camera. Job completed.
MSA-DCS | WA3872591 | UNIT 1 cell B31 - smashed glass to bottom window | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 12 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-18 09:45:00 | Fail | Glass replaced
MSA-DCS | WA3872621 | SITE COST Airconditioning fault at the front gate -POD | Casuarina Prison | WSM-BR-SITE | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 12 Dec 2020 | 2020-12-12 19:25:45 | 2020-12-24 13:30:00 | Fail | Arrived on site and signed in, carried leak check, found leaking on suction rotoloc valve,tightened up and added leak seal to system,topped up charge and tested all running ok at present.
MSA-DCS | WA3872626 | alarm l003 domestic water pump in fault | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 12 Dec 2020 | 2020-12-12 20:19:51 | 2021-02-17 12:47:00 | Fail | No faults found.
MSA-DCS | WA3872642 | Unit 2: Water leak between cell 13 and 14 ,unknown water leak | Hakea Prison-Unit 2 | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 13 Dec 2020 | 2020-12-13 11:42:00 | 2020-12-13 10:21:00 | Pass | Relaced broken fitting on the flush pipe and inlet vakve
MSA-DCS | WA3872645 | SITE COST Newly installed water Booster pump is not working,Unit 1 and gate house got affected | Wooroloo Prison Farm-Pump House | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 13 Dec 2020 | 2020-12-13 12:59:41 | 2020-12-14 14:00:00 | Fail | COMPLETED
MSA-DCS | WA3872667 | Fence Zone 4 alarm will not reset- it goes off | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Dec 2020 | 2020-12-13 16:44:34 | 2020-12-13 15:45:00 | Pass | Arrived onsite & zone 4 is reset now. tested alarms & all ok. adjusted sensitivity on controller & retested operation. z5 also reported alarming. tested but all is ok
MSA-DCS | WA3872690 | Wooroloo Prison Farm - Unit 1 - Pod 8 - Access Door - lock jammed. | Wooroloo Prison Farm | GMP-BR- HO | Carpentry | Materials (CA) | ACE LOCK & SAFE | 0 | CLOSE | 13 Dec 2020 | 2020-12-13 20:19:28 | 2020-12-13 18:20:00 | Pass | Attend to Wooroloo Prison Farm ( After Hours )open jammed lock on Pod Door Unit 1 Pod 8 New lock fitted .
MSA-DCS | WA3872692 | Greenough Regional Prison - Perimeter camera numbers 48, 23, 24, 12, 14, 22, 25, 44 & 45 are dirty. | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 16:30:00 | Pass | Use EWP to clean cameras on internal perimeter, external perimeter, near U3 and Industries. Checked at Gatehouse. Images are bright and clear.
MSA-DCS | WA3872697 | The intercom in the minimum yard is keep going off | Broome Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 08:00:00 | Pass | Test minimum cell call group with officers and confirm function.
MSA-DCS | WA3873079 | Unit 8, D wing - Hot water system leaking, failed seal | Hakea Prison | SPA-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 07:16:30 | 2020-12-16 11:20:00 | Fail | Replaced hot water unit, waiting for electrician to wire it up
MSA-DCS | WA3873101 | Unit 7, G11 - Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-17 12:30:00 | Fail | Replaced broken light switch
MSA-DCS | WA3873105 | CCU, H9 - Broken viewing hatch and frame | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 07:31:48 | 2020-12-14 13:15:00 | Pass | VEIWING HATCH FRAME REPAIRED
MSA-DCS | WA3873109 | CCU, Staff kitchen - lino floor lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 14 Dec 2020 | 2020-12-16 17:00:00 | 2021-01-05 11:31:00 | Fail | new vinyl flooring installed
MSA-DCS | WA3873113 | Unit 9, A/B wing lobby - lobby door glass panel broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 07:36:40 | 2020-12-16 12:45:00 | Fail | BOTTOM PANEL GLASS RE GLAZED
MSA-DCS | WA3873122 | Medical centre/health centre - Insulin fridge door lock faulty unable to open (bolt lock) | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 0 | CLOSE | 14 Dec 2020 | 2020-12-14 11:44:54 | 2020-12-14 13:44:00 | Fail | Attend site and install padlock and eyelets to fride so it can be secured and used
MSA-DCS | WA3873124 | Unit 4, C6 - cell call not working (cannot be heard from control room) | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 07:41:15 | 2020-12-14 12:15:00 | Pass | Rectified and fixed cell call point. Tested ok, job completed.
MSA-DCS | WA3873129 | Boiler house - Main Air compressor will not run | Hakea Prison | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CLEVELAND COMPRESSED AIR SERVICES | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 07:51:54 | 2020-12-22 15:15:00 | Fail | Works complete. Quote sent through to Maintenance Planning for remedial work
MSA-DCS | WA3873136 | Unit 4, C5 & C9 - Cell call very quiet | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 07:57:24 | 2020-12-14 14:45:00 | Pass | Rectified and fixed cell call point (C5 and C9), tested working ok. Job completed.
MSA-DCS | WA3873149 | Unit 4, Control room - Aircon leaking water | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:01:23 | 2020-12-31 12:30:00 | Fail | Completed replacement of condensate pump
MSA-DCS | WA3873186 | Unit 6, B wing - cleaning cupboard tap has come off & it is unable to put back on threading pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:21:47 | 2020-12-14 10:30:00 | Pass | Nill
MSA-DCS | WA3873195 | C wing, Grille non operational - can not secure prisoner behind grilles | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:30:48 | 2020-12-14 19:00:00 | Pass | 14/12/20Part was jammed, not allowing gate to close properly.
MSA-DCS | WA3873209 | Unit 1, Damaged isolation valve | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:37:08 | 2020-12-14 13:00:00 | Pass | Job cancelled
MSA-DCS | WA3873211 | Jeelia, Office - door lock sticking | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:40:34 | 2020-12-16 14:45:00 | Fail | 14/12/2020 On site. Inspected and assessed issue with lock. Parts required.16/12/2020 On site. Supplied and fitted new cylinder to restore normal function.
MSA-DCS | WA3873216 | Unit 5, Cell B10- toilet cistern failing to refill with water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 08:30:00 | Pass | Nill
MSA-DCS | WA3873217 | Gate house - Personal duress alarm faulty | Karnet Prison Farm | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 08:37:00 | Pass | Adjust one duress to the correct numbers and replace faulty duress with site stock
MSA-DCS | WA3873219 | Unit 13, Cell D9- Sink a big water leak running out of side | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-16 10:30:00 | Pass | Nill
MSA-DCS | WA3873222 | Unit 2, Cell B2- sink/drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 09:30:00 | Pass | Nill
MSA-DCS | WA3873230 | Unit 4, Cell B12- Toilet cistern in the cupboard is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:47:08 | 2020-12-14 09:30:00 | Pass | Nill
MSA-DCS | WA3873234 | Hotham, whole unit - Door lock sticking | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-14 12:00:00 | Pass | Attend site. Serviced and adjusted lock to restore normal function.
MSA-DCS | WA3873237 | Unit 5, Cell B10- cell call is hard to hear by POD control, its still functioning but faint | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-16 14:00:00 | Pass | Unit 5 B10 tested working ok.
MSA-DCS | WA3873239 | Security Office- CCTV most east OIU (143) has a frozen view on the indigo terminal | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 08:52:16 | 2021-07-01 10:30:00 | Fail | Powered down the decoder and allowed to cool. Managed to restart decoder after multiple attempts. Video restored. Approval received to connect network switch into Security network. Fibre patch leads and SFP installed, IP conflicts resolved and Indigo system Reprogrammed. Decoders no longer required and out of service.
MSA-DCS | WA3873250 | Unit 3, Lobby - Water cooler not cooling water | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-21 13:05:00 | Fail | No escort available All working okay CHECKED UNIT SECURED FAUCET NO ISSUE WITH COLD WAS WORKING WELL A401830117
MSA-DCS | WA3873255 | INF (10)- Control Room sliding window is vry difficult to open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 13:00:00 | Pass | replaced sash rollers
MSA-DCS | WA3873272 | Unit 5, B & D Wing Oven fan not working properly | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 08:45:00 | Pass | Test fan ok, start speed good & no noise. Left Unit operation in all modes.
MSA-DCS | WA3873279 | Amenities- Bore water channel is blocked and flooding back of Amenities | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Pumps n Pipes | 0 | CLOSE | 14 Dec 2020 | 2020-12-14 13:10:20 | 2020-12-14 10:15:00 | Pass | REMOVED BUILD UP OF TREE FIBRES AND CLEARED BLOCKAGE
MSA-DCS | WA3873290 | Hotham, A&B wing - no cell power | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 09:07:59 | 2020-12-14 11:30:00 | Pass | No cell power.
MSA-DCS | WA3873365 | Unit 17, Internal Airlock door on A/C wing catching on at the lock.Lock appears to have/coming loose | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 09:55:06 | 2020-12-14 13:15:00 | Pass | Replace screws and loctite in place, Adjust door seal to allow correct operation.
MSA-DCS | WA3873405 | sewerage plant unit 1 and 2 alarms faulty | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | Daniel Chrisp Pty Ltd | 0 | CLOSE | 14 Dec 2020 | 2020-12-14 14:14:45 | 2020-12-14 15:28:00 | Fail | Watercon employee attended site 14/12/2020 performed master reset on PLC after a power failure, tested functionality and restarted plant.
MSA-DCS | WA3873504 | Unit 10 D2 main lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 11:13:23 | 2020-12-14 14:45:00 | Pass | On site. Service and repair main cell lock to restore normal function.
MSA-DCS | WA3873507 | Unit 9, Cell D7- Service duct lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 11:14:48 | 2020-12-14 14:00:00 | Pass | Attend site. Removed foreign debris and serviced lock. Normal function restored.
MSA-DCS | WA3873543 | Unit 3, Cell D13- Window mesh damaged, see notes below | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2021-01-21 14:00:00 | Fail | REPAIRS TO DAMAGED MESH COMPLETED
MSA-DCS | WA3873548 | MPU (8)- SO's office & Staff TV Room- Air Con blowing hot air | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-15 09:30:00 | Pass | Arrived on site and signed in, checked over aircond found compressor overload tripped, checked windings all ok, found capacitor shorted out, picked up new one and return to site, fitted new capacitor turn on and test run unit all running ok at present.
MSA-DCS | WA3873554 | Unit 13, Cell D4- Sink and shower drain blocked. (Sink spout sprays water everywhere.) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 09:30:00 | Pass | Nill
MSA-DCS | WA3873559 | Unit 6, Cell C13- when water turned on in basin, water comes out the floor drain beneath | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 10:30:00 | Pass | Nill
MSA-DCS | WA3873578 | ktchen when staff is puting code in it is not excepting and still activating | Maddington (South East Metro) | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-15 08:45:00 | Pass | Attended siteInvestigated issue with alarm being activated when exiting in the eveningsPhoned monitoring centre and found Z1 Staff Room PIR, Z7 Staff Room Reed, Z14 Workstation work hall PIR are activating the alarm after it is being armedAdvised by staff the staff member it has happened to is not present and unable to retrieve further informationFrom the history provided by the monioring centre this is indicating no fault to be found. Provided information to the site on the prodcedure that should occur when arming the alarm in futureSite will monitor the behaviour of the alarm system and advise if any further issues occurLeft site
MSA-DCS | WA3873653 | Water has been turned back on at Unit 1- Please attend to check all systems are back up & running | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 12:17:56 | 2020-12-15 07:46:00 | Pass | Inspected system after repair - all ok
MSA-DCS | WA3873660 | Unit 1, Cell C8- Stainless steel Toilet pan damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 12:26:10 | 2020-12-14 17:05:00 | Pass | Replaced damaged stainless steel cover plate on the toilet
MSA-DCS | WA3873755 | Level 2 - 4x cupboard doors that have fallen off | East Perth | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-21 12:30:00 | Pass | attended site and carried out repairs to the cupboard doors.
MSA-DCS | WA3873758 | Level 2, Male toilets - blown light | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-15 15:00:00 | Pass | Found globe in fitting to be faulty went and sourced globe and installed new
MSA-DCS | WA3873763 | Unit 2, Cell D6- Viewing window is smashed | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-16 13:00:00 | Pass | VEWING WINDOW GLASS RE GLAZED AND SLIDING SCREEN REPAIRED
MSA-DCS | WA3873825 | Laundry- Water line to laundry is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 14:13:38 | 2020-12-15 15:05:00 | Fail | COMPLETED
MSA-DCS | WA3873828 | Unit 3 MATV no SBS channel, signal weak | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-14 20:00:00 | Pass | Tested signal from unit 3 antenna and unit 4 antenna, signal strength good.Checked all terminations and splitters in unit office, advised that at 6pm and 7:30pm picture quality is poor for 5 minutes.Switched all tv on in unit 3 and monitored, no change in quality. Checked signa strength from various TV points in unit 3 all ok.Monitored until 7:30pm and checked all TVs. No signal drop.No issue's found
MSA-DCS | WA3873952 | Isolation valve has a crack in the pipe in front yard - not heavily leaking | Bandyup Prison-Unit 5 House 9-Ground Floor-External Yard | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 12:00:00 | Pass | Attend site,Excavated burst isolation valve,Shut water down to prison, supplied and installed new as required.Tested works on completion and reinstated removed bake box and grass
MSA-DCS | WA3881498 | Infirmary HC7 damage to split system pipework | Casuarina Prison | GMP-BR- HO | Air Conditioning | Ducted Split System (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 14 Dec 2020 | 2020-12-18 17:00:00 | 2021-01-04 08:30:00 | Fail | Arrived on site and signed in checked the damaged pipework. Damage now repaired and ok.
MSA-DFES | WA3873336 | Rear engine bay door #6 - tensioning spring has snapped | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 17:00:00 | 2021-01-11 10:00:00 | Fail | Complete
MSA-DFES | WA3873887 | ground perimeter fence sign has been ripped off by vandalised - see notes | DFES - SWORD - State Wide Operational Response Div | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-15 12:47:00 | Pass | Protek have attended site and reattached the sign back to the fence line.
MSA-DTAG | WA3873346 | The appears to be an issue with de activating the building alarm out of hours- See notes below | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-15 10:00:00 | Pass | Tested system test ok. Note Area 1 must be selected to disarm building. Area 6 will only arm all areas and disarm area 6 only. System ok
MSA-DTAG | WA3873631 | A/C is not working on levels 3 & 5 – north side of floors | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-15 13:30:00 | Pass | Attend site. Access BMS and found level 3 and 5 to be offline. Access level 3 and check BMS controller. Found controller to have power. Power cycle controller and wait to reboot. Access lev 6 BMS and check status. Found lev 3 to reset but lev 5 is still offline. Return to BMS controller on level 3 and power cycle again. Return to BMS on level 6 and wait for system reboot. Found level 3 and 5 to now be online. Monitor temps on level 3 and 5. Found floor temps to drop. Ac is working as normal.
MSA-DTWD | WA3873088 | A block, fire panel - zone 34 in alarm | East Perth Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 14 Dec 2020 | 2020-12-14 17:00:00 | 2021-01-14 13:30:00 | Fail | Attended site due to false alarm in zone 34. Couldn’t identify which sensor went into alarm, requires further investigation.Re-attended site to investigate zone 34 & 37. Replaced 2 x Series 65 smoke detectors & bases. All OK upon departure.
MSA-DTWD | WA3873198 | front of tower, near gazebo - Uneven paving | West One Services | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 17:00:00 | 2021-03-25 13:55:00 | Fail | Repaved
MSA-DTWD | WA3873199 | Tower block, level 3 - female and mens toilet waste water pipe leaking(floor drain) | West One Services | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 11:30:00 | Pass | Complete: correct start date - 16/12/20
MSA-DTWD | WA3873204 | Level 3, Kitchen - Missing tile (wall tile) near fridge | West One Services | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 14 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-22 08:00:00 | Fail | REPLACE X 2 TILES
MSA-DTWD | WA3873292 | Tower Block, Lvl 3 ladies toilets- broken cubicle door lock | West One Services | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-21 13:15:00 | Fail | Adjust door
MSA-DTWD | WA3873315 | Eastern end of A Block, Vandalised evap A/C supply water pipe ground level. | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-15 17:12:00 | Fail | Repaired and modified vandalised pipe
MSA-DTWD | WA3873595 | Chiller 2, both compressors on fault | West One Services | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 14 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 16:00:00 | Pass | Attended site signed in and investigated chiller 1 fault, found chwp to have 2 blown fuses, replaced fuses and tested ciuld not find any issue as to why fuses had blown.left operational. Investigated chiller 2 faults and found cwp to require an adjustment on the contactor overload, tested and reset faults left both compressors running and system operational
MSA-DTWD | WA3873620 | Tower block, Lift 1 (left hand side) is stuck on level 3 | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | FLDCOMP | 14 Dec 2020 | 2020-12-15 17:00:00 | 2020-12-14 15:30:00 | Pass | DOOR OPERATOR - DRIVE BELT - COMPONENT OUT OF ADJUSTMENT
MSA-DTWD | WA3873640 | A block Richmond St boundary/street-Trees need to be cut back - please see notes | Leederville Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 14 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-15 08:00:00 | Pass | LABOUR - Labour$100 per hour x 1.75 hours x 4 staff = $700700$1.00$700.00 Generic Technician_MATERIALS - Materials$100 per hour x 1.75 hours x 2 vehicles = $350. Adjusted downwards to $300 to meet budget allowed.300$1.00$300.00. works completed.
MSA-DTWD | WA3877526 | ** Retrospective order ** Tripped circuit breaker on switchboard | West One Services | GMP-BR | Electrical | General Electrical (EL) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 14 Dec 2020 | 2020-12-14 11:30:00 | 2020-12-14 09:58:00 | Pass | Found door without power. The circuit breaker on distribution board appeared in the on position but after a reset the power to the door was restored. Tested door and battery operation. Adjusted door leaf to that the flush bolt could be used. All ok.
MSA-DCA | WA3874477 | zone 40 vesda it is sitting in alarm | Art Gallery of WA - James St-Centenary Gallery-Level One | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 13:30:00 | Pass | Attended site found that Z40 1st floor centenary was in airflow fault. Checked flow and found pipe 2 in high airflow fault at 150%. Accessed centenary roofspace and traced pipework back, found that vesda pipe had come apart at elbow join towards east side of roofspace. Rejoined pipe and flows returned to 101%. Deisolated vesda unit, all ok.
MSA-DCA | WA3874742 | Fault on FIP – Code RED ASE. System 1 fault. Please inspect fault and reset panel | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor-Reception | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 15:00:00 | Pass | Investigate code red comms fault, rectify and reset
MSA-DCA | WA3874746 | remove graffiti from PICA wall opposite Blue Rooms - photo to follow in email | PICA-Main Building-External Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 13:00:00 | Pass | job completed - cleaned graffiti
MSA-DCA | WA3874829 | SCU unit leaking (Attention Craig Hogan) | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 15 Dec 2020 | 2020-12-15 19:47:48 | 2020-12-15 19:30:00 | Pass | Htg Water leak on return pipe called in to PFM who raised to DLGSC. Isolated actuated valves in MG L1 Stores Room. Drained water from piping. Removed faulty section of piping and repaired. Installed and tested under pressure. No leaks. Bled air from FCU 1. Opened actuated valves. Closed job.
MSA-DCS | WA3874141 | Wandoo Rehabilitation Facility: Perimetre fence zone 10 in constant alarm | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Dec 2020 | 2020-12-15 10:31:43 | 2020-12-15 11:45:00 | Fail | Attended and found zone10 ultrawave intermittently alarming, recalibrate zone and test, stable and secured. Job completed.
MSA-DCS | WA3874194 | Unit 5, D11 - floor drain hole spits put water when sink in use | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 12:30:00 | Pass | Nill
MSA-DCS | WA3874203 | SOP, A10 - Toilet cistern runs constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-16 10:30:00 | Pass | Nill
MSA-DCS | WA3874215 | Unit 3, D wing yard - D wing yard needs Razor wire re positioning. | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 15 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 14:30:00 | Pass | 17/12/20Removed and replaced damaged razor wire from Unit 3 roof
MSA-DCS | WA3874217 | Recreation, prisoners first toilet - floor waste blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-18 12:10:00 | Fail | Fixed leaking toilet
MSA-DCS | WA3874220 | Education, Male staff toilet - faulty cistern, may require replacement | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-18 12:37:00 | Fail | Replaced faulty system
MSA-DCS | WA3874226 | Unit 7, E2 - tap broken on basin | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-18 11:50:00 | Fail | Basin cracked unable to uninstall badly corroded tap.
MSA-DCS | WA3874238 | Unit 1, B14 - Viewing glass smashed in door | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 07:59:35 | 2020-12-15 12:30:00 | Pass | VIEWING GLASS PANEL REPLACED
MSA-DCS | WA3874244 | Unit 1, A9 - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 08:08:56 | 2020-12-15 10:30:00 | Pass | Repaired light
MSA-DCS | WA3874246 | Unit 5, extremely low water pressure entire unit | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 08:09:08 | 2020-12-15 11:30:00 | Pass | Nill
MSA-DCS | WA3874249 | Unit 8, Control room - Vesda Unit in Alarm. Alarming with FLOW and ZONE | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 08:14:45 | 2020-12-15 12:00:00 | Pass | Vesda flow faulty pipe 3 low flow fault. Cleaned pipework and reset vesda. All ok
MSA-DCS | WA3874301 | Laundry, Work Area- Security camera not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 08:50:49 | 2020-12-15 13:15:00 | Pass | Attended and check cctv , as per officer on site they’ve lost one of the camera view. Currently all cameras are woking ok. No defect found.
MSA-DCS | WA3874324 | missing section of ducting to cleaners closet in Unit 1 B/D Wing | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-18 13:30:00 | Pass | replaced damaged shower vent
MSA-DCS | WA3874383 | unit 3 cell 47 bed light faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-15 15:00:00 | Pass | Replaced faulty light with LED
MSA-DCS | WA3874396 | Main Kitchen, Water not heating up. Bain marie beeps continuously when ON. | Nyandi Training Academy | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 09:49:42 | 2021-01-19 17:15:00 | Fail | 15/12/2020Shannon Bain Marie beeping as soon as turned on Fault find Found motors jammed Found fill level sensor faulty. Bypass and talk to Evelyn Happy use temporary without sensors Parts required:1 x Float Switch 19/1/2021Shannon & Beau Isolate unit Drain Remove Bain Marie from housing Remove and replace float Reassemble Silicone area Rewire Fill, and heat to test ok Drain unit
MSA-DCS | WA3874418 | Visit centre - air con not cooling, water not going through pads | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 10:02:58 | 2020-12-21 09:08:00 | Fail | COMPLETED
MSA-DCS | WA3874427 | Upstairs & downstairs office ilets blocked (gargling suspect blockage) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 15:15:00 | Pass | Unblocked badly blocked sewer at the back of Urquahart
MSA-DCS | WA3874465 | Triage resident toilet toilet flush button damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 10:28:24 | 2020-12-18 09:30:00 | Fail | Replaced toilet cistern
MSA-DCS | WA3874495 | Unit 1, pod 9 - 2x broken glass panels - (7/8 foot high of the ground) | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-17 17:00:00 | Pass | BROKEN GLASS PANELS REPLACED
MSA-DCS | WA3874516 | Unit 9, Cell A14- Vinyl flooring lifting | Hakea Prison | SPA-BR | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2021-04-21 14:00:00 | Fail | VINYL FLOORING IN CELL REPLACED WITH NEW
MSA-DCS | WA3874523 | Rectification of collapsed desk partitioning | Welshpool | WSM-BR-SITE | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 11:00:00 | Pass | carried out repairs to the collapsed desks and partitioning.
MSA-DCS | WA3874570 | kitchen meat slicer Commercial Meat Slicer Cutting Thickness Adjust Handle has broken off-see note | Hakea Prison | WSM-GR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2021-02-10 11:00:00 | Fail | 16/12/20Check slicer Found handle broken off and requires replacing Adjustment plate still free to move08/02/2021 - NO SIGNED SLIP AS DONE IN OUR WORKSHOP!Pick up slicer and remove to workshop for extra repairs Remove corroded fittings on shaft Punch out broken roll barSilicone control panel Install new handle and assembly, loctite in place. Test unit Automatic drive not working Fault find Found relay faultySource partInstall and test unit ok Reassemble and lubricate slides Test unit ok10/02/2021Deliver slicer to dock
MSA-DCS | WA3874605 | Unit 2 B8 Prisoners Lock Jammed Unable to open Cell Door | Melaleuca Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 12:00:34 | 2020-12-15 14:30:00 | Pass | Attend site. Replaced failing prisoners lock. Tested on several keys. Functioning normally.
MSA-DCS | WA3874610 | Bakery- Internal freezer alarm is beeping & is not at temperature | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 15 Dec 2020 | 2020-12-15 16:05:28 | 2021-01-07 12:30:00 | Fail | Arrived on site and signed in, isolated power replaced sensor cable, turned on and tested still showing fault, checked probe all ok,controller faulty,picked up new controller, fitted turned on and tested all running ok at present.BRA approved 7th Jan 21
MSA-DCS | WA3874617 | Outpatients Area- Door that Unit 6 enter hold cell has dropped and will not open probably. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-18 10:30:00 | Pass | Adjust hinges and lift door.Install locking washers to hinge fixings.
MSA-DCS | WA3874627 | Unit 4, Lobby- Front grill lock hard to operate sometimes | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 09:15:00 | Pass | Attend site. Service/repair grille lock. Tested with several keys. Normal function restored.
MSA-DCS | WA3874645 | Unit 2, Cell B10- Rubber leaking at back of toilet pan | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-18 13:00:00 | Pass | Replaced leaking rubber
MSA-DCS | WA3874650 | Unit 14, Cell D4- Shower has flooded due to shower not draining | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 11:30:00 | Pass | Nill
MSA-DCS | WA3874664 | Unit 14 - B9 has a blocked sink. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-16 12:30:00 | Pass | Nill
MSA-DCS | WA3874684 | farm packing room switch board keeps tripping out | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 12:57:01 | 2020-12-15 18:30:00 | Pass | Power tripping out, repaired.
MSA-DCS | WA3874702 | Unit 1 & 2- Electrical Room- Fire Panels showing faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 13:15:21 | 2021-01-19 14:30:00 | Fail | 15/12/20 JNAttended site for followingUnit 2 C/D 3/4 pipe 4 blocked. Vacuumed pipe and cleaned sample point and levels normal.Unit 1 C/D 1/2 Vesda-E unit showing ‘detector fault’. Online manual states laptop needs to be connected with software to diagnose fault. Ranout of time with escort to complete works need to return tomorrow and diagnose code with software.16/12/20 KS JNFurther investigation of U1 C/D 1/2 vesda found error code 833 with message ‘firmware not compatible with hardware - flow processor’.Contacted xtralis technical support, emailed diagnostic report and device info awaiting further advice from xtralis.18/1 KSPicked up parts and attended site and fitted new vesda to unit 1 C/D cells 1/2Left normal.
MSA-DCS | WA3874710 | Lenard, Cell C03- Shower doesnt work | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 10:45:00 | Pass | Replaced faulty contorl box. Job delayed due to are not safe to work in.
MSA-DCS | WA3874772 | Assessments, Rear Corridor- Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2021-04-28 14:18:00 | Fail | Found capillary line snapped inside condenser. Unit has lost all refrigerant. New hp/LP and Leak check and repair required. BRA Declined 28/04/21
MSA-DCS | WA3874775 | Unit 7, Cell H13- Toilet pulled away from the floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 14:40:00 | Pass | Replaced toilet
MSA-DCS | WA3874787 | Pharmacy, Disabled toilet- Bad odour coming from toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-16 12:30:00 | Pass | Repaired leaking seal from toilet
MSA-DCS | WA3874788 | Unit 4 - A Wing door handle faulty | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2021-01-29 14:30:00 | Fail | replaced door handles
MSA-DCS | WA3874789 | Unit 4, Cell B4- Toilet cistern when pressed takes a long time to work | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2021-02-17 12:49:00 | Fail | Nill
MSA-DCS | WA3874790 | SHU (9) - West cells A4, A5 and B5 leaking taps | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 14:42:39 | 2020-12-16 09:30:00 | Pass | Nill
MSA-DCS | WA3874816 | control gate house zone 5 camera 2 not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Dec 2020 | 2020-12-15 19:23:06 | 2020-12-15 16:00:00 | Pass | Found camera displaying green image encoder online and ok reset camera and tested ok recommend replacing psu and camera if it happens again
MSA-DFES | WA3874421 | FF Wet Area - Blocked drains | CFRS Joondalup | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 16:45:00 | Pass | Investigate blocked drains located Joondalup Fire station, check both tanks and ldiverterAttempt to plunge blockage multiple times from outside gully, once blockage has cleared flush line and paper test , re check tanks and diverted, all running fine Pack up and clean up worksite
MSA-DFES | WA3874640 | inbetween dorms 1 and 2 easter side leaking toilet on station officers side | VFRS Mandurah | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 09:00:00 | Pass | Repairing leaking toilet cistern between dorms 1 and 2. Replaced outlet seat seal, adjusted inlet valve, cleaned inside of the cistern. Tested, all works good, no leaks.
MSA-DTAG | WA3874448 | level 5 room 5.01 - push to exit button doesn't work. | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 08:30:00 | Pass | Jo0b completed - repaired egress button
MSA-DTAG | WA3874828 | Room 6.01 duress alarm cable has burn marks around cable near wall socket | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 09:00:00 | Pass | Attended Room 6.01 duress alarm cable. Burn marks appear to be rubber markings on cable, and not burns. All tested and working okay.Job completed
MSA-DTWD | WA3874251 | T block Lvl 2, T228 Large conference room - Motorized blinds will not fully open, see notes below | Murdoch Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2021-01-13 14:25:00 | Fail | completed & Invoiced
MSA-DTWD | WA3874308 | Block 2, ground level 2, male toilets - Urinal cistern leaking | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-15 15:49:00 | Pass | Fix leaks
MSA-DTWD | WA3874313 | Auditorium- Faulty batteries | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2021-02-03 14:30:00 | Fail | job completed - replaced faulty batteries
MSA-DTWD | WA3874599 | Adjacent Science block internal Road in garden Bed. fire hydrant leaking | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-15 15:15:00 | Pass | Fixed leaking hydrant
MSA-DTWD | WA3874635 | Science, S6 Block passage Fridge No 1 left side - industrial fridge not going down to temperature | Murdoch Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-17 11:30:00 | Fail | Rechecked fridge operation all ok, unit cycling, cleaned up and completed paperwork.
MSA-DTWD | WA3874736 | Lvl 1- Main water meter leaking on our side Harold Street | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Dec 2020 | 2020-12-16 17:00:00 | 2020-12-16 10:15:00 | Pass | water meter had been ran over and had cause damage to pipes. Replaced pipework after water meter.
MSA-DTWD | WA3874799 | ground hallway 2x faulty bottle fillers | Clarkson Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-16 15:37:00 | Pass | Replaced fountain taps x2
MSA-DTWD | WA3874802 | Fire alarms need to reset | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 0 | CLOSE | 15 Dec 2020 | 2020-12-15 19:08:10 | 2020-12-15 17:09:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Brian Blechynden 0419 900 980Priority #: 0Work Order Number: WA3874802Call out Date: 15/12/2020Target finish: 15/12/2020Original information: T Block - Fire alarms need to reset, the booster pump started because they were working on fixing a leak and the building evacuated but did not call DFES.Attended site:Date: 15/12/20Start Time: 16.00Finish Time: 17.00Techs on Site: 1Works Carried Out:Turned of electric and diesel pumps. Filled up diesel tank with 20 litres of fuel they had on site. Still needs more. Looked like coolant on the ground around the pump. Need to look at that and top up the diesel tank.Reset FIP left diesel pump fault isolated because of low fuel level.Need to check config for why the EWIS activates for a pump run and also the pager didn’t activate on the pump run. Returned to siteDate: 16/12/20Start Time: 13.30Finish Time: 16.00Techs on
MSA-MRWA | WA3874613 | Hard stand area transportable 2x lockable doors need to be rectified- see notes | Materials Engineering Branch | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 15 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 13:10:00 | Pass | Replace 2 x cylinder s to Transportable
MSA-DCA | WA3875575 | plantroom please investigate faults on boiler | Maritime Museum Victoria Quay-Main Building | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2021-01-15 16:30:00 | Fail | Attended site. Boiler 2 in error 2 fault code. Raised PO for Boilertronics to attend. Please refer to Boilertronics service report for in depth analysis of works carried out in adjustment of combi valve and gas settings. Works completed boiler operating correctly.
MSA-DCA | WA3875689 | steel bar part of glass sheet is bent | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-Entrance To Conference Room- East Side | GMP-BR | Building | Internal Screens (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-18 15:00:00 | Fail | Bent steel bar removed and replaced with stainless discs as directed by client
MSA-DCA | WA3876552 | All main entry doors are not working. | State Theatre Centre (Heath Ledger Theatre) | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 16 Dec 2020 | 2020-12-16 21:34:29 | 2020-12-17 19:07:00 | Fail | Inspected door on ground floor level and found all lock overide switches in lock mode. Switched back and tested all ok and locking from access butfound door 1045728 is not locking found no voltage coming out of lock out put on besam black controller and lock is also not working recommend door to be powertrained with es200 besam kit with 2x ixio sensors. Site are putting overnight Guard on door. Braf to be raised17/12/20 - Carried out powertrain as per quotation and setup and tested all ok. When testing found that the access system was locking the door randomly on its own requires access to rectify
MSA-DCS | WA3874989 | Unit 4, Cell L45 - exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 09:00:00 | Pass | Replace Unit 4 Cell L45 exhaust fan
MSA-DCS | WA3874991 | Unit 1, Hut toilets - leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-23 13:00:00 | Fail | Complete
MSA-DCS | WA3874995 | Unit 1, Hut Urinal tap - leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-23 09:00:00 | Fail | Complete
MSA-DCS | WA3875000 | Bakery - Proover has ceased heating with no moisture | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 0 | CLOSE | 16 Dec 2020 | 2020-12-16 11:19:35 | 2020-12-21 07:29:00 | Fail | COMPLETED 16/12
MSA-DCS | WA3875004 | unit 2 middle landing shower taps leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-24 10:00:00 | Fail | Complete
MSA-DCS | WA3875006 | unit 1 hut toilet cistern - fault not filling | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-23 14:00:00 | Fail | Complete
MSA-DCS | WA3875011 | unit 2, top landing urinal exhaust fan faulty | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 09:00:00 | Pass | Replace Unit 2 urinal fan
MSA-DCS | WA3875015 | WWTP mixer motor not working | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-22 09:30:00 | Pass | Repair WWTP mixer motor isolator
MSA-DCS | WA3875017 | staff quarters - window broken | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-17 10:00:00 | Pass | broken window replaced
MSA-DCS | WA3875022 | Zone 4 & 14 - constantly in alarm (fence alarm) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 07:36:16 | 2020-12-16 09:30:00 | Pass | Inspected fence cable cable sealed and tested fine however fence warped and rocks in the wind needs re tensioning
MSA-DCS | WA3875023 | Zone 6 - microwave alarm in constantly | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 07:38:11 | 2020-12-16 10:24:00 | Pass | No issue found on site with microwaves all site alarmed and tested ok
MSA-DCS | WA3875028 | Medical Centre, Staff Toilet behind officers desk - leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-18 13:50:00 | Pass | Replaced leaking rubber
MSA-DCS | WA3875030 | Unit 6, B wing showers - Basin tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-18 14:40:00 | Pass | Replaced faulty spindle
MSA-DCS | WA3875032 | Unit 7, F wing - Air Ducts not extracting air | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 16 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-21 10:00:00 | Fail | Replaced timers and tested operation. All ok
MSA-DCS | WA3875033 | Unit 7, G wing - end light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 11:30:00 | Pass | Repaired lights
MSA-DCS | WA3875048 | Unit 2, Cell A4- Window will not lock or stay in up position | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 16 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-17 11:30:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3875050 | Unit 14, Cell C5- Shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 09:30:00 | Pass | Nill
MSA-DCS | WA3875076 | Unit 13, B/D kitchen splash back - alarms constantly going off everyday | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 08:09:25 | 2020-12-16 13:37:00 | Pass | Relates directly to WA3857785 - BRAF not approved have advised client16/12/20 JN KSInvestigated faults in unit 14 as followsB/D 5/6 fault previously reported on the 8/12/20, faulty vesda unit showing incorrect flow readings. Waiting on approval and partsB/D 9/10 found that vesda was in fault due to pipe 1 low airflow. Cleaned out pipework with vacuum and removed dust from sampling point and sampling point cover. Flows returned to normal.
MSA-DCS | WA3875088 | Unit 1, B Wing- West ablution blocks- basin taps faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 13:45:00 | Pass | Attended site,Locate pillar taps to unit 1 B wing ablution block to be unservicable.Remove 4x pillar taps and supply and install new as required with mini stops and flexi leads as required.Tested works on completion
MSA-DCS | WA3875090 | Sterlize zone- main door into prison, self closer not working properly & door not closing | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 10:00:00 | Pass | Ease and adjust door closure
MSA-DCS | WA3875092 | Recreation- 2x wall mounted fans not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-23 08:30:00 | Fail | Tested power supply to plug in fans, power supply good. wall fans are faulty but are plug in style (site property) I have advised staff that these will need replacing at their cost as they're not hard wired fans covered by breakdown cost centre.
MSA-DCS | WA3875094 | Entry, 3x flag pole ropes are damaged | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 12:45:00 | Pass | Replaced flag pole ropes
MSA-DCS | WA3875095 | Health Centre- Nurse storeroom x1 & CCU door x2 - bubbles in vinyl floor/trip hazard | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-14 14:30:00 | Fail | BUBBLED AREA'S OF VINYL CUT OUT & RE STUCK
MSA-DCS | WA3875158 | Sencond floor - aircon not working, wont turn on | Warminda Hostel | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 08:55:53 | 2020-12-16 13:01:00 | Pass | Reset the aircon unit and adjustments on control. Tested on cooling . Aircon is working good
MSA-DCS | WA3875168 | Jasper, Cell A07- Shower cuts out & unable to be used | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 12:20:00 | Pass | Replaced faulty solenoid, button and control box
MSA-DCS | WA3875172 | Unit 1 A Wing Ablutions extract fans not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-15 13:00:00 | Fail | Replaced exhaust fan controller unit.
MSA-DCS | WA3875214 | Unit 7 - A1 Cell A1 window spring broken wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-17 15:15:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3875226 | Laundry water taps damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 12:50:00 | Pass | Replaced pipe and taps for washing machine
MSA-DCS | WA3875230 | Laundry- 2x Damaged Powerpoints | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 09:30:00 | Pass | Replaced 2 broken GPOs
MSA-DCS | WA3875235 | Abattoir all sterilzer sinks traps leaking require replacement | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2021-02-15 13:15:00 | Fail | All parts replaced
MSA-DCS | WA3875284 | Unit 5, Cell B1- Prisoner lock fault, see notes below | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-31 11:00:00 | Fail | Replace worn barrel.Replace door plate, lock and hinges.
MSA-DCS | WA3875304 | Unit 2, Cell D6- Window spring is faulty on cell window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-17 12:30:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3875315 | Yeeda, B Wing living area- smashed window (approx 1200x450) | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-05 15:45:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3875317 | Jasper, Cell B08- Samshed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 13:00:00 | Pass | replaced smashed window
MSA-DCS | WA3875323 | Jasper B08 Broken double power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-16 14:30:00 | Pass | Replaced damaged gpo
MSA-DCS | WA3875331 | Zone Control 2, office- Electric gates not working | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 11:17:36 | 2020-12-17 15:41:00 | Fail | Attended site and repaired gate control faults.Tested OKJob Complete
MSA-DCS | WA3875346 | Unit 13, Cell D1- Toilet blocked, plunger has not worked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 11:28:31 | 2020-12-17 08:30:00 | Pass | Nill
MSA-DCS | WA3875356 | Unit 13 - B13 Main light in cell not working, - see notes | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 08:30:00 | Pass | Repaired faulty lights in unit 13 b13
MSA-DCS | WA3875374 | Unit 6, Cell C8- Window vent is bent & will not open or close | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-17 15:00:00 | Pass | DAMAGED VENT REPAIRED
MSA-DCS | WA3875377 | Gascoyne B1 mould to be cleaned off ceiling | Wandoo Rehabilitation Facility | WSM-BR-SITE | Cleaning | Cleaning (CL) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-04 10:15:00 | Fail | Mould Clean Gascoyne B1 and B2
MSA-DCS | WA3875441 | Library - Aircon not cooling | Boronia Pre-release-AK19 - Library, Education Personal Development | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 14:21:00 | Pass | Found condenser fan capacitor faulty. Returned following day with replacement capacitor, installed and ran up. Monitored unit, all ok.
MSA-DCS | WA3875451 | Vegetable Preparation - leaking pipe under potato peeler | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2021-03-18 09:30:00 | Fail | Nill
MSA-DCS | WA3875500 | Metal Shop - hand grinder cable is damaged, cable also to be shortened | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 13:00:00 | Pass | Repaired damaged grinder in metal shop
MSA-DCS | WA3875512 | Visits - 2x fire alarm faults | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-11 08:50:00 | Fail | 2 x faults reported on Social Visits SFIPChecked MFIP, no faults present. Checked with POD guards, not aware of any issues.Checked Social Visits SFIP, no faults present. Checked system fault log, last fault was a mains power failure on 16/12/20.Left system in normal working order.
MSA-DCS | WA3875623 | gate house door control computer down | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Dec 2020 | 2020-12-16 18:41:03 | 2020-12-16 17:00:00 | Pass | Attended site checked and found reception door control workstation can’t be login. Reboot workstation and software. Checked all service back online after work.
MSA-DCS | WA3875656 | unit 2 cell D14 HW tap spindle damaged | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-27 14:00:00 | Fail | Replaced hot spindle from van stock
MSA-DCS | WA3875673 | Psych Services- Metal wall panel faulty, might be loose | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 15:41:25 | 2020-12-29 12:30:00 | Fail | Carried out repairs to metal flashings around the aircon unit in psych services office.
MSA-DCS | WA3875701 | ISU camera's in ob cells have lost all vistion | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Dec 2020 | 2020-12-16 20:30:23 | 2020-12-16 19:30:00 | Pass | System restarted password inserted tested ok
MSA-DCS | WA3876080 | perimeter pole light 21B is not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 16:52:06 | 2020-12-21 13:30:00 | Fail | Replaced Pole light with LED 21B
MSA-DCS | WA3876566 | The diesel jacking pump is not turning off - The fire system | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Dec 2020 | 2020-12-16 22:44:18 | 2020-12-16 21:34:00 | Pass | WA3876566. Casuarina Prison. CM. Arrived on site and spoke with guards. They said that diesel jacking pump was running. When I got to the pump room the actual diesel fire pump 1 was running. Attempted to stop the pump with the stop button but that failed to activate. Manually stopped pump. Possible faulty stop solenoid as when I started and stopped the pump the solenoid worked intermittently. Have isolated diesel pump 1 in case of reoccurring issue, will require further investigation by electrician. Pump fuel is currently 55% and fuel will be required. Photos of solenoid in docs18/12Removed and adjusted fuel pump arm and spring - re-installed and checked operationA lot smoother and getting full travelReplaced stop solenoid and tested all ok
MSA-DFES | WA3875148 | Gate/fencing (south side of property) - damaged (see notes) | DFES Regional Office - Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2021-02-12 10:00:00 | Fail | Fencing and gate hardware to replaced to damaged sectionsReplace Section of Mesh RencingReplace bolt lock on gate
MSA-DFES | WA3875337 | Ground - Hot water system constantly having water fluctuations. | CFRS Welshpool | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-06 07:30:00 | Fail | Rheem service agent attended and repaired fault under warranty as the part only lasted 6 months.
MSA-DFES | WA3875372 | PPC room light flickering faulty light has been marked | Metropolitan VFRS | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 09:00:00 | Pass | Attended site, investigated faulty light fitting in PPC Room. Left site to get replacement parts. returned to site with replacement parts. Replaced faulty fitting, all working.
MSA-DFES | WA3875440 | ground kitchen Left Hot water urn closest to stoves is leaking from spigot - see notes | CFRS Perth | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-12 11:47:00 | Fail | Replaced boiler tap due to it was leaking tested new tap and working properly
MSA-DFES | WA3875458 | L1 station office/gym blown fluro lights | Success Career Fire Station (Temp Site) | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 15:45:00 | Pass | Repaired 2 Lights on Level 1 that were faulty.
MSA-DFES | WA3875524 | Security camera's Security camera issues on playback also one disconnected | Armadale Regional Office | GMP-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-17 17:08:00 | Pass | Check recordings, found camera had returned by itself at 923am Thursday 17th.Recordings back to dec 1, stopped December 10@ 758am. Run constant ping on rear camera 7 (10.70.160.208) that’s dropped offline, all looks ok nothing irregular. Also client advised they have not got a lot of recordings, check over system, currently has 15 days, adjusted resolution and frame rate on all cameras from 1920x1080 and 25fps to 1280x720, now have 42 days of recordings. Swap camera 7 from port 7 to 8 on recorder as possible port fault. Cam back up and ok.
MSA-DFES | WA3875581 | 2x florescent lights in tunic room not working | CFRS Welshpool | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 14:45:00 | Pass | Located 2 x Faulty lights in Tunic room and repaired accordingly.
MSA-DFES | WA3875596 | Entry Gate key pad has no power | CFRS Ellen Brook | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 15:30:00 | Pass | Locate faulty key pad. The remote for the gate works and the key pad on the inside off the gate is working. The key pad on the out side of the gate is faulty. I checked for voltage and had 1 volt dc and the cable was low voltage wire. I then checked the working key pad volts and had -17 volts dc. All off the circuits were on at the switchboard. Advised staff to contact a security contractor or a access control contractor.
MSA-DFES | WA3875647 | Dorm 3- light is not working | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 16:30:00 | Pass | Identified faulty lights in dorm 3. Replaced tube starter and tombstone. All working
MSA-DFES | WA3875663 | Entry Gate key pad has no power | CFRS Ellen Brook | GMP-BR | Electrical | General Electrical (EL) | Securex Security Systems & Services | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-17 09:00:00 | Pass | 17/12/2020, 800-900System is a Nice brand automatic gate.Traced issue back to gate motor decoder unit. No voltage appears to be getting out of device.Tested figure 8 between decoder and keypad and showed continuity ok.Power appears to be getting into decoder but nothing outThis requires a auto gate tech to attend.
MSA-DTAG | WA3875178 | ground Male public toilet (opposite café) toilet blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 14:24:00 | Pass | Complete
MSA-DTAG | WA3875195 | Car Park Upper/Lower levels SAT carpark gates to be coded - see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-22 10:30:00 | Pass | SAT Basement Carpark gates configured to open on 25th December 2020 as requested.All Public Holidays programmed for 2020 and 2021.Job completed
MSA-DTAG | WA3875290 | Front of building - Graffiti on front pillar of building | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-19 14:00:00 | Pass | Removed grffiti
MSA-DTAG | WA3875667 | Lvl 10,Registry of Births, Deaths and Marriages- flickering light, see notes below | Westralia Square | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-21 08:00:00 | Pass | Attended site and signed in with security. Got access card for level 10. Found flickering light in reception. Supply and replace tubes and starters to fluro. Tested all okay. Signed out. Job complete
MSA-DTAG | WA3876571 | Supreme Court Basement - Judges Carpark - Burst Sprinkler Pipe | Supreme Court-Supreme Court Building-Basement | GMP-BR-HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Dec 2020 | 2020-12-16 23:59:30 | 2020-12-17 22:00:00 | Fail | Supreme CourtAttended site for a sprinkler leak in judges car parkFound the incoming towns main 100mm pipe leaking from a weld on a flange pieceHave had to isolate incoming towns main supply to building, have informed client that sprinkler system is off lineMeasured up pipe work to be replaced17.12.20- arrived onsite and turned on 1x sluice valve- it turned water back on to both domestic and sprinkler system- will need further investigation into why both are off the same isolation valves- will return tonight to carry out repairs17.12.20 (after hours)- isolated and drained mains- replaced leaking section of 100mm main with newly fabricated pipe- re filled system and checked for leaks, all ok- reset and de isolated syste
MSA-DTWD | WA3875184 | A Block, Main Security Desk- CCTV has stopped displaying cameras | East Perth Campus | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 1 | CLOSE | 16 Dec 2020 | 2020-12-17 17:00:00 | 2020-12-16 14:45:00 | Pass | 16/12/2020, 1345-1445IT department has been doing works onsiteSince their works cameras in C block are down.There is no NVR in C blockSteve Meyer is going to try locate plans of CCTV system.17/12/2020, 1030Steve Meyer advised to close this job, he will take it up with his IT department.15/01/2021Programme rejected claim because previous signature slip did not have 'yes'added new signature slip with completion marked 'yes'No Works done, only signing of signature slip so no Safety docs required
MSA-DTWD | WA3875419 | AC plant room faulty chiller 1 pump | West One Services | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-17 13:46:00 | Pass | Replaced contractor , require electrician as more faults in board
MSA-DTWD | WA3875595 | Science block Chiller CHR- E2 Chiller keeps tripping out and turning off after reset. | Murdoch Campus | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2021-01-18 16:26:00 | Fail | Site we requested we returned to campus on 7/1/21 to repair chiller, found condenser fans tripped out on chiller causing compressors not to start made good and test condenser fans (1 already ordered on other BRAF). Chiller cycling on high temperature due to 41C ambient,
MSA-DTWD | WA3875602 | D Block, Cafe- Cool Room is not working, electricity supply to be checked, see notes below | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 16 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-22 12:30:00 | Pass | Cool room power. Replace fuse and check isolation points. Re-energised from isolation points that were in unknown locations by site
MSA-DTWD | WA3875634 | T block diesel leak from fire booster pump - please see notes | Murdoch Campus | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 16 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 14:10:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Brian BlechyndenPhone Number: 0419900980Work Order Number: WA3875634Priority #: 2 - Medium PriorityCall out Date: 16/12/2020Target finish: 21/12/2020WO# Value: $1000Original information: T block diesel leak from fire booster pumpScope of Work:Investigate water and diesel spill leakClean up water/diesel on floorNote:Must isolate FIP before running Fire Pump as it triggers EVAC (17/12/2020) - Work NoteDate: 17/12Start Time: 11:10Finish Time: 14:10Techs on Site: 1Works Carried Out:Investigated diesel leakIsolated fire panelFound leak coming from fuel filter O-ring spitting outRefitted O-ring and re fitted fuel filterTested pump no apparent leaksCleaned up spillage with rags and mop and bucket.Materials and Equipment Used:RagsMop bucketSystem Status on Departure:NormalThe above mentioned works have been carried out as arranged and the system was l
MSA-DCS | WA3876736 | PTZ12 (camera62) No display and unable to connect to the camera. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Dec 2020 | 2020-12-17 10:29:03 | 2020-12-17 15:40:00 | Fail | Attended site and repaired camera faults.Tested OKJob Complete
MSA-DCS | WA3876749 | Wooroloo Prison Farm perimeter lights need a timer reset | Wooroloo Prison Farm-Reception | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 17 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-17 10:00:00 | Pass | Re-programmed timer
MSA-DCS | WA3876797 | Kitchen - Rational Oven, stops working, and error reading is ' reset gas' The oven is not usable | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 17 Dec 2020 | 2020-12-17 11:17:15 | 2020-12-17 12:00:00 | Fail | 17/12/20Called as requested to the oven not working correctly. Found the the bottom heat exchanger burnt out with holes in it. Also the blower and ignition unit failed due to water ingress. Also checked the top heat exchanger and found it be weeks away from burning out. Parts required (Going ahead on job #18647)1x top heat exchanger1x top heat exchanger1x burner1x burner blower1x ignition probes1x earth probe1x gasket1x screws1x ignition unit4x gasket1x nuts2x gaskets2x gaskets
MSA-DCS | WA3876816 | Unit 7, H11 - Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-17 14:00:00 | Pass | Repaired light
MSA-DCS | WA3876854 | Unit 6, Cell B2- toilet button is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-22 10:30:00 | Pass | Nill
MSA-DCS | WA3876866 | unit 6, B11 - Extractor Fan not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 12:00:00 | Pass | Inspected ductwork and cleaned to allow airflow. Found grill blocked from side which was not visible. Used nitrogen to remove blockage. All ok
MSA-DCS | WA3876901 | Unit 5, B wing, Kitchen - sink spout leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-18 16:16:00 | Pass | Replaced leaking seal
MSA-DCS | WA3876903 | Kitchen,Stairs to mezzanine floor- Stainless slide attached to stairs needs fixing, see notes below | Hakea Prison | GMP-BR- HO | Building | Steel Work (BU) | Midolo Building Services | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2021-01-13 12:30:00 | Fail | WELDED SLIDE BACK ONTO ATTACHMENT POINTS
MSA-DCS | WA3876905 | Unit 1, A13 - Cell Door main lock broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 17 Dec 2020 | 2020-12-18 08:41:53 | 2020-12-17 10:45:00 | Pass | Attend site. Service and repair main lock. Tested with several keys. Normal function restored.
MSA-DCS | WA3876907 | Yeeda, entry gate- Tongue for pedestrian gate keeps getting stuck | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-17 11:30:00 | Pass | Attend site. Replaced failed lock to restore normal function.
MSA-DCS | WA3876914 | Unit 1, chemical store room sink leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2021-01-04 10:00:00 | Fail | Complete
MSA-DCS | WA3876916 | Unit 1, C/D, 5/6 - Smoke Vesda Showing fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 17 Dec 2020 | 2020-12-18 08:49:18 | 2020-12-17 09:38:00 | Pass | 17/12/20 CM/PW. Attended site for intermittent vesda fault on vesda CD 5/6 in unit 1. On arrival found that fault had cleared but within 10 minutes fault had returned. Went to unit and cleared cells 5&6 in both C and D. Sampling points were all very dirty and dusty and therefore used a cloth and vacuum and cleaned them. De isolated fat and Vesda unit sitting normal on departure.
MSA-DCS | WA3876917 | Shared facilties- leaking water pipe in ground outside tap | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-24 12:00:00 | Pass | Complete
MSA-DCS | WA3876920 | Visits light fitting not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-21 15:00:00 | Pass | Repair Visits light fittings
MSA-DCS | WA3876924 | Kitchen, Control Pod- Hydro Tap Filter is blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 09:56:00 | Pass | Filter service done
MSA-DCS | WA3876945 | Omnitrax offline across the entire permitter | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Dec 2020 | 2020-12-17 17:07:45 | 2020-12-17 19:22:00 | Fail | Replace controller and test
MSA-DCS | WA3876972 | entrance near courthouse-swipe card reader is loose - see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-17 13:00:00 | Pass | Attended site checked and found ACC reception card reader is loose and missing screw. Rectified the problem and tested all ok.
MSA-DCS | WA3877016 | Karakin, B Wing- Smashed sash window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2021-01-15 11:30:00 | Fail | SASH WINDOW REGLAZED
MSA-DCS | WA3877154 | Admin superintendents office TV Reception problem | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | CLOSE | 17 Dec 2020 | 2020-12-18 10:58:48 | 2020-12-18 12:45:00 | Fail | Attended site and checked reports for Armory door, downloaded and emailed report as per PFM request. Alldownloaded ok.Job completed.
MSA-DCS | WA3877170 | Unit 1, A Wing- Door handle is faulty | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-18 11:00:00 | Pass | repaired loose handle
MSA-DCS | WA3877173 | SHU (9) - North Ceiling to outside visits covered area is hanging down | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2021-01-20 13:00:00 | Fail | SHEET SECURED
MSA-DCS | WA3877238 | Ground floor - light globes blown in several locations within the office. | Midland (North East Metro) | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-22 14:00:00 | Pass | Replaced all blown lights throughout the office as requested
MSA-DCS | WA3877259 | POD 2, Kitchen exhaust fan not working on oven | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 17 Dec 2020 | 2020-12-18 12:55:24 | 2020-12-21 14:30:00 | Fail | Replaced faulty Range hood
MSA-DCS | WA3877279 | Level 3, rear staircase - Card reader is not working | East Perth | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Dec 2020 | 2020-12-18 13:09:56 | 2020-12-21 08:57:00 | Fail | Attended siteReplaced faulty card reader with a Gallagher Prox Milfare Card Reader Serial: 1517408123Tested multiple times, confirmed workingAdvised site of the outcome
MSA-DCS | WA3877560 | Reception staff kitchen Hydro Tap tripping the circuit Breaker | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 11:30:00 | Pass | Replaced element TO BILLI QUADRA A40189200D and filter service
MSA-DFES | WA3876939 | Entry Gate key pad has no power | CFRS Ellen Brook | GMP-BR | Electrical | General Electrical (EL) | Anvil Doors | 1 | CLOSE | 17 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-17 12:01:00 | Pass | Attended Ellenbrook Fire station , Key pad to auto gate not working -- traced Fault to cable damage Repaired damaged , Replaced cable and Tested to be working.
MSA-DTAG | WA3877195 | 1987 plantroom Check water level in cooling tower - see notes | Supreme Court | GMP-BR-HO | Air Conditioning | Evaporative Coolers (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-18 09:00:00 | Pass | Return to site. Access plantroom BMS. Remove all overrides and return all setting back to normal. Check operation of plant, working ok.
MSA-DTAG | WA3877216 | 1987, 3rd Floor, kitchen- Filter tap lights flashing | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 17 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 12:59:00 | Pass | Unit working okay on arrival. The mains water had been turned off to the building to carry out a repair on Friday. The unit is now working okay since it’s been back on. Called back but nothing wrong with unit met Iain Johnston... agreed unit working ok maybe that staff member did not know what safety button does.
MSA-DTWD | WA3876836 | Roof of B block, exhaust fans for toilet - faulty, noisy | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 17 Dec 2020 | 2020-12-17 17:00:00 | 2021-10-07 12:30:00 | Fail | REMOVE AND REPLACE TOILET EXHAUST UNIT
MSA-DTWD | WA3876847 | Block 10, Room 10G2 Staff Room- Numerous lights have broken fitting s | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 17 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-04 11:15:00 | Fail | Attended site and signed in. Got keys from facilities. Located 10g2. Removed faulty light fittings from concrete roof. Replaced with new led surface panels. Repaired 2 x light fittings using parts from old fittings that were still okay. Refitted diffusers to fittings. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3877588 | G block room G17 blocked floor waste drain - Falcetta on site | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-17 18:30:00 | Pass | drainsflush unblock drain
MSA-DTWD | WA3877599 | A block AG27B Male Toilets Last cubicle – toilet leaking water on the floor-see notes | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 17 Dec 2020 | 2020-12-24 17:00:00 | 2021-01-07 12:00:00 | Fail | Campus closed was unable to attend to re opened
MSA-DCA | WA3877923 | Multiple lights are out in the PCC- Confirm locations with David De Villiers | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 18 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 16:00:00 | Pass | Rectified all blown and faulty lamps and iron core ballasts.
MSA-DCA | WA3877942 | Alert High water usage (leak) triggered for controller PCC- see notes below | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 18 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 13:30:00 | Pass | Tap timers were reset
MSA-DCS | WA3877774 | Gate house - Front door security lock is failing | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Dec 2020 | 2020-12-18 10:32:44 | 2020-12-18 09:00:00 | Pass | Rectified and fixed the logic block issue main entry door, tested ok. Job completed.
MSA-DCS | WA3877817 | Unit 14, D4 - toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-22 11:30:00 | Pass | Nill
MSA-DCS | WA3877826 | Unit 1, D wing - grill not working (solenoid is broken) | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 3 | CLOSE | 18 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-30 14:30:00 | Fail | 18/12/20Attended site.Waited 1/2 hours.Advised no escorts.Told to return another day.23/12/20Attended site.Casuarina advised that there was not issue at the time.30/12/20Replace limit switch
MSA-DCS | WA3877884 | Kitchen- 1st rational oven not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 18 Dec 2020 | 2020-12-18 12:12:39 | 2021-01-07 11:30:00 | Fail | Returned 7/01/21 and replaced Fan Motor. tested ok.
MSA-DCS | WA3877903 | Shut off & restart on boilers for Unit 13 & 14 - see additional notes below | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-21 16:00:00 | Pass | Nill
MSA-DCS | WA3877916 | CCU (11) - control room - 3 monitors have frozen, Unable to see any live feeds from various cameras | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Dec 2020 | 2020-12-18 12:37:39 | 2020-12-18 10:26:00 | Pass | Restart and fixed the issue on WS2 CCU, job completed.
MSA-DCS | WA3877918 | Main Fridge in the SPU is not getting to its setpoint temp | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 08:40:22 | 2021-01-12 08:27:00 | Fail | Quote declined 12/01/20. Invoicing costs to date.
MSA-DCS | WA3877961 | Grounds - Walkway concrete ramp has been lifted by tree roots (approx 30-40mm) trip hazard | Boronia Pre-release-External Area-Ground Floor | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | Midolo Building Services | 3 | CLOSE | 18 Dec 2020 | 2020-12-29 17:00:00 | 2021-02-23 15:00:00 | Fail | REMOVED OFFENDING TREE CAUSING FOOTPATH TO LIFT - RE INSTALL NEW FOOTPATH
MSA-DCS | WA3877968 | Unit 1, Gym- Fluro lights are not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 16:30:00 | Pass | Replaced 2x LED light fittings in unit 1
MSA-DCS | WA3877992 | ground floor kitchen lack of pressure from HW and sink is blocked | Welshpool | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 09:28:41 | 2020-12-18 11:00:00 | Pass | Complete, please read job notes.
MSA-DCS | WA3878020 | Jasper B05 Smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-05 13:00:00 | Fail | WINDOW RE GLAZED AND WELDED
MSA-DCS | WA3878026 | Security panel battery is low please investigate- Keys to be collected at reception PFM office | Riverbank | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 15:30:00 | Pass | -collect keys from PFM office -attend site -locate the panel with a faulty battery -replace the faulty battery in the panel with a new one -reset the date and time on the keypad -panel is missing a permaconn for monitoring purposes -left site -return keys to PFM officeSupplied part:Battery 1x 12V 7AH
MSA-DCS | WA3878043 | Laundry - check power points leading to washing machines | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 10:10:11 | 2020-12-18 13:30:00 | Pass | Checked washing machine GPOs
MSA-DCS | WA3878169 | Unit 2, A wing , Camera C4 - is not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2021-04-08 17:30:00 | Fail | Two technicians attended site and installed new CAT6 cable from Unit 2 CCTV Equipment rack thru ceiling space to Camera location. Terminated both ends of cable, tested and connected into network. Checked camera picture and refocused.
MSA-DCS | WA3878170 | ground floor kitchen water pressure is low and no HW | Welshpool | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | Water2water Pty Ltd | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 12:08:45 | 2020-12-18 16:29:00 | Pass | Replaced Venturi and filter
MSA-DCS | WA3878241 | Unit 10 control room Remote Monitor for cell calls showing B02 fault | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 13:08:36 | 2020-12-18 16:00:00 | Pass | Rectified and clear the fault on B02 cell call, job completed.
MSA-DCS | WA3878294 | gate house pod, simplex fire system keeps activatiing | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 14:34:38 | 2021-01-22 10:21:00 | Fail | Arrived on site and found external stores Open Circuit Fault. Went to external stores end of line and found an open circuit. The MCP box says top ^ which I can only assume means heads up to the ceiling. Tracing of cable very limited as external stores shut and unable to get officer with keys to attend area. Tested the break glasses that were accessible on the outside and found open circuit on all of them. This will be required to be done inside of business hours so access can be made. Also will need a scissor life that can go upto 10m as external stores offices are very high. Have isolated external stores as this is intermittent. This will need rectified ASAP as devices keep going in and out of fault.22/1/21 MB JNInvestigated ext stores zones on graphics system and found all modules in external stores in open circuit. Checked history logs for anything including external stores and found M1-137 external stores power supply fault intermittent on 18/12/20 and all zones in open circuit
MSA-DCS | WA3878327 | Unit 1, Cell C16- Toilet pan seals leaking into the shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 15:28:41 | 2020-12-24 11:35:00 | Fail | Replaced cracked toilet and toiler seat. Replaced leaking seals
MSA-DCS | WA3878362 | intercom system - tamper fault - beeping non-stop - unit 1 | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Dec 2020 | 2020-12-19 20:16:36 | 2020-12-19 08:30:00 | Pass | Attended site checked and found U1C7 cell call point tamper alarm keep activating. Replaced with Hakea stock spare cell call point. Tested all ok after replacement. Need to order cell call point CI-CC X 1 back to Hakea stock.Hakea stock was replaced
MSA-DFES | WA3877900 | Fence line - electric fence wire has snapped | FESA RHQ - Forrestfield | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 18 Dec 2020 | 2020-12-21 17:00:00 | 2020-12-18 15:00:00 | Pass | Repaired break in lines and tensioned all lines of electric fence
MSA-DFES | WA3878055 | garden areas station 5 on front verge has a damaged length that is leaking - see notes | CFRS Daglish | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-19 15:15:00 | Pass | Call out & Labour & Retic Parts
MSA-DFES | WA3878056 | External access keypad for security sliding gate isn’t working (see notes) | CFRS Daglish | GMP-BR | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 09:00:00 | Pass | Tested found access control board side B not working transferred to card side A retested working ok.
MSA-DFES | WA3878238 | Warehouse low battery in the security system, system now constantly beeping - | DFES Fleet & Equip Serv Fleet Appliances Prog Bran | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 11:15:00 | Pass | 21/12/20 - Ryan Vesty, Joshua ParkFound faulty battery over 6 years old.Replaced and tested, all ok.
MSA-DFES | WA3878244 | Serve Room- light not working | Armadale Regional Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 18 Dec 2020 | 2020-12-29 17:00:00 | 2021-01-11 14:45:00 | Fail | Could not get access to services room as staff on site did not have keys to access nor knew where to obtain them. Will have to return to complete.
MSA-DTAG | WA3877832 | One of the lights in the Registry waiting areas is flickering | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 18 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 11:03:00 | Pass | Replaced 3 x blown fluoro tubes in registers areaReplaced 8 x blown pl lamps in registers area Replaced 1 x broken light cover in registers area
MSA-DTAG | WA3877841 | Graffiti tag in the male public toilets requiring removal | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 2 | CLOSE | 18 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-22 17:00:00 | Pass | Removed graffiti
MSA-DTAG | WA3877845 | Male public toilets - toilet leaking | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Dec 2020 | 2020-12-18 17:00:00 | 2020-12-31 12:30:00 | Fail | Replaced inlet valve and outlet washer in duct
MSA-DTAG | WA3878083 | Lvl 5, Female Toilet (Near Court 52)- Toilet leaking | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2021-03-10 11:15:00 | Fail | COMPLETED
MSA-DTAG | WA3878092 | Lvl 5, Male and Female Toilet- Syringe boxes are not secure & accessible | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-24 11:00:00 | Fail | removed boxes for another contractor to install
MSA-DTAG | WA3878101 | L 2A stairs 2 x slip noses in stairwell leading to 2A need damaged | Central Law Courts | GMP-BR-HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Midolo Building Services | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-08 14:15:00 | Fail | SLIP NOSES HAVE BEEN RE SECURED
MSA-DTAG | WA3878147 | Non-contact room in the custory area - A prisoner has vomited, Bio clean required(see note location) | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 18 Dec 2020 | 2020-12-18 15:35:16 | 2020-12-18 19:30:00 | Fail | Job completed as per WO.
MSA-DTWD | WA3877908 | T block cafe freezer - ceiling light full of water and not secured seals broken, see notes below | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-04 13:45:00 | Fail | Attended site and signed in. Got keys from facilities. Located cafe. Checked out freezer light. Found to work okay but hanging from freezer roof. Fitting cracked and damaged. Disconnect and removed faulty light. Supply and replace with new led weatherproof batten. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3878107 | Southern Hall Bathroom Flat C Right hand side sink blocked | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-21 10:30:00 | Pass | Cleared blockage
MSA-DTWD | WA3878148 | Storage - High level water | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 18 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-22 11:45:00 | Pass | No more issues with alarm
MSA-DCS | WA3878380 | Conrol room: CCTV monitoring system is not accessble unable to acess via keyboard | Karnet Prison Farm-Main Complex External Area | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Dec 2020 | 2020-12-19 12:34:58 | 2020-12-19 12:00:00 | Pass | Attended site checked and found Control Indigovision Monitor mouse and keyboard no response. Checked batteries are ok. Traced cable back to workstation in comms room and located problem to be the USB extender not responding. Reboot USB extender for mouse and keyboard. Tested all ok after work.
MSA-DCS | WA3878392 | Gas coin- unit Laundry area -Water leak from the washing machine | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 19 Dec 2020 | 2020-12-19 14:25:49 | 2020-12-19 13:20:00 | Pass | Cleared blocked main drain to Unit A
MSA-DCS | WA3878393 | gate house - main door buzzer not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-22 15:30:00 | Pass | Door buzzer found faulty replaced with new from van stock. Retested ok.
MSA-DCS | WA3878414 | Control room -Unit 7- Air condition keeps on tripping | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Dec 2020 | 2020-12-20 15:02:24 | 2020-12-24 14:30:00 | Fail | Pressure held, evacuated unit, charged unit with r22, ran up unit, all ok.
MSA-DCS | WA3878427 | Alarms went down in unit 1, throughout whole unit. Security Risk | West Kimberley Regional Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Dec 2020 | 2020-12-20 06:54:55 | 2021-01-13 16:00:00 | Fail | Removed old UPS that was faulty and installed new Smart UPS and Programmed. Tested operation with Mains Fail & HLI to Gallagher. All in working order.
MSA-DCS | WA3878440 | Aircon in front gate control room is faulty | Casuarina Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 20 Dec 2020 | 2020-12-21 08:00:01 | 2020-12-22 14:35:00 | Fail | Arrived on site and signed in,checked pressure test system held pressure overnight, released nitrogen and vac out system and recharge with R22, test run unit all running ok at present.
MSA-DCS | WA3878443 | Couple of cameras 37 and 141 got no picture | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Dec 2020 | 2020-12-29 17:00:00 | 2021-06-28 12:06:00 | Fail | Repaired multiple faults and tested ok.
MSA-DCS | WA3878444 | HAKEA-GATEHOUSE- Zone 1- Internal px is not activating. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Dec 2020 | 2020-12-21 08:29:18 | 2020-12-20 14:00:00 | Pass | Attended site checked and found Internal Zone 1PX not activating during the walk test. Reboot Senstar module for Internal Zone 1 PX. Walked test and confirmed with Control alarm activated and reset correctly after.
MSA-DCS | WA3878465 | CCU Unit 11 - Cell D3 - Night vision camera is very dark. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Dec 2020 | 2020-12-21 10:26:49 | 2020-12-22 07:30:00 | Fail | Accessed IR illuminator, Tested and found no power. Located and replaced failed fuse in roof space patch panel. Tested and confirmed operation of IR during day. Reviewed video from overnight on 21/12 and confirmed IR illuminator operating correctly.
MSA-DCS | WA3878466 | Key watcher time is not correct, 7 minutes different | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-22 09:00:00 | Pass | Check of keywatcher time corrected to correct time. Staff advised
MSA-DCS | WA3878472 | CCTV Cameras in different locations, some of them are not working. | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Dec 2020 | 2020-12-21 11:52:30 | 2021-02-04 16:30:00 | Fail | Replaced X2 Honeywell IP fix dome cameras with new Axis IP fix dome. Job completed .
MSA-DCS | WA3878473 | SITE COST Elec Oven in unit 7 is not working | Hakea Prison | WSM-BR-SITE | Electrical | Materials (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 20 Dec 2020 | 2020-12-20 16:20:26 | 2020-12-20 14:20:00 | Pass | Dried out electrics and reset safety switch, tested ok.
MSA-DTWD | WA3878493 | North Metro TAFE-Balga Campus-Block O - All zones have dropped out in O Block | Balga Campus-Block O | GMP-BR | Security | Security Management System (SE) | Casa Security Pty Ltd | 0 | CLOSE | 20 Dec 2020 | 2020-12-20 19:38:51 | 2020-12-20 18:00:00 | Pass | Restored the system to arm all areas
MSA-DCS | WA3878808 | visits room, camera 99 frozen cannot PTZ | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 07:29:15 | 2020-12-21 15:30:00 | Pass | Attended site checked and found Camera 99 PTZ function is not working. Reboot Fiber modem in gate house equipment room still not working. After reboot camera and Fiber modem on field then tested all ok.
MSA-DCS | WA3878827 | unit 7 G7 Tap Broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-23 09:55:00 | Pass | Replaced broken toilet seat button
MSA-DCS | WA3878835 | Unit 7 Regi oven keeps turning off | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 07:45:27 | 2020-12-22 11:55:00 | Fail | Installed new contactor, test function ok now.
MSA-DCS | WA3878841 | unit 6 regi ovens One oven keeps turning off | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 07:50:17 | 2020-12-22 12:30:00 | Fail | Replaced new thermostat, test operation ok
MSA-DCS | WA3878846 | control pod alarm system continues to activate | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 11:53:25 | 2020-12-21 12:00:00 | Fail | Z-1D incorrectly set. Changed to isolate but tested ok. Set to isolate as per instruction from officer due to high traffic area during daytime. Other CCTV old alarms cleared. System tested ok.
MSA-DCS | WA3878866 | entry pod CCU duct 6 alarm showing alarm fault | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 11:56:27 | 2020-12-21 10:00:00 | Pass | Attended site checked and found CCU DUCT 6 door alarm keep activating in Control. Checked on field found the door recently been replaced and the door magnet for reed switch hasn’t been installed back after replacement. Tested reed switch working ok with spare magnet. Customer will get door technician back to install the magnet.
MSA-DCS | WA3878869 | entry pod recreation alarm showing in fault | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 12:06:43 | 2020-12-23 13:30:00 | Fail | Attended site to replace the faulty 8 input expansion card. Tested it ok after replacement. Gallagher C200680X1
MSA-DCS | WA3878875 | Drug Detection offices - step on stair, requiring repairs as given out/broken | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | Midolo Building Services | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 08:06:12 | 2021-01-08 08:30:00 | Fail | STEP REPAIRS COMPLETED
MSA-DCS | WA3878889 | Unit 3, Cell B2 - sliding window cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2021-01-07 13:00:00 | Fail | WINDOW SASH RE GLAZED
MSA-DCS | WA3878899 | unit 10 C/D Wing Exit Door Glass cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 08:17:23 | 2020-12-21 14:45:00 | Pass | reglazed door glass
MSA-DCS | WA3878912 | S O P - A13 Toilet not flushing and cistern not filling | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 08:25:49 | 2020-12-21 14:21:00 | Pass | Nill
MSA-DCS | WA3878917 | perimeter, Right light tower 22a is not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-21 11:30:00 | Pass | Replaced perimeter Light pole 22A
MSA-DCS | WA3878919 | Bakery prover not heating, didital temp gauge is flashing | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 08:29:22 | 2021-03-10 15:15:00 | Fail | COMPELTED 10/3/21
MSA-DCS | WA3878941 | unit 6 B wing showers sink tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 10:29:00 | Pass | No issues found all taps in working order
MSA-DCS | WA3878947 | Unit 3 - D12 Window needs fixing - not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-04 13:00:00 | Fail | spiral balances renewed & frame repaired
MSA-DCS | WA3878953 | unit 6 D6 toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 13:45:00 | Pass | Replaced faulty washer and flushing mechanism
MSA-DCS | WA3878955 | Unit 3, D11 - Window unattached. (unit 3 lobby next to SO room) | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 12:51:49 | 2020-12-21 14:00:00 | Fail | replaced spiral balances
MSA-DCS | WA3878966 | Unit 4, B wing - shower pressure is very low, only one person can shower at a time | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 08:56:13 | 2020-12-21 14:22:00 | Pass | Nill
MSA-DCS | WA3878975 | Unit 4 B1 external bricks can be removed from the wall - see notes | Casuarina Prison | GMP-BR- HO | Building | External Walls (BU) | Midolo Building Services | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2021-04-06 12:30:00 | Fail | Brickwork repaired
MSA-DCS | WA3878979 | Unit 7, D11 - not hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 09:03:35 | 2020-12-21 14:25:00 | Pass | Nilk
MSA-DCS | WA3878984 | Unit 4, Cell G25 - toilet cistern button broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-22 09:00:00 | Pass | Fixed cistern button - no parts required
MSA-DCS | WA3878987 | unit 2 cell 14 door lock broken | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 09:07:22 | 2020-12-21 13:00:00 | Pass | Replaced Broken Prisoners Privacy Door Lock on Cell 14 Unit 2C Wooroloo Prison Farm
MSA-DCS | WA3878994 | Unit 1, A9 - basin Tap continually running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 09:09:22 | 2020-12-22 09:30:00 | Fail | Nill
MSA-DCS | WA3878996 | unit 6 A15 Toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 15:06:00 | Pass | Replaced faulty washer due to being faulty and new flexi
MSA-DCS | WA3879003 | Unit 14, B5 - Water faucet pressure slowly running- hot and cold taps. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 13:28:00 | Pass | Nill
MSA-DCS | WA3879011 | unit 1, B10 - key stuck in prisoner lock | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 13:15:05 | 2020-12-21 11:00:00 | Pass | Open locked cell , prisoners Privacy lock had malfunctioned rendering door unable to be opened replaced broken Privacy lock .
MSA-DCS | WA3879016 | Unit 14, D02 - sink leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-24 11:32:00 | Pass | Nill
MSA-DCS | WA3879017 | Unit 14 - B9 internal cel light not operating | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-22 13:00:00 | Pass | Repaired faulty lights in unit 14 b9
MSA-DCS | WA3879020 | Unit 7, D9 - system has broken away from wall bracket and is not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-24 08:30:00 | Pass | Nill
MSA-DCS | WA3879032 | Unit 1 - C5 power point has a faulty switch | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-22 10:00:00 | Pass | Replaced damaged gpo in unit 1 c5
MSA-DCS | WA3879045 | Unit 14, B & D Officers post door wont open via key | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 13:30:35 | 2020-12-30 12:15:00 | Fail | Remove barrel, dismantle, remove foreign object, obtain temp. barrel from another door.Replace barrel.
MSA-DCS | WA3879061 | Poultry shed - Electrical box faulty (possible damaged from sparks) | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 09:48:30 | 2020-12-22 15:00:00 | Fail | Investigate Poultry Shed fault. Replace mains connection box
MSA-DCS | WA3879063 | CCU, D4 - reading light switch has been pushed inwards into bed head renedering the switch unusable | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 09:55:50 | 2020-12-21 15:00:00 | Pass | Reinstalled damaged cell switch in CCU d4
MSA-DCS | WA3879066 | B Wing, Ablution block- toilet pan is damaged | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2021-02-03 10:08:00 | Fail | Replacec pan, had a few issues gaining entry to finish pan off
MSA-DCS | WA3879102 | Unit 5, Cell D13- toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 10:29:03 | 2020-12-22 08:30:00 | Pass | Nill
MSA-DCS | WA3879107 | Unit 14, D Wing- Lighting in cleaning stores need fixing, see notes below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-22 11:30:00 | Pass | Repaired faulty lights in unit 14 store rooms
MSA-DCS | WA3879111 | Unit 1, Cell D10- Missing door lock strike plate | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 10:35:16 | 2020-12-22 13:30:00 | Fail | Replace worn hinges and weld on strike plate
MSA-DCS | WA3879115 | Unit 4, Cell B2- Personal lock plate has come away from door | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-30 10:30:00 | Fail | Require parts.Weld on strike and repair lock.
MSA-DCS | WA3879130 | medical centre safe contaiting meds needs to be open connot open | Melaleuca Prison | GMP-BR- HO | Security | Safes (SE) | AAA Ability Locksmiths | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 14:43:50 | 2020-12-22 12:00:00 | Fail | 21/12/2020 Attend site, investigate issue with safe require parts. 22/12/2020 onsite supply and install replacement locks.
MSA-DCS | WA3879158 | Official visits - Office Key stuck in door visits lobby area. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-27 09:45:00 | Fail | Remove jammed key, service and replace bolt throw.Replace lever pack.
MSA-DCS | WA3879160 | Textiles - Sewing machine light post needs checking to see if it is live. | Casuarina Prison | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-24 07:32:00 | Pass | Investigated and tested sewing machine in textiles, all ok
MSA-DCS | WA3879161 | Unit 14 - B9 Light switch or ballast seems to be faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-24 07:35:00 | Pass | Repaired faulty lights in unit 14 b9
MSA-DCS | WA3879177 | Sally port door is not secure due to a power surge | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 15:32:04 | 2020-12-21 12:00:00 | Pass | 21/12/20Inspect doors.No fault found.
MSA-DCS | WA3879185 | unit 17 cell A14 plug socket has been burnt out | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 11:38:31 | 2020-12-22 08:30:00 | Pass | Replaced damaged cell gpo in unit 17 a14
MSA-DCS | WA3879192 | Unit 2B-POD 2-The oven in the living accommodation is not working. Electric | Wooroloo Prison Farm-Prisoner Accommodation Unit 2B | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-22 13:00:00 | Pass | Repaired element in oven
MSA-DCS | WA3879193 | Gym- Solenoid Failed - STN 27 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 11:47:26 | 2020-12-21 14:45:00 | Pass | changed faulty valve
MSA-DCS | WA3879199 | unit 4 B and D wings cell vent have airflow issues | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 11:50:45 | 2020-12-21 15:00:00 | Pass | Repaired vent system, reset O/L and tested.
MSA-DCS | WA3879208 | Unit 15 - The Whole Unit Aircon in the wings is not working correctly it is far to hot - see notes | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 12:05:05 | 2020-12-21 15:05:00 | Pass | Arrived on site and signed in, checked over aircond found units feeding wings are heating/ventilation systems only(no cooling).
MSA-DCS | WA3879329 | Gwynlea Building, Ground, STS Office - Water leaking from reverse cycle air con unit | Nyandi Training Academy | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-22 15:45:00 | Pass | Cleaned the Evaporator coil, fan scroll and drain line.
MSA-DCS | WA3879343 | Gym, Main Entry Door -damage on bottom of door due to flooding in area back in May | Nyandi Training Academy | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-29 12:15:00 | Fail | Carried out repairs to the bottom of door leading into gym.
MSA-DCS | WA3879390 | Program room 5 - how water urn not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-04 09:40:00 | Fail | This unit was working on arrival. Checked operation, all appears okay. Checked with Steve from maintenance it was correct location and model. A40421253A
MSA-DCS | WA3879407 | Unit 2 - Fire alarm falsely activating, can't shut noise/reset | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 18:18:59 | 2020-12-21 15:37:00 | Pass | WA3879407 21/12 Melaleuca Prison. Fire alarm in unit 2. Checked and found C/D 15&16 VESDA unit show alarm. Reset alarm. Panel showing 2 x faults due to ongoing works. Everything else normal on departure.
MSA-DCS | WA3879408 | Unit 14, Cell D01- Tamper alarm sounding. (Suspected water damage casuing it) | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-21 17:30:00 | Pass | Attended Unit 14, drilled out Rivets and noted water damage on PCB. Removed Cell call and replaced cell call unit. Tamper alarm continued t activate when cell call removed. Checked RJ45 Plugs Cell call and found corrosion across pins, removed and replaced RJ45 plug. Tested circuit to equipment rack before connecting. Reconnected cell call and tested to Unit Control, good audio both ways.
MSA-DCS | WA3879420 | MPU, Cell M19 - no water from the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 14:37:16 | 2020-12-23 08:30:00 | Fail | 22/12: 1:30pm couldn’t gain access into mpu
MSA-DCS | WA3879424 | Unit 13 - False activating fire alarms ( see notes) | Casuarina Prison | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 18:42:06 | 2021-02-02 12:06:00 | Fail | WA3879424 21/12 Casuarina Prison. Unit 13 vesda fault A/C 7&8. Went to vesda unit and display was completely dead. Removed 24v as power was present and then reinstated after 5minutes. Unit appears normal, tested sampling points and not getting any readings. Unit if faulty and needs to be replaced.Attended site and replaced faulty unit as quoted, fitted new shield and tested. All ok
MSA-DFES | WA3878878 | station officers ensuit bathroom blocked drain in shower area | CFRS Claremont | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-22 08:20:00 | Pass | Unblocking the shower drains
MSA-DFES | WA3879122 | whole of station infestation of redbacks please check whole station | CFRS Vincent | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 14:00:00 | Pass | Carried out full spider treatment around external perimeter areas of fire station (up to 4 meters height), unless obstructs or unsafe. Treated walls, drains, lamps, seatings, around door and window frames, roof covers, gutters downpipes etc. No current internal problem reported.
MSA-DFES | WA3879147 | Whole station infestation of red back spiders | CFRS Perth | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-22 15:50:00 | Pass | Carried out pest treatment for spiders to following areas : internal tunic and hose rooms. Around all external perimeter areas up to 4 meters height ( unless obstructed or unsafe).
MSA-DFES | WA3879151 | Decommission sprinkler head which was covered over by newly laid shed foundation | DFES Baldivis | GMP-BR | Plumbing & Drainage | Materials (PD) | Dom's Total Grounds Maintenance | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 19:00:00 | Pass | 2 x Out of Metro Area Call Outs & LabourParts $18.00
MSA-DFES | WA3879385 | Engine room door 2 - received impacted damage to bottom panel | CFRS Fremantle | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 21 Dec 2020 | 2020-12-22 17:00:00 | 2020-12-21 17:30:00 | Pass | COMPLETED
MSA-DTAG | WA3878904 | Clock needs to be fixed on the CCTV camera's | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-22 10:00:00 | Pass | -attended site -investigated issue with clocks on work stations showing incorrect times -found all work stations are syncing time from the server-gained access to the server cabinet and resolved the time sync issue, all ok.-whitest in the communications room upstairs found archiver 1 Workstation beeping due to a failed hard drive, it is a 3TB seagate 3.5inch
MSA-DTAG | WA3878907 | Cameras CCTV2, No. 12, 15 & 16 not working | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2021-04-27 12:38:00 | Fail | Installed ptz camera replacement as per upgraded works approval.Checked camera and tested all okAdvised site of the outcome
MSA-DTAG | WA3878923 | Possible faulty alarm panel - please check there is no issue with the alarm panel in the garage | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-22 13:15:00 | Pass | -investigated issue with alarm being activated on Saturday’s via the magistrates parking area-found site is deactivating the wrong area-provides the correct area 1 to be disarmed-all ok left site
MSA-DTAG | WA3878942 | several cameras on different levels have lost connection - no visual | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 21 Dec 2020 | 2020-12-21 12:43:25 | 2021-01-20 14:30:00 | Fail | 21/12/2020: Technician attended site, multiple cameras unable to connect to server, connected to each camera andchecked live view and status of cameras. Restarted camera through software, all cameras restored, downloadeddiagnostic report from each camera and server. Logs sent to milestone.22/12/2020: Technician attended site and downloaded logs from camera and server, checked firmware of cameras.Milestone will review both logs.20/01/2021: Technician attended site, identified multiple Axis cameras dropping due to stream error. Found existingfirmware has bug causing memory leaks. Updated firmware, streaming fine.Job completed.
MSA-DTAG | WA3879015 | Basement, Custody- Sub floor outside interview rooms is spongy when weight is applied | Supreme Court | GMP-BR-HO | Flooring | Timber (FL) | Midolo Building Services | 3 | CLOSE | 21 Dec 2020 | 2020-12-30 17:00:00 | 2021-03-09 09:45:00 | Fail | FLOOR & WALLS REPAIRED - PAINTING TO BE ORGANISED BY IAN
MSA-DTAG | WA3879029 | Lift 1 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-21 10:50:00 | Pass | Car on park. Rode lift no issue. Rts to be closed out at $0
MSA-DTWD | WA3879403 | Muresk Hall - Leaking pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 2 | CLOSE | 21 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-24 16:00:00 | Pass | Repaired leaking pipe and replaced leaking valve
MSA-DCA | WA3881152 | ZONE 10, Reticulation leak | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Water (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-24 08:00:00 | Fail | Two sprinklers in zones 8 and 10 were broken from vandalism. There were replaced and left in working order
MSA-DCS | WA3879549 | Jeelia B-wing - Unable to insert the key to unlock the front door of the wing | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 09:48:21 | 2020-12-22 08:00:00 | Pass | Attend site to replace cylinder on B-Wing front door.
MSA-DCS | WA3879674 | Unit 2 C4 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 07:24:20 | 2020-12-22 10:00:00 | Pass | Reset retested ok
MSA-DCS | WA3879681 | visits Non Contact Room 3 Speaker not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 07:27:41 | 2020-12-22 11:00:00 | Pass | Power cycle of power supply retested ok. ***System recommend replacement no parts available for current system.***
MSA-DCS | WA3879692 | unit 3 A wing urinal blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-22 12:00:00 | Pass | Complete
MSA-DCS | WA3879719 | Unit 16 Fire alarms going off in fault, unable to reset | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 11:56:15 | 2020-12-22 10:24:00 | Pass | 22/12/20 JN - CasuarinaUnit 16 cell A4 in flow fault. Found toothpaste smeared on sample point grate. Cleaned toothpaste and unit returned to normal. Multiple other cells went in and out of fault while at the unit. Advised unit control that they will need to check every cell that goes into fault to see if sampling vent is obstructed/has been tampered with.
MSA-DCS | WA3879733 | Unit 5 - Court Yard solenoid is faulty | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 08:07:00 | 2020-12-22 10:00:00 | Pass | Replaced faulty valve
MSA-DCS | WA3879743 | Oval lights not comming on at night | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 08:12:09 | 2020-12-22 11:00:00 | Pass | Replaced faulty timer and re-programmed
MSA-DCS | WA3879746 | Cell D6 light switch inside cell broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-24 07:36:00 | Pass | Repaired damaged cell switch in CCU d6
MSA-DCS | WA3879789 | Unit 7 G Wing Cleaning Cuboard sink blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-23 12:50:00 | Pass | Unblocked badly blocked sewer drain
MSA-DCS | WA3879829 | Unit 2, Turnstile gate on free constantly whether switch on or off | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-22 12:30:00 | Pass | Attended unit 2, confirmed Turnstile free access, and noted buzzer functioned when “Free/Secure” Switch set to secure. Accessed Turnstile Control PLC in head of Turnstile and noted Alarm LED active. Reset controller, tested Turnstile operation, and corrected buzzer wiring to ensure buzzer sounded when Turnstile insecure.
MSA-DCS | WA3879847 | ISU - no camera feed on monitors. (RCD tested this morning and hasn't reset since) | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 13:12:18 | 2020-12-22 12:00:00 | Pass | No camera images on desktop monitor (#1) or overhead displays (#2, 3 or 4). Restarted PC, found Indigo Control Centre password and changed monitor layouts. Brief training provided for staff.
MSA-DCS | WA3879886 | unit 1 cell call unable to answer | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 17:33:32 | 2020-12-22 12:30:00 | Pass | Attended site checked and found Unit 1 cell call error caused by main cell call computer not working. Computer will be fixed under job WA3879890. Tested cell call working in Unit 1. Job completed
MSA-DCS | WA3879890 | unit 3 cell call not working loud buzzing noise | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 17:35:44 | 2021-01-22 10:00:00 | Fail | Buzzing noise was from errors on old server failure. New server since installed and new config has been synced to unit and alarm message manually removed. Two tech test of multiple intercoms and all is now functioning fine.
MSA-DCS | WA3879895 | unit 4 PRU visits family south west camera is blury and lines | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 09:36:37 | 2020-12-23 13:00:00 | Fail | This is being auctioned on WA4358005.
MSA-DCS | WA3879897 | Unit 4 programs camera 46 black and blue screen | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 09:38:17 | 2020-12-22 16:15:00 | Pass | Checked Camera 46 is ok on Indigovision workstation. Can’t see problem reported. Can see some spider web on camera. Will clean up camera during the maintenance ( Camera is high ).
MSA-DCS | WA3879907 | gate control seeking screen on the main monitor not activating alarm and is blue | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 09:42:06 | 2020-12-22 17:30:00 | Pass | Checked and found the main CCTV Monitor is working ok when Perimeter alarms activated. Can’t see the problem.
MSA-DCS | WA3879910 | Abattoir, prisoners toilet wash sink foot operated tap faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-24 12:00:00 | Pass | Started job on verbal request, correct start date and time 22/12/2020 @ 09:00
MSA-DCS | WA3879928 | PTZ Camera, number 1 has intermittent fault | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 18:07:55 | 2021-01-14 08:00:00 | Fail | replaced encoder 1 power supply
MSA-DCS | WA3879933 | Zone 14A MW constant activation | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 18:10:55 | 2021-10-11 15:00:00 | Fail | Replaced faulty SW tranceiver and alinged, job completed.
MSA-DCS | WA3879936 | Zone 14 mircowave, receiver number 32 constant activation | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 18:15:58 | 2021-02-19 10:00:00 | Fail | ran reports on system & found transceiver working correctly. adjacent zone has a fault but advised site to raise a separate job
MSA-DCS | WA3879945 | Alarm sensor in door frame is popping out | Maddington (South East Metro) | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 10:24:41 | 2020-12-22 15:45:00 | Pass | -attend site -located faulty read switch -replaced faulty read switch-applied silicone to hold read switch in place due to oversized hole from installation-read switch in door frame was also loose from installation, silicone was also applied to hold it in place-tested all okParts supplied - 1x 19mm flush mount read switch
MSA-DCS | WA3879950 | conrol perimeter internal MF fence zone 1 not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 10:29:21 | 2020-12-22 14:00:00 | Pass | Tested working ok. Recommend on next routine maintenance that sensitivity be adjusted.23/12/20 recalled by site, replaced cable ties & tested all panels ok. found fault with EBI alarm settings. rectified & tested back to gatehouse. job complete
MSA-DCS | WA3879951 | conrol perimeter internal MF fence zone 13 and 14 not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 10:31:49 | 2020-12-23 10:15:00 | Pass | Zone 13- end of line resistance unstable. Found poor connection. Repaired join, replaced cable ties. Tuned and tested ok. Zone 14- replaced cable ties. Tuned and tested ok. Parts used:400 x 180mm cable ties
MSA-DCS | WA3880030 | Unit 1, B7 - Viewing window smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 11:15:17 | 2020-12-22 15:45:00 | Pass | reglazed smashed viewing window AND FRAME REPAIRS
MSA-DCS | WA3880036 | Unit 4, A & C Regi Sink is Leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-24 11:39:00 | Pass | Nill
MSA-DCS | WA3880043 | Murchison B wing Cell #B07 Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-23 13:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3880053 | Pump needs re setting and station settings need checking because tank is running dry | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 11:31:47 | 2020-12-22 15:50:00 | Pass | AS PER ATTACHED DOCUMENTS, REFERRED TO PROGRAMMED FACILITY MANAGER FOR FURTHER ACTION
MSA-DCS | WA3880069 | Sewer Mulcher is in fault mode, is not working & wont reset | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 11:43:09 | 2020-12-22 16:27:00 | Pass | Investigate alarm to muncher,Got Electrician to test the system.Reset and test muncher working ok.
MSA-DCS | WA3880092 | Unit 7, E Wing Yard- MWB Man Hole Cover Broken | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2021-01-13 11:00:00 | Fail | CONCRETED INFIL AND WELDED ON STEEL PLATE
MSA-DCS | WA3880097 | Unit 7, Cell E1- External light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-23 10:30:00 | Pass | Replaced light switch
MSA-DCS | WA3880105 | Unit 7 H6 External Light Switch Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-23 09:00:00 | Pass | Replaced broken light switch.
MSA-DCS | WA3880108 | Unit 7, Cell H8- External light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-23 11:30:00 | Pass | Replaced light switch
MSA-DCS | WA3880115 | Unit 10, Cell D5- Tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-29 11:20:00 | Pass | Replaced leaking spindles
MSA-DCS | WA3880144 | Admissions- main monitor for camera feeds has a error "check signal cable" | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 16:10:29 | 2020-12-22 16:30:00 | Fail | EBI door control screen ok, CCTV monitor blank. Power to monitor ok. Monitor on the wrong source. Possibly knocked while cleaning. Changed source to VGA. Tested ok.
MSA-DCS | WA3880151 | Unit 13, Cell C6- Sink tap is not working, no water comes out when truned on, shower is ok | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 12:14:16 | 2020-12-23 11:30:00 | Pass | Nill
MSA-DCS | WA3880197 | Gatehouse- Air Con not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 12:39:31 | 2020-12-22 14:33:00 | Pass | Was on site carrying out repairs to this unit on work order WA3878440.
MSA-DCS | WA3880199 | unit 2 cell B1 Main lock catches when turning the key | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 12:47:04 | 2020-12-22 14:30:00 | Pass | Attend site to inspect main lock on cell B1 in unit 2. Replace worn out driver.
MSA-DCS | WA3880212 | unit 2 cell D13 prisoner in cell unable to open main lock by officers | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 17:03:24 | 2020-12-22 15:45:00 | Pass | Attend site to gain entry to Cell D13 in Unit 2 as prisoner was trapped in the cell. Unable to unlock, required to cut the bolt to open.
MSA-DCS | WA3880224 | Reception kitchen vinyl floor lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2021-01-05 14:00:00 | Fail | DAMAGED AREA'S OF VINYL REMOVED & REPLACED
MSA-DCS | WA3880499 | Visits Centre - Fire alarm panel showing fault, unable to reset | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 17:57:24 | 2020-12-22 16:29:00 | Pass | 22/12/20 JN - Hakea PrisonL4 D4 showing as missing in FIP. Replaced sensor all ok.
MSA-DCS | WA3880752 | Unit 5 A wing showers tap in the middle no hot water - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 14:11:45 | 2020-12-23 08:45:00 | Pass | Replaced faulty spindle. Struggled to unscrew it due to corrosion
MSA-DCS | WA3881108 | Unit 3, B wing- PA speaker not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-23 11:00:00 | Pass | Pa for unit 2 and 3 working all ok but phones do not work for unit 2 pa phone tech to attend and fix
MSA-DCS | WA3881120 | Unit 13 - B Wing Camera B Wing window ( no 7 ) showing as No Video Input. - SEME on site | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-23 11:30:00 | Pass | Reset and tested equipment. Removed Encoder card and let cool down and slot back in. Camera working normal after works.
MSA-DCS | WA3881124 | Unit 6, front entrance - Small Electronic gate can not be operated by the elec system in control | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2021-01-19 11:45:00 | Fail | Replaced lock. Tested everything functioning as normal.Sourced lock from Hakea PFM Stores. Need to replace FES112 24v lock.Lock ordered to replace at Hakea Stores
MSA-DCS | WA3881161 | Unit 4, B/D - Urn in BD side is only filling small amount of water. (see notes) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-24 09:35:00 | Pass | Not much water in the unit on arrival. Opened up unit to see. Not filling much at all. Had to go back to the car to get correct parts. Changed level sensors and tap. Put back together. Checked to see if unit filling up. Normal operation
MSA-DCS | WA3881223 | Master control room kitchen - Leaking hot water Urn | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-23 13:35:00 | Pass | Tap had come loose and causing unit to leak. Re fitted and now not leaking. Unit has condensation behind LCD and isn’t in great condition. Couldn’t determine age as no serial number/model number plate visible.A40189432K Single Housing + Rheem WL A401894332Rheem leaking - tightened Rheem Tap and Descaled TapMaster Control Room
MSA-DCS | WA3881226 | Unit 14, No hot water (maintenance have tried to purge but it will not light) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Dec 2020 | 2020-12-22 20:19:57 | 2020-12-24 08:04:00 | Fail | Nill
MSA-DCS | WA3881228 | Outdoor Area - Faulty sprinklers | Walcott Centre (Central West Metro ) | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 2 | CLOSE | 22 Dec 2020 | 2020-12-29 17:00:00 | 2021-01-04 16:20:00 | Fail | REPLACED FAULTY SPRINKLER
MSA-DCS | WA3881230 | Unit 2, Cell A1 & B3- Possible blockage in cell | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 16:33:47 | 2020-12-23 09:34:00 | Pass | Cleared blocked showers and refitted toilet seat in B3
MSA-DFES | WA3881192 | Drink fountain - hot water leaking out of Pipe | VFRS Falcon | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-23 10:30:00 | Pass | Move releaf pile behind water fountain to a safe location so no one burns them self’s
MSA-DTAG | WA3879767 | level 13 ,meeting room 13.02 duress faulty - gets activated on second attempt after re-setting | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-22 11:30:00 | Pass | Attended site. Tested Duress for Meeting Room, simulated testing multiple times and all okay.Advised to press button, wait about 5 or 10 seconds and only then reset. This will ensure wireless receiver is sendinginput opens and closes correctly.If problem persists, will need to swap transmitter and/or dual button duress module.Job completed.
MSA-DTAG | WA3879823 | custody cell 2 sink not working - see notes | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-22 16:30:00 | Pass | Arrived on site and waited for access. Inspected and found the full pressure to the sink. Adjusted the inlet flow and tested multiple time all working good. Updated the site contact about the job status.
MSA-DTWD | WA3881199 | Cooling Tower leaking | West One Services | GMP-BR | Air Conditioning | Cooling Tower (AC) | Precise Air Group | 1 | CLOSE | 22 Dec 2020 | 2020-12-23 17:00:00 | 2020-12-23 09:00:00 | Pass | Attended service call as per schedule and did pre-startpaperwork, obtained keys and accessed plantroom.Inspected cooling tower and found it to be spraying waterout the side. Put mounting clip back on pad which hadfallen off and tightened to prevent water leaking out.Saw that silicone had cracked and was causing the leak,it seems to have been fixed by tightening the mountingbracket. All ok.
MSA-DCA | WA3881977 | Shaggy chilled water piping | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Plumbing & Drainage | Materials (PD) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 17:00:00 | 2021-01-28 08:00:00 | Fail | Job raised by PFM. Supported lower hanging brackets with construction grade timber as a temporary measure to reduce the sagging in the pipework and take the weight of the pipework off the upper support bracket which has split right down the main structural beams. Will assess during business hours tomorrow to decide if further action required.All repairs to be quoted separately.
MSA-DCS | WA3881326 | Karnet Prison farm control room - CCTV is down | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 10:54:19 | 2020-12-23 10:00:00 | Pass | Found on stuck in loop reset and changed programming to help prevent issues in the future
MSA-DCS | WA3881351 | unit 4 cell K 42 shower taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Dec 2020 | 2020-12-31 17:00:00 | 2021-01-04 11:00:00 | Fail | Complete
MSA-DCS | WA3881364 | Unit 2, Cell 41 (observation cell) - Cell call system and not working | Roebourne Regional Prison | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 07:58:04 | 2020-12-31 16:15:00 | Fail | Ran new Cat6 cable from cell 4.1 to the CI8 outside of U2 control. Intercom tested loud and clear. Parts used:Site spare Cat6 cableConsumables
MSA-DCS | WA3881372 | Unit 2, C1 - Metal grate missing from sink, fit new plug & waste with metal grate | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 14:00:00 | Pass | Replaced seized, damaged and corroded waste
MSA-DCS | WA3881373 | Unit 2, B9 - Metal grate missing from sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 14:20:00 | Pass | Reppaced missing grate
MSA-DCS | WA3881377 | Unit 2, A wing showers - Metal grate missing from sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-14 15:18:00 | Fail | Replaced grate
MSA-DCS | WA3881396 | Unit 6, D6 - Toilet leaking and broken tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-29 16:10:00 | Pass | Rewashed badly leaking and corroded tap
MSA-DCS | WA3881398 | Unit 6, D5 - toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-23 16:10:00 | Pass | Replaced outlet washer and inlet valve
MSA-DCS | WA3881402 | Unit 10, C/D dayroom - Broken tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-29 12:40:00 | Pass | Replaced leaking spindles in the basin
MSA-DCS | WA3881421 | Reception, Wash Room- Washing Machine belt rubbing on bottom panel | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 09:05:46 | 2020-12-23 14:59:00 | Pass | Arrived to find pulley had shaken loose, retightened and added loctite. Tests ok.
MSA-DCS | WA3881441 | Unit 1, C & D Common Area- Fans not working | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 09:25:53 | 2020-12-23 12:00:00 | Pass | Investigate and repair unit 1 c and d common area fans
MSA-DCS | WA3881523 | Download CCTV footage. Please see Ian Roetheli on arrival | Wandoo Rehabilitation Facility | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 10:27:56 | 2020-12-23 12:30:00 | Pass | Run through DOWNLOAD AND PROTECT and INCIDENT PLAYER features on Indigo CCTV system with Ian Roetheli. User manual to be supplied to site for use by security.
MSA-DCS | WA3881529 | Entry Building- Air Con is not working | Bandyup Prison | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 10:34:01 | 2021-09-08 09:43:00 | Fail | COMPLETED
MSA-DCS | WA3881541 | unit 14 - Boiler will not light and has several fault codes | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 14:37:26 | 2020-12-23 14:00:00 | Pass | Drive to site, gain entry to prison and then gain access to the plant room, I found that there was some air in the gas line and that the low gas switch needs to be re set so I done this and then fired heater up,waited for around 20 minutes and then left site
MSA-DCS | WA3881550 | Unit 17- Power point in regi cupboard behind fridge is loose & hanging off wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-24 07:33:00 | Pass | Reinstalled damaged gpo in unit 17 store room
MSA-DCS | WA3881551 | Unit 13, D16 - toilet blocked, tried plunging but did not work | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-24 11:26:00 | Pass | Nill
MSA-DCS | WA3881553 | SHU (9)- Cell A9, night light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-05 10:30:00 | Fail | Attended SHU - unable to gain access Booked in and returned repaired lights
MSA-DCS | WA3881555 | Unit 14, Cell D2- Leaking tap in sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-04 12:29:00 | Pass | Nill
MSA-DCS | WA3881559 | Unit 13, Cell D4- toilet bowl appears to be leaking at the base | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-08 13:30:00 | Fail | No leak found
MSA-DCS | WA3881562 | Unit 4, lunch room - both hot & cold tap have little to no water coming out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 10:52:24 | 2020-12-23 15:30:00 | Pass | Nill
MSA-DCS | WA3881564 | Unit 14, A & C Drinking water tap is leaking | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-24 10:35:00 | Pass | Unit leaking Badly through bubbler. Had to return to the car for correct parts. Hard time finding water isolation. Replaced bubbler, normal operation
MSA-DCS | WA3881632 | Unit 14, D7 - The grille above the window in D7 is jammed and will not move | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 14:45:00 | Pass | lubricated grill
MSA-DCS | WA3881698 | Unit 2, Cell C13- Main Lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 12:06:54 | 2020-12-23 13:30:00 | Pass | Attend site, service main cell lock.
MSA-DCS | WA3881700 | Unit 4, Lobby- Water Cooler not cooling water | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2021-03-03 09:15:00 | Fail | Removed existing fountain and installed new fountainInstalled new Maxiflow Filter System A40191358K + Zip Sitemaster Fountain A40191359L 20201110303011 Bubbler removed old unit to tip
MSA-DCS | WA3881760 | Serpentine, self care - Camera 131 losses picture intermittently | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 12:47:00 | 2020-12-23 15:00:00 | Pass | Camera power supply power cycled reset retested ok.
MSA-DCS | WA3881792 | Middle security door in gate house is not functioning (see notes) | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 12:58:38 | 2020-12-24 21:30:00 | Fail | Attended site and investigated the fault.Checked power and connections on middle security electric strike.Conducted test.All ok at departure
MSA-DCS | WA3881800 | Mian kitchen - main electrical control panel on meat freezer is full of water | Bandyup Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 17:22:31 | 2021-01-05 16:00:00 | Fail | Received call for issues with meat coolroom.Accessed kitchen.Checked controller and discussed with chef.Opened electrical cover and dried.Visually inspected coolroom controller and seemed dry and operating okay.Resealed inside conduit connection in electrical box.Temperature okay.Chefs advised.
MSA-DCS | WA3881805 | Unit 3, POD 6 - hot water urn disconnected as faulty | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 13:26:02 | 2020-12-23 15:30:00 | Pass | Unit is under warranty. Call to be lodged with Zip to repair. Checked water supply to unit, okay. Site requested a loan unit as warranty call by external contractor Zip cannot be done until January - returned and installed loan Boiling Water Urn to site - once warranty repairs were completed by Zip returned and removed loan unit when given access .
MSA-DCS | WA3881831 | Administration, Lunch Room - Aircon unit in Staff Demountable lunchroom is showing an E3 error | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-24 15:47:00 | Pass | Fault due to high ambient. Reset and test. All ok
MSA-DCS | WA3881864 | Prison to reception door alarm constantly sounds | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Reception Area | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 14:08:22 | 2020-12-24 13:45:00 | Pass | Attended site to replace the faulty door strike. Tested all ok after replacement. ES9000 X 1.5/1/21 job recalled by Tim, re attend site & found magnet loose in door, reassembled & tested ok.
MSA-DCS | WA3881871 | Laundry- verandah security lights not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-29 11:00:00 | Pass | Replaced PE cell and tested lights
MSA-DCS | WA3881874 | Kitchen, Rear loading dock cool room - has no power | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 18:14:29 | 2020-12-23 16:00:00 | Pass | Kitchen fridge has no power, someone had hit emergency stop, reset and tested.
MSA-DCS | WA3881911 | Zone 5 perimeter fence constantly alarming | Boronia Pre-release-External Area | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 14:37:56 | 2020-12-23 17:00:00 | Pass | Zone 5 fence alarm was constant alarm. Checked sensor cable with tester found sensitivity is high. Adjusted sensitivity threshold and cut counts. Tested all ok after work.
MSA-DCS | WA3881926 | Temporary Sally Port - re-establish power to the Camera's | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-05 14:30:00 | Fail | Returned to transportable in Temp Sally Port. Restarted remaining camera, cleaned spider webs from gate facing cameras and confirmed good picture at control room.
MSA-DCS | WA3881928 | Perimeter, entry control, zone 14 in constant alarm | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 18:52:07 | 2020-12-23 18:30:00 | Pass | Attended site and investigated the fault.Checked Senstar server and found that there is cable problem on Omnitrax processor 1.When checked temperature in EC7 was 55C ( in Omnitrax enclosure over 55C).Left open doors of enclosure and cabinet.After 45 minutes temperature dropped to 43C.Conducted test.All ok at departure.
MSA-DCS | WA3881933 | Kitchen, Rationale oven not steaming now | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 18:40:57 | 2021-01-14 11:00:00 | Fail | 23/12/20Called as requested to the oven not working. Found a control fuse blown due water getting into the top heat exchanger then leaking through the burner and blower damaging both. attempted to seal the burner port but was unable to therefor the oven is unusable. Parts required 1x burner 1x blower1x electrodes 14/01/21Completed repairs as required tested all ok now.
MSA-DCS | WA3881936 | Gatehouse, control room- Wall mounted hot water unit not heating | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-24 14:00:00 | Pass | Unit was in Economy mode and had switched itself off. Reset unit and informed staff of correct operation.
MSA-DCS | WA3881940 | Unit 14 - Boiler failing to reignite | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 19:08:08 | 2020-12-24 09:30:00 | Fail | Sign in carry out tool checks. Meet with escort travel to unit 13 boiler room. Reset boiler but kept faulting at main flame. Gasfitters had cut into line a few days ago and purged out the gas. Opened test point which had pressure behind it but didn’t smell of gas. Had to vent out line till there was gas and burner could start. Once started flame was weak and eventually got stronger until was just gas in line. Watched get up to temperature and deemed the issue fixed. Packed up travel back to office and carried out tool check and signed out
MSA-DCS | WA3881965 | Medical Centre- Pharmacy, medication fridge is in alarm & spiking in temperature | Wandoo Rehabilitation Facility | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 15:19:25 | 2020-12-24 14:00:00 | Pass | Found pharmaceutical fridge struggling to maintain temperature. Cleaned condenser coil and replaced condenser fan with new motor. All working well however fridge is fairly old.
MSA-DCS | WA3881989 | MDAS Receiver 120 on transponder 601 is in fault | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2021-08-19 11:00:00 | Fail | Alarms cleared and received confirmed as functional. Prison staff not aware of this alarming in recent history. Due to location and EWP hire requirements replacement not recommended at this time.
MSA-DFES | WA3881316 | One fluro light as well as the cover has fallen out in the corridor | CFRS Claremont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 23 Dec 2020 | 2020-12-23 17:00:00 | 2021-01-21 14:15:00 | Fail | Replaced 19 Lights throughout Building.
MSA-DFES | WA3881503 | Main admin - Air Con number 5 is not working | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 17:00:00 | 2021-02-05 11:00:00 | Fail | Picked up parts, attended site, located & isolated ac5.replaced & rewired heater. Re instated power & tested operation ok. Disposed of old part
MSA-DFES | WA3881763 | Retic system needs resetting & checked & multiple sprinklers broken | CFRS Armadale | GMP-BR | Plumbing & Drainage | Drainage (PD) | Dom's Total Grounds Maintenance | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-30 19:30:00 | Fail | Replace Solenoid, Broken Fitting, 4 x Nozzles & 3 x Pop UpsCall Out & Labour & Retic Parts
MSA-DFES | WA3881819 | Lvl 1- ICT Kitchen- Zip hot water tap not working | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-24 11:04:00 | Pass | Replaced faulty Hot pump. All working ok diagnosed and replaced hot pump on A40189194P Zip Hydrotap
MSA-DFES | WA3882004 | Server Room - Air Con is not cooling | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 20:32:29 | 2020-12-23 18:30:00 | Pass | Server room was not getting down to temperature due to the 42 degree ambient temperature cleaned condenser coils which helped and temperature of room come down to an acceptable temperature
MSA-DFES | WA3882021 | Engine room doors - main engine room door wont go up | CFRS Belmont-Main Building | GMP-BR | Building | Doors (BU) | Go Doors | 0 | CLOSE | 23 Dec 2020 | 2020-12-24 00:44:31 | 2021-04-07 10:00:00 | Fail | COMPLETED
MSA-DTAG | WA3881416 | Main FIP needs to be checked & reset after DFES call out | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 12:58:59 | 2020-12-23 10:15:00 | Pass | Fire alarm in 87 building due to works. Contractors deisolated panel but alarms were still active. Was normal when arrived on site. Reset anddeisolated zone. All ok.
MSA-DTAG | WA3881428 | Technician to attend on Tues 29 Dec at 07.00am, scheduled power outage may affect security CCTV | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 23 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 12:30:00 | Pass | Attended site for planned power outage. Safe shutdown and restoral of services whilst electricians conduct switchboardworks.Job completed.APPROVED BRAF ATTACHED.
MSA-DTAG | WA3881533 | 1st Floor, Buss P's office- Door closing mechanism detached from wall | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-24 09:30:00 | Pass | Reattached door closer
MSA-DTAG | WA3881547 | Lower ground floor, Court 6- Air Conditioning set too cold | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-07 09:21:52 | Fail | Attended site and assisted bms tech with replacement of wall sensor in court 6. Confirmed operation of aircon.
MSA-DTAG | WA3881998 | Lvl 1, President's chambers- Metal panel fallen from window frame | Supreme Court | GMP-BR-HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 23 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-24 08:30:00 | Pass | Reattached panel
MSA-DTWD | WA3881665 | Tower block - sliding automatic door, faulty to close takes about 5 goes before closing | West One Services | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 23 Dec 2020 | 2020-12-24 17:00:00 | 2020-12-23 14:45:00 | Pass | Found that the old plastic floor guide has worn down and the door was hitting the frame when closing and bouncing back open, replaced floor guide and adjusted door, tested all ok.
MSA-DTWD | WA3881878 | D Block, External door, G Floor leading to fire stairs, door handle is faulty & wont lock | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 0 | CLOSE | 23 Dec 2020 | 2020-12-23 18:18:04 | 2020-12-23 16:00:00 | Pass | Replaced damaged door handle
MSA-DCA | WA3882335 | Roof top- Chiller 1 is in fault | Collection and Research Centre Welshpool-Harry Butler Centre | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Dec 2020 | 2020-12-29 17:00:00 | 2021-01-04 16:30:00 | Fail | Please refer to work logs. Quotation submitted for applicable repairs. Quotation approved original work order to be closed out.
MSA-DCA | WA3882501 | seal of A/C 4 coils fallen, due to high outside air temp | Art Gallery of WA - James St-Main Building (Block B)-Level 4 | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-29 10:00:00 | Pass | 29-12-2020 0800-1000Due to Rooftop works installing ductwork to AHU 4 and SAF being currently isolated, outside air is being drawn back into the building mixing with the common return air. Used materials on site to block path of air across AHU 4 Cooling Coil.Closed job.
MSA-DCS | WA3882089 | Perimeter fence Beam Zone 1 will not deactivate | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 10:27:49 | 2020-12-24 08:30:00 | Pass | Attended site checked and found Zone 1D PE BEAM has been isolated on Gallagher and can’t be armed again. Logged in as system operator in Gallagher Control Center to rectify the problem. Tested all ok after work.
MSA-DCS | WA3882123 | C4 camera, perimeter, south east side of prison - Camera no signal | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 11:01:29 | 2021-03-15 11:30:00 | Fail | Accessed Equip Cab (EC6) and confirmed still no video at modem in cabinet. Access camera on pole top and on opening noted camera Power Led On. Tested for video out from camera, confirmed. Fault in cable between camera and fibre modem. NOTE: Recent work in this cabinet by another contractor. Removed 4RU mains power mounting panel in base of cabinet where we found a BNC-BNC joint in cable feed for C4 camera. Close inspection of joint indicated very poor connection where Coaxial cable pulled out of BNC Plug. Reterminated both plugs and reconnected. Gate control confirmed good video on monitor from camera C4. Reinstated panes in EC6 and cover on camera housing.
MSA-DCS | WA3882134 | air con issue-air con blowing Hot air and slight burning smell from aircon vent | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 07:00:44 | 2020-12-24 12:30:00 | Pass | Completed priority 1 call out
MSA-DCS | WA3882179 | unit 5, Cell B13 - No water supply | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-04 08:30:00 | Fail | Nill
MSA-DCS | WA3882183 | unit 5, Cell B15 - No water supply | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-04 09:30:00 | Fail | Nill
MSA-DCS | WA3882193 | SHu, A6 - OBS light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-05 11:30:00 | Fail | Attended SHU - unable to gain access.Booked in access. Returned and repaired light 5.1.21
MSA-DCS | WA3882199 | Unit 9, A6 - floor drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 07:51:49 | 2020-12-29 09:15:00 | Fail | Unblocked floor drain
MSA-DCS | WA3882204 | Control room - tamper alarm in zone 4 - not able to clear screens | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 11:59:10 | 2020-12-24 10:30:00 | Pass | Attended site checked and found Zone 4 Fence was in tamper alarm before. Checked on field in EC cabinet sensor cable end of line resistor measuring correctly. Reboot controller and tested alarm activated and reset correctly.
MSA-DCS | WA3882206 | Control room - No PTZ on camera 33 | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 08:01:03 | 2021-04-01 09:30:00 | Fail | Picture ok, no PTZ. Used CCTV tester before the TX fiber modem in Admin to test the camera. Camera ok. Reset the transmitter fiber modem. Image and all a PTZ functions tested ok at the gatehouse.
MSA-DCS | WA3882210 | Unit 1, A wing - Cleaning room pressure tap is broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 08:03:51 | 2020-12-24 11:43:00 | Pass | Nill
MSA-DCS | WA3882213 | Unit 9, C Wing End Grille - Window & frame pulled off end grill | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 24 Dec 2020 | 2020-12-31 17:00:00 | 2021-01-07 11:00:00 | Fail | SASH REPAIRED & RE FITTED
MSA-DCS | WA3882236 | Gym - Termite investigation | Casuarina Prison | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2021-06-08 08:30:00 | Fail | Termite Treatment To Gym Floor.
MSA-DCS | WA3882247 | abattoir - # 2 chiller not working | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 08:26:58 | 2020-12-24 12:30:00 | Pass | Found faulty wiring on condenser fan motor 2 and repaired .left system operational
MSA-DCS | WA3882258 | Unit 7 Regi Oven not turning on | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 08:36:35 | 2020-12-24 12:00:00 | Pass | 24/12/2020 - Arrive at site to check oven not working, found fan motor overload had tripped. Reset and turned up to 1 amp as was set down to 0.63 and motor rates at 0.9. Ran on heat for 30mins and all working well, cutting in and out of temp nicely. Note control fuse has been bypassed by previous contractor, 10amp glass fuse if required in future.
MSA-DCS | WA3882265 | Rectify lighting circuits in gymnasium | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-24 15:00:00 | Pass | Replaced faulty ballast and repaired damaged cables
MSA-DCS | WA3882267 | Unit 8, Service Room Behind S/O Office- Water Heater Leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 08:49:01 | 2020-12-24 19:20:00 | Pass | Replaced section of burst pipe i the roof space. Waited for electrician to make the area safe as there was water dripping on the electrical boxes. Struggled to find access to roof space.
MSA-DCS | WA3882269 | ISU (Harding), Cell C02- Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-24 14:00:00 | Pass | Replaced broken switch with a new one. Test ran ok.
MSA-DCS | WA3882277 | Unit 13, A/C - cold water fountain the A/C dayroom has a blocked drain & looks like alge is building | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 24 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-24 11:20:00 | Pass | Fountain had blocked drain with mould coming out of it. Returned to car for correct parts to clean. Removed drain and cleaned drain and plumbing. Cleaned up. Normal operation
MSA-DCS | WA3882285 | PE Beam in Zone 11 is constantly alarming, see below notes | Roebourne Regional Prison | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 09:00:58 | 2021-04-13 10:30:00 | Fail | traced fault to beam stack 1 at bottom of stack. replaced beam set & realigned as required. tested zone for cctv & alarms ,all ok
MSA-DCS | WA3882294 | Bakery - Prover is not heating | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 13:06:52 | 2020-12-29 09:25:00 | Fail | COMPLETED 24/12/20
MSA-DCS | WA3882321 | Unit 4 - Latch on personal lock on D4 gets stuck when opening door, door cannot lock when this happe | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-30 11:30:00 | Pass | Replace latch and repair lock.
MSA-DCS | WA3882349 | Unit 14 - circulation pump is leaking in the plant room & will not isolate | Casuarina Prison | GMP-BR- HO | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 14:30:00 | Pass | Nill
MSA-DCS | WA3882360 | Unit 6, B Wing grill will only open from control room operation panel, at present it will not close. | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 14:01:06 | 2020-12-24 12:00:00 | Pass | 24/12/20Inspect fault.Working at gate.Not working from control panel.Access control issue. Call SEME
MSA-DCS | WA3882370 | Unit 1, B & D- Disconnect water supply to oven | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-05 08:30:00 | Pass | Nill
MSA-DCS | WA3882399 | sewage line block in poly pipes at the tanks | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 14:50:54 | 2020-12-24 13:30:00 | Pass | Unblocked pump
MSA-DCS | WA3882429 | Unit 4, Cell D12- Water is dribbling out of the tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 11:37:52 | 2020-12-24 12:30:00 | Pass | Nill
MSA-DCS | WA3882447 | unit 1 - c13, c14, c15, c16 - fire panel showing fault, can't reset | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 12:25:43 | 2020-12-25 10:35:00 | Pass | JN - Melaleuca PrisonFixed following faults:Unit 1 A/BCells 7/8, 11/12, 15/16Unit 1 C/DCells 5/6, 7/8, 13/14, 15/16Unit 2 A/BCells 7/8
MSA-DCS | WA3882453 | unit 1 - cell B5 - cell door is jamming in frame | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 12:22:27 | 2020-12-24 15:30:00 | Pass | Carried out repairs to cell door that was jamming
MSA-DCS | WA3882479 | unit 3 - very low water presure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Dec 2020 | 2020-12-25 13:08:19 | 2020-12-24 15:00:00 | Pass | Nill
MSA-DCS | WA3882505 | door between health care and crisis care not securing, opening itself | Melaleuca Prison | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 18:06:01 | 2020-12-24 15:45:00 | Pass | Attend site. Refit bottom hinge and replace screws.
MSA-DCS | WA3882509 | Main Area, Back left hand end- Cockroaches are coming out holes in ceiling | Midland (North East Metro) | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 24 Dec 2020 | 2020-12-31 17:00:00 | 2021-01-08 17:20:00 | Fail | Roof Treatment Cockroaches.
MSA-DCS | WA3882511 | unit 8 - water leak in ceiling | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 18:42:09 | 2020-12-24 16:30:00 | Pass | Investigated water leak to see if it had caused electrical damage in unit 8 no damage found
MSA-DCS | WA3882513 | unit 8 - water leak in ceiling | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 18:46:34 | 2020-12-24 17:00:00 | Pass | water coming from plumbing pipe, not an air conditioning unit. Plumber will need to investigate
MSA-DCS | WA3882573 | control room - fire panel fault - data card fault, alarming, every 2-3 mins | Boronia Pre-release | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 22:28:57 | 2020-12-24 21:39:00 | Pass | JN BoroniaFault on FIP - P:05 C:02 D:607 Data Card Fault OneFault not present when arrived on site. Checked history logs and fault started at 1815 and stopped at 1905. Fault hasn’t come back currently 2100. If intermittent fault comes back to confirm what card the panel is referencing and further fault find.
MSA-DFES | WA3882256 | Main automated security gate to rear yard - jammed closed, not working. | Butler Career Fire Station | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 12:35:39 | 2020-12-24 16:00:00 | Fail | Attended Butler Fire Station - Main power to the gate has tripped causing Power outage to auto gate. Reset power and tested gate -- all working fine
MSA-DFES | WA3882369 | Breathing Apparatus Room- Tap in sink 3 of BA room leaking from button above spout | CFRS Perth | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2021-02-11 09:31:00 | Fail | Replace veggie sprayer head on 3rd sink in ba room
MSA-DFES | WA3882397 | Back of workshop - Card reader number 26 is not working | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 14:47:03 | 2020-12-24 14:00:00 | Pass | 24/12/20 - Ryan VestyChecked reader, tested with access card, checked all connections.No fault found, all working ok.
MSA-DFES | WA3882433 | Engine Room front door 1 - Perspex panel has screws sticking out and holes in frame | CFRS Welshpool | GMP-BR | Building | Doors (BU) | Go Doors | 2 | CLOSE | 24 Dec 2020 | 2020-12-31 17:00:00 | 2021-04-15 15:30:00 | Fail | COMPLETED
MSA-DFES | WA3882470 | excess hot water pouring from pipe - outside boiler room | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 24 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-24 14:30:00 | Pass | Checked leak in boiler room found the relief valve discharging
MSA-DFES | WA3882510 | Engine room doors - main engine room door wont go up | CFRS Belmont-Main Building | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 24 Dec 2020 | 2020-12-24 18:37:25 | 2020-12-24 17:15:00 | Pass | Arrived on site. Isolated supply to roller door and then reinstated when appropriate.
MSA-DTAG | WA3882325 | Ground Level Fault on Fire Panel | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 24 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-24 12:00:00 | Pass | Investigated fire panel fault
MSA-DTAG | WA3882373 | Lvl 3, Male toilet- Door closer bracket is loose | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 24 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-24 11:15:00 | Pass | Repaired door closer
MSA-DCS | WA3882588 | On the internal microwave zone 7 is unresponsive | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Dec 2020 | 2020-12-26 07:49:30 | 2020-12-29 11:00:00 | Fail | Reset TX and RX units. Adjusted alignment. Zone tested ok back to the gatehouse but alignment voltage is at the bare minimum.
MSA-DCS | WA3882596 | unit 2 rear fire door - issues with locking and unlocking door | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Dec 2020 | 2020-12-25 13:54:15 | 2020-12-25 11:30:00 | Pass | Found door issue is unrelated to security system got site to call a locksmith to fix
MSA-DCS | WA3882597 | unit 2 rear fire door - issues with locking and unlocking door | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AAA Ability Locksmiths | 0 | CLOSE | 25 Dec 2020 | 2020-12-25 15:05:46 | 2020-12-25 13:00:00 | Pass | Attend site after hours, inspect unit 2 rear fire door main lock.
MSA-DCS | WA3882605 | gatehouse - trouble tempa transponder 4 (infirmary) | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-31 08:00:00 | Pass | On arrival we noted that there was no Tamper Alarm active for Transponder 4 (Infirmary), however there was an active Tamper Alarm for Transponder 1 (Administration). Attended Admin Comms room and found the transponder rack door insecure. Resecurred door and confirmed alarm had cleared.
MSA-DCS | WA3882613 | internal zone 1A not activating | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Dec 2020 | 2020-12-26 16:44:35 | 2020-12-25 20:15:00 | Pass | Attended site, confirmed with Control staff that the zone did not activate when walk tested earlier in evening. Attended zone 1, confirmed Rx test point voltages all within limits, walk tested zone and confirmed activation with gate control staff. No further action.
MSA-DCS | WA3882630 | kitchen - no power to dishwash | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Dec 2020 | 2020-12-27 07:26:34 | 2020-12-26 11:30:00 | Pass | P1 after hours call outInvestigate and repair power to dishwasher
MSA-DCS | WA3882631 | Fire alarm is going on for the entire unit | Casuarina Prison-Prisoner Accommodation Unit 3 | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Dec 2020 | 2020-12-26 11:44:16 | 2020-12-26 10:51:00 | Pass | Unit 3 DBA and low pressure alarm overnight, likely due to pump running. Reset panel and alarm cleared, deisolated panel all ok.
MSA-DCS | WA3882632 | In diary water cooler in kitchen is pouring, turned water off | Karnet Prison Farm | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-30 10:30:00 | Pass | 29/12/20-Arrived on site and inspected found the parts broken needed parts. Collected parts from supplier 30/12/20- returned to site installed the new parts and reconnected water and tested the water cooler. All working in order.
MSA-DCS | WA3882635 | Unit 15 -Circuit breaker tripped.Affecting the Air con Ventilation Fan | Casuarina Prison-Prisoner Accommodation Unit 14 | WSM-MW-HO | Air Conditioning | Materials (AC) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 26 Dec 2020 | 2020-12-26 12:16:40 | 2020-12-26 14:30:00 | Fail | P0 after hours call outInvestigate and repair unit 15 air con fan
MSA-DCS | WA3882636 | Fire alarm is going on for the entire unit 16 | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Dec 2020 | 2020-12-26 12:14:39 | 2020-12-26 10:49:00 | Pass | Unit 16 flow faults on MADs in panel. Cleared out all sampling points and metal grates in faulty cells, faults did not clear. Ongoing issues with installation, unable to resolve during an AH callout.Task closed out as open task relating to the cleaning of the units is currently open
MSA-DCS | WA3882651 | unit 1 - AC not working | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Ducted Split System (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Dec 2020 | 2020-12-27 10:56:52 | 2020-12-26 15:45:00 | Pass | Found unit operating but struggling with high heat load and moisture content. Turned off unit to allow water to drain and test ran unit. All operational.
MSA-DCS | WA3882675 | Wooroloo Prison Farm - Officer's gym - Entry door lock has become loose and cannot be secured. | Wooroloo Prison Farm | GMP-BR- HO | Carpentry | Materials (CA) | ACE LOCK & SAFE | 2 | CLOSE | 26 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-29 09:00:00 | Pass | Replaced damaged lock on officers Gym door New Lock keyed to GYM key.
MSA-DCS | WA3882676 | Wooroloo Prison Farm - Gym House- Laundry door handle is loose. | Wooroloo Prison Farm | GMP-BR- HO | Carpentry | Materials (CA) | ACE LOCK & SAFE | 2 | CLOSE | 26 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-29 09:30:00 | Pass | Tightened Lock on Gym House - Laundry Door
MSA-DCS | WA3882706 | 1 camera monitor not working in entry control room | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Dec 2020 | 2020-12-26 23:58:11 | 2020-12-30 16:15:00 | Fail | Found drivers old and not working fully with new hdmi extender updated drivers and tested hdmi extender all ok
MSA-DFES | WA3882649 | Hot water system in the bathroom is faulty .No hot water | CFRS Daglish | GMP-BR | Electrical | Materials (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 26 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-26 11:45:00 | Pass | Attended site and located no hot water to officer’s quarters shower. Found isolator out back to be turned off. Turned it back on and tested cable,no faults found. Notified staff that water would take a while to hear back up and if it did not to contact a plumber
MSA-DCS | WA3882722 | Unit 1 -3 fault and 3 Isolate in the panel -Corridor | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 Dec 2020 | 2020-12-27 12:36:06 | 2020-12-27 11:59:00 | Pass | 27/12/20 JN - Melaleuca PrisonFixed following faults:Unit 1 A/BCells 7/8, 11/12, 15/16Unit 1 C/DCells 5/6, 7/8, 13/14, 15/16Unit 2 A/BCells 7/8
MSA-DCS | WA3882731 | All the unit 2 - 6 cameras not working in the gate. | Roebourne Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Dec 2020 | 2020-12-27 17:44:32 | 2020-12-28 13:30:00 | Fail | On arrival at prison was advised by Control officer that Cell Call was displaying Node 2 Fault. Attended unit 2 where we found fibre network switch locked up. Power reset the switch and confirmed Cameras now visible at gate control. Node 2 alarm on cell call now clear.
MSA-DCS | WA3882732 | Zone 13 and 19 are not activatin. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Dec 2020 | 2021-01-05 17:00:00 | 2021-07-16 15:30:00 | Fail | Confirmed zone 19 fence operational and part replenished in stock.
MSA-DCS | WA3882734 | Entry pod camera not responding | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Dec 2020 | 2020-12-27 13:59:09 | 2021-01-21 09:41:00 | Fail | Tested system all tested ok
MSA-DCS | WA3882761 | control room monitor unable to get username and password | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Dec 2020 | 2020-12-27 19:48:09 | 2020-12-27 13:55:00 | Pass | Instructed Gate Control Operator thru login process to identify workstation login name and then howto log the workstation back in.
MSA-DCS | WA3882788 | Cool fridge in the A side dining room, showing high temp. To be attended to Tuesday 29/12/2020 | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 27 Dec 2020 | 2020-12-31 17:00:00 | 2021-01-04 11:00:00 | Fail | Arrived on site and found fridge not cooling due to no gas in system (gas leak)Isolated unit and leak checked. Unable to locate. Will need to return with parts to repair.
MSA-DCA | WA3882866 | Failed reticulation zones. | Perth Cultural Centre Precinct | GMP-BR | Building | Materials (BU) | Earth & Water Pty Ltd | 1 | CLOSE | 28 Dec 2020 | 2020-12-29 10:07:45 | 2020-12-30 14:45:00 | Fail | Zones 13, 14 & 15 had issues with vandalized sprinklers and sticky nozzles .Damaged sprinklers were replaced and silicon spray was used to release grit within sticky nozzles
MSA-DCS | WA3882833 | Casuarina Prison Control Room- Camera in unit 14 D wing down | Casuarina Prison-Administration | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Dec 2020 | 2020-12-29 08:16:14 | 2021-03-03 10:37:00 | Fail | Attended site and repaired camera and encoder.Tested OKJob CompleteParts (SEME Stock):Lens Wipes
MSA-DCS | WA3882834 | Cell call system for the whole site- unable to receive and return on system.. | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Dec 2020 | 2020-12-28 12:11:10 | 2020-12-28 11:00:00 | Pass | Review machine not showing voice logs. Unable to connect to mapped network drive. Reconfigured network drive with credentials and all is ok now.
MSA-DCS | WA3882840 | Loose wire in the kitchen toilet fan, requested for tomorrow attendance | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Dec 2020 | 2020-12-29 05:28:28 | 2020-12-28 12:00:00 | Pass | Investigate and repair kitchen toilet exhaust fan
MSA-DCS | WA3882874 | Mdas machine is not working properly, coming up with multiple error codes. | West Kimberley Regional Prison | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 16:40:00 | Pass | Contacted site and arranged to investigate fault with Facility Manager.Traced fault to corrupt file in system Database - provided instruction over the phone to restore the Database - fault rectified.Monitored fault and requested site conduct PDA test over next 24hrs - no further issues occurred.Works complete
MSA-DCS | WA3882898 | BLOCK H-CCTV monitor issue, | Banksia Hill Detention Centre-Block H Accommodation | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Dec 2020 | 2020-12-28 17:50:52 | 2020-12-28 17:00:00 | Pass | ISU Indigo station showing Windows desktop screen. Logged in and setup the 4 monitors. Wrote up some basic instructions for staff. One copy left in ISU, two copies left with security Officer JENNY COOTE.
MSA-DCS | WA3882909 | UNIT 4a- Cell 50- Cell lock is dodgy | Wooroloo Prison Farm-Prisoner Accommodation Unit 4a Block 1 | GMP-BR- HO | Building | Materials (BU) | ACE LOCK & SAFE | 2 | CLOSE | 28 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-29 10:20:00 | Pass | Replaced deadlatch on Unit 4A - Cell 50
MSA-DCS | WA3882913 | Control Room - Zone 13 Internal Microwave and Perimitrax failed to activate when tested. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Dec 2020 | 2020-12-29 17:19:04 | 2020-12-28 20:15:00 | Pass | Zones showing as secure but alarming when breached. Microwave ok locally. Reset internal modules SM8 and SM9 via UCM program. Dropped power to SM9 in the internal perimeter EC. Both zones alarmed and reset when tested.
MSA-DCS | WA3882917 | Unit 2 -Control room door lock is broken | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 28 Dec 2020 | 2020-12-28 22:40:52 | 2020-12-28 20:30:00 | Pass | Attend site after hours, repair Chubb 3R35 lock on unit 2 control room door.
MSA-DFES | WA3882868 | Storm water drains in backyard filling up and bad smell coming out | CFRS Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 28 Dec 2020 | 2020-12-28 14:06:55 | 2021-03-19 09:13:00 | Fail | Replaced cast iron lids on 2 soak wells due to they couldn’t be lifted off to clear them out. Got them cleared out.
MSA-DFES | WA3882906 | sewerage pump alarm going off- outside main building | VFRS Mundaring- TO BE DECOMMISSIONED VFRS Mundaring-Main Building | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 28 Dec 2020 | 2020-12-31 17:00:00 | 2021-03-22 10:00:00 | Fail | Replace sump pump due to the old one as stoped working tried to repair but was in serviceable
MSA-DTAG | WA3908999 | RETROSPECTIVE WORK ORDER-No monitoring signals from Tecom-Att on the 28/12 | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-31 16:00:00 | Pass | Swap Permaconn unit on Tecom panel. Tested and commissioned signals through to Spain monitoring Centre. All is online and in working order.
MSA-DCA | WA3883212 | Foyer - FIP has LOOP fault | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 17:00:00 | 2020-12-29 11:00:00 | Pass | Fault - open loop - Loop 1 - Performed loop test.Side A 114Side B 114Fault cleared
MSA-DCA | WA3883214 | External, graffiti on the SLWA wall west side towards Francis Street. | State Library of WA-Main Building-External Area-West Zone | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-06 13:15:00 | Fail | Removed graffiti
MSA-DCS | WA3882924 | Admissions - Sally port door for vehicle access wont close - stuck open | Banksia Hill Detention Centre | GMP-BR- HO | Building | Security Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 02:01:17 | 2020-12-29 08:45:00 | Pass | Signal to OPEN/CLOSE sent from security system ok. Staff already know to check the safety beams for obstructions and cleanliness. Recommend door control company check all safety beams. Tested ok.
MSA-DCS | WA3883002 | Unit 6, B Wing- Grille will not close- access control issue | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-31 11:16:00 | Pass | NOTE: This job started and completed on 24/12/2020. Requested by Maintenance to try and get operational before the holiday weekend. Contacted unit 6, confirmed status of Grill and that it was safe to operate remotely. Accessed and operated Close Relay and confirmed with unit grill closing. Requested unit control officer take control of Grill and confirm operation. Unit control confirmed ability to open and close grill.
MSA-DCS | WA3883003 | Unit 1, Cell B5- Cell door jamming in frame | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 06:54:14 | 2020-12-29 10:30:00 | Pass | Attended site to investigate work request, job carried out previously no work required
MSA-DCS | WA3883005 | Unit 1, C 13-14 & C 15-16- Fire Vesda showing faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 06:55:41 | 2020-12-30 06:55:00 | Pass | Attended site and found both Vesdas in unit 1 C 13/14 and C 15/16 now both normal.Checked with SO and they where happy to leave as is.
MSA-DCS | WA3883006 | Unit 1, A & B Day Room- Fans not working | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-08 12:00:00 | Fail | Replaced broken fans
MSA-DCS | WA3883038 | Unit 1, Internal air phones not operating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 07:27:35 | 2020-12-29 10:00:00 | Pass | No power at Master station in control room. Traced cabling, found power supply had been unplugged so the GPO could be used. Relocated to power board. Tested ok to B and D wings. Labelled power supply.
MSA-DCS | WA3883046 | Lenard, B Wing External light- Wall mounted light damaged | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-05-11 12:30:00 | Fail | Will quote to replace blown lamps. Replaced lamps as required , all lights operational.
MSA-DCS | WA3883047 | Lenard, A Wing - broken powerpoint in Kitchen | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 10:00:00 | Pass | Replaced faulty GPO and tested new one ok.
MSA-DCS | WA3883049 | kitchen near cool room- Emergency light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 13:30:00 | Pass | Replaced lamp and starter, test ran ok.
MSA-DCS | WA3883050 | Lenard A wing lounge - gas heater damaged near phone | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-12 14:00:00 | Fail | Replaced faulty gas valve
MSA-DCS | WA3883052 | Edvoc 1, Class 4- broken door panel Approx 650 x 500 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-15 13:30:00 | Fail | DOOR PANEL RE GLAZED
MSA-DCS | WA3883055 | Unit 3, Cell A16- Tap loose and leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 15:20:00 | Pass | Replaced corroded tap and adjusted pipework to suit
MSA-DCS | WA3883056 | Cleaning Workshop- Concrete floor damaged near roller door | Hakea Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo Building Services | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2021-04-07 15:30:00 | Fail | CONCRETE FLOOR REPAIRED
MSA-DCS | WA3883058 | kitchen, Loading doc fridge- Fan limit switch not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 07:49:57 | 2020-12-29 09:00:00 | Pass | Temporarily fixed door switch on fridge kitchen loading dock
MSA-DCS | WA3883060 | Unit 10, A & B Dayroom- GPO Smashed between Fridge and Water Fountain | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 07:51:39 | 2020-12-29 10:00:00 | Pass | Fixed power point not working day room
MSA-DCS | WA3883063 | Unit 7, Cell E21- Viewing hatch smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 07:54:28 | 2020-12-29 13:30:00 | Pass | reglazed obs panel and repaired viewing hatch
MSA-DCS | WA3883066 | Unit 7, Cell S9- Copper pipe under sink broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 14:00:00 | Pass | Replaced damaged washer and tightened loosen nut
MSA-DCS | WA3883069 | Unit 1, D Wing Dayroom Door- Door hard to lock & unlock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 07:59:12 | 2020-12-29 11:30:00 | Pass | Attend site to unit 1 day room door. Inspect due to unlock/lock. Replace bolts.
MSA-DCS | WA3883070 | Unit 5, C8 - Window unable to stay | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-08 11:00:00 | Fail | SPIRAL BALANCES RENEWED and re fit pull handle
MSA-DCS | WA3883081 | Hotham, Cell B6- Top cell lock (personal) playing up | Wandoo Rehabilitation Facility | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-13 15:47:00 | Fail | Attend site, inspect lock on cell B6. Replacement cylinder required. Reattend site to install.
MSA-DCS | WA3883083 | Unit 3, A/C - day room sink needs resealing - water is running under the sink into cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-31 13:00:00 | Pass | OLD DAMAGED SILICONE REMOVED & NEW APPLIED
MSA-DCS | WA3883084 | kitchen bread slicer not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-30 12:42:00 | Pass | NO FAULTS FOUND 29/12/20
MSA-DCS | WA3883086 | Unit 5, B12 - Window will not stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-08 09:30:00 | Fail | SPIRAL BALANCES RENEWED
MSA-DCS | WA3883087 | Unit 5, Cell A8- Tap is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-29 12:00:00 | Pass | nil
MSA-DCS | WA3883090 | Unit 3, A6 - Window not opening/shutting rods | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 09:30:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3883091 | Unit 13, Cell B4- Sink tap & shower tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 12:30:00 | Pass | nil
MSA-DCS | WA3883092 | Unit 3, A3 - Window faulty needs attention/rods | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 08:45:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3883093 | Unit 5, Tearoom- no water pressure, hot & cold taps minimal pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 14:00:00 | Pass | nil
MSA-DCS | WA3883095 | Unit 6, Cell C13- Water comes out the floor drain beneath | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 11:00:00 | Pass | nil
MSA-DCS | WA3883096 | Unit 3, C4 - Window runners damaged/faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 11:30:00 | Pass | RE NEW SPIRAL BALANCES AND WINDOW STOPS
MSA-DCS | WA3883097 | Unit 3 - B Wing Dayroom- Left sink leaking from underneath | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-31 12:00:00 | Pass | nil
MSA-DCS | WA3883099 | Unit 5, Cell A4- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-29 13:00:00 | Pass | nil
MSA-DCS | WA3883101 | Unit 3, D12 - Window not opening closing /runners | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 13:15:00 | Pass | THIS JOB IS A DOUBLE UP OF #WA3878947
MSA-DCS | WA3883103 | Unit 5, Cell C7- Blocked drain on the floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-18 13:48:00 | Fail | Nill
MSA-DCS | WA3883105 | Unit 3, A07 - rods need fixing on window runners as faulty/damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 10:30:00 | Pass | RE NEW SPIRAL BALANCES AND RE FIX PULL HANDLE
MSA-DCS | WA3883115 | Unit 13, Cell D14- Shower & basin is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 15:00:00 | Pass | nil
MSA-DCS | WA3883118 | Unit 5, Cell C7- Cell alarm faulty, pod unavle to hear voice when pressed | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-29 12:00:00 | Pass | Tested cell call , confirmed low level audio cell to Gate Control. Cleaned out Microphone apperature and retested, advised by control officer audio level now acceptable.
MSA-DCS | WA3883120 | Unit 13, D wing - window glass shattered held in place by laminate coating | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-13 14:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3883122 | Zone 3 mircowave is not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 08:20:59 | 2020-12-29 12:00:00 | Pass | Checked for local activation. Reset both the receiver and transmitter. Cleaned microwave covers and removed some weeds. Tested ok back to the gatehouse.
MSA-DCS | WA3883123 | Zone 4 permi trax not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 08:23:23 | 2020-12-29 13:00:00 | Pass | Plot graph not registering any activity. Reset module in Obs post 1. Ran plot graph and walk tested. Tested ok to the gatehouse.
MSA-DCS | WA3883124 | Zone 8, permitrax not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 08:24:13 | 2020-12-29 14:30:00 | Pass | Ran plot graph on Senstar PC. Walk tested and calibrated. Tested ok to the gatehouse.
MSA-DCS | WA3883131 | Unit 3, Staff room has severley reduced water flow | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-31 11:00:00 | Pass | nil
MSA-DCS | WA3883132 | Unit 13, Cell C6- Basin tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-31 14:00:00 | Pass | nil
MSA-DCS | WA3883136 | Visits entry prisoner changing area broken light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-04 10:30:00 | Pass | Repaired faulty lights in visits change room
MSA-DCS | WA3883139 | Unit 13, C Wing- emergency exit door lock plate cover missing 3 security screws | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 12:45:00 | Pass | Job was exit sign falling off (Not a lock)Sign had been refitted by another contractor.
MSA-DCS | WA3883140 | Unit 5, C2 - shower leaking water into B2 cell below and under lino in C2 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 08:40:43 | 2020-12-29 15:00:00 | Pass | Pressure tested shower concelad set and drain. No issues. GroutMissing on the floor in the shower
MSA-DCS | WA3883142 | Unit 14, Oven not keeping temperature | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-02-09 10:10:00 | Fail | Returned and fit new timer and mode switch. Timing and cool down functions working ok now.
MSA-DCS | WA3883144 | INF(10)- Treatment room airconditioning unit not working properly | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 08:45:58 | 2020-12-30 09:55:00 | Fail | Checked over aircond found unit running,checked pressures and operation, all running ok at present.
MSA-DCS | WA3883145 | Unit 4, D16 - 1/4 turn shower taps leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 11:30:00 | Pass | Arrived on site and inspected found the shower leaking. Needed 1/4 turn anti ligature spindle. Collected parts from supplier. Returned to site and removed the faulty spindles and replaced with new spindles for hot and cold. Reconnected water and tested all working in order.
MSA-DCS | WA3883152 | Admin Area- Air Con is not working correctly | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 09:03:47 | 2020-12-30 08:45:00 | Pass | Arrived on site and signed in, checked over aircond found unit tripped out on hp,belts ok,reset and tested all running ok at present.
MSA-DCS | WA3883157 | Unit 6, B Wing, service duct between cells 11 and 12 has water leaking down over the walls | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 09:05:31 | 2020-12-29 10:00:00 | Pass | nil
MSA-DCS | WA3883159 | Perimeter lighting in the medium prions - timer failed to turn on the lights | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-22 16:30:00 | Fail | Checked Gallagher and perimeter lighting isn’t apart of that system. Check CCTV playback and can see lighting is in fact activating.
MSA-DCS | WA3883164 | Zone C3 temp sally port - in constant alarrn | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 09:10:18 | 2021-02-03 10:00:00 | Fail | Multiple faults in multiple locations found in this Intelliflex zone. Problems included use of non coaxial cable to link parts of Intelliflex Cable and not peeling back foil of screen from centre conductor insulator.
MSA-DCS | WA3883171 | Unit 2 A wing, A10 - cell call system not working | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 09:11:33 | 2020-12-30 12:30:00 | Fail | Confirmed one-way audio from Control to cell. Drilled out cell call retaining rivits, Tested with new replacement cell call, same problem. Tested cell call at CI-8a controller card, good communications both ways. Tested cabling, found Fault with Mic wire. Removed end of bed-end to access cable junction. Removed excess cable and reterminated cable end. Tested cell call to local control, good audio both ways.
MSA-DCS | WA3883172 | Unit 2 B wing, B24 - cell call system faint from both ends | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 09:13:54 | 2021-04-29 14:00:00 | Fail | Disconnected existing CI-8 controller and removed from equip cabinet. Installed new CI8a controller and wired into network. Connected Cell Call cabling to RJ46 adapted leads and plugged into CI-8a. Reset Node and restarted all nodes on network. Tested cell call in call B24, good audio both ways. Tested cell associated with new controller and random cells on unit two. System operating correctly
MSA-DCS | WA3883187 | PDA display screen in constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 09:32:28 | 2020-12-29 15:30:00 | Pass | Fault caused by TR1.4.6 dropping offline. Badly corroded wiring at TR1.4.5 causing voltage drop. Cut away corroded wiring. MDAS receiver online. Voltage lower than ideal but it is keeping the receiver powered.
MSA-DCS | WA3883195 | Hotham, Cell A5- Toilet flush button keeps falling off | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 09:06:00 | Pass | Replaced flushing button to toilet in cell A5.
MSA-DCS | WA3883196 | Jeelia, Cell A1- External light switch faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-05 10:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3883215 | Unit 16, C wing - No Power to cell lights C01, C02, C04 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 10:06:56 | 2020-12-30 10:00:00 | Pass | Repaired faulty lights in unit 16 c wing
MSA-DCS | WA3883243 | Unit 4, Cell K 42 - shower taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 13:00:00 | Pass | Arrived on site and inspected found the spindle faulty. Collected parts from supplier. Removed the faulty spindle and replaced with new spindle for both hot and cold. Reconnected water and tested all working good.
MSA-DCS | WA3883260 | Front reception - damaged front door of office Centre (wooden door) | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 10:53:11 | 2021-01-05 11:00:00 | Fail | Carried out repairs to the vandalised front door leading to reception.Re-Attended site undercoated and painted repaired door.
MSA-DCS | WA3883266 | Main Kitchen - Power point between water tank and shelf not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-05 09:30:00 | Fail | Replaced broken gpo
MSA-DCS | WA3883292 | Unit 5, B & D Wing- Ceiling lights not working, 5 sets are not functioning | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-04 09:30:00 | Pass | Repaired faulty lights in unit 5 d wing landing
MSA-DCS | WA3883294 | reset building - kitchen sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-30 11:00:00 | Pass | nil
MSA-DCS | WA3883298 | kitchen, Loading doc fridge- Fan limit switch not working | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 11:42:51 | 2021-02-10 15:30:00 | Fail | Replaced door switch and guard. Tested operation. All ok
MSA-DCS | WA3883307 | Unit 3, Cell C10 - Toilet pan & sink broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-31 12:50:00 | Pass | Replaced broken basin and toilet. Adjusted pipe work to suit
MSA-DCS | WA3883310 | Unit 3, Cell C10 - Shelving damaged & mirror smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-03-18 15:45:00 | Fail | MIRROR AND SHELVING REPLACED
MSA-DCS | WA3883315 | Unit 1, Cell A7- Toilet pan seals leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-04 08:48:00 | Pass | Replaced leaking seals at the toilet
MSA-DCS | WA3883318 | Kitchen, Work Area- Evap Air-Con Water pump not Working | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 11:56:20 | 2020-12-29 16:15:00 | Pass | Cleared blockage and replaced solenoid. All ok
MSA-DCS | WA3883326 | Unit 2, Regi Area- Wall exhaust fan faulty louvers not opening | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-05 13:30:00 | Pass | Replaced broken fan
MSA-DCS | WA3883339 | Unit 1, A/B store room - Broken Light Switch | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 12:13:05 | 2020-12-29 13:30:00 | Pass | Fixed broken light switch unit 1 storeroom
MSA-DCS | WA3883346 | Unit 2, B11 - Service duct - Extraction Vent Ducting Flexible Tubing Broken | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-05 10:30:00 | Pass | Found ducting in B1 plumbing duct tripped. Replaced with new 200mm ducting. All ok
MSA-DCS | WA3883347 | Unit 2, C1 - sink hot tap leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 09:40:00 | Pass | Replaced leakinf spindle
MSA-DCS | WA3883350 | Unit 2, D7 - sink tap leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-04 10:13:00 | Pass | Replaced leaking spindles at the basin
MSA-DCS | WA3883380 | Fire system fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 13:22:56 | 2020-12-30 11:16:00 | Pass | cleared fault on Az 8 unit 6 due to vesda being isolated.
MSA-DCS | WA3883384 | Camera 143 in SHU control pointing at the east wing of the MPU is frozen. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 13:19:55 | 2020-12-29 16:00:00 | Pass | BRAF approved on WA3873239 - No further works required under this work order
MSA-DCS | WA3883408 | Main Kitchen - Small hotbox not heating up | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-30 16:00:00 | Pass | 30/12/20 - Arrived at site liaise with kitchen, identify hot, when I checked the hot box and everything was working correctly, removed panels, checked components and everything tested okay, had a conversation with the chef and he said that's nothing is wrong, another probably cause is user error messing around with the temperature controller.
MSA-DCS | WA3883420 | Gate house, kitchen sink flick mixer tap fault | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-31 10:15:00 | Pass | Inspected and found the kitchen sink tap leaking from sprout. Need new tap. Collected parts from supplier and returned to site. Removed the faulty tap and installed new tap. Reconnected water and tested all working good.
MSA-DCS | WA3883424 | Control room - WRPE 6 interface disconnected (possible tamper alarmer) | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Dec 2020 | 2020-12-29 18:25:08 | 2020-12-29 16:30:00 | Pass | WRPEC6-Interface Disconnected. HLI interface to solar winds dropped off at14:05 and then stored 14:05:20. Tested network to EC6 and getting reply’s of 1ms on all devices. Fault rectified by itself and restored.
MSA-DCS | WA3883428 | Unit 2, Cell C4- Flush button jammed & hard to flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-21 13:38:00 | Fail | Nill
MSA-DCS | WA3883429 | Unit 2, B Wing- Appears to be a leak coming from the roof | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-21 13:45:00 | Fail | No plumbing issue
MSA-DCS | WA3883430 | Unit 7 A Wing laundry tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-21 13:30:00 | Fail | Nill
MSA-DCS | WA3883431 | Unit 3, Cell J2 - No red light when activating cell call | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 16:30:00 | Pass | Attended cell call in 3J2, Tested cell call and noted that the Red LED activated on test. Tested multiple times with same result. Unable to reproduce Fault, no fault found.
MSA-DCS | WA3883432 | Unit 3, Cell J7 - Loud crackling in cell call speaker | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 18:15:00 | Pass | Tested cell call, low level audio from control to cell, advised by control very noisy, unreadable at Control. Tested with new cell call, now good audio. Difficulty in mounting due to Dyna bolt holding mounting plate in location. Cell call face plate standing 6mm proud of mounting plate due to bolt. Using Dremel tool cut overhanging threaded bolt, still not enough, sliced retaining nut in half to enable Cell call to fit. Riveted in place retested to Control.
MSA-DCS | WA3883446 | Gate control - gate control door jamming (door dropped alignment) | Karnet Prison Farm | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 15:39:13 | 2021-01-12 12:00:00 | Fail | ADJUSTED STRIKER PLATE TO PREVENT JAMMING
MSA-DCS | WA3883448 | Unit 2, control room - both camera monitors intermittently working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 16:56:19 | 2020-12-29 19:15:00 | Pass | Unit 2 CCTV Screens lagging. System resources running high CPU 93%. Shutdown PC and powered up. System now running 75% but recommend replacing unit.
MSA-DCS | WA3883449 | Unit 3-Major gas leak | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 29 Dec 2020 | 2020-12-29 21:44:50 | 2020-12-29 22:00:00 | Fail | Attended job and found that pipe had been cut with pipe slice on gas main to unit 3 ablution block, also had to purge gas to a few areas after repair
MSA-DFES | WA3883016 | Power circuit is out | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 29 Dec 2020 | 2020-12-29 17:00:00 | 2020-12-29 09:30:00 | Pass | CompleteAttended site and located power tripped out to main gate. Found rcd to have tripped, reset and tested all in working order. Notified staff and signed out
MSA-DFES | WA3883025 | Training Room- Split system is leaking water from inside control panel | VFRS Secret Harbour | GMP-BR | Air Conditioning | Ducted Split System (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 09:30:00 | Pass | Attended service call, found ac in training room has blocked drain, isolated power, cleared drain line with bore clearer, tested with water. Re instated power ok.
MSA-DFES | WA3883028 | foul stench coming from the COMCEN Kitchen Drain | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-30 12:21:00 | Pass | Kitchen smell job
MSA-DFES | WA3883033 | Shower head in Station officers bathroom constantly dripping | CFRS Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-30 08:47:00 | Pass | Repairing shower leaks.
MSA-DFES | WA3883035 | Cornice/ceiling has cracked and is falling away above duty room door in engine room | Kensington (old) | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2021-01-11 09:15:00 | Fail | Attended site at under batten ceiling to appliance bay
MSA-DFES | WA3883285 | Station Officers Dorm- Air Con is not cooling | CFRS Welshpool | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2021-02-09 15:30:00 | Fail | Replaced airconditioner
MSA-DFES | WA3883330 | Officers Bathroom - Tap handle in officers shower has broken | CFRS Daglish | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-30 15:01:00 | Pass | Repairing tap handles
MSA-DFES | WA3883348 | 2nd Floor, Section & corridor outside Commissioners Office- Light bulbs not working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 15:00:00 | Pass | Arrived onsite and signed in Located 6 x Square downlights that have gone faulty outside the commissioners office on floor 2. We will only be fixing 5 and leaving the one above the reception desk due to glare. I could not source replacement parts immediately because all nearby outlets are on Christmas break. Have ordered parts and will return to complete. Repaired 5 Square down-lights and tested for function .
MSA-DFES | WA3883364 | BA service room & cleaners store - 1x twin & 1x single lights not working | Success Career Fire Station (Temp Site) | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 29 Dec 2020 | 2021-01-06 17:00:00 | 2020-12-30 14:15:00 | Pass | Repaired light in Cleaners Store Room and BA room as per work order.
MSA-DFES | WA3883387 | Station Officer (front) bathroom- Exhaust fan in bathroom noisy – sounds like it will seize | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 29 Dec 2020 | 2021-01-04 17:00:00 | 2020-12-31 08:15:00 | Pass | Arrived onsite and signed in Located seized fan in dorm toilet. Will need to source replacementNotified station officer and will return to complete works. Arrived onsite and replaced fan. All is working correctly. Notified staff and left site.
MSA-DTAG | WA3883415 | Court Registry - A slat from the ceiling has fallen down | Armadale Courthouse | GMP-BR-HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 29 Dec 2020 | 2020-12-30 17:00:00 | 2021-01-12 15:30:00 | Fail | CEILING PANELS INSTALLED
MSA-DTAG | WA3887636 | RETROSPECTIVE WORK ORDER - isolate & de-isolate the FIP at Supreme Court for building works | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 29 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 17:15:00 | Fail | 29/12 KS 09:30Attended supreme courts in normal hours to carry out isolations for works.Will require returning later this afternoon to de isolate.29/12 KS 17:00Returned to site after hours to de isolate fire system.Left system normal.30/12 KS 06:45Attended supreme courts in normal hours to carry out isolations for works.Will require returning later this afternoon to de isolate.30/12 KS 17:30Returned to site after hours to de isolate fire system.Left system normal.31/12 KS 06:30Attended supreme courts in normal hours to carry out isolations for works.Will require returning later this afternoon to de isolate.31/12 KS 17:00Returned to site after hours to de isolate fire system.Left system normal.
MSA-DTWD | WA3883009 | BLD 875, Pen- Burst water pipe, isolated at the moment and safe - see notes below | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 3 | CLOSE | 29 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-15 11:30:00 | Fail | job completed - Repair burst water pipe to Piggery
MSA-DCA | WA3883610 | Admin Building, 1st floor west end AC fault | Collection and Research Centre Welshpool-Administration and Library Building-Level One-Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 16:30:00 | Pass | Attended site. Admin central west AC system not cooling correctly. Applied tests and checks, oil present on condenser coil. Investigation found refrigerant leak present with system locked out on LP safety. Pressure tested system to 2000kpa. Located refrigerant leak on condenser coil capillary line. Braised and repaired refrigerant leak. Repressure tested system to 2000kpa (system to have held pressure.). Evacuated system and charged with 11.2kg R438a (R22 substitute refrigerant). Applied tests and checks. System operating correctly.
MSA-DCS | WA3883532 | Unit 7, B Wing Kitchen - Tap in secondary sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-25 11:30:00 | Fail | nil
MSA-DCS | WA3883534 | Unit 4, A Wing Shower door latch not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 30 Dec 2020 | 2021-01-06 17:00:00 | 2021-03-16 11:45:00 | Fail | Temp repair. require parts.Cut out old lock, install new lock (lock modified to suit application) to cut out and replace handles to suit new lock position.
MSA-DCS | WA3883564 | Control Room- multiple internal zones fault, listed below | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 07:55:20 | 2021-01-04 14:30:00 | Fail | Repaired and tested the last of the zones on the list. All zones ok.
MSA-DCS | WA3883565 | Control Room- Multiple internal faults listed below | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 07:59:29 | 2021-01-04 16:30:00 | Fail | Repaired and tested the last of the zones on the list. All zones ok.
MSA-DCS | WA3883567 | Unit 6, Cell N6- Cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 07:53:30 | 2020-12-30 09:00:00 | Pass | Fixed broken cell light a6
MSA-DCS | WA3883569 | Front door, 2nd door in is catching at the bottom | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 08:08:15 | 2021-01-08 11:00:00 | Fail | no charges - closed off compfin
MSA-DCS | WA3883579 | Kitchen, pizza oven not heating | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 08:30:44 | 2021-02-08 13:00:00 | Fail | 30/12/2020Check oven Found top deck steam not working at allCheck all elements and simmerstats, heating ok.Isolate top solenoid as not working at all and predict was stuck open. Found middle deck steam knob not returning and requires replacing. Found middle deck LED Not working Found middle deck contactor buzzing but working ok. Parts required:1 x Solenoid 1 x Contactor 1 x green neon1 x Red neon1 x Steam switch assy8/2/2021Sign in Carry out COVID tests Isolate power and water Remove and replace faulty quoted parts Install solenoid opposite to prevent leakingHeat and test unit Ok All elements working All LED's working All steam decks working
MSA-DCS | WA3883583 | Laundry, Number 6 washing machine faulty door latch | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 08:39:54 | 2020-12-30 11:15:00 | Pass | AMS751298 - WA3883583 - No6 wm faulty door latchNo 6 Washing machine "Door fault:"Inspect and test machine, trace fault to a broken door cam and a worn door wheel.Supply and fit door cam and wheel.Assemble and test washing machine, washing machine tests ok.
MSA-DCS | WA3883609 | Admin - Air Con is not working correctly | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-18 09:23:00 | Fail | Complete
MSA-DCS | WA3883618 | Unit 5, A Wing- Shower is blocked, further details below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-22 08:33:00 | Fail | Nill
MSA-DCS | WA3883635 | Bakery - the tagliavini oven is continually sounding burner failure | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 10:09:33 | 2020-12-31 15:24:00 | Fail | no fault found NOTE - FIRST REPORTED 30/12/20 - NO FAULT FOUNDJOB RECALLED 31/12/20 - INVOICED ON SAME JOB AS SAME ISSUE.
MSA-DCS | WA3883655 | ISU C wing - tap snapped off | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 15:44:00 | Pass | Replaced damaged tap and adjusted pipework to suit
MSA-DCS | WA3883667 | Unit 1, Cell D3- TV aerial point has been smashed | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-04 08:30:00 | Pass | Attended site. Replaced TV Point in Unit 1, Cell D3. Tested OK.
MSA-DCS | WA3883673 | reception, senior officers door - frame is damaged, out of alignment | Wooroloo Prison Farm | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-07 11:00:00 | Fail | Attended site and carried out repairs to the aluminium frame surrounding glass in order to strengthen door frame.
MSA-DCS | WA3883676 | Main kitchen - Gas malfunction warning on main oven | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 30 Dec 2020 | 2020-12-30 15:01:40 | 2020-12-30 13:00:00 | Pass | Replaced Ignition box & retest, flame current steady now. Left unit operational.
MSA-DCS | WA3883681 | Unit 5, Cell D1- Ceiling light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-05 08:30:00 | Pass | Repaired Cell Light U5 D1
MSA-DCS | WA3883682 | Main kitchen - hot system is not starting up, (gas hot water) | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 11:11:05 | 2020-12-31 10:46:00 | Pass | Could not find signature book, was on site from 7am until 9am. Hot water units were working correctly when I got there. Must of been a air pocket in line from gas leak previous night
MSA-DCS | WA3883683 | Unit 6, Cell D12- Bottom bunk light is not working (globe has been changed) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-06 11:30:00 | Pass | Repaired fault light in Unit 6
MSA-DCS | WA3883705 | Front door electric strike working intermittently | Greenough Regional Prison | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 11:37:41 | 2021-01-01 21:30:00 | Fail | Attended site, confirmed door strike fault,(top jaw not releasing). Removed old electric strike from door frame and fitted new FES112 Custodial Strike. Found the face plate of the strike would not fit the existing rebate in door frame. Used grinder and Dremel to widen rebate (about 0.5mm) to fit face plate. Tested operating of strike using Request to Exit key switch. Strike functioning correctly.
MSA-DCS | WA3883708 | Laundry- Number 2 washing machine showing “AD” fault | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 11:45:32 | 2021-01-12 13:00:00 | Fail | AMS751380-WA3883708 - No2 washing machine showing "AD" fault05/01/21 - Inspect and test, trace fault to a broken door handle. Adjust and cramp loose door wire. Bush to be sourced and fitted on return visit.12/01/21 - Supply and fit new door handle
MSA-DCS | WA3883710 | Reset, out the front - drain is blocked and needs unblocking drainage issues | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 11:46:15 | 2020-12-31 08:38:00 | Pass | Inspexted stormwater system. No issues found. Water drained away.
MSA-DCS | WA3883717 | Perimeter - EC4 controller. low power alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2020-12-30 14:00:00 | Pass | Attended EC4 Cabinet, Tested output voltage from PSU (13.89vdc) Tested voltage at controller card plug 1 (12.69vdc) found voltage drop of over 1.0vdc at fuse carrier. Removed fuse, tightened carrier folder and restored fuse. Retested voltage at controller card (13.69vdc), Controller alarms cleared.
MSA-DCS | WA3883721 | principal's office in admin - air con not cooling | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 12:14:59 | 2021-01-18 08:16:00 | Fail | New unit commissioned & set to work
MSA-DCS | WA3883722 | unit 4, D14 - shower water pipe broken and leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-05 13:00:00 | Pass | Inspected the job and found the pipe broken. Need parts 4/1/21- collected parts from supplier and returned to site. Tried to remove the shower section from the demountable could remove it. Could not access the pipe work. Refitted the shower back. Need to discuss with the maintenance department before proceeding further. 5/1/21- returned to site and removed the gyprock panel behind the fibre glass shower. Gained access to the pipe work. Removed the faulty section and fabricated and installed new pipe section. Refitted the shower Rose and tested all working good.
MSA-DCS | WA3883724 | Unit 6, Cell C6- Sink tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-05 08:25:00 | Pass | Replaced ministop and adjusted water flow
MSA-DCS | WA3883725 | Kitchen, Work Area- Rational oven No 1 steamer tank is leaking | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 12:32:06 | 2021-01-07 10:30:00 | Fail | Replaced steam tank and tested ok
MSA-DCS | WA3883727 | Unit 1, Staff lunch Room- Hydro Tap Not Cooling & Filter needs changing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-07 09:35:00 | Pass | Filter service all working okay
MSA-DCS | WA3883752 | industries 1.3 officw door - key gets stuck in lock | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 11:20:00 | Pass | repaired lock cylinder on Industries door 1.3
MSA-DCS | WA3883754 | Squash courts - entry door will not unlock | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-04 10:00:00 | Pass | repaired lock on entry door to squash courts
MSA-DCS | WA3883766 | Gatehouse, Sallyport- Green entry light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-05 16:30:00 | Pass | Found that lights have not yet been connected into the main computer system and cables are in a junction box under the lift up floor in front on the DGP panel in the equipment room upstairs in the Gatehouse. Have informed the maintenance staff and they will chase up SEME and the door installers to see when is going on. Job is complete on our side of things.
MSA-DCS | WA3883767 | Bakery - Freezer Drain element not working & freezer will cut out shortly | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 14:27:05 | 2020-12-31 10:30:00 | Pass | Arrived on site, signed in tools and walked to bakery, found drip tray to be completely full of ice. No ice on coil. Turned off unit and began to melt ice with hot water hose, whilst removing ice found drain to be blocked, cleaned out drain turned frdezer back on and put through manuel defrost once reached temp, drain heater working, drip tray heaters working and defrost working, due to drain being blocked ice was building up in the drip tray, drain is unblocked and all ok.
MSA-DCS | WA3883769 | Visits room - Fire Panel Showing Fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 14:24:34 | 2020-12-31 11:19:00 | Pass | Attended site and found many of the prisons panel off line.After checking found all remote FIP’s and mimics off line so not reporting alarms over the network.Tried re booting via network but unable to. Went to every panel and mimic and found comms network started to work and cleared all faults onsystem.
MSA-DCS | WA3883771 | Unit 4, Cell A12- Toilet does not flush, low water pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-18 08:30:00 | Fail | Nill
MSA-DCS | WA3883772 | Unit 4, Cell A5- water in toilet constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2021-01-18 09:30:00 | Fail | Nill
MSA-DCS | WA3883773 | Unit 4, B Wing- Tiles in middle shower cubicle are cracked around the drain | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-08 12:00:00 | Fail | 06/09/21 - closing job cost to date as site not given us response on access - cost for labour only/inspection
MSA-DCS | WA3883774 | Unit 7, H wing - toilets are blocked in cells 1 threw to 12 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 30 Dec 2020 | 2020-12-30 18:45:25 | 2020-12-30 18:34:00 | Pass | Checked gully’s and IO’s outside the wing- no isseus found.Flushed toilets and basins in the wing several times- no draining issues found. Everything flushing and draining away properly.
MSA-DCS | WA3883777 | Grounds, Equipment store lock has broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 14:51:38 | 2020-12-31 09:30:00 | Pass | Cut open jammed lock and replace.
MSA-DCS | WA3883778 | unit 2, A13 - top right corncer of cell door is banging the frame when closing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-20 10:30:00 | Fail | Replace hinges.Replace door plate, lock and weld on strike.
MSA-DCS | WA3883800 | Person duress alarm display screen in constant alarm - tamper | Hakea Prison-Main Gatehouse | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Dec 2020 | 2020-12-31 00:06:14 | 2020-12-30 22:30:00 | Pass | Unit 7 reporting tamper alarm but cleared before arriving on site. Checked logs and found been alarming at 7:30pm. Checked receiver and tamper, no fault found its working correctly. Also ran stress test on unit and all is ok now.
MSA-DFES | WA3883749 | Between the CFRS & the VFRS front driveway the retic is blocked- see further details below | VFRS Mandurah | GMP-BR | Plumbing & Drainage | Drainage (PD) | Dom's Total Grounds Maintenance | 3 | CLOSE | 30 Dec 2020 | 2021-01-07 17:00:00 | 2021-03-05 13:00:00 | Fail | Rob Reynolds attend has repaired issues
MSA-DTAG | WA3883595 | 1903 Building, Basement, Control Room - Power issues following shutdown | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 30 Dec 2020 | 2021-01-05 17:00:00 | 2020-12-31 09:00:00 | Pass | Tech works electricians not ready to cut power over. Electricians on site advised possibly swapping back to newswitchboard on Saturday. Will need new out of hours work order if and when they proceed and Mario to confirm with ChrisK for approval. Electricians on site have my phone number for when it is needing to go ahead.
MSA-DTAG | WA3883624 | fault in zone 9 fire panel | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 30 Dec 2020 | 2020-12-30 13:43:00 | 2020-12-30 12:00:00 | Pass | Faulty detectors in zone - would recommend replacing
MSA-DTAG | WA3883729 | faulty air-conditioning - Extremely hot and muggy in both the court building and CJS building | Rockingham Justice Complex | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 09:40:00 | Pass | Attended site and signed in. Accessed bms and inspected aircon systems. Found all operating correctly. Found ahu1 serving admin area supplying 13 degree air. Monitored operation and found room temps lowering. Suspect consecutive high ambient days is causing the system to struggle to cool. Adjusted the start times to help the system condition the space.
MSA-DTAG | WA3883758 | ground - testing of duress alarm system was no audible alarms sounding. | Rockingham Justice Complex | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Dec 2020 | 2020-12-30 18:01:26 | 2021-01-06 09:00:00 | Fail | Installation of PC speakers and Configuration tested ok.
MSA-DTAG | WA3883775 | Ground - Male public toilets is leaking quite substancially . | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Dec 2020 | 2020-12-31 17:00:00 | 2020-12-31 12:30:00 | Pass | Replaced inlet valve and outlet washer
MSA-DCA | WA3883914 | high temperatures on AC9 | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 31 Dec 2020 | 2021-01-04 17:00:00 | 2021-01-11 09:04:00 | Fail | AHU 9 requires investigation alongside controls technician to adjust, tune the control strategy.Unit is over shooting SP's. Adjusted control in manual mode to bring parameters back within spec.
MSA-DCA | WA3883986 | External door is not secure | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Door Entrance Area | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 31 Dec 2020 | 2020-12-31 14:42:30 | 2021-01-04 11:30:00 | Fail | Attend site to fix stage door escape panic bar not latching leaving building unsecured. The locking mechanism was readjusted to ensure the latch was operational.
MSA-DCA | WA3884006 | Lights flickering constantly | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Female Toilets | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-02-12 09:00:00 | Fail | Investigated flickering lights in female toilets, bank of 9 lights have a slight flicker on load due to using led tubes on fitting designed for standard tubes.Ordered CAP 31 Load correction device, returned once in stock to install. Supplied and installed specialized driver for lighting rectification. Quote supplied for specialized installation
MSA-DCS | WA3883844 | Mimic or Master computer in the master control room is down | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Dec 2020 | 2020-12-31 10:09:09 | 2020-12-31 08:45:00 | Pass | Attended site checked and found Gallagher workstation 1 monitor showing blank in control. Checked monitor and KVM extender are ok. Located problem to be the workstation in equipment room upstairs. Reboot workstation and bring all service back.
MSA-DCS | WA3883872 | Reception area - light out | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-07 17:00:00 | 2021-01-04 14:00:00 | Pass | Repaired lighting in reception area.
MSA-DCS | WA3883874 | Level 1, Duty room 1 - door not closing properly | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 07:09:24 | 2021-01-05 13:00:00 | Fail | attended site and repaired door handle and stricker that was not operating correctly.
MSA-DCS | WA3883883 | Gate house, Equipment room - indoor aircon unit leaking water | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 07:30:52 | 2020-12-31 12:00:00 | Pass | Job complete
MSA-DCS | WA3883889 | Health, pharmacy - lock on pharmacy hatch faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 07:40:18 | 2020-12-31 10:45:00 | Pass | Attend site to remove sliding window lock, return to workshop to customise lock/cylinder as requested by client. Return back to site to fit and supply 4 keys.
MSA-DCS | WA3883895 | Unit 7, H wing - Cold Water tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 07:52:48 | 2020-12-31 14:25:00 | Pass | Replaced broken handle on tbe rhs basin
MSA-DCS | WA3883900 | Unit 3, D5 - Sink waste grate broken, | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-14 14:30:00 | Fail | Replaced new sink waste
MSA-DCS | WA3883932 | Unit 3, D wing - oven not heating | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-05 11:00:00 | Pass | Unit 3, D Wing oven not heating. Check oven & controls. Disconnect power. Dismantle & remove top. Locate faulty timer. Alter wiring to suit. Assemble & test.
MSA-DCS | WA3883945 | Unit 3, Cell C3 - Light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-08 08:30:00 | Pass | Investigate and replace unit 3 cell c3 light
MSA-DCS | WA3883947 | Unit 2, Cell 29 - Light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-08 10:00:00 | Pass | Investigate and replace unit 2 cell 29 light
MSA-DCS | WA3883948 | Unit 2, Cell 57- Light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-08 12:30:00 | Pass | Investigate and repair unit 2 cell 57
MSA-DCS | WA3883949 | Unit 2, Cell 50- Light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-08 11:30:00 | Pass | Investigate and replace unit 2 cell 50 light
MSA-DCS | WA3883951 | Unit 2, outside lower landing light fittings not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-08 14:00:00 | Pass | Investigate and repair lower landing light fittings in unit 2
MSA-DCS | WA3883953 | abattoir sterilizer sink foot operated tap leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-02-15 13:00:00 | Fail | Inspected found the foot operated tap leaking. Tried to service the tap but could nit service it. Need new parts. Collected parts from supplier and returned to the site. Installed the new foot tap. Reconnected water and tested multiple times all working in order.
MSA-DCS | WA3883956 | unit 2 outside lower landing showers waste pipe broken under building | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-04 13:00:00 | Pass | Collected pars and arrived on site. Found the 50 mm tarp broken. Removed the broken trap and installed new trap. Tested all working good
MSA-DCS | WA3883958 | laundry boilers keep going out | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-04-06 13:15:00 | Fail | Inspected the gas HWU in the Landry. Found no 2&3 HWU working fine. Found unit no 1 not lighting tired to restart the unit still the unit not lighting. Found unit no 4 working intermittently. Unit no 1&4 need complete service.Unit no 1 isolated
MSA-DCS | WA3883959 | Unit 1, control room dunit 1 control door electronic lock not working oo | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-05 12:00:00 | Pass | Door closer not working locksmith to be called
MSA-DCS | WA3883961 | Kitchen - air-con, leaking dripping water | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-05 10:15:00 | Pass | Arrived on site and signed in, checked over aircond found condensate pump had failed,picked up new one returned and fitted,turned back on and tested all running ok at present.
MSA-DCS | WA3883968 | House 3, Unit 5- Electronic lock is not locking | Bandyup Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 10:07:22 | 2020-12-31 14:15:00 | Pass | Attended site checked and found Unit 5 House 3 front entry door handle lock tongue is jamming from the frame. Electric door strike is working ok. Help customer file the lock tongue to prevent it from jamming from the frame. Informed customer that if problem happens again call door technician to fix it. Not SEME job.
MSA-DCS | WA3883971 | Farm - system 1 fault on York tower | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 10:11:30 | 2020-12-31 15:00:00 | Pass | Check chiller and found loose cable on controller, cut and re-terminate .test and left system operational
MSA-DCS | WA3884000 | Karakin, A wing, Cell A07 - Broken bed side light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-04 12:00:00 | Pass | Replaced light switch and lamp, test ran ok.
MSA-DCS | WA3884019 | Self Care Unit - Camera 131 not functioning correctly | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 12:26:02 | 2020-12-31 14:15:00 | Pass | On arrival confirmed image from camera distorted and discoloured. Attended unit Equipment cupboard, checked, on hand held monitor, image from camera, same as at gate control. Power reset camera, correct image now showing. Returned to Gate Control and confirmed good video image.
MSA-DCS | WA3884022 | Unit 3, C Wing yard- Wash down hose reel broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2020-12-31 15:00:00 | Pass | Tightened loosen house clamp on ree hose
MSA-DCS | WA3884024 | Unit 2, Cell D9- Sink grate broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-14 13:40:00 | Fail | Installed new basin waste
MSA-DCS | WA3884027 | unit 4, Control Lobby- Water cooler not working | Hakea Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-07 08:41:00 | Pass | Power to gpo okay water okay fountain not chilling needs ARCUS or a refrigeration specialist to attend quoted to replace as unit very old and believe compressor failing may not be worth spending money on repairs
MSA-DCS | WA3884041 | Perimeter Zones F1 & F2 in constant alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 13:05:18 | 2021-02-03 11:00:00 | Fail | Swapped zones F2 and F3 back to their correct positions on the IF board. Checked calibration and tested ok.
MSA-DCS | WA3884046 | SITE COST Unit 1, Cell C1 - toilet blocked | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 31 Dec 2020 | 2020-12-31 17:57:09 | 2020-12-31 18:30:00 | Fail | Unblocked sewer line in c1. Checked sewer line outside the wing. Water draining properly.
MSA-DCS | WA3884047 | Turner, C wing, Cell A06- Shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-02-10 11:55:00 | Fail | Replaced faulty parts
MSA-DCS | WA3884048 | External Gatehouse- Fire supression system leaking near Warton road | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-04 13:55:00 | Pass | FOUND LEAK AND FIXED IT. BROKEN PARTS
MSA-DCS | WA3884053 | External sally port camera not operating correctly | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Dec 2020 | 2021-01-06 17:00:00 | 2021-01-05 14:00:00 | Pass | Staff Identified Cam 25 no fault found tested working ok.
MSA-DCS | WA3884068 | Visits Centre - Air Con not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 15:55:38 | 2021-01-04 13:00:00 | Fail | Repaired AC. Running good.
MSA-DCS | WA3884078 | Kitchen next to Unit 1 - Dishwasher is not working. | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 17:08:02 | 2021-01-01 14:15:00 | Pass | 01/01/21Customer complaining dishwasher continuously running Remove cover and found relay stuck on due to cockroaches in relay.Remove cover and cockroaches Spray machine Reassemble and test, ok Bottom rinse arm requires stopper in end.
MSA-DCS | WA3884081 | Cell calls from Unit 1 to the gatehouse is not working. | Greenough Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Dec 2020 | 2021-01-01 17:39:26 | 2021-01-02 00:00:00 | Fail | Attended Unit 1, checked LED indicators on network switch, no activity showing on cell call equipment port. Tested cable and found no continuity on wire 1 on RJ 45 lead. Cut of plug on CI-3210 end and crimped now plug on, retested lead, continuity showing on all wires. Reconnected cell call console to network, confirmed calls now diverting to Gate Control, cleared alarm.
MSA-DTAG | WA3883909 | Ground level, R111 - Technician attend Monday 4 Jan 21 at 07.00am – reset the BMS after shut down | Supreme Court | GMP-BR-HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-07 09:56:00 | Pass | Confirmed aircons operating after power shut down.Found ac3 serving court 3 cutting out on hp. Found system stopped cutting out after a while.Monitored and found unit operating after a few days of operation.
MSA-DTAG | WA3884049 | Hot water (Reem) system is leaking under the sink in the Jury Room | Rockingham Justice Complex | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Dec 2020 | 2021-01-08 17:00:00 | 2021-01-11 12:26:00 | Fail | Arrived on site and inspected found the 25 Ltd HWU leaking. They don’t want to replace the unit. They unit to be capped off. Need to fix an appointment for access with site contact Collected parts from supplier and returned to site. Removed the faulty hwu and pipe work. Fabricated pipe to suit the kitchen mixer tsp. Removed the safe tray and capped the waste pipe. Cleaned the kitchen cabinet.
MSA-DCS | WA3886821 | Access gate to perimeter fence at prerelease unit is not shutting properly, not secured | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Jan 2021 | 2021-01-01 18:30:54 | 2021-01-01 15:45:00 | Pass | Cardax sending OPEN, CLOSE and STOP signals ok. Issue with the pedestrian gate not always fully closing and not locking without a manual push from an officer. Tested ok. Sprayed lock with CRC later in the day and still testing ok. Door closer may need adjusting by auto door contractor.
MSA-DCS | WA3886823 | Unit 5 C6 toilet in cell is leaking | Hakea Prison-Unit 5 | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Jan 2021 | 2021-01-02 10:24:29 | 2021-01-01 13:32:00 | Pass | No escort available at the time of arrival.Repaired leaking toilet cistern in Unit 5 B6.Wrong location on work order.
MSA-DCS | WA3886848 | Turner office - cell call not working | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Jan 2021 | 2021-01-01 18:05:36 | 2021-01-04 15:45:00 | Fail | replace faulty cell call handset in turner. tested ok after replacement. job complete.
MSA-DCS | WA3886858 | Access gate to perimeter fence at prerelease unit is not shutting properly, not secured | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | AFD Contracting | 1 | CLOSE | 01 Jan 2021 | 2021-01-02 15:17:57 | 2021-01-02 12:10:00 | Pass | 02/01/21Recalibrate 'close' limit
MSA-DCS | WA3886860 | Wandoo Rehabilitation Facility - Hotham Unit - Air con is not operating. | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 01 Jan 2021 | 2021-01-02 16:06:53 | 2021-01-02 11:00:00 | Pass | Brian Service Report 02/01/2021: Travel to site, investigate hothan AC unit, unit running properly, reduce the water and adjust waterflow to the pad to stop water overflowing on the pad. pack up. left site
MSA-DCS | WA3886869 | unit 4 - 5 cells without power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 01 Jan 2021 | 2021-01-01 20:43:09 | 2021-01-01 20:45:00 | Fail | Replaced shorted power point with a new one, test ran ok.
MSA-DCA | WA3886919 | Grafiti removal at the back of state library | Perth Cultural Centre Precinct | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 15:51:33 | 2021-01-04 09:45:00 | Fail | Removed graffiti
MSA-DCS | WA3886880 | Perimeter fence and Microwave has been damaged and in alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Jan 2021 | 2021-01-03 00:13:11 | 2021-05-12 07:00:00 | Fail | Rectified and fixed perimeter sensors multiple faults due to vandalism , job completed.
MSA-DCS | WA3886888 | Unit 2 plant room white water pipe(100 mm) is leaking through ceiling. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Jan 2021 | 2021-01-03 06:57:07 | 2021-01-04 14:18:00 | Fail | Attended site and found that there was a 25mm hot return pie that had a pin hole leaking onto the pvc
MSA-DCS | WA3886890 | Fire system fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 11:31:48 | 2021-01-02 09:41:00 | Pass | After hours call to Hakea Prison for panel fault in zone control 2.Found panel clear when arrived checked history found to be alarm in unit 7 F wing all normal nowReset alarm in pod left system normal.
MSA-DCS | WA3886891 | kitchen - cooler room not operating | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 11:54:31 | 2021-01-02 12:30:00 | Fail | Replaced the capacitors.
MSA-DCS | WA3886897 | Banksia Hill Detention Centre- Broken window in ISU in A wing | Banksia Hill Detention Centre | GMP-BR- HO | Carpentry | Materials (CA) | Midolo Building Services | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 12:42:38 | 2021-01-05 14:30:00 | Fail | FRAME REPAIRED - WINDOW RE GLAZED & SEC FILM ADDED
MSA-DCS | WA3886898 | Turner Unit cell call system not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 12:45:51 | 2021-01-02 14:00:00 | Fail | turner unit cell call is working, staff did not pass on message to use PTT on node
MSA-DCS | WA3886909 | ISU unit observation cell camera is not feeding | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 13:35:06 | 2021-01-02 11:45:00 | Pass | ISU screens not working. Layouts not displaying cameras. Reset up layouts and cameras. Tested and operational. Showed staff how to setup screens if its fails.
MSA-DCS | WA3886927 | Fence zone 5 fence alarm, keeps activating | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Jan 2021 | 2021-01-02 17:33:02 | 2021-01-02 16:45:00 | Pass | Zone 5 fence alarming regularly. End of line resistance tested ok. Replaced some missing cable ties. Calibrated and tested ok.
MSA-DCS | WA3886933 | unit 1 cell 23A - cell call system audio working in cell but unable to hear anything in control room | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 15:06:00 | Pass | Phone called site and site reported no issues from unit 1 or 2 on any cell calls
MSA-DCS | WA3886934 | Crisis care unit cell CC3 toilet is constantly running | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 14:42:00 | Pass | Replaced inlet valve and outlet washer
MSA-DCS | WA3886940 | Hakea Prison - Cell C02 - Unit 4 - Cell call system not working. | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-04 09:00:00 | Pass | Poor audio in cell and in control. Removed, stripped and cleaned intercom. Assembled, secured and tested. Lou’s and clear in cell and in control.
MSA-DTAG | WA3913442 | Retrospective work order for works to carry out door repair | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 02 Jan 2021 | 2021-01-04 17:00:00 | 2021-01-02 11:00:00 | Pass | Inspected door and found door had been knocked off track refitted door and tested all ok at time of test.
MSA-DCS | WA3886964 | Internal zone 1 microsonics is light blue and internal zone 1 permitrax not activating. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jan 2021 | 2021-01-04 08:01:14 | 2021-01-03 10:45:00 | Pass | Zone 1 microphonics - reset power to controller in IF1. Tested ok locally with programmer. Tested ok to gatehouse. Zone 1 internal Perimitrax - walk tested with plot graph running. Zone not sensitive enough to activate. Lowered threshold on Senstar PC. Tested again. Alarms and resets ok at gatehouse.
MSA-DCS | WA3886971 | UNIT 5-HOUSE 7- Electronic lock on door keeps popping open when top lock is undone | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Jan 2021 | 2021-01-03 12:13:28 | 2021-01-06 16:30:00 | Fail | Lock replaced tested ok
MSA-DCS | WA3886974 | Unit 12-CCU-Camera 52 courtyard -No Video | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jan 2021 | 2021-01-04 08:28:19 | 2021-01-04 11:00:00 | Fail | Confirmed no video from camera visible in CCU control, at CCU CCTV rack, or roof interconnection cabinet. 24vac power supply to camera good at fuse. Power reset camera, video restored.
MSA-DCS | WA3886976 | Perimeter Security light-pole got broken and the light damaged -Light -36 | Casuarina Prison-Gatehouse | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Jan 2021 | 2021-01-04 08:32:17 | 2021-01-04 13:30:00 | Fail | Isolated and secured fallen pole light. Picked up boom lift and repaired light.
MSA-DCS | WA3886977 | SHU -Unit 9-West -Cell A6-Observation light is damaged | Casuarina Prison-Gatehouse | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Jan 2021 | 2021-01-04 08:34:57 | 2021-01-05 09:30:00 | Fail | Attended SHU - unable to gain access - Booked in , Returned and repaired light
MSA-DCS | WA3886979 | SHU -Unit 9-east-Cell B7-Main lock is sticking ,required a Locksmith | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 03 Jan 2021 | 2021-01-04 08:36:51 | 2021-01-03 10:30:00 | Pass | Service main lock and replace fixings
MSA-DCS | WA3886982 | Unit 5-control room door, main door by SO's office is not closing | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 0 | CLOSE | 03 Jan 2021 | 2021-01-03 12:58:18 | 2021-01-03 13:30:00 | Fail | carried out repairs to door that was not closing.
MSA-DCS | WA3887006 | Access gate to perimeter fence at prerelease unit is not shutting properly, not secured | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | AFD Contracting | 0 | CLOSE | 03 Jan 2021 | 2021-01-03 18:51:48 | 2021-01-13 14:30:00 | Fail | 03/01/21Lock mechanism. Require further work.05/01/21Returned to site after 03/01/21 visit.Replaced gate lock.Re-programmed gate.Require further programming.Gate is working13/01/21Re-configure PE Beams
MSA-DCS | WA3887031 | UNIT 5-A WING- Hot water pipe has burst. Unable to isolate mains. | Hakea Prison-Unit 5 | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 03 Jan 2021 | 2021-01-03 17:21:03 | 2021-01-25 09:50:00 | Fail | Replaced hot water unit
MSA-DCS | WA3887044 | Karnet Prison Farm - no water available onsite. | Karnet Prison Farm | SPA-GR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Jan 2021 | 2021-01-03 18:52:50 | 2021-01-18 15:00:00 | Fail | COMPLETED
MSA-DCS | WA3887386 | health centre - aircon heat pump fan blown | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 03 Jan 2021 | 2021-01-04 16:34:40 | 2021-01-05 12:00:00 | Fail | Call-out after hours. 03-01-2021 1630 - 1800Received call-out. Attended site. Signed in and was escorted to Medical Building. Carried out inspection of AC 1. OFM fan blade and support bracket loose and broken. Unable to repair. Took all details required to quote repairs. Isolated, disconnected, bagged OFM grill. Turned AC 1 on and is operating for now. Due to current hit weather, unit may not function correctly and efficiently until repairs completed. BRAF to be submitted and needs to be approved before works can go ahead.Works on going.BRAF submitted and approved. Arranged parts and equipment for works. Gas bed access to site. Replaced faulty fan blade and left new spare inside AC 1, Medical Building. Closed job.
MSA-DCS | WA4040417 | Abattoir floor damaged ** job completed** | Karnet Prison Farm | GMP-BR- HO | Flooring | Concrete (FL) | Midolo Building Services | 3 | CLOSE | 03 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-03 15:00:00 | Pass | Resurfaced floors
MSA-DCA | WA3887274 | Multiple reticulation leaks within the PPC please investigate all | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Materials (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-04 17:00:00 | 2021-01-05 11:30:00 | Fail | Fixed a stuck solenoid, 2 broken sprinklers and 4 leaks in the Urban Orchard
MSA-DCA | WA3887297 | Lift faulty stuck ground floor | Subiaco Arts Centre-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 04 Jan 2021 | 2021-01-04 12:06:28 | 2021-01-04 11:17:00 | Pass | Lift out of order, customer explained that the fan in car was making a very loud vibrstion noise and turned of fan, found lift in inspection mode due top top of car trap door switch open circuit due to the car fan vibrating, cleaned fan and repostioned, tested operation all ok left in service
MSA-DCA | WA3887322 | Fire detector in fault "L1S84" | Art Gallery of WA - James St-Administration Block (Block A)-Level One | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-04 13:10:00 | Pass | Attended site to look at loop 1 sensor 84 as requested. Found isolated and in maintenance fault.Removed detector and fitted new reset and left normal.
MSA-DCA | WA3887335 | Glass door have been smashed (make safe) | Sunset Hospital Heritage Precinct-Building G-Two Storey Ward Block-Ground Floor-Main Entry | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-04 16:00:00 | Pass | Installed 12mm ply to two doors and two windows that have been smashed. Windows and doors have been made safe.
MSA-DCA | WA3887340 | Boiler 2 in fault | Maritime Museum Victoria Quay-Main Building | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 09:30:00 | Pass | Attended site. Boiler 2 to still be faulting since last Boilertronics. Raised PO for Boilertronics to attend. Investigation found flame rod/flame scanner defective. Site technician to have replaced defective parts. Carried out tests and checks. Boiler operating correctly. Please refer to attached Boilertronics service report for in depth analysis.
MSA-DCA | WA3887349 | Light post opposite Polly Cafe has a broken light cover | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-04 19:00:00 | Pass | Inspected and dismantled lolypop light to find the lamp holder bracket inside fitting has completely rusted through and snapped caused the iron core ballast to drop and then also breaking the diffuser holder. All parts are broken and will need to return with new brackets.I have removed all internal parts of light and screwed down the diffuser for the meantime.Lights are at end of life.
MSA-DCA | WA3887524 | RETROSPECTIVE WORK ORDER-multiple faults on fire panel- ALREADY ATTENDED | Subiaco Arts Centre-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 04 Jan 2021 | 2021-01-04 17:00:00 | 2021-01-04 11:05:00 | Pass | Attended Site - Investigated battery fault - Replaced faulty batteries - 2x 12AH.Did soft reset to panel (FIP) - fault cleared and normal.
MSA-DCA | WA3887755 | foyer box office smoke detector in fault | Perth Concert Hall-External Area-Ground Floor | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 14:30:00 | Pass | Attended site and found panel normal but withL5 D1 Z14 status normal but in alarm test fail status. Carried out alarm test of device found to test ok.Panel now clear left panel normal.
MSA-DCA | WA3887780 | Toilet is running constantly | Perth Concert Hall-Main Building-Ground Floor-Toilet - Queens Personal Private - Back of Board Room | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-06 13:30:00 | Pass | Replaced gaulty inlet valve
MSA-DCA | WA3887781 | Cistern is faulty | State Library of WA-Main Building-Ground Floor-Female Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-06 07:50:00 | Pass | Replaced leaking bellow at the 1st cubicle. Out of order signs attached on the last two cubicles as well. No issues found.
MSA-DCA | WA3887784 | Urinal has a faulty flush button | State Library of WA-Main Building-Level 1-Male Toilets - Near Lift Foyer - East | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-06 08:53:00 | Pass | Replaced broken flush button
MSA-DCA | WA3887842 | main foyer Lifts 1&2 - firermans key switch is faulty | State Library of WA-Main Building-Ground Floor-State Records Entry Foyer | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 14:00:00 | Pass | Lift 1 fan was unplugged from toc board, reconnected tested and lift rts. Lift 2 fan running. - To be closed out at $0
MSA-DCA | WA3887843 | main foyer Lifts 1&2 - both lifts faulty extraction fans | State Library of WA-Main Building-Ground Floor-State Records Entry Foyer | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMP | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-05 10:55:00 | Pass | Fire recall on ground floor works but key very difficult to remove. Recommend replacing barrel Key 9000, obr createdTo be closed out at $0
MSA-DCS | WA3887195 | fault on main panel control unable to open unit control doors 1,2,3,4 | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Jan 2021 | 2021-01-04 11:07:34 | 2021-01-04 15:30:00 | Fail | On notification of fault, attended unit 3 equipment room. Found UPS "OFF". Restarted ups and monitored equipment to ensure connected equipment came back on-line. Confirmed restart of PoE switch, Decoders and camera. Confirmed with Gate Control that alarms had cleared. Returned to unit in afternoon. Load tested UPS. Output at 25% with displayed run time of 55 min.
MSA-DCS | WA3887215 | drug detection unit - drive way mirror pole damaged (snaped) as exiting kennels | Hakea Prison | GMP-BR- HO | Building | General Building (BU) | Midolo Building Services | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 07:24:13 | 2021-01-04 14:00:00 | Pass | NEW MIRROR & POLE INSTALLED
MSA-DCS | WA3887240 | Unit 10, B1 - vinyl flooring lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 04 Jan 2021 | 2021-01-06 17:00:00 | 2022-03-14 09:30:00 | Fail | vinyl floor repairs
MSA-DCS | WA3887253 | Unit 7, S7 - toilet leaking onto floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 09:10:00 | Pass | Replaced leaking outlet washer
MSA-DCS | WA3887256 | Old front gate, Outside Staff Gymnasium - NO hot water to females showers | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 07:52:08 | 2021-01-05 07:50:00 | Pass | Temperature in the female and male bathroom checked. No issues found. No issues wirh hwu either
MSA-DCS | WA3887258 | Unit 8, Senior officers office - aircon leaking from the roof | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 07:54:28 | 2021-01-04 14:45:00 | Pass | Foind main 40mm drain which cassette condensate pump pumped into had started to sag causing overflow. Resected drain, cleared and test flow. All ok.
MSA-DCS | WA3887261 | Unit 4, C2 - cell call cannot be heard in cell | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 07:56:55 | 2021-01-04 08:00:00 | Pass | Poor audio in cell and in control. Removed, stripped and cleaned intercom. Assembled, secured and tested. Lou’s and clear in cell and in control.
MSA-DCS | WA3887266 | MCR Camera Faults - see notes regrading camera and locations | West Kimberley Regional Prison | GMP-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Jan 2021 | 2021-01-04 15:58:58 | 2021-01-18 08:12:00 | Fail | Temporary repairs made under this works order - final repairs made under lightning strike job
MSA-DCS | WA3887271 | Unit 2 , Cell A16- Prisoner lock faulty from inside | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:03:57 | 2021-01-04 15:30:00 | Pass | Replaced damaged Prisoners Privacy lock in Unit 2 cell A16
MSA-DCS | WA3887279 | Main Laundry- Dryer 1 is not working | Bandyup Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:09:22 | 2021-01-12 10:00:00 | Fail | Tested to find damaged wire on over temp switch. Remade and test ok
MSA-DCS | WA3887283 | Unit 1, Female staff toilets - door lock faulty, not locking | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:10:07 | 2021-01-04 10:40:00 | Pass | Adjusted door frame lock strike on female toilets Unit 1
MSA-DCS | WA3887284 | PDA constant alarming | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-03-03 12:00:00 | Fail | Faulty PDA was replaced on 12/01 with site spare. 03/03/2021 replacement PDA delivered to site.
MSA-DCS | WA3887289 | Unit 7, D Wing- Fridge not holding temperature | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 10:45:00 | Pass | Checked over fridge found down to temp and all running ok at present.
MSA-DCS | WA3887293 | Unit 3, Control Room- Switch panel to control the lighting does not work | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-15 12:30:00 | Fail | 15/01/2021 12:30. Tested cables and found one pair (BL/W) open circuit. Unable to identify location of cable damage. Reconfigured wiring to use cable screen as return for light control switches. Tested switches, all operating correctly.
MSA-DCS | WA3887295 | Unit 14, A/C control room entry door buzzer not working. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 15:00:00 | Pass | Removed electric strike from door frame, cut out failed buzzer and installed new replacement buzzer. Reduced electric strike and confirmed operation of strike and buzzer. Working correctly.
MSA-DCS | WA3887302 | SOG Pod- A Number of cameras not available on the indigo system | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 12:00:00 | Pass | Checked with POD, no information in POD, no knowledge of fault. Checked with Security SO who advised that they had reported fault. Cameras were all on-line. Cameras were all in Units 1-4. All cameras were now responding. This fault was related job no WA3887195.
MSA-DCS | WA3887306 | Unit 6, Cell C4- Toilet has faulty flush button | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 11:30:00 | Pass | Nill
MSA-DCS | WA3887308 | Unit 13, Cell B4- smell coming from toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 14:30:00 | Pass | no issue found
MSA-DCS | WA3887311 | Unit 2, Cell C14- Hot water basin tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 14:40:00 | Pass | Re-seated and replaced hot spindle
MSA-DCS | WA3887313 | Unit 2, C & D Day Room- Kitchen tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 14:38:00 | Pass | Re-seated and replaced hot spindle
MSA-DCS | WA3887323 | Microphonics fence, Zone 23 - Microphonics fence cables faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:32:10 | 2021-01-04 12:00:00 | Pass | Replaced nearly every cable tie on the bottom cable run. Checked zone calibration. Tested ok locally and back to control.
MSA-DCS | WA3887328 | Medical- Air Con not working (fault E9) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-07 16:00:00 | Pass | Complete. Replaced condenser fan capacitor
MSA-DCS | WA3887330 | Unit 5, office - aircon leaking water, possible drain blocked | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 11:45:00 | Pass | Found drain blocked cleaned drain and drip tray, flushed, all flowing ok at present.
MSA-DCS | WA3887331 | Admissions, Movement Coordinator office- Air con not working ( fault Po5) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-07 11:30:00 | Pass | Complete. Replaced main switchboard power fuses.
MSA-DCS | WA3887333 | Dairy - wash down pump has seized | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:39:51 | 2021-01-05 11:00:00 | Fail | Attended site and inspected. Pump seized, collected pump from yard and delivered to site.We collected pumps and parts required from yard and arrived on site. On arrival we were informed that this job is closed. They will do the job internally.
MSA-DCS | WA3887336 | Unit 5, control room - aircon unit not cooling properly | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 12:45:00 | Pass | Checked over aircond found system running, checked pressures all ok, checked full operation all running ok at present.
MSA-DCS | WA3887345 | Lenard, Cell B01- Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-04 11:00:00 | Pass | Replaced broken light switch witha new one,test ran ok.
MSA-DCS | WA3887346 | Unit 14, A/C wing - element in Regi oven is failing- takes along time to heat up when preparing food | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-18 11:25:00 | Fail | Returned and fit new element & gasket. Test all elements & operation ok.
MSA-DCS | WA3887350 | SITE COST Unit 4, Cell J2- Key keeps stucking in the lock | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 04 Jan 2021 | 2021-01-04 12:51:31 | 2021-01-04 14:30:00 | Fail | Replaced damaged Prisoners Privacy Lock on Cell J2 Unit 4
MSA-DCS | WA3887354 | Unit 6, A wing -vinyl in the door way of A wing kitchen (self care) is lifted | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-04-09 11:30:00 | Fail | rubber flooring repairs
MSA-DCS | WA3887358 | Unit 16, B Wing, Cell B3 shower is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-21 11:30:00 | Fail | Nill
MSA-DCS | WA3887359 | Unit 3, Control room - fire alarms keeps going off at least once a day/faulty | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:56:16 | 2021-01-05 08:56:00 | Pass | Pressure switch to be replaced as per - WA3890263
MSA-DCS | WA3887362 | Unit 13, C Wing showers are having drainage issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 14:30:00 | Pass | Nill
MSA-DCS | WA3887363 | main building ground Repair flickering light in Director's office in Pilbara Wing. | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 08:56:45 | 2021-01-04 11:45:00 | Pass | Repaired lighting in office of Pilbara wing.
MSA-DCS | WA3887365 | Unit 2, B Wing. Cell B11 - toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 12:30:00 | Pass | Nill
MSA-DCS | WA3887368 | Unit 13, A Wing, Cell A5- Shower and sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 15:30:00 | Pass | Nill
MSA-DCS | WA3887375 | Unit 14, Day room - fridges on A/C & B/D are note keeping food cold | Casuarina Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 10:00:00 | Pass | Checked over fridges in both wings,found one fridge in a/c wing faulty,site going to organise new one.
MSA-DCS | WA3887376 | Gate House- light flickering above visitors entrance | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 13:00:00 | Pass | Replaced faulty lights in gatehouse using 12 ft ladder
MSA-DCS | WA3887379 | Unit 15, A & C, Cell C1- bed light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 10:30:00 | Pass | Investigated faulty lights in unit 15. Found water amongst lights. Advised maintenance
MSA-DCS | WA3887384 | Unit 5, PA System is not functioing | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-04 13:30:00 | Pass | Attended Unit 5. Noted on arrival that the unit PA system was being used. Checked with control staff who advised PA had not worked over weekend, but was working today. Confirmed dial-tone on phone tested multiple PA calls. System Working correctly, unable to reproduce fault.
MSA-DCS | WA3887390 | Unit 4, D Wing, Cleaning room has no water pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-13 12:30:00 | Fail | Nill
MSA-DCS | WA3887396 | health centre Grill door lock is sticking when key is inserted | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-06 09:45:00 | Pass | Attend site, service and lubricate deadbolt and adjust striker.
MSA-DCS | WA3887397 | Unit 14, A & C Day Room- Water fountain is leaking & overflowing on floor | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 09:17:19 | 2021-01-04 15:27:00 | Pass | Replaced bubbler cartridge
MSA-DCS | WA3887400 | Perimeter tower A2 Faulty lighting cuts on and off | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 08:30:00 | Pass | Repaired perimeter light
MSA-DCS | WA3887423 | Zone 7 cowling - keeps alarming | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 10:00:00 | Pass | Zone 7 found ok on arrival, ask by officer to resolve fault zone 10 constant alarm on cowling. Investigated tested reinitialised retested ok.
MSA-DCS | WA3887426 | Pit tamper zone 16 P36 sensor | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-22 16:45:00 | Fail | Replacement of Reed switch and rewiring due to corrosion.
MSA-DCS | WA3887452 | Unit 2, A3 - sinks taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 10:44:00 | Pass | Replaced faulty spindles
MSA-DCS | WA3887453 | unit 2 office door not closing properly and jumping open | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 10:02:02 | 2021-01-04 12:00:00 | Pass | Adjusted door frame lock strike - Unit 2 Office
MSA-DCS | WA3887459 | Control room - Zone 5 in constant alarm | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 10:06:24 | 2021-01-04 13:15:00 | Pass | Attended site checked and found Zone 5 Fence in constant alarm. Checked in EC cabinet found sensor cable too sensitive. Recalibrate sensor cable and tested it ok after work.
MSA-DCS | WA3887467 | Unit 2, A2 - Toilet Pan Seals Leaking Sewage into Service Duct | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 10:18:53 | 2021-01-04 13:12:00 | Pass | Replaced tpilet seals and flush pipe
MSA-DCS | WA3887469 | unit 2 A-B day room Water Cooler Drain Blocked & Over flowing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 10:20:32 | 2021-01-04 18:16:00 | Pass | Unblocked badly blocked sewer line that is connected to the drinking fountain
MSA-DCS | WA3887498 | All Areas - no water to prison | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 04 Jan 2021 | 2021-01-04 14:49:39 | 2021-01-04 12:30:00 | Pass | Nill
MSA-DCS | WA3887553 | unit 14 wing B/D Cells 5/6 vesda fault.-please see notes | Casuarina Prison | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-21 07:14:00 | Fail | At VESReprogram VES relaysSector 1 relay 4 for F1Sector 2 relay 5 for F1Sector 3 relay 6 for F1Sector 4 relay 7 for F1Re-wire the VES Relay 2 “Urgent fault” in parallel with “Minor fault” relay 3 and ensure the cable terminates at the DGP XP10 module in input L2M44.At DGP XP10 module next to VESReconfigure the wiring for the inputsL2M41-SPAREL2M42-VES ISOLATE (Rly 1)L2M43-WING A CELL 7 VES F1 (Rly 4)L2M44-VES FAULT (Rly 2 & 3)L2M45-WING C CELL 7 VES F1 (Rly 5)L2M46-WING C CELL 8 VES F1 (Rly 6)L2M47-SPAREL2M48-WING A CELL 8 VES F1 (Rly 7)L2M49-SPAREL2M50-SPARETest operation of the VES from each cell
MSA-DCS | WA3887559 | Reticulation operation inspection inside and outside prison wall | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 11:19:34 | 2021-01-06 10:00:00 | Fail | AWAITING PUMP REPLACEMENT
MSA-DCS | WA3887564 | Jeelia C wing Cell C1 Inside cell light switch not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 11:30:00 | Pass | Replaced light switch
MSA-DCS | WA3887577 | Whole tenancy - pest control required as spiders & cockroaches coming out & running over staff | Midland (North East Metro) | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-08 18:00:00 | Fail | Spiders & cockroaches treatment to all premises.
MSA-DCS | WA3887580 | Unit 13, A & C. Cell C07- Toilet is broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 12:54:00 | Pass | Nill
MSA-DCS | WA3887582 | Unit 13, A & C. Cell A01- toilet is continuously flowing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 09:30:00 | Pass | Nill
MSA-DCS | WA3887585 | Unit 1, Cell A9- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-05 09:30:00 | Pass | Nill
MSA-DCS | WA3887594 | Garments- Lock to front entrance door only works with some keys | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 09:00:00 | Pass | Service lock and replace bolt throw
MSA-DCS | WA3887596 | Unit 1, Cell A16- GPO has Broken Mech wont switch off | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 15:30:00 | Pass | Signature slip
MSA-DCS | WA3887598 | Reception, Front Desk - 4 Mech Light switch has 1 Mech Broken | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 13:30:00 | Pass | Repaired broken light switch
MSA-DCS | WA3887604 | unit 3 pool room window frame is damaged | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-03-16 16:00:00 | Fail | DAMAGED TIMBER BEADS REPLACED - WINDOW REGLAZED
MSA-DCS | WA3887610 | Education, Demountable Office- water running outside of the demountable & flooding around the side | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-20 11:30:00 | Fail | 18/1 : started digging on side of demantable to locate the water main (opposite side to where it was flooded) to get it ready to re join when we cut in, couldn’t find it and we dug all the way along, need to return with locator 19/1: found a 32mm line at end of de mantle , unsure as to what it feeds, maintenance recuested we just install the ball valve and leave it to stop the leak, isolated water to install ball valve, further investigation found it was a T branch under the demantable , we found a 40mm branch line that feeds health admin20/1 run poly line in 50mm from new valve where we cut in to pick up the 40mm line that feed health admin, 32mm branch has now been deleted as it is a dead leg and doesn’t feed water to anywhere.
MSA-DCS | WA3887616 | Unit 1, Cell C1- Viewing glass smashed in door | Hakea Prison | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-06 10:00:00 | Pass | VIEWING WINDOW RE GLAZED
MSA-DCS | WA3887647 | SB1 (Between U15-U16) - Lobby Area-SB1- health consultant room no 1 lock is broken/damaged | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 09:45:00 | Pass | Service and lubricate lock.
MSA-DCS | WA3887686 | Gate House, Lobby Area- Air Con not working front gate pod area | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-20 12:30:00 | Fail | Arrived on site and signed in,system held pressure,vac out system and recharged,tested operation all running ok at present.
MSA-DCS | WA3887691 | Unit 2, A & B Wing- B Wing shower on south side no water pressure | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 14:36:00 | Pass | Cleared debris out of shower head and flow restrictors
MSA-DCS | WA3887697 | Unit 4, Cell D2- Fire sprinkler broken & flooding the entire cell & both wings | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 04 Jan 2021 | 2021-01-04 17:27:32 | 2021-01-04 17:25:00 | Pass | damaged sprinkler head - drained system and refilled using spares onsite - refilled system and checked pressures all good.
MSA-DCS | WA3887789 | Amenities - broken water pipe /water leaking on to road | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-05 12:30:00 | Pass | Nill
MSA-DCS | WA3887796 | Unit 7, Cell S1- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 15:00:00 | Pass | broken light
MSA-DCS | WA3887798 | CCU - Electronic Front Door not automatically re-securing | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 14:43:40 | 2021-01-05 08:00:00 | Pass | Electric strikes working ok on all 3 CCU doors. The door on the Prisoner Reception side of the building appears to affected by the strong wind. There is too much movement of the door when it is closed. The magnet and reed switch move too far apart causing the system to think the door is open and preventing the other doors from opening because of the interlock. The door between CCU and Medical has dropped on its hinges making it harder to close. Spoke toHakea Industries Manager who will organise on site maintenance to look at the doors.
MSA-DCS | WA3887799 | Unit 8, C/D Wing Control room door - Electronic Front Door not automatically re-securing | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 14:45:03 | 2021-01-05 09:00:00 | Pass | All doors tested ok electronically. It is possible to get through the door quickly, pull it shut part of the way and then let the door close on its own and the door will bounce open because the strike remains powered for a few seconds to let staff through. Have spoken to the Hakea Industries Manager about the fault. If it continues to be an issue maintenance may adjust the door closer but it would be better practice for everyone to pull the doors fully closed.
MSA-DCS | WA3887807 | Unit 8, Cell A4- Service duct drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 10:00:00 | Pass | Unblocked sewer line
MSA-DCS | WA3887810 | education building Outer door faulty door lock, unable to lock door | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 12:10:00 | Pass | Attend site replace faulty security door lock and adjust strike to outer door education block for correct operation.Date on site: 05/01/2021Time on site: 11:10am - 12:10pm
MSA-DCS | WA3887812 | Unit 8, B9 - Service duct flooring rusting away | Hakea Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo Building Services | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-20 13:00:00 | Fail | RE NEW CONCRETE FLOORING
MSA-DCS | WA3887825 | Medical Centre- Self closer to the door not working | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 15:18:58 | 2021-01-04 18:30:00 | Pass | Attended site, investigate issue and readjusted door lock as required
MSA-DCS | WA3887827 | Unit 1, Cell C6- Vinyl Flooring Lifting in Cell | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-03-19 14:45:00 | Fail | DAMAGED VINYL UPLIFTED - NEW VINYL LAID
MSA-DCS | WA3887835 | Gate Control- USB extender box no power to MDAS screen 1 mouse | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 10:30:00 | Pass | On investigation no power at KVM extender Rx (no led on mouse or Keyboard). Tested from workstation PC in equipment room, same issue. Restarted Workstation PC. Mouse and keyboard now functing correctly.
MSA-DCS | WA3887857 | Perimetre fence - Response road gate not responding to computer commands. | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-06 09:30:00 | Pass | Attended response gate with ERU staff, tested operation of gate, found to be operating correctly. Unable to reproduce fault.
MSA-DFES | WA3887290 | 1st floor, corporate server room - Card management system is offline | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-04 10:30:00 | Pass | 4/1/21 - Dylan ParslowInvestigated issues with Pacom software.Found SQL shutdown.Restarted SQL and tested operations, all ok.
MSA-DFES | WA3887477 | admin training exteria-whole air con unit has come off the wall on the outside | VFRS - Armadale | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-12 17:30:00 | Fail | Re locate split ac onto ground as brackets have pulled out from wall
MSA-DTAG | WA3887499 | 1903 ground Mazza JA’s staff chambers Airconditioners not working | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-04 15:22:00 | Pass | Inspected aircons in staff chambers and found no power to sub board. Electrician re connected power. Tested operation of aircons. Found all ok
MSA-DTAG | WA3887508 | Mens toilet- Registry and Public - Flush button not working and water not draining | Mandurah Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-02-01 15:00:00 | Fail | Complete
MSA-DTAG | WA3887518 | Various ceiling lights need replacing including Court rooms | Mandurah Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 08:30:00 | Pass | Replaced faulty and blown lamps and fluoro throughout courts and custody
MSA-DTAG | WA3887655 | Ground male public toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-07 12:30:00 | Pass | Complete
MSA-DTWD | WA3887185 | A block, Admin area - 2 auto doors timers are not unlocking and unable to set to auto | Munster Campus (ACEPT) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 04 Jan 2021 | 2021-01-04 17:00:00 | 2021-01-04 13:50:00 | Pass | 04/01/2021, 1330-1350Deleted incorrect holiday schedule, doors working
MSA-DTWD | WA3887186 | B block, alarm panel - showing faulty alarm (lights flickering) unable to disarm alarm | Munster Campus (ACEPT) | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 04 Jan 2021 | 2021-01-04 17:00:00 | 2021-01-04 14:30:00 | Pass | 04/01/2021, 1350-1430Replaced dgp1 battery and powersupplySystem now ok.
MSA-DTWD | WA3887265 | Fire Panel shows "COM PORT TIMEOUT" fault | Perth Campus B2 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-06 15:20:00 | Pass | Attended site 6 January for reported issue with Fire System, found system lockup/unable to operate controls.Unable to reset system, carried out power down/system restored to normal. Monitor as discussed with facilities management.
MSA-DTWD | WA3887418 | A block, plant room - chiller 2 in fault | Leederville Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-05-28 15:41:00 | Fail | Supply & installation of 34kgs of R134a Refrigerant, as a variation to existing works on Trane RTWD - chiller 2 circuit 2,
MSA-DTWD | WA3887432 | A19 - Air con system cooperating, but very noisy thorough out A Block please rectify | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 09:00:00 | Pass | A19: Found the evap on Space ducted split system noisey in the ceiling space. Used a ladder to access the unit , found the belt cracked and was making a noise that became amplified down the duct work. Replaced the belt using spare belt on site , test ran all ok.
MSA-DTWD | WA3887541 | L1 outside of building Remove graffities around the building | Perth Campus B1 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 12:45:00 | Pass | REMOVAL OF GRAFFITI FROM OUTSIDE OF L1 BUILDING
MSA-DTWD | WA3887550 | Level 1, outside the building - graffities around the building | Perth Campus B1 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 13:45:00 | Pass | REMOVAL OF GRAFFITI FROM OUTSIDE OF BUILDING
MSA-DTWD | WA3887595 | A block L1 AF2.06.1 Wooden window frames rotting and deteriorating | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-02-22 15:00:00 | Fail | Works completed as per scope on approved BRAF quote
MSA-DTWD | WA3887668 | A block chiller room not air con to building | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 14:05:00 | Pass | Arrived on site and signed in found water chiller off due to water flow from cooling tower being too hot. this was because tower pumps had been off for three days. reset and monitored AHU had locked out reset left all areas coming down to 22 degrees.
MSA-DTWD | WA3887676 | Block 9, 1st Floor- end boiler/plant room - Door wont unlock | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 04 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-05 10:00:00 | Pass | Block 9 - 1st Floor Boiler/plant room door wont lock.Lock repaired.
MSA-DTWD | WA3887687 | Block 8, G Floor, Toilet duct in male disabled- Main water isolation valve stuck on | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 13:20:00 | Pass | Install new valve and replace basin set
MSA-DTWD | WA3887711 | Block 8, G Floor- Disabled toilet in ladies leaking water on to floor. | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 13:22:00 | Pass | Replace leaking no pan cone
MSA-DTWD | WA3887717 | Block 1, Customer Service lunch room - Boiling Billy leaking water from inside. | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 12:55:00 | Pass | Reported that unit was leaking on return from Christmas break. Unit turned back on and leak first eased then stopped. Nothing found internally or during operation. Possibly thermal contraction and expansion cause units o rings to shrink causing leak. Once turned back on and up toTemperature to seal once again Unit is over 10 years old if ongoing issue recommend replacing
MSA-DTWD | WA3887802 | Block 10, First Floor, Room 10F89- Hole in plasterboard wall | Thornlie Campus | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 16:00:00 | Pass | Patch and repaint wall
MSA-DTWD | WA3887844 | Lift 5 not operational | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMP | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-05 11:26:00 | Pass | Car L and P RCD tripped. Located to car fluorescent. Ordered 2 tubes and starters. Also lift in fault 169 battery low, disable landing calls obr for battery.To be closed out at $0
MSA-MRWA | WA3887731 | Lvl 2, Near room 237 & 228- LED Light requires refurbishment please attend and remediate. | Don Aitken Centre MRWA Head Office-Main Building-Second Floor | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 04 Jan 2021 | 2021-01-11 17:00:00 | 2021-02-12 07:30:00 | Fail | Attended site and signed in. Located faulty light fittings. Removed from ceiling. Supply and replaced led drivers internal to light fittings. Refitted to ceiling and tested all okay. Signed out. Job complete
MSA-MRWA | WA3887763 | Schneider UPS battery failure please attend and remediate – Possibly under warranty | Road Network Operation Centre (RNOC)-Main Building-Second Floor-Real Time Traffic Operations | GMP-BR | Security | Monitoring (SE) | Secure Power Solutions Pty Ltd | 1 | CLOSE | 04 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 09:30:00 | Pass | Reset alarm and Rectified high temp by reversing fans at front of cabinet as instructed by Brendon Mitchell.
MSA-DCA | WA3888008 | Main Foyer - lift 1 unresponsive, stuck on ground floor | Subiaco Arts Centre-Main Building | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 05 Jan 2021 | 2021-01-05 17:00:00 | 2021-01-05 08:54:00 | Pass | Lift running on arrival, no events logged. Fan bearing noisy and causing vibration, removed fan for repair and kept lift in service. Informed building manager of situation, raised follow up for re install
MSA-DCA | WA3888383 | 2x light poles are not working | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-07 13:05:00 | Pass | Replaced 2 x 125w MV high output lamps, repaired existing lamp holder in lollipop light with spare from under ramp.
MSA-DCS | WA3887886 | Perimeter fence at unit 4 - gate jammed in open position. | Bunbury Regional Prison-Administration | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 13:15:38 | 2021-01-05 09:00:00 | Pass | Found broken "com" wire on safety beam circuit at Gate Control PCB. Terminated multiple "com" wires in terminal and fed single wire to PCB. Tested operation of gate from control PCB and from SMS workstation in PRU Control room. Gates operated correctly.
MSA-DCS | WA3887917 | On the perimeter fence- C4 camera is reading no signal. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 09:57:34 | 2021-03-15 11:30:00 | Fail | This job completed on work order WA3882123. See this job for details.
MSA-DCS | WA3887979 | Main Gate Pod, Fire Panel - various faults (see notes) | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 11:13:50 | 2021-01-05 10:52:00 | Pass | Attended site and found node 7 Education modules missing.Checked Node 7 found normal re booted nose and got back on line left system normal.
MSA-DCS | WA3888016 | Unit 7, F7 - Viewing Hatch damaged and rubber seal missing | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 07:49:20 | 2021-01-06 09:00:00 | Fail | VIEWING WINDOW RE GLAZED AND SEAL REPLACED
MSA-DCS | WA3888024 | Unit 8, A/B wing clothes dryer - constantly shutting off during cycle | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 2 | CLOSE | 05 Jan 2021 | 2021-01-07 17:00:00 | 2021-06-25 09:30:00 | Fail | 25/06 - BJ attended site - Return to site supply and fit new door switch cover, test machine - tests ok.
MSA-DCS | WA3888030 | Unit 7, Regi oven - not heating up | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 05 Jan 2021 | 2021-01-07 17:00:00 | 2021-04-06 13:30:00 | Fail | Date - 7/1/21Make - Convotherm Model - AR 40Serial - AES02014051Technician - BMArrived at site liaise with kitchen staff, walk to location, identify oven, isolate remove panels, test/fault find diagnose and found the heating element contactor has lost a phase and requires replacement, 1x 3-5KW 240v 3 pole contactor06/04/21 WS. Called as requested to fit parts required fitted tested all working correctly now.
MSA-DCS | WA3888057 | Unit 6, Day Room- Pipe under regi oven is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-15 13:30:00 | Fail | Nill
MSA-DCS | WA3888066 | Unit 13, Cell C11- Toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-08 08:30:00 | Pass | Nill
MSA-DCS | WA3888069 | CCU (11), Cell C6- Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-12 08:30:00 | Fail | Nill
MSA-DCS | WA3888071 | SOG Base - HSE corridor 2x fluros out (2 globes per light) | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-05 12:00:00 | Pass | Repaired light
MSA-DCS | WA3888072 | Unit 13, Cell A5- Shower drain has blocked again | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-18 09:28:00 | Fail | nil
MSA-DCS | WA3888083 | INF (10), OBS cell 2 - Light casing has a large crack in it. The light is still working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 15:00:00 | Pass | Replaced damaged lights in infirmary b2. Site stock used, waited access for cell
MSA-DCS | WA3888084 | Outside Office - Fluro light not working | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 10:45:00 | Pass | Replaced failed lamps and starter of office light. Replaced damaged light fitting with led batten.
MSA-DCS | WA3888096 | Unit 6, Court yard is lifting (trip hazard) | Casuarina Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | Midolo Building Services | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-13 10:00:00 | Fail | 13/01 - INSPECTED ONLY - DOUBLE UP OF WA3627672
MSA-DCS | WA3888098 | Unit 4, D Wing, Door sign for sprinkler switch off valve missing | Casuarina Prison | GMP-BR- HO | Signage | General Signage (SI) | Automatic Fire Protection (ARA) | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-15 11:30:00 | Fail | Replaced signage on sprinkler room on D wing landing.
MSA-DCS | WA3888126 | Main laundry- Dryer door hinges is broken | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 09:00:08 | 2021-01-28 13:00:00 | Fail | Electrolux Dryer #1 Bottom loading door hinge required
MSA-DCS | WA3888144 | Unit 1, Urn auto boiler is faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 11:05:00 | Pass | Replaced faulty element, calibrated. Replaced dripping tap!Tested diagnosed Rheem A40184067J unit empty on arrival not heating or filling replaced Assy Tap Kit and Element tested checked working
MSA-DCS | WA3888146 | Waste Water Plant- Fan Faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-02-24 13:30:00 | Fail | Investigate waste water plant fan. Requires parts to repair.
MSA-DCS | WA3888163 | Offical Visits, non contact first room visitors side- Light is flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 08:30:00 | Pass | Repaired lights in official visits
MSA-DCS | WA3888166 | Textiles, workshop - 2x sewing machines lights not working | Casuarina Prison | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-05 13:30:00 | Pass | Repaired 2 x security machine lights in textiles
MSA-DCS | WA3888168 | Textiles, workshop - power board faulty, shock received. board power turned off | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-07 08:30:00 | Pass | Investigated and tested power board in textiles. All ok
MSA-DCS | WA3888174 | Gate House -Eastern Sally Port Door is faulty and the pin isn't coming down | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 09:33:16 | 2021-01-05 18:20:00 | Pass | 05/01/21Picked up scissor lift hire. Checked ram for pins.Checked limits on motor - all ok.Slight adjustment
MSA-DCS | WA3888178 | Unit 1, Plumbing duct between cell 14 & 15- blocked sewer shaft | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 13:41:07 | 2021-01-05 14:31:00 | Fail | Blocked rising shady between the cells due to excessive toilet paper. Plunged drain and cleaned work area once completed
MSA-DCS | WA3888181 | Outdoor Area - Faulty tap timer for sprinkler reticulation | Walcott Centre (Central West Metro ) | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-08 10:00:00 | Pass | changed out faulty tap timer
MSA-DCS | WA3888222 | Jasper, Cell A07- Shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-02-10 09:20:00 | Fail | Replaced faulty parts
MSA-DCS | WA3888306 | Unit 5, A Wing, Cell A3- tube light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-05 13:30:00 | Pass | Repaired light in A3 Un5
MSA-DCS | WA3888317 | Unit 1, Cell C8- Blocked toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-15 11:32:00 | Fail | nil
MSA-DCS | WA3888318 | Inner sallyport grill form vehicles is not working | Greenough Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 18:52:08 | 2021-01-06 08:45:00 | Fail | 05/01/21 - 06/01/21Inspect gate - not operating.Fault found with safety edge, re-calibrated.Clean track.
MSA-DCS | WA3888344 | unit 2 staff kitchen Hydro Tap not cooling and filter needs changing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-07 10:12:00 | Pass | Filter service all working okay
MSA-DCS | WA3888350 | Kitchen, work area - Fridge 4 unit icing up | Hakea Prison | SPA-BR | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 11:13:14 | 2021-02-10 12:00:00 | Fail | Completed leak check and repair. Unit operational.
MSA-DCS | WA3888393 | Admin, All Toilets Blocked and floor Drains overflowing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 11:46:07 | 2021-01-05 17:25:00 | Pass | Unblocked sewer line behind admin area
MSA-DCS | WA3888404 | Unit 1 C10 cell door split | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 11:46:15 | 2021-05-05 12:00:00 | Fail | ENTIRE CELL DOOR REPLACED
MSA-DCS | WA3888417 | unit 6 low water presure through the units toilet bowls and taps | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 12:03:53 | 2021-01-06 11:30:00 | Pass | In my opinion we are getting a lot of sand in the water mains after a cut in by the new build in december, same issues in unit 3 4 5 and 7 in recent weeks. Not just small amounts of sand, we have been clearing maybe half a cup full out of each cell water supply lines.
MSA-DCS | WA3888443 | kitchen dishwasher not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 12:28:02 | 2021-01-06 16:00:00 | Fail | 06/01/21Called as requested to the dishwasher not working correctly not filling. Found the water turned off and the hood switch out of position made good tested all ok.
MSA-DCS | WA3888456 | main laundry No5 washing machine uni mac keeps stopping | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 12:37:49 | 2021-01-28 10:30:00 | Fail | Found cold water valve faulty and requires changing
MSA-DCS | WA3888458 | laundry No3 dryer stopping and starting and showing up with error | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 12:40:06 | 2021-01-28 11:30:00 | Fail | Tested machine, suspect gas valve not passing gas all of the time. Recommend new gas valve be fitted
MSA-DCS | WA3888461 | Front gate, Cashiers office - unable to lock safe | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 12:40:40 | 2021-01-05 15:35:00 | Pass | Replace 9v battery in safe.
MSA-DCS | WA3888462 | visits Non-Contact Room 1 Prisoner side Lock Hard to Operate (Locking & Unlocking) | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 15:00:00 | Pass | Attend site to service custodial lock to secure door.
MSA-DCS | WA3888464 | unit 1 C14 Sink grate broken - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-14 11:35:00 | Fail | Installed new sink grate, previous grate was corroded, also adjusted pipework for new grate
MSA-DCS | WA3888488 | unit 1 C8 Main lock keys catches | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 11:45:00 | Pass | Attend site to repair damage/fault on main cell lock door in unit 1.
MSA-DCS | WA3888540 | External staff access gate Gate lock sticking -see notes | Mandurah | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Bullant Security Pty Ltd | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 14:10:00 | Pass | Attend site, service lock, unable to repair will need to return with new lock and extended face plate. Date on site: 06/01/21 Time on site: 11:10am - 11:40amRe attend site,replace mortice lock and extended face plate for correct operation. Date on site: 06/01/21 Time on site: 12:55pm - 14:10pm
MSA-DCS | WA3888553 | Old Health Admin Area- Toilet seat is broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 13:14:10 | 2021-01-06 12:30:00 | Pass | Nill
MSA-DCS | WA3888555 | SOG Pod- Control room received a PDA alarm during night | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 08:30:00 | Pass | Unable to determine origin of the transmitter ID 0223888273, however it is not registered on system. Changed programming do system will not display unauthorised alarms.
MSA-DCS | WA3888558 | Bakery- Light to the mezzaine are are tripping out | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 12:30:00 | Pass | Investigate and repair tripping lights at bakery mezzanine.
MSA-DCS | WA3888561 | Bakery - lights out to the workshop | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 14:00:00 | Pass | Investigate and repair bakery workshop lights
MSA-DCS | WA3888576 | Unit 1, B/D wing - replace broken skylights | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 13:51:48 | 2021-01-06 10:30:00 | Pass | JOB RE-ISSUED AS A P0 (WA3909139) - CLOSING THIS JOB OFF COST TO DATE
MSA-DCS | WA3888579 | Security office- computer not downloading | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 13:56:38 | 2021-01-06 13:00:00 | Pass | Clear windows Xperia cashe system work ok now but needs updating
MSA-DCS | WA3888583 | Light flickering constantly | Boronia Pre-release-AM08 - Prisoner Accommodation House 3-Ground Floor-Bedroom 2 | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-07 16:00:00 | Pass | Replaced failed lighting in bedroom 2 of house 3
MSA-DCS | WA3888602 | Unit 1, A & C- Three pin Plug top on polisher needs fixing | Casuarina Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 13:00:00 | Pass | Repaired Unit 1 Floor polisher
MSA-DCS | WA3888605 | Social Visits non contact booths 1-5 Staff Notification Button not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 14:37:29 | 2021-04-06 11:00:00 | Fail | Replaced button on booth 3 prisonernside. All buttons on prisoner side and visitor side tested ok. Parts used:Telemecanique Mechanical switch
MSA-DCS | WA3888615 | Kaartdijin Mia - Office Carpet is badly worn in office with large holes in it. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-03-30 15:00:00 | Fail | Flooring repairs completed
MSA-DCS | WA3888622 | Visits area, Lobby Area- fly buzzer is not working | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 10:00:00 | Pass | Repaired bug zapper in Visits
MSA-DCS | WA3888630 | SOG office indigo control centre screens frozen | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | COMP | 05 Jan 2021 | 2021-01-05 19:22:44 | 2021-01-05 17:30:00 | Pass | Work performed by Dirk Malan 05/01/2021:Attended site. Rebooted PC as Monitors were not displaying anything. Logged Indigo & Command Centre back in for Operators. Systems all OK.Job completed.Work completed under Warranty.Closed of at $0
MSA-DCS | WA3888639 | Perimeter/Pod- Zone 4 mircowave in constant alarm | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 19:37:33 | 2021-01-05 18:00:00 | Pass | Attended site checked and found Zone 4 MW keep alarming. Checked on field found Zone 4 MW A receiver stuck in alarm. Reboot Zone 4 MW A transmitter and receiver. Tested all ok after work.
MSA-DCS | WA4771374 | SHU (9), Cell 5 east wing shelf is damaged | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 05 Jan 2021 | 2021-01-07 17:00:00 | 2021-07-30 09:00:00 | Fail | SHELVES MANUFACTURED - NEW JOB TO BE ISSUED WHEN SITE WANT THEM INSTALLED
MSA-DFES | WA3888053 | Driveway Gate - faulty not opening unless opened manually | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | Go Doors | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 11:50:00 | Pass | COMPLETED
MSA-DFES | WA3888349 | all of facility including 1x carpark blown light globes replace with LED | VFRS Mundaring | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-13 13:30:00 | Fail | Picked up gear and EWP at 0630. Arrived on site at 0736 and repaired all defective lights. Finished task at 1330 and attended next job on site.
MSA-DFES | WA3888368 | Corridor smoke detector faulty zone 1 ceiling | CFRS Vincent | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-08 13:30:00 | Pass | In ceiling detector faulty. Trap door faulty. Replaced detector. Repaired trap door.
MSA-DFES | WA3888385 | Numerous station window treatments require repair - see notes | CFRS Maddington | GMP-BR | Building | Windows (BU) | NEYLOR | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-04-21 11:20:00 | Fail | completed & Invoiced
MSA-DFES | WA3888389 | Garden - Broken gear-drive sprinkler front lawn- (marked with orange paint) | VFRS Mundaring | GMP-BR | Plumbing & Drainage | Drainage (PD) | Dom's Total Grounds Maintenance | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-09 07:30:00 | Pass | Out of Metro Call Out & Labour & Retic Parts
MSA-DFES | WA3888563 | Link Area Door- engine room has had the self-closing mechanism on the wooden door damaged | VFRS - Armadale | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 09:30:00 | Pass | Removed existing damaged door closer and installed new door closer.
MSA-DFES | WA3888634 | Roller door controllers are intermittant & one wont close from pad | VFS Bullsbrook | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-03-02 11:00:00 | Fail | Complete
MSA-DFES | WA3888635 | Security light on North side on compound (floodlight) not working | VFS Bullsbrook | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-19 09:00:00 | Fail | Arrived on site Chris the captain advised that the light works off a PECELL he said all other lights are working fine. The light is 4.2 meters high. There is roof access and harness points on the roof. The globe looks faulty recommend replacing the light with a LED fitting. I tried to reach the light with the 8 ft ladder to confirm if there was power and the light but I could not reach. Will require to return with a new light, extension ladder (should not need it but take one just in case) , harness, rope and lanyard. Advised Chris off work completed. I had 30 minutes lunch I have taken time off total hours worked
MSA-DFES | WA3888661 | dorm 5 bathroom lock on door not working (door to lockers) | CFRS Perth | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 14:30:00 | Pass | Replace faulty mortice lock on bathroom door
MSA-DFES | WA3888665 | admin Operational Delivery Office An air conditioning vent cover has come off - see notes | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-19 15:30:00 | Fail | Replaced AC Vent
MSA-DFES | WA3888668 | admin Operational Delivery Office cover panel on the top of the electrical conduit pole fallen-notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-07 14:15:00 | Pass | Located pole with top cover fallenResecured cover up with screws
MSA-DTAG | WA3888123 | Auto open Front door sensor would not allow alarm to be set. Zone currently isolated. | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 11:15:00 | Pass | Found that the reed switch has been knocked off while the door was being put back on on Saturday, refit the reed switch and tested, all ok.There will be no charge for this call out - we are putting it to warranty
MSA-DTAG | WA3888193 | Basement Lift 3 is out of service – members of staff were stuck in lift | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 16:45:00 | Pass | When responding to the callback dated 05.01.2021, the Schindler Technician found a problem with your equipment. Some componentsof the car door operator were worn out. Following our attendance, the equipment was left in service.To be closed out at $0
MSA-DTAG | WA3888260 | custody cell 2 toilet needs to be cleaned - see notes | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 19:30:00 | Pass | Custody Cell 2
MSA-DTAG | WA3888575 | 1987 L2 room R111 reset the BMS to allow Sheriff’s Office A/C to start at 06.00am | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-05 16:00:00 | Pass | Adjust bms schedule
MSA-DTAG | WA3888590 | Registry Area Plastic cover on lowest step outside Magistrate’s entrance to court 1 come off | Armadale Courthouse | GMP-BR-HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Midolo Building Services | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-08 14:30:00 | Pass | REPAIRS MADE TO STEP - COVER RE ATTACHED
MSA-DTAG | WA3888677 | Fire panel fault - D4 Zone 8- Basement Lift Lobby | Supreme Court-Supreme Court Building-Level 1 | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 21:25:24 | 2021-01-05 19:15:00 | Pass | Complete
MSA-DTWD | WA3888063 | Hole in main line in retic near gardeners shed | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | LD TOTAL | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-13 09:00:00 | Fail | Job at Rockingham Tafe WA3888063 completed on 13/01/2021. All related paperwork has been attached
MSA-DTWD | WA3888135 | S Block Library S206 - counter power has been severed | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 13:02:45 | 2021-01-05 11:45:00 | Pass | Attended site and signed in. Met with staff on site. Located desk power in s block. Found to be all hardwired power through desks that are partly dismantled for removal. Isolated all cabling from desks. Pulled out all data cabling and emergency buttons. Made safe at floor level where cables start. Removed ducting up desk to allow to be removed. Left all cables there until new furniture is brought to site. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3888159 | E block ground level restaurnat kitchen Repair water system leak in ceiling space N/E | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-06 08:03:00 | Pass | Attended site,Completed repairs to the burst aquatherm hot water line in the ceiling of the kitchen. Tested works on completion
MSA-DTWD | WA3888197 | Lift 1 east block Button pushed through on control panel in lift | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-05 13:30:00 | Pass | Lvl 6 button has been smashed in. Created obr ‘button replacement’.
MSA-DTWD | WA3888198 | Wooden Boat works- Alarm panel faults | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 10:30:00 | Pass | 06/01/2021, 1000-1030Replaced Zn 15 battery, ok
MSA-DTWD | WA3888227 | A Block, Ladies toilet constantly leaking middle cubicle | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 11:12:00 | Pass | When onsite 3 toilets were leaking was requested to repair all.I pulled them apart the outlet washers were bubbled and not sealing at baseI removed them and replaced with new.The inlet valves had build up of what looks like red dirt causing them not to fully shut off.I removed them and replace with new inlet valves.Put the cisterns back together and test.
MSA-DTWD | WA3888231 | External grounds retic storage tank Retic concrete water storage tank leaking badly from side wall | Midland Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 05 Jan 2021 | 2021-01-06 17:00:00 | 2021-01-07 08:30:00 | Fail | Emailed BRAF with report and cost to replace irrigation storage tank on the 24-2-2021.Job cancelled, Western Irrigation to invoice cost to date only. Advised 13-8-2021 job being sent out for quotes, Western Irrigation closed off the job 16-8-2021.Any questions please contact Eric Reedman at PFM
MSA-DTWD | WA3888256 | House 8, Kitchen- Faulty sink backboard | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lee Carpentry | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-02-02 12:00:00 | Fail | replaced backbard
MSA-DTWD | WA3888267 | Main alarm panel batteries areas 65 & 69 have been drained-Please call Rick prior to attendance | Naval Base | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-06 08:45:00 | Pass | 06/01/2021, 745-845Replaced both batteriesCleared ok
MSA-DTWD | WA3888272 | 822A - Front door lock faulty | Muresk Institute | GMP-BR | Building | Doors (BU) | Lee Carpentry | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 09:00:00 | Pass | replaced lock
MSA-DTWD | WA3888398 | T Block- T038 hairdressing The main Glass entry door is catching and need refitting | Murdoch Campus | GMP-BR | Building | Doors (BU) | WELLARD GLASS | 2 | CLOSE | 05 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-13 11:50:00 | Fail | job completed- ADJUST FRAMELESS HINGED DOOR LOCATED TO38
MSA-DTWD | WA3888424 | L2 staff kitchen 4 moths old Billi keeps blowing fuse. - see notes | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 05 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-06 13:23:00 | Pass | Spoke to Site - advised that better to get Warranty Call so no charges will apply - chased up Billi to attend free of charge under warranty - followed up with them several times on behalf of client have not charged for this.
MSA-DTWD | WA3888679 | the side door of the building is not working can't close it, site is not secured | Balga Campus | GMP-BR | Building | Doors (BU) | LIGHTHOUSE LOCKSMITHS | 0 | CLOSE | 05 Jan 2021 | 2021-01-05 22:13:06 | 2021-01-05 19:30:00 | Pass | repairs to locks
MSA-DCA | WA3889255 | RO unit has low water level fault | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 09:28:00 | Pass | COMPLETED
MSA-DCA | WA3889523 | RETROSPECTIVE WORK ORDER-broken controller on FCU 7 do not attend | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 06 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-08 17:00:00 | Pass | Humidifier 7 faulting repeatedly on zone humidity and controller. Under investigation.Checked related components and followed fault testing procedure.With Manufacturer assistance continued investigation. Unable to identify cause of faults. Submitted quotations for further investigation, new unit.Closed job.
MSA-DCS | WA3888714 | cameras are down, alarms going off. Cell call system is has network error too. | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 07:44:12 | 2021-01-06 13:00:00 | Fail | Major power recover back on site. Cleared all network errors on cell call system. Checked all MDAS transponders are back on line. Cameras are back online ( except the ongoing issue ones ). Security system back to normal.
MSA-DCS | WA3888715 | Power outage, have got the perimeter lights on, might be power trip. | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 07:47:45 | 2021-01-06 14:47:00 | Fail | HV Fault - report written and sent to PFM
MSA-DCS | WA3888750 | Cool room(bonning room) not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Materials (EL) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 05:40:26 | 2021-01-06 14:00:00 | Pass | found cool room to have a blocked drier . replace part , test and left system operational.
MSA-DCS | WA3888833 | Yeeda units - Camera #155 has unclear vision in night mode | Banksia Hill Detention Centre | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 06:47:58 | 2021-01-06 09:28:00 | Pass | Slime found on camera B8 looks like human waste site will clean
MSA-DCS | WA3888899 | /boilerhouse workshop - boiler #2 out on fault (boiler turned off but in fault position) | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 07:46:26 | 2021-01-06 11:45:00 | Pass | Drive to site sign in and gain access to boiler room, found middle boiler in LFL. Fault position no 1 so I opened up the burner and cleaned the ignition electrode I then checked the damper which I found to be ceased up so I spent some time freeing and lubricating this so that it moved properly I then put it all back together and tested, I carried out several lights and then took it up to pressure with no issues. I did notice the bearings in the fan motor need to be overhauled ASAP. Gauge glasses on the hurst boiler will not blow down as there is a condensate line attached to the same pipe work but it does not have a steam trap on it so steam is pushing against the gauge glass blowdown at all times
MSA-DCS | WA3888905 | Unit 5, B2 - Light near bed full of water | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Jan 2021 | 2021-01-08 17:00:00 | 2021-03-26 13:00:00 | Fail | Replaced lights
MSA-DCS | WA3888921 | Security Area- PDA 92 is faulty battery has been changed but still keeps activating | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-02-24 08:00:00 | Fail | MDAS tramsmitter 92 has been replaced with new, hand over spare MDAS transmitter to security department to be used as spare.
MSA-DCS | WA3888945 | Unit 13, Cell A6- Hot & Cold taps are not working, no water coming out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 12:55:00 | Pass | Nill
MSA-DCS | WA3888946 | Unit 7, C Wing- Kitchen sink needs resealing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-18 09:43:00 | Fail | Nill
MSA-DCS | WA3888980 | Unit 15, C wing - fire alarm showing faulty codes (see notes) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 09:03:24 | 2021-01-06 14:48:00 | Pass | Attended site and found three cells in fault and two disabled on panel.Cells C-5,C-7 & D-15 in fault at time also other cells went in and out of fault and appears to be flow related as fell doors are open and closed.Went to all 64 units and adjusted flow fault settings to plus and minus 30% of normal flow. Also updated descriptions to show cell number in unit to help with fault finding.Previously all had the same descriptions.
MSA-DCS | WA3888983 | Unit 17, control room -fire panel fault, alarm sounding. will not reset | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 09:07:17 | 2021-01-07 08:55:00 | Pass | Attended site and carried out the following works.1: Attended unit 17 and checked MADS and changed setting on all units to increase flow monitoring to plus and minus 30% of normalised.Also while at units updated MADS unit description to indicate cell it covers.Note all faults seem to be due to the flow variation in the pipe and not dust in sample points.2: Checked unit 15 again as they had reported more faults found to be cell A-15 had a high flow.Adjusted settings to allow for higher flow.
MSA-DCS | WA3888988 | SITE COST Unit 6, Cell 6 - toilet wont flush | Bandyup Prison | WSM-BR-SITE | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 13:10:38 | 2021-01-06 10:42:00 | Pass | Attended site,Re assembled flush mechanism to toilet located at unit 6 in cell 6.Tested works on completion
MSA-DCS | WA3888997 | INF(10) - Urn in the dayroom has no water coming out of it. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 08:59:00 | Pass | Replaced broken tap. Asset captured
MSA-DCS | WA3888999 | Unit 14, Cell A8- Tap is leaking/constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 13:30:00 | Pass | Nill
MSA-DCS | WA3889001 | Unit 3 - D3 Cell D03 window spring faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 13:30:00 | Pass | SPIRAL BALANCES RE NEWED - MINOR FRAME REPAIR
MSA-DCS | WA3889012 | Unit 15,16, and 17 - continually losing hot water, hot water keeps shutting down | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 09:17:37 | 2021-01-06 22:00:00 | Pass | Nill
MSA-DCS | WA3889205 | kitchen no water coming through the taps | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 15:01:19 | 2021-01-06 12:04:00 | Pass | Attended site,Investigate no water to kitchen, flush taps to remove potential air lock. Unsure of exact cause.Tested all taps for correct function.
MSA-DCS | WA3889216 | Gatehouse- power failure has caused communication error for systems | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 19:12:30 | 2021-01-08 15:30:00 | Fail | Restarted equipment and arranged for repair of server. Confirmed SMS system operating correctly and cameras recording.
MSA-DCS | WA3889251 | Unit 4, Cell A10- Window being held in place with Toilet Roll, falls out when not held/suported | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 13:00:00 | Pass | SASH REPAIR AND SPIRAL BALANCES RE NEWED
MSA-DCS | WA3889257 | Unit 3, Cell D4- Window does not stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-14 10:00:00 | Fail | SPIRAL BALANCES RENEWED
MSA-DCS | WA3889266 | Unit 13 - B Wing day room sink is leaking underneath into cabinet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-28 14:23:00 | Fail | Nill
MSA-DCS | WA3889298 | Level 4, Kitchen - Zip unit filter is flashing | East Perth | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-07 08:20:00 | Pass | Replaced, flushed and reset zip filter. Dispenser head loose, resecured.Zip Service Moore St East Perth L4 Replaced filter checked unit 2020062251053
MSA-DCS | WA3889299 | entry building zone 4 alarm will not process once activated | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 15:59:58 | 2021-01-06 14:30:00 | Pass | Reset tested ok
MSA-DCS | WA3889374 | Unit 4 Leaking fire Hydrant requires repair behind Unit 4 | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-21 07:55:00 | Fail | Overhauled leaking hydrants
MSA-DCS | WA3889405 | Education staff kitchen - Zip hot water unit, water is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 13:30:00 | Pass | Replaced float system. Tested and allowed to fill. All working and isolating correctly.
MSA-DCS | WA3889407 | Visits hall - Zip water unit, leaking from outlet | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 12:06:00 | Pass | Replaced leaking tap, removed header tank, lubricated and replaced. Cleared blocked feed like as causing slow flow. All now ok
MSA-DCS | WA3889414 | Unit 1, House 7, Cell 1 Cell call volume is low- Reed switch is missing | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 17:30:00 | Fail | Cell Call CELL 1 audio soft. Reterminated cable and adjusted volume pod for speaker, but to no avail. Replaced CI-CC and tested operation, all is in working order. Reed switch for Cell 1 damaged and not working. Replaced Reed Switch and Magnet, tested operation and all is in working order.
MSA-DCS | WA3889417 | Unit 2, House 2- Speakers not very load throughout the house and some not working. | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-15 09:30:00 | Fail | Replaced Amplifier and tested operation with PA Calls. All is in working order.
MSA-DCS | WA3889427 | ISU camera's in D wing all not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 18:00:09 | 2021-01-06 15:30:00 | Pass | Issue with old dvr not starting up properly gots system running again but there are storage alarm S
MSA-DCS | WA3889438 | ISU A, B and C wing no non essential power | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 18:09:39 | 2021-02-10 11:30:00 | Fail | Restored power
MSA-DCS | WA3889446 | kitchen workshop Convotherm not heating correctly KIT00004 | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 14:16:40 | 2021-05-24 13:30:00 | Fail | Date - 7/1/21Make - Convotherm Model - OD 20:20.Serial - NVTechnician - BMArrived at site liaise with kitchen identify oven, isolate remove panels, test/fault diagnose and found that the steaming elements are faulty and require replacement, also found the door seal is faulty and requires replacement and the water level prove requires replacement to, Further testing requires once parts are replaced.3x 14.4 KW 240v elements3x element seal1x door seal1x water level sensor probe06/04/21 WS. Called as requested to fit parts required fitted tested all working correctly now. 2x 20amp fuses require24/05/21 WS. Called to site to fit parts required fitted tested all working correctly now.
MSA-DCS | WA3889455 | Unit 1 end of A wing Side Window Winder is Broken | Melaleuca Prison | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-12 09:30:00 | Pass | Removed damaged window winders and replace.
MSA-DCS | WA3889460 | End of B wing End Window Winder is Broken | Melaleuca Prison | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-12 12:30:00 | Pass | Removed broken window winders and replaced.
MSA-DCS | WA3889464 | unit 2 A-B wing kitchen Stainless Steel Draw Fronts are Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Commercial Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-20 11:30:00 | Fail | Supplied and fitted new stainless steel drawers to kitchen cabinets.
MSA-DCS | WA3889465 | Unit 2 C-D wing Stainless Steel Draw Fronts are Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Commercial Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-20 16:00:00 | Fail | Supply and install new stainless steel drawers to the kitchen cabinets.
MSA-DCS | WA3889513 | unit 1 D2 leaking tap | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 16:02:33 | 2021-01-07 09:40:00 | Pass | Replaced leaking spindle
MSA-DCS | WA3889516 | SITE COST entry building zone 4 alarm not processing | Bandyup Prison | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 20:13:32 | 2021-01-19 09:06:00 | Fail | Attended siteSigned in and completed check inLocated Zone4 microwave ReceiverRe-soldered power for positive and negative wires onlyHeat shrink applied to both wiresClosed zone 4 and checked working correctlyAdvised by control room all workingPacked up and left site
MSA-DCS | WA3889527 | No camera control in the visit room/ lost camera control Camera number 99-105 | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 17:13:20 | 2021-01-07 13:30:00 | Pass | Reset tested ok
MSA-DFES | WA3889173 | Ground- Hole in bitumen of rear yard of station | CFRS Welshpool | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-14 16:30:00 | Fail | job completed - Asphalt repair in rear yard of station at DFES (380 Welshpool Rd, Welshpool)
MSA-DTAG | WA3889030 | Lower ground level, custody - Custody Duress alarms are not sounding when activated | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 13:34:25 | 2021-01-06 11:15:00 | Pass | Custody PC was found to be using audio out from AOC Monitor with no volume. Disable sound deviceand set default to TV screen and tested
MSA-DTAG | WA3889105 | 1903 Judges Lift is not working - out of order | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-20 15:59:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA3889163 | Lvl 1, Offices 204, 205 and 207 - Air conditioners are not working | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-07 14:30:00 | Pass | Investigate AC in room 204/205. Gas leak repair.
MSA-DTAG | WA3889337 | ground Cockroaches have been seen throughout the building on the ground floor | Midland Courthouse | GMP-BR-HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-15 17:50:00 | Fail | Cockroaches treatment to the ground floor area including offices, kitchen, and external area.
MSA-DTAG | WA3889474 | L23 & 124 Goods Lift Lobby Door not locking properly and on Level 23 does not lock when closed-note | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 16:30:00 | Pass | Checked doors on programming and reconfigured various door and controller settings, unable to attend both L23 and L24due to site contact unavailability. Return needed in the morning with Waiverleigh or Corbin to check door state andoperation.Job complete and operating correctly.APPROVED BRAF ATTACHED.
MSA-DTWD | WA3889092 | D block chiller has gone out no air con for whole building-Precise need to contact NRP | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 06 Jan 2021 | 2021-01-06 14:03:27 | 2021-01-06 13:00:00 | Pass | Troy Wuest- Attended P0 call at Joondalup Campus, accessed plantroom and removed cover to chiller to view controls. Found no alarms present in the log. NRP have attended with Precise and they NRP have found the control logic is not setup correctly. This has now been adjusted and is all OK. NRP have found conflicting issues present inside the BMS and will be providing Precise Air a quote to rectify, once received we will submit to Programmed. Works completed, chiller now running - all ok.
MSA-DTWD | WA3889198 | J Block, Room J20, Cleaners room sink is blocked | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 11:45:00 | Pass | Unblocked cleaners sink
MSA-DTWD | WA3889289 | C block outside C101 fire extinguisher has been used and needs to be replace 1.5kg | Munster Campus (ACEPT) | GMP-BR | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | SCAVENGER SUPPLIES PTY LTD | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-14 09:07:00 | Fail | Installed new 2kg C02 Extinguisher and signs-COMPLETED
MSA-DTWD | WA3889296 | G Block, Room G14- Damaged door handle | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-16 09:45:00 | Fail | job completed - replaced faulty lock
MSA-DTWD | WA3889356 | main foyer billi quodra not working- Please give Dennis a call prior to attendance | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 16:08:00 | Pass | Replaced faulty Elelmenet. Calibrated and now all ok
MSA-DTWD | WA3889377 | Grounds - Various tree branches and bushes blown down | Thornlie Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-12 08:00:00 | Pass | Tree works completed. Customer signature slip signed by John Naylor, Thornlie TAFE.
MSA-DTWD | WA3889380 | Block3, 1st floor- Test Cell plant room, access doors open area rotted away | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-02-24 14:30:00 | Fail | Removed existing doors and installed new doors. Existing door hardware was reused.
MSA-DTWD | WA3889386 | Block 6, Ground, Cabinet Making store- External access door rotted away | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-25 11:00:00 | Fail | As the existing door is no longer in use, we have covered the outside of the door with sheet metal. This has been fit to the doorway and painted to match existing colours onsite.
MSA-DTWD | WA3889415 | Freezer needs turning on and computer pad requires resetting to temp after ceiling light replacemen | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 17:00:00 | 2021-01-08 10:01:00 | Fail | Attended site and found freezer short of refrigerant. Reclaimed refrigerant and pressure tested with nitrogen. left over night to confirm if leak is pressent. Found leak on suction line. repaired leak on suction discharge line. charged with 10kg of R404A refrigerant. checked operation of fridge and signed off job as complete.
MSA-DTWD | WA3889433 | block 3 ground Engine Test Cell 1 Oil Drain sink broken off wall | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 06 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 13:22:00 | Pass | Re install sink
MSA-DTWD | WA3889450 | D block L1 main foyer Lift button Exterior ground floor doesn’t work | East Perth Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-06 15:47:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3889482 | A block air con not cooling down area- please attend Thursday | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 06 Jan 2021 | 2021-01-07 17:00:00 | 2021-03-24 15:45:00 | Fail | Attended site, and installed new unit.
MSA-DTWD | WA3889521 | D block D8 Stairwell – Faulty Circuit Breaker in Switchboard | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 06 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 08:01:00 | Pass | Repalced 10amp rcd with 20amp.job completed
MSA-DCA | WA3889749 | Leaking water pipe | Sunset Hospital Heritage Precinct-Building V-Interdenominational Chapel | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 13:10:00 | Pass | Investigated water leak on bore system
MSA-DCA | WA3890031 | Kitchen lift has stopped - see notes | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-ABG.23 - Kitchen | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 18:00:00 | Pass | completed non chargable
MSA-DCS | WA3889624 | Community Rooms 1,2 & 3 - Exterior building lights not working | Boronia Pre-release-AH19 - Administration, Education Senior Officers and Programs-Ground Floor-Community Room 1 | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-07 13:30:00 | Pass | Replaced failing time clock to exterior lighting of community rooms 1,2+3
MSA-DCS | WA3889645 | Unit 7, office - camera monitor not working, unable to see wings | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 07:40:01 | 2021-01-07 09:00:00 | Pass | Found power supply plug for Quad switcher partially out of GPO. Plugged back in and confirmed power light turned on and video images on screen.
MSA-DCS | WA3889648 | Security Area, office - PDA 180 faulty | Casuarina Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jan 2021 | 2021-01-11 17:00:00 | 2021-02-24 09:30:00 | Fail | Deleted the faulty MDAS transmitter and configured new. Tested ok and working. Job completed.
MSA-DCS | WA3889654 | Unit 6, D9 - Toilet float require adjusted. Slow water flowing in the system | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 09:30:00 | Pass | Held up in unit due to short staff
MSA-DCS | WA3889656 | Visits, Non Contact Rooms- Blue lights flashing | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 16:00:00 | Pass | Light is at the gatehouse for the random pat down searches. Light was flashing constantly. Repaired and tested ok.
MSA-DCS | WA3889657 | Unit 6, D9 - Pipework in maintenance cupboard was is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 10:30:00 | Pass | Nill
MSA-DCS | WA3889658 | Unit 6, Control Room Staff toilet- Extractor fan not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-07 15:00:00 | Pass | Repaired fan
MSA-DCS | WA3889659 | Unit 7, Cell H25- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 11:00:00 | Pass | Replaced light switch
MSA-DCS | WA3889662 | Unit 6, Cell D6- Viewing hatch glass hatch | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 08:08:16 | 2021-01-07 10:45:00 | Pass | RE GLAZED CELL D10 OBS PANEL (NOT D6- AS ABOVE)
MSA-DCS | WA3889663 | Unit 6, rear of B&D wing - water bubbling to surface(Unsure if reticulation or main) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 08:06:56 | 2021-01-07 10:30:00 | Pass | Nill
MSA-DCS | WA3889666 | ISU- 24V signal not at ISU resulting in no non essential power | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-29 16:41:00 | Fail | Completed all repairs and tested ok.Job Complete
MSA-DCS | WA3889667 | Unit 14, A6 - water pressure in cell tap is low | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 08:33:00 | Fail | This work order is a double up (sign slip attached from original job from 14/1
MSA-DCS | WA3889669 | Unit 4, Cell B13- Window does not stay up (risk of breaking) | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 09:30:00 | Pass | SPIRAL BALANCES RE NEWED
MSA-DCS | WA3889670 | Unit 14, A12 - Pressure is very low in the shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 12:30:00 | Fail | Nill
MSA-DCS | WA3889672 | Unit 6, Cell C9- push button for toilet is getting stuck in & not releasing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-15 14:30:00 | Fail | Nill
MSA-DCS | WA3889730 | SITE COST unit 2 security monitor has gone blank - SEME on site | Melaleuca Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 13:20:58 | 2021-01-07 10:30:00 | Pass | Unit 2 Camera screen not working. Checked screen and found no signal on HDMI input. Input to screen is VGA changed source and cameras all back up now.
MSA-DCS | WA3889831 | Unit 5 investigate faulty zip tap | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-02-25 09:15:00 | Fail | Removed existing Zip unit and installed a new system and commissioned. REMOVED OLD UNIT TO TIP - 2 TECHS
MSA-DCS | WA3889836 | Lenard A04 shower constantly running (solonoid) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-29 10:30:00 | Fail | Replaced faulty parts in the plumbingduct
MSA-DCS | WA3889858 | ground floor front door lock not latching, back office door closer not working | Warminda Hostel | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 11:22:17 | 2021-01-07 13:30:00 | Pass | Attended site and carried out repairs to lock on the front door.Carried out repairs to the hydraulic door closer.
MSA-DCS | WA3889929 | Unit 1, Ground floor, staff disabled toilet - Leaking tap and toilet in staff disabled toilet | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-18 08:59:00 | Fail | Arrived on site and inspected found the the tap leaking. Could not find any isolation. Need to isolate the water meter to repair the tap. Inspected the cistern. Working intermittently need to change the cistern. Will come back on Saturday at 8.30 am. Access organised with the site person Gained access to the building on Saturday. Isolated water. Removed the faulty tap and replaced with new tap. Reconnected water and tested all working good. Returned to site. Removed the faulty cistern and installed new cistern. Tested all working good.
MSA-DCS | WA3889948 | kitchen work area L/H Back Range Hood Fan Tripping RCD | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-03-08 08:00:00 | Fail | VSD controlling exh fan motor speed is overheating due to it’s internal cooling fan not working. Will see if still available .will estimate to repair.Original fans not available due to covid-19 , fitted alternate fans to restore operation of variable speed drive. Recommend original cooling fans be sourced after Pandemic ends, if they are available.
MSA-DCS | WA3889953 | Kitchen, Work Area- Hanging GPO has no power | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 13:00:00 | Pass | Reterminated loose cables supplying gpo. Yest ran ok.
MSA-DCS | WA3889959 | Gatehouse, medium prison - UPS is offline | Bunbury Regional Prison | GMP-BR- HO | Electrical | UPS System Maintenance (EL) | Sapio Pty Ltd | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 21:08:11 | 2021-01-07 14:00:00 | Pass | Rectified Cooling / Heat effecting the UPS.
MSA-DCS | WA3889997 | SITE COST Security office of Amin building - downloaded computer is not working | Banksia Hill Detention Centre | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 18:14:13 | 2021-01-07 16:00:00 | Pass | Activex error controls lowered reset retested ok.
MSA-DCS | WA3890006 | gate house hub modom level loss alarm | Pardelup Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 22:24:57 | 2021-01-13 10:00:00 | Fail | On inspection found voltage drop (1v) across fuse carrier for modem in EC, corrected. Checked fibre rack and unable to find cause of alarms after power restore.
MSA-DCS | WA3890015 | Inner gate does not open | Melaleuca Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 18:37:45 | 2021-01-07 18:15:00 | Pass | 07/01/21Gate fully jammed.Heat had expanded gate to catch post.Adjusted gate hinges.
MSA-DCS | WA3890016 | main kitchen BRAT pan broken down | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 14:39:40 | 2021-01-08 12:30:00 | Pass | Replaced Rubber Safety Cover to tilt switch. However one foot has broken away, one is ready to break and other two, and their chasis connection points are corroded and will fail sometime. Also noted flue guards and internal panels showing corrosion. Unit should be replace. As food product was in pan, arranged for some "blocks" to be put under units chasis to prevent possible incident if any feet fail. unit is heavy and would tilt over, risking injury. Blocks will reduce risk greatly for just now.
MSA-DFES | WA3889729 | Main unit system for air con is not working for all units | Butler Career Fire Station | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 13:07:31 | 2021-01-07 13:00:00 | Pass | Completed works as per scheduled service call out & report.Advised client of works carried out, all working correctly.
MSA-DFES | WA3889776 | corporate DC L1 air con is to warm no water flow to condensor | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-02-23 11:00:00 | Fail | Installed new control system for temperzone supplementary units in ict server room. Calibrated sensors and controls. Confirmed all operating correctly.
MSA-DFES | WA3889880 | main ground Female toilet (1st one) Toilet not flushing properly/not flushing at all | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-08 12:16:00 | Pass | Servicing toilet cisterns
MSA-DFES | WA3889917 | L1 Light in the Ladies toilet entry is out. Suspect blown light bulb | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 12:45:00 | Pass | Located 3 x Faulty lights in the hallway and inside first floor ladies toilet. Repaired and tested for function.
MSA-DFES | WA3889962 | Front sprinkler on McDowell side of front apron lawn is not working. | CFRS Welshpool | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-09 11:40:00 | Pass | Repair Large Gear Drive Sprinkler & all other leaks & breakages
MSA-DFES | WA3889964 | Ceiling tiles damaged and exposed insolation in entry to Fire station. (within engine room) | CFRS Daglish | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 08:00:00 | Pass | work complete
MSA-DFES | WA3890028 | 3 Lights not working in Information Resources Room | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 13:30:00 | Pass | Located 3 faulty lights in Information Resources room and repaired accordingly.
MSA-DFES | WA3890030 | ground FF dorm 1 Top and middle door hinge on dorm door damaged | CFRS Osborne Park | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 09:45:00 | Pass | work completed as per signature slip
MSA-DFES | WA3890034 | gym air con not working | CFRS Fremantle | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-08 09:30:00 | Pass | Investigate AC 7.
MSA-DTAG | WA3889652 | BRS (court security) have been locked out of their Security System which unlocks or secured doors | Rockingham Justice Complex | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jan 2021 | 2021-01-07 11:49:36 | 2021-01-07 12:00:00 | Fail | Network error no cause evident in logs, Complete reset of site computer security system conducted. Workstations reconnected tested now working ok.
MSA-DTAG | WA3889696 | G Floor, Court 3- Fabric panel has fallen off the wall | Perth Children's Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 08:15:00 | Pass | magnetic catch installed on wall panel to re fix
MSA-DTAG | WA3889739 | Camera fault - showing yellow not green graphics | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 15:00:00 | Pass | Restarted Milestone Drivers, extracted license information, adjusted and cleared faults with smart wall CCTV, checkedand cleared any firewall blocks on servers integrating Pacom/Milestone. Cleared and all running okay. Advised site thesystem appears to be giving login authentication error, however, CCTV HLI still operates 100 percent.Job completed.
MSA-DTAG | WA3889741 | L1 External Staff Entrance Door Not opening properly | Perth Children's Court | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 12:00:00 | Pass | Tested Door Function. Mag lock instantly locks on release. Changed settings and time to suit mag lock on Paycom System. Now the lock stays open for 3 seconds before attempting to latch. Job Complete.
MSA-DTAG | WA3889800 | L12 Lift 2 – lift shuddered/stopped between floors & doors opened | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-07 17:45:00 | Pass | T4 faults in controller, found level 14 landing door lock knocking skate. No more adjustment on landing door lock, madeadjustments to car door skate and tested lift to every level. Lift back in service.To be closed out at $0
MSA-DTAG | WA3889804 | No hot water from shower – south corridor past Court 11 & adjacent to Judges chambers | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-07 15:20:00 | Pass | Investigated lack of hot water. Advised by Ian that there is an electrical issue. Ian advised to close of work order, as he was going to issue new work order to Electricians.
MSA-DTAG | WA3889808 | Technician required to attend at 07.00am Saturday 9 January 2021 to assist HVAC- see notes below | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-09 09:30:00 | Pass | Work with HVAC to investigate level 1 fire signal
MSA-DTAG | WA3889995 | L6 Adjust A/C BMS timer to remain on tonight – 7/1/21 | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 11:00:00 | Pass | Attend site. Access BMS. Return time schedules back to previous times. Save new schedule. Check operation of plant, working ok.
MSA-DTAG | WA3890032 | 1987 L4 plantroom Check power supply to HWU pump unit | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-28 09:26:00 | Fail | Tested power to hwu and pumps and tested thermostats and found fault to be pump on wall. Returned to replace blown fuses once motor was replaced
MSA-DTWD | WA3889768 | A Block, Room A131 Male Toilet- Repair patch damaged wall | Leederville Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-02-09 16:00:00 | Fail | Repair and paint bathroom wallapply anti graffiti
MSA-DTWD | WA3889835 | Block 3, 1st Floor, test cell plant room- mutliple lights & emergencyexits not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 15:00:00 | Pass | Replaced faulty fluros and light switch throughout block 3 1st floor plant room
MSA-DTWD | WA3889842 | Block 10 L1 external Switchboards DB4 and DB5 have no seal to roof space - see notes | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-08 13:30:00 | Pass | Attended site and signed in. Located block 10. Checked out switchboards. Isolated incoming power. Installed fire rated pillows to top entry of switchboards. Dusted cleaned and vacuumed dirt and leaves from switchboard. Reinstated power. Checked and tested all okay. Job complete
MSA-DTWD | WA3889847 | Block 10, Pathway- Coms pit lid broken outside ladies toilet. | Thornlie Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-08 15:00:00 | Pass | Attended site and signed in. Located toilet area of block 10. Found Comms pit next to pillar to be pushed into pit base. Removed dirt and lid. Clean up pit and made good pit base and re instated pit lid. All okay. Job complete
MSA-DTWD | WA3889848 | Block 3F ground Engine Test Cell 1 Door close broken on personnel door. | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 13:30:00 | Fail | Replaced existing door closer with new TS83 Dorma door closer and mounting bracket.
MSA-DTWD | WA3889849 | Block 12, External south wall - Evac speaker not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 15:30:00 | Pass | Attended site and signed in. Located block 12. Found external speaker to be hanging and facing ground. Can’t move to face the evacuation area. Re fixed to wall. Advised that now the demountable unit is in front of the muster point to installed another speaker facing the area. Ordered parts. Will return next week to complete. Job not completeAttended site and signed in. Got speaker from supplier. Installed in position to not be blocked by demountable. Ran conduit and cabling over to new speaker from existing. Tested all okay. Job complete
MSA-DTWD | WA3889853 | Block 10 L1 10F85 Door hinge screws broken | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 15:13:00 | Pass | Remove existing screws from hinges and install nutserts to door and new screws to hinges.
MSA-DTWD | WA3889863 | T Block, Drinking fountains have little pressure, possible blocked filters | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-08 10:47:00 | Pass | Adjusted flow rates to the bubblersadjusted flow on fountainsA40139044E T BLOCK COURTYARDA401390528 T BLOCK T GRND FLOOR LOUNGEA40139045F T BLOCK GYMA40139053E T BLOCK OUTSIDE GYMA40139051C T BLOCK 1ST FLOOR NEAR LIFTSA40139050B T BLOCK L1 ACROSS FROM T108A40139049J T BLOCK L1 OUTSIDE ROOM T136A40139048I T BLOCK L2 ACROSS FROM T207
MSA-DTWD | WA3889961 | B9 First Aid room - wall sinks taps x 2 and sink waste faulty | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 15:00:00 | Pass | Fix taps
MSA-DTWD | WA3889971 | G Block, Air Con is not cooling | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-08 11:30:00 | Pass | Accessed the roof aircon at G block, found stage one on aircon one tripped out on defrost sensor. Reset and checked the operation all ok .
MSA-DTWD | WA3889983 | A block L1 A49 Water leak from drain pipe under sink. Water dripping downstairs in walkway. | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-27 12:30:00 | Fail | Replaced leaking fitting and pipework
MSA-DTWD | WA3889986 | block 3 ground male and female toilets Exhaust fans not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 1 | CLOSE | 07 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-11 12:29:00 | Fail | TRAVELLED TO SITE. LOGGED ON TO SITE. MET WITH MANAGER. GAINED ACCESS TO SITE. TOILET EXHAUST FANS APPEAR TO BE OPERATING. WAS INFORMED OF POSSIBLE POWER FAILURE AND TIME CLOCK MAY NEED RESETTING. CHECKEDAND RESET TIME CLOCK. CHECKED OPERATION AND CHANGE OVER. TIMER REQUIRES REPLACEMENT. FOUND DIGITAL TIMER HAS FAILEDPICKED UP PARTS FROM SUPPLIERS. RETURNED TO SITE. GAINED ACCESS TO SITE. ISOLATED AND CHECKED NO POWER AT MSSB. REPLACED DIGITAL TIME CLOCK WITH ANALOGUE TIME CLOCK AS PER REQUEST FROM JOHN. REMOVED ISOLATION AND CHECKED OPERATION. ALL OK. COMPLETED PAPERWORK AND LOGGED OFF JOB AND SITE.
MSA-DTWD | WA3889988 | Level 3, Roof Deck- Wooden door damged (hinge & lock) | Perth Campus B1 | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 14:00:00 | Pass | Attended site and checked in with a staff member.Went up to level 3 and found the timber door on the roof deck.The door sits 1500mm from floor level, so I may need a second pair of hands to make repairs.I couldn’t open the door, as there was no one on site to give me a key at that time.Left site to collect a platform ladder.Returned to site, signed in, and collected a key from Facilities.Managed to get the door open to inspect the hinge. The hinge had become loose due to oversized screw holes.Completed JSA.Left site to collect all materials needed to make repairs.Returned to site and proceeded to make repairs to the door edge by drilling out 5.5mm holes then fitting 6mm timber dowel with epoxy glue.Hinge was left off until glue and dowel had fully set.Repairs were made to the split lining board. The split piece was there, so I was able to fix it back in place using the epoxy glue, which would give it a better bond.Hinge was refitted to the door, and the door was check for o
MSA-DTWD | WA3890017 | N Block, Room N106- Air Con unit in cafe seating area faulty | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-04-21 13:30:00 | Fail | Accessed site completed relevant sign in procedures , gained access to canteen split system unit , upon investigation found that indoor fan motor is noisy and requires replacement , qrf submitted 21/04/21Accessed site completed relevant sign in procedures and covid safe app wa requirements, electrically isolated cafeteria seating area unit , removed covers and faulty indoor fan motor , reinstalled new indoor fan motor , reassembled unit , reinstated power and tested operation , all ok
MSA-DTWD | WA3890018 | Block 10 ground 10G66 Creche External door has paint damage and showing weather damage | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 07 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 15:23:00 | Pass | Sand back and paint door.Install new weather seal.
MSA-DTWD | WA3890023 | Block 1 ground Jobs and skill Duress alarm has faulty activation | Thornlie Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 2 | CLOSE | 07 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 14:00:00 | Pass | Returned to site to install new wireless 'Request For Assistance System
MSA-DCA | WA3890243 | Urban Orchard - retic, Zone 10 & 8 high water usage alarm. | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Water (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 08 Jan 2021 | 2021-01-08 17:00:00 | 2021-01-08 10:15:00 | Pass | job completed - Replace the internals of the 3 x 50mm Solenoid Valves in Urban Orchard valve box as existing are very old and clogged andcontinue to leak
MSA-DCA | WA3890662 | Admin roof space - fire detector in fault L8S73 | Art Gallery of WA - James St - Administration Block (Block A) | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 16:30:00 | Pass | Detector in admin roof space causing intermittent pre-alarm. Most likely caused by extreme hot weather. Isolated detector until temperaturesdecrease. On site security to reinstate detector.
MSA-DCA | WA3890760 | Exhaust Fan 27 is overloaded. Please inspect | State Library of WA-Main Building-Level 3-3.41 - Preservation Services - North | GMP-BR | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 12:00:00 | Pass | Attended site. No faults on MSB indications for EXF 27. No active alarms on BMS for EXF 27 or any other EXF. Using Mech Drawings and Airflow Schematic, unable to locate fan. Will monitor and locate during PM.Closed job.
MSA-DCA | WA3890792 | Open Loop - Fire Panel - Code Red Box in fault | Collection and Research Centre Welshpool | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 08 Jan 2021 | 2021-01-09 01:01:59 | 2021-01-08 22:20:00 | Pass | Performed loop test panel reset operating correctly.
MSA-DCS | WA3890200 | Perimeter - Camera 6 & 27 are unclear/discouloration | Banksia Hill Detention Centre | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 07:08:33 | 2021-08-30 06:52:00 | Fail | Works complete as per BRAF
MSA-DCS | WA3890205 | Gatehouse, Control room - Cameras are frozen | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Jan 2021 | 2021-01-08 11:13:49 | 2021-01-08 12:30:00 | Fail | Attended site checked and found both CCTV and Security workstations in Control and Reception are not working properly. Further check located the problem to be the Gallagher and Indigovision server down. Rectified the problems and bring all service back online. Also terminated new Cat 6 cable for the CCTV workstation USB extender in Control as office request to elaminate the wireless mouse intermittently frozen problem.
MSA-DCS | WA3890213 | Vegetable Preparation, Workshop - processing coolroom reading higher than normal temps | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 07:23:37 | 2021-01-11 14:30:00 | Fail | Arrived on site and signed in,checked over coolroom after weekend found unit still running but second isolator turned off, turned on and tested all running ok at present.
MSA-DCS | WA3890216 | Unit 4, B wing - window is cracked/broken in B wing shower area | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 11:30:00 | Pass | WINDOW RE GLAZED AND ATTACHED - SPIRAL BALANCES RE NEWED
MSA-DCS | WA3890222 | Unit 4, D wing - light switch in cleaning cupboard is faulty, switch loose | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-08 12:00:00 | Pass | Replaced faulty lights switch in unit 4 cleaning cupboard. Returned to check parts after pest control attended
MSA-DCS | WA3890249 | Unit 14, B8 - shower drain clogged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 12:30:00 | Pass | Nill
MSA-DCS | WA3890252 | Unit 5, B9 - toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 14:30:00 | Pass | Nill
MSA-DCS | WA3890257 | Control room - monitor screen - urine and laundry showing open on screen but are physically locked - | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 07:55:14 | 2021-01-08 15:00:00 | Pass | Attended site checked and found Urine and Laundry doors showing open on screen but physically closed. Further check located the problem to be the Cardax Controller software problem the doors attached to. Reinstalled the controller software and tested all ok after work.13/1/21 recall replace controller with site spare, program & test ok
MSA-DCS | WA3890259 | Unit 6, B Wing- Shower cubicle 1 (nearest door) is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-21 09:30:00 | Fail | Nill
MSA-DCS | WA3890262 | Swimming Pool - Sodaash Pump is not working | Wooroloo Prison Farm | WSM-BR-SITE | Recreation | General (RC) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-22 12:59:00 | Fail | Soda Ash pump inspected in workshop. Replacement is required. BRAF is to follow.
MSA-DCS | WA3890263 | Unit 3, office - fire alarm is continually going off at least 3-4 times a day (see notes) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 08:00:33 | 2021-01-08 11:07:00 | Pass | 13/1Attended site and adjusted pressure switch cut ins and out. Adjusted pressure switch to suitable pressure. Tested multiple times - operatingcorrectly however recommend pulling apart29/1/21. BR&CW• arrived at site• isolated valve and turn all ball valves of to take jacking pump out• remove jacking pump• pulled apart jacking pump to check why making so much noise, lubricated pump and put pump back together. Tested multipletimes, sounding better will require replacement in the future if further deterioration occurs
MSA-DCS | WA3890267 | Kitchen, Cooking Area- Large kettle in the center on right hand side, not heating properly | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 08:08:36 | 2021-01-08 16:00:00 | Pass | 08/01/21Called as requested to the kettle not working correctly slow to heat. Found the potentiometer water damaged so replaced with new tested working better left under observation.
MSA-DCS | WA3890271 | Unit 1, A-B common area underneath red mail box- Double GPO Loose in the wall & Cracked | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 10:00:00 | Pass | Replaced broken gpo, tested new one ok.
MSA-DCS | WA3890283 | Unit 4, D Wing - Store room light is not working, globes have been changed but still not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-08 15:00:00 | Pass | Repaired faulty lights in unit 4 cleaning cupboard. Returned to inspect after pest control attended
MSA-DCS | WA3890287 | Kitchen - Large kettle not getting hot | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 15:00:00 | Pass | Large Kettle not getting hot in kitchen. Check kettle & controls. Dismantle, found wiring to elements burnt off. Return & remove burnt out wiring, repair wiring, reconnect to elements. Test all circuits. Assemble and run.
MSA-DCS | WA3890297 | INF (10) B4 - Toilet system in cell B4 is continually running. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 09:30:00 | Pass | Nill
MSA-DCS | WA3890307 | SOG Base, ERU Hut- extractor fan is not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 09:30:00 | Pass | Replaced broken fan
MSA-DCS | WA3890310 | admin building emergency tones in audible | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | COMPFIN | 08 Jan 2021 | 2021-01-09 09:01:27 | 2022-05-27 21:03:00 | Fail | Repaired multiple PA and EWIS faults in admin and gatehouse.Tested OKJob Complete
MSA-DCS | WA3890318 | Kitchen - Flyscreen front door of kitchen hinges and closer faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-06-02 11:00:00 | Fail | no charges - closed off compfin
MSA-DCS | WA3890324 | Kitchen - Flyscreen rear door of kitchen hinges and closer faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-06-02 15:00:00 | Fail | supplied and installed new screen door to kitchen rear entry.
MSA-DCS | WA3890331 | Kitchen - Rational oven door not closing properly | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-15 08:45:00 | Fail | Removed & readjusted as well as tightening grub screw, refitted and tested ok.
MSA-DCS | WA3890335 | Kitchen - Kitchen water filter below urn leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 09:50:00 | Pass | Replaced leaking filter.
MSA-DCS | WA3890337 | Kitchen Tap under sink leaking nearest main entry | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 08:13:00 | Pass | Repaired leaking sink mixer.
MSA-DCS | WA3890341 | Void - Toilet The pan adaptor is leaking behind the toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 10:30:00 | Pass | Nill
MSA-DCS | WA3890412 | Repair double GPO in gwynlea kitchen wall & lights in Cells 5&9 not working-see notes | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 16:00:00 | Pass | Replaced failed mounting blocks in Gwynlea kitchen and repaired cell’s 5,9+10 lighting.
MSA-DCS | WA3890446 | Bakery- Power box has become deatched from machine wires exposed needs reattaching | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 08:00:00 | Pass | Repaired damaged control box on dough rolling machine in bakery
MSA-DCS | WA3890449 | Unit 2, B Wing- Tap spout broken off in cleaning room & sink is half hanging off wall | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-14 15:30:00 | Fail | Nill
MSA-DCS | WA3890532 | Main reception door into secure area is not closing | Maddington (South East Metro) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 11:41:31 | 2021-01-11 12:00:00 | Fail | supplied and installed new hydraulic closer to main reception door.
MSA-DCS | WA3890554 | Gate housee - Fire alarm showing fault | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 12:05:15 | 2021-01-08 15:24:00 | Pass | SFIP at Node 3 Self Care Unit 2B had crashed and showing Node 3 Loop 3 fault on MFIP.Carried out cold reboot on Node 3 and system returned to normal operation. Checked panel but no apparent cause for crash, possible mains power surge or similar.Left system in normal working order.
MSA-DCS | WA3890555 | Re Entry house- Hose reel has no pressure | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 12:07:15 | 2021-01-08 14:34:00 | Pass | Hose reel is outside the main entrance to Re-entry House is brand new, no issue with hose reel itself. Hose water jet is reaching around 5 to 6m.This hose reel has always had lower water pressure than others on site and the underground pipework feeding the hose reel needs to be checked as it is suspected the pipe may be crushed or kinked.
MSA-DCS | WA3890559 | MDAS is coming up in areas that are not activating | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 12:08:07 | 2021-01-19 16:28:00 | Fail | Investigated Education and Programs areas for duress accuracy as per Security Manager. Identified multiple receiver faults, repaired and recalibrated area.Tested OK.Job Complete
MSA-DCS | WA3890612 | Unit 3 C wing showers right hand sink no hot water from the tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-15 08:50:00 | Pass | Replace leaking tap
MSA-DCS | WA3890615 | service road Behind Admin Building Tall Light Pole Light Cover Hanging Off Light | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-05-12 14:00:00 | Fail | Will source price and availablity of roadway lights diffusers.Returned and fitted new diffusers and retaining clips.Safety wired clips closed to prevent birds undoing them.
MSA-DCS | WA3890646 | Education, Room 2- PO's office air con failing | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Jan 2021 | 2021-01-09 13:38:08 | 2021-01-14 12:34:00 | Fail | Arrived on site and signed in, carried out final checks,system all running ok at present.
MSA-DCS | WA3890652 | 1 & 2 Day rooms - window locks wont unlock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 11:30:00 | Pass | Attend site to remove locks to have new keys made. Reattend site to install locks and supply 2 new keys.
MSA-DCS | WA3890682 | visits hot water urn leaking (sespect may need replacement 2011 D.O.M) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-27 14:00:00 | Fail | Replaced broken urn
MSA-DCS | WA3890744 | Unit 1 cell B23 shower damaged needs to be waterproofed and cracked tiles on wall fixed | Bandyup Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-02-10 15:00:00 | Fail | Removed loose tiles and waterproofed wall.Supplied and installed new wall tiles to shower recess.
MSA-DCS | WA3890782 | Karnet Prison Farm - All cameras are frozen in the control room | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Jan 2021 | 2021-01-08 21:41:38 | 2021-01-14 14:52:00 | Fail | Found issue with pc over heating shaped pc with new on cpu running at 30% and at 70c
MSA-DCS | WA3890784 | SITE COST - Rear of Unit 2 - Water leak from an outside kitchen pipe. | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 08 Jan 2021 | 2021-01-08 22:16:09 | 2021-01-08 21:30:00 | Pass | nil
MSA-DCS | WA3890786 | Unit 3 West Side A & C Wing - Fire Suppression malfunction and has flooded 4 units. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 08 Jan 2021 | 2021-01-09 00:26:36 | 2021-01-09 00:10:00 | Pass | Casuarina 8/1/21Unit 3 sprinkler head set off by inmates. Attended site and shut off water supply to system awaiting return visit from sprinkler fitter to repairand reinstate system.Attended site, drained down system and replaced sprinkler head from workshop stock, refilled system and all ok on departure.
MSA-DCS | WA3890788 | Unit 3 West Side A & C Wing - Fire Suppression malfunction and has flooded 4 units. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 08 Jan 2021 | 2021-01-09 00:34:54 | 2021-01-08 22:30:00 | Pass | only isolated valve as i was onsite, ara took the repairs over and will turn service back on
MSA-DCS | WA3895708 | Retic pipe causing flood near staff car park | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-09 11:00:00 | Pass | dug out and repaired with coupling
MSA-DCS | WA3895712 | Retic not working, please check pumps | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | WESTERN IRRIGATION PTY LTD | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-19 10:00:00 | Fail | 8-1-2021 Check operation of Melaleuca Prison pumps, could not fault pumps.12-4-2021 Technician found multiple start times on controller and times on stations that do not exist. Reprogrammed controller with client.19-4-2012 Install identification labels on pumps and in control cubicles as requested by Larry Grohovaz.
MSA-DFES | WA3890380 | SES panel will not arm | SESU Mundaring | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 12:00:00 | Pass | 08/01/2021, 1100-1200System was going haywire by a possible power surge all expanders offline keypads going on and off. Rebooted system and tested all okChecked and corrected programming.
MSA-DFES | WA3890488 | House air con is faulty, not working/cooling | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-02-26 11:00:00 | Fail | Removed ductwork and existing ACInstalled new ACCommissioned and airbalancing completed
MSA-DFES | WA3890590 | Facility Managers’ Office set BMS alarms to addresses, phone numbers and set priorities. - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-03-18 15:44:17 | Fail | Returned to site and confirmed all alarm priorities have been set to listed value. Confirmed bms is sending email out. Reported this to pfm and completed job.
MSA-DTAG | WA3890345 | Lvl 4- water in the Female disabled toilet close to Court 41 is running continuously | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-02-10 16:02:00 | Fail | COMPLETED
MSA-DTAG | WA3890516 | Various lights are not working in the below locations | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-15 10:45:00 | Pass | Replaced tubes in varies location
MSA-DTAG | WA3890602 | ground Lift 10 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 16:15:00 | Pass | Lift at G. Multiple 149 t5 errors. Ground floor door closer weight cord has broken. Needs repair. Obr created lift off for repairsTo be closed out at $0
MSA-DTAG | WA3890665 | L4 Chair brackets in one of the public seats are broken - see notes | Central Law Courts | WSM-BR-SITE | Furniture | Commercial Furniture (FU) | Midolo Building Services | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 10:00:00 | Pass | CHAIR BRACKETS REPLACED
MSA-DTAG | WA3890667 | Judicial Support Office- Aircon is reported to not be working efficiently | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-12 12:00:00 | Pass | Return to site. Access BMS and check zone temp. Found temp to be 22.8 degrees in area. Check vav box and found max airflow to have reduced as is close to setpoint. Area temps is normal and system is working correctly.
MSA-DTAG | WA3890670 | Cleaner’s room between staff toilets- Taps over sink remain dripping and do not turn off | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 09:35:00 | Pass | Rewashed leaking tap
MSA-DTWD | WA3890208 | Level 2, Room 237 - leaking toilet | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 17:52:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3890210 | Level 2, Koolark - water leaking on Billi | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 08 Jan 2021 | 2021-01-14 17:00:00 | 2021-04-01 16:30:00 | Fail | Billi unit leaking and replaced
MSA-DTWD | WA3890295 | E Block- Stores entry double door not opening when swiping access card on reader | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-08 16:30:00 | Pass | Investigate door faults. Check door devices and programming. Run report history for door. Reset door access zones and schedule. Fix door programming for door devices. Test and check maglocks ok. Test swipe entry ok, confirm with security guard access card Note: Door brackets need fixing or filing down, not closing properly automatic
MSA-DTWD | WA3890359 | Lvl 5,Plant Room - Chiller 2 stage A will not run. Stage B & C out on fault | Perth Campus B2 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-03-18 10:33:00 | Fail | Attended and confimed BRAF works complete after by chiller specialist. Confimed chiller operation. All ok. Work area tidy. Note there is a DAS is awaiting approval for equipment.
MSA-DTWD | WA3890462 | F Block, FG39- Auto doors to CSC will intermittently get stuck open, could be a faulty sensor | Carlisle Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 08 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-08 14:35:00 | Pass | Found external sensor faulty causing door to stay open, replaced sensor and tested door all ok, all works approved by frank. Found door faulted again when packing up and found battery’s faulty as well, replaced battery’s and tested door all ok
MSA-DTWD | WA3890695 | Graffiti on C Block near C109 | East Perth Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 08 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-11 14:50:00 | Pass | REMOVAL OF GRAFFITI FROM C BLOCK NEAR C109
MSA-DTWD | WA3890705 | Block 9 ground plant room Chiller tripping out. | Thornlie Campus | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 11:00:00 | Pass | Chilled water pumps and chiller reset by client after fault registered. Arrived on-site and checked operation and for any active or history of alarms. Non found and systems running as normal.
MSA-DTWD | WA3890752 | ground customer service air con not working | Armadale Campus - 40 Commerce Ave | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 08 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-11 09:30:00 | Pass | Found unit to be operating on arrival. Informed unit didn't appear to be working before weekend but is now running. Checked full operation of unit. Checked and found no active fault alarms. Unit operating as normal. Possible power issue in area at the time.
MSA-DTWD | WA3890779 | rear auto door A block will not close | East Perth Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 08 Jan 2021 | 2021-01-08 20:54:30 | 2021-01-11 10:02:00 | Fail | 8/1/21 - Found top set of pe sensors to be intermittent. Even when cleaned the door would still reopen. Temporarily disconnected top set to get door working. Security could not stay back for them to be changed.Return Monday to replace 2 sets of pe sensors.11/1/21 - Returned to site and replaced 2x sets of pe sensors, tested all ok.
MSA-DCA | WA3890829 | several light poles vandelised | Perth Cultural Centre Precinct-Urban Orchard-Ground Floor | GMP-BR | Building | General Building (BU) | Techworks Electrical | 1 | CLOSE | 09 Jan 2021 | 2021-01-11 17:00:00 | 2021-01-09 15:00:00 | Pass | Inspected all poles to find several light diffusers have been knocked off due to vandalism throughout the night, lamps have also been smashed in the process.Rectified all broken lights, snapped brackets and missing lollypop diffusers.Also re fixed a few lights that have been shaken but haven't had the diffuser fall off.Used all spares from underneath ramp near cleaners office.
MSA-DCA | WA3890842 | Batavia Gallery -Aircon-High temperature high humidity alarms | Shipwreck Galleries-Main Building-Ground Floor | GMP-BR | Building | Air Curtains (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Jan 2021 | 2021-01-10 09:26:25 | 2021-01-28 15:24:00 | Fail | Attend site and inspected humidity alarm in Batavia Gallery (Sunday 10/01).Found boilers to have both faulted on E04 (water missing in the system).Checked pump pressures.Pump pressures ok (400kpa discharge – 75-100kpa Suction).Isolated and checked strainers.Both found to be clean.Attempted to reset boilers.Boilers not clearing faults.System must have air causing an air lock.Bleed air from the boilers and the header.Small amount of air purged.Throttled discharge on HW pump to build up pressure and try force air to the top of the system (where the auto air bleeds are located).After a significant amount of time try to purge the air from the system, it was decided the boilers may require inspecting by Boilertronics.Setup dehumidifiers in the Batavia Gallery and manually controlled the CHW / HW valves overnight.Returned in the AM the following day (Today).HW pump left on over night to try push the air to the auto air bleeds / return normal flow.Purged air from the boilers f
MSA-DCS | WA3890822 | Key watcher boxes -6 boxes not working with the security code and not releasing the keys | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 11:00:10 | 2021-01-09 09:10:00 | Pass | Attended site checked and found customer complaints Keywatcher KWT-3&KWT-4 were showing error message and can’t be logged in to get key. Error message has been reset when technician arrived. And functions of the Keywatcher ps are ok, can’t see the problem. Advised customer to call again if problem happens.
MSA-DCS | WA3890827 | 3 monitor screens for Safe cells are not working | Casuarina Prison-Health Centre Administration | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 12:23:14 | 2021-01-09 10:30:00 | Pass | Checked and found Casuarina CCU 2 workstation frozen, all cameras on three monitors frozen. Tried to restart Indigovision Control Center or soft restart workstation no success. Computer just no response. Need to hard reboot the computer and bring all service back. Tested all ok after work.
MSA-DCS | WA3890831 | Cell B1 -Intercom Not working | Broome Regional Prison-Management Security Section B | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jan 2021 | 2021-01-10 08:35:32 | 2021-01-12 09:15:00 | Fail | found spare cable also only 4 cores working. spliced cable & terminated. tested operation & all is in working order.
MSA-DCS | WA3890833 | main kitchen - refigerator not working | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 12:45:15 | 2021-01-09 10:30:00 | Pass | Arrived to site and accessed kitchen area.Discussed with chef.Checked over system.Found condensing unit not running.Isolated, removed panels.Checked pressure controller and HP switch activated.Tripped due to extreme ambient temperatures.Adjusted HP setpoint slightly higher.Unit started okay.Advised chef and explained findings.Will contact Bandyup Kitchen later today to check on operation.
MSA-DCS | WA3890847 | Control room cameras not working-all the cameras | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 14:29:57 | 2021-01-09 13:00:00 | Pass | Attended site checked and found workstation for video wall is off. After reboot video wall workstation, all cameras are back online on video wall and desktop. More investigation work on video wall workstation will be completed on job WA3890782
MSA-DCS | WA3890867 | cell call unit 6: C10 - not working | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 17:25:07 | 2021-01-09 15:00:00 | Pass | Attended site checked and found Unit6 C10 cell call stuck on remote display but not on cell call console in office. Tried to call C10 in office through console and it work and reset call on remote display. Tested cell call in C10 back to normal after.
MSA-DCS | WA3890868 | YEEDA unit - leaking pipe in ceiling | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 17:28:12 | 2021-01-12 11:55:00 | Fail | Replaced leaking section of pipe.
MSA-DCS | WA3890882 | UNIT 2-CND WING-EXTERNAL DOOR- Not closing. | Melaleuca Prison | GMP-BR- HO | Building | Security Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 18:52:02 | 2021-03-17 17:00:00 | Fail | Investigated door control issues, checked cabling and door control equipment, found doors are designed to keep power on the lock until the door is in the closed position but tongue of lock is not activating for long enough to allow strike to latch. Found that if door is slammed with very extreme force, it actually latches. Liaised with door contractor to inspect and test door. Found door hinges were bent and newly installed rubber seal around door was causing excessive pressure to closing mechanism. Door contractor modified hinges and removed rubber seal. Tested door after mechanical repairs with maintenance officer and door contractor and all is operating correctly. According to door contractor, there is still a defect with door frame causing slight misalignment of tongue to strike. Contractor he will further modify door for perfect alignment.Prison advised they are still having intermittent issues with Unit 2 door control. Reattended site and found read switch on same door a
MSA-DCS | WA3890887 | UNIT 5-A WING 9&10- Toilet leaking, Sewerage leaking into unit. | Casuarina Prison-Prisoner Accommodation Unit 5 | GMP-BR- HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 19:40:07 | 2021-01-09 18:30:00 | Pass | nil
MSA-DCS | WA3890896 | Alert-Gallagher Centre-High temp equip room has changed state to open | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 11:32:00 | Pass | Job completed via phone support
MSA-DCS | WA3890898 | Gate-house: equipment room thermostat has changed | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-28 10:02:00 | Fail | Room reaching high temp a Alarm 30c on days over 45 Aircon need to be addressed system working correctly as intended
MSA-DFES | WA3890851 | Pavement outside the kitchen window, Water leaking from underground up. | CFRS Malaga-Paved Courtyard | GMP-BR | Building | Materials (BU) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 15:22:37 | 2021-01-09 15:15:00 | Pass | 09/01/2021Investigate leak in blue line to copper source part repair test job complete
MSA-DFES | WA3890862 | steel gate front parking lot not working | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Steel Fencing & Gates (BU) | Go Doors | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 16:47:51 | 2021-01-09 14:30:00 | Pass | works completed
MSA-DFES | WA3890869 | External area, Shed - 02 fault roller door, roller door unable to reset. | VFRS Mundaring- TO BE DECOMMISSIONED VFRS Mundaring-External Area | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 17:26:20 | 2021-01-09 15:30:00 | Pass | 09/01/2021, After hours 1515 - 1530Reported that roller door reed is not sealing.On arrival it was working correctly.Checked the reed seems all ok.No issues apparent onsite.
MSA-DFES | WA3890876 | BMS alarm has been activated. High temp alarm. | DFES Cockburn Emergency Services Complex-Main Building-Level 1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 17:53:45 | 2021-01-09 16:10:00 | Pass | Callout for alarms on bms. Found cwp2 on alarm. No faults found, Reset and checked server room temperatures.
MSA-DTWD | WA3890843 | outside tap - unable to turn tap off, gushing water | Joondalup Kendrew Campus-Block D | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 09 Jan 2021 | 2021-01-09 13:48:48 | 2021-01-09 11:30:00 | Pass | nil
MSA-DCA | WA3890935 | A/C unit is leaking from the ceiling in admin 2 office | PICA | GMP-BR | Electrical | General Electrical (EL) | Precise Air Group | 0 | CLOSE | 10 Jan 2021 | 2021-01-10 13:37:55 | 2021-01-10 14:00:00 | Fail | Attended site regarding leaking AC. Found Hitachi Ducted split to have overflowed safety tray and soaked the sealed ceiling. Set point was at 18c and it had been left running over night. Also p trap was blocked and virtually inaccessible for maintenance. Removed p trap and safety tray drain run and flushed, reassmbled and test ran, all ok. Due to damage to ceiling and potential for it to collapse in I've let Reese Whitney from Programmed know they need builder to attend asap and I've closed the room to staff until the ceiling gets repaired.
MSA-DCS | WA3890929 | SITE COST Cell 9-Cell door unable to Lock | Wooroloo Prison Farm-Prisoner Accommodation Unit 3 Block 2 & Ablutions | WSM-BR-SITE | Building | Doors (BU) | ACE LOCK & SAFE | 0 | CLOSE | 10 Jan 2021 | 2021-01-10 13:21:29 | 2021-01-10 12:15:00 | Pass | Repaired damaged lock on Cell 9 Unit 3 Wooroloo Prison farmLock rekeyed , deadlatch replaced as well as door frame strike .
MSA-DCS | WA3890937 | SITE COST Unit 2 Cell B7 - the prisoner key lock is jammed, key stuck on the door and won't open | Melaleuca Prison | WSM-BR-SITE | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 10 Jan 2021 | 2021-01-10 13:55:38 | 2021-01-11 09:15:00 | Fail | Attend site after hours. Required to replace strike on cell door main lock. Reattend site following day to install.
MSA-DCS | WA3890951 | SITE COST UNIT 13- Computer screens that control access to units are not working. | Casuarina Prison-Prisoner Accommodation Unit 14 | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jan 2021 | 2021-01-10 14:50:35 | 2021-01-10 13:15:00 | Pass | Attended site checked and found Unit 13 EBI and CCTV Monitors are blank. Further check located the EBI workstation is down. Restart EBI workstation and bring access control service back online. Also bring all cameras back onto Indigovision Monitors.
MSA-DCS | WA3890969 | MPC cell not recording - camera | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jan 2021 | 2021-01-10 17:54:49 | 2021-01-11 12:30:00 | Fail | Found issue with user passwords and logins reset security admins passwords and tested all ok all cameras recording and no video loss
MSA-DCS | WA3890976 | No power on site. Lifts, garage door and computers don't have power. | East Perth | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 10 Jan 2021 | 2021-01-10 20:10:46 | 2021-01-10 19:30:00 | Pass | Restored power to site.
MSA-DCS | WA3890981 | Wooroloo Prison Farm - Gatehouse Comms Room - Airconditioning units are not working properly. | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 10 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-18 12:08:00 | Fail | COMPLETED
MSA-DCS | WA3890982 | GATEHOUSE - PIT TEMPER FAULT - ZONE P35 SENSOR | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-22 12:45:00 | Fail | Cabling repairs and replacement of connections retested ok.
MSA-DCS | WA3890986 | Perimetre fence - Response road gate not responding to computer commands. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jan 2021 | 2021-01-11 02:28:01 | 2021-01-11 15:30:00 | Fail | Confirmed cable between Gatehouse control equipment and Gate controller intact as Lock pin is operating as required, though gate not opening. Referred to Maintenance for the attention of Gate technician.11/01/2021 14:30. Assisted AFD with access to gate and allignment testing.
MSA-DCA | WA3895391 | light fitting coming away from ceiling rose | PICA-Main Building-Level 1-Administration Office 2 | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 10:00:00 | Pass | Investigated hanging light due to water leak, old fixings were too small and because ceiling got wet they fell through, refixed light with larger fixings and holds up fine. Ceiling will not be as strong as it originally was so there is a potential that the problem could happen again and fixing could fall through would recommend replacing the gyprock or replacing fluro to a lighter plastic fitting.
MSA-DCA | WA3895493 | Zones 1 & 14 - Reticulation leak | Perth Cultural Centre Precinct - Museum Plaza (James Street) | GMP-BR | Plumbing & Drainage | Water (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 10:45:00 | Pass | Repairs to sprinklers
MSA-DCA | WA3895494 | Leak in ceiling space please investigate | PICA-Main Building-Level 1-Administration Office 2 | GMP-BR | Building | Ceiling (BU) | ICS Australia | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 12:41:00 | Pass | Investigated and applied glue to ceiling joists
MSA-DCA | WA3895686 | L1 Clay’s Office and surrounding offices AC in Clay’s office is not working. - see notes | Collection and Research Centre Welshpool-Administration and Library Building-Roof Level-Rooftop Plant - Above Administration | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-18 10:00:00 | Fail | Attended site. AC system not operating correctly. Applied tests and checks to find HP transducer defective. Ordered applicable parts via Temperzone Australia. Awaiting parts to arrive. Picked up parts from company workshop. Reattended site 0800 18-1-21. Removed and replaced defective transducers, cabling and HP sensors. Tested system operation. System operating correctly. Left site 1000 18-1-21.
MSA-DCA | WA3895753 | Reception lighting track blown | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-03-16 09:30:00 | Fail | Investigated track lighting not working, tripped rcd at dynalite board, once circuit was back on 3 out of 3 of the led lights were not operating still, checked all contactors and dynalite channels and all are working correctly, voltage present across both circuits inside track light but 3 individual lights on the track were blown.Will need to replace 3 of the leds with new.See photos attached for model of LED and style.Ordered new parts and picked up once arrived .Replaced all 3x blown led track lighting, tested for correct operation and direction of light across the admin desk.
MSA-DCS | WA3895190 | Cool room failure and chiller not working | Karnet Prison Farm-Dairy Cool Room | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 11 Jan 2021 | 2021-01-11 09:14:17 | 2021-01-11 12:00:00 | Fail | found faulty motor capacitor , pick up part and replace. Left system operational.
MSA-DCS | WA3895285 | Site wide - PDA is not activated when press ,Multiple failure | Broome Regional Prison-Gatehouse Administration | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jan 2021 | 2021-01-11 14:48:38 | 2021-01-11 15:30:00 | Fail | Attend site,checked with officers & after they rebooted MDAS is ok. checked MDAS log, tr6 had comms failure on bus line. stress tested but all is ok. tested 11/1 & 12/1/alarms work fine
MSA-DCS | WA3895319 | L2 computer room cannot log into security system | East Perth | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jan 2021 | 2021-01-11 11:17:45 | 2021-01-11 08:51:00 | Pass | Attended siteLocated site credentials for the security system (CCTV)Logged into the CCTV systemFound camera spot monitor locations movedRe-allocated video feeds to correct positions on the spot monitorChecked all okLeft site
MSA-DCS | WA3895326 | Unit 13 - B9 blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-15 09:30:00 | Pass | nil
MSA-DCS | WA3895333 | Unit 4 - D11 Cell tap turns but no water comes out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 11:30:00 | Pass | Nill
MSA-DCS | WA3895340 | Reception - South Water leak coming through the ceiling of long holding cell (near light) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-13 17:00:00 | 2021-03-23 12:00:00 | Fail | 14/1 notes: will need a job raised for Hellwig a to remove a light in roof so we can access and repair pipe , willBe organised with casuarina maintenance Works have been arranged and booked in with maintenance, security and Hellwig electrical for Tuesday 2/1/21 8:30am23,3,21. Completed burst pipe at high level in corridor.Repalce section off pipe work Hellwig electrucal disconnected power supply to lights.
MSA-DCS | WA3895342 | INF (10) - Cell Call B9 not working. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 14:00:00 | Pass | Tested cell call. Press button not initiating call. Drilled out retaining rivets, removed cell call, connected RJ45 adaptor and cell call, tested to Local Control. Good audio both ways, fixed cell call into apatite & secured with rivits.
MSA-DCS | WA3895345 | SOG Pod Screens are blank with unable to connect message on screen. - see notes | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jan 2021 | 2021-01-11 11:37:51 | 2021-01-11 10:30:00 | Pass | Attended control room. On arrival noted workstation for GLU's 15-18 was on and operational. Video for cameras showing on-screen when selected. No fault found.
MSA-DCS | WA3895350 | Unit 13 - A2 Cold water tap on sink jammed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 08:30:00 | Pass | Nill
MSA-DCS | WA3895358 | unit 3 D wing grille faulty as of 1745hrs, needs repairing | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 07:45:50 | 2021-01-11 14:00:00 | Pass | 11/01/21Unit 3 D wing grille - fixed limit head and replaced fuse.Grille door running.
MSA-DCS | WA3895366 | Unit 5 Cell C 9 the water from the sink overflowing on to the floor in the cell. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-11 15:30:00 | Pass | Nill
MSA-DCS | WA3895379 | Unit 13 - B6 Personal bed light in cell B6 not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-14 08:30:00 | Pass | Replaced faulty lights switch in unit 13 b6
MSA-DCS | WA3895383 | Unit 14 - B2 C eiling panel above B02 in the wing buckled inwards- see notes | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 12:30:00 | Pass | RE FIXED CEILING PANELLING
MSA-DCS | WA3895385 | unit 7, H wing dayroom - cold water tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 10:00:00 | Pass | Replaced broken tap
MSA-DCS | WA3895389 | unit 9, b6 - Viewing Hatch glass smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 08:09:45 | 2021-01-11 12:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3895394 | unit 8, A/B Wing - Light Fitting broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-03-02 15:00:00 | Fail | Replaced broken lights.
MSA-DCS | WA3895399 | unit 1, A4 - Cell call very loud & distorting what is said | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 08:15:19 | 2021-01-11 10:45:00 | Pass | Adjusting the volume on the cell call helped with the clarity in the control room but not in the cell. Removed original plug to accommodate the new style intercom. Tested loud and clear in the cell and in control.
MSA-DCS | WA3895412 | unit 1, C14 - Main lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 08:17:15 | 2021-01-11 11:25:00 | Pass | Attend site to damaged lock in unit 1. Replace bolt throw.
MSA-DCS | WA3895413 | Unit 14 - A6 No water pressure, water is dribbling out from this cell from tap and shower. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 10:30:00 | Pass | Nill
MSA-DCS | WA3895423 | Edvoc 2 comms cub - No power to comms rack | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 13:00:00 | Pass | Attended site and checked power to comms rack in ED VOC 2.There is power and security equipment is online
MSA-DCS | WA3895429 | Unit 1, C10 - Top Bunk Cell Call Not Working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 08:34:50 | 2021-01-11 15:00:00 | Pass | Traced fault to the CALL2 terminals on the bottom bunk intercom. Replaced intercom. Reset U1 CI-3210 to clear C10 tamper alarms. Tested C10 top and bottom bunks. Both tested ok. Parts taken from PFM stockPFM stock replaced with new
MSA-DCS | WA3895442 | Unit 5 Valve won't shut off requires replacement | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 10:30:00 | Pass | Found 3 faulty valves and replaced all 3
MSA-DCS | WA3895452 | Gymnasium, Front Entrance - Broken Wire to STN 27(Requires Tracker.) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 13:30:00 | Pass | located broken wires on system and repaired.
MSA-DCS | WA3895465 | Unit 5, 2x C wing showers are not working they are either blocked or the spindles have broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-18 15:30:00 | Fail | Nill
MSA-DCS | WA3895501 | Unit 3, Cell B1- Flusher buttom jammed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-25 14:30:00 | Fail | Nill
MSA-DCS | WA3895502 | Unit 3, Cell D7- Toilet flushing but not draining/flooding | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-21 13:30:00 | Fail | Nill
MSA-DCS | WA3895569 | Turner C wing HWU leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 10:14:54 | 2021-02-03 05:54:00 | Fail | BRAF declined, close off work order as is
MSA-DCS | WA3895600 | ground A wing training cells Door locks on training cell doors are faulty. | Nyandi Training Academy | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-27 10:30:00 | Fail | Attend site to service cell locks in cell wing A Date on site: 15/1/21Time on site: 1030 - 1530Re-attend site to finish servicing locks in cell wing ADate on site: 27/1/21Time on site: 0900 - 1030
MSA-DCS | WA3895601 | Control, Internal F1 alarm no camera activation | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jan 2021 | 2021-01-11 18:34:39 | 2021-01-12 17:00:00 | Fail | Reset controllers associated with CCTV and inputs. See Sig slip and work logs for details.
MSA-DCS | WA3895602 | Disconnect 3 phase HWS and energise PowerPoint for Sea Container freezer connection. See notes below | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 1 - Kitchen Area | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 10:30:00 | Pass | Reconnected hws
MSA-DCS | WA3895627 | Unit 1, Cell 1&2 c/d wings - Vesda faulty - false alarming | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 10:48:38 | 2021-01-11 13:12:00 | Pass | Complete
MSA-DCS | WA3895628 | Unit 8, Cell C12- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 13:00:00 | Pass | Replaced light switch
MSA-DCS | WA3895643 | unit 1 B15 toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 10:57:09 | 2021-01-11 16:40:00 | Pass | Unblocked toilet. Apple stuck in tbe pan collar
MSA-DCS | WA3895651 | Unit 2, Cell B11 - Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 09:30:00 | Pass | Nill
MSA-DCS | WA3895710 | laundry workshop Dryers 3 and 4 not reaching the temperature showing on control panel | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 11:29:43 | 2021-01-12 13:45:00 | Fail | Breakdown - AMS754688 - WA3895710 - laundry workshop Dryers 3 and 4 not reaching the temperature showing on control panelDryer #3 - fuse blown, elec test, no fault found supply and fit fuse. Tests ok.Dryer #4 Inspect and test dryer, Suspect low gas pressure, staff to monitor dryer
MSA-DCS | WA3895719 | main chlorine plant at front of prison sample line faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 16:00:00 | Pass | COMPLETED
MSA-DCS | WA3895732 | medical center toile blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 11:52:21 | 2021-01-11 21:10:00 | Pass | Unblcoked sewer line in the disabled toilet
MSA-DCS | WA3895756 | Unit 1, D11 - Fault description Toilet Pan Seals Leaking into the Shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 12:11:08 | 2021-01-11 18:50:00 | Pass | Replaced leaking seals at the toilet and flush pipe.
MSA-DCS | WA3895771 | Medical Centre- staff room zip unit not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 12:26:10 | 2021-01-14 13:45:00 | Fail | Replaced pump.HOT PUMP TO ZIP HYDROTAP J11461
MSA-DCS | WA3895774 | Unit 6, Cell 12- Exhaust fan faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 13:30:00 | Fail | Replaced exhaust fan
MSA-DCS | WA3895776 | Unit 6, Cell 9- double GPO switch plate damaged not mech | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 14:00:00 | Fail | Replaced cracked light switch
MSA-DCS | WA3895777 | Reception, property storeroom- 6x lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-21 10:30:00 | Fail | Replaced 6x LED batten lights
MSA-DCS | WA3895778 | Unit 2, Cell B1- Bunk light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 14:30:00 | Fail | Replaced bed light fittings and switch
MSA-DCS | WA3895781 | Unit 5, House 4- 2x rangehood lights missing | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 15:30:00 | Fail | Replaced range hood globes
MSA-DCS | WA3895783 | Unit 5, House 7, Bedroom 3- fan switch faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-21 12:00:00 | Fail | Replaced ceiling fan in bedroom
MSA-DCS | WA3895784 | Unit 5, House 2, Bedroom 3- fan switch faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-21 13:30:00 | Fail | Replaced ceiling fan in bedroom
MSA-DCS | WA3895785 | Unit 5, House 7, Oven not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-21 14:30:00 | Fail | Replaced damaged oven
MSA-DCS | WA3895787 | Unit 5, House 5, Hot plate not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-02-22 09:00:00 | Fail | Replaced cracked cook top
MSA-DCS | WA3895789 | Unit 5, House 4, Microwave GPO not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 16:00:00 | Fail | Replaced faulty powerpoint
MSA-DCS | WA3895796 | Common room door - Flyscreen entry door can not be locked | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 10:00:00 | Pass | Replaced damaged lock on Security screen Door Unit 2B - Pod 4
MSA-DCS | WA3895816 | Hotham, Cell A03- Cell door bottom main lock difficult to lock by most unit staff keys | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 12:48:12 | 2021-01-11 14:50:00 | Pass | Serviced main lock on Hotham A3.
MSA-DCS | WA3895835 | SOG Pod- Tap on basin is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-02-17 13:30:00 | Fail | Nill
MSA-DCS | WA3895840 | SOG Pod- Response Road perimeter fence gate fails to open and close and also does not secure | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 12:57:31 | 2021-01-11 15:15:00 | Pass | 11/01/21Internal perimeter gate - adjusted limits as limits were not contacting
MSA-DCS | WA3895863 | Unit 10, C/D wing - hot water tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 08:30:00 | Pass | Replaced corroded spindle
MSA-DCS | WA3895874 | oval - Point post snapped off at ground level | Banksia Hill Detention Centre | GMP-BR- HO | Recreation | General (RC) | Midolo Building Services | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-04-01 12:00:00 | Fail | Replaced posts
MSA-DCS | WA3895883 | kitchen sink - sink tap faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-12 08:15:00 | Pass | COMPLETED
MSA-DCS | WA3895914 | Jeelia, C wing, C02 - Cell light switch (Ceiling light) not functioning . | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 13:48:18 | 2021-01-12 10:15:00 | Pass | Replaced momentary switch in cell, test ran ok.
MSA-DCS | WA3895916 | Unit 7, Cell C9- Window not staying open, struts broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 09:30:00 | Pass | SPIRAL BALANCES RE NEWED - MINOR FRAME REPAIR
MSA-DCS | WA3895933 | Kitchen- Air Con constantly trips out | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-07-08 10:30:00 | Fail | Complete
MSA-DCS | WA3896130 | Male toilets- Blocked drain in urinal | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 12:45:00 | Pass | Arrived on site and inspected found the urinal trout blocked. Used plunger and sprites of salts to clear the blockage. Tested multiple times all working in order.
MSA-DCS | WA3896138 | Staff Lunch Room- Faulty/broken panel ceiling light | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 12:25:00 | Pass | Repaired light in staff lunchroom
MSA-DCS | WA3896143 | Ground floor, Central office - Gap under rear door of building, missing weather strip | Midland (North East Metro) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 12:00:00 | Pass | Supplied and installed weather seals to the bottom of all external doors.
MSA-DCS | WA3896154 | Gatehouse, control room - zone 13, fence alarm unable to be cleared | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 15:53:37 | 2021-01-12 10:46:00 | Pass | Found video wall pc to be frozen, restart machine, save log files to further investigate why machine froze in the first place. Machine does seem to be warm. Adjust all 3 monitor outputs from 1920x1280 to 1280x720. Test multiple cameras on screens, resolution to the naked eye is not affected. This will create less load on machine. Have spoken to seme supervisors and will follow up with possible new machine as issue is constant. Machine and video wall is all currently ok and working. Control room also asked to check camera 34 and 35 camera tampers, they can not be clear d via senstar. Check cabinet at zone 14/15 cabinet, cameras visually look ok (up high), control equipment ok, reboot cameras, fault still there. Will need to follow up with camera tampers once I have some tech support from senstar.
MSA-DCS | WA3896158 | Control Room- Lost monitors | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jan 2021 | 2021-01-12 00:22:47 | 2021-01-11 17:03:00 | Pass | Reset and test monitor alarms. All ok.
MSA-DFES | WA3895408 | Rear engine room, Roller doors #3 - not coming down | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 11:30:00 | Pass | Attended Duncraig Fire Station. Checked Bifold Door 3 and found that the PE beams were out of Alignment. Re adjusted PE Beams and tested door. Door now works fine. Please refer to the attached service report.
MSA-DFES | WA3895748 | 2nd floor, male toilets - 4th cubicle is blocked | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 13:45:00 | Pass | Cleared toilet on 2nd floor male toilets plunged and cleared the blockage tested
MSA-DFES | WA3895993 | external door at end of passage way west end door not locking | CFRS Ellen Brook | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 10:30:00 | Pass | Work completed
MSA-DFES | WA3896041 | maintenance of work shop floor air con leaking | Fleet Management Services - O'Connor Workshop | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 15:00:00 | Pass | Travel to site. Sign in and access AC 15 leaking water. Isolate unit and dismantle. Drain excess water from unit. Disconnect unit drain and found to be clear. Found blockage to be in exit of unit drain tray. Clear blockage from drain tray. Reconnect drain and test operation. Run water through drain and found ti drain out as normal. Run 3 ltrs of water through unit and found to drain freely. Reassemble unit and deisolate. Turn on unit and test operation, working ok.
MSA-DTAG | WA3895447 | Registry Area - No water pressure when using hot and cold taps in kitchen/bathrooms | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 10:30:00 | Pass | Complete
MSA-DTAG | WA3895490 | 1903 external A/C unit copper drain pipe has detached from the north east elevation wall | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 10:00:00 | Pass | Attend site. Access side of building with copper pipe pulled off wall. Copper pipe is old drain from previous room airconditioning units mounted in window. Use safety bunting to block of work area. Access copper pipe and remove unsecured section. Remove old saddles from wall.
MSA-DTAG | WA3895845 | Female public tiolets is blocked and unable to flush, has currently overflown | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 14:05:00 | Pass | COMPLETED
MSA-DTAG | WA3895910 | L9 R9.3 Special COVID 19 clean required - see notes | Central Law Courts | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | OCS SERVICES PTY LTD | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-11 20:00:00 | Pass | Job completed - Coronavirus Special Clean
MSA-DTAG | WA3896099 | Ceiling of Custody - smell coming from ceiling | Mandurah Courthouse | GMP-BR-HO | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-15 09:40:00 | Fail | The ceiling of custody area odour coming from the ceiling.
MSA-DTAG | WA3896159 | Ground Floor & 2A- Front Court registry has lost power, emergency lighting appears to be on. | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 11 Jan 2021 | 2021-01-11 20:41:55 | 2021-01-11 20:10:00 | Pass | Xavier attended site on 11/01/21 from 6pm, waited to get access to site for 45min, once on site checked and tested all the power to Level 2, tested all electrical switchboard and found main isolater for DB2 was tripped off. reset and rechecked all power. no other faults were found everything back on and to normal.Informed site.
MSA-DTWD | WA3895431 | Canteen kitchen - Pendant GPO has a cracked housing that requires replacement; | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 15:15:00 | Pass | Attended site and signed in. Got keys from reception. Located canteen kitchen. Found broken gpo for fridge. Disconnected and removed faulty outlet. Supply and replace with new pendant gpo. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3895513 | L1 Chalk and cheese cafe Reseal and repaint damage wall | Perth Campus B2 | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 11 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 13:30:00 | Pass | Work completed
MSA-DTWD | WA3895555 | F block Fire alarm fault intermittent | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-05-05 08:25:00 | Fail | F BLOCK FIP FAULTRESET PANEL-ALL CLEARMONITORING FAULT-HAS NOT RETURNED-ALL GOODCOMPLETED
MSA-DTWD | WA3895584 | Building opposite to red building - external door deadlock damaged | West One Services | GMP-BR | Security | Locksmith (SE) | DIAMOND LOCK AND KEY | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-12 14:00:00 | Pass | DescriptionMichaella Petrov signed MSA Authorised Sign OffRoad JobDate of Attendance:Locksmith completed the following :Supply and install 201 cylinder with 2 x new keys. Also refit lock found onsite as it had been brokenoff.
MSA-DTWD | WA3895665 | Bike shed - roller door lock swipe card access damaged broken | West One Services | GMP-BR | Security | Access Control (SE) | Casa Security Pty Ltd | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 14:00:00 | Pass | Advised that a separate electronic lock required
MSA-DTWD | WA3895812 | H block machinery shed Roller door will not stay down so unable to lock up shed | Mandurah Campus (formerly Peel) | GMP-BR | Building | Doors (BU) | UNIVERSAL DOORS | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-01-11 14:15:00 | Pass | ATTENDED SITE TO INSPECT & REPAIR THE REPORTED FAULTY ROLLERDOOR, RESET TRAVEL LIMITS, CHECKED OPERATION, ALL OK.
MSA-DTWD | WA3895919 | Block 4, Ground floor plant room- A/C not working | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 11 Jan 2021 | 2021-01-12 17:00:00 | 2021-03-19 16:30:00 | Fail | Attended site, found both stages of the ground floor aircon at block 4 had no had , braf being sent.Found gas leak on stage 1. repaired leak on suction line valve. charged with nitrogen and pressure tested unit and charged with 8kg of R407A Refrigerant.Stage two found leak on tx valve. replaced tx valve and charged with nitrogne to pressure test. charged with 8kg of R438A regrigerant.Please note unit is approx 20 years old and should be replaced2 x Nitrogen2 x Big Blue
MSA-MRWA | WA3895621 | Fluorescent Light fitting not working, please remediate before hours 6 and 7 am. | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-833-Office | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 11 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-12 07:00:00 | Pass | Attended site and signed in. Located level 8 room 33. Found fluro over desk to not be working. Replaced tubes and still didn’t work. Supplied and replaced electronic ballast. Retested and all okay. Signed out job complete
MSA-DCA | WA3901267 | FCU no 6 is leaking- WAMS technicians already on site attending to this issue | Shipwreck Galleries-Main Building-Level 1-Library | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 08:00:00 | Pass | Attended site. FCU 6C leaking water. Applied tests and checks. Investigation found main gravity fed drain blocked. Isolated system and removed excess water with wet/dry vaccum. Cut and cleared drain, replaced p-trap and primed p-trap. Tested drain flow (ok). Carried out rust treatment to CHW V emergency drain tray and insulated CHW valve pipework. Allowed paint to dry. To reinstate FCU tomorrow morning. Returned to site. Reinstated FCU. Completed tests and checks. System operating correctly.
MSA-DCA | WA3901309 | please isolate smoke detectors/smoke beams in atrium due to cleaning works | King Street Arts Centre-Main Building-Ground Floor | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-13 16:30:00 | Pass | 07:30 Isolated atrium and adjoining corridors for cleaning16:00 Deisolated all isolated zones on FIP and returned to normal
MSA-DCA | WA3901636 | Level 4 plant room, boiler 1 has faulty high temp cable | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 16:36:00 | Pass | Contractor replaced faulty HT Probe cable on 12-01-2021 while on site for PM.Closed job.
MSA-DCS | WA3899808 | gate house keywatcher key bunch 30 stuck in key cabinet | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 07:23:11 | 2021-01-12 12:30:00 | Pass | Restart relay board to relay bank with key 38, test multiple times, all ok, sees it slip for more notes.
MSA-DCS | WA3900539 | internal Permatrax zone 2 and 3 internal MW zone 3 not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 09:30:00 | Pass | Sourced replacement SM1000-1 from PFM stores. Replaced SN2Sm2 in EC1. Module powered up ok. Zone 3 microwave ok in the field. Zones 3 microwave internal, 3 microwave external and 3a internal Perimitrax tested ok. Parts used:48VDC power supply MEANWELL NDR-240-48
MSA-DCS | WA3901045 | Unit 4/3 yard - Concrete slab needs repair where it has been removed by a plumber - see notes | Hakea Prison | GMP-BR- HO | Building | General Building (BU) | Midolo Building Services | 2 | CLOSE | 12 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-20 15:00:00 | Fail | RE NEW CONCRETE FLOOR
MSA-DCS | WA3901060 | pre release unit personel and double gates intermittent opening/closing | Bunbury Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 09:45:00 | Pass | AFD contacted onsite and the confirm they have job to repair and have ordered parts.
MSA-DCS | WA3901066 | Unit 6 - B5 water leaking through vent from cell above | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 15:30:00 | Pass | Nill
MSA-DCS | WA3901071 | B06 in Unit 14 has a leaking shower head and minimal pressure from basin tap. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 11:30:00 | Pass | Nill
MSA-DCS | WA3901093 | laundry ipso 10kg washing machine making grinding sound in the back | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-21 13:00:00 | Fail | Noise from shock absorbers. To be replaced. Replaced 21/1/21 OK
MSA-DCS | WA3901105 | unit 5 control office air con leaking water near GPO | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 08:15:35 | 2021-01-12 14:30:00 | Pass | Awaited guard in entry building.Accessed unit 5 control.Found A/C running and leaking.Isolated.Removed covers.Leaking from left side secondary drain bung.Reseated.Still leaking from corner.Possible small crack in plastic in drain section.Unit running okay.Measuring up for replacement as we have been to this prior regarding water leaks.
MSA-DCS | WA3901111 | pedestrian gate, Safety IR beam is not working | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-14 09:24:00 | Pass | AFD has job and parts ordered. They are replacing the hardware.
MSA-DCS | WA3901121 | Unit 14 - B & D Water fountain B/D wing smashed - Parts are in the Maintenance Office | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-02-25 08:28:00 | Fail | 16/2 : new bottle filler tap and puller tap have arrived and now in our sea container, just waiting for the cover to arrive in order to complete works.
MSA-DCS | WA3901147 | A3 Door is Dragging on the floor | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-12 13:30:00 | Pass | Carried out repairs to cell door hinges
MSA-DCS | WA3901158 | PIR unit 3, outside cell 21 - constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 08:50:38 | 2021-11-05 08:00:00 | Fail | Check operation of unit 3 pir outside cell 21 ok.
MSA-DCS | WA3901163 | Unit 3, PIR outside cell 05 - constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 08:56:17 | 2021-08-04 16:00:00 | Fail | Trace fault, rectified and fixed fault. Job completed.
MSA-DCS | WA3901166 | Unit 2, PIR outside cell 09 - constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 08:58:09 | 2021-01-15 10:30:00 | Fail | replaced pir & tested ok.
MSA-DCS | WA3901171 | Unit 2, PIR - shows on screen as unit 2, cell 09 unit manager 2 - no actual PIR in area | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 08:58:52 | 2021-01-13 16:30:00 | Fail | deleted from site plan
MSA-DCS | WA3901174 | PIR outside Unit 1, cell 15 - is currently not showing on screen | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 09:00:59 | 2021-01-14 12:30:00 | Fail | located pir, configured on Gallagher site plan. tested ok
MSA-DCS | WA3901180 | Zone 10 mircowave, transmitter 19 - alarm showing it is shunted (microwave working alarm wont clear) | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 09:03:15 | 2021-01-14 11:00:00 | Fail | investigated alarm issue, realigned & adjusted unit. reterminated connections. tested ok.
MSA-DCS | WA3901183 | A Wing, Cell 12- Hot & Cold tap faulty | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-19 08:59:00 | Fail | Arrived on site and inspected found the the cold tap handle broken. Tap leaking. Traced the cold isolation. Could not trace hot isolation. We will come back tomorrow to investigate further Returned to site and traced hot water pipe and isolation. Serviced the spindles. Went to supplier to get the tap handles. Found the parts are obsolete. Need to order new tap set from supplier Collected the parts from supplier. Returned to site fitted the new spindles. Flange were not fitting. Need new flanges. Collected parts from supplier and returned to site. Installed new flange and tested all working good.
MSA-DCS | WA3901189 | Zone 1, inferred - Constance alarm | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 09:11:50 | 2021-08-19 16:30:00 | Fail | Replaced defective IR BEAMS and aligned.job completed.
MSA-DCS | WA3901190 | Zone 1B, Microwave, transmitter #2 - reading as open circuit and tamper | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 09:13:31 | 2021-01-15 09:30:00 | Fail | realigned tx & rx units, tested ok.
MSA-DCS | WA3901192 | Zone 1, gate inferred - showing open circuit and tamper | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 09:14:34 | 2021-01-15 12:30:00 | Fail | resoldered terminal & resealed tamper. job complete.
MSA-DCS | WA3901193 | Zone 4, Omintrax - constant activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 09:15:58 | 2021-08-03 14:30:00 | Fail | Attended site and repaired omnitrax faults, calibrated and monitored for correct and stable operation.Tested OKJob Complete
MSA-DCS | WA3901224 | Unit 2, Cell A1- Sink cold tap leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-14 09:40:00 | Pass | Replaced spindle for leaking cold tap in basin. Work disrupted by lockdown of prisoners.
MSA-DCS | WA3901231 | Unit 2, Cell B6- Sink cold tap leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-14 11:51:00 | Pass | Replaced spindle for cold and hot tap in basin
MSA-DCS | WA3901236 | Unit 2, Cell B3- Double GPO Mech Broken | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-13 11:30:00 | Pass | Replaced faulty gpo with a new one, test ran ok.
MSA-DCS | WA3901246 | Unit 2, Cell D16- Prisoners Lock jamming in door | Melaleuca Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-13 10:50:00 | Pass | Replace lock on unit 2, D16.
MSA-DCS | WA3901254 | unit 2 B13 Shower Tap leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-14 14:45:00 | Pass | Replaced leaking cold tap in shower with like for like quarter turn spindle
MSA-DCS | WA3901273 | A-Wing cell 7 - Repair faulty lights in training cell 7 | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-12 11:00:00 | Pass | Repaired lighting of cell 7
MSA-DCS | WA3901277 | Control Pod, CCTV cameras are frozen | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 10:20:31 | 2021-01-12 13:15:00 | Pass | Restart dvm machine, test, all ok. See sig slip for more notes
MSA-DCS | WA3901322 | control MDAS transponder 9 unit 2 tamper alarm | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-12 12:00:00 | Pass | Found cabinet door on Transponder cabinet had dropped, causing microswitch armature arm to be out of allignment. Adjusted door to realign microswitch armature.
MSA-DCS | WA3901335 | Control, MDAS admin low battery | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-12 13:30:00 | Pass | Removed failed battery, installed replacement, tested for charging, and confirmed alarm cleared on MDAS workstation.
MSA-DCS | WA3901358 | Oval - speakers are very faint - not hearing any announcements over the speakers - PA system | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-21 13:00:00 | Fail | Replace amplifier, source 3 pin XLR plug and solder to input cable. 2 x technician test to set up amp config/volume to oval speakers. Speaker volume and quality greatly improved.
MSA-DCS | WA3901420 | Base of security fence has gaps and needs to be fixed to Harding Yard (ISU) | Banksia Hill Detention Centre | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-13 11:00:00 | Pass | 13/01/21Tied over the lacing every 2nd diamond to secure mesh to Harding yards
MSA-DCS | WA3901459 | INF (10)- Service duct between C1 & C2 has a leaking water pipe. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-15 08:30:00 | Pass | Nill
MSA-DCS | WA3901527 | Level 2, open plan area - lower 2 workstations that were previously raised on blocks | East Perth | WSM-BR-SITE | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-18 12:00:00 | Pass | Attended site and carried out modifications to workstations on level 2
MSA-DCS | WA3901536 | 3rd house on the left front tap leaking - please call Jim for exact location | DCS - 6 Driscoll Drive Canning Vale | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 12:00:00 | Pass | Capped off two tap outlets
MSA-DCS | WA3901603 | Unit 6, C/D wing - camera screens not working, since power failure since last night | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 14:33:44 | 2021-01-12 16:36:00 | Pass | HP client cannot see WS. WS located and booted. All ok.
MSA-DCS | WA3901607 | Unit 4, Cell A4- Toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-21 14:30:00 | Fail | Nill
MSA-DCS | WA3901664 | Interview room 3, swipe card reader faulty | Rockingham Justice Complex | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 15:26:06 | 2021-01-13 10:00:00 | Pass | Attended site and checked Gallagher system, all tested and working ok, issue found with electronic lock stuck. Resetpower and lubricated lock. All retested and working ok.Job completed
MSA-DCS | WA3901688 | Zone 4 Perimetre microwave constantly alarming. | Bandyup Prison-Unit 6-Ground Floor-Control Room | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Jan 2021 | 2021-01-12 21:30:00 | 2021-01-12 21:00:00 | Pass | Attended site and investigated the fault.Checked MW zone 4 for any obstruction.Checked power and connections on microwave sets in zones 4A and 4B.Found loose connection - resecured and conducted test.(Used sundries)All Ok at departure.
MSA-DCS | WA3909006 | RETROSPECTIVE WORK ORDER - Assist plumbing contractor in repairs post flooding - see notes | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 12 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 13:21:00 | Pass | Arrived onsite and had to wait for the plumber as they were not starting til 830 so got in at 9.Attended site to Isolate and remove smoke detector in Yeeda block laundry boiler cupboard to allow ceiling to be removed for plumbers to carry out leak repairs. Plumber was no onsite until 8:30.Ceiling replaced - Re-install detector and de-isolate.
MSA-DFES | WA3901675 | The water meter has been run over and the water cannot be shut off to the property- see notes below | VFRS Falcon | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 12 Jan 2021 | 2021-01-12 20:12:59 | 2021-01-13 14:31:00 | Fail | Attended delayed by fire in Kwinana arrived after hours searched area all around station could not find leak at water meter, called all local stations but got no advice re a leak there. On return route checked in at Greenfields no leaks there either.
MSA-DTAG | WA3901110 | Registry / Counter Area Flickering light in counter area | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 16:30:00 | Pass | Attended site and signed in. Located flickering light in reception. Got approval to work. Used big ladder to access light fitting. Replaced tubes and starters. Clean and tidy site. Signed out. Job complete
MSA-DTAG | WA3901197 | L10 camera not working on vision software indicating yellow as green | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-12 13:30:00 | Pass | Attended site and checked system. Reset Milestone software as was not communicating with Unison software. Reset andall retested ok. Turned off services to the slave PC as may be causing issues. Tested and L10 camera all working ok.Job completed.
MSA-DTAG | WA3901199 | L6 room 603 alarm off | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-12 13:30:00 | Pass | Reset system and cleared all alarms. All tested and working OK.
MSA-DTAG | WA3908994 | RETROSPECTIVE WORK ORDER - Garage AirKey remote for Sue Smith not working - ATT 12/1 | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Keys & Access (SE) | Sapio Pty Ltd | 3 | CLOSE | 12 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 09:00:00 | Pass | Reprogrammed airkey for Sue Smith.Job completed.
MSA-DTWD | WA3898111 | B block L2 B208 Male toilet tap is leaking / B209 male flush button jamming | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-18 11:15:00 | Pass | Arrived on site and inspected found the the outlet valve stuck. Ordered parts from supplier. Inspected the tap the aerator is missing. Will come back with parts. Collected parts and returned to site. Fitted the aerator to the tap. Tested all working good. Removed the faulty cistern and installed new cistern. Tested all working good
MSA-DTWD | WA3901196 | N Block, Outside Fence- Colorbond fence panel has been kicked in leaving area unsecured. | Midland Campus | GMP-BR | Building | General Building (BU) | AWB Co. | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 17:30:00 | Fail | The fence panel was heavily dented, and some of the corners were bent. These corners were straightened.The top profile was unscrewed, and lifted out of position to allow the fence panel to be refitted.The top profile was fitted, and all hex screws put back in place.The fence could do with be replaced due to damage, so sizes were taken to purchase a new panel.The fence is now secure.
MSA-DTWD | WA3901203 | print/side office HW urn leaver rusty and broken | West One Services | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-13 13:15:00 | Pass | Replaced broken tap. Replaced filter.
MSA-DTWD | WA3901209 | Science Block Male WC room S9- 3.1- Urinal push button not working water not flowing | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-12 17:48:00 | Pass | Fix urinal
MSA-DTWD | WA3901411 | Chiller 2 compressor 1 keeps going to Lock Out despite recycling | Perth Campus B1 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-03-23 16:24:00 | Fail | All BRAF works on this job have now been completed. Chiller is back up and running. Work are has been left tidy.
MSA-DTWD | WA3901454 | C Block, Room C007- Light fitting is not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-15 10:56:00 | Pass | Repalced fualty fluors and electronic ballast to c007 lights.
MSA-DTWD | WA3901557 | A block L1 A111 repair to data port 1L - 4 - 1 | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-19 12:34:00 | Pass | Identified and rectified data fault, outlet has been damaged or possibly bumped with a cable plugged in and broken then data mech. Replaced with new mech and tested for correct operation.Eric from programmed also on site did a safety audit and all was OK.
MSA-DTWD | WA3901568 | Block 3 ground fitting and machining No mains power to workshop | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 09:30:00 | Pass | Repaired faulty switch. All now working
MSA-DTWD | WA3901627 | A Block, Issues with alarm panel intermittently showing error code. | Carlisle Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 3 | CLOSE | 12 Jan 2021 | 2021-01-19 17:00:00 | 2021-02-09 10:10:00 | Fail | Attended on second occasion to complete works
MSA-DTWD | WA3901677 | Several areas- Alarm system not working | Thornlie Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 2 | CLOSE | 12 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-17 14:50:00 | Fail | Walk-test conducted over two days BRAF approved
MSA-MRWA | WA3901670 | Leaking toilet pan please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Third Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Jan 2021 | 2021-01-13 17:00:00 | 2021-01-13 08:15:00 | Pass | Replaced leaking seal on the 3rd cubicle
MSA-DCA | WA3905168 | faulty high temp cable on boiler #1 | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-04-19 12:43:00 | Fail | COMPLETED
MSA-DCA | WA3905200 | faulty lighting - urban orchard & area adjacent Livingston Cafe | Perth Cultural Centre Precinct-Cultural Centre Square-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 11:00:00 | Pass | 5x lamps blown and 2 tripped circuits, lights have been shaken again as one of the light diffusers was half unscrewed due to vandals.Rectified and tested all lights in orchard and outside Livingstone Cafe.
MSA-DCA | WA3905461 | ground remove 2 x external taps and fit with a cap so water cannot be accessed. see notes | Short Street Theatre | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 13 Jan 2021 | 2021-01-13 15:46:38 | 2021-01-13 17:11:00 | Fail | Removed all outside hose taps
MSA-DCA | WA3905622 | wash basins and floor drains blocked and backing up | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Female Toilets - Foyer Area | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 13 Jan 2021 | 2021-01-13 17:32:18 | 2021-01-13 15:33:00 | Pass | Cleared blocked drain
MSA-DCS | WA3905012 | Zone 1 perimeter, tamper alarm going off. | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 06:12:33 | 2021-01-13 12:00:00 | Pass | Insect infestation cleaned and insect repellent applied through beam set. Tested ok
MSA-DCS | WA3905063 | Unit 7 G Wing Cleaning Cupboard Hot tap broken, unable to switch off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 07:05:23 | 2021-01-13 17:15:00 | Pass | Replaced leaking and corroded tap
MSA-DCS | WA3905107 | gate house cardax system not working | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 07:36:53 | 2021-01-13 15:30:00 | Pass | Reset tested ok
MSA-DCS | WA3905130 | education 1 and 2 camera's 36 and 94 not picture | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 07:52:19 | 2021-01-13 14:30:00 | Pass | Attended site and investigated the fault.Tested cameras video signal - OK.Reseted power to fibre modem transmitters in Education 1 and Education 2 comms cabinets.Conducted test on PTZ cameras 36 and 94.All back to normal and operational
MSA-DCS | WA3905133 | perimeter inner fence on zones 8 and 9 off line | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 07:54:41 | 2021-01-13 16:30:00 | Pass | Attended site and investigated the fault.Checked power and connections on FlexPS processor in zones 8 and 9.Reseted power to processor and conducted test.All ok at departure
MSA-DCS | WA3905134 | laundry room door is faulty and will not lock | Karnet Prison Farm | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 13 Jan 2021 | 2021-01-19 17:00:00 | 2021-03-25 10:20:00 | Fail | DOOR REPLACED & PAINTED
MSA-DCS | WA3905150 | unit 2 C1 bunk light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 15:00:00 | Pass | Replaced bed light push button switch
MSA-DCS | WA3905151 | Unit 1 control room Vesta fire panel continually beeps | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 08:07:15 | 2021-01-13 10:37:00 | Pass | Complete
MSA-DCS | WA3905202 | INF (10) - B Wing The toilet system for cell B5 is continually running and does not fill up. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-21 15:30:00 | Fail | Nill
MSA-DCS | WA3905209 | Unit 1 - A Wing A3 toilet leaking water from base | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-21 13:41:00 | Fail | Nill
MSA-DCS | WA3905227 | Front Gate, X ray Machine - The x ray machine is not working. There is power however will not start | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 09:15:05 | 2021-01-13 14:00:00 | Pass | Restarted PC. Changed video source from HDMI to VGA. Tested ok.
MSA-DCS | WA3905247 | Laundry - double power point not working. It is a 15amp point | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-03-04 06:50:00 | Fail | Install 2 power points in laundry
MSA-DCS | WA3905286 | security/entry 2x duress alarms not responding and not batteries | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 09:52:35 | 2021-02-25 10:00:00 | Fail | Attended site.Located faulty units.Reprogrammed two new Bosch SE2-SN-304 transmitters - supplied by SEME.Tested PDA’s 11 and 39.All ok at departure
MSA-DCS | WA3905294 | Unit 4, A Wing, Cell A06 has a blocked sink and tap is leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-21 10:30:00 | Fail | Nill
MSA-DCS | WA3905313 | Sewege plant soda ash pipes blocked | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 10:19:25 | 2021-01-14 09:40:00 | Pass | Cause was due to lack of water (lubrication).Watercon employee attended site 13/01/2021 - ProMAP wouldn't allow me to select any date prior to 14/01/2021.Installed new bags of soda ask, removed air block in pump, cleared blockage in inlet.
MSA-DCS | WA3905317 | unit 2 C wing cells 1 to 8 ants coming in through window grille | Melaleuca Prison | WSM-MW-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 10:23:36 | 2021-01-14 10:30:00 | Fail | Carried out a service for ants at melaleuca prison. There were reports of ants located in cells 1-8 in unit 2 c wing. Residually Sprayed all ducts in between cells and around the external perimeter of all cells in c block.
MSA-DCS | WA3905347 | kitchen ants infestation | Melaleuca Prison | WSM-MW-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 10:45:51 | 2021-01-14 11:00:00 | Fail | Carried out a service for ants at melaleuca prison. There were reports of ants located in the kitchen. Applied ant gel to all active ant trails, as well as residually spraying underneath the bench tops and around the external perimeter. Currently the kitchen does not have any pest control maintenance, it is highly recommended that this is carried out on a monthly basis minimum, by a qualified pest control technician.
MSA-DCS | WA3905355 | Oval, Market garden - Repair broken retic riser's | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 14:30:00 | Pass | ADDED STAKES TO SUPPORT RISERS DUE TO EXCES PRESSURE IN THE SYSTEM.
MSA-DCS | WA3905358 | Unit 4 - D2 main light has water in it/needs to be replaced/damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 13:30:00 | Pass | Repaired faulty lights in unit 4 d2
MSA-DCS | WA3905378 | Unit 13, A wing - Light switch faulty needs repairs/replacing cell A2 | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 10:30:00 | Pass | Replaced damaged lights and switches in cell a2
MSA-DCS | WA3905388 | Unit 1, A wing, cell A10 - toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-21 08:30:00 | Fail | Nill
MSA-DCS | WA3905395 | Unit 13, A Wing- tap spindle hard to turn/seized | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-21 11:30:00 | Fail | Reported as cell A9
MSA-DCS | WA3905404 | Unit 2, C wing, C7 - Window is cracked. The bottom window part. The window that slides up | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 11:30:00 | Pass | SLIDING SASH, PULL HANDLE & SPIRAL BALANCES RENEWED
MSA-DCS | WA3905410 | Unit 4, B wing shower window is cracked all over | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 13:00:00 | Pass | RE NEW SLIDING SASH, HANDLE & SPIRAL BALANCES
MSA-DCS | WA3905414 | Hallway near reception Hallway light switch has pushed through the wall plate- see notes | Mandurah | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-13 16:30:00 | Pass | Replaced damaged switch plate in hallway.
MSA-DCS | WA3905417 | Unit 2, A wing, A9 - outside light switch for inspection light is broken (switched pushed in) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-18 08:30:00 | Pass | Replaced damaged cell switch in unit 2 a9
MSA-DCS | WA3905418 | Unit 3, Cell C12- Personal lock doesnt work | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-20 11:30:00 | Fail | Replace hinges and lock.Replace weld on strike.
MSA-DCS | WA3905420 | Unit 14, B wing,B08 - prisoner light in cell damaged and not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 12:00:00 | Pass | Repaired faulty lights in unit 14 b8
MSA-DCS | WA3905421 | Unit 13, D Wing- No Video Input on Camera 416 on the Security Office monitors. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 11:33:41 | 2021-01-14 11:00:00 | Pass | Removed failed encoder card from slot, programmed replacement card and connected analogue camera feed. Configured Indigo vision head-end for new card IP address and ensured video was recording. Reconfigured monitors in Unit 13 & Security SO office.
MSA-DCS | WA3905511 | Security, office - CCTV not connecting to Network | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 12:27:52 | 2021-02-09 14:41:00 | Fail | Investigated and rectified fault.Tested OKJob Complete
MSA-DCS | WA3905513 | Transponder TR3 - Unit 1 control room ceiling - multiplex point 36 | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 12:27:57 | 2021-01-28 11:35:00 | Fail | Unit all ok possible over heat as it is located in a roof
MSA-DCS | WA3905530 | laundry dryer area No3 dryer showing fault | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 12:33:07 | 2021-01-14 10:25:00 | Pass | #3 Dryer showing fault - inspect and test dryer, re-terminate E/SNP wiring, remove front panel, trace fault to pinched wire, remove and insulate wire. Test dryer - ok.
MSA-DCS | WA3905590 | PE Alarm Zone 14 is in constant alarm and will not reset. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 13:05:16 | 2021-04-13 15:00:00 | Fail | traced fault to faulty beamset at H2 on stack, replaced beamset & realigned as required. tested zone for cctv & alarms. job complete
MSA-DCS | WA3905609 | Industries control gate - lights on ceiling faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-15 15:00:00 | Fail | Replaced damaged lights
MSA-DCS | WA3905612 | Industries admin tearoom - black water spout lever on the water cooler broken/ | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-15 14:45:00 | Pass | Replaced faucet and bubbler cartridge Serviced twin system
MSA-DCS | WA3905654 | Reception, Property Store Room- Electronic door handle not working correctly | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 14:30:38 | 2021-01-14 16:00:00 | Fail | Intermittent fault with the handle of the fob reader type lock. Not a job for SEME. Spoke to onsite maintenance officer to refer job to locksmith
MSA-DCS | WA3905655 | Unit 3, B4 - door handle loose/faulty comming off | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-03-11 10:00:00 | Fail | NEW PULL HANDLE INSTALLED
MSA-DCS | WA3905656 | Boot shop - main water pipe to industries burst | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-13 15:30:00 | Pass | Nill
MSA-DCS | WA3905661 | Camera 025 (429) inner gates - pixels are dropping in and out | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 14:47:54 | 2021-01-14 09:30:00 | Pass | Found issue with stream adjusted bitrate and iframe settings to accomodate no more pixels on movement
MSA-DCS | WA3905668 | Unit 3, Cell C11- Window Frame broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-25 15:15:00 | Fail | REPAIRS COMPLETED - SPIRAL BALANCES RENEWED
MSA-DCS | WA3905670 | Unit 2, B Wing- water leaking to bottom landing when water is spilled on floor | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-27 14:15:00 | Fail | REPAIRED LEAK PENETRATION TO SHOWER DUCT
MSA-DCS | WA3905673 | Unit 4, Cell J10- Lock is stuck and prisoner stuck in cell | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 13 Jan 2021 | 2021-01-13 19:16:16 | 2021-01-13 17:15:00 | Pass | opened jammed Prisoners Privacy cell lock Unit 4 / J10new Lock fitted and strike secured with Torx security screws
MSA-DCS | WA3905699 | Unit 14 - A/C wing kitchen on/off electrical switch damaged under urn | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-18 10:00:00 | Pass | Attended and isolated damaged oven switch. Picked up replacement and installed and tested
MSA-DCS | WA3905745 | Unit 2, PIR outside cell 17 no activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 16:36:45 | 2021-08-05 11:00:00 | Fail | Replaced damaged PIR, calibrated and tested OKParts(SEME):1 x PIR
MSA-DCS | WA3905746 | Unit 3, PIR outside officer pod no activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 16:38:42 | 2021-08-05 15:00:00 | Fail | Rectified and fixed fault, job completed.
MSA-DCS | WA3905748 | Kitchen - dishwasher not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 16:44:33 | 2021-01-28 15:30:00 | Fail | 15/01/21Found dishwasher continuously running Fault findFound timer faulty causing wash pump relay to stay on Found rinse tank element faulty on 1 leg and requires replacing Parts required and unit needs cleaning and removal of cockroaches. Customer still able to use unit Parts required: 1 x timer 1 x rinse element 1 x Relay1 x Gasket28/1/2021Sign in Isolate unit Remove and replace timer Remove and replace relay Clean and spray base of unit as heavily infected with cockroaches Remove and replace rinse tank elementFill unit Found rinse arm missing end cap Remove and replace Heat and test unit OkNoted: filter dirty, advise manager and he is getting maintenance to replace
MSA-DCS | WA3905759 | Control Room - Monitors for the fence - are all frozen | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Jan 2021 | 2021-01-14 00:40:59 | 2021-01-14 14:55:00 | Fail | job completed under WA3890782
MSA-DFES | WA3905248 | Engine room door - door #2 - brackets have pulled out of ceiling | CFRS Canning Vale | GMP-BR | Building | Roller Shutters (BU) | Go Doors | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 12:30:00 | Pass | COMPLETED
MSA-DFES | WA3905281 | Engine Room door 1 cables are broken | CFRS Canning Vale | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 13:30:00 | Pass | COMPLETED
MSA-DFES | WA3905432 | Fire fighters Changeroom No 20 - flickering light | CFRS Welshpool | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-14 10:45:00 | Pass | Investigated flickering light. Found that actual issue was the engine bay lights tripping the RCD when switch was turned on. Determined fault tolie within one of the fittings. All 4 fittings show signs of wear and tear and have requested to upgrade them all with new fittings.
MSA-DFES | WA3905460 | FF Shared toilet (Dorm 2 and 3)- Toilet in the shared ensuite is not flushing correctly. | CFRS Malaga | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-14 10:22:00 | Pass | Investigate leak at cistern,flusbuttons are worn and cistern need d replacing source parts and installed tested jobcomplete ,ministop not working so replaced for new
MSA-DFES | WA3905597 | Engine room - vertical bifold door, left laminated window cracked & may requires replacing.1.6mx0.9 | CFRS Duncraig | GMP-BR | Glazing | Door Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-16 16:11:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSMADE SAFE 2 CRACKED PANELS WITH SAFETY FILM1-1000 X 1000, 2-500 X 300RETURNED LATER DATE TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS2-973 X 1640POLISHED EDGESFROST TINT FILM APPLIED TO ONE PANEL IN FACTORY10.5 L/M OF DOUBLE SIDED TAPE USED
MSA-DFES | WA3905627 | kitchen over cook top power point blank cover coming away from wall exposed wires | CFRS Hope Valley | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 13:00:00 | Pass | Located damaged blank plate. Replaced with new.
MSA-DFES | WA3905636 | Faulty Remote for gate. may Need a replacement, has a faulty circuit board. | CFRS Joondalup | GMP-BR | Building | Steel Fencing & Gates (BU) | Anvil Doors | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-21 03:45:00 | Fail | Attended Joondalup Fire Station. Auto gates need new Air keys and Transmitter installed. Cost of works exceeds purchase order value. Submitted BRAF (Pending approval). See attached service report, BRAF, Quote and sign off sheet.21.1.21-- Attended Joondalup Fire Station and installed 2 x additional air key remotes and receiver to auto gate. Tested gate operations and confirmed that the new air key remotes and receiver are working correctly.
MSA-DTAG | WA3905252 | Several Base Build Cameras have lost connection to the server - see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 12:00:00 | Pass | Attended site. Reset 9 x Axis Cameras, tested, all OK.Job completed
MSA-DTWD | WA3905155 | A block courtyard rear repair umbrella cable broken off A Block Rear Courtyard | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-04-20 09:50:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3905160 | canteen kitchen GPO is not working | West One Services | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 12:45:00 | Pass | Attended site and signed in. Located kitchen. Checked all gpos. Found circuit r4 not working. Tested to find tripped RCD in switchboard. Reset and tested all appliances and circuit function. All okay. No faults present. Huge chance circuit was overload with kitchen appliances. Loaded up circuit and no trip. All okay. Signed out. Job complete
MSA-DTWD | WA3905231 | A block, level 3,A354 kitchen - Hot water unit not working | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-13 13:50:00 | Pass | Run and test all working okay MAY NOT BE KEEPING UP WITH DEMAND A401901059 BILLI QUADRA
MSA-DTWD | WA3905262 | A19 student support offices- ceiling fluro lights not working behind the reception & meeting room | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 11:45:00 | Pass | Attended site and signed in. Located customer service. Found lights out. Replaced tubes, starters and ballast as required. Tested all okay. Job complete
MSA-DTWD | WA3905276 | Creche - broken exit door | Perth Campus B1 | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 17:30:00 | Pass | replace damage fence and door and paint
MSA-DTWD | WA3905296 | U Block disabled toilet door will not lock from inside | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 15:10:00 | Pass | Job completed - replaced damaged turn adapter and refir lock on disabled toilet in U block
MSA-DTWD | WA3905386 | A Block, Level 2 access control doors offline | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 0 | CLOSE | 13 Jan 2021 | 2021-01-13 15:15:37 | 2021-01-14 16:01:00 | Fail | job completed -Contacted site management John B.Investigated fault. Faukt relating to Contorllers on level2 battaery faukts.Replaced batteries. 4 x 12V 5 Ah Van stockReset fault on controllers tested Doors OK.Notified management when departed sit
MSA-DTWD | WA3905403 | E block Ground E59 Two under bench fridges not working | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-04-08 16:00:00 | Fail | Complete rectification works as per work orders. Test operation. No faults present job complete.
MSA-DTWD | WA3905422 | E block transportable cat trapped in roof panel needs to be removed | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 0 | CLOSE | 13 Jan 2021 | 2021-01-13 15:32:36 | 2021-01-13 15:00:00 | Pass | Accessed roof where staff suspect cat to be, left roof open as requested to close following morning
MSA-DTWD | WA3905438 | P Block, Outside fence- wire on the cyclone wire fence & gate have been cut | Midland Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 14:15:00 | Pass | two holes repaired in fence and gate with new cyclone fencing
MSA-DTWD | WA3905572 | AHU C1, C Block- Air Con unit still not working correctly - see notes below | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 10:00:00 | Pass | Cannot get access as the staff go home at 1500hrs and won't be able to get on the bms or get keys. Told to return tomorrow, was in mandurah doing work for another clientCarried out checks on the air-conditioning systems in block a&b , found the system running ok and the temperature was down in the office . Chiller and sensors need checking next time bms is checked for calibration.
MSA-DTWD | WA3905625 | A block ground Hitachi A/C noisy outdoor fan - see notes | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-02-01 13:27:00 | Fail | Found the Hitachi high wall split in the stores office in A block cutting out on high head pressure. The base of the condenser has rusted away and the fan motor jams on the grill. Suref up the base with marine ply so it can run , only temporary fix. Graf being sent through.BRAF DECLINED - CLAIM SUBMIT
MSA-DTWD | WA3905634 | E Block, Kitchen E58 - 2x leaking taps | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-29 07:22:00 | Fail | Repaired several leaking taps and also replaced 2x isolation valves that had seized and leaking
MSA-DTWD | WA3905650 | C Block - Faulty smoke detector in room C14- Attendance Thursday 14thJanuary | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 1 | CLOSE | 13 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 08:23:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Mike DayWork Order Number: WA3905650 Priority #: 1 - High PriorityCall out Date: 13/01/2021Target finish: 14-1-21PFM Contact & details:Work order contact: Mike DayPhone number: 0407 476 354Original information: C Block - Faulty smoke detector in room C14- Attendance Thursday 14thJanuaryWork Note - Attended site:Date: 14/1/21Start Time: 7.30Finish Time: 8.30Techs on Site: EdWorks Carried Out: Checked detector that went in alarm yesterday caused by cleaners. Analogue value was ok. Left zone 9 isolated for cleaners and they will de-isolate themselves once works finished.
MSA-DTWD | WA3905657 | A block unable to arm campus on the security key pad | Rockingham Campus | GMP-BR | Security | Security Management System (SE) | BJ SYSTEMS | 2 | CLOSE | 13 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-14 08:15:00 | Pass | Unable to retrieve information on input that is causing issues on system. Dennis has agreed that security will get this information for us ASAP for return Note: Dennis has not returned emails regarding information required for job. Job closed
MSA-DTWD | WA3905662 | A block L1 Water feature not working A Block Rear Courtyard | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-20 13:56:00 | Pass | Inspected water feature not working. Reset tripped rcd , tested pump all working properly. Water tank was empty so filled up. Turned on, all working properly now.job completed
MSA-DTWD | WA3905663 | S block, Level 1, S108 - aircon not working | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 13 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-14 15:00:00 | Pass | Accessed site completed relevant sign in procedures, aircon working as per spec , removed covers and unclogged drain and tested all ok , noticed slight condensation on face of unit , insulated to remove future moisture, refitted covers , all ok
MSA-DCA | WA3909233 | replace the Powder Fire Extinguisher in block A due to loss of charge | Sunset Hospital Heritage Precinct-Building A-Infirmary-Ground Floor | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-19 09:15:00 | Pass | Supplied and installed new DCP fire extinguisher.
MSA-DCA | WA3909287 | distibution board RCD tripping blue 4 | PICA-Main Building-Level 1 | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-14 16:00:00 | Pass | Attended site and found rcd tripped. I turned rcd back on and rcd did not trip. So i walked around and found all power points on that circuit to see if there was something that was plugged in previously that caused it to trip but everything was still plugged in. I attempted to do a insulation resistance test but could not do safely with how full the db was and while it was still live. If rcd trips again we would need to attend in the morning so we can isolate board. The cause of the tripped rcd may of been caused by a previous water leak a few days ago and still had some moisture some where on the circuit and has now dryed out. I then tested from the feild to ensure the rcd was still operating and the rcd tripped passing the test.
MSA-DCA | WA3909357 | request to remove faulty electrical equipment from Fiji room | Perth Cultural Centre Precinct-Fiji Room-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-15 09:00:00 | Pass | removed associated hardware with screen without disrupting the current workings of the FIJI and PCC
MSA-DCS | WA3908945 | Comms room display monitor only showing on half of the monitor. | Walcott Centre (Central West Metro ) | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 14 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-12 12:30:00 | Fail | Work performed by Nathan Groenewald 14/01/2021:Collected parts required for job.Attended site and relocated monitor and adjusted views.Work performed by Lee Kiok 12/02/2021:Attended site, installed Master NTP Server, Synced NVR & all camera times to NTP Server.Job completed.APPROVED BRAF ATTACHED
MSA-DCS | WA3908981 | zone 11 external permatrax false alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 07:33:52 | 2021-03-11 16:16:00 | Fail | Repaired and calibrated Zone 11.Tested OKJob Complete
MSA-DCS | WA3908989 | Stores next to water storage tank Broken Reticulation Pipe | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 07:49:08 | 2021-01-14 10:50:00 | Pass | BROKEN SPRINKLER THAT WAS REPLACED.
MSA-DCS | WA3909002 | unit 10, C16 - Top bunk light smashed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 08:05:45 | 2021-01-14 11:00:00 | Pass | Repaired light
MSA-DCS | WA3909037 | Unit 13, B & D dayroom- water cooler leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 08:58:21 | 2021-01-15 13:05:00 | Fail | Reconnect water supply and check for leaks all seems okay
MSA-DCS | WA3909039 | Unit 2, SO's Office- AC not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-02-26 13:45:00 | Fail | Replaced condenser fan and PCb. Operation at time of departure
MSA-DCS | WA3909042 | Unit 4, B Wing Cleaning cupboard light switch not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 11:30:00 | Pass | Repaired damaged switch in unit 4 store
MSA-DCS | WA3909044 | Unit 2, D wing - sink in D10 blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 15:30:00 | Fail | Nill
MSA-DCS | WA3909048 | Library- 2x lights in vaulted ceiling area not working | Boronia Pre-release-AK19 - Library, Education Personal Development | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-14 13:30:00 | Pass | Repaired lighting in library.
MSA-DCS | WA3909056 | kitchen combe asking reset gas 32.2 | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 09:10:09 | 2021-01-14 13:15:00 | Pass | Replaced both Ignition Module & blower after approval given. Test operation ok now.
MSA-DCS | WA3909064 | Ceiling damaged due to water leak from exhaust fan ducting/dropper | Boronia Pre-release-AJ21 - Stores - Urine Analysis and Uniform Store-Ground Floor-Urine Analysis Room | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-09-30 14:00:00 | Fail | ROOF LEAK FIXED, CEILING REPAIRS MADE, CEILING PAINTED
MSA-DCS | WA3909088 | Boiler house - Steam leak on main steam line above boiler number 2 on flange closest to the boiler | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 09:44:07 | 2021-01-22 10:30:00 | Fail | Got signed in and escorted to boiler house. Opened and cleaned flange ( faces are pitted and worn) fit new spiral wound gasket. Closed up flanges and ran the boiler up to full pressure no leaks.
MSA-DCS | WA3909091 | Sewage plant - blockage in one of the lines | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 0 | CLOSE | 14 Jan 2021 | 2021-01-14 13:45:43 | 2021-01-14 16:49:00 | Fail | Fixed blockage rectified issue present with blockage - retested and receded plant.
MSA-DCS | WA3909110 | Unit 14, B Wing, Cell B08- light switch is hanging off the wall (Inoperable) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 08:30:00 | Pass | Repaired damaged lights switch in unit 14 b8
MSA-DCS | WA3909139 | Unit 1, B & D Wing- skylights damaged | Casuarina Prison | SPA-BR | Roofing | Rooflights and Skylights (RF) | Midolo Building Services | 0 | CLOSE | 14 Jan 2021 | 2021-01-14 14:18:19 | 2021-02-15 19:22:00 | Fail | 12X SKYLIGHTS REPLACED - ROOF REPAIRS MADE
MSA-DCS | WA3909160 | Admissions, holding cells 5 - smashed cell window approx 800x800 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-02-15 12:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3909164 | Unit 1 A wing - Magnetic grill not working | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 08:30:00 | Pass | Ryan Nicholson (15/01/2021) - Work NoteTravel to site. Inspect gate. Found gate closed and unresponsive due to Access control fault when tried out keyswitches. Recommend Seme look at system. Could not operate gate to do checks.
MSA-DCS | WA3909214 | Canteen and Chaple - Flood lights faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 10:30:00 | Pass | Investigate and repair flood lights at Chapel and Canteen
MSA-DCS | WA3909219 | Kitchen - Dough mixer showing fault | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 12:16:18 | 2021-01-15 11:40:00 | Pass | 15/01/21Customer complaining mixer cutting Turn mixer on and working ok Unit working ok Found cockroaches in controller Spray and clean cockroaches out Test unit ok
MSA-DCS | WA3909245 | Security Area - Control Room - download footage for security | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-14 15:36:00 | Pass | download footage & deliver to Mr Booth
MSA-DCS | WA3909298 | sentence planning lights faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 14:00:00 | Pass | Repaired 2 x broken lights
MSA-DCS | WA3909299 | egg packing room - GPO faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 12:00:00 | Pass | Investigate and repair GPOs at Egg Packing room
MSA-DCS | WA3909300 | Programs room 1&2 - faulty electrical timer | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 13:00:00 | Pass | Disconnect faulty timers on BWU at Programs room
MSA-DCS | WA3909303 | Shared Facilities, car park undercover area - lights fallen down | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 08:30:00 | Pass | Investigate and repair light at shared facilities undercover area
MSA-DCS | WA3909304 | Shared facilities - Toilet light broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 08:30:00 | Pass | Investigate and replace shared facilities toilet light
MSA-DCS | WA3909305 | ABS, Electrical junction box has come away from wall - See Mark Spanswick ABS - VSO | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 15:00:00 | Pass | Investigate and replace junction box at Abattoir
MSA-DCS | WA3909333 | zone 10 in multiple activation faults | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 14:22:14 | 2021-03-16 13:00:00 | Fail | Observe and conduct full test on UW zone 10, activation confirmed from gatehouse control room. Job completed.
MSA-DCS | WA3909368 | Unit 2, House 1- Controllers are offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 09:00:00 | Pass | Unit 2 House 1 Expanders offline. Tested controller and all is ok. Found GBUS1 faulty. Relocated terminations to GBUS2 and tested operation, all is in working order.
MSA-DFES | WA3909149 | Rear door entry - from carport) into station is jamming and very difficult to open. | CFRS Armadale | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-21 14:00:00 | Fail | Existing door was delaminated and hinges were dropping casuing door not to close properly. Door and hinges were replaced with new solid core door and hinges. All existing hardware was reused on the door. Door was painted to match existing colour.
MSA-DFES | WA3909157 | admin security system Tecom GPRS off line-please call prior to attendence | DFES Regional Office - Belmont | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-14 12:45:00 | Pass | 14/01/2021, 1215-1245Fuse blew in the powersupply and was running off a battery till 6am when it went offline. Replaced fuse and battery gotall systems working again.
MSA-DFES | WA3909335 | front garden no pressure to sprinklers - see notes | CFRS Armadale | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-16 19:22:00 | Pass | Call Out & LabourSupply 7 x Popup Sprinklers & 7 x MP Rotor Nozzles
MSA-DFES | WA3909364 | Lecture room 3 - Air Con has stopping working, see notes below | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-03-15 16:00:00 | Fail | Removed pcb , repaired pcb, refit pcb. Replaced capacitors and contactors. Running good
MSA-DTAG | WA3909040 | ground Public Disabled Toilet lock faulty | Armadale Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 10:45:00 | Pass | ADJUST AND SECURE LOCK
MSA-DTAG | WA3909159 | Lvl 1, Staff Room- Infestation of midges around bin store,G4S staff room & west door entrance | Central Law Courts | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-20 07:15:00 | Fail | Treated to control flying insect pests in internal compound, and surrounding areas - corridor, staff room, aroundcontractor sign in and west side entrance areas. Pheromone pads placed appropriate spots. Seclira fly bait to walls toall areas stated.*There is a Starkey wall mounted UV unit on wall in bin store area that is not operating, needs 2 x15w tubes and 2 xstarters, follow up or repair / replace at next service.
MSA-DTAG | WA3909161 | Lvl 3, Court 34 is experiencing issues with cooling | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 14:30:00 | Pass | Attend site. Investigate court 34 cooling issues. Access BMS and check court temps. Found court to be 22.8 degrees. Vav box supplying minium airflow. Access court and check sensor calibration. Found sensor reading correctly, 22.8 degrees. Court temp setpoint is 22.5 degrees. VAV box will reduce airflow as temperature reaches setpoint. AC in court 34 working as normal.
MSA-DTAG | WA3909162 | Basement custody monitors are not working | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-20 14:52:00 | Fail | Multiple no2 faulty, taken away for possible repair or replacement. Follow up reqFollow up, install new quad decoder, test, all ok
MSA-DTAG | WA3909200 | Carpark court users issues with roller door - see notes | Joondalup Courthouse | GMP-BR-HO | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-15 13:30:00 | Pass | Door operating on arrival but pes were covered in spider webbing and the bottom rail was bent probable cause of the door not operating correctly, cleaned off pes and controller guides and bottom rail, removed bottom rail and straightened up, refitted tested and left in working order, also cleaned pes on remaining roller shutters as told by the guard they were also having issues with them, HIGHLY RECOMMEND ANNUAL SERVICE DUE TO THE USE TO ALL 4 ROLLER SHUTTER DOORS, TO PREVENT ON GOING ISSUES.Pictures att show damaged bottom rail before and after bent then straightened and also the state of the pes.
MSA-DTAG | WA3909242 | It would appear that the several CCTV camera's a lagging in the picture frames | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 11:00:00 | Fail | CcTV hard drive requires replacement in Raid storage quote to be provided. 25/01/21 Drive replaced rebuilt will take approx 8 - 24 hours normal operation to occur after this time.
MSA-DTAG | WA3909244 | 1987 Check the WIP in Sheriff’s Office - see notes | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 08:45:00 | Pass | Checked Sheriff's office WIP comms back to master WIP, could hear master WIP but not Sheriff's office. Confirmed with Ampac that we had installed the correct WIP type 219-0007. Replaced unit with another one from van stock and WIP comms worked both ways all okay.
MSA-DTWD | WA3908962 | Entrance C and B blocks Auto door malfunctioning - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 14 Jan 2021 | 2021-01-14 17:00:00 | 2021-01-14 11:48:00 | Pass | 1064275. Found safety sensors staying on causing door to stay open, cleaned and adjusted sensors and checked over door, reset and tested all ok, also lubricated sticking entry switch
MSA-DTWD | WA3909031 | L1 mens toilets near bike locker - shower leaking | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-27 15:00:00 | Fail | reseat and rewasher taps to shower
MSA-DTWD | WA3909047 | B block L2 male toilet tap dripping | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 13:00:00 | Pass | Arrived on site and inspected found the lhs tap leaking. Serviced both hot and cold tap. Changed the tap washer. Tested all working good
MSA-DTWD | WA3909059 | D Block. 2nd Floor, Ladies toilet end cubicle water leaking on floor from behind toilet bowl | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 15:00:00 | Pass | Arrived on site and inspected found the the pan leaking. Removed the pan found the pan rubber to the copper pipe and kee seal faulty. Could get the pan rubber from any supplier as they are obsolete. Removed the copper pipe and Fabricated new pipe work to suit the new parts. Refitted the pan. Tested all working good.
MSA-DTWD | WA3909085 | S Block, class room exit doors have sticky lock barrels difficult to unlock and lock | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-14 17:00:00 | Pass | Job completed - replaced 7 damaged oval cylinders on exit doorsof S block
MSA-DTWD | WA3909141 | A block, honeywell room - aircon temp faulty | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-20 09:13:00 | Fail | Found the Honey well room in A block needs a wall sensor as a dividing wall has been put up and the temperature gets to cold . Will need to order another senor.SIMON HAS ADVISED THAT DAIKIN LOOKED AT JOB WHILST CARRYING OUT OTHER QUOTED WORKS AND HAVE ADVISED AN ADDITIONAL UNIT WILL NEED TO BE INSTALLED TO MAKE THE SITUATION WORK. JOB IS CLOSED ONLY 1 HOUR CHARGE FOR TECH ON SITE TO DIAGNOSE
MSA-DTWD | WA3909183 | Outside Plant Room - B Block chiller is tripping off line ( High motor current alarm Stage 1.) | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-29 08:30:00 | Fail | Unit tripped on high motor current, raised PO for Airvision to attend
MSA-DTWD | WA3909186 | Holes in bitumen Blocks 3 & 1 – OSH issue | Thornlie Campus | GMP-BR | Paving & Roadworks | Paving (PR) | MR POTHOLE | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-15 13:00:00 | Pass | Job completed - Asphalt repairs at blocks 1 and 3 at Thornlie TAFE
MSA-DTWD | WA3909203 | T Block, Cafeteria freezer- freezer not reaching temperature, error "defrost" | Murdoch Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 0 | CLOSE | 14 Jan 2021 | 2021-01-14 15:53:47 | 2021-01-14 14:45:00 | Pass | Urgent P0Travelled to site. Met with maintenance. Investigated freezer and found unit operating as normal and reaching setpoint. Checked operation and refrigerant charge of all of system and found no issues. Was informed of control showing defrost alarm. Found alarm indicator flashing but no active alarms. Cleared light. Watched system reach and cycle off at -18 deg setpoint and cycle back on at -16 deg. Informed maintenance for outcome.
MSA-DTWD | WA3909286 | building 832, ladies toilet - rubber boot at rear of toilet perished | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 13:00:00 | Pass | job completed - Replace perished seal to ladies toilet building 832
MSA-DTWD | WA3909288 | LEvel 1, S121 - aircon remote for aircon nor working may require replacement | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-14 15:58:00 | Pass | Accessed site completed relevant sign in procedures, found air conditioner remote to be faulty , replaced with new all working ok
MSA-DTWD | WA3909291 | A block L1 fire panel zone 27 faulty sensor | East Perth Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-14 15:36:00 | Pass | Replaced 2x faulty conventional smoke detectors in supply air plant rooms. All ok and clear now
MSA-DTWD | WA3909318 | Investigate chiller 2, BMS fault | West One Services | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 14 Jan 2021 | 2021-01-15 17:00:00 | 2021-01-19 12:18:00 | Fail | Accessed site completed relevant sign in procedures,attempted to rectify bms issue , currently have no access, accessed plantrooms and located individual routers forremote access to bms server , will return on Monday tocontinue worksReturned to site , recitfied bms issue located global controller and gained access to bms system , allocated dedicated bms computer to site
MSA-DTWD | WA3909354 | F-Block, FG36 - Blocked floor drain,under sink(when the sink is used water spills out all over flool | Carlisle Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-20 14:37:00 | Fail | Unblocked gully outside
MSA-DTWD | WA3909370 | Wire Fencing has been vandalised- see note below | Thornlie Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 14 Jan 2021 | 2021-01-19 17:00:00 | 2021-02-24 16:43:00 | Fail | Works were scoped and BRAF was submitted to completed works.BRAF was declined to continue to undertake works.
MSA-MRWA | WA3909323 | Front office sink - The tap in the sink of the NDM building is dripping quite significantly. | Materials Engineering Branch | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 09:33:00 | Pass | Rewashed tap. Struggled to isolate water due to corroded isolation valve outside
MSA-DCA | WA3913455 | Ladies toilet - light fitting in ladies toilet not working. replacement globes failed | Collection and Research Centre Welshpool-Administration and Library Building-Level One-Women's Toilet | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-22 15:00:00 | Fail | Replaced em fluro light for 1x new LED fitting, and 1x new emergency spitfire next to new light
MSA-DCA | WA3913748 | Level 3, Server Room- AC 2( Daikin unit), flashing red light | State Library of WA-Main Building-Level 3-3.3 - Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-15 15:00:00 | Pass | Attended site. Carried out investigation on AC 2 L3 Server Room at SLWA. During investigation was unable to fault unit while in operation and no faults were active while in operation.Will monitor and discuss with client.No further faults or alarms flashing on indication panel. Space conditions being meet.Closed job.
MSA-DCA | WA3913839 | loading bay 2 x external spotlights are on continuously - see notes | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-03-18 07:15:00 | Fail | Complete
MSA-DCA | WA3913858 | Large wooden double doors into Dutchwrecks Gallery - dropped slightly & are scrapping on floor | Shipwreck Galleries-Main Building-Level 1-Dutch Wreck Gallery | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-15 09:00:00 | Fail | Replaced hinges as required and supply one extra hinge as per clients request
MSA-DCS | WA3913378 | unit 17 B/D Day room fire hose cabinet lock not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-18 12:30:00 | Pass | No Fault found, Lubricate lock.
MSA-DCS | WA3913383 | unit 14 shower in C12 - drain is blocked and overflows | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-28 13:31:00 | Fail | Completed under WA3954042
MSA-DCS | WA3913387 | health all drains severely blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-21 09:50:00 | Fail | Unblocked drain at health. Sewrr line damaged furtehr down the line
MSA-DCS | WA3913390 | Unit 10 D5 Viewing Hatch Smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 15 Jan 2021 | 2021-01-16 07:37:11 | 2021-01-15 10:30:00 | Pass | VIEWING HATCH REGLAZED
MSA-DCS | WA3913395 | perimeter south ptz rec ptz zone 9,12 camera's not focusing correctly and maybe need cleaning | Bandyup Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jan 2021 | 2021-01-15 11:42:06 | 2021-07-26 08:07:00 | Fail | replaced camera & tested ok. job complete.
MSA-DCS | WA3913396 | Unit 7 H7 cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-18 10:30:00 | Pass | Repaired light
MSA-DCS | WA3913399 | Unit 6 A14 Toilet not secured to floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 13:05:00 | Pass | Replaced toilet and adjusted pipe work
MSA-DCS | WA3913402 | Unit 7 H7 tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-15 14:10:00 | Pass | Replaced corroded tap
MSA-DCS | WA3913410 | Unit 3 D14 Cell sliding window mesh damaged | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-21 13:00:00 | Fail | REPAIRS TO DAMAGED MESH CARRIED OUT
MSA-DCS | WA3913421 | Unit 3, D13 - Cell sliding window mesh damaged | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-21 12:00:00 | Fail | REPAIRS TO DAMAGED WINDOW MESH COMPLETED
MSA-DCS | WA3913441 | INF (10) - Office infirmary control room door entry lock very stiff and requires attention. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-18 14:45:00 | Pass | Temp. repairReplace GMK barrel.
MSA-DCS | WA3913451 | Unit 3, Court Yard - garden tap is pouring out water and will not turn off. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-16 12:16:00 | Fail | Nill
MSA-DCS | WA3913491 | Unit 3, B & D - Requires new door handle as it has been ripped off | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 15 Jan 2021 | 2021-01-16 09:08:28 | 2021-01-15 13:30:00 | Pass | Require parts, obtain parts, replace damaged handles and spindle.
MSA-DCS | WA3913495 | nit 15, C Wing - Personal key (cell C06) snapped off in lock, part key still in lock | Casuarina Prison | WSM-BR-SITE | Security | Keys & Access (SE) | Lock It Locksmiths | 1 | CLOSE | 15 Jan 2021 | 2021-01-16 09:12:41 | 2021-01-15 11:00:00 | Pass | Open cell. remove barrel, dismantle, remove broken key and reassemble.
MSA-DCS | WA3913552 | Unit 3, TV reception is not working correctly | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-22 10:00:00 | Pass | Checked signal strength at unit 3, signal is OKsystem is not on the vast satellite system all units are powered down and not connected.Spoke with Lindsay Mercer and gone through and checked all units and confirmed all running on the Digital antenna on each building
MSA-DCS | WA3913608 | Unit 3, Control Room- plug connection is very loose and cracked | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-03-23 11:30:00 | Fail | Current plug and socket mounted in a location where it is constantly knocked by the control officer when using Grill Control panel. No compatible replacements available. Disconnected socket and removed from console. Extended connection cable for door controls and drilled new 32mm hole to mount socket close to side panel, away from existing control equipment. Reconnected door controls and tested from both consoles.
MSA-DCS | WA3913682 | Unit 1 A wing - Grill not working, electrical issue | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jan 2021 | 2021-01-16 11:40:46 | 2021-01-15 16:05:00 | Pass | Replaced faulty push button, found intermittent faults still occurring. Repaired multiple wiring issues with old cabling.Tested OK.Job CompleteParts:Push Buttons, Consumables
MSA-DCS | WA3913756 | Gatehouse, Control Room- Faulty lock | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-02-19 10:00:00 | Fail | Attend site, inspect control room door. Striker plate binds with the frame, new striker plate installed. On testing it was found that the door closer also requires to be replaced. Part ordered and re-attended site to install new door closer. Due to COVID restrictions this job was placed on hold until authorised by site to allow back on premises.
MSA-DCS | WA3913758 | gate house roller door has come of its hinges | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 15 Jan 2021 | 2021-01-15 16:47:09 | 2021-01-15 13:30:00 | Pass | 15/01/21Re-adjust limits on roller door automation
MSA-DCS | WA3913797 | Bakery Water cooler leaking from the bottom of unit. | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-15 15:13:00 | Pass | No repairs required as fountains due to be scrapped and a new system to be installed
MSA-DCS | WA3913800 | Perimeter - sennet network reporting mutiple data pass fails | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jan 2021 | 2021-01-15 17:30:21 | 2021-01-15 17:00:00 | Pass | Attended site and investigated the fault.Checked power and connections to Senstar network controller.Reseted power.Conducted test on all perimeter sensors.All back to normal and operational
MSA-DCS | WA3913822 | Unit 6 - B10 no water flow from tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-29 13:30:00 | Fail | Nill
MSA-DCS | WA3913854 | Assessments Right Side of Rear Corridor Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-19 13:48:00 | Pass | Job already quoted.on previous job. Waiting on approval. Closing this job.
MSA-DCS | WA3913860 | Unit 2 - B3 toilet will not flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-10 13:16:00 | Fail | Job completed under WA3966673
MSA-DCS | WA3913892 | Security, office - cell call voice log not working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jan 2021 | 2021-01-16 15:14:27 | 2021-03-24 16:13:00 | Fail | Performed upgrades and modifications to Security downloads computer.Job CompleteParts:Network CablesPrivacy Screen
MSA-DCS | WA3913893 | Unit 2, Outside cell Doors of A-8 A -11 A -13- Flooring damaged | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-03-08 08:00:00 | Fail | DAMAGED SECTIONS OF FLOORS REPLACED
MSA-DCS | WA3913924 | Level 1, Room 3, Interview room- Rubber strip come away from door | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-08 10:30:00 | Fail | attended site and carried out repairs to insertion rubber that had fallen out.
MSA-DFES | WA3913363 | Office repairs to blinds - see notes | DFES Fleet & Equip Serv Fleet Appliances Prog Bran | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 15 Jan 2021 | 2021-01-21 17:00:00 | 2021-02-01 15:48:00 | Fail | completed & Invoiced
MSA-DFES | WA3913369 | Engine room earth leak on lighting circuit Blue 1 RCD keeps tripping - see notes | CFRS Welshpool | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-02-09 13:45:00 | Fail | We identified circuit B1 tripping. We isolated the fault to the 3rd light in the bank and disconnected the light. In the bank of 4, 1 is faulty, 1 doesn’t work and all 4 are damaged and are showing signs of fatigue. There are also 2 additional lights on the other side of the engine bay that have 1 of 2 tubes faulty. I recommend we get all replaced at the same time to prevent re attending for a similar fault. I have noted the surrounding LED lights to match, will seek approval. 12foot A frame required.
MSA-DFES | WA3913375 | ground kitchen Faucet over sink leaks substantially when turned on | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 15 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-18 10:30:00 | Pass | Arrived on site to investigate leaking kitchen tap, station empty, no response via phone calls or door knocksInvestigate leaking sink faucet when water is turned onRemove damaged sink spout, orings and plastic locking broken, Supply and install new sink swivel outlet Test operation and check for leaksPack up and clean up worksite
MSA-DFES | WA3913464 | S.O Dormitory Shower Shower drain blocked in Station Officers dorm | Kensington (old) | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-20 15:00:00 | Pass | Cleared grass out of dg tested and cleared blockage
MSA-DFES | WA3913497 | BA Service Room- 1x twin fluro light not working | Success Career Fire Station (Temp Site) | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-19 14:45:00 | Pass | Located 1 Fluro in store room and 1 Fluro just outside store room not working. Changed 2 tubes in both and new ballast in 1. Tested and energised. Lights working when left site
MSA-DFES | WA3913515 | Bottom Pump - Bottom Dam has low water fault | FESA RHQ - Forrestfield | GMP-BR | Mechanical Services | Pumps (MS) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 14:22:00 | Pass | Thompson pumps attended site during Christmas period after been called directly from applied training to attend. fault has been repaired and works complete. waiting on invoice from Malcolm Thompson pumps
MSA-DFES | WA3913647 | North side of engine room - Charger cable has been pulled out of the roof | CFRS Hope Valley | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 15 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 12:45:00 | Pass | Located damaged ceiling rose. We reconnected the fitting. We proved continuity throughout the DC charging system and proved voltage. All is working.
MSA-DFES | WA3913774 | electric fence near BA house towards front second wire from bottom snapped | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 15 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 15:45:00 | Pass | Repair and replace section of electric fence wire behind BA store Tension remaining fence wires
MSA-DFES | WA3913788 | Training room - glass sliding door lock not working | CFRS Osborne Park | GMP-BR | Building | Doors (BU) | ADVANCED LOCK & KEY | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-18 19:15:00 | Pass | Replace damaged lock to sliding door
MSA-DFES | WA3913904 | Exhaust fan in male toilet located in Transportable out the front of main administration | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-27 13:30:00 | Fail | Located faulty fan in male toilets. Fan was seized. Tested for power and power is available. We need to order in the replacement part and install. Will need to seek approval
MSA-DFES | WA3913910 | Corridors and Reception Void - There are spiders accumulating in all of the high ceilings and window | FESA RHQ - Forrestfield | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-30 08:45:00 | Fail | Carried out inspection of internal areas. Requested internal areas eg. Corridors, high ceilings of reception and office suites cockroaches or not be treated today, as staff around and won't leave until late. As per instructions, I treated around external perimeter of building (unless obstructed or staff around). Treated all safely accessible areas, incl. roofs, around door and Window frames, drains, seatings, portable toilets, wall and paths areas, using a residual insecticide.Carried out a treatment for spiders to the internal high ceilings of the admin block at DFES academy. Used a ULV (ultra low volume) mister to reach all high ceilings to target spider activity/webbing. No entry into academy for at least next 4 hours, when re-entering, be aware of any falling spiders. Please do not brush off webs for at least 2 weeks.
MSA-DTAG | WA3913448 | 1903 basement Apparent drop in pressure caused the fire alarm to be triggered | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 15 Jan 2021 | 2021-01-15 12:28:55 | 2021-01-15 11:00:00 | Pass | Arrived on site and. Found the judges carpark sprinkler system down in pressure there were no active alarms or isolations on the fipPumped system back up to pressure and monitored it - pressure and sprinkler system seemed fine on departure
MSA-DTAG | WA3913454 | 1903 L1 Mazza JA chambers - bathroom Leaking cistern in bathroom | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-15 16:32:00 | Pass | Replaced leaking parts of the toilet. Unable to contact Ian.
MSA-DTAG | WA3913659 | L10 Registry of Births, Deaths and Marriages - lights need to be attended to - see notes | Westralia Square | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-20 09:00:00 | Pass | Arrived on site,signed in , contacted Bree to gain access , discussed with Bree what needed to be done , completed jsa, changed and replaced various tubes and globes , tested lights and all working correctly , cleaned up work area,completed paperwork,signed out ***job complete***
MSA-DTAG | WA3913666 | Level 2 (ground) - Lift 3 displaying out of order. Doors will not open, lift not responding | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-15 15:48:00 | Pass | Job completed - Found right hand car door hanger bolt loose, making doors not align not closing correctly. Made adjustment and tested, lift backin serviceTo be closed out at $0
MSA-DTAG | WA3913846 | level 6, plant room-Noise emitting from Chiller 2 - vibration sound travelling through level5 court | Central Law Courts | GMP-BR-HO | Refrigeration | Chiller (RE) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 15 Jan 2021 | 2021-01-22 17:00:00 | 2021-03-15 07:49:00 | Fail | Attend site with projects Supervisor and carry out assessment of noise. Put pricing together for pipework modifications. Assess spring mounts and found could do with adjustment. Braf submitted. Braf declined.
MSA-DTAG | WA3913908 | sheriff Office, kitchen - water filter taps water pressure low | Supreme Court | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-18 14:59:00 | Pass | Filter service all working okayserviced billi system A402011524
MSA-DTAG | WA3913936 | water leaking from ceiling - in basement | Supreme Court-Supreme Court Library-Basement Level 1 | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 15 Jan 2021 | 2021-01-16 00:48:16 | 2021-01-15 23:08:00 | Pass | Tightened loosen nuts at the hwu.
MSA-DTWD | WA3913746 | Glasshouse power cable has been cut | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-20 14:31:00 | Pass | Arrived on site , signed in , spoke to fm about job, tested to see if circuit was deenergised , circuit was dead, site happy , completed paperwork, signed out ***job completed ***
MSA-DTWD | WA3913750 | C block, Foyer - Fault showing on fire panel (F Block Sip Z5 ST:Conv Flt) | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 15 Jan 2021 | 2021-01-18 17:00:00 | 2021-05-05 07:59:00 | Fail | Fault monitoredRCT - Reactive MaintenancePriority:1 - High PriorityService:NoDescription:C block, Foyer - Fault showing on fire panel (F Block Sip Z5 ST:Conv Flt)Site:5739Location:South Metro TAFE-Mandurah Campus (formerly Peel)Address 1:Education Drive GREENFIELDS-COMPLETED
MSA-DTWD | WA3913815 | ground Remove burnt out bin in walkway between D and E Blocks | Joondalup Kendrew Campus | GMP-BR | Cleaning | Hazardous Materials (CL) | AWB Co. | 2 | CLOSE | 15 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-27 11:45:00 | Fail | Attended site, signed in,spoke to pfm about job, completed jsa,set up work area, removed bin and bin box , removed footing of bin as requested, leveled out dirt on ground, swept up work area , ***job completed ***
MSA-DTWD | WA3913841 | block 8 L1 plant room A/C 4 not running. - attend Monday 18/1 | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 15 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-18 10:33:00 | Pass | Stage 1 compressor fuse blown and burnt out. Replaced with new 3 pole breaker. Checked operation. All ok.
MSA-DTWD | WA3913847 | unit 6 Paint & Dec wash room Power point for chilled water unit pulled out of wall exposed wires | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 15 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-18 08:45:00 | Pass | Replaced broken gpo to water fountain in block 6. Job completed
MSA-DCA | WA3916560 | Mechanical equipment -RO plant is in Fault | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Security | Security Management System (SE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-17 17:19:00 | Pass | After hours call out. Attended call out. L4 Central Plant Room. RO supply tanks low water alarm. RO Plants faulted. Checked pre filters and carbon tanks. Main water on, no supply issues. Reset RO Plant and monitored operation and pressures. No Humidifiers had faulted. Quotation for spare RO Plant pump and RO supply pump will be submitted. Due to age and high demand on both pumps it is recommended that a spare of each are on site.
MSA-DCA | WA3916623 | His Majesty's Theatre-Theatre Building - Chiller 1 - Compressor 2 Fault. | His Majesty's Theatre-Theatre Building | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 16 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-19 14:00:00 | Fail | Airvision attended and completed the repair
MSA-DCS | WA3916555 | all the CCTV cameras in the gate house is not recording and faulty | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jan 2021 | 2021-01-17 06:47:13 | 2021-01-16 09:45:00 | Pass | Attended site and investigated the fault.Found that NVR 2 stop recording.Restarted IndigoVision NVR 2 and conducted test.All back to normal and operational15/2/21 Work order to be invoiced at cost to date. another work order will be released for replace NVR
MSA-DCS | WA3916565 | Burst pipe in unit 7 B4 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 12:19:59 | 2021-01-25 10:30:00 | Fail | This job has been left past due day due to P1s WA3953062 and WA3953081 and also dealing with WA3945766, WA3934769, WA3945926, WA3887610
MSA-DCS | WA3916572 | UNIT 3-ABLUTIONS-No hot water to the site. | Wooroloo Prison Farm-Prisoner Accommodation Unit 3 Block 2 & Ablutions | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 13:08:44 | 2021-01-19 11:30:00 | Fail | Arrived on site and inspected found there is no hot water. Found both lhs and rhs Bosch hydropower not working. Started the lhs hwu. Could not start the rhs hwu. We will come back on Monday to investigate further.
MSA-DCS | WA3916574 | Kitchen holding fridge icing up. unacceptable temp to repaired asap | Casuarina Prison | GMP-BR- HO | Equipment | Building Equipment (EQ) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 13:27:45 | 2021-01-18 08:30:00 | Fail | Arrived on site,unit had defrosted,put fan back in p[lace and turn back on,arcus to arrive at 09:00 on monday to repair.
MSA-DCS | WA3916575 | UNIT 17-Cell A13-Showing up disabled on the system and also showing a fault. | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 13:33:41 | 2021-02-25 07:39:00 | Fail | Attended site on the 16/1/21 for faults on unit 17 FIP. Found 9 faults. faults are missing faults on Aspirating detectors on cells A13-16 and cells C13-16. Had to leave site due to bushfires before I could get investigation underway. I returned the morning on 17/1/21 and went into roof space and used vacuum to clean out units. Will need to return during business hours to reset and reprogram.29/01/21 EI JVRe-attended site L7D59 zone 868 in analogue fault.Device is a Wagner MASD mounted in the 1st floor plant room that detects within the ceiling space above the West Day room.Sample points are not visible & a large step ladder is required to access the hatch and a long extension ladder is then required to access the ceiling space to have a look for the sample points, currently not sighted.In attempting to blow vac the sample pipe the fault cleared for a brief period but returned to fault soon after.Recommend access be provided to clear the sample points.FPS engaged to clean out a
MSA-DCS | WA3916588 | UNIT 4- D14-Cell call has been painted over, control room not receiving. | Hakea Prison-Unit 4 | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 14:45:01 | 2021-01-22 10:00:00 | Fail | 22/01/21 pickup part and travel to site to replace the faulty cell call point. Tested all ok after replacement. CellGuard CI-CC/270/120 X 1.
MSA-DCS | WA3916594 | Unit 1 cell 16 - basin tap constantly running | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Jan 2021 | 2021-01-17 11:38:26 | 2021-01-16 16:18:00 | Pass | Replaced leaking spindles and a15. Unblocked tpilet as well.
MSA-DCS | WA3916622 | SITE COST unit 1 - cell D12 - light fitiing delibratley broken by prisoner, exposing wires | Hakea Prison | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 18:18:34 | 2021-01-18 14:30:00 | Fail | Replaced broken light
MSA-DCS | WA3916624 | CONTROL ROOM- Fault on the fire panel to zones 4 and unit 6. | Bandyup Prison-Entry Building-Ground Floor-Control Room | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 13:30:00 | 2021-01-16 12:08:00 | Pass | Bandyup prison. Call out for fault on a vesda in unit 4. Found filter needing replacing on vesda in J block zone 1. Replaced filter with new one and returned system to normal.
MSA-DCS | WA3916634 | Casuarina Prison - Check systems after systems after power outage. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 19:52:27 | 2021-01-16 20:00:00 | Fail | Attended site.Checked security systems: PDS,CCTV,MDAS,Cell Call located in Crypt and control room.Tested.All ok at departure
MSA-DCS | WA3916635 | Casuarina Prison - Check systems after power outage. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 19:58:39 | 2021-01-16 19:00:00 | Pass | Tested power at distribution boards after power had reset
MSA-DCS | WA3916636 | Casuarina Prison - Check systems after power outage. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 16 Jan 2021 | 2021-01-16 20:01:37 | 2021-01-16 18:10:00 | Pass | work complete
MSA-DFES | WA3933497 | ** Job already attended too ** South West Roller Door is not operational | VFRS Mundaring | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 16 Jan 2021 | 2021-01-18 17:00:00 | 2021-01-16 11:00:00 | Pass | COMPLETED
MSA-DCA | WA3930266 | Mechanical fault - alarm onground floor | Art Gallery of WA - James St | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 17 Jan 2021 | 2021-01-18 14:04:23 | 2021-01-18 13:30:00 | Pass | After hours call out. Attended site. Controllers 8 + 9 in alarm. Controller 9 operating correctly, alarm stuck. Controller 8 no power, FCU 8 no power, breaker at MSB for FCU 8 tripped. Humidifier breaker tripped also. Investigated fault. 1 of the 3 heater banks faulty. Disconnected faulty heater bank. Tested operation of Humidifier. Power on, all alarms cleared. Humidifier operating under design but conditions being met at present. Quotation for replacement of heater bank set to be submitted.Using unit details, requested pricing from manufacturer. Quotation to follow.
MSA-DCS | WA3930285 | Perimeter Fence Monitor is faulty - No Display | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jan 2021 | 2021-01-18 20:51:53 | 2021-01-18 09:15:00 | Pass | Monitor went black overnight. Upon arrival it was working. Checked all connections on back of monitor and PC. Power cycled monitor. Everything functioning normal.
MSA-DFES | WA3930282 | access door to garage won't open and close, won't secure, faulty lock | VFES Karnup | GMP-BR | Building | Materials (BU) | PEEL LOCK SERVICES PTY LTD | 0 | CLOSE | 17 Jan 2021 | 2021-01-17 22:00:47 | 2021-01-17 19:30:00 | Pass | job completed - latch replaced
MSA-DCA | WA3931113 | James Street, Zone 14 requires sprinklers to be relocated | Art Gallery of WA - James St | GMP-BR | Plumbing & Drainage | Drainage (PD) | Earth & Water Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 14:15:00 | Pass | Moved sprinklers out of the way of foot traffic from staff parking on zone 14
MSA-DCA | WA3934341 | Bathroom window is cracked | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 2-M2 - Dressing Room M2 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-10 12:25:00 | Fail | window reglazed with 6.38 trans lami 1275x340 with 3m platform ladder 2 men 2 tube black silicone 1.8 lm 1mm dst tape and 1X 3mm glazing block
MSA-DCA | WA3937191 | Air Con fan is not working | His Majesty's Theatre-Theatre Building-Ground Floor-Kitchen | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-19 10:30:00 | Pass | Investigate VAV G5 serving kitchen and airflow is minimal th trough supply air outlets. Check Chilled water supply and damper position. Ken notified and BAE to be engaged to investigate air flow and reliable controls setup
MSA-DCA | WA3943623 | Plantroom - BMS offline | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - Car Park | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-20 09:00:00 | Fail | Attended site. BMS system and remote access not operating correctly. Raised a P.O. for Schneider to attend. Schneider to have attended site 19-1-21. Carried out tests and checks, reset automation server and checked cabling and configuration of modem. Ran and tested BMS front end access and remote access (ok). It’s is advised a different modem/antenna is utilised along with a Telstra SIM card as signal is inclined to drop in and out resulting in loss of remote access. Works completed, please refer to attached Schneider service report for in depth analysis and findings.
MSA-DCS | WA3930731 | Health, Cage Door- Lock is jammed | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 07:16:20 | 2021-01-20 11:00:00 | Fail | Attend side to service locks on Health cage door. Requires parts. Reattend site with parts. Install new OFR cylinder.
MSA-DCS | WA3930734 | Jeelia, B Wing Lounge Door- Lock is jammed | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 07:18:37 | 2021-01-18 13:30:00 | Pass | Adjusted cam on cylinder.
MSA-DCS | WA3930737 | Unit 14, Cell C7- Lock on the judas hatch will no longer lock, latches but does not lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-25 11:30:00 | Fail | Temp. repair barrel.Replace barrel.
MSA-DCS | WA3930742 | Gym- Prisoner changeroom- Tap & pipe under basin is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-17 13:07:00 | Fail | Nill
MSA-DCS | WA3930761 | Unit 14, A & C Day Room- refrigerated cold water system not working. | Casuarina Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-15 10:15:00 | Fail | Chiller removed for repair or to be replaced installed chiller after manufacture repairs
MSA-DCS | WA3930765 | Bakery- Hot water urn in day room leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-03 12:05:00 | Fail | Replaced silicone tube kit and inlet solenoid
MSA-DCS | WA3930782 | Unit 5, A & C day room power point broken | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-18 10:00:00 | Pass | Replaced damaged gpo in unit 5 dayroom
MSA-DCS | WA3930783 | INF (10)- Floor buffer PV2160373 exposed wires plug broken | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-18 13:00:00 | Pass | Repaired damaged floor polisher in infirmary
MSA-DCS | WA3930785 | Unit 4, Cell A7- Cell window has fallen out (window stored in SO's office) | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-22 10:30:00 | Fail | SPIRAL BALANCES RENEWED & PULL HANDLE REFIXED
MSA-DCS | WA3930790 | Unit 13, Cell A11- Shower is blocked (plunger does not work) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-28 14:30:00 | Fail | Nill
MSA-DCS | WA3930793 | Unit 13, Cell D9- Tap head is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-28 15:30:00 | Fail | Nill
MSA-DCS | WA3930797 | Unit 2, A Wing- Main shower door very hard to open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-03-05 13:00:00 | Fail | REPLACE HINGES
MSA-DCS | WA3930800 | Security area- Service duct door SHU ally. Key watcher 3 lock is broken on door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 11:35:41 | 2021-01-18 10:30:00 | Pass | Service and replace bolt throw -SHU ally Service duct.Replace lock - Key watcher front gate.
MSA-DCS | WA3930806 | Unit 13, B & D Day Room- Cold water fountain is leaking from inside | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-03 10:30:00 | Fail | Replaced jug filler and bubbler
MSA-DCS | WA3930812 | Unit 1, Cell D12- Cell Call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 07:44:30 | 2021-01-18 14:00:00 | Pass | Had to wait for Trauma Clean to finish cleaning the cell before ai could access it. Cell call not activating when call button pressed. Replaced intercom and installed RJ45 wiring adapter. Tested loud and clear in cell and in control. Parts used:Cell Guard CI-CC cell intercomCell Guard RJ-45 adapter
MSA-DCS | WA3930816 | ISU, Cell B08- scratched camera lense | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-07-06 15:30:00 | Fail | Camera replaced under WA4354775. Camera in B05 also damaged. Replaced Perspex cover with site spare. Cells B05, B06, B07 and B08 all have clear images. Parts used:Bosch Flexidome 9000 lens protector S-F01U296019
MSA-DCS | WA3930817 | Medical - Air Con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-01 14:01:00 | Fail | Complete. Defrosted coil and monitored for a number of days. All okay. Access panel not required at this stage. May be required in the future.
MSA-DCS | WA3930834 | C8,C9 and D1 light switches broken Light Switch Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 10:00:00 | Pass | Replaced broken light switches
MSA-DCS | WA3930837 | Unit 10 B4 Light Switch Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 11:00:00 | Pass | Replaced broken light switch U10 B4
MSA-DCS | WA3930839 | unit 9 D7 Light Switch Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 12:30:00 | Pass | Repaired broken light U9 D7
MSA-DCS | WA3930843 | Gatehouse- Antiram barrier faulty & the pins are not engaging on the internal eastern sallyport door | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 12:14:54 | 2021-01-18 16:00:00 | Fail | 18/01/21Picked up scissor lift.Checked all functionality of anti ram.Carried out full diagnostics on relays etc.Access control issue has been determined.Internal drive pins could not find fault.
MSA-DCS | WA3930846 | Unit 7 F Wing Cleaning Cuboard Light Switch Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 12:00:00 | Pass | Replaced light switch
MSA-DCS | WA3930849 | Hakea West Side Pump- Pump faulty, see notes below | Hakea Prison | SPA-BR | Mechanical Services | Pumps (MS) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 07:46:12 | 2021-02-03 16:30:00 | Fail | Investigate faults with Hakea West pumps, drain and inspect irrigation storage tank.Submitted BRAF 12-4-20212 with report and cost.
MSA-DCS | WA3930852 | Unit 7 Control room Fire Alarm System continually activating | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 14:10:00 | Pass | VESDA reset OK
MSA-DCS | WA3930853 | Unit 2, Cell D1- Cell call not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 08:23:42 | 2021-01-19 14:45:00 | Fail | Replaced cell all in unit2 D1. Tested and working as per normal.
MSA-DCS | WA3930857 | Unit 5, Jacques intercom system is not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 08:25:00 | 2021-01-20 08:30:00 | Fail | Restarted the service and switched ports on back of amplifier. Tested. Everything working as normal
MSA-DCS | WA3930859 | Unit 6, N Wing Cleaning Cupboard - Tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 10:10:00 | Fail | Replaced 1/4 spindle
MSA-DCS | WA3930861 | Unit 8, Cell A10 - Tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 10:30:00 | Fail | Replaced leaking and corroded tap
MSA-DCS | WA3930862 | kitchen water leaking into lights | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 12:28:54 | 2021-01-19 14:00:00 | Fail | Replaced water damaged lights after leak was repaired and ceiling dried.
MSA-DCS | WA3930863 | CCU, Cell H11- Camera lens damaged | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 08:29:52 | 2021-01-18 15:30:00 | Pass | Camera ok, Perspex viewing window scratched by prisoner. Removed and replaced viewing window. Tested ok. Parts used:Bosch SPP camera window S-F01U296091
MSA-DCS | WA3930867 | kitchen bakers oven keeps tripping out | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 12:31:18 | 2021-01-18 11:00:00 | Pass | Isolated water damaged bakers oven, requested plumbers, requested Bake-Quip to attend after water leak is repaired and test bakers oven before commissioning again.
MSA-DCS | WA3930868 | Unit 8, D Wing - PA Speaker faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 08:30:00 | Pass | Adjusted the output volume of the PA amplifier to stop the D wing speaker from cutting out. All areas tested ok.
MSA-DCS | WA3930871 | Unit 7, E Wing Dayroom - Window is cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-22 12:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3930874 | Unit 2, A & C - Toaster keeps tripping power | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-21 14:00:00 | Pass | Investigated and tested and decommissioned faulty commercial toaster in unit 2
MSA-DCS | WA3930879 | Laundry - No power to cleaning room | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 15:00:00 | Pass | Investigated power loss to cleaning room in laundry. Restored power and tested
MSA-DCS | WA3930888 | Unit 5, Cell A14- Main lock faulty, see notes below | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 12:47:31 | 2021-01-18 10:30:00 | Pass | Attend site, replace main cell lock with refurbished unit. Tested.
MSA-DCS | WA3931115 | control room zone temper EO1 SN1 TU21 fault | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 08:57:29 | 2021-03-08 15:00:00 | Fail | Replaced reed switches on faulty EC cabinet 2. Tested and working. No other open faults on senstar screen.
MSA-DCS | WA3932540 | kitchen water leak into the oven tripping everything | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 13:20:16 | 2021-01-18 14:30:00 | Fail | Found 40mm hot ring main in kitchen roof with a pin hole flooding the ceiling, isolated main and made repairs, ring main very corroded
MSA-DCS | WA3932859 | MPU (8)- Power socket knocked out of wall. See further notes below | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 09:25:36 | 2021-03-24 10:30:00 | Fail | Organised access to remove safe in front of damaged gpo. Replaced damaged gpo and tested
MSA-DCS | WA3933055 | unit 1 D wing showers Waste pipes damaged under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 09:17:57 | 2021-01-18 11:45:00 | Pass | Replaced broken trap and waste polipe
MSA-DCS | WA3933120 | SITE COST Unit 2, Cell B13- Viewing hatch, metal plate missing. See notes below | Casuarina Prison | WSM-BR-SITE | Building | Windows (BU) | Midolo Building Services | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 13:28:40 | 2021-01-18 16:45:00 | Fail | FRAME REPAIR & REPLACED DAMAGED PARTS
MSA-DCS | WA3933505 | Bakery, Workshop - automated tap, pin is broken on power pack | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-03-31 15:30:00 | Fail | Supplied a new power pack for the Electricians to wire up.Handed it to the maintenance office
MSA-DCS | WA3934723 | Unit 5, Cell B13- metal rod that helps hold the window in place has come loose from the frame. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 12:00:00 | Pass | WINDOW FRAME REPAIRS CARRIED OUT & SPIRAL BALANCES RENEWED
MSA-DCS | WA3934769 | Back of Unit 5, Water leak, water bubbling out of ground. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 10:00:23 | 2021-01-20 15:30:00 | Fail | 18/1: investigate, ensure area is safe and create material list
MSA-DCS | WA3935295 | Unit 3, Cell C2- Drum to lock is broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-03-03 11:30:00 | Fail | Install cylinder escutcheon. Require parts.Replace barrel, door plate, lock, hinges and weld on strike.
MSA-DCS | WA3935432 | Unit 4, Cell D2- Cell light is rusted out (was flooded with water) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-20 10:00:00 | Pass | Repaired faulty lights in unit 4 d2
MSA-DCS | WA3936093 | Unit 4 - B Wing - Water pressure in cell B12 is low. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-11 10:30:00 | Fail | Nill
MSA-DCS | WA3937711 | Main stores, Purchasing office - Crack in the main Door Glass | Hakea Prison | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 10:00:00 | Pass | DOOR GLASS PANEL REPLACED
MSA-DCS | WA3937840 | Unit 10, Cell B11 Plumbing duct- Pipe from sink waste cracked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 10:53:00 | Fail | Replaced trap and adjusted pipework
MSA-DCS | WA3938357 | Market Gardens - Solenoid broken - see notes | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-21 11:30:00 | Pass | RELOCATED VALVE FROM CURRENT POSITION TO NEW LOCATION ON THE OTHER SIDE OF THE ROAD AND RECONNECT AND REWIRE TO EXISTING SYSTEM.
MSA-DCS | WA3938987 | Market Gardens solenoid broken - see notes | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-21 09:30:00 | Pass | RELOCATING VALVE TO OTHERSIDE OF ROAD AND MAIN LINE TAKE OFF NO LONGER REQUIRED.
MSA-DCS | WA3939623 | Unit 13-18 - Investigate regithermic oven in unit 13 to 18 power loss | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-03-19 07:49:00 | Fail | Investigated switchboard in unit 13-18 to move regi ovens to essential power. Installed and removed loggers
MSA-DCS | WA3939655 | Unit 6, Cell A20- Tap Broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 11:20:00 | Fail | Replaced leaking and corroded tap
MSA-DCS | WA3939681 | Unit 7, Cell E17- Water leaking from under sink, pipe split | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-27 09:00:00 | Fail | Replaced loosen toilet and seat
MSA-DCS | WA3940029 | Bakery- Bun rounder Blade broken | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-03-09 12:15:00 | Fail | 09/03/21Sign in Locate unit in stores Found front cover broken by strapping Remove unit to safe working area Found blade broken and missing Locate knife in bakery inside prison Wait for delivery of partExpose knife assemblyTig weld knife in placeCheck operation Reassemble unit
MSA-DCS | WA3940121 | Unit 5, House 10- Cell Call no out going | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 15:52:10 | 2021-01-20 07:45:00 | Fail | Fitted new connections to comms board. Tested. Everything working as normal
MSA-DCS | WA3940569 | kitchen bakery oven has had water leaking on it and not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 12:01:37 | 2021-01-19 13:20:00 | Fail | COMPLETED 19/1/21
MSA-DCS | WA3940694 | Sewege plant soda ash pump not working | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 12:05:33 | 2021-01-19 17:34:00 | Fail | Flushed soda ash lines, removed blockage. Dosed tank with soda ash to bring from 4.6 to 7.1. DE circulated seage to mix soda ash solution.
MSA-DCS | WA3942003 | Unit 1, Cell A16 - Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-18 15:25:00 | Pass | Replaced 2x leaking spindles
MSA-DCS | WA3942014 | Unit 1, Cell A1 - Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-18 16:30:00 | Pass | Replaced leaking spindle
MSA-DCS | WA3942015 | Unit 1 C15 Bottom Bunk Light not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-29 15:00:00 | Fail | Repaired bed light
MSA-DCS | WA3942123 | Unit 1, Cell C15 - Shower & Sink Taps Leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 12:34:34 | 2021-01-18 14:50:00 | Pass | Replaced 3x leaking spindles
MSA-DCS | WA3942232 | Bakery- Bread divider D20, hydrolic ram issue | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-04-29 16:00:00 | Fail | RETURNED TO SITE 29/4/21
MSA-DCS | WA3942669 | Laundry, Cleaning Store - Washing machine is not working, no power to it, | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-17 12:00:00 | Fail | Laundry cleaning Store washing machine faulty, no power to it. Electricians checked power supply in room all working. Check machine & controls, remove for repair. Dismantle, all legs seized, seals breached, full rebuild required. Make necessary repairs. Assemble & test. All working, return to store.
MSA-DCS | WA3943632 | Abattoir- broken power switch on slaughter floor | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-22 10:00:00 | Fail | Investigate damaged switch.Source replacement parts.Replace damaged switch.
MSA-DCS | WA3943827 | unit 1 C and D wings cells 1,2, and 14 fire alarm panel coming up with 2 faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 12:26:00 | Pass | cleared sampling points
MSA-DCS | WA3943897 | Level 2, corridor - over head fluro lights out - above Cathies desk | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-19 10:00:00 | Pass | Repaired lighting on level 2
MSA-DCS | WA3944023 | Unit 9 - Cell B - Personal lock jammed | Hakea Prison | WSM-BR-SITE | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 22:23:56 | 2021-01-19 10:15:00 | Fail | Attend site after hours. Unit 9 cell C9 personnel lock failing. Gained entry, returned to site next day with required replacement cylinder.
MSA-DFES | WA3943683 | L2 male toilet cubicle 4 is blocked - see Ian prior to attendance | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-19 08:45:00 | Pass | Sign in investigate blocked toilet, fill in take 5,Plunge toilet several times, test several times found nothing wrong, possibly push buttons not pushed properly to flush all paper etc.all job complete
MSA-DFES | WA3943715 | Change Room 2- Exhasut Fan isnt working at all | VFRS Kwinana | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-22 12:45:00 | Fail | Identified faulty exhaust fan. Replaced old fan with new. All working.
MSA-DFES | WA3943739 | main door for amenties cannot be opened by handle, can uplock handle goes up and down | VFRS Kwinana | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-22 11:30:00 | Fail | Pull apart lock find that old spindle spacer had disintegrated. Replaced spring behind the spindle behind the handle which will now hold the spindle in the correct position and fix the lock.
MSA-DFES | WA3943781 | Back of pump house- Hot & Cold water taps are leaking out of the tops | VFRS Kwinana | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-19 14:21:00 | Pass | Replaced tap
MSA-DFES | WA3943871 | ground garden & lawn Retic repair, check/refurbish sprinkler head front near driveway is damaged | CFRS Osborne Park | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-30 12:30:00 | Fail | Retic Repaired
MSA-DTAG | WA3930880 | All court rooms and Judicial Chambers hot air blowing- see notes | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 12:36:25 | 2021-01-18 12:00:00 | Pass | Travel to site. Access BMS and found all fantail unit room temps to be 30 degrees. Check chiller plant and found all 3 chillers in fault. Access roof and check faults. Found chillers 4 and 5 to have system failed fault. Found chiller 3 to have freeze protection fault. Reset chillers and check operation. Found all 3 chillers to start and operate as normal. Check operation pressures and temperatures found to be normal. Monitor operation for a couple of hours and found no issues. Possible power supply issues has caused unit failures. No other issues found with chillers.
MSA-DTAG | WA3931502 | 1903 L2 jury room bathrooms bees in the bathroom | Supreme Court | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-19 08:25:00 | Pass | Bees activity in court 2 toilet no access due to court in progress.
MSA-DTAG | WA3934604 | ground In Session” Button not working in Room 5.06 | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-18 12:00:00 | Pass | Attended Room 5.06 In Session button not working, reterminated switch connection. Tested, all OK.Job completed
MSA-DTAG | WA3936723 | Lvl 5, Lift Lobby- Temperamental swipe access, further notes below | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 13:00:00 | Pass | Attended Level 5 West Door, tested card reader OK. Reset Door Controller and checked logs, found wrong PIN codewas used.Job completed.
MSA-DTAG | WA3944015 | Registry area - Air conditioner not working properly (Room Temp registering at over 25 degrees) | Mandurah Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-27 16:00:00 | Fail | Completed repairs to system 1 as per work notes
MSA-DTWD | WA3930681 | Air conditioner cooling tower- Loud tapping noise from tower CT2. | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 18 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-19 10:30:00 | Pass | Adjusted the condenser fan cowling
MSA-DTWD | WA3930858 | B block brick has been thrown through window | East Perth Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 18 Jan 2021 | 2021-01-18 12:23:39 | 2021-02-12 12:00:00 | Fail | ATTENDED SITEBOARDED UP BROKEN PANEL2-1710 X 1220 PLUS 10 SCREWS2 MEN REQUIREDRETURNED LATER DATE TO REGLAZE 6MM GREY HEAT SOAKED TOUGHENED SAFETY GLASS1-1710 X 217015.5 L/M OF RUBBER REPLACED4 MEN REQUIRED
MSA-DTWD | WA3934081 | C block cafeteria - Auto door to cafeteria has a fault displayed | Bentley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-18 12:24:00 | Pass | 1069298. Found door in lock mode fault, reset door and checked over, tested all ok, advised facilities that faulty may be caused from turning door to auto mode before unlocking manual lock
MSA-DTWD | WA3935541 | E Block, AHU 5 not working | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-19 10:00:00 | Pass | Attended site as requested and completed pre-startpaperwork. Accessed AHU 5 and found to not be running.Traced fault to fire alarm panel on ground floor , switchwas set to off position. Reinstated to auto and test ranunit, running all ok.
MSA-DTWD | WA3941466 | T block L2 drinking fountain east end that is not working correctly | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 14:05:00 | Pass | Unit cannot have a bottle filler added to it liaised with service manager/Zip and site and advised accordingly
MSA-DTWD | WA3943698 | M Block, Male Student toilets- Urinal button is broken | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-02-19 13:45:00 | Fail | Replaced broken cistern button
MSA-DTWD | WA3943703 | 25Aberdeen Museum St Entry-Various bricks sticking up creating trip points | Perth Campus B1 | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-03 14:30:00 | Fail | Repair paving
MSA-DTWD | WA3943724 | Air Con not cooling | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 11:22:00 | Pass | Hey 10 actuator for 10b east dampers works carried. Airflow and actuator movement now free. Temps to area via bms at 22.31 degrees.
MSA-DTWD | WA3943768 | A block L1 control room BMS will not log on | East Perth Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-20 10:00:00 | Fail | Checked BMS and rectified the issue.
MSA-DTWD | WA3943878 | L1 Lighting multiple lights blown - Please have AJ attend | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-17 10:30:00 | Fail | Repalced multiple lamps and control gear to areas as shown by site.job completed
MSA-DTWD | WA3943886 | O block Retic O block south leaking mainline. | Balga Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 16:00:00 | Pass | Locate and repair broken reticulation pipe, recommission system.
MSA-DTWD | WA3944009 | M block, M009 - Room 009 the air conditioning doesn't seem to be working. | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 18 Jan 2021 | 2021-01-21 17:00:00 | 2021-04-16 15:00:00 | Fail | Accessed site completed relevant sign in procedures and covid safe app wa requirements, accessed m block roof , electrically isolated apac unit , removed faulty condenser fan and 30uf capacitor and replaced with new , reassembled and reinstated power , tested operation all ok
MSA-MRWA | WA3943682 | Café area East - Investigate run signal to AC units switching on/off repeatedly | Don Aitken Centre MRWA Head Office-Main Building-First Floor-Cafe Area | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Mizco Pty Ltd | 1 | CLOSE | 18 Jan 2021 | 2021-01-19 17:00:00 | 2021-01-20 09:00:00 | Fail | Repairs to air con
MSA-DCA | WA3945603 | High Humidity alarm in Batavia Gallery. Please investigate | Shipwreck Galleries-Main Building-Ground Floor-Batavia Gallery | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-03-04 14:30:00 | Fail | Attended site. Batavia gallery humidity out desired limits. Applied tests and checks. Investigation found boiler to have tripped out. Engaged boilertronics to attend site. Isolated and dismantled boiler to investigate possibility of build up of ingress in to HX, pumps, & check valves (ok) with no signs of build up. Reassembled boiler and tested operation. Reinstated BMS to dehumidification mode for batavia gallery. System operating correctly.
MSA-DCA | WA3945783 | Slip street cable gate will only raise a few inches before stopping. Please inspect. | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-11 16:10:00 | Fail | Tested unit found the clutch faulty. Being so close to the water it’s corroded. Also had to man handle the 180 key barrel to open it. It is now operating after a bit of lubricant but might fail again so please quote as a second item to replace. Ps could not locate programmed asset no. Braf raised and approved.Returned to site Replaced motor and door latch. Tested operation, all ok.
MSA-DCA | WA3946159 | Main care park - Car park auto gate not operating | Shipwreck Galleries-Main Building-Carpark | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-20 10:57:00 | Pass | A40029595N. Call to site. Attend to auto gate. Restore gate to running rail, remove excessive build-up of sand and debris from local area. Test operational and safety features of unit for several operations - all okay now.
MSA-DCS | WA3945505 | Unit 6, Lunch Room - Tap in the tearoom continually dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 13:30:00 | Pass | Nill
MSA-DCS | WA3945508 | Unit 2, Cell A9- Finger tab on viewing hatch missing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 19 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 14:15:00 | Pass | REPAIRS TO VIEWING HATCH SLIDING SCREEN COMPLETED
MSA-DCS | WA3945512 | INF (10) - Obs Cell 3 Lock appears to be loose | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 19 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-27 10:30:00 | Fail | Cell Occupied - No Access.Service lock, resecure fixings with loctite
MSA-DCS | WA3945516 | Unit 2, Cell C9- Sink grate missing. (further notes below) | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-27 11:05:00 | Fail | Replaced grate
MSA-DCS | WA3945528 | Unit 1, Cell D2- Vinyl damaged on walls | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 07:39:22 | 2021-01-21 12:45:00 | Fail | DAMAGED AREAS OF WALL VINYL REPLACED
MSA-DCS | WA3945530 | Unit 1, Cell D12- Toilet push button faulty. Futher notes below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 07:37:57 | 2021-01-19 15:30:00 | Pass | Replaced faulty button mechanism
MSA-DCS | WA3945534 | Courts, Passage between 6 and 7- Light fitting broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 13:30:00 | Pass | Replaced and repaired broken lights
MSA-DCS | WA3945536 | Unit 9, Cell B4- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 11:30:00 | Pass | Repaired bed light
MSA-DCS | WA3945538 | Unit 7, G Wing Cleaning Cupbaord- Drain Blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 12:00:00 | Fail | Unblocked badly blocked drain
MSA-DCS | WA3945545 | MMS, Cell B1- Cell call not operating correctly | Broome Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 07:47:05 | 2021-02-04 20:00:00 | Fail | Ran new cable to cellcall. Installed new CI8A controller as it was still sending false calls when cable disconnected. Tested overnight. No more troubles. Functioning as per normal.Used 115M of underground Cat6 cable and One CI8A Controller.
MSA-DCS | WA3945553 | SITE COST Internal perimeter fence - D4 & D7 mircowave is not resetting | Casuarina Prison | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Jan 2021 | 2021-01-19 11:49:22 | 2021-01-19 10:30:00 | Pass | D4 Microwave internal voltage was low. 4.8v. Reset the unit and it went back to normal voltage. Zone is sealed. D7 PE Beam had bird feces on cover. Cleaned and reset zone. Zone is sealed. Internal permitted functioning per normal.
MSA-DCS | WA3945560 | CCU, Cell C8- Window Broken | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 07:46:40 | 2021-01-20 11:45:00 | Fail | FRAMEWORK REPAIR, MODIFY, RESET - RE-INSTALL AND SECURE EXISTING GLASS
MSA-DCS | WA3945580 | Unit 3 C wing dayroom broken window | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 08:04:21 | 2021-01-19 16:00:00 | Pass | DAYROOM WINDOW REGLAZED, REPAIRS MADE AND WELDING TO SECURE
MSA-DCS | WA3945591 | Unit 5, Door to main electrical room- Door handle damaged | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 08:24:19 | 2021-01-19 09:30:00 | Pass | Attend site and repaired handle on unit 5 main electrical door.
MSA-DCS | WA3945592 | Unit 13 - A5 shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-29 09:23:00 | Fail | Nill
MSA-DCS | WA3945606 | Low battery warning on the alarm | Riverbank | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-19 13:15:00 | Pass | Inspected 2 x houses and 1 x main building and found no low battery condition. Found house #1 has fail to communicate trouble condition. Found house #2 has date and time trouble (rectified as required, tested all ok). Cant locate the main control panel on the main building (tried to ask Karl M, Erwin D and Michael Z for the panel whereabouts but to no avail, no one knows). No trouble condition on main building
MSA-DCS | WA3945609 | unit 3 wall urn not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-22 14:50:00 | Pass | System on and working on arrival. Checked filter, all good was only changed on 7/12/20. Made sure system was getting water and heating. All good. Also checked out unit 5 chilled issue as well
MSA-DCS | WA3945676 | Unit 3, Cell B10- Toilet is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-29 10:30:00 | Fail | Nill
MSA-DCS | WA3945677 | unit 13 cell A6 water not coming out of taps | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-28 14:27:00 | Fail | Nill
MSA-DCS | WA3945691 | SITE COST unit 3 cell 25 lock is broken | Wooroloo Prison Farm | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 19 Jan 2021 | 2021-01-19 13:37:29 | 2021-01-19 13:30:00 | Pass | Replaced broken lock on Cell 25 Unit 3 New lock keyed and fitted .
MSA-DCS | WA3945726 | Kitchen- Bell not reaching temperature | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 10:05:44 | 2021-01-19 13:09:00 | Pass | Kitchen Bell not reaching temperature. Check kettle & controls, no ignition. Agent dismantled & replaced ignition module. Assemble all & test.
MSA-DCS | WA3945766 | Unit 6, Cell D8- Pipe leaking in plumbing duct | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 15:30:00 | Pass | Nill
MSA-DCS | WA3945776 | Kitchen - Deep fryer not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 10:50:17 | 2021-02-26 15:30:00 | Fail | 20/1/21Attended kitchen Issue - Gas Deep fryer not workingFound problem with thermostat system, not responding when reached temperature.Parts required 1 x thermostat 1 x thermopile 26/2/21Fitted parts to fryer and checked operation of thermostat.
MSA-DCS | WA3945812 | Unit 3 B14 Basin tap requires replacement, seat broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 11:00:19 | 2021-01-19 17:53:00 | Pass | Replaced corroded tap
MSA-DCS | WA3945823 | main kitchen main oven not going to temp reset gas code coming up and making funny noise | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 19 Jan 2021 | 2021-01-19 15:11:41 | 2021-02-01 13:00:00 | Fail | Returned 1/02 and replaced parts as approved.
MSA-DCS | WA3945836 | Unit 5, A wing - cell ventilation not working (from cell A7 onwards) | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 11:17:20 | 2021-03-05 11:30:00 | Fail | Repaired cell vent fans.
MSA-DCS | WA3945872 | Recreation, Resident toilet- sink is blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 11:53:00 | Pass | Unblcoked basin drain.
MSA-DCS | WA3945879 | Assessments, Staff Kitchen- Sink tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-25 13:10:00 | Fail | Replaced leaking and corroded tap
MSA-DCS | WA3945881 | Unit 8, Control Room- Door Control monitor is blank | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 11:53:51 | 2021-01-19 15:30:00 | Pass | Monitor power tested ok. Input source correct. EBI Station program froze and shut down. Restarted work station PC. Logged into Station program and setup CCTV monitors. Doors tested ok.
MSA-DCS | WA3945882 | Unit 6, Cell A24- Main Door Lock not operational ( Doesn’t unlock sometimes, jamming up ) | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 11:55:23 | 2021-01-19 14:50:00 | Pass | Attend site and swapped out main lock on unit 6.
MSA-DCS | WA3945889 | kitchen ant infestation | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 11:39:10 | 2021-01-20 08:20:00 | Pass | Treatment of main kitchen ant infestation and external areas.
MSA-DCS | WA3945894 | Reset (formally Outcare) located outside the prison blocked sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 12:07:38 | 2021-01-20 08:57:00 | Pass | Unblocked Sink
MSA-DCS | WA3945903 | abittior container freezer not working | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 12:15:30 | 2021-01-21 08:56:00 | Fail | system low on refrigerant , carried out a leak check, found leak in condenser . system not repairable
MSA-DCS | WA3945920 | Unit 5, C2 - cell window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-22 13:30:00 | Pass | NEW SPIRAL BALANCES INSTALLED
MSA-DCS | WA3945926 | Amenities - Bad water leak, Burst pipe below ground…. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 12:37:43 | 2021-01-20 11:30:00 | Pass | Nill
MSA-DCS | WA3945930 | Reception - Light requires to be removed to allow access for plumbers to make repair on leaking pipe | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-03-23 15:00:00 | Fail | Organised access, removed ceiling light for plumbers, returned once leak was fixed, repaired and reinstalled
MSA-DCS | WA3945963 | Unit 1, shower block - leaking shower | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3945967 | little ants in numerous locations | Wandoo Rehabilitation Facility | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 13:30:00 | Pass | Ant Treatment Using Termidor To Music, Education & Library And Spot Treat Rests On Oval And Paths.
MSA-DCS | WA3945968 | Education center, kitchen- Urn Faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-22 09:30:00 | Fail | Water to Prison off this afternoon unable to carry out job RETURNED 21.2.21 once access given unit is instantly tripping power disconnected element not tripping needs warranty call for replacement element organised warranty callout Zip Econoboil
MSA-DCS | WA3945969 | Unit 2, Cell A5- Metal frame work missing on inside of viewing hatch (leaving glass exposed) | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-18 10:00:00 | Fail | FRAMEWORK REPAIRS COMPLETED
MSA-DCS | WA3946004 | unit 2 perimeter gate officer keys getting stuck in lock | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 13:31:47 | 2021-01-20 15:45:00 | Fail | Attened to site , pedestrain gate to unit 2 - needs new lock ( non stock item ) informed site that i would source a new lock and return , another day .Returned next day ( after phoning site in the morning - and site said no escorts available - come on Friday )Maintenance called me later that day - and asked when i could return - as above i had already tried to get booking but Prison escorts was unavailable )made it back today Wednesday and completed work New lock and cylinder fitted .( after Prison eventually organized themselves )
MSA-DCS | WA3946011 | WWTP, Pump House- Seals leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-28 13:30:00 | Fail | work complete
MSA-DCS | WA3946016 | SHU (9) - West hot and cold tap won't turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-02-08 08:30:00 | Fail | Nill
MSA-DCS | WA3946108 | kitchen fault with HWS | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 14:55:28 | 2021-01-21 10:55:00 | Fail | COMPLETED
MSA-DCS | WA3946131 | Reception - Office VP Room Key jammed in lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 19 Jan 2021 | 2021-01-19 19:22:06 | 2021-03-26 10:00:00 | Fail | Remove jammed key from lock, service lock, replace bolt throw temp. repair requires all worn VP to be replace before new lock can be installed.Waiting for Security to order new keys and install onto key bunches.Install new lock keyed to VP key.
MSA-DCS | WA3946140 | Unit 6 - B Wing grille not opening on button press | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 15:27:06 | 2021-01-20 14:02:00 | Pass | Followed up with site site will call afd to get the motor fixed
MSA-DFES | WA3945737 | Appliance bay -mesh on bottom of engine bay doors where it has been damaged/become loose. | CFRS Welshpool | GMP-BR | Building | Doors (BU) | Go Doors | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-03-19 16:45:00 | Fail | Complete
MSA-DFES | WA3945752 | compressor room from house, air con not working | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-09 15:57:42 | Fail | Replaced compressor on compressor room aircon. Ran system up and confirmed correct operation
MSA-DFES | WA3945755 | Lecture Room 4 - Air Con isnt blowing cold air | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 09:30:00 | Pass | Service call completed
MSA-DFES | WA3945873 | entrance ceiling tiles have come off metal and roofing hanging down | CFRS Daglish | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-13 11:00:00 | Fail | Attend site and repair ceiling
MSA-DFES | WA3945919 | Simulation Centre kitchen HWS has constant flow of water running from relief pipe into sink | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 14:50:00 | Pass | Urn still has Zip warranty reported to site and asked to arrange warranty call to get float valve replaced under warranty -
MSA-DFES | WA3945927 | Simulation center/underground bunker - ducted aircon not working - is on only on 1 stage. bl | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Ducted Split System (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-17 12:27:00 | Fail | Braf not approved
MSA-DFES | WA3946027 | Station Officer’s Ensuite- Inner lip of the bowl was broken by a falling can of Glen 20 | CFRS Osborne Park | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-11 12:00:00 | Fail | Replaced toilet due to was cracked and dangerous
MSA-DFES | WA3946095 | Simulation Centre -Evidence of mouse infestation in kitchen cupboards | DFES Regional Office - Belmont | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 13:35:00 | Pass | Treated for rodents and cockroaches. Attrathor and gel bait to appropriate spots internal areas. Repellant residualspray external perimeter and around drains and penetrations. Placed 4x baited Peti stations to internal areas.
MSA-DTAG | WA3945608 | Basement, Custody - Existing door closer seized | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-22 16:15:00 | Pass | New door closer installed
MSA-DTAG | WA3945613 | Exterior Court 3 - Electronic Gate locking plate not connecting as gate has come out of alignment | Armadale Courthouse | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-19 12:00:00 | Pass | Remount catch plate on magnetic lock
MSA-DTAG | WA3945649 | ground rear garden Retric on rear lawn and side lawn does not appear to be working | Perth Children's Court | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-24 16:00:00 | Fail | Repair Broken Pipe & Fittings from Tree roots
MSA-DTAG | WA3945650 | Basement, Custody - Garage door on sallyport – left side closes at different speed to right | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | AFD Contracting | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-19 14:20:00 | Pass | Inspect operation testing okcleaned track and all ok
MSA-DTAG | WA3945656 | Basement, Custody- Existing toilet door strip cell 1 perished | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-02-16 09:00:00 | Fail | DOOR STRIP SEAL REPLACED
MSA-DTAG | WA3945745 | Lvl 4, pump room- Water pump fault – circuit constantly tripping (new pump required) | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-30 09:30:00 | Fail | Replaced faulty pump. NoPower to it
MSA-DTAG | WA3945746 | CCTV camera 13 not working - see notes | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-16 07:00:00 | Fail | Work performed by Cian O'Halloran 19/01/2021:Attended site, camera not accessible without boom lift and prior arrangement with site due to parking spaces 34, 35 and36 being in front of camera. Reset camera and attempted to ping camera. Camera has failed and will need replacing.Work performed by Cian O'Halloran & Drake Van der Merwe 16/02/2021:Attended site. Replaced Camera 113 on Pole 7. Set up and tested.Job completed.APPROVED BRAF ATTACHED.
MSA-DTAG | WA3945749 | Ground, Registry- Broken seat (replace from stock stored in level 6 plant room) | Central Law Courts | WSM-BR-SITE | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 08:30:00 | Pass | SEAT REPLACED (FROM EXISTING STOCK ON SITE)
MSA-DTAG | WA3945771 | Ground, FIP -Technician required from 08.00am Saturday 23 January 2021 until approximately12 noon | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 08:20:00 | Pass | Completed HVAC testing on level 1. System normal on departure.
MSA-DTAG | WA3945774 | L14 Door 14.04 – when securing door continues to beep - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-20 10:30:00 | Pass | Attended Level 14 Door 14.04 Card Reader intermittently beeping on Exit. Reconfigured Card Reader settings andtested, OK.Job completed.
MSA-DTAG | WA3945805 | 1903 & 1987 -FIP Technician attend 06.30am Saturday 23 January 2021 assist with power shut down | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 15:15:00 | Pass | Work performed by Lee Kiok 23/01/2021:Attended site and assisted Security System for Power Shut Down.Found Camera 113 offline prior to Shut Down.Affected Equipment: Reception & Security Office Monitors, 43 Camera offline. Restored Access Control & CCTV inCustody, set up Screen View as per request (ext camera). Technician to return when full power restored.Work performed by Nathan Groenewald (25/01/2021)Attended site for UPS shutdown. All works completed ok. Reloaded camera presets.Recommend installing small UPS for Security Office camera monitors.Job completed.Received a call from Security, need to return as there is an issue with a monitor.Reattended site and found separate UPS offline, repowered up and loaded camera presets.Job completed.APPROVED BRAF ATTACHED.
MSA-DTAG | WA3945807 | 1903 & 1987 -FIP Technician attend 06.30am Saturday 23 January 2021 assist with power shut down | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-24 19:30:00 | Pass | WA394580723/01/21 EI @ 630amIsolated zones 7 & 11 on the MFIP & informed Code Red fire alarm monitoring of the fault signal due to planned temporary power outage fortoday.Placed info tag on the MFIP.Isolated zones on SFIP building 87, zones 1 basement & level 4 zone 15.Placed info tag on the SFIP.Isolations to facilitate building/electrical works by others.Onsite Contractor “Tech works” Gary ph 0467 095 980 to call ARA tech to re-instate zones for over night coverage today Saturday 23 whensuitable.WA3945807 after hours callout23/01/21 EI @ 715pmDe-Isolated zones 7 & 11 on the MFIPDe-Isolated zones on SFIP building 87, zones 1 basement & level 2 zone 15.WA394580724/01/21 EI @ 630amIsolated zone on SFIP building 87, zone 1 basement.Placed info tag on the SFIP.Isolations to facilitate building/electrical works by others.Informed Code Red fire alarm monitoring of the fault signal due to planned temporary power outage for todayWA3945807 after hours callout24/01/21 EI
MSA-DTAG | WA3945810 | 1903 & 1987 -FIP Technician attend 06.00am Wednesday 27 January 2021 to reset timer in BMS System | Supreme Court | GMP-BR-HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-28 13:00:00 | Fail | Return to site. Power issues has now been resolved to in the 1987 building. Turn on all pumps and exhaust fans. Found exhaust fans to run in correct direction. Access plantroom with AC 1, 2 and 3. Turn on power supply, found AC 1 to start and run as normal. Found AC 2 to start but motor bearings are now extremely noisy. Found chiller to be on fault, found stage 2 to have tripped high pressure safety switch. Reset switch and power cycle chiller. Found chiller to reset and start. Monitor operation and found to work as normal. Work my way though the building and check operation of all three phase AC units. Found units to start and operate as normal. Check cooling tower fan operation, found water to be warmer than normal. Further investigation found cooling tower fan blades to broken. Programmed to raise separate job to repair. All plant now operating as normal.
MSA-DTAG | WA3945841 | L10 The door lock does not lock or open at Rohan’s office. | Westralia Square | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 13:18:00 | Pass | Attended site, adjust door closer hold back for correct operation.Date on Site: 21/01/2021Time on Site: 12:48pm - 1:18pm
MSA-DTAG | WA3945992 | Barrister’s Robing Room Men’s bathrooms - Cistern is leaking | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 15:33:00 | Pass | Fixed leaking toilet.
MSA-DTAG | WA3946053 | Basement, Judges Carpark - Water tap valve in underground car park is leaking | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-30 10:48:00 | Fail | Replaced leaking stop cock
MSA-DTAG | WA3946128 | Registry entrance Door to the registry entrance has dropped and is hitting the frame when it closes. | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-22 13:15:00 | Pass | REPAIRS MADE TO REGISTRY DOOR FRAME & HINGES
MSA-DTWD | WA3945598 | AHU C1, C Block- Air Con unit still not working correctly - see notes below | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-02-15 14:32:00 | Fail | Checked the temperature of the water found it not coming down enough . Chiller two the main chiller had only one compressor running, reset the chiller and restarted. The temperature came down to 7 deg and holding.15/2/21: Closed off , parts ordered to repair on another job .
MSA-DTWD | WA3945770 | GG20 tool store air con not working - Engie on site | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-19 13:00:00 | Pass | Checked the split in the stores , all working ok , cleaned the condenser and condenser senor. Unit running at max is to small to cool the area in the stores.
MSA-DTWD | WA3945830 | BLD 822, Flat A, Bathroom- Middle vanity leaking pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 11:30:00 | Pass | Job completed - Repair leaking vanity pipes to Flat A building 822
MSA-DTWD | WA3945837 | Block 6, Bricklaying - Water leaking from silt pit | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-02-15 19:25:00 | Fail | dig to expose broken pipe
MSA-DTWD | WA3945904 | F block, FT1 corridor - Faulty lock on door between FT1 and FG11-1 | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 19 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 10:45:00 | Pass | F Block - faulty door lock between FT1 - FG11.1Lock replaced.
MSA-DTWD | WA3945935 | Back of science lab toilets - Faulty Service door | Muresk Institute | GMP-BR | Building | Doors (BU) | Lee Carpentry | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 14:30:00 | Pass | Repairs to door
MSA-DTWD | WA3946017 | C Block, Room C101- Main Air Con not operating | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 11:30:00 | Pass | Accessed site , completed relevant sign in procedures, gained access to room c101 , found both units to be running , carried out testing on unit , found a supply air of 18dgr supplied by both units , tested compressor amps cu2 at 13a and cu1 at 10a both within fla range , all ok
MSA-DTWD | WA3946052 | E Block, Kitchen E74- 2x water isolators are broken | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-22 16:00:00 | Pass | Replaced isolation valves and serviced taps
MSA-DTWD | WA3946059 | South East cnr of C block tree fallen in garden | Balga Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 07:30:00 | Pass | Tree works completed
MSA-DTWD | WA3946065 | A Block East, West entry Auto Door Ground Floor, the door is continuously opening and closin | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-19 16:07:00 | Pass | 1069524. Found mode switch broken and external sensor self actuating, adjusted outside sensor and replaced broken mode switch
MSA-DTWD | WA3946078 | B Block East Entry Door lock has failed | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 09:00:00 | Pass | job completed - Repaired oval cylinder & serviced lock & adjusted striker
MSA-DTWD | WA3946117 | Carpark 2 Large tree on a lean with exposed roots – ready to fall | Thornlie Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 19 Jan 2021 | 2021-01-20 17:00:00 | 2021-01-24 10:30:00 | Fail | Tree removed and stump grinding completed.
MSA-DTWD | WA3946122 | B block B2122 faulty door lock | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 13:45:00 | Pass | B2122 Door lock faultyLock repaired.
MSA-DTWD | WA3946144 | F block Repair GPO in the library computer area. | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 15:00:00 | Pass | Arrived on site,signed in,spoke to pfm about job , completed jsa, isolated gpo, removed old gpo and mounting block, replaced with new gpo and mounting block, re energised gpo , tested gpo and working as intended , cleaned up work area , completed paperwork, signed out ***job completed***
MSA-DTWD | WA3946147 | L block Fallen tree branch Western end | Balga Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 08:10:00 | Pass | TREE WORKS COMPLETED. SIGNED OFF BY CAMPUS ON PO & COMPLETED JOB SLIP.
MSA-DTWD | WA3946166 | Basement _External - Broken window | Kwinana Automotive Centre-Block A-Lower Ground | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 19 Jan 2021 | 2021-01-22 17:00:00 | 2021-02-11 09:05:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSMADE SAFE BROKEN PANEL 6.38 CLEAR LAMINATED SAFETY GLASS1-450 X 920 PLUS SAFETY FILM 2-800 X 1500RETURNED LATER DATE TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-840 X 22986.3 L/M OF DOUBLE SIDED TAPE USED2 MEN REQUIRED
MSA-DCA | WA3951010 | Ground, Cool room freezer - Water puddle outside the cool room freezer, current gauge reading attach | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor-Cool Room | GMP-BR | Refrigeration | Coolroom (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 12:30:00 | Pass | COMPLETED
MSA-DCA | WA3951078 | plantroom HBRC BMS is offline. | Collection and Research Centre Welshpool-Harry Butler Centre | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 15:13:12 | 2021-01-20 13:30:00 | Pass | Attended site. BMS control system remote access not operating correctly. Applied tests and checks, raised PO for Alerton to investigate issue. Investigation found dynamic sim to have lost comms and applicable communication with HBC IP address. Alerton to have reconfigured IP address comms between modem and PC. Recommendation to change from a dynamic sim card to a static sim card for any future power cycle issues.
MSA-DCA | WA3951128 | Dress Circle - female toilet is out of order | His Majesty's Theatre-Theatre Building-Level 1-Dress Circle | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 15:15:00 | Pass | Replaced faulty inlet valve and washer
MSA-DCA | WA3951135 | Ground, Stage Door, Assembly Area Toilet - The basin is cracked | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Door Lobby | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 09:17:00 | Pass | Replaced basin
MSA-DCA | WA3951147 | Kitchen ground floor - no air floor in kitchen due to BMS control | His Majesty's Theatre-Theatre Building-Basement-Kitchen | GMP-BR | Plumbing & Drainage | Water (PD) | Building Automation & Electrical Services Pty Ltd | 1 | COMPFIN | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 17:00:00 | Pass | Released the 'Manual' control and BMS reverted back to 'Auto' control with the calculated required airflow setpoint of 437I/s. VAV box opened and achieved required airflow. Check supply air outlets within the kitchen to verify airflow was present
MSA-DCA | WA3951154 | Men’s Stalls - The automatic urinal flush mechanism is not working. | His Majesty's Theatre-Theatre Building-Level 2-Upper Circle Male Toilets | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-03-16 12:18:00 | Fail | Replaced faulty solenoid
MSA-DCA | WA3951325 | freezer not working | Perth Concert Hall-Main Building-Basement-Dumb Waiter Motor Room | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-22 16:30:00 | Fail | Carry out investigation of coolroom unit on Carpark level within condenser compound and it's associated pipework and equiptment and report findings for a quotation.22/1/2021 - Take details of running pressures and temperatures record all relevant information rand report findings.18/2/2021 - Notified By D.Kirwin that this job is now being subbied out to another contractor.
MSA-DCA | WA3951512 | Humidity alarm (high) for galleries 1 - 6 | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Gallery 4 | GMP-BR | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 20 Jan 2021 | 2021-01-21 03:53:36 | 2021-01-21 02:30:00 | Pass | Attended,Monitored humidity condition back to correct levels.Checked humidifiers.
MSA-DCS | WA3950674 | Two cameras are not operating, controller 5 is not operating. 8.02 hub modem rack fault. | Pardelup Prison Farm-Administration Unit Office | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 06:50:43 | 2021-03-02 14:00:00 | Fail | 22/01/2021 Replaced failed power supply, fibre modem and transferred 3000 controller from house 1 to Industries. 02/03/2021 Installed new 6000 controller and 8 HBus module in House 1. Systems all back on line
MSA-DCS | WA3950713 | Jeelia, Control door lock fail | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 11:15:38 | 2021-01-20 09:30:00 | Pass | Attend site to look at control door failure. Required new OFR cylinder and cam.
MSA-DCS | WA3950714 | Admin, Door near councelling room - Door lock fail | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 07:18:07 | 2021-01-20 09:30:00 | Pass | Attend site to check door lock fail. Faulty/worn keys. Gate hour SO and Security SO agreed to set function on air lock door to Passage mode.
MSA-DCS | WA3950719 | Unit 1, SO office- Air conditioner is leaking. | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-20 14:20:39 | Pass | Checked over for leak,found screen in pump blocked,removed and cleaned aswell as drip tray,flushed to check operation,all flowing ok now.
MSA-DCS | WA3950723 | Unit 6, lock is jamming where the key to medication is stored. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 20 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-22 11:00:00 | Pass | Obtain key and lock from Security. replace lock.Return key and worn lock to Security.
MSA-DCS | WA3950726 | PTZ cameras not responding | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 11:30:06 | 2021-01-20 12:30:00 | Fail | Restarted all servers in relation to fault. All PTZ now responding with Senstar system as per normal.
MSA-DCS | WA3950728 | Zone 1 & 12-check sensitivity of fence | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 07:32:13 | 2021-02-11 14:00:00 | Fail | Removed all old cabling and steel cableties on Z12, top and bottom Sections. Installed new cable and conditioned cable to work correctly. Put end of line water proof box with one mega ohm resister. Joined senstar cable to underground coax with water proof box. Calibrated and tested cable to achieve correct sensitivity for the system. Tested with control. Working as per normal. Materials used. 53m of senstar cable 2 x waterproof splice box’s.
MSA-DCS | WA3950731 | Zone 9 inner alarm constantly activating | Wandoo Rehabilitation Facility | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 07:33:49 | 2021-02-12 12:30:00 | Fail | Replaced faulty southwest mw with new uw , configured and calibrate. Job completed.
MSA-DCS | WA3950741 | Unit 6, C wing shower room drain cap in the middle shower stall can be removed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jan 2021 | 2021-01-27 17:00:00 | 2021-05-31 09:30:00 | Fail | Tap and died two new threads into face plate off floor waste gully.To prevent inmate lifting shower waste
MSA-DCS | WA3950743 | Case planning - Air Con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Jan 2021 | 2021-01-22 17:00:00 | 2021-02-01 14:02:00 | Fail | Complete
MSA-DCS | WA3950773 | Master Control room - Fire panel fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 12:05:11 | 2021-02-23 10:32:00 | Fail | Work PerformedTechnician Note20/01/21 EI 10amAttended site.During Site attendance the site went into lock down due to altercation within guard house involving others.Asked by staff to briefly depart & re-visit.On revisit site lock down due to medical emergency.Attended zone control 2 & checked FIP status normal.Attended POD FIP & confirmed 2 x faults present relating to the “Visits non contact area”.No access to visits due to personnel movement.Faults read as1. L4S21 zone 14 visitors non contact visit room 4smoke detector reporting a missing fault.2. L4S31 zone 14 visitors contact tea prep West thermal detector reporting a multi dev fault.Re-visit required once access possible/authorised.Advised POD staff.1/02/21 BG/EIAttended site but turned away. No access at this point in time.22/2/21 BG JGFault rectified as part of another task. Fault cleared at time of arriva
MSA-DCS | WA3950812 | Unit 2 C-D wing Seme reported electric current running through outer airlock door | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 12:27:05 | 2021-01-20 12:00:00 | Pass | Checked door and door frame for stray voltages to building rarth and an independant earth and all checks out ok , no voltage present.
MSA-DCS | WA3950813 | Outpatients Area, Dental Room - Air Con vent falling out | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-20 13:29:44 | Pass | Checked over vent,found support clip for core had come loose,resurced to core and refitted into outlet.
MSA-DCS | WA3950819 | Unit 6, Cell D6- Toilet Duct between cells D5 and D6 the toilet systern is not filling up, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 12:30:00 | Pass | Nill
MSA-DCS | WA3950825 | Unit 1 toilets back hut flexi hose basin mixer burst | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-21 08:30:00 | Pass | Burst flexi on basin mixer, had to replace mixer
MSA-DCS | WA3950834 | visits centre fluro lights and fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-22 11:30:00 | Pass | Investigate and repair visits light circuit not working
MSA-DCS | WA3950856 | Unit 6, N10 - Toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-27 09:50:00 | Fail | Replaced outlet washer and inlet valve
MSA-DCS | WA3950859 | Unit 6, Service duct between A23 and A24 - leaking water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-27 10:00:00 | Fail | Fixed leaking flushpipe
MSA-DCS | WA3950921 | Unit 7 Cell D6, window will not stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 16:00:00 | Pass | SPIRAL BALANCES RENEWED TO WINDOW
MSA-DCS | WA3950929 | Unit 7 Leaking tap needs repairing in Cell D6 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-26 13:11:00 | Fail | Nill
MSA-DCS | WA3950932 | Unit 14, A7 - light switch is loose on the outside of A7 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 09:40:30 | 2021-01-20 13:00:00 | Pass | Replaced damaged cell switch in unit 14 a7
MSA-DCS | WA3950935 | Bakery, Workshop - The arm on the bread slicer needs a bolt and screw on the lever arm. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 09:44:37 | 2021-01-22 17:30:00 | Fail | COMPLETED 22/1/21
MSA-DCS | WA3950944 | INF (10) B2 in infirmary tap continually running. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-18 13:40:00 | Fail | Nill
MSA-DCS | WA3951017 | Yeeda, B Wing Laundry- Ceiling is damaged after burst water pipe | Banksia Hill Detention Centre | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-04-08 09:15:00 | Fail | REPAIRS MADE TO DAMAGED CEILING
MSA-DCS | WA3951072 | Unit 6 - A11 - There is water running down the wall from the air vent above the sink. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-10 09:30:00 | Fail | Nill
MSA-DCS | WA3951083 | Front car park - Damaged pit | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-22 15:00:00 | Pass | Investigate and replace damaged pit near front car park.
MSA-DCS | WA3951096 | Paint Shop - Day Room hot water urn not working , cold water not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 09:11:00 | Pass | Billi unit. Filter due x 9 and in fault on arrival. Ran system through checks. Returned to car. Replaced Billi filter, it cleared the fault. Ran system to correct temp, hot and cold. Normal operation A40332306A
MSA-DCS | WA3951151 | dairy disconect pump and make safe | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-22 10:00:00 | Pass | Disconnect and make safe dairy pump
MSA-DCS | WA3951156 | education window glass loose in fram needs packers and glazing bead- see notes | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-03-10 13:00:00 | Fail | RE SET GLASS AND BALANCES
MSA-DCS | WA3951169 | main kitchen GPO for slicer keeps tripping unsure if machine or GPO faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-21 08:30:00 | Pass | Replaced damaged plug top
MSA-DCS | WA3951288 | Gymnasium, Front Entrance - Reinstate Reticulation cut off due to new build | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-23 21:45:00 | Fail | REINSTATE PREVIOUS RETIC THAT WAS DISCONNECTED AND DAMAGED. NO PARTS USED, FACILITY SUPPLIED ALL PARTS
MSA-DCS | WA3951365 | kitchen cooking area, dishwasher is working intermiterdly - see notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 13:50:18 | 2021-02-10 14:00:00 | Fail | 21/01/21Arrived at site liaise with kitchen, identify dishwasher, isolate remove panels, test/fault find diagnose and found the rinse thermostat, over temp are faulty supply and replace, reassemble all components and test all components for correct and found that the 2 of the door switches are faulty and require replacement, bypassed the switches to get them going until parts come in, also found both the temperature gauges are faulty and require replacement, the 3 indicator lights are faulty and require replacement, the on/off switch requires replacing, 1 x reed switch magnet1 x magnetic reed switch for rinse tank1 x door reed switch1 x orange indicator light 240v1 x red indicator light1 x green indicator light2 x circular temperature gauge1 x on/off switch10/2/20Fitted parts and tested all ok.
MSA-DCS | WA3951382 | farm shed chain saw shed GPO faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-22 11:30:00 | Pass | Investigate and replace farm shed gpo
MSA-DCS | WA3951409 | Security office CCTV monitor #3 not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-03-15 09:00:00 | Fail | Unable to locate anyone who knew about the fault. All monitors in the security office in admin tested ok. All gatehouse control monitors tested ok. Found issue with the Indigo setup in ICF. Setup all 4 monitors with an Indigo window.
MSA-DCS | WA3951419 | Hole in the road by staff car park entry caused retic flooding | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 09:00:00 | Pass | Works completed 21/1/2021
MSA-DCS | WA3951432 | Server room, gate house - UPS alarm - warning ID 114, component MON, | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Elec Power Technologies | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 19:17:55 | 2021-01-20 18:15:00 | Pass | Server room, gate house - UPS alarm - warning ID 114, component MON, message at end of screen - bypass unable to trace
MSA-DCS | WA3951433 | Unit 17 - There is a fault sounding for cell A 13. - see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-24 14:51:00 | Pass | EI/JVAttended site FIP displaying missing faults on L8D43 to 51.MASD’s AC Cells 13 to 16.Inspected the MASD’s within the roofspace and restored the APIC card which is intermittently dropping off the network.Observed the FIP faults L8D43 to 51 restore to normal operation.Cause unknown.Consultation with manufacturer required - recommend installer organise
MSA-DCS | WA3951439 | Unit 17 - B & D Emergency power shut down switch has been removed - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 15:27:03 | 2021-01-21 09:00:00 | Pass | Repaired damaged e-stop in unit 17 kitchen
MSA-DCS | WA3951480 | Control Room - Security doors are not showing status whether open or closed. | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 21:19:33 | 2021-01-20 19:45:00 | Pass | Found server services stuck in a loop bringing down that Gallagher controllers reset and tested all ok
MSA-DFES | WA3950846 | Plant Room , Chiller #2 Failure. Investigate cause and report. See further notes below | DFES Cockburn Emergency Services Complex | GMP-BR | Refrigeration | Chiller (RE) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 15:30:44 | Pass | Travelled to site and signed in. Accessed chiller and found no active alarms as site has reset earlier. Found touch screen not working. Reset switch for touch screen and confirmed operation. Ran up chiller 2 and confirmed correct operation. Suspect power spike caused trip as the chiller units are very sensitive to incoming power
MSA-DFES | WA3950889 | station officers office air con unit drain valve blocked | VFRS Mandurah | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 10:00:00 | Pass | Removed drain blockage
MSA-DFES | WA3950986 | Cyclone wire fence has been damaged | Metropolitan VFRS | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-25 09:05:00 | Fail | Replaced the existing damaged fence panel with a new section of chainmesh fence and new strainer wires. Unmanned site - have attached completion photos
MSA-DFES | WA3951049 | front middle engine room door - damaged unable to secure and not automatically working | CFRS Fremantle | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-03-26 12:30:00 | Fail | COMPLETED
MSA-DFES | WA3951256 | Large tree branch has fallen in the back of fire station (size of a bus) | WA VES Association - Guildford (old fire station) | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Dom's Total Grounds Maintenance | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 17:00:00 | Pass | Tree Loppers attended & removed fallen branch
MSA-DTAG | WA3951258 | Lift from basement carpark - doors open and close a couple of times before going up or down | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 16:38:21 | 2021-10-21 15:00:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA3951292 | ground sally port the bollards in front of the sallyport roller door have glitched - see notes | Supreme Court | GMP-BR-HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-02-09 13:45:00 | Fail | Paul Cullum (09/02/2021) - Work NoteReturned to site. Accessed motor j/boxes. Opened up each one, tested motor cables from this point. Each motor found to have earth faults (0.15 / 0.26 / 0.34 Meg Ohms to earth. Tested motor windings 21/21/42 ohms each). Limit and light j/boxes for each bollard not touched for now, as the 3 bollards will now need to be totally removed, serviced/repaired.Left off / down / isolated in control panel.Paul Cullum (09/02/2021) - Work NoteCannot remove bollards for inspection as all screws siezed. Accessed pit and opened up the 3 bollard motor j/boxes.Poor condition, tested motors from this point, all three have serious earth faults.Now we need to remove the three bollards (drill fixings) install cover plates.At workshop each bollard will need to be inspected, stripped, obtain faulty parts, rebuilt, tested and returned to site.Also recommend replacing cabling from pit back to control panel. 1cable has been stripped of outer insulation,others brittle
MSA-DTAG | WA3951315 | 1987 Judicial basement carpark Digi-lock on door from judicial carpark to lift is seizing | Supreme Court | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 13:00:00 | Pass | Attended site to disassemble lockwood digital lock and service and lubricated lock.
MSA-DTWD | WA3950841 | A block L1 A114 no power to all lights in the room | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 13:00:00 | Pass | Attended site and inspected lights out. Found a seperate master switch which turned classroom lights off. Dave asked if we could have them switched separately so we ran a hard active from the master switch to the classroom light switch.
MSA-DTWD | WA3951004 | cafe L2 cafe freezer room motor not working - see notes | Perth Campus B1 | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-25 19:02:00 | Fail | Returned to site. Gained access to L2 kitchen and checked operation of thermostat control device. Confirmed program and parameters sets. Freezer running to set point. Work area left tidy. BRAF approved.
MSA-DTWD | WA3951192 | L2 International student Centre UG Split duct Air flow issue | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-20 16:48:00 | Pass | Attended site gained access and carried out inspection of office. Confirmed VAV 7-1 to 7-4 were operating. Traced duct work back to FCU. Split found to have occurred in ductwork at point of what looked like an old repair. The split was allowing air to escape into roof space and not providing cooling to office. Record duct size left site to collect materials. Returned to site repaired duct and tested for air leak. All ok. Checked and reconfirmed VAV operation. Air flow restored. Work area left tidy.
MSA-DTWD | WA3951298 | E block, room E002 requires pest control for white ants | Balga Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 0 | CLOSE | 20 Jan 2021 | 2021-01-20 17:11:50 | 2021-01-21 14:00:00 | Fail | 20/1 Injected pier under subfloor with 1 Litre Termidor @ .6% and inspected E002 & part E00121/1 Injected 3 Litres Termidor to live activity in walls E002 and subfloor pier
MSA-DTWD | WA3951304 | Lvl 7, male staff toilet is not flushing | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 16:30:00 | Pass | repaired both cisterns in male staff directorate
MSA-DTWD | WA3951309 | Block 10, Creche - Influx of red back spiders in and around both Creches | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 14:50:00 | Pass | Treated to control spiders to both crèche rooms, internal and external areas inspected. Residual spray external walls, around doors, windows, fencing, downpipes, light fixtures, etc.Spot treated internal areas where spiders were located - under desk, top of window frame, behind trough, behind book shelf.
MSA-DTWD | WA3951321 | Entrance next to pink container drinking fountain nozle fauty | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 17:30:00 | Pass | replaced bubbler and jug filler
MSA-DTWD | WA3951354 | L2 disable toilet not flushing | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 19:00:00 | Pass | repaired 5 cisterns
MSA-DTWD | WA3951425 | A block L2 A273 Hot water unit not working. | Leederville Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 20 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 12:28:00 | Pass | Replaced filter and inlet solenoid.
MSA-MRWA | WA3951023 | L1, Kitchenette - Replace 90mm failed downlight | Don Aitken Centre MRWA Head Office-Main Building-First Floor-Cafe Kitchen | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 07:59:00 | Pass | Replaced faulty downlight in tea room.
MSA-MRWA | WA3951093 | L1, Male toilet - Western most urinal leaking please remediate. | Don Aitken Centre MRWA Head Office-Main Building-First Floor-A1.02-Toilet and Shower-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 16:00:00 | Pass | Checked both urainals and no issues found
MSA-MRWA | WA3951097 | L1, Male toilet - Flick mixer leaking please remediate | Don Aitken Centre MRWA Head Office-Main Building-First Floor-A1.02-Toilet and Shower-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 15:50:00 | Pass | Replaced faulty mixer tap on the left hand side
MSA-MRWA | WA3951116 | Field store Air conditioning not cooling air. Fan in room is running but blowing warm air only. | Materials Engineering Branch-Admin Building-Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 13:30:00 | Pass | AC repaired
MSA-MRWA | WA3951133 | RTTO, western most UPS in error, please investigate and remediate. | Road Network Operation Centre (RNOC) | GMP-BR | Electrical | General Electrical (EL) | Secure Power Solutions Pty Ltd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-21 11:45:00 | Pass | job completed - Attended faulty UPS
MSA-MRWA | WA3951254 | Temp sensor not reliable, please investigate and remediate | Don Aitken Centre MRWA Head Office-Main Building-First Floor-Cafe Area | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Mizco Pty Ltd | 3 | CLOSE | 20 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 11:26:00 | Pass | job completed - Attended to site to complete the required workTested Controller input. No issues.
MSA-MRWA | WA3951463 | blocked urinal | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor-Toilet-Male | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jan 2021 | 2021-01-21 17:00:00 | 2021-01-20 18:07:00 | Pass | Unblocked urinal
MSA-DCA | WA3952161 | Stairs next to PICA, brick work come away from last row of stairs creating a hazard | Perth Cultural Centre Precinct-Wetland Area-Ground Floor | GMP-BR | Paving & Roadworks | Paving (PR) | ICS Australia | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 16:15:00 | Pass | Cleaned up loose pavers and recent red into place
MSA-DCA | WA3952387 | Zone 6 & 7 retic not working-please investigate. | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-23 15:15:00 | Pass | Work Completed:- Connected common wires- Replaced broken sprinklers- Called off sprinklers on Zone 7
MSA-DCA | WA3952404 | first floor, public toilets -2 x mixer taps are very stiff and not working | Maritime Museum Victoria Quay-Main Building-First Floor-Male Toilets | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-25 17:00:00 | Pass | Replaced two flick mixers in male toilet. Took a while to find isolation valve
MSA-DCS | WA3951665 | Reception, D/O Rooms 2,3,4,5 and S/O Induction room- Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-29 15:45:00 | Fail | Job is a duplicate and has already been quoted. See worklog
MSA-DCS | WA3951667 | Boiler House - Boiler 2 out on fault (boiler turned off but in fault position) | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 21 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 12:00:00 | Pass | Boiler 2 was in fault on the pilot position. Opened burned checked and cleaned flame rod. Opened up fan and checked due to strange noise but could find any issues other than noise. Tested multiple times without fault.
MSA-DCS | WA3951691 | Lenard, A Wing Kitchen- Broken double power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-21 10:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3951715 | Unit 14 -air con is operating it is not as effective as usual and struggling to cool the area | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 11:29:50 | Pass | Checked over aircon found to be running,coil clean,washed filter as slightly dirty,gas pressures ok,unit running fine.
MSA-DCS | WA3951723 | Gate house, Prison entry gate - door not able to close correctly | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 07:51:10 | 2021-01-25 08:59:00 | Fail | Security is working however lock is hitting door frame lock and door closer need to be adjusted Carpenter cAlled
MSA-DCS | WA3951737 | Laundry, Wash House- Ceiling fan faulty (EWP is required) | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-24 15:00:00 | Fail | Replaced fan.
MSA-DCS | WA3951739 | MDAS receiver fault | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 07:57:23 | 2021-01-21 09:00:00 | Pass | Transponder 14.1.7 frequently failing and restoring during the night. Located the receiver on the MDAS map and found in the field. Removed and replaced. Tested ok. Parts used:Bosch MDAS receiver EA102A-304 from site stock. Need to order replacementSite Stock replaced with new
MSA-DCS | WA3951768 | SOG Base - computer system keeps freezes | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | COMP | 21 Jan 2021 | 2021-01-22 08:14:13 | 2021-01-22 08:30:00 | Fail | WA - Nathan Groenewald (22/01/2021) - Work NoteAttended site. Checked main PC, found CPU running high due to Indigovision software . Traced further and due to cameras drawing alot of usage.Dropped frame rate of all cameras and retested.All running better but CPU from Indigovision cameras running high. Reccomend replacing NUK with new server PC suitable for 23 cameras accounting for usage from Ubiquiti link.CPU before changes 32%CPU after changes 17%Job completeto be closed of at $0Work completed under Warranty.
MSA-DCS | WA3951817 | security office - security camera work station feed down | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jan 2021 | 2021-01-21 16:28:47 | 2021-01-21 13:41:00 | Pass | Test structured data and optic fibre network, test SFP modules. Multiple fibre links down between admin and medical plant room. Repatch admin network switch through alternative network path and test ok.
MSA-DCS | WA3951828 | Unit 3, Cell D9- Toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-29 08:22:00 | Pass | Nill
MSA-DCS | WA3951830 | G Floo, Admin office - Electrical light switch which has split | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 08:40:27 | 2021-01-21 10:15:00 | Pass | Replaced failed light switch.
MSA-DCS | WA3951831 | Jasper, B Wing - smashed window approx 1200x500 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-03-12 12:30:00 | Fail | WINDOW RE GLAZED & SECURITY FILM APPLIED
MSA-DCS | WA3951833 | SHU (9) - The Whole Unit water coming through celling Aircon vents, Aircon has frozen up | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 08:43:23 | 2021-01-22 10:29:35 | Fail | Arrived on site and signed in,checked over aircon found water coming from condensation from flexibal connection,picked up insulation tape returned to site,covered flexi connection.Should fix the problem as section of duct was unisulated.
MSA-DCS | WA3951849 | Unit 4 - C Wing grille fail stuck half way | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 21 Jan 2021 | 2021-01-21 12:57:09 | 2021-01-21 12:00:00 | Pass | 21/01/21Tested and re-aligned.Fault checked.Working fine
MSA-DCS | WA3951890 | Unit 2, A & B Wing Dayroom- 4x Fans not working (Scissor Lift required) | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-22 13:30:00 | Pass | Replaced broken fans
MSA-DCS | WA3951911 | Unit 2 C-D wing - Hellwig Scissor Lift required | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-29 13:30:00 | Fail | Repaired light and fans
MSA-DCS | WA3951971 | Reception area female toilet lights not working - see notes | Midland (North East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 09:00:00 | Pass | Replaced blown lamps in toilets as required.
MSA-DCS | WA3951991 | Interview Room 5 Duress Alarm Duress alarm triggers when power is turned off - see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-21 16:45:00 | Pass | Fault appears related to backup batteries that have been identified for replacement under maintenance.
MSA-DCS | WA3952001 | Unit 2, A-B wing outer air lock door - Door Lock Tung Face Worn ,Grooves Door Not Shutting Properly | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 10:30:45 | 2021-01-28 09:30:00 | Fail | On site, service air lock door, test door. Door stops required to be replaced. Reattend site to install and adjust door stops.
MSA-DCS | WA3952002 | Unit 2, C-D wing outer air lock door - Door Lock Tung Face Worn ,Grooves Door Not Shutting Properly | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 10:32:53 | 2021-01-28 10:45:00 | Fail | Attend site, service air lock door, test door. Door stops required to be replaced. On site. Install and adjust door stops.
MSA-DCS | WA3952005 | unit 2, Electrical room fire panel - Fire Panel Fault L2M64 Wing C/D Cells 13/14 Fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 10:35:49 | 2021-01-22 09:49:00 | Pass | Attend site and found Vesda in unit 2 C/D 13&14 in intermittent low flow fault due to blocked sample points from dirt.Cleaned sample points and increased flow and normalised and left normal.
MSA-DCS | WA3952018 | Security office - Computer clock is not at actual time | Pardelup Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-04-07 13:30:00 | Fail | Installed Aerial for Time server on exterior of Hub building and cabled to Rack inside building. Mounted time server in SMS rack and connected to power and network switch. Programmed as time sync for Time server.
MSA-DCS | WA3952054 | Receptions 1st Gate to reception from sterile zone Lock barrel faulty, keys getting stuck | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 11:12:17 | 2021-01-21 13:15:00 | Pass | Attend site, service and repair 570 series cylinder.
MSA-DCS | WA3952060 | Unit 9, Cell A13- Floor waste blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 11:21:56 | 2021-01-22 10:16:00 | Pass | Unblocked floor drain, delayed due to being understaffed
MSA-DCS | WA3952142 | Unit 13 - A7 leak on shower sceen selicon is off | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 11:00:00 | Pass | NEW SILICON INSTALLED TO STOP LEAKING
MSA-DCS | WA3952176 | PTZ 2 perimeter camera - unclear and unable to move and zoom | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 13:16:02 | 2021-01-27 17:19:00 | Fail | Repaired multiple camera faults and tested okJob Complete
MSA-DCS | WA3952181 | Unit 14, A & C - Element Bolts have snapped off & some are missing inside the oven | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-25 10:10:00 | Pass | Removed riveted threads of two bolts that had broken off and re-rivet new threads in. Replaced bolts & retest all elements ok.
MSA-DCS | WA3952182 | main office work area Aircon not cooling and appears to have little airflow | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-03 15:00:00 | Fail | unit running pok
MSA-DCS | WA3952195 | assesments building, MDAS receiver fault | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 13:39:42 | 2021-01-22 08:00:00 | Pass | Replaced faulty receiver with new one. Cleared error messages on PC. Tested ok. Parts used:Bosch EA102A-304 MDAS receiver
MSA-DCS | WA3952213 | Old Front Gate, Locksmiths office- Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 14:08:07 | 2021-01-22 14:30:00 | Fail | Found control fuse blown on arrival. Suspect due to old fuse. Replaced fuse and ran up unit successfully. TD of 12. Room temp dropped from 28 degrees to 24 during attendance. Fully operational at time of departure.
MSA-DCS | WA3952251 | kitchen fluro light has broken away from ceiling | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 14:59:33 | 2021-01-22 10:30:00 | Pass | Replaced damaged light fitting in kitchen area
MSA-DCS | WA3952401 | unit 13 switchboard FIP buttons are broken | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-23 10:27:00 | Fail | attended site to take photos of correct keypad required.22.2.2021 - Keypad replaced
MSA-DFES | WA3951950 | Outside gym - Broken pipe under paving | CFRS Malaga | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 12:31:00 | Pass | Investigate water leak under paversIsolate water supply, remove brick paving and excavate down to leak, expose leak and collect fittings from supplierRemove old damaged split tee and install new fittings, turn water on and flush water line p, check for leaks Back fill hole and re-install pavers, pack up and clean up worksite
MSA-DFES | WA3952014 | front of building sewage pump alarm is in alarm high level and fault light on panel | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 13:45:00 | Pass | 21.01.2021Investigate high alarm at drain pit ,opened pit ,cleaned sensor stick which was full of gunk, pit low level, reset alarm button all seems good!
MSA-DFES | WA3952228 | TV Room - Air Con not working | CFRS Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-22 09:30:00 | Fail | Diagnosed fault outdoor fan motor & impeller.
MSA-DFES | WA3952236 | Main tap in kitchen is leaking at the base of the tap. | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-29 15:15:00 | Fail | Replaced tap spout cause the old one was broken and leaking
MSA-DFES | WA3952274 | L2 Strategic Procurement Blown fluoro light above desk | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 13:45:00 | Pass | Located Faulty light on Level 2. Was instructed which light it was in Procurement Level 2. Replaced and tested for function.
MSA-DFES | WA3952388 | Server room - aircon error No gas | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-03-16 12:30:00 | Fail | Aris Moulavasilis (24/03/2021) - Work NoteTravelled to suppliers & picked up parts & materials.Travelled to site parked & signed in.Completed JSA and eliminated all hazards.Next I gained access to Ac condensing unit & added trace Gas.Leak testing started by using digital leak detector.Investigation was completed at the condensing unit, flare nuts, all other compressions fitting & pipe work ect.As leak was not located at condensing unit, indoor unit was dismantled & checked for leaks.Leak was located on the evaporator coil, this was reported to my supervisor.After discussing it was agreed that replacing the Ac unit would be a better option for the client.All tooling was packed up & information relayed to DEFES staff.
MSA-DTAG | WA3951851 | Lvl 10, Front Counter - Broken 3-seater waiting chair in public area | Westralia Square | GMP-BR-HO | Furniture | Office Furniture (FU) | Midolo Building Services | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 11:30:00 | Pass | BROKEN SCREW REPLACED & ALL FITTINGS RESECURED
MSA-DTAG | WA3952062 | Level 3 public corridor lift call button is broken | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 21 Jan 2021 | 2021-01-21 15:24:21 | 2021-01-21 12:40:00 | Pass | When responding to the callback dated 21.01.2021, the Schindler Technician found that the equipment had been subjected tovandalism which had affected one of the components. The landing panels / indicators were damaged. Following our attendance, theequipment was left in service.
MSA-DTAG | WA3952569 | Basement custody cells connection/cable to cell TVs from DVD player in the control room is broken | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 08:00:00 | Pass | Job complete
MSA-DTAG | WA3952604 | lift not working in carpark - out of service - Lift #2 | Supreme Court-Supreme Court Building-Ground Floor | GMP-BR-RC | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 21 Jan 2021 | 2021-01-22 00:09:53 | 2021-01-21 23:00:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3951776 | G block L1 G 103: Music Replace two flouro fittings that are not working in the workroom.-see notes | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 14:30:00 | Pass | Repalced 2x faulty light fittings with new led as shown by site.job completed
MSA-DTWD | WA3951829 | H block HG05/HG06 No power to air con units | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-21 14:15:00 | Pass | Job complete
MSA-DTWD | WA3951913 | house 14 & 15, Bathroom - low water pressure in showers | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 12:30:00 | Pass | Job completed - Repair low water pressure to showers houses 14 and 15
MSA-DTWD | WA3951984 | L1 Cleaners room key broken off in lock. | Perth Campus B2 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 16:20:00 | Pass | Repair lock to Cleaners store
MSA-DTWD | WA3952059 | D block Ball valve that feeds water to fire hydrant is rusted & handle has broken off. | Carlisle Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-16 17:45:00 | Fail | replaced valve within valve box, replaced rheem tap
MSA-DTWD | WA3952069 | Block 7, Cafeteria kitchen, Water leaking from hole mixer spout. | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-09 17:00:00 | Fail | replaced 2 tap sets and spouts
MSA-DTWD | WA3952072 | Campus, Path way between block 1 & 7- Brick paving lifting causing trip hazard. | Thornlie Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-29 10:15:00 | Fail | Remove sunken & broken pavers to main walkway and re lay
MSA-DTWD | WA3952092 | Block 8, Ladies toilet- Tap for cold water leaking on r/h basin | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-09 16:00:00 | Fail | rewashered and reseated tap
MSA-DTWD | WA3952104 | 19Ab rear alleyway next to dust extract- daikin evaporator noisy & banging | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-03 11:22:00 | Fail | Attended site gained access and collect keys. Accessed building 6 isolated split A/C and replaced fan guards. Noted fan motor mounting bolts were loss and tightens. Tested and checked unit all ok. Fan blades no longer rubbing. Work area left tidy.
MSA-DTWD | WA3952133 | L block, lift not working | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-10-21 15:00:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3952145 | Lvl 2, Library - Fix lighting as required | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 15:30:00 | Pass | Attended site and signed in. Got keys from facilities. Located library lighting with facilities. Found various fittings out and covers missing. Replaced lamps in all fittings as required that we could reach off a ladder. Placed covers back to fittings securing with cable ties for safety. Signed out job complete.Light not fixed due to need man lift and site can’t supply it today.
MSA-DTWD | WA3952152 | Lvl 3, Room A356- Faulty power point | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 11:15:00 | Pass | Attended site and signed in. Got keys from facilities. Located classroom. Found no power to gpos. Identified circuit and found to be tripped. Reset and tested outlets. All okay. Inspected all gpos to be okay. Signed out. Job complete
MSA-DTWD | WA3952200 | A block, rear auto door will not close, sensor faulty | East Perth Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 16:04:00 | Pass | Arrived onsite and found controller not responding. Replaced part and tested unit and all ok Returned to site for faulty door. Inspected door and found external sensors were faulty, replaced 1x microhead sensors, tested door operation a number of times, all working fine.
MSA-DTWD | WA3952232 | D Block- No air conditioning to the building, burnt out contactor to VSD pump drive | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-25 15:41:00 | Fail | NRP attended and completed works
MSA-DTWD | WA3952249 | large metal door into the Gym area of T Block, the upper rail has come away from the door frame | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 12:30:00 | Pass | repair sliding door track
MSA-DTWD | WA3952385 | S block S3 and S4 rattling when the wind is from the North East, check for loose sheets on roof | Murdoch Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 14:20:00 | Pass | eaves loose - re fit
MSA-DTWD | WA3952386 | E block ground SK2 the combi/ steamer oven has a broken control switch | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 2 | CLOSE | 21 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-10 12:50:00 | Fail | COMPLETED 10/2 12.50PM
MSA-DTWD | WA3952402 | H block, roof, H200 - Evap aircon dumping water all the time. | Midland Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Precise Air Group | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 17:30:00 | Pass | Completed pre working at heights checklist set up ladder, harness and accessed roof, isolated unit and carried out test for dead, found solenoid valve to be faulty and T piece for water inlet to sump dump split, isolated water supply. Found other unit with same problem isolated also, found both to be brittle from sun damage. Packed up and gathered information from unit and submitted quotation for repairs. DAS to be submitted.
MSA-DTWD | WA3952591 | Level 1 - W112 card reader not illuminating or working | Perth Campus B1 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 21 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 16:00:00 | Pass | Found that the reader cable had been cut.Re ran reader cable to ceiling andcre terminated cable.Checked and tested reader and door operation to confirm reader wiring is correct.
MSA-MRWA | WA3952169 | Door not completely closing | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor-Reception Area | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 Jan 2021 | 2021-01-22 17:00:00 | 2021-01-21 16:35:00 | Pass | Pe wiring loom and lock signal wires had dropped into door track due to original sticky pads falling off. Removed all damaged wires. Refitted locking relays. Drilled holes in 300 beam and cable tied cables in place. Repaired damaged pe sensor. Tested locking. All ok.
MSA-DCA | WA3952887 | AC is leaking through the ceiling into Admin office 1-see notes | PICA-Main Building-Level 1-Administration Office 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 12:37:15 | 2021-01-22 12:00:00 | Pass | Attended site regarding AC drain leak in admin 1.Accessed FCU and removed old p trap and associated pvcpipe. Found spigot and p trap blocked. Obtained new easyto clean p trap and installed with modified drain pipe.Test ran all ok. Completed paperwork and left site
MSA-DCA | WA3953041 | Fault on the FIP sub panel in Old Workshop Building. Also issues with isolating certain areas | Maritime Museum Victoria Quay-Large and Small Winch Rooms-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-22 13:30:00 | Pass | Attended and investigated fault with engineering FIP. Detector head was removed in workshop and not returned to base (construction demolition works going on). Returned detector back to base. Removed fault. Isolated zones 40, 41 and 42 during works. Main FIP in fault while zones disabled. Fault removed when eng. FIP zones enabled.
MSA-DCA | WA3953088 | main ground HWU faulty requires inspection - see notes | State Archives Repository Dianella-Main Building | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 09:04:00 | Pass | Inspected hwu in working order
MSA-DCA | WA3953105 | toilets Bathroom toilet sink has a constant running leak | State Archives Repository Dianella-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 08:45:00 | Pass | Rewashed two taps
MSA-DCS | WA3952873 | Unit 16 - Switchboard electrical switchboard door lock broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-25 11:45:00 | Pass | Check lock function with keys - no fault found, lubricate lock
MSA-DCS | WA3952881 | Unit 16 - D12 sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-10 12:30:00 | Fail | Nill
MSA-DCS | WA3952906 | Gardens western retic controler faulty. - see notes | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 08:42:09 | 2021-01-28 10:15:00 | Fail | faulty wiring and broken coil. fixed wire and replaced coil
MSA-DCS | WA3952919 | medical centre staff lunch room, Door Lock Jammed and Unable to lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 08:48:39 | 2021-01-22 12:00:00 | Pass | Attend site and serviced door. Required new cylinder. Go back to workshop to to key new cylinder and reattend site to install.
MSA-DCS | WA3952928 | 1st toilet block 2A hot is scolding | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 13:01:18 | 2021-08-03 14:45:00 | Fail | COMPLETED
MSA-DCS | WA3952934 | ISU B console desk - just lost vision on all monitors for observation cells | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 13:02:59 | 2021-01-22 15:00:00 | Fail | Brought back on monitor screens. Half of the selection of cameras would not come up. Went to main comms room and you could see cameras on main workstation. There was an error with the time sync on workstation in ISU 2. Had o reconfigure the pc to be in exact sync with Axis cameras to bring them back online. All working as per normal
MSA-DCS | WA3953023 | ground team leaders office, light in team leaders office as it is flickering whilst switched on | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 09:30:00 | Pass | Fixed flickering light grounds team leaders office
MSA-DCS | WA3953054 | Unit 16 - B3 Hot water will not turn off in the shower. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-23 10:00:00 | Pass | Spindle damaged needs replacing
MSA-DCS | WA3953057 | reset centre - aircon keeps cutting out. Have reset it twice but keeps shutting down | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-08 11:59:27 | Fail | Arrived on site,checked pressure test,system held,released nitrogen and vac out system,recharege system with R22 and test operation,all running ok at present.
MSA-DCS | WA3953062 | Unit 6 At the rear of the unit on A/C side there is a water leak - see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 10:30:05 | 2021-01-22 12:30:00 | Pass | Nill
MSA-DCS | WA3953068 | kitchen pendant power plug damaged | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-22 13:00:00 | Pass | Replaced pendant power outlet
MSA-DCS | WA3953069 | kitchen meat slicer has got a faulty plug | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-22 11:30:00 | Pass | Repaired cable and replaced plug top on meat slicer
MSA-DCS | WA3953081 | Unit 1 - D Wing Numerous basin taps are not working, this is part of the new fit out. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 10:57:15 | 2021-01-22 13:30:00 | Pass | Nill
MSA-DCS | WA3953115 | Unit 3 - Court Yard fence, damage to fence line on A/C side. | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-03-12 09:00:00 | Fail | 05/02/21Inspect and measure damaged fence at Unit 312/03/21Install rail to broken panel and fix off mesh
MSA-DCS | WA3953119 | SOG base, main entry - light flickering | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 14:30:00 | Pass | Repaired light
MSA-DCS | WA3953162 | Visits, Main visits room - Evap air con not working (No water supply) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-01 13:56:00 | Fail | Complete. Replaced transformer.
MSA-DCS | WA3953180 | visits centre light faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 15:00:00 | Pass | Investigate and repair visits light
MSA-DCS | WA3953202 | Unit 1m hut 17 - window frame broken | Karnet Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-17 10:30:00 | Fail | FRAME REPAIRED/NEW FRICTION STAYS INSTALLED
MSA-DCS | WA3953208 | Unit 5, plant room - Pipe burst in plant room, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 16:24:56 | 2021-02-25 13:54:00 | Fail | Nill
MSA-DCS | WA3953219 | video link latch on front entrance door remaining in unlock possition | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 16:29:35 | 2021-01-22 15:30:00 | Pass | Latch on the electric strike intermittently sticking open causing the door to remain unlocked when it closes. Removed strike, cleaned and sprayed with Inox. Tested ok.
MSA-DCS | WA3953271 | Medical Centre, Essential Meds - electric gate not closing | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 13:02:48 | 2021-01-22 16:30:00 | Pass | Electric strike working correctly but the gate will not lock without lifting the gate. It appears as though the tongue sticks out too far from the lock. Job to be referred to a lock Smith.
MSA-DCS | WA3953275 | Unit 5 - Plant-Room Electrician required to disconnect leaking pump and reconnect new pump. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 13:10:53 | 2021-01-22 16:00:00 | Pass | Disconnected and re-connected pump
MSA-DCS | WA3953277 | bakery - Freezer door edge has been damaged and has come off, | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 10:30:00 | Pass | Arrived on site and signed in,checked freezer,found angle covering heater had been ripped off,mesured up,picked up new angle return to site,trim angle to size aand secure to door frame.
MSA-DCS | WA3953309 | kitchen work area Rational Oven #1:Temperature Probe showing incorrect readings | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 13:33:56 | 2021-01-23 12:05:00 | Pass | Check probe accuracy in Hot Water and found accurate. Check Diagnostic & found all probe sensors ok, no other recent errors. Staff reported also that steam was too dry yesterday. Check function of quench ok, operate unit on steam for some time but unit functioned very well. Left unit operational.
MSA-DCS | WA3953323 | Unit 3 SO office A/C leaking large amount of water on floor when running | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-29 10:00:00 | Fail | Cleared bug debris.and drain. Tested flown all ok
MSA-DCS | WA3953384 | Unit 17 - Front Entrance front gate unable to open. Seems like the lock is offset. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 18:29:51 | 2021-01-22 16:15:00 | Pass | Adjust strike.
MSA-DCS | WA3953393 | Unit 5, officers station -filtered water chilled water not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 13:42:00 | Pass | PLEASE CLOSE OUT NO CHARGE THIS UNIT ALREADY HAS A REPLACEMENT UNIT ORDERED PREVIOUSLY ON ANOTHER WORK ORDER WAITING FOR AREA TO BE READY SO WE CAN INSTALL
MSA-DCS | WA3953398 | Unit 14 - D1 Sink Water Fawcett in leaking consistently | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-15 11:39:00 | Fail | Nill
MSA-DCS | WA3953401 | Unit 14 - C5 Replace lock tounge as it was cut off to get a prisoner out of his cell | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-25 10:15:00 | Pass | Replace mortise lock
MSA-DCS | WA3953424 | unit 6 PA not working network error | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-02 18:30:00 | Fail | Attended unit 6, checked PA amp cables and connections in equipment rack. PA amp on and inputs connected. Tested PA service from CI-3210 console, PA connection timed heard no audio from CI-OH handset. Disconnected handset and Meter tested all wires from handset to external RJ12 console plug. Took handset to adjacent unit and tested, handset worked correctly. Reset Unit 6 CI-3210 console. Tested PA call, now working correctly.
MSA-DCS | WA3953437 | very little water pressure in unit 1 & gate house (shared water supply) | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jan 2021 | 2021-01-23 15:34:50 | 2021-01-23 13:00:00 | Pass | Job completed
MSA-DFES | WA3952937 | Mezzanine, 2x lights not operating | Success Career Fire Station (Temp Site) | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-25 10:15:00 | Pass | CompleteAttended site and replaced faulty fluros and ballast on the mezzanine all in working order
MSA-DFES | WA3953061 | SO dorm - Aircon in S.O Dorm making loud crumbling and vibrating noises on start up | CFRS Wangara | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-04-07 16:00:00 | Fail | Replaced condensate pump assembly in s/o dorm.
MSA-DFES | WA3953129 | Simulation centre, secured Storeroom downstairs - double power points not working -see notes | DFES Regional Office - Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 10:00:00 | Pass | Investigated faulty gpos in simulation centre. Found field RCD gpo tripped. Reset gpo. All working.
MSA-DTAG | WA3952734 | Duress alarms faulty - Level 6 - registry counter desk 1, Level 8 - room 8.01, 8.02 , 8.04 | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 22 Jan 2021 | 2021-01-22 11:45:09 | 2021-03-09 11:00:00 | Fail | Work performed by Michael Tomlinson & Ken Moore (22/01/2021)Attended site. Found Pacom IOC board faulty. Deleted and re-programmed inputs to get back working. Still 2x Duressinputs on L8 that need fixing but all others are back up and running.Work performed by Ken Moore (04/02/2021)Replaced Input Board on Level 6. Checked all 32 inputs.Work performed by Ken Moore (05/02/2021)Replaced Input Board on Level 9. Checked all 48 inputs. Found Mezzanine Board faulty, requires replacing.Work performed by Ken Moore 05/03/2021:Level 8 Intercom, faulty LAN cable between door & switch. New cable run needed.Work performed by Ken Moore & Ryan Craven 09/03/2021:Repaired wiring from rooms 8.01,8.02,8.03, 8.04 and 8.08, Retested all inputs at controller to Level 10 control DMJC, all tested and working correctly. Job complete
MSA-DTAG | WA3953017 | Lost feed for camera to carpark | Mandurah Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-02-01 14:45:00 | Fail | 22/1/21 - Dean SimpsonChecked inputs and power cabling.Further investigation with taller ladder required.27/1/21 - Dean SimpsonTested camera and found it faulty. Requires replacement.BRAF submitted.1/2/21 - Ryan VestyReplaced camera and power supply.All tested ok.
MSA-DTAG | WA3953033 | L3 court 34 lock on the front door of court 34 is intermittently difficult to lock. | Central Law Courts | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-25 11:35:00 | Pass | Attended site and serviced front entry door lock to L3 Court 34 for correct operation.Date on Site: 25/01/2021Time on Site: 10:50am - 11:35 am
MSA-DTAG | WA3953237 | Level 3, Court 38 - There is a flickering light inside of courtroom 38 | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 08:00:00 | Pass | Job complete
MSA-DTAG | WA3953430 | CCTV not allowing to view recorded footage | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 13:45:00 | Pass | Cameras not recording reset up on system retested ok.
MSA-DTAG | WA3953472 | Ground, custody control room - Vision to the Sally Port camera No. 26 keeps dropping off | Midland Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 08:12:00 | Pass | Attended siteLocated and investigated cam 9 (26)Found power supply over heating causing the encoder to drop out which the camera is connected to as it is analogueReplaced power supply camera, camera functional all workingAdvised site of the outcomeLeft siteSupplied Part:1x Sinpro 3.5VDC 25.7A Power supply
MSA-DTWD | WA3952945 | Rear Courtyard - Repair water supply to fountain pump | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-25 11:45:00 | Pass | Arrived on site and inspected found the float to the tank is working fine and the tank full. There was no power to the pump. Tried to trace the cable could not find the Switch. The FM will call the eletrican to check.
MSA-DTWD | WA3952947 | A block L3 A325 Repair Power and data point 3L and power GPO hit in A325 | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-01 14:30:00 | Pass | Completed works as required - 1x dbl gpo replaced, 1x data point and mounting blocks replaced
MSA-DTWD | WA3952965 | D block, level 1, D102 - aircon not working | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-03-23 10:00:00 | Fail | Collected parts from workshop. Attended site and completed pre start paperwork and signed in.Accessed unit and isolated.Removed pcb, fan motor/blade and capacitor and replaced with new. Reinstated power to system and test ran. Found system to start and run with out fault. Observed system run and left unit in good working order.
MSA-DTWD | WA3953009 | A block L2 A256 air con warm | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-03-19 12:30:00 | Fail | Reattended site signed in located room and checked with employees inside room to see if there have benn any further issues since the compter upgrade was completed. All clients have been happy with the airconditoner system .left all operational
MSA-DTWD | WA3953022 | C block, level 1, C101 - Replace broken spout on water cooler | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 13:05:00 | Pass | Replaced broken faucet.
MSA-DTWD | WA3953028 | D block, Level 2, open area - the VAV 2.21S actuator making a loud noise | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Precise Air Group | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-09 16:00:00 | Fail | Picked up required parts attended site and signed in located system, isolated vav 2.21 set up large ladder and replace faulty actuator with new, tested and left operational
MSA-DTWD | WA3953095 | T Block TM156 - Fume cabinet extraction fan is not working | Munster Campus (ACEPT) | GMP-BR | Equipment | Building Equipment (EQ) | SW HART & CO | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-04-21 10:25:00 | Fail | VSD Faulty, New VSD Fitted. Re-tested. Passed.
MSA-DTWD | WA3953107 | Level 3 (roof) - Remove graffiti from walls | Perth Campus B4 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-25 14:30:00 | Pass | REMOVAL OF GRAFFITI FROM WALLS
MSA-DTWD | WA3953117 | north block, Level 2, Emergency Control Room - correct operation of Fire Panel with approved matrix | Perth Campus B1 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | FLDCOMP | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-10-27 13:22:00 | Fail | Repair
MSA-DTWD | WA3953121 | ladies toilet ground admin building 3x toilets seats and toilet damaged | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 11:00:00 | Pass | COMPLETED
MSA-DTWD | WA3953141 | E block ground cool room E33 fans are blowing out cardboard - Att simon Kenwood | Bentley Campus | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-03-04 14:00:00 | Fail | COOLROOM - CLEAN BLEACHED 2 OTHER GRILLS. RUSTY FANS - BRAF TO REPLACE AWAITING PRICE.
MSA-DTWD | WA3953142 | admin building, ground floor - entire row of flighting out | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 11:30:00 | Pass | Attended site and signed in. Got keys from facilities. Found lights on row 4 not working. Checked power at fuse. Found blown. Tested circuit and found no fault on lights. Replaced fuse and lights not operating. Tested power and nothing at lights. Switch okay, 2 way wired. Located other switches in IT store room. IT have stacked up the computers on the wall and pressed the switch to middle causing to arc and spark. Disconnect and removed both switches from store room and bypassed wiring. Tested all lights working. Signed out. Job complete
MSA-DTWD | WA3953154 | Science Block various rooms - Multiple lights out & Ceiling lab light blown(see notes for rooms) | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 09:30:00 | Pass | Complete Attended site and replaced multiple fluros on site
MSA-DTWD | WA3953250 | Ground kitchen - Back door lock faulty | Thornlie Campus | GMP-BR | Building | Doors (BU) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 10:10:00 | Pass | Back door to kitchen lock faulty.Lock repaired.
MSA-DTWD | WA3953295 | W block L1 W106 male toilet light not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 11:19:00 | Pass | Replaced faulty fluros and lamp holders
MSA-DTWD | WA3953319 | B block L1 B105 light switch faulty | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 14:50:00 | Pass | Replaced faulty light switch to b105 storeroom
MSA-DTWD | WA3953365 | A block L1 A126 Dead rat in ceiling space A126 Staff Lunch Facility | East Perth Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 07:10:00 | Pass | Dead rodent removed from behind fridge in staff lunch facility A126
MSA-DTWD | WA3953370 | T block L2 executive office air con fault | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 10:00:00 | Pass | Checked office areas and BMS. No issues or faults found.
MSA-DTWD | WA3953402 | Level 2, cafe L2 - lights blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-02 13:00:00 | Fail | Attended site and signed in. Got keys from facilities. Located cafe lights. Found heaps of lights out. Replaced tubes and starters to many lights. Replaced lamps to downlights. Replaced fuse to blown circuit. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3953466 | C block, Walk in coolroom C11 is tripping circuit breaker | Bentley Campus | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 22 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 12:00:00 | Pass | ATTENDED FOUND COOLROOM OFF ON BREAKER. REST TO TEMPEATURE, TESTED. NO FAULT FOUND. System failed again due to faulty compressor. Works to replace compressor carried out by other tech.
MSA-DTWD | WA3953467 | B block, B2421 - aircon leaking water from indoor unit | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-02 16:30:00 | Fail | No leaks found. Maintenance are going to monitor and if possible locate leak for repairs.No further communication from maintenance regarding water leaks. Job closed off.
MSA-DTWD | WA3953468 | E block, male toilet E7 - system is leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-17 16:30:00 | Fail | Repaired cistern
MSA-DTWD | WA3953470 | D block, D32 External – Break in underground water services causing flooding and sunken paving | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 18:30:00 | Pass | repaired pipe, backfill and replace pavers
MSA-DTWD | WA3953471 | E Block, E58 Large Scale Kitchen – 4 x damaged flyscreens to windows on east wall | Bentley Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-29 16:15:00 | Fail | Rewire 11 flyscreen screens complete11 - 980 X 50010 l/m of spline
MSA-MRWA | WA3953083 | Ground level, Male toilet - Full flush button not working. | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor-Toilet-Male-AG.01 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 14:45:00 | Pass | Replaced leaking bellows
MSA-MRWA | WA3953087 | Inlet Valve not working. | Don Aitken Centre MRWA Head Office-Main Building-Second Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 15:35:00 | Pass | Replaced faukty bellow
MSA-MRWA | WA3953098 | Leak from water recipient, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Third Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 15:53:00 | Pass | Inspected plumbing duct. No issues found.
MSA-MRWA | WA3953170 | Courtyard Ice machine, excessive vibrating and rattling - see notes | Materials Engineering Branch-Admin Building-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 22 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-18 10:00:00 | Fail | Repaired vibrating ice maker A40189273N ADJUSTED AND TIGHTENED LOOSE BACK COVER A40189272M
MSA-DCS | WA3953483 | Unit 2- Gas HWS is leaking and flooded the floor | Karnet Prison Farm-Dairy External Area | SPA-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 08:55:26 | 2021-02-11 16:00:00 | Fail | Replaced 260L storage unit & flu
MSA-DCS | WA3953492 | All security system in Unit 4 is crashed. | Albany Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 16:10:39 | 2021-01-23 11:00:00 | Pass | Talked site though fault finding found power unplugged to main rack all tested ok
MSA-DCS | WA3953503 | UNIT 4- Cell call systems are not working in unit 4. | Hakea Prison-Unit 4 | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 13:57:53 | 2021-01-23 12:41:00 | Pass | Attended site checked and found U4 office can’t answer cell call or make PA call. Further check located the problem to be the faulty cell call handset in office. Replaced with second hand handset and tested all ok after replacement.
MSA-DCS | WA3953504 | Aircon is visit room is not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 13:59:13 | 2021-01-23 13:30:00 | Pass | Attend site on callout. Sign in and follow entry protocols. Access visitor room and found unit to have E5 fault, communication error between indoor and outdoor unit. Power cycle unit and and found fault to reset. Found unit to start. Check operation of unit and found to operate as normal. Found both stages to run as normal. Tighten all electrical conection on printed circuit board and wall controller. Unit is working with no faults.
MSA-DCS | WA3953507 | Unit 3 A6 cell call is not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Jan 2021 | 2021-01-24 10:40:21 | 2021-01-25 10:00:00 | Fail | Replaced Bottom Cellcall. Top unit is just a push button so no need to replace. Tested. Everything working as per normal
MSA-DCS | WA3953521 | Cell call system is at fault - CCU | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 16:32:21 | 2021-01-23 13:15:00 | Pass | Checked and found CCU H5 cell call stuck on remote display and cell call not working in H5. Called H5 from office console and reset the stuck call on remote display. Testedall cell calls in H5 working ok after.
MSA-DCS | WA3953531 | Vesda fire alarm fault - not connecting to system - fire panel: unit 14 INC | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 17:39:39 | 2021-01-23 15:30:00 | Pass | 23/01/21 EIWA3953531Attended site after hours callout to unit 14.Identified damaged remote fire mimic in control room LCD80.Checked comms cable continuity OK.Checked LCD80 for voltage and measured 27.4VDC supply.Replacement display required.Replaced VESDA filter in Wing AC Cell 1/2.Note:Wing BD Cell 5/6 VESDA identified information tag placed on mimic VESDA as requiring replacement.28/01/21 EI/JVReplaced faulty mimic for new OK.
MSA-DCS | WA3953542 | Perimeter fence - camera temper alarm - C35 and C36 | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Jan 2021 | 2021-01-23 19:36:42 | 2021-01-28 09:00:00 | Fail | Rectified and fixed tamper fault, job completed.
MSA-DCS | WA3953546 | Gatehouse - Restraint room - Water leaking from the ceiling through the smoke alarm. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Jan 2021 | 2021-01-24 18:05:14 | 2021-01-23 20:30:00 | Pass | Job completed
MSA-DCS | WA3954028 | Retrospective W/O - Gatehouse - Restraint room - roof drip tray for A/C damaged or broken | Bandyup Prison-Entry Building | GMP-BR- HO | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 23:30:00 | 2021-01-27 08:53:00 | Fail | COMPLETED
MSA-DFES | WA3953548 | Cockburn Emergency Services Centre-Main Building - | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 23 Jan 2021 | 2021-01-23 21:17:44 | 2021-01-23 20:00:00 | Pass | ComepleteAttended site and located non working power to Simone. Found rcd to have been tripped. Reset and Tested, all in working order. Notified staff and signed out
MSA-DCS | WA3953567 | Gallagher system in gatehouse is down, cameras and other functions been lost | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Jan 2021 | 2021-01-24 12:02:19 | 2021-01-24 10:15:00 | Pass | Video wall had been turned off recovered and tested all ok
MSA-DCS | WA3953578 | INF Control room -Safe cell monitor is not funtioning | Casuarina Prison-Outpatients Health Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Jan 2021 | 2021-01-24 13:13:45 | 2021-01-25 00:00:00 | Fail | Found pc frozen reset and tested ok
MSA-DCS | WA3953596 | Health department cell call B5 INF is not working, | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-27 09:45:00 | Pass | Replaced push button that’s integrated into cellcall unit. Configured cellcall to suit. Tested. Everything operating as normal.
MSA-DCS | WA3953614 | No water pressure in the gate house and unit one | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-25 14:15:00 | Pass | Arrived on site and inspected found the water pressure us 425 kpa in the unit one shower blocks.
MSA-DCA | WA3953694 | Preservation Area - Fault on VESDA is L4 Preservation area. Please inspect | State Library of WA-Main Building-Level 4 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 25 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 08:15:00 | Pass | VESDA 4th floor on rare book room in fault. System inspected reset. Operating correctly.
MSA-DCA | WA3953697 | Lift 4 & 5 (Back of house Goods lifts) are not functioning | State Library of WA-Main Building-Ground Floor-GF09 - Lift Corridor - Near Security Office | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 25 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 09:30:00 | Pass | job completed - Both lifts on ground floor and landing button working but car not taking calls. Both controllers displayed lifts in as normal.Error in log for lift 4 -7, 733, 720 and 10. Lift 5- 86. Reset both lifts and monitored ok. Lifts RTSTo be closed out at $0
MSA-DCA | WA3953810 | ground, Sewage pump 2- Pump 2 light is showing in fault and alarm is sounding in sprinkler cupboard | Maritime Museum Victoria Quay-Robert Steele Marine Engineers Display-Ground Floor-Pump Room | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Ballantyne Plumbing Gas & Electrical | 1 | CLOSE | 25 Jan 2021 | 2021-01-25 17:00:00 | 2021-01-25 12:00:00 | Pass | Repairs to pump
MSA-DCA | WA3953814 | HBRC Fault on Chiller 2 & CHWP2. Faulted early AM on Sunday 24th Jan, BMS alarm. Please investigate | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 16:30:00 | Pass | Attended site. Chiller 2 CHWP & chiller in fault. Applied tests and checks. Investigation found CHWP and chiller to have faulted due to a site power interruption. Reset CHWP VSD and chiller system. Switched lead lag and monitored system operation. System operating correctly.
MSA-DCA | WA3953852 | Level 5 roof, cooling tower drain is leaking | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 16:30:00 | Pass | Inspected CT 1 and 2 for water leaking as reported by contractor. Identified leaking from Drain. Seems to be blockages also as when valve opened minimal water drains.Cut drain side of isolation valve for inspection. Opened valve and cleared debris and sediment build up. Arranged replacement parts. Fitted new removable couplings for future access.
MSA-DCA | WA3953932 | Graffiti - concrete tables urban orchard & panels on western side of state library | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 11:45:00 | Pass | Graffiti removal from concrete tables in the urban orchard & panels on western side of state li
MSA-DCA | WA3954001 | various locations, irrigation has several breakages | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 25 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-25 12:15:00 | Pass | Job completed - Replace broken sprinklers and nozzles
MSA-DCS | WA3953705 | Control pod - Unit 4 Vesda L14 25S1 standard analog fault | Bandyup Prison | GMP-GR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 07:34:56 | 2021-03-15 11:57:00 | Fail | Bandyup 25/1/21 BGUnit 4 J block zone fault on arrival. Upon investigation found vesda comms was lost between field aspirator and control room display unit. Power cycled unit and comms was regained. Noticed rodent droppings in field unit causing fault. If fault returns recommend new relay board be fitted.Unit 6 cell 11 intermittently causing analog fault on FIP. Replaced with new XP95 smoke.Unit 4 J block zone fault has returned. Rebooted Vesda and unit will not normalise. Unit is EOL and is no longer serviceable # vls-30415/03/21 EIAttended site and replaced damaged VESDA VLS in unit 4 J block OK.Test operation & signals back to the POD FIP OK.System status displaying normal on departure.
MSA-DCS | WA3953708 | gate house, Staff room area door - no working permanently unlocked (controlled from master control) | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Jan 2021 | 2021-01-25 11:38:03 | 2021-01-25 09:00:00 | Pass | Staff door permanently unlocked. Checked devices on door and found Breakglass pressed. Reset breakglass and tested operation, all in working order.
MSA-DCS | WA3953720 | Unit 7, F3 - Main lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 07:50:27 | 2021-01-25 10:30:00 | Pass | Attend site to look at main lock in unit 7 F3. Replaced driver bush and serviced lock.
MSA-DCS | WA3953722 | Reception store, Property store - Electric door handle not working. Unable to lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 07:52:31 | 2021-01-25 12:30:00 | Pass | Attend site. Electronic door handle not workings. Unable to lock. Replaced faulty C lever handle and has been programmed to reception door.
MSA-DCS | WA3953723 | Unit 8, C9 - Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 07:55:07 | 2021-01-25 09:30:00 | Pass | Replaced damaged switch
MSA-DCS | WA3953727 | Unit 6, C10 GPOs burnt in fire in cell | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 07:56:29 | 2021-01-25 10:30:00 | Pass | Replaced burnt gpo
MSA-DCS | WA3953733 | Unit 7, E wing day room - hot water tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:00:44 | 2021-01-25 14:14:00 | Pass | Replaced leaking spindle
MSA-DCS | WA3953737 | Unit 9, compound - water tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:03:48 | 2021-01-25 15:25:00 | Pass | Replaced outdoor tap abd washer
MSA-DCS | WA3953743 | Jeelia C7 Faulty light switch | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 09:30:00 | Pass | Replaced faulty switch
MSA-DCS | WA3953750 | Jeelia B Wing Mice present in the area, please eridicate | Wandoo Rehabilitation Facility | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 12:15:00 | Pass | .
MSA-DCS | WA3953751 | Kitchen - all plumbing backed up and blocked, all sinks, drains, and toilets | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 25 Jan 2021 | 2021-01-25 12:10:42 | 2021-01-25 13:15:00 | Fail | Cleared blocked drain.Hand dig and repaired broken sewer drain outside the kitchen.
MSA-DCS | WA3953754 | Video link, Court Room 10 - Lock faulty on door. Not latching | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:07:03 | 2021-01-25 10:45:00 | Pass | Attend site. Lock faulty on door, not latching. Filed out striker plate to allow the door to lock correctly.
MSA-DCS | WA3953768 | Unit 2, C4 - smoke detectors blocked | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:18:59 | 2021-01-25 14:21:00 | Pass | cleaned out and reset all ok
MSA-DCS | WA3953769 | Unit 2, C10 - smoke detectors blocked | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:21:49 | 2021-01-25 14:22:00 | Pass | cleaned out and reset all ok
MSA-DCS | WA3953775 | Unit 2 AB Dayroom window winder chain is broken | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-03-10 14:00:00 | Fail | NEW WINDING MECH INSTALLED
MSA-DCS | WA3953785 | Unit 4, C & D wing yards - Items stuck in the razor wire needs removing | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-12 08:30:00 | Fail | 12/02/21Remove items stuck in razor wire at Unit 4 C and D wing
MSA-DCS | WA3953788 | Video link, front door - Integrity of main lock needs to be checked. Prisoner accessed after hours | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:35:21 | 2021-01-25 11:20:00 | Pass | On site. Inspect video link front door lock and and electric strike plate.
MSA-DCS | WA3953789 | Bakery - Gas rack oven keeps showing on screen serial communicator inverter & beeping not heating up | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:30:03 | 2021-01-25 12:30:00 | Pass | COMPLETED 25/1/21
MSA-DCS | WA3953794 | Unit 5, Near cell C15 - Light fitting damaged new fitting required | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 13:30:00 | Pass | Installed new light
MSA-DCS | WA3953804 | Unit 2 - A6 twisted metal bar on sides of window has been bent out of joint | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 14:00:00 | Pass | WINDOW FRAME REPAIRS COMPLETE
MSA-DCS | WA3953813 | Unit 3 - C9 window runners not working | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 09:30:00 | Pass | NEW SPIRAL BALANCES INSTALLED
MSA-DCS | WA3953817 | Unit 3 - D7 window runners not working | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 11:30:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3953824 | Unit 3 - B3 window runners not working | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 10:30:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3953827 | The cell call in cell 2.02 is not activating in the Unit Control. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 08:58:58 | 2021-01-28 09:34:00 | Fail | Found cell call working tested all ok no issues after multiple tests
MSA-DCS | WA3953830 | The Personal Duress Alarm 22 is not working at all. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 09:03:09 | 2021-01-28 09:48:00 | Fail | Deprogrammed old 22 duress and programmed un new duress unit parts on site
MSA-DCS | WA3953841 | Unit 2, D1 & D2 - smoke detectors blocked | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 09:08:55 | 2021-01-25 14:24:00 | Pass | Found U2 Cells D1 and 2 sampling point to be deliberately blocked by prisoners.Cleaned sampling point and returned airflow to normal.
MSA-DCS | WA3953844 | Unit 13 - A3 has no water pressure from the taps | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-08 12:30:00 | Fail | Nill
MSA-DCS | WA3953850 | Unit 5 - C13 trap under basin is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-11 08:30:00 | Fail | Nill
MSA-DCS | WA3953862 | Unit 2 - A Wing shower not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-16 15:30:00 | Fail | Nill
MSA-DCS | WA3953870 | Unit 13 - C3 shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 08:30:00 | Fail | Nill
MSA-DCS | WA3953878 | Outpatients Area - Toilet Prisoner toilet is constantly flowing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-18 14:39:00 | Fail | Nill
MSA-DCS | WA3953887 | Unit 14 - A14 broken light switch cover | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 09:33:26 | 2021-01-25 15:00:00 | Pass | Replaced damaged cell switch in unit 14 a14
MSA-DCS | WA3953909 | Official visits - Front Entrance Faulty lock on (white) double door entry gate | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-16 14:30:00 | Fail | Require parts.Cut off old hinges, weld on new hinges, service lock, adjust strike and escutcheon.
MSA-DCS | WA3953915 | SHU (9) - Control Room 2 X Monitors in SHU control have crashed and need attention. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-25 11:00:00 | Pass | All monitors where not in correct sequence upon arrival. Put everything in correct order. No more problems with the system after a restart
MSA-DCS | WA3953921 | Unit 2 - B & D D wing grill failed to open, had to use handle to open, | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 09:48:13 | 2021-01-25 13:10:00 | Pass | 25/01/21Adjust limit strike plate on D wing grille.No fault present with B wing grille.
MSA-DCS | WA3953933 | Unit 15 - Control Room screen for the gill control box has smashed - see notes | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Jan 2021 | 2021-01-25 13:53:47 | 2021-01-25 12:40:00 | Pass | Contacted Niall from PFM - Confirmed job is to be closed - site to rectify through project directly - no further works by SEME - Close and invoice cost to date.
MSA-DCS | WA3953940 | Unit 2 - D7 sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-29 12:30:00 | Pass | Blockage cleared quite easily, maintenance and unit staff have plungers which they do not use
MSA-DCS | WA3953951 | POD 1, Unit 4 - has intermittent fault with antenna | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Recreation Equipment (EQ) | Sapio Pty Ltd | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 08:30:00 | Pass | Tested all points and TVs, all showing very high signal strength.Job completed.
MSA-DCS | WA3953952 | Recreation tv antenna and associated outlets - faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Recreation Equipment (EQ) | Sapio Pty Ltd | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 09:30:00 | Pass | Attended site, reported faulty antenna and points in Recreation Hall.Job requires new install of Antenna and TV Point in Recreation Hall, not a breakdown, but new install.Job completed.
MSA-DCS | WA3953955 | Unit 2 - B & D Cleaning cupboard on B wing is leaking water from ceiling, near the vent in the room. | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 12:00:00 | Pass | ON INSPECTION IT WAS FOUND TO HAVE BEEN COMPLETED - JOB A DOUBLE UP
MSA-DCS | WA3953958 | UNIT 4, B wing - washing machine making very loud nosie (bearing) | Wooroloo Prison Farm | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 11:00:00 | Pass | Unit 4, B wing washing machine making loud noise. Check machine & controls. Run machine thru all cycles. Found main bearings to be noisy but machine works ok. To replace bearings would require major overhaul. Cheaper to wait till not working.
MSA-DCS | WA3953961 | Unit 14 - B10 internal light switch is broken. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 13:00:00 | Pass | Investigate and replace unit 14 cell b10 light switch
MSA-DCS | WA3953962 | 2a, first shower blocked - light faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 16:30:00 | Pass | Replaced 4x LED lights
MSA-DCS | WA3953964 | Main kitchen - light Fitting needs attention faulty/damaged | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 13:30:00 | Pass | Replaced faulty light fitting in kitchen area
MSA-DCS | WA3953965 | Unit 14 - A10 Inside light switch is damaged and has large crack. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 10:16:21 | 2021-01-25 15:00:00 | Pass | Replaced damaged cell switch in unit 14 a10
MSA-DCS | WA3953969 | Main kitchen - hot water heaters faulty, tight hand side not turn on and left side not heating | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-25 15:15:00 | Pass | Arrived on site and inspected found the both unit working in order at 73C. Tested the unit with taps running. Both units started and working fine.
MSA-DCS | WA3953974 | Main kitchen - bell not heating to temperature, next to BRAT pan | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 15:00:00 | Pass | 27/01/21Arrived at site liaise with kitchen, identify bell, isolate remove panels, test/fault find diagnose and found that the front potentiometer is faulty and requires replacement, also found the micro limit switch was loose and has and intermittent fault will require replacement as well.Part Required1x front potentiometer+knobFitted by another supplier
MSA-DCS | WA3953980 | Unit 14, D12 - Shower is leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 09:30:00 | Fail | Nill
MSA-DCS | WA3953982 | Unit 8 wing cameras are frozen unable to reset | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 10:21:38 | 2021-01-25 12:30:00 | Pass | Traced fault to EBI workstation 11. Shutdown and restarted. Logged onto station and setup CCTV monitors. Tested ok.
MSA-DCS | WA3953990 | Unit 7 - Court Yard water fountain leaking from filter | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 10:30:00 | Fail | Replaced Filter System with new AP11 Dura Filter System inc filter and all parts/fittings and connected to existing Waterware Fountain
MSA-DCS | WA3954008 | Unit 14 - A9 Shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 11:42:00 | Fail | Nill
MSA-DCS | WA3954021 | Unit 14 - A15 Shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 23:30:00 | Fail | Nill
MSA-DCS | WA3954027 | Unit 14 - C16 Shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 13:27:00 | Pass | Nill
MSA-DCS | WA3954034 | Unit 14 - C13 hower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 09:30:00 | Pass | Nill
MSA-DCS | WA3954039 | Unit 14 - A4 Shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 12:30:00 | Fail | Nill
MSA-DCS | WA3954042 | Unit 14 - C12 hower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 09:30:00 | Pass | Nill
MSA-DCS | WA3954045 | Unit 14 - C9 Shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 13:30:00 | Pass | Nill
MSA-DCS | WA3954048 | Unit 14 - C10 Basin & shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 13:30:00 | Fail | Nill
MSA-DCS | WA3954051 | Pre release unit double access gate opening/closing fault | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 11:10:52 | 2021-01-27 12:30:00 | Fail | 25/01/21Attend site. Assess fault. Replacement parts required. Modify controller so gates can still be used in interim27/01/21Replace PE Beams. Modify controller back. Test operation
MSA-DCS | WA3954052 | Unit 9, A7 - Tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 11:06:10 | 2021-01-25 16:46:00 | Pass | Replaced 1/4 spi dles on the basin
MSA-DCS | WA3954053 | Unit 14 - C5 Basin & shower draining slowly - overflow issues | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 14:30:00 | Fail | Nill
MSA-DCS | WA3954055 | Video link, comms room - Air Con overheating | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 11:13:28 | 2021-01-29 14:30:00 | Fail | Replaced faulty cb's. No fault with AC. Unit fully operational.
MSA-DCS | WA3954058 | Unit 14 - C1 Shower head constantly dripping. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 15:30:00 | Fail | Nill
MSA-DCS | WA3954059 | Unit 9, control room - Sliding Window to A/B side frame broken | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 11:15:08 | 2021-01-25 17:00:00 | Pass | FRAMEWORK REPAIRS COMPLETED
MSA-DCS | WA3954061 | Unit 2, D16 & D2 - Smoke detectors blocked | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 11:17:08 | 2021-01-25 14:26:00 | Pass | cleaned out and reset all ok
MSA-DCS | WA3954091 | Unit 7 - B4 Toilet cistern for cell B4 is filling very slowly. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-08 15:30:00 | Fail | Nill
MSA-DCS | WA3954124 | unit 1 cell C12 Lino damaged in big areas | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | COMPFIN | 25 Jan 2021 | 2021-01-29 17:00:00 | 2022-06-21 14:30:00 | Fail | damaged flooring removed - prep work done, vinyl replaced
MSA-DCS | WA3954126 | Unit 1 B wing dayroom door lock Lock needs service hard to operate | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 12:20:00 | Pass | Attend site and repair lock on Unit 1 B Wing door.
MSA-DCS | WA3954128 | Unit 1 B1 Metal skin of cell door broken away, need welding | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-18 11:30:00 | Fail | METAL DOOR SKIN WELDED BACK IN PLACE
MSA-DCS | WA3954136 | unit 1 A wing shower room Grates missing from both sinks | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-27 12:12:00 | Pass | Replaced 2 grates in the shower sinks
MSA-DCS | WA3954164 | Reception, Bathroom - sink mixer faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 09:30:00 | Pass | COMPLETED
MSA-DCS | WA3954166 | Unit 1, showers - shower head broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3954190 | Unit 6, C3 - Duct leaking between cell C3+ C4, spraying water, flooding into wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Jan 2021 | 2021-01-26 13:58:31 | 2021-01-27 12:10:00 | Fail | Nill
MSA-DCS | WA3954203 | Cleaning, Court Yard - Bin lifter not working, electrical | Casuarina Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 15:30:00 | Pass | Repaired faulty bin lifter in cleaning workshop
MSA-DCS | WA3954204 | gate house 18-19 multiple perimeter lights not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-03-10 16:00:00 | Fail | Collected lamps and replaced son t lamps in exterior perimeter lights
MSA-DCS | WA3954205 | Urquart cell B06 Faulty shower Temp valve | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-29 13:15:00 | Pass | Replaced faulty tmv
MSA-DCS | WA3954214 | unit 8 cell calls and PA non fuctioning | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Jan 2021 | 2021-01-25 18:43:46 | 2021-01-25 16:30:00 | Pass | Cell intercoms tested ok. All call only worked to the cell intercoms and not the day room or wing speakers. Found the mains power plug for the amplifier half out of the GPO. Plugged in properly, tested ok.
MSA-DFES | WA3953906 | ICV Shed - Motion sensor/after dark light over the personnel door not functioning | VFRS Mundaring | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-09 10:30:00 | Fail | Complete
MSA-DFES | WA3953947 | Main Building (Radio Comms Section), female toilets -Tiles cracking and falling away in female toile | DFES Regional Office - Belmont | GMP-BR | Plastering | Plastering (PL) | AWB Co. | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-03-09 14:04:00 | Fail | Arrived at site, signed in and set up work area. Removed loose tiles to make area safe. Requires a 1100x610mm rectangle to be re tiled. Tiles are plain white 150x150mm. There are a few tiles onsite but not enough to complete. Old backing/adhesive may need to be taken back so tiles sit flush.
MSA-DFES | WA3954096 | Ground floor, Operation Room - Air conditioner in the operation room is not working correctly | Metropolitan VFRS | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 12:00:00 | Pass | Waited for access. Found unit in office had no power, reset power & tested.found low on gas. Repaired leaking flare fitting & recharged with gas
MSA-DFES | WA3954168 | Level 1 Air conditioner to outside study demountable not cooling | CFRS Armadale | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 17:00:00 | Pass | Replaced capacitors.
MSA-DFES | WA3954171 | Rear Yard -27 - Rear yard drain (next to RCR Pad) blocked with sediment / dirt. | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-03-19 11:33:00 | Fail | Investigate blocked storm water drain located back left corner near rcr padLift storm water lids and barricade, lift pump tank lids and inspect Attempt to locate inlets and outlets with water down drain pieces Will need to return with camera before jetting to locate pipes and issuePack up and clean up worksite 7:30-8:30am 4/3/21
MSA-DFES | WA3954173 | PPC storage area - Circuit breaker for lights and fans in the PPC storage area keeps tripping. | CFRS Hope Valley | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 10:30:00 | Pass | Investigated fault with circuit W8. We narrowed the fault down to one light which had faulty and damaged internals. We replaced this light and tested the circuit. The circuit tripped 15mins later. I believe this was just a nuisance trip. We tested the circuit continuously after this trip and everything is working fine. Completed works and stayed onsite for testing.
MSA-DFES | WA3954178 | dorm 9 ground constantly flowing and running | CFRS Perth | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-29 12:42:00 | Pass | Replaced inlet valve in toilet cicten due to old one failed
MSA-DFES | WA3954183 | ground engine room 1 in front of pump | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-27 13:15:00 | Pass | Attended Duncraig Fire Station-- measured up replacement glass panels to counterweight doors-- BRAFF ad Quote for the replacement glass panels is attached. Please refer to the attached service reports and site photos.Thank you
MSA-DFES | WA3954184 | engine room check sensor door has come down whilst pump is in doorway | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-27 14:00:00 | Pass | Attended Duncraig fire station--- Carried out inspection to all safety devices fitted to door. As per the service report the PE beams are working correctly however the bump edge safety device does not appear to be operating correctly. It is our recommendation that a replacement bump edge safety strip is reinstalled to the counter weight door. BRAF to follow.Thank you
MSA-DFES | WA3954202 | ground engine room Floodlighting and perimeter lighting to the building are not functioning | DFES Baldivis | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-10 09:30:00 | Fail | Investigate issue with lights, site has requested that we installed a floodlight where there is already cabling in a junction box. There is also a metal halide light that is dull that we will also swap. We will match the LED floodlights with surrounding lights. Will need to seek approval.
MSA-DFES | WA3954209 | VMSO fluro light flickering | DFES Regional Office - Joondalup | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-27 10:30:00 | Pass | Locate faulty lights. Replaced faulty tubes and starters with new
MSA-DFES | WA3954216 | ground pathway between shed and station has become washed out and uneven | VFES Karnup | GMP-BR | Paving & Roadworks | Concreting (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-18 15:30:00 | Fail | Existing pathway has been excavated and removed and concrete path has been installed
MSA-DFES | WA3954266 | ground split air con is leaking when turned on and not working reliably in general | VFES Karnup | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 09:30:00 | Pass | Completed repair of blocked drain & filters as per notes
MSA-DTAG | WA3953892 | Multiple lights out on multiple levels | Central Law Courts | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 25 Jan 2021 | 2021-01-25 13:34:15 | 2021-01-25 13:33:00 | Pass | Replaced blown fuse to light circuits ground floor and level 4.job completed
MSA-DTAG | WA3954092 | Lighting faulty multiple locations-Domestic Violence Office, Magistrate Chambers' & Magistrates hall | Joondalup Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-01 13:30:00 | Pass | Replaced blown lamps throughout courthouse
MSA-DTWD | WA3953949 | B Block between levels 2 & 3 faulty stairway light | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 15:00:00 | Pass | Attended site, signed in, spoke to fm about job, located lighting, completed jsa, isolated lighting circuit, removed old light from ceiling, replaced with new light, re energised circuit, tested lighting, working as intended, site happy , cleaned up work area, completed paperwork,signed out *** job completed ***
MSA-DTWD | WA3954013 | Car park - Carpark 6 remove tree stump it is a tripping hazard. | Balga Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-16 07:30:00 | Fail | STUMP GROUND OUT
MSA-DTWD | WA3954031 | T block - Glass exit door not locking outside massage area Should be always locked unless swipe card | Murdoch Campus | GMP-BR | Security | Access Control (SE) | Total Security Systems Pty Ltd | 1 | CLOSE | 25 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-16 10:30:00 | Fail | 25/1/2021 - Jose Pereira - 12.30pm to 1pmThe lock intermittently locking recommend a replacement maglock16/2/2021 - Tahni Macara - 7am to 10.30amRemoved V-lock and replaced with mag lock. Tested and commissioned door.
MSA-DTWD | WA3954038 | F block, FG37 Corridor - Faulty lock on double door between FG31 and FG37 | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 25 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-27 10:20:00 | Pass | F Block - door lock faulty between FG31 - FG37.Lock repaired.
MSA-DTWD | WA3954197 | T Block Level 2 fire curtain adjacent T226 Fire curtain bleeping/ fault at the control box | Murdoch Campus | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-25 17:00:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Work Order Number: WA3954197 Priority #: 2Call out Date: 25/01/2021Target Start: 29/01/2021Target finish: 29/01/2021Original information: T Block Level 2 fire curtain adjacent T226 Fire curtain bleeping/ fault at the control box. Attended site:Date: 25/01/2021Start Time: 16:00Finish Time: 17:00Techs on Site: 1Works Carried Out:Reset timeout fault on controller for fire curtain in server room on 2nd floor in T block. Controller normal on departure.System Status on Departure:Normal
MSA-DTWD | WA3954256 | B Block - Room B2305 - Panasonic AC split system not working | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 25 Jan 2021 | 2021-01-29 17:00:00 | 2021-07-16 09:00:00 | Fail | Diagnosed unit to have a PCB issue as discribed with indicated fault code on controller. Ordered parts from suppliers. Fitted new PCB and cap resistor. Removed isolation and started unit. Found fault code not cleared. Was informed possible issue with TXV actuator. Tested and found to be open circuit on 2 circuits. Ordered and picked up part. Returned to site and fitted. Found unit to still be in fault. Contacted Daikin tech support. Daikin returned call well after finish time at 16.45 and informed that fault was "unusual" but needed to be in front of unit to diagnose. Returned to site. Contacted Daikin tech support again and was informed that there is a 2 to 3 hour wait on call back. Now waiting ??Discussed with Daikin tech support but unable to determine why unit is still in fault. Discussed with service manager Simon and sent email to him explaining repairs and investigation so far to engage Daikin tech to attend and rectifier issue.Daikin attended and rectified issue.
MSA-MRWA | WA3954148 | Desk 42 motor not operating correctly motor/controller out of sync please remediate | Road Network Operation Centre (RNOC)-Main Building-Second Floor | GMP-BR | Electrical | General Electrical (EL) | SCHIAVELLO SYSTEMS (WA) PTY LTD | 1 | CLOSE | 25 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 13:00:00 | Pass | Reset control box
MSA-DCS | WA3954312 | Fence of Zone 15 Cowling keeps going off. | Wooroloo Prison Farm-External Areas | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jan 2021 | 2021-01-26 09:27:57 | 2021-01-26 10:00:00 | Fail | Calibrate faulty mx and test the zone , job completed.
MSA-DCS | WA3954393 | Visits area - TDA transponders are beeping | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jan 2021 | 2021-01-26 10:29:28 | 2021-01-26 08:30:00 | Pass | Rectified and fixed the Transponder fault, job completed.
MSA-DTAG | WA3954453 | three lifts is not working need to be fixed asap | Supreme Court | GMP-BR-HO | Building | General Building (BU) | Schindler Lifts Australia | 1 | CLOSE | 26 Jan 2021 | 2021-01-27 15:52:35 | 2021-01-26 17:46:00 | Pass | When responding to the callback dated 26.01.2021, the Schindler Technician found that one of the components had been damageddue to misuse or improper use of the equipment. The main power supply was faulty. Following our attendance, the equipment was left in service.
MSA-DCA | WA3954645 | Grass beds near Beaufort street, sprinkler has been pulled off and pipe has been pulled up | Perth Cultural Centre Precinct | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 15:00:00 | Pass | job completed - Fixed leak in Zone 16 with joiner & cleaned up disturbed soil. Replaced 2 pro spray sprinklers and MP rotators.
MSA-DCA | WA3955399 | Behind the bar - drain pit in ground is filled with smelly water | PICA-Main Building-External Area | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 14:47:00 | Pass | Inspect storm water tank behind pica bar, will have to organise a pump out.
MSA-DCS | WA3954601 | house 4 - Report of light circuit tripping out – requires investigation | Boronia Pre-release-AL10 - Prisoner Accommodation House 4 and 5 | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 11:30:00 | Pass | Tested lights
MSA-DCS | WA3954606 | CCU (11), C3 - Hot water tap & 260mm metal spindle come unsecured. Tap & Spindle taken to security | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 07:32:32 | 2021-01-27 12:16:00 | Pass | Nill
MSA-DCS | WA3954608 | SHU (9), A4, west wing shower tap will not turn off water, water gushes even in off position. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 07:36:54 | 2021-01-27 15:30:00 | Pass | Nill
MSA-DCS | WA3954610 | MPU (11), M12 - water not working in cell sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 07:40:50 | 2021-02-24 08:34:00 | Fail | 19/2 : still waiting for the new cartridge to arrive at ‘galvins Osbourne park’ , we have been told they are expecting it to arrive Monday or sometime next week
MSA-DCS | WA3954613 | unit 1, D wing - taps have come off. Shower taps om SP office restraints cabinet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 07:44:38 | 2021-01-27 10:30:00 | Pass | Nill
MSA-DCS | WA3954614 | Unit 3, C10 - main light faulty (works Intermittently) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 08:30:00 | Pass | Investigate and repair unit 3 c10 cell light
MSA-DCS | WA3954620 | Unit 14, A & C wing, kitchen - tap buttons & handles on tap area loose and can be taken apart | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-28 08:30:00 | Pass | Nill
MSA-DCS | WA3954622 | Unit 6, D6 - toilet running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-27 13:30:00 | Pass | Nill
MSA-DCS | WA3954625 | Unit 13, D wing - grill jammed shut, unable to open | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 0 | CLOSE | 27 Jan 2021 | 2021-01-27 11:57:17 | 2021-01-27 09:30:00 | Pass | 27/01/21Inspect fault. Release jammed pinion.Tested.All working okay.
MSA-DCS | WA3954629 | Unit 4, B&D wing - hot water urn not working, no water coming out of it | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 08:00:10 | 2021-01-27 11:16:00 | Pass | All working on arrival Level sensors look newReplaced inlet solenoid
MSA-DCS | WA3954632 | SITE COST PODS/security - PTZ recreation camera faulty | Bandyup Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jan 2021 | 2021-01-27 12:02:10 | 2021-02-19 16:00:00 | Fail | Attended site and investigated the fault.Checked power supply and connections.Tested fibre link.Checked IndigoVision encoder.Checked PTZ functions on cam19 PTZ recreation.All ok at departure
MSA-DCS | WA3954639 | SITE COST PODS/security - front sliding doors showing open on system when closed | Bandyup Prison | WSM-BR-SITE | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jan 2021 | 2021-01-27 12:04:27 | 2021-01-27 12:30:00 | Fail | Replaced with new sensor on sliding door
MSA-DCS | WA3954642 | entry budiling, amenities/ staff area - cold water not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 11:45:00 | Pass | Replaced cold pump.
MSA-DCS | WA3954643 | Unit 1, control - exhaust fans not working in staff toilets & air lock | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-22 15:30:00 | Fail | Roof top exhaust fans require replacing. recommend roofing contractor be allocated job to replace
MSA-DCS | WA3954644 | Recreation, - external jacaranda park & water fountain PowerPoint keep tripping | Bandyup Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-22 08:00:00 | Fail | Reset power to outdoor power points and tested
MSA-DCS | WA3954666 | Visits area - one officer post air conditioning faulty | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-27 10:00:00 | Pass | Arrived on site and signed in,found aircon to be running,checked over to make sure everything running ok,no faults detected.
MSA-DCS | WA3954678 | MPU (8), M1 - window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-01-29 10:30:00 | Pass | replaced spiral balances
MSA-DCS | WA3954681 | MPU (8), M4 - window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-01-29 12:30:00 | Pass | replaced spiral balances
MSA-DCS | WA3954728 | Vegetable Preparation the waste pipe on the sink has broken off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-03-17 13:30:00 | Fail | Nill
MSA-DCS | WA3954733 | Vegetable Preparation coolroom wall metal damaged | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-01-27 11:30:00 | Pass | Straighten and refit corner flashing to coolroom panel.
MSA-DCS | WA3954813 | Farm - faulty water pump (electrical fault) | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 09:20:56 | 2021-01-27 16:00:00 | Pass | Restored power to Pump 2 ,traced out control and power cct. Drew a layout and control flow diagram for the Farm staff and instructed them on the control quirks of that switchboard . Test ran both pumps for 15 mins ok.
MSA-DCS | WA3954831 | Unit 2 - B13 Toilet needs unblocking, attempted with plunger. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 11:30:00 | Pass | Nill
MSA-DCS | WA3955123 | Security Area - Office PDA # 23 is not activating. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-01-28 10:00:00 | Pass | Tested but works intermittently. Have replaced with a spare one from security. Will order new one and put back in security.
MSA-DCS | WA3955185 | Unit 14 - A3 Window grill vent not operational, | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-18 15:00:00 | Fail | REPAIRS MADE TO GRILL VENT
MSA-DCS | WA3955207 | Unit 2, A16 - water leaking at base of WC pan | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 10:27:42 | 2021-02-10 12:00:00 | Fail | Replaced pan as per braf
MSA-DCS | WA3955226 | Gascoyne - A1, B3, B4, B5 & B6 have mould on ceilings | Wandoo Rehabilitation Facility | WSM-BR-SITE | Building | Ceiling (BU) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-10 11:30:00 | Fail | Mould Remediation
MSA-DCS | WA3955257 | ISU Harding C wing air con not cooling | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-01 13:58:00 | Pass | Complete
MSA-DCS | WA3955323 | unit 3 toilet blocked ablusion block opposite unit 3 office | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 11:34:42 | 2021-01-27 14:00:00 | Pass | Attended site,Cleared blockage to toilet in unit 3 aspirin block next to unit 3 office. Tested on completion
MSA-DCS | WA3955340 | Unit 2C Ablution block in front of cell 31 - leaking water pipe | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 13:00:00 | Pass | Attended site,Locate burst pipe in wall to ablution block unit 2c.Remove existing basin from wall,Use jackhammer to remove tiles and cement to expose failed pipework.Supply and install new copper pipework as required for repair. Reinstate removed cement to flush wall and reinstall and connect basin. Tested works on completion.
MSA-DCS | WA3955345 | Main Kitchen - HWS in toilet is leaking- may need replacing 25litre Rheem | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 14:32:00 | Pass | Attended site,Supply and install new rheem 25L storage hws to ablution block external to kitchen.Electrician completed disconnect and reconnect including installation of isolator as required. All works tested on completion
MSA-DCS | WA3955348 | Unit 3 Ablutions near the office Gas HWS pilot light wont relight | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-27 14:30:00 | Pass | Attended site,Ablution block near unit 3 office. Clean and test pilot lights to the 2 hws to ensure correct function. Tested units on completion
MSA-DCS | WA3955349 | Unit 1 D12 Metal rod missing from toilet push button | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 11:47:50 | 2021-02-09 10:15:00 | Fail | Replaced missing button
MSA-DCS | WA3955359 | Lenard C04 shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 16:00:00 | Pass | Fixed leaking shower
MSA-DCS | WA3955362 | Serpentine cell 06 smashed window Approx. 450 x 1200 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-12 14:00:00 | Fail | NEW WINDOW GLASS INSTALLED
MSA-DCS | WA3955414 | Unit 7 Regi area Fluorescent light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 10:30:00 | Pass | Repaired light
MSA-DCS | WA3955418 | Unit 6 Regi area Leak under the sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 12:55:43 | 2021-01-29 13:50:00 | Fail | Repaired leaking tap in kitchen
MSA-DCS | WA3955500 | Zone 10 Perimeter - PE Beams constantly alarming | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 14:08:31 | 2021-01-27 17:30:00 | Pass | Alarm due to high wind and weeds in the detection area removed before arrival. Recommend similar area affected have the weeds and other loose objects removed to prevent false activations. Zone secure on departure
MSA-DCS | WA3955504 | Health Administration - power point not working in metal health room | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 11:30:00 | Pass | Investigate and repair PowerPoint in mental health room
MSA-DCS | WA3955531 | Unit 6, B10 - Very low water pressure from sink tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-19 10:20:00 | Fail | Replced valve and adjusted flow
MSA-DCS | WA3955532 | Unit 6, C3 - tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-19 11:00:00 | Fail | Rewashed tap
MSA-DCS | WA3955533 | gatehouse comms room 1 x air-con not working (comms going into alarm due to heat) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-03 14:45:00 | Fail | Complete
MSA-DCS | WA3955546 | SB1 (Between U15-U16) - Front Entrance Lock on Main Entry Gate between Units 15 and 16 isnt working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 14:45:35 | 2021-01-28 10:00:00 | Pass | Adjust strike.Top hinge is coming loose, Require AFD to attend, Maintenance notified
MSA-DCS | WA3955607 | infirmary safe cell lock will not open prisoner in cell | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 27 Jan 2021 | 2021-01-27 20:25:06 | 2021-01-27 18:45:00 | Pass | Attend site after hours open jammed cell and service lock
MSA-DFES | WA3955176 | Rear yard - The soak well at rear of engine room is holding stagnate water | CFRS Murdoch | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-03-17 10:04:00 | Fail | Cleaning the soakwell
MSA-DTAG | WA3954713 | Lift 10 - Panel door lift 10 is loose. The lock is the G4S security offic | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-27 13:30:00 | Pass | Cop key lock has fallen out. Spoke with NS in stock in Sydney. Lift off. AS EP notified. Obr created.
MSA-DTAG | WA3955018 | 1987 L1 Sheriffs Office No lights/power in basement carpark or stairwell. | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 09:15:00 | Pass | Lights and power working on inspection
MSA-DTAG | WA3955432 | 1903 Roller door controls show “flashing green light - see notes | Supreme Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 14:17:00 | Pass | 27/1/21 - Door was showing direction fault possibly due to full power shut down and re wiring of the building over 4 days of the weekend. Removed access control and reset door direction and reset limits re installed access control. Tested operation all ok.28/1/21 - The phases had been corrected again so the door was travelling in the wrong direction. Reset the door. And tested. All good.
MSA-DTAG | WA3955538 | Power shutdown, technician required to attend 05.30pm Wed 27 Jan 2021 – contact Gary 0467 095 980 | Supreme Court | GMP-BR-HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 20:30:00 | Pass | Attended site at 530pm to isolate fip for power shutdown, returned to site at 8pm to deisolate when power was reinstated.
MSA-DTAG | WA3955539 | 1903 basement Power shutdown, technician required to attend 05.30pm Wed 27th Jan | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 21:30:00 | Pass | All mains power restored. Powered up all systems and logged in and checked all programs. All cameras ok and all doorsok.Job completed.
MSA-DTWD | WA3954570 | Level 1,A Block, A120A Leederville Cafe - Repair hot water system leak | Leederville Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jan 2021 | 2021-01-27 17:00:00 | 2021-02-08 14:15:00 | Fail | Arrived on site and gained access to the site. Inspected found the rhs of the hot water circulation pump system manifold was rusted. Isolated water and hwu. Could not get the parts. Order parts from the supplier. Returned to site reconnected water and hwu. We will come back once we have the parts. Returned to site. Isolated hot water system. Removed the manifold. Collected parts from supplier and returned to the site. Fabricated and installed new manifold and refitted the pumps. Reconnected water and power. Tested all working in order.
MSA-DTWD | WA3954577 | Level 1,A Block, A107, cafe - lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 27 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 09:15:00 | Pass | Attended site and signed in. Get keys from security. Located cafeteria and found various lights out and flickering. Replaced all tubes and starters to lights in cafeteria and kitchen. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3954590 | D Block, Library - password override required for card access printer | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 1 | CLOSE | 27 Jan 2021 | 2021-01-27 17:00:00 | 2021-01-27 11:30:00 | Pass | Ascertain fault. IT replaced printer with non compatible printer. IT have also deleted user generic login. Programmed card access. Reconnected old printer. Programmed user privileges as required by Tracey
MSA-DTWD | WA3954722 | N block, level 1, N106 - Roller Shutter wont lock to cafe | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 12:00:00 | Pass | Repair lock
MSA-DTWD | WA3954730 | N block, Level 1,N106, Cafe - blocked drains | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-27 13:16:00 | Pass | Arrived on site and inspected found the sink near the rim burner blocked. Cleared blockage and tested multiple times all working in order.
MSA-DTWD | WA3954741 | K block storeroom roof broken skylight | Balga Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | AWB Co. | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-04 11:00:00 | Fail | Measured for replacement sheets to roof of storeroom K blockPicked up materials and replaced 2x roof and fibreglass sheets, removed all waste from site.
MSA-DTWD | WA3955107 | E block kitchen E58 service fridge not working running at 30 deg | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 13:00:00 | Pass | Very low refrigerant charge. Located and repaired leak with replacing liquid line Schrader valve and recharged system with refrigerant. All ok
MSA-DTWD | WA3955250 | A block ground server room has a faulty PIR sensor | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BJ SYSTEMS | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-02 12:45:00 | Fail | Replaced faulty 360 PIR in A Ground server room with new PIR. All working correctly
MSA-DTWD | WA3955317 | E block E39 corridor cool room 2x faulty padlocks | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-09 13:50:00 | Fail | E39 - Cool room padlocks faulty.Padlocks repaired.Job could not be completed in time frame due to Covid lockdown.
MSA-DTWD | WA3955336 | entrance to Ward 2 - Q-Block alarm panel to emergency air system is in fault | Joondalup McLarty Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-02-17 15:30:00 | Fail | Investigated the alarm panel, found the circuit board to be faulty, panel keeps saying no signal on inputs 3-8 while only the first two inputs are in use. All attempts to remedy the problem result in the errors popping up continuously. Have found no other issue with the front face plate of the unit or the input voltage. The same error occurred on the other unit mid last year. Will require to order a new circuit board and replace once it is in.Supplied and installed new panel
MSA-DTWD | WA3955411 | House 15 front door faulty | Muresk Institute | GMP-BR | Building | Doors (BU) | Lee Carpentry | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-24 12:00:00 | Fail | Job completed - replaced door
MSA-DTWD | WA3955412 | T-Block, Level 1, room T108, T109, T110 - worn door locks | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 13:00:00 | Pass | Serviced locks on rooms
MSA-DTWD | WA3955458 | F block AG05 library Lighting cct R4 not working - See Glen Pearson for more details. | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-28 10:15:00 | Pass | Attended site and signed in. Got keys from facilities. Located library light fitting not working. Tested and found faulty connections and old fitting. Advised to replace with led. Disconnect and removed faulty light. Supply and replace with new led panel with recess kit to suit ceiling tile. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3955499 | D block, level 1 Exterior - Fountain Pump, not operating | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-02 14:54:00 | Pass | Replaced pump and fittings.all working fine,job completed
MSA-DTWD | WA3955534 | B5- Level 3 - Room A356 No power to parts of room (west wall) | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-28 11:45:00 | Pass | Attended site and signed in. Got keys from facilities. Located classroom. Found no power to gpos. Identified circuit and found to be tripped. Reset and tested outlets. All okay. Inspected all gpos to be okay. Signed out. Job complete
MSA-DTWD | WA3955540 | B Block B2126 - RCD has tripped | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 27 Jan 2021 | 2021-02-03 17:00:00 | 2021-01-27 15:30:00 | Pass | Attended site, signed in, completed jsa, located switch board, located circuit, unplugged all appliances, rcd reset , plugged in all appliances and circuit didn’t trip, fm going to keep an eye on it, site happy, *** job completed ***
MSA-DTWD | WA3955574 | C Block Level 1 & 2 - C1117 & Level 2 Kitchen have rats - require rat baits | Joondalup Kendrew Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 27 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-01 10:20:00 | Pass | Rodent baited C Block floors 1 & 2
MSA-MRWA | WA3955368 | Real Time Traffic operations Desk 2.19 Desk inoperable – please investigate/remediate | Road Network Operation Centre (RNOC) | GMP-BR | Furniture | Office Furniture (FU) | SCHIAVELLO SYSTEMS (WA) PTY LTD | 1 | CLOSE | 27 Jan 2021 | 2021-01-28 17:00:00 | 2021-01-27 13:00:00 | Pass | Reset control box
MSA-DCA | WA3955920 | plant room/level 1, water leaking through to level below from chilled water pipe work | Art Gallery of WA - James St-Centenary Gallery-Level One | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 11:48:00 | Pass | Water leak reported by client and job raised. Attended site. The previous day builders had raised sagging pipe work and re supported to rafters causing the piping to move and breaking some seals. Isolated sections and drained water. Carried out repairs. No longer leaking. Tested under pressure and set flow to original positions. Closed job.
MSA-DCA | WA3956070 | High temp in Molecular lab, currently reading 27 degrees. | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Molecular Lab | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-29 16:30:00 | Pass | Attended site. Molecular lab 2 system to not be operating correctly. Applied tests and checks. Investigation found system to have a Refrigerant leak present. Isolated system and pressure tested to 2500kpa. Located leak on TXV join. Soldered and repaired leak. Re pressure tested system to 2500kpa and left system to hold pressure. Rechecked (system to have held pressure). Evacuated system to 500 microns (ok). Charged system with 6kg R410a. Carried out tests and checks. System operating correctly.
MSA-DCA | WA3956153 | Café AC too cold for occupants and site advised boiler not running | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-11 13:00:00 | Fail | Attend site. Investigate boilers and found not to be running. Check for any obvious faults but none present. BAE controls to investigate.
MSA-DCA | WA3956219 | Roller Grille as broken and cannot open gallery space. | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Gallery 2 | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-04-29 12:53:00 | Fail | 28/1/21 - Curtain of grille has jammed and broken many clips.Temporary repair used to get grille in up position. For exhibition!29/4/21 - Attended site for repairs to roller grill. Repaired as required.However we found more issues that were also repaired.Spring tension adjusted and tested in operation by Adrian and all ok!
MSA-DCA | WA3956259 | external Cover bollard hole at Beaufort Street end. Bollard has been stolen. | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Building | Materials (BU) | Image Bollards | 0 | CLOSE | 28 Jan 2021 | 2021-01-28 18:06:59 | 2021-01-28 16:30:00 | Pass | repairs to bollards
MSA-DCA | WA3956298 | Conservation car park Toilet in Conservation car park is running continuously from cistern | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-09 14:30:00 | Fail | Replaced outlet wsdher and flexi
MSA-DCA | WA3956306 | Courtyard Courtyard laneway between main building and admin building is leaking - see notes | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-09 15:03:00 | Fail | Replaced corroded and leaking tap
MSA-DCA | WA3956342 | The auto door on the disabled toilet is not opening automatically. | Maritime Museum Victoria Quay-Main Building-First Floor-Disabled Toilet | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 10:30:00 | Pass | 1003291. Found batteries dead causing Privacy kit to not work, replaced batteries in 2x privacy kits and reset, tested door all ok
MSA-DCA | WA3956345 | public 2 x cubicles in female toilets have the ½ flush option not functioning | Maritime Museum Victoria Quay-Main Building-Ground Floor-Female Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-24 10:30:00 | Fail | Replaced broken buttons, two cubicles need new outlet valves
MSA-DCA | WA3956347 | How water unit in cupboard in toilet area is making loud noises continuously. Please inspect | Maritime Museum Victoria Quay-Main Building | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-24 11:40:00 | Fail | Replaced faulty pump and adjusted pipework
MSA-DCA | WA3956348 | 1 x cubicles in male toilets has the ½ flush option not functioning | Maritime Museum Victoria Quay-Main Building-Ground Floor-Male Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-24 12:00:00 | Fail | Replaced one button, outlet valve broken two new outle valves required
MSA-DCS | WA3955681 | Gate 3 at Zone 6 not able to reset even though it's locked | Wooroloo Prison Farm | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Jan 2021 | 2021-01-28 09:20:17 | 2021-01-28 08:15:00 | Pass | Rectified and fixed the mx fault on metal gate zone. Job completed.
MSA-DCS | WA3955761 | Hotman, B2 - half flush button on toilet not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-22 10:50:00 | Fail | Inspected faulty cistern needs new button and new cistern. replaced full cistern as old parts could not be sources
MSA-DCS | WA3955764 | front gate - sink trap leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 07:31:39 | 2021-01-28 16:38:00 | Pass | Replaced waste and trap to kitchen sink
MSA-DCS | WA3955769 | Unit office - aircon exhaust button will not reset on main panel | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 07:39:33 | 2021-03-29 16:30:00 | Fail | New motor installed new indicator lights installed bearings checked and greased, all speeds tested and checked all ok
MSA-DCS | WA3955771 | Unit 5, A wing - 2 showers not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-11 08:30:00 | Fail | Nill
MSA-DCS | WA3955772 | Unit 1, A3 - toilet flush faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 07:45:00 | 2021-02-11 16:30:00 | Fail | Nill
MSA-DCS | WA3955800 | unit 10, A wing - leak from roof, burst pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 08:07:35 | 2021-01-28 15:53:00 | Pass | Replaced burst section of pipe, job delayed due to having to wait for escort, and unit being understaffed, tested new section no leak.
MSA-DCS | WA3955809 | Internal zone 10 microwave - constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 08:14:22 | 2021-01-28 15:30:00 | Pass | Cleared away rubbish. Checked input voltage to Receiver and Transmitter and checked alignment. Monitored throughout the day. Tested ok.
MSA-DCS | WA3955842 | Sally port door & gate control door is not operational intermittently working | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Jan 2021 | 2021-01-28 12:36:05 | 2021-01-28 13:00:00 | Fail | Rubber stripping looking recently applied causing door to be misaligned and interlocking triggering. Removed retested ok staff advised.
MSA-DCS | WA3955858 | Demountable - main light switch, sticking hard to turn on/off | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 08:50:16 | 2021-01-28 11:45:00 | Pass | Replaced faulty light switch demountable
MSA-DCS | WA3955889 | Canteen - power keeps tripping out fridges | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 28 Jan 2021 | 2021-01-28 13:11:56 | 2021-01-28 11:30:00 | Pass | Reset power, noted that circuit is very overloaded and not protected by an RCD, site to make decision on rectifying.
MSA-DCS | WA3955913 | cleaning office sewing room air con is cutting out and coming up with error service 2 | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-16 11:50:00 | Fail | COMPLETED
MSA-DCS | WA3955933 | SHU (9) - Control Room Computer screen and main Doors of the SHU do not have power. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-03-31 15:30:00 | Fail | work order to be invoiced at cost to date.
MSA-DCS | WA3955938 | Unit 16 - C13 loose tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-10 13:30:00 | Fail | Nill
MSA-DCS | WA3955940 | Unit 2 - B Wing Tap spout in B Wing Cleaning Room has broken off.-see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-15 15:30:00 | Fail | Tap was repair able, but prisoners and yanking the tap when hose is connected and causing the tap to come apart,
MSA-DCS | WA3955945 | Kaartdijin Mia Require 2 x locks turned around so as locks can be unlocked from outside not inside. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-01-28 11:00:00 | Pass | Swap handles locking direction on two doors to allow correct operation
MSA-DCS | WA3955948 | Skills kitchen repair / Replace hot water system | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-01-29 15:30:00 | Pass | COMPLETED
MSA-DCS | WA3955980 | Unit 6 - D7 Top Bunk reading light faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-01-29 10:00:00 | Pass | Investigate and repair unit 6 cell d7 bed light
MSA-DCS | WA3956049 | Administration - Toilet Urinal Blocked, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-08 10:30:00 | Fail | Nill
MSA-DCS | WA3956053 | SB1 (Between U15-U16) - screws falling out of gate hinges - see notes | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-05 10:30:00 | Fail | 05/02/21Inspect hinges, remove, realign and fix screws
MSA-DCS | WA3956079 | Supply and install Jacques System to Albany RP Visits | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-01 14:12:00 | Pass | Travel costs related to WA3794642 Supply and install Jacques System to Albany RP Visits - unable to share with other works due to this fault requiring urgent attendance.No further works required
MSA-DCS | WA3956083 | visits are air con is not cooling down | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-17 12:51:53 | Fail | Arrived on site and signed in tools,checked over evap,founf fan and pumps working,all dampers opened up,unit running as designed.
MSA-DCS | WA3956089 | unit 1 - D7 Toilet running constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-10 15:30:00 | Fail | Nill
MSA-DCS | WA3956140 | Loose flyscreens to main hall windows | Nyandi Training Academy | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-10 10:30:00 | Fail | FLYSCREENS RE SECURED
MSA-DCS | WA3956193 | Staffroom Ladies sink leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-16 08:05:00 | Fail | Let hot water run for 15mins no leaks found
MSA-DCS | WA3956204 | L1 male toilet blocked | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 13:21:05 | 2021-01-28 16:15:00 | Pass | Arrived on site and inspected found the level 1 male toilet blocked. Plunged multiple times to clear the blockage. Tested multiple times all working in order.
MSA-DCS | WA3956231 | Market Gardens, Day Room - water filter light flashing (brand: billi model number: 994001) | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-15 09:45:00 | Fail | Removed unit to workshop for repairsReplaced filter plv and level sensor assemblyrepaired Billi System replaced filter PLV Level Sensor Kit and Wiring Loom Kit A40191363G
MSA-DCS | WA3956233 | Unit 6 - shower pressure low | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-08 11:30:00 | Fail | Nill
MSA-DCS | WA3956266 | Lenard C wing day room - broken window Approx. 1200 x 450mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-03-03 11:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3956269 | Yeeda C wing day room - broken window Approx. 600mm x 600mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-03-03 10:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3956366 | Various Ants and Cockroaches throughout - see notes | Rockingham Justice Complex | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-10 17:45:00 | Fail | Ants and Cockroaches treatment - Internal & External
MSA-DFES | WA3956012 | change room engine bay, no HW | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-10 15:30:00 | Fail | Rheem service attended repaired faults all tested all ok
MSA-DFES | WA3956040 | ground various areas - lights faulty - see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-09 12:00:00 | Fail | Complete
MSA-DFES | WA3956077 | Ground floor outside fire booster door uneven pavers - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 09:00:00 | Pass | Remove section of pavers and relay. Pavers were cut on a strange angle hence why they were all uneven.
MSA-DFES | WA3956275 | Engine bay doors are all noisy and neighbours complaining | CFRS Vincent | GMP-BR | Building | Doors (BU) | Anvil Doors | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-01 12:00:00 | Pass | Attended Vincent Fire Station to attend to engine Bay doors due to the excessive noise during operation (reported by the fire stations neighbors). All doors were readjusted and re- lubricated and now operate quietly. -- Note there is no permanent fix to this issue besides attend and lubricating the engine bay doors more frequently between services.Thank you
MSA-DFES | WA3956351 | CH-2 Chiller Fault is from a possible power spike. | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-23 11:30:00 | Fail | Attend site with Trane chiller tech. Access roof plant and connect laptop to chiller. Download fault history and confirm chiller resent faults due to voltage drop during operation. Found voltage to drop to from 415 to 360, causing line voltage and compressor fail to start faults. Download all faults history from unit 1 compressor 1 and 2. Unit 2 compressor 1 and 2. Chillers are currently operating as normal.
MSA-DTAG | WA3956146 | Basement, Custody Cell 3 - Water fountain in cell 3 is not working. pls attend at 7am | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-01 08:45:00 | Pass | Adjusted and cleaned flow restricor
MSA-DTAG | WA3956152 | 1903 Lift No3 not working | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 15:30:00 | Pass | Had to reset 2 lifts and change some wiring on the hydronic lift 4. All issues caused from previous electrical works to building
MSA-DTAG | WA3956160 | L14 kitchen The tap mixer/purified hot & cold water is broken - see notes | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-01 13:44:00 | Pass | Water leak causing tap not to operate. Replaced dual and inlet solenoids. Dispenser lens cracked but operating okay. Advised not to replace yet until an issue.A402021446 Billi Quadra Compact
MSA-DTAG | WA3956162 | Female Change rooms (behind bike storage area) wall fan not working | Central Law Courts-Main Building-Basement | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-04 08:30:00 | Pass | Job complete
MSA-DTAG | WA3956183 | basement, Custody interview room - window has been shattered | Perth Children's Court | GMP-BR-HO | Glazing | Window Glass (GL) | O'Brien Glass With Care | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-15 13:45:00 | Fail | Supply and install vision window clear anodized coloured
MSA-DTAG | WA3956294 | 1903 roof Cooling tower fan not functioning correctly | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-01-30 14:00:00 | Pass | Attend site 1907 building. Access roof condenser water loop cooling towers. Found cooling tower 1 fan blades to have broken off hub. Found cooling tower 2 water distributor not turning. Found tower water temp to be too high. Isolate tower 1 fan motor. Unbolt motor mounts and flip entire motor. Unbolt fan hub from shaft. Secure motor into position untill replacement blade is sourced. Access cooling tower 2 isolate fan motor. Access water distributors and remove top nuts and grub screw. Lubricate and grease shaft to free up movement. Test operation with 3 water pumps running and found to turn. Test operation with 2 pumps running and found to turn. Test operation with one pump running, found water pressure not enough to turn but not as much cooling required. Tower is working satisfactory. Follow up with DAS once new fan is located. Access plantroom 1987 building, found water on plantroom floor. Found cooling tower to overflow when turned off. Carry out check by setting of valves. Found to
MSA-DTWD | WA3955755 | H2 Student support office - Main entry door lock faulty | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 28 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 09:25:00 | Pass | job completed - unjammed locked
MSA-DTWD | WA3955882 | E block E200 ground floor - Tap dripping in wash trough (stripped spindle) | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-11 12:24:00 | Fail | Replaced leaking tap
MSA-DTWD | WA3955885 | S block Science building chiller keeps tripping out | Murdoch Campus | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-29 14:00:00 | Pass | Attended site and carried out diagnostics on chiller and reset compressor A and report has been sent to the campus to replace chiller
MSA-DTWD | WA3955929 | E block ground Restaurant Kitchen dishwasher waste pipe leaking | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 10:30:00 | Pass | Arrived on site and inspected found the plug and waste rubber faulty. Collected parts and returned to the site. Replace with new rubber and refitted the trap. Tested multiple times all working in order.
MSA-DTWD | WA3955951 | I Block - Hot water tap is playing up again. No pressure or hot water in kitchen sink. | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-19 15:00:00 | Fail | Replaced anode
MSA-DTWD | WA3956030 | U block Damaged section of the wall outside the Glazing roller door | Balga Campus | GMP-BR | Building | External Walls (BU) | AWB Co. | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-02-11 16:00:00 | Fail | Attend site to investigate broken wall. Source Bricks andrebuild wall
MSA-DTWD | WA3956058 | Canteen - Remove broken freezer compressor | Rockingham Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-03 16:00:00 | Fail | Gathered required information off Dennis. Picked up reclaim bottle returned to site. Reclaimed refrigerant. Removed condenser unit from under kitchen cabinet. Disposed of and cleaned up work area completed paperwork and signed out
MSA-DTWD | WA3956118 | male staff toilets A012 - urinal not flushing | Naval Base | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-09 09:13:00 | Fail | Urinal cistern not flushing. Removed stainless cover then tested button. Got nothing. Removed the hose and internals cleaned them out lubricated air flushers, tested them and then re installed and tested in cistern with flush. Everything is working
MSA-DTWD | WA3956120 | B block BG6 Spray Booth No:2 actuators seem to be working fine, flaps open - see notes | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-15 10:00:00 | Fail | Works complete
MSA-DTWD | WA3956126 | E Block, Kitchen E74 - insulation coming threw the aircon vents | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-03-04 04:30:00 | Fail | SUB CONTRACTOR HAS ATTENDED SITE AND CARRIED OUT DUCT WORK REPAIRS AS QUOTED JOB IS COMPLETE
MSA-DTWD | WA3956179 | B block, B018 - Check faulty door lock/key to B018 and check 4 x faulty paddlocks | Balga Campus | GMP-BR | Building | Doors (BU) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 14:45:00 | Pass | job completed - replaced 4 gate padlocks, 3 school padlocks and 4 damaged locks
MSA-DTWD | WA3956188 | Room B16, B Block Electrical - Roof mounted Email A/C not operating | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-03 13:30:00 | Fail | Arrived on site signed in. Checked in with Dennis. Assisted by Dave with working at height. Tested system found unit short on refrigerant. Checked for found service valve with slight leak possibley due to over condensing on hot days tightened Schrader valve retested all ok. Regased system using van stock R22. Tested system all ok 750gms R22 used. cleaned up work site. Completed paperwork.
MSA-DTWD | WA3956192 | S block - spider infestation Redbacks | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-08 09:00:00 | Fail | Indoor spider control
MSA-DTWD | WA3956200 | F Block, FT15 - Compressor filters fault. Constantly running | Carlisle Campus | GMP-BR | Equipment | Compressors, Generators (EQ) | CLEVELAND COMPRESSED AIR SERVICES | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 17:30:00 | Pass | Complete
MSA-DTWD | WA3956245 | B block, hot water running threw toilet system | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 28 Jan 2021 | 2021-01-29 17:00:00 | 2021-01-28 18:00:00 | Pass | located open breach, replaced spouts
MSA-DTWD | WA3956276 | E-Block, G block - Kendrew-E-Block Restaurant kitchen ceiling light not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-02 12:30:00 | Pass | Replace various damaged lights, globes, drivers, starters within kitchen - E block
MSA-DTWD | WA3956336 | L block lift Only working intermittently - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 16:55:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3956350 | B Block, Tech workshop Workshop rear entry door lock faulty | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 28 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 11:45:00 | Pass | repairs to lock
MSA-DTWD | WA3956356 | M&V Blocks Repair uneven concrete path between M&V Blocks | Balga Campus | GMP-BR | Paving & Roadworks | Asphalt (PR) | AWB Co. | 3 | CLOSE | 28 Jan 2021 | 2021-02-04 17:00:00 | 2021-04-22 12:27:00 | Fail | To remove concrete path and prep for new concrete path To pour concrete path allowing time to put a finish on path Materials been removed and concrete will need to be barrowed into job site.Includes rubble and Debris removal from site
MSA-MRWA | WA3955645 | Server Room High Temp Alarm | Don Aitken Centre MRWA Head Office-Main Building-Basement-IT Server Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 28 Jan 2021 | 2021-01-28 04:55:05 | 2021-01-28 03:15:00 | Pass | Attended callout. Found crac unit 1 in hp fault. Muted alarms, checked over unit and reset hp. Tested operation of unit. Temps started coming down. Pressures and temps on pump station 1 were not nominal. Switched crac units over as a precaution. Pump station 1 requires further investigation. Watched temps stabilise. Filled in paperwork, signed off. Left site.
MSA-MRWA | WA3955904 | CRAC unit, pump 2 failure and automictic transfer | Don Aitken Centre MRWA Head Office-Main Building-Basement-IT Server Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 28 Jan 2021 | 2021-01-28 13:23:06 | 2021-01-28 15:30:00 | Fail | works completed
MSA-DCA | WA3956713 | Mixer tap has only hot water coming out - see notes | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-First Aid Room and Toilet | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-09 10:29:00 | Fail | Checked cold water temp to basin it’s 26,7degs .No issues found.
MSA-DCA | WA3956814 | sewer pump alarm | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1 | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Ballantyne Plumbing Gas & Electrical | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 15:15:00 | Pass | Found dirty probe.
MSA-DCA | WA3957100 | Lift front of house is stopping intermittently between floors | His Majesty's Theatre-Theatre Building-Ground Floor-Front of House Management | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 14:15:00 | Pass | Found key switches in car for all floors turned off.
MSA-DCS | WA3956483 | Control room lock for unit 1 faulty | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Jan 2021 | 2021-01-29 10:34:45 | 2021-01-29 12:30:00 | Fail | Replaced defective custodial lock, job completed.
MSA-DCS | WA3956564 | Unit 9, A6 - mirror cracked | Hakea Prison | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 2 | CLOSE | 29 Jan 2021 | 2021-02-02 17:00:00 | 2021-03-19 13:00:00 | Fail | NEW MIRROR FITTED
MSA-DCS | WA3956565 | Unit 10, A1 - Viewing hatch glass cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 07:53:48 | 2021-01-29 15:45:00 | Pass | replaced broken obs panel
MSA-DCS | WA3956572 | Zone control 2, kitchen - Hot Bain Marie thermostat faulty | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jan 2021 | 2021-02-02 17:00:00 | 2021-02-11 11:30:00 | Fail | Repaired Bain Marie
MSA-DCS | WA3956573 | Unit 6, B wing - laundry door lock cannot be unlocked | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jan 2021 | 2021-02-02 17:00:00 | 2021-01-29 12:45:00 | Pass | Open lock with Locksmith key bunch, Dismantle lock to check for fault - No FaultCheck Officers key bunches - Keys are worn
MSA-DCS | WA3956579 | Unit 3, C wing, Cleaning Cupboard - Leaking fire hydrant | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 29 Jan 2021 | 2021-01-29 12:01:36 | 2021-02-02 11:36:00 | Fail | Technician Note29/1/21BR & CW•investigated leak in unit 3•organised security to take photos of pipework and got pipe measurements.•security emailed photos and measurements to Carl for quoting.-Picked up parts from fire main- drain down system-remove all rusted pipe work and trim- install all new pipe work and trim-fill system up for block 3- check all work-paint new pipe work- Re-Instate system
MSA-DCS | WA3956589 | Boiler house, workshop - Steam leak on mine line above boiler number 2 (EWP required) | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-12 12:30:00 | Fail | Remove the insulation around pipework, found pinhole leak coming from elbow.Depressurised boilers, cut into pipework and replaced section of pipework horizontal and vertical with new elbow and b-press together.Started boilers and test - no leaks. Install new lagging.
MSA-DCS | WA3956598 | Unit 13, D12 - Shower tap in cell is constantly leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-12 12:30:00 | Fail | Nill
MSA-DCS | WA3956609 | Unit 3, C wing -Leaking water pipe and drain is blocked in C wing cleaning closet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 08:20:55 | 2021-02-18 15:30:00 | Fail | Nill
MSA-DCS | WA3956610 | Albany Prison Razorwire support wire damaged | Albany Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-01-29 18:30:00 | Pass | 11/01/21 - 20/01/21Replaced top roll support cable as discussed
MSA-DCS | WA3956635 | Market Gardens - retic pump for orchid is not operating | Wooroloo Prison Farm | WSM-MW-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 08:35:41 | 2021-02-01 10:15:00 | Fail | Market gardens retic pump for orchid not operating. Check pump & controls. Repair leak in indicator valve. Prime pump & run. Return & check, prime. Return, check sprinkler lines. Repair, plug blower. Report to staff.
MSA-DCS | WA3956644 | Unit 2A Washing machine - not working | Wooroloo Prison Farm | WSM-MW-SITE | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-25 10:00:00 | Fail | Washing machine faulty in 2B. Check both machines & controls. All working correctly at time of attendance.
MSA-DCS | WA3956812 | Unit 2,Cell D52 - light faulty wont stay on switch faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-10 08:30:00 | Fail | Investigate and repair unit 2 cell D52 light
MSA-DCS | WA3956833 | Unit 2, top landing shower - No hot water/faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-09 09:45:00 | Fail | Relit hwu
MSA-DCS | WA3956858 | Unit 14 Fire Alarm - faulting constantly (up to 6 times an hour) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 10:45:57 | 2021-01-29 15:45:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3956892 | Print Shop - Lunch Room Broken tap leaking in Print Shop Lunchroom sink. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-18 13:49:00 | Fail | Nill
MSA-DCS | WA3956912 | Unit 16 - B2 shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-10 14:30:00 | Fail | Nill
MSA-DCS | WA3956920 | Gate House - Perimeter Fence Response Road Gate Failed | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Jan 2021 | 2021-01-29 15:16:22 | 2021-01-29 14:00:00 | Pass | Attended and check EBI function , working ok but motor not working advised site maintenance to request different contractor who handles the motor/mechanical vehicle gates.
MSA-DCS | WA3956921 | Official Visits - entry door latch not release once commanded from officers desk (see notes) | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 11:13:14 | 2021-01-29 15:00:00 | Pass | Attended and check the issue, custodial lock for official visits door not locking . Advised site maintenance that the systems control the door still under honeywell.
MSA-DCS | WA3956936 | unit 10 C8 Water dripping from Cell Call | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 11:20:51 | 2021-02-03 09:05:00 | Fail | Rectified and fixed the cell call point. Test function ok and back to normal operation.
MSA-DCS | WA3956983 | Unit 14 - D2 Drains blocked in cell D2 and the cell is omitting a strong stench. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-17 13:09:00 | Fail | Nill
MSA-DCS | WA3957039 | Main Admin, ladies toilet - toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 11:55:04 | 2021-01-29 14:22:00 | Pass | Cleared blocked toilet
MSA-DCS | WA3957054 | Unit 7 A wing stove not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-16 09:10:00 | Fail | Returned 16/02 and fit parts and tested ok.
MSA-DCS | WA3957110 | Unit 6 Timber decking split & broken and dangerous | Bandyup Prison | GMP-BR- HO | Flooring | Timber (FL) | Midolo Building Services | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-04-16 12:54:00 | Fail | INSPECTION LABOUR ONLY - Invoicing cost to date, BRAF emailed 31/3/21 $33100.00 + GST if approved a LVM job will be raised.
MSA-DCS | WA3957113 | Unit 5 Timber decking split & broken and dangerous | Bandyup Prison | GMP-BR- HO | Flooring | Timber (FL) | Midolo Building Services | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-04-16 12:48:00 | Fail | INSPECTION LABOUR ONLY - Invoicing cost to date, BRAF emailed 24/3/21 $30100.00 + GST if approved a LVM job will be raised.
MSA-DCS | WA3957162 | unit 4 dayroom north lock is spinning | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 12:49:18 | 2021-01-29 16:35:00 | Pass | Attend site, gain entry to faulty door unit 4 day room. Replaced internal components to external handle for correct operation.Date on site: 29/01/2021Time on site: 3:35pm - 4:35pm
MSA-DCS | WA3957213 | One of the CCTV cameras has been offline since Sunday | Walcott Centre (Central West Metro ) | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 13:42:23 | 2021-01-29 16:30:00 | Pass | Found camera offline and couldn't connect to network. Rebooted camera and restored. Checked all camera times andfound multiple camera times not matching up. Re synced all camera times and checked time match all good.
MSA-DCS | WA3957240 | Gate house - Response Gate Failed, SEME have attended and stated that it is a mechanical issue | Casuarina Prison | SPA-BR | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 29 Jan 2021 | 2021-01-29 18:11:29 | 2021-02-18 14:45:00 | Fail | 29/01/2021Locking pin not functioning. Spoke to Mario Kovac and arranging to replace controller.12/02/2021Replace Gate Controller. Issue found with Limit Switch on locking pin.15/02/2021Locking pin actuator drawing too much power. Remove for diagnostic and possible replacement. Replace Limit switch by combining 2 products to make suitable replacement.18/02/2021Replace Locking Pin Actuator. Install second power supply to suit new actuator.
MSA-DCS | WA3957253 | market garden - broken 100mm mainline to be connected to perpendicular 100mm mainline.-see notes | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-25 14:30:00 | Fail | cracked pipe in 100 ml main line
MSA-DCS | WA3957256 | Unit 1, door buzzer to loud - door buzzer was replaced today and is too loud | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 14:28:37 | 2021-01-29 15:30:00 | Pass | New custodial lock has built in piezo sounder and no volume control, rectified to lessen the sound.
MSA-DCS | WA3957259 | Main Door & door to medical centre not opening and closing correctly-see notes | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-01-30 14:34:54 | 2021-01-29 17:30:00 | Pass | Locks working ok electronically. Issue is mechanical in nature. Job needs to be referred to a locksmith.
MSA-DCS | WA3957332 | Unit 2 A-B Dayroom by the water cooler Repair Damaged Grey Rubber Flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Rubber (FL) | Midolo Building Services | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-03-08 08:00:00 | Fail | DAMAGED SECTION OF RUBBER FLOORING REMOVED & REPLACED WITH NEW
MSA-DCS | WA3957369 | Front Entrance disabled toilet by health entrance leaks heavily at the back of basin when flushed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-18 14:30:00 | Fail | Nill
MSA-DCS | WA3957401 | equipment room gate house, air con fault | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 29 Jan 2021 | 2021-01-29 20:55:01 | 2021-03-29 15:30:00 | Fail | Temporary unit removed
MSA-DCS | WA3957412 | Cell Call System is alarming - Cannot reset. | Broome Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Jan 2021 | 2021-01-30 03:57:16 | 2021-04-23 13:00:00 | Fail | Spoke with the site regarding the issueSite SO advised the issue has not occurred since the phone support was providedNo further issue to reportJob can now be closed
MSA-DFES | WA3956540 | Engine room - receiver failed for rear engine room doors | CFRS Joondalup | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 29 Jan 2021 | 2021-01-29 17:00:00 | 2021-02-22 08:00:00 | Fail | Attended Joondalup Fire Station. Found that receiver has burnt out to rear engine room doors so the remote for these rear doors cannot be used. Rear doors are now only operable by push button until the transmitter is replaced. Please see attached service reports and Photos. BRAF to carry out the repair works is attached.Thank youWorks As per approved BRAF have been completed on 22.2.21-- Please see attached updated Signature slip and service report for the attendance to carry out works as per the approved BRAF
MSA-DFES | WA3957158 | Pest control issue- Rodent droppings in Reception & spiders & cockroaches in engine bay change rooms | FESA RHQ - Forrestfield | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-01-30 09:30:00 | Pass | Carried out a service for rodents, cockroaches and spiders to DFES academy. Rodent droppings were sighted within a store room in admin, added 2x baited rodent stations here, both with 2 types of rodenticide to encourage quick feeding. Treated all change rooms and the circuit room for spiders and cockroaches via ULV misting. No re-entry to treated zones for at least 4 hours, when re-entering, please be aware of any falling spiders. Do not brush off webbing for at least 2 weeks. Please allow up to 1Week for rats to enter new stations as they are neophobic. Misting to internal areas would be ideal after hours every 6 months to control internal activity.
MSA-DFES | WA3957244 | Change rooms - There are tiles broken or cracked in various changerooms (see long description) | FESA RHQ - Forrestfield | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-06-29 07:00:00 | Fail | Supply and install replacement tiles as required throughout changerooms 1-5.Clean soap scale and dirt from tiles and apply penetrating sealer
MSA-DTAG | WA3956834 | Paccom unison system keeps logging people out unable to process access cards | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 11:30:00 | Pass | Adjusted cabling on level 10 control room and restarted client workstation
MSA-DTAG | WA3956851 | Basement FIP - Technician required to attend at 07.00am Saturday 30 January (see notes) | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-01-30 12:00:00 | Pass | After hours callouts to isolate detection zones 8to11 in basement for works.Deisolated at 1130am
MSA-DTAG | WA3956945 | Ground - Public female toilet is blocked. | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-01 09:15:00 | Pass | Arrived on site and cleared the blockage and tested multiple times all working in order.
MSA-DTAG | WA3957165 | ground court room 3 public entry door can still be pulled open after lock has been engaged. | Armadale Courthouse | GMP-BR-HO | Building | Automatic Doors (BU) | Bullant Security Pty Ltd | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 14:15:00 | Pass | Attend site, service lock and tighten screws for correct operation.Date on site: 29/01/2021Time on site: 2:15pm - 2:45pm
MSA-DTAG | WA3957376 | Air lock between custody & court room 1 Light bulb faulty | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-03 08:00:00 | Pass | Attended site and signed in. Got taken to area by security. Found light out in air duct. Replaced tubes and starters and didn’t work on one side. Replaced faulty ballast. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3956631 | Admin area - safe unable to open - PLEASE call site before attending | Naval Base | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 2 | CLOSE | 29 Jan 2021 | 2021-02-02 17:00:00 | 2021-06-03 10:28:00 | Fail | Job completed on the 25th Februayr 2021 at 10:28am.
MSA-DTWD | WA3956655 | block 1, ground, male toilets - Urinal cistern has stuck button | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-10 15:30:00 | Fail | replaced inlet valve and adjusted button
MSA-DTWD | WA3956662 | Block 7, female toilet - Disabled toilet cistern constantly running | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-10 17:33:00 | Fail | replaced button assembly and slave bellows bridge assembly
MSA-DTWD | WA3956689 | k block, K05 Walk in Freezer - walk in Freezer in the canteen has stopped working | Midland Campus | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-29 12:30:00 | Pass | Travelled to site, signed in upon inspection and testing of electrics found spade connector from junction box connections to compressor loose, repaired ok.Checked HRC fuses and power to unit all ok. Found settings on analog defrost timer wrong, adjusted, also found internal cooling switch turned off in freezer room. Ran system checked gas pressures and temps, freezer was down to -12c upon leaving.
MSA-DTWD | WA3956747 | various lights are not working - foyer, room AT208 & AT229 (see notes) | Kwinana Automotive Centre | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-08 10:30:00 | Fail | Attended site and signed in when staff arrived on site and allowed us in. Located rooms with lights out. Repaired tubes and ballasts as required. Checked out lights on foyer. Found 5 x wall lights out. Replaced lamps and ignitors as Required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3956781 | V Block Staff room ant infestation | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-08 09:30:00 | Fail | Indoor ant control
MSA-DTWD | WA3956801 | Block 3 ground male toilets Water leaking from toilet bowl | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-09 14:00:00 | Fail | inspect all toilets, no problems found campus will monitor
MSA-DTWD | WA3956869 | B Block extraction fans not working | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-09 08:44:00 | Fail | SUB CONTRACTOR HAS ATTENDED SITE AND CARRIED OUT QUOTED WORKS AS PER BRAF - JOB IS COMPLETED
MSA-DTWD | WA3956876 | Room F53 swipe card reader not working | Rockingham Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-11 13:45:00 | Fail | Room F53 IT door strike not working. Replaced strike on door, all ok now
MSA-DTWD | WA3956940 | E Block - Walk in freezer door seal needs repair, ice forming inside door | Bentley Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-05 09:00:00 | Pass | COMPLETED
MSA-DTWD | WA3956951 | ground workshops has a faulty security alarm panel need to be replaced | Clarkson Campus | GMP-BR | Security | Security Management System (SE) | BJ SYSTEMS | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-04 16:45:00 | Fail | Dang Nguyen & Dion Maher (03/02/2021) - Work NoteAttend site to repair faulty RAT, replace RAT, all ok. Found issue with old controller, request to replace. Checked with IT, issue to get online. Return requiredDang Nguyen & Dion Maher (04/02/2021) - Work NoteUpgrade 3000 Controller to 6000, tested all ok
MSA-DTWD | WA3956976 | L2 west tower block white board fallen down broken bracket | West One Services | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 29 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-09 10:00:00 | Fail | Re-fitted white boards and cut out mouldy carpet and replaced
MSA-DTWD | WA3957226 | Horticulture nursey - there is a tap which has copper piping leaking in nursery (see notes) | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-08 10:30:00 | Fail | Water leaks at nursery. Leak in ground was loose compression fitting, clean out around the fitting and tightened fitting up. Leak and no water to tap at nursery. Locate and isolate water to h block. Perfor tap service. Washer stuck in tap not allowing water through. Water leaking from spindal. Removed and replace washer and internal 0 ring. Lubricate and test.
MSA-DTWD | WA3957297 | House 1 kitchen Faulty dishwasher leaking water | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Lane's Plumbing | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-01 15:00:00 | Pass | Repairs to dishwasher
MSA-DTWD | WA3957331 | A-Block 2nd floor mens urinal West End continuously running, isolated in duct | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-01 12:15:00 | Pass | Arrived on site and inspected found the the outlet washer and bellows faulty. Collected parts from supplier and returned to site. Replaced faulty parts with new. Tested multiple times all working in order.
MSA-DTWD | WA3957352 | K block Flickering light at AMEP Balga reception. High ladder required | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-12 12:28:00 | Fail | Repalced faulty fluro and controls gear.job complete
MSA-DTWD | WA3957363 | U Block - U015 Repair door frame & door closer, door doesn't close properly | Balga Campus | GMP-BR | Building | Doors (BU) | M Construction (WA) | 2 | COMPFIN | 29 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-03 08:52:00 | Pass | BRAF was declined, job has been closed without charge.
MSA-MRWA | WA3957045 | Blocked Cubicle please remediate | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor-A5.01-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Jan 2021 | 2021-02-01 17:00:00 | 2021-02-08 12:55:00 | Fail | Tested all urinals in level 5 no blockage found.
MSA-DCS | WA3957417 | Vehicle gate alarm is not deactivate in , it is constamtly alarming | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jan 2021 | 2021-01-31 06:11:59 | 2021-02-01 10:00:00 | Fail | Replaced Heavy Duty reed switch on magnet on front gate. Tested and working as per normal
MSA-DCS | WA3957418 | Perimeter light 27A 26, 28 and 30 both And B not working not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 30 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-15 10:00:00 | Fail | Replaced light fitting on perimeter light pole 27A
MSA-DCS | WA3957432 | In CCU camera 14 not working, screen is blank | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Jan 2021 | 2021-01-30 12:19:10 | 2021-02-04 16:14:00 | Fail | Damage camera replaced with new. Job Completed through WA3878472.
MSA-DCS | WA3957471 | Albany Regional Prison - Gate Control Room - Cell call log not working. | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jan 2021 | 2021-02-05 17:00:00 | 2021-05-07 10:30:00 | Fail | Found VM software frozen. Reset and reconfigured log program tested all ok changed some settings so make system more stable
MSA-DTAG | WA3957426 | Zone area 2 not alarming-to be attended on Monday | Mandurah Courthouse-Main Building | GMP-BR-HO | Building | Materials (BU) | SONTEC WA PTY LTD | 3 | CLOSE | 30 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-01 09:45:00 | Pass | 1/2/21 - Ryan VestyProgrammed RAS to arm/Disarm all areas as required.Tested all ok.
MSA-DCS | WA3957488 | 7 -Dwing 3 -Shower tap is not working | Casuarina Prison-Self Care Unit 7C and 7D | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-18 08:30:00 | Fail | Nill
MSA-DCS | WA3957489 | 4 B wing -Tap broken in Cleaning room | Casuarina Prison-Prisoner Accommodation Unit 4 | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-12 09:30:00 | Fail | Nill
MSA-DCS | WA3957490 | 14 B wing Cell 10 -Tap leaking sink | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Jan 2021 | 2021-02-05 17:00:00 | 2021-02-12 12:30:00 | Fail | Nill
MSA-DCS | WA3957491 | 2 B wing Cell 3 -Toilet not flushing properly | Casuarina Prison-Prisoner Accommodation Unit 2 | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-10 13:17:00 | Fail | Job was raised incorrectly as we already had a job for unit 2 B3, this one was in cell D3 unit 2
MSA-DCS | WA3957492 | Crypt -Kitchen Spout leaking | Casuarina Prison-Gatehouse | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-12 15:30:00 | Fail | Nill
MSA-DCS | WA3957498 | Camera no.135 - no picture | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Jan 2021 | 2021-02-01 08:34:39 | 2021-01-31 10:30:00 | Pass | Camera back online,test all functions ok and back to normal operations. Job completed.
MSA-DCS | WA3957500 | In the control room-the graphics on display scree for different areas are not appearing. | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Jan 2021 | 2021-02-01 08:35:11 | 2021-01-31 11:00:00 | Pass | EBI WS lost of graphics, power cycle and turn the system back online. Job completed.
MSA-DCS | WA3957517 | UNIT 6- Cell call system in Cell C1 is not functioning. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jan 2021 | 2021-01-31 15:14:05 | 2021-01-31 14:00:00 | Pass | Rectified and fixed the cell call C01, job completed.
MSA-DCS | WA3957526 | Main Kitchen broken power point | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-19 12:00:00 | Fail | Investigate kitchen gpo’s.Source parts and replace gpo’s.
MSA-DCS | WA3957527 | Gate house in the crypt ,power point broken in kitchen | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-16 15:00:00 | Fail | Investigated and found crypt kitchen power overloaded. Split circuits and tested
MSA-DCS | WA3957528 | Unit 1 , B Wing inspection light in cell B8 not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-15 10:00:00 | Fail | Repaired faulty lights in unit 1 b8
MSA-DCS | WA3957529 | Unit 14 B wing bunk light not working in B12 | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-19 10:00:00 | Fail | Replaced damaged switch in b12. Removed damaged bed light. Retrofit new stainless shroud at workshop. Returned and reinstalled new bed light
MSA-DCS | WA3957530 | Unit 13 B and D wing outside light switch not working in B8 And D1 | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-17 15:00:00 | Fail | Repaired and replaced faulty lights and damaged switches in unit 13. Cells b8, d12, d1
MSA-DCS | WA3957546 | Zone A5 security check not activated not showing alarm | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jan 2021 | 2021-01-31 18:43:30 | 2021-01-31 17:00:00 | Pass | Check gallagher systems ok and normal , conduct walktest for zone A5 electric fence and activation is confirmed GH control room. Job completed
MSA-DFES | WA3957514 | Technicial Work shop -Fire Panel Fault -System 1 | Fleet Management Services - O'Connor Workshop-Main Building | GMP-BR | Building | Materials (BU) | Critical Fire Protection & Training | 1 | CLOSE | 31 Jan 2021 | 2021-02-01 17:00:00 | 2021-01-31 11:45:00 | Pass | Attended site to investigate FIP fault. Site was not manned at this time. Western Power doing works on the street.
MSA-DFES | WA3957547 | Cockburn Emergency Services Centre-Parking area - sliding gate is not opening automatically. | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Building | Steel Fencing & Gates (BU) | Go Doors | 2 | CLOSE | 31 Jan 2021 | 2021-02-03 17:00:00 | 2021-02-01 12:00:00 | Pass | COMPLETED
MSA-DCA | WA3961036 | Zone 10 & 14 leaking water | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Plumbing & Drainage | Drainage (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-02 09:30:00 | Pass | job completed - replaced 1 vandalised sprinkler zone 10- replaced 3 vandalised sprinklers zone 14
MSA-DCA | WA3961140 | leaking pipe in level 1 | Art Gallery of WA - James St | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-02 09:00:00 | Pass | Leaking water pipe is the Heating Water piping near L1 Plant Room entrance. Water leak was directly related to the low temperature callout from 01-02-2021.No further leaks.
MSA-DCA | WA3961141 | building management system fault | Art Gallery of WA - James St | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-02 10:24:00 | Pass | No issues found regarding BMS operation that we weren't already aware of and monitoring.
MSA-DCA | WA3961190 | Low temperatures throughout Centenary Building - all floors | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 01 Feb 2021 | 2021-02-02 01:53:40 | 2021-02-02 01:30:00 | Pass | After Hours Callout. Attended site. Common HW temperature low, 17°c. Heating Call on but ETS valves not open. Carried out reset on BMS. Monitored. ETS valves opened. HW temperature rise slowly as demand reduced to 72°c. No further High Priority Alarms active that are not already noted and disregarded.
MSA-DCS | WA3960430 | EBI Board door controller not working - user cannot login | Banksia Hill Detention Centre-Administration | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Feb 2021 | 2021-02-01 09:41:11 | 2021-02-01 11:30:00 | Fail | Operator locked out of Gallagher door control system in Key Control. Logged in as Administrator to reset password for the Operator login. Tested ok. Indigo CCTV videowall partially frozen and one screen with no input. Located workstation and restarted. Reconfigured video wall across the four monitors. Tested ok.
MSA-DCS | WA3960533 | Admin air-con not working again | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 01 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-15 07:43:00 | Fail | Complete
MSA-DCS | WA3960547 | Gate House - Front Entrance-Keywatcher malfunctioning | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Feb 2021 | 2021-02-01 11:42:57 | 2021-02-01 09:30:00 | Pass | Key Cabinets 2 & 3 found intermittently not opening. Power cycle of affected units retested now working ok.
MSA-DCS | WA3960550 | unit 7 G12 tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 07:46:26 | 2021-02-02 07:50:00 | Fail | Rewashed tap
MSA-DCS | WA3960568 | Unit 8 C9 Light above bed broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-15 09:30:00 | Fail | Repaired broken light
MSA-DCS | WA3960569 | Unit 16 - B & D polisher/buffer damaged plug top | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-16 08:30:00 | Fail | Replaced damaged floor polisher plug in unit 16
MSA-DCS | WA3960573 | kitchen - Rational Oven No 3 recently overhauled. Oven opens mid way through an aborted Clean cycle | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 08:08:14 | 2021-02-08 11:35:00 | Fail | Instructed staff to clean more often. Rang kitchen on 15/2 for results and oven hasnt been doing it now.
MSA-DCS | WA3960577 | Unit 14 - B12 shower leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-12 11:30:00 | Fail | Nill
MSA-DCS | WA3960580 | Unit, B14 - Cell viewing window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 08:18:20 | 2021-02-01 11:00:00 | Pass | reglazed glass
MSA-DCS | WA3960584 | Unit 1 , B10 - Inspection window broken in door | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 08:21:34 | 2021-02-01 12:30:00 | Pass | reglazed broken glass
MSA-DCS | WA3960587 | Cell B7 Viewing window cover is falling out - see notes | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-17 14:00:00 | Fail | INSPECTED UNITS 1,2,3 - ALL WINDOWS IN WORKING ORDER - NO COVER FALLING OUT EVIDENT
MSA-DCS | WA3960596 | Unit 14 The sink is blocked in cell B01 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-12 13:30:00 | Fail | Nill
MSA-DCS | WA3960611 | unit 3 D wing cleaning cupboard tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-11 14:30:00 | Fail | Nill
MSA-DCS | WA3960628 | Cent5ral Admin, Steven Reddy office - lock is faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-08 09:15:00 | Fail | Attend site, serviced lock. Working correctly.
MSA-DCS | WA3960635 | Unit 1 A1 Hole in main window | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 09:04:28 | 2021-02-01 16:15:00 | Pass | reglazed window
MSA-DCS | WA3960639 | Unit 3, Cell D6 sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-11 13:30:00 | Fail | Nill
MSA-DCS | WA3960640 | gate control D2 internal omni trax intemittent activation | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 09:07:25 | 2021-03-03 16:30:00 | Fail | Observed zone activity whilst working in the Control room this morning. No activity in this zone between 06:30hrs & 12:00hrs today. Ran report on zone activity in last month. Noted regular activity on zone at times of daily Walk Test, no significant activity after the burst of activity on 01/02/2021. No further action taken.
MSA-DCS | WA3960820 | Unit 1 - Water leak in 'D' WING cleaning cupboard (coming from pipes on RHS) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-17 14:30:00 | Fail | Nill
MSA-DCS | WA3960828 | Camera 40 female PTZ no picture No image on monitor for Camera 40 (Old female yard PTZ 1) | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 10:11:59 | 2021-02-15 16:45:00 | Fail | Checked and found Camera 40 ( old female yard PTZ1 ) has been replaced by Camera 29 ( FEM_YARD PTZ1 ) in December 2020. Old camera was kept in system for footage reason only. Confirmed with customer and deleted camera from system.
MSA-DCS | WA3960864 | unit 5 house 10 bath extraction fan not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-22 10:00:00 | Fail | Replaced faulty wall exhaust fan
MSA-DCS | WA3960865 | main kitchen 2 lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-22 11:30:00 | Fail | Replaced kitchen lights with LEDS
MSA-DCS | WA3960868 | unit 5 house 7 electronic lock not fuctioning | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 11:11:43 | 2021-02-25 15:00:00 | Fail | Attended site.Checked Cardax Controller 3000 in house 7 in unit 5.Checked power and connections on front electric strike.Conducted test.Electric strike is fully operational.
MSA-DCS | WA3960869 | unit 5 house 1 kitchen mixer tap split | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-17 11:00:00 | Fail | Arrived on site and inspected found the tap having pin hole. Collected parts from supplier and returned to the site. Removed the faulty tap and installed new tap. Tested multiple times all working in order.
MSA-DCS | WA3960871 | kitchen vegi mixer not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-18 13:45:00 | Fail | Arrived on site and inspected found unit 4 j block. All taps working in order
MSA-DCS | WA3960872 | unit 2 C7 HW spindles leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-03-24 09:30:00 | Fail | Arrived on site and inspected found the the spindles faulty. Tried to repair the spindles. Couldn’t repair them. Need new spindles. Ordered parts. Collected parts from supplier and returned to site. Replaced hot and cold spindle in the hand basin. Hot and cold in shower. Tested all working good
MSA-DCS | WA3960876 | health centre treatment room 1 air con will not ajust higher that 15 deg | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-03-03 16:05:00 | Fail | Replaced controller whilst on maintenance.Returned to check over unit and checked operation.Unit running okay.Paperwork completed.
MSA-DCS | WA3960880 | Unit 7, Regi Area- Vinyl flooring is lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-03-11 08:30:00 | Fail | TRIMS INSTALLED TO SPLIT JOINS IN VINYL
MSA-DCS | WA3960884 | Unit 1, Cell C2 - Floor waste blocked; grate missing from sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 11:23:39 | 2021-02-02 09:53:00 | Pass | Unblocked drian and replaced broken waste
MSA-DCS | WA3960927 | Unit 5, A23 - Numerous officers are experiencing difficulty operation the cell door main lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 12:02:33 | 2021-02-02 14:30:00 | Fail | Attend site, keys not working on main lock. Parts required, reattend site same day to fit new driver bush and service lock.
MSA-DCS | WA3960963 | Internal Sally port Camera not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 12:40:10 | 2021-02-02 13:00:00 | Fail | No image on Indigo CCTV system. No image from camera at the Indigo rack cards. Traced fault to blown fuse in the camera power supply. Replaced fuse, camera tested ok.
MSA-DCS | WA3960992 | Unit 3, D Wing - cleaning cupboard far hot water pipe loose/disconnected | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-11 15:30:00 | Fail | Nill
MSA-DCS | WA3961004 | SOG, conference rooms, and HR office - essential power points not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 13:50:42 | 2021-02-02 12:30:00 | Pass | Replaced RCD
MSA-DCS | WA3961005 | house six no water at all | Boronia Pre-release-AK23 - Prisoner Accommodation House 6 and 7-Ground Floor | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 01 Feb 2021 | 2021-02-01 17:55:14 | 2021-02-01 18:00:00 | Fail | isolations seized on meter, water corp valve by passes, there are rpz internal to boundary and acckrding to Australian standards the must be one on the meter.
MSA-DCS | WA3961019 | External fence cameras are operational, PTZ not working correctly | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Feb 2021 | 2021-02-01 18:21:36 | 2021-02-01 15:45:00 | Pass | Attended site, checked and found PTZ has been back to normal and has restored itself.
MSA-DCS | WA3961029 | unit 13, A13 - potential blockage fault in taps | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-12 13:30:00 | Fail | Noll
MSA-DCS | WA3961063 | Left hand front sallyport door arm limiter in motor is incorrectly set | Bunbury Regional Prison | SPA-BR | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 15:19:05 | 2021-02-04 15:30:00 | Fail | 01/02/21Adjust open limit.Test operation.03/02/21Thoroughly test limit switches and corresponding relays. Test contactor and apply contact cleaner. Issue appears to be with motor clutch.04/02/21Adjust motor clutch to maximum. Flush and replace Auto Trans. fluid. Clutch still does not hold gate. Replace motor.Lubricate hinges.
MSA-DCS | WA3961143 | Gatehouse - Zone 5 - Light pole 14 is not working. | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-10 11:30:00 | Fail | Investigate and repair perimeter lighting
MSA-DFES | WA3960986 | Applied Training ground -fault showing maintenance Gas Prop | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Gas (PD) | WA BOILER SPARES & SERVICE | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-02 10:30:00 | Pass | Remove air actuated gas valve and install blanking flange. Pressure test and left tagged out of service.Further work order will be raised when required
MSA-DTAG | WA3960606 | Basement - Since Sunday morning the duress alarm passage way 2 is setting itself off | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-02 11:00:00 | Pass | Install new button at custody hall 2. Test, all OK.
MSA-DTAG | WA3961003 | ground court 3 air con not working | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-05 14:54:00 | Fail | Arrived on site and signed in. Completed jsa and hot works permit. Accessed works site and reclaimed gas from stage 1. Could weld straight away due to courts in session. Once court had finished brazed out the filter drier and installed the new filter drier. Confirmed no leaks. Evacuated system and recharged with r22 gas. Turned system on and confirmed correct operation. Cleared debris from worksite and completed paperwork.
MSA-DTAG | WA3961011 | Public toilets holders have been removed and require replacment- photo to be emailed | Joondalup Courthouse | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 01 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-03 11:30:00 | Pass | Bar through paper towel easy to remove and use as a weapon. Supplied two new bars and made secure with brackets so can not easily be removed. Two screws need to be removed to replace the towel roll.
MSA-DTAG | WA3961040 | SAT - the cameras not working | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-01 18:00:00 | Pass | Upgraded firmware on 3x axis cameras, adjusted permissions and view groups for milestone
MSA-DTAG | WA3961058 | Front entrance , Auto doors - utomatic door was not able to be ‘locked open | Central Law Courts | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 01 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-02 10:30:00 | Pass | Found that the keyswitch is not wired into the unit, only access control, I have connected the open signal into the unit so they can use it when required, tested all ok.
MSA-DTWD | WA3960977 | Main entry Exterior Lord Street Repair Sign to Lord Street Entrance | Mount Lawley Campus | GMP-BR | Building | Steel Work (BU) | AWB Co. | 1 | CLOSE | 01 Feb 2021 | 2021-02-02 17:00:00 | 2021-02-21 09:00:00 | Fail | Attend site and remove damaged sign and store in safe place
MSA-DCA | WA3961437 | Urban orchard - all lights are out, not coming on at night | Perth Cultural Centre Precinct | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-02 15:30:00 | Pass | James Street bolards lights breaker tripped. IR tested circuit with low reading and passed.Checked all other boards and override lights to ensure working operation and checked all time clocks for 06.30 to 18.30 everyday.
MSA-DCA | WA3961506 | Plant Room - Boiler in fault | Shipwreck Galleries-Main Building | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-02 13:00:00 | Pass | Attended site. Boiler system to have faulted. Applied tests and checks. Investigation found B2 to have faulted on an E02 error. Checked system strainers (clean) checked system for air (no air present). Reset boiler and monitored operation. Boiler operating correctly with no faults present and cause of fault to be unknown.
MSA-DCS | WA3961343 | Unit 13 - C12 shower head and taps leaking, sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-12 14:30:00 | Fail | Nill
MSA-DCS | WA3961380 | IR Beam A2 internal constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 11:58:56 | 2021-02-02 11:30:00 | Pass | Rectified and fixed the A2 IR beam set, job completed.
MSA-DCS | WA3961389 | External gardens zone 9 (not inside Prison)Solenoid always runs whil system is on | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 08:03:49 | 2021-02-15 09:00:00 | Fail | FAULTY VALVE - REPLACED WITH NEW
MSA-DCS | WA3961398 | Administration, staff room - Zip Hydrotap fault filter change | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Staff Kitchen and Dining Area | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-03 13:50:00 | Pass | Changed and flushed filter as was due.
MSA-DCS | WA3961407 | Unit 7, B5 - Door has dropped and may require new hinges | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-15 12:00:00 | Fail | Unable to attend on time due to covid lockdown.Replace hinges and adjust lock.
MSA-DCS | WA3961409 | Stores Broken external door key snapped and locking pins are missing - see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 08:23:39 | 2021-02-02 12:00:00 | Pass | Replace lock on external door.
MSA-DCS | WA3961436 | unit 2 A/B wing HW scolding hot | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-08 11:32:00 | Fail | Waited at the gate due to no escort. The issue is woth a boiling unit. Maintenance guy said that he will raise a new work order (P1) for a different contractor.
MSA-DCS | WA3961440 | Official Visits Lock needed on male toilet | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-03-12 12:30:00 | Fail | Unable to attend on time due to covid lockdown. Require parts.Install toilet indicator bolt with packer to door
MSA-DCS | WA3961454 | Vegetable Preparation - Workshop-sink has been knocked by a fork lift all plumbing work is broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-03-19 12:33:00 | Fail | Nill
MSA-DCS | WA3961503 | Unit 1 C wing dayroom Door to dayroom lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 13:50:04 | 2021-02-02 14:00:00 | Fail | Onsite, replaced bush an serviced lock.
MSA-DCS | WA3961536 | control room - cell call system (tacera gui) in fault not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 10:09:44 | 2021-02-09 00:00:00 | Fail | Attended site, repaired Tacera systems and tested OK.Job Complete
MSA-DCS | WA3961564 | Stores boom gate - boom gate not operating | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 10:24:50 | 2021-02-02 15:45:00 | Pass | 02/02/21Access control issue.Contact SEME.
MSA-DCS | WA3961573 | ISU D06 toilet not flushing | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-10 13:30:00 | Fail | Replaced faulty parts
MSA-DCS | WA3961581 | ISU B/D air con not working (suspect seized fan) | Banksia Hill Detention Centre | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-03-31 16:09:00 | Fail | Completed leak check and repair, tested evactuated charged unit. All ok.
MSA-DCS | WA3961588 | Amenities - Front Entrance Retic flooding entrance, possible faulty valve | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-23 11:00:00 | Fail | replaced broken sprinklers
MSA-DCS | WA3961594 | Unit 3, central yard - rear grille into new C wing yard can only be open from the central yard side | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 15:08:34 | 2021-02-02 13:00:00 | Pass | Onsite, Serviced and cleaned out lock.
MSA-DCS | WA3961596 | Stores, faulty washing machine (machine at stores for collection) | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-12 11:55:00 | Fail | 09/02/21 - Collect W/M from Wandoo stores11/02/21 - water inlet valve blocked, disassemble, clean and reassemble. Test operation, ok.12/02/21 - Return W/M to Wandoo stores
MSA-DCS | WA3961599 | Gatehouse - electric fence voltage is dropping our on most zones | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-18 16:30:00 | Fail | investigated interrogated systems. performed adjustments & tested ok
MSA-DCS | WA3961601 | Bakery bread slicer - right hand side every second blade is working & some circular part has broken | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 15:19:19 | 2021-02-02 15:15:00 | Pass | COMPLETED
MSA-DCS | WA3961603 | Bakery- Bread Mixers rollers have deteriated & falling apart | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 15:21:28 | 2021-03-23 11:15:00 | Fail | RETURNED TO SITE, ROLLERS REPLACED BY ANOTHER CONTRACTOR WHILST BAKEQUIP WAITED FOR PART.
MSA-DCS | WA3961616 | unit 1 B11 View hatch damaged & timber work | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 11:26:08 | 2021-02-08 12:00:00 | Fail | RE NEW VEIWING HATCH TO CELL DOOR
MSA-DCS | WA3961628 | Bakery - Fridge temp ( cool room ) to bakery is running at +17deg | Casuarina Prison | SPA-BR | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 16:08:00 | 2021-02-16 14:20:28 | Fail | Continue vacing out system and recharge with gas,test operation all running ok at present.
MSA-DCS | WA3961656 | Rear Stores Yard- Security pole light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-03-02 10:30:00 | Fail | Investigate why pole light isn’t working.
MSA-DCS | WA3961678 | SOG base reception PC keeps freezing | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-15 14:30:00 | Fail | Install and program Gallagher server on workstationRemove Nuc and return to ProgrammedTest and commissionAPPROVED BRAF ATTACHED
MSA-DCS | WA3961710 | Stores rubber on air bridge is gone and needs replacing | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-26 11:00:00 | Fail | 12/02/21Inspect air bridge.Measure up rubber stop.Source materials.26/02/21Install dock bumper
MSA-DCS | WA3961747 | Control room - MDAS fault #05 programs & cogskills low battery | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-16 08:30:00 | Fail | Replaced faulty MDAS transponder back up batteries, job completed.
MSA-DCS | WA3961754 | Emergency siren is not working | Melaleuca Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | COMPFIN | 02 Feb 2021 | 2021-02-02 18:52:30 | 2021-02-02 16:00:00 | Pass | Evacuation and Emergency button connected to one of the 3210 controller in GH Control room not working. Coordinate with SEME service department and I’ve been advice that the system set-up is subject for re-evaluation and re-design with the approval of PFM.
MSA-DCS | WA3961777 | Turner C wing HWU leaking | Banksia Hill Detention Centre | SPA-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 14:26:00 | Pass | nil
MSA-DCS | WA3961780 | Stores Boom Gate - control panel is intermittently none responsive | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 16:15:31 | 2021-02-03 10:45:00 | Pass | Jacques intercom unit in stores frozen. Restarted unit and tested network. Network was fine but unit froze after a short while again. Logged onto main Jacques server up above gatehouse. Restarted all services and ran some tests. Everything functioning as per normal.
MSA-DCS | WA3961792 | Jasper C Wing - Broken water pipe | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 22:20:43 | 2021-02-02 21:05:00 | Pass | Cut concrete and repaired damaged pipe
MSA-DFES | WA3961516 | Main Workshop Area - Toilet (adjacent to Dining Room) - Extraction Fan is un-serviceable | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-08 15:30:00 | Fail | Located faulty fan and tested. Fan has seized due to wear and fatigue. Will seek approval for a replacement fan and return to site to replace.
MSA-DTAG | WA3961418 | Door No 1 unable to be unlocked, barrel spinning – this is a fire exit. | Supreme Court | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 12:29:14 | 2021-02-02 09:45:00 | Pass | Attended site to service and change cam for 570 barrel.
MSA-DTAG | WA3961595 | 1987 Sheriff's Office Lights are out in back stairwell | Supreme Court-Supreme Court Building | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 02 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-04 12:00:00 | Pass | Inspected light and found damaged due to age. Replaced and tested working
MSA-DTAG | WA3961698 | Level 6 - Air conditioning is not functioning on levels 3 & 5 | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 02 Feb 2021 | 2021-02-02 17:04:31 | 2021-02-08 10:30:00 | Fail | Attend site. Check controls bms on level 6. Found floors to all be online and working as normal. Finalise paperwork.
MSA-DTAG | WA3961704 | Stairwell steps to Court 3 & 4 from Custody - blood stains (Blood is also on the wall of Pod 1) | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-08 10:57:00 | Fail | Completed as per WO.
MSA-DTAG | WA3961762 | Court dock 2 - Seats in court dock 2 are loose | Rockingham Justice Complex | WSM-BR-SITE | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-03 09:30:00 | Pass | removed and re-fixed chairs
MSA-DTWD | WA3961561 | A block L1 A146 BMS cannot access times schedule | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Building Automation & Electrical Services Pty Ltd | 3 | CLOSE | 02 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-23 15:30:00 | Fail | Attended site and rectified the issue
MSA-DTWD | WA3961775 | BLD 824 - External spotlight is strobing on and off | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 02 Feb 2021 | 2021-02-03 17:00:00 | 2021-02-03 10:00:00 | Pass | job completed - replaced LED flood light
MSA-DCS | WA3961992 | Maintenance office fire extiguisher 4.5 kg ABE powder needs to be exchanged as was used fire | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 07:31:13 | 2021-02-12 11:25:00 | Fail | Supplied a 3.5kg CO2 and 4.5kg DCP Fire Extinguisher to Gatehouse.
MSA-DCS | WA3961995 | unit 4 perimeter fence zone 5,6 and 10 fail to activate on testing | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Feb 2021 | 2021-02-05 17:00:00 | 2021-06-09 11:00:00 | Fail | Stripped down "Splice Kit" junctions and reconnected, reusing existing splice kits where possible. Confirmed circuit electrically intact with 10k ohm EoL stable. Tested operation of zone to Gate control, confirmed operation.
MSA-DCS | WA3961996 | unit 4 perimeter cowling zones 2,3,4,5,6,7,9 and 10 did not activate on testing | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Feb 2021 | 2021-02-05 17:00:00 | 2021-06-15 12:00:00 | Fail | Indicated zones tested, recalibrated and then tested again. False alarms appear to be rectified and zones are alarming as intended.
MSA-DCS | WA3961999 | Unit 6 - D12 blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-10 10:30:00 | Fail | Nill
MSA-DCS | WA3962003 | Unit 17 - Toilet staff toilet blockage - see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-15 14:30:00 | Fail | Nill
MSA-DCS | WA3962006 | SITE COST Unit 14 - A & C damaged powerpoint - see notes | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 03 Feb 2021 | 2021-02-03 11:49:58 | 2021-02-03 11:30:00 | Pass | Replaced broken gpo
MSA-DCS | WA3962011 | Unit 13 - B & D tap leaking near kitchen | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 07:54:43 | 2021-02-03 09:35:00 | Pass | Looked for unit leaking could not find leaking fountains perhaps duplicated with something else
MSA-DCS | WA3962022 | visits area non contact room 4, fire alarm constant alarm | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 07:44:40 | 2021-02-10 10:11:00 | Fail | 9/02/21 EIAttended site unit 4 VESDA pipe 4 wing B blocked sample points.Cleared blocked sample points. System status displaying normal on departure.Revisit required for visits area non contact room 4 fault investigation.BG 10/2/21Attended site and replaced a detector in visit room four. This cleared both fault.Whilst on site mimic in Gatehouse down. Rebooted network. Network communications re-established. System normal at time of departure
MSA-DCS | WA3962029 | Unit 17 - C11-silver plate on the locking mechanism on the personal lock is loose. | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-03-03 10:00:00 | Fail | Tighten mortise lock body and face plate screws.
MSA-DCS | WA3962080 | metal shop welder had a damaged plug | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-15 12:30:00 | Fail | Replaced 2x faulty plug tops
MSA-DCS | WA3962118 | Unit 2, B & D wing showers - window slider broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-15 10:00:00 | Fail | SPIRAL BALANCES RE NEWED
MSA-DCS | WA3962119 | Unit 1 - B & D The B/D shower ventilation was damaged during the Incident - see notes | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 09:09:48 | 2021-02-08 10:00:00 | Fail | MEASURMENTS TAKEN AND GIVEN TO JIM GIBSON - ADVISED BY HIM PRISON METAL SHOP TO FABRICATE AND INSTALL DAMAGED VENT
MSA-DCS | WA3962126 | SITE COST Unit 5, Cell D2- Faulty light switch with exposed wiring, cover plate has been removed | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 03 Feb 2021 | 2021-02-03 13:16:41 | 2021-02-03 09:30:00 | Pass | Replaced broken light switches.
MSA-DCS | WA3962134 | Unit 2, Officers toilet - exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-12 10:00:00 | Fail | Investigate and replace unit 2 officers toilet exhaust
MSA-DCS | WA3962139 | WWTP office GPO faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-10 15:00:00 | Pass | Investigate and repair/replace faulty gpo in wwtp office
MSA-DCS | WA3962146 | WWTP old plant sea container GPO faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-10 08:30:00 | Pass | Investigate and repair wwtp sea container gpo
MSA-DCS | WA3962151 | Unit 4, Cell G28 - shower taps leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-09 11:00:00 | Pass | Reseated both taps and replaced both washers
MSA-DCS | WA3962182 | SB1 (Between U15-U16) - Room 3- damaged lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-25 13:15:00 | Fail | Require partsRemove mortise lock, remove casting burrs on lock latch, re install and adjust strike. Parts not used.
MSA-DCS | WA3962184 | Unit 13, Cll A15- Tap connected to the sink will not stop running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-12 10:30:00 | Fail | Nill
MSA-DCS | WA3962191 | Unit 13 - A16 Tap won't turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-12 11:30:00 | Fail | Nill
MSA-DCS | WA3962195 | PO office fluro light is faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-15 10:30:00 | Fail | Job has already been completed on a different work order
MSA-DCS | WA3962209 | Unit 1 - B12 - personal lock faulty | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-03-09 11:00:00 | Fail | Unable to attend on time due to covid lockdown.No escort available to enter wing. Replace hinges, barrel, door plate, weld on strike plate and refit pull handle.
MSA-DCS | WA3962266 | Stores front entrance External Stores Freezer door roller have snapped and door cannot cool properly | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 03 Feb 2021 | 2021-02-03 14:30:00 | 2021-02-03 14:24:12 | Pass | Arrived on site,checked over freezer door,found all 4 rollers broken,left site picked up new rollers,returned to site and replaced broken ones,tested door operation all ok.
MSA-DCS | WA3962267 | Admin, Tea room- water filter fault, light flashing | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-08 08:40:00 | Pass | Service and filter replacement on Billi Alpine unit. System has had previous leak by working ok now. Normal Operation
MSA-DCS | WA3962342 | Front Gate- Anti ram barrier fault | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 12:05:45 | 2021-02-03 13:30:00 | Pass | 03/02/21Replace broken rod end. Lubricate bearings.
MSA-DCS | WA3962436 | main kitchen salad bar unit showing temperature of 11degrees. | Nyandi Training Academy | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 13:11:50 | 2021-02-04 10:00:00 | Pass | unit running well
MSA-DCS | WA3962448 | Main Kitchen-commercial dishwasher water leaking under dishwasher | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-11 09:45:00 | Fail | 11/02/21Sign in Carry out Covid testsFound water underneath dishwasher Run unit and found waste leaking Found nuts on waste completely loose Check seals, ok. Tighten waste up and test Check for leaks ok
MSA-DCS | WA3962455 | Stores - external of the wire - coolroom not holding temp | Bandyup Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 13:28:17 | 2021-02-03 16:00:00 | Pass | Attended site. Cool room system servicing stores area not cooling and temps to be outside of acceptable range. Applied tests and checks. Investigation found system to have tripped on HP. Reset HP and tested operation, checked refrigerant pressures (ok) cleaned condenser coil (ok). Adjusted Fan speed controller. Tested operation. System operating correctly with no faults present. Coolroom maintaining 2c. Left site.
MSA-DCS | WA3962476 | Main kitchen Combi Oven/Steamer Ringing sound when oven is ON. Possibly due to faulty fan. | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-03-04 10:40:00 | Fail | Returned 4/03 to fit the correct new fan motor, tested ok.
MSA-DCS | WA3962490 | unit 6 D11 Main Lock Faulty, not engaging sometimes | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 14:16:47 | 2021-02-04 09:40:00 | Pass | Attend site, replace worn out driver bush and service lock.
MSA-DFES | WA3962141 | Applied Training Ground USAR container Bee infestation please eridicate | FESA RHQ - Forrestfield | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 03 Feb 2021 | 2021-02-04 17:00:00 | 2021-02-03 13:20:00 | Pass | Carried out a service for bees at Wa Fire & Emergency Services Academy. There were reports of bees located under ashipping container, due to this the bees could not be safely removed and had to be treated. Thoroughly dusted theentrance point under the shipping container. It's recommended that this hole is sealed to avoid bees returning in thefuture.
MSA-DTAG | WA3962163 | L14 keypad on this door on level 14 has been reported as faulty | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 03 Feb 2021 | 2021-02-03 13:45:45 | 2021-02-03 12:00:00 | Pass | Power cycled keypad reader, restarted controller 18 and door controller to force RS485 connectiontested and confirmed operational
MSA-DTAG | WA3962504 | Lower ground (1903) and 1st floor (1987) Courts 6, 7, 10 and 11 Clocks have stopped | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 03 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-05 08:30:00 | Pass | Inspected clocks and replaced batteries and made safe
MSA-DTWD | WA3962167 | F Block, FG39-Auto doors @ CSC will intermittently get stuck open, seems like sensor may be faulty | Carlisle Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 03 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-03 14:10:00 | Pass | Found that one of the pe sensors and the photo board were failing, replaced faulty components and tested, all ok.
MSA-DCA | WA3963278 | water leak in zone 15 | Perth Cultural Centre Precinct-Urban Orchard-Ground Floor | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-04 13:30:00 | Pass | Work Completed:- Locate leak and isolate ball valve- Expose area- Reuse valve box to cover flush valve- Remove ball valve handle and leave in box
MSA-DCS | WA3963125 | Unit 2 - cell D 8 - toilet cistern not filling up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-15 13:30:00 | Fail | Nill
MSA-DCS | WA3963128 | whole of unit 13 daily stats on the screen of the same panel showed incorrect data - see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 04 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-08 13:23:00 | Pass | 8/02/21 EI/JGAttended site found VESDA unit 13 wing BD Cell 9/10 pipe 2 valve reporting stuck open/closed fault.Performed a manual valve scan clearing fault.System status displaying normal on departure.
MSA-DCS | WA3963156 | Unit 1 B wing prisoners water fountain not getting cold | Bandyup Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-25 11:15:00 | Fail | Working okay on arrival. May have been over use on a hot day and struggling to keep up. Checked other fountains nearby, all chilling okay.
MSA-DCS | WA3963191 | Extern gardens (outside the prison)Retic line break external zone 9/10 next to microphonic sensor | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 08:40:13 | 2021-02-05 09:30:00 | Fail | EXPOSED CRACKED PIPE AND FIXED WITH SUPPORT STRAP AND PATCH.
MSA-DCS | WA3963205 | unit 4 cells 1-9 reception for TV's not very good | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-15 11:00:00 | Fail | Work performed by Cian O'Halloran 11/02/2021:Attended site.Fault find TV issues.Located amplifier in roof space of Cell 9 in Unit 4A.Amplifier requires replacing. IKUSI TAE 1120(3264) line extender amplifier.Also UDL 420 6 way tap 20db.Work performed by Cian O'Halloran 15/02/2021:Replace amplifier and splitter in roof space of Cell 9 Unit 4A.Tested, all OK.Job completed.
MSA-DCS | WA3963275 | abattoir roof all whirly birds broken | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-11-10 14:15:00 | Fail | whirly birds replaced with new
MSA-DCS | WA3963301 | Unit 6 - B Wing cleaning cupboard sink has a water head that has broken off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 08:30:00 | Pass | Nill
MSA-DCS | WA3963347 | stores coms room Cabinet key broken in lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 10:58:30 | 2021-02-05 12:05:00 | Fail | Attend site to remove broken in lock in Comms room. Keys require cutting back at workshop. Reattend site to check keys.
MSA-DCS | WA3963365 | Pharmacy Essential Meds- Both gates in and out of essential meds not locking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 11:14:11 | 2021-02-05 11:30:00 | Fail | Attend site, replaced lock on gate. Other gate requires a new electric strike. Parts required to be ordered. Reattend site and install new electric strike. SEME is required to attend site for electrical works required. Discussed with customer on site. Our repairs are completed. Site to organise to have SEME attend site.
MSA-DCS | WA3963372 | Pharmacy - Tap leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 11:18:41 | 2021-02-09 13:35:00 | Fail | Replaced leakingtap
MSA-DCS | WA3963382 | Gardens western retic controller tripping out again | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 11:24:52 | 2021-02-05 11:00:00 | Pass | USING TRACKER UNIT FOUND BROKEN WIRE TO SOLENOID, REPAIRED WIRE AND TESTED AND SYSTEM IS OK
MSA-DCS | WA3963385 | Unit 1, Cell C9- Cell Call panel has been removed | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Feb 2021 | 2021-02-04 15:29:01 | 2021-02-04 15:44:00 | Fail | Tested intercom multiple times, all ok. No fault found. Light switch plate in cell is missing though.
MSA-DCS | WA3963386 | Unit 4 - A9 window pane falling from frame | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-18 13:00:00 | Fail | NEW SLIDING SASH & WINDOW BALANCERS INSTALLED
MSA-DCS | WA3963387 | Unit 14, Cell C16- Water leak under wash basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-16 10:30:00 | Fail | Nill
MSA-DCS | WA3963392 | Print shop door has dropped or is sticking making it difficult to open and close | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-03-02 11:30:00 | Fail | Unable to attend on time due to covid lockdownReplace hinges, remove threshold, service lock and replace bolt throw. Require PartsInstall door seal strip to bottom edge of door.
MSA-DCS | WA3963399 | Unit 1 B4 toilet blocked - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 11:38:19 | 2021-02-09 09:10:00 | Fail | Unblcoked blocked toilet.Prisoner flushed power point down the toilet
MSA-DCS | WA3963422 | HR corridor Whirly bird has seized bearings on roof | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 11:51:20 | 2021-05-18 15:00:00 | Fail | NEW WHIRLY BIRD INSTALLED
MSA-DCS | WA3963443 | Unit 1 - Back up generator struggled to start after power outage due to fire | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 12:08:39 | 2021-03-18 08:26:00 | Fail | Repair Completed
MSA-DCS | WA3963549 | Boiler house, workshop - Boiler number 2 out on fault | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 14:12:35 | 2021-02-12 13:30:00 | Fail | Fault find on Boiler #2, would not start.Found loose wore on mod motor, tightened up all connections
MSA-DCS | WA3963555 | reception and SO's office air con visible leak and needs re gasing | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 14:26:59 | 2021-02-05 16:30:00 | Fail | Attended site. Reception/SO office AC system not operating correctly. Applied tests and checks. Investigation found system to have a refrigerant leak present. Pressure tested system to locate leak on condenser coil bend. Left site to pick up additional parts. Returned to site. Braised and repaired leak. Re pressure tested system and inspected for leaks, investigation found another leak on a separate section of the condenser coil. Repaired and braised leak. Re pressure tested system (system to have held pressure). Evacuated and charged system with 4kg R438a. Tested operation. System operating correctly.
MSA-DCS | WA3963599 | Flickering light in visitor toilet & downlight fallen from roof in kitchen | Maddington (South East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 11:06:00 | Pass | Replace flickering light in toilet and re secure light in kitchen
MSA-DCS | WA3963612 | Monitor in reception for cameras not working | Maddington (South East Metro) | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-05 15:00:00 | Pass | Attended site and reset system and reloaded camera layouts. All reloaded and tested ok. Job complete
MSA-DCS | WA3963615 | New entry card isnt unlocking internal doors | Maddington (South East Metro) | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-17 12:30:00 | Fail | Work performed by Nathan Groenewald (05/02/2021)Attended site and checked Gallagher system cleared all alarms and all tested ok. Unable to test card as site contact is notavailable. Technician to reattend job.Work performed by Drake Van der Merwe (11/02/2021)Arrived on site, site could not find defective card. Technician to return next week.Work performed by Drake Van der Merwe (17/02/2021)Checked cards and found issue with Mifare cards not compatible with GBUS T10 readers.Site recently upgraded by another contractor.Sapio job completed.
MSA-DCS | WA3963666 | zone 5 camera 2 is down | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Feb 2021 | 2021-02-04 21:16:19 | 2021-02-04 22:30:00 | Fail | Attended site checked and found Zone5 Camera2 showing green on monitors. Checked on field found no camera signal feed into Indigovision encoder in EC cabinet. Reboot camera from EC cabinet by disconnected and reconnected the power to camera. Tested all ok after work.
MSA-DCS | WA3963685 | CCTV cameras not working on monitor in control room | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 18:53:09 | 2021-02-05 08:00:00 | Pass | Rectified and fixed ebi ws, job completed.
MSA-DCS | WA3963687 | Fire alarm has set off sprinklers and needs to be turned off. | Casuarina Prison-Gatehouse | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 04 Feb 2021 | 2021-02-04 23:37:19 | 2021-02-04 22:39:00 | Pass | Casuarina PrisonAttended site for broken sprinkler head in unit 1Found sprinkler head had been tampered with and broken causing it to activateChanged out broken head with a new oneRefilled sprinkler installationCleared fip
MSA-DTAG | WA3963172 | L4 Faulty lights in Magistrates stairwell | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 12:00:00 | Pass | Job complete
MSA-DTAG | WA3963179 | 1903 Basement Timber service panel has detached from wall – new MDF panel required | Supreme Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-03-30 11:36:00 | Fail | NEW MDF INSTALLED SECURELY
MSA-DTAG | WA3963254 | Custody duress alarm passage way 2 is now staying red following testing this morning fault returned | Perth Children's Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-05 10:30:00 | Pass | Investigated fault, liaised with guards/ Checked over system and reviewed arm and disarm procedures with onsite guards. Found no fault, user error. Ran through arm/disarm correct procedure with guards.
MSA-DTAG | WA3963292 | 1987, Lvl 2- A/C flow in President Buss Chambers is very low | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-19 14:35:24 | Fail | Replaced faulty dp switch on chillers 2. Confirmed correct operation
MSA-DTAG | WA3963435 | Basement, Sallyport- Aluminium wall panel next to fire exit has become detached | Supreme Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-04 13:30:00 | Pass | LOOSE INFILL PLATE RE ATTACHED TO BOTTOM OF WALL
MSA-DTAG | WA3963438 | Basement, Sallyport- Single fire exit door in sallyport is very hard to open/close-door needs planed | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-04 14:30:00 | Pass | ADJUSTMENTS MADE TO DOOR FRAME,ALL CHECKED NOW OPERATIONAL
MSA-DTAG | WA3963661 | Front Door latch is loose. Top screw to the latch has lost its grip | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 04 Feb 2021 | 2021-02-05 17:00:00 | 2021-02-05 08:45:00 | Pass | FRONT DOOR LATCH RESECURED
MSA-DTWD | WA3963413 | Aberdeen entrance (Garden Bed) - Reticulation celenoid valve is broken | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 14:00:00 | Pass | Replace solenoid and pipework make sure working
MSA-DTWD | WA3963469 | E Block, Faulty security sensor 053 | Bentley Campus | GMP-BR | Security | CCTV Surveillance (SE) | CONNECT SECURITY SYSTEMS | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-07-12 11:44:00 | Fail | replaced sensor and damaged cable with new
MSA-DTWD | WA3963586 | Chiller 1 not working, no fault showing (see futher notes below) | Mandurah Campus (formerly Peel) | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-12 15:29:00 | Fail | Icon Logic completed repairs to chiller 1.
MSA-DTWD | WA3963588 | Chiller 2 not working, no fault showing (see futher notes below) | Mandurah Campus (formerly Peel) | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 04 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-15 16:00:00 | Fail | Picked up part from supplier went to site. Signed in checked in with Sharyn. Gained access keys and equipment. Isolated and locked out unit. Removed old actuato and installed new. Tested and monitored operation, all ok. Cleaned up and completed paperwork and signed out
MSA-DCS | WA3963935 | Unit 15 D12 - Keyhole face plate faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 05 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-19 12:00:00 | Fail | tighten mortise lock, face plate and strike screws
MSA-DCS | WA3963942 | Laundry - dryer is skipping cycles | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 2 | CLOSE | 05 Feb 2021 | 2021-02-09 17:00:00 | 2021-04-14 13:50:00 | Fail | Found soft start not seeing 22v input from contactors Aux. Quote for repairs done 11/02/21 waiting on approval to proceed.
MSA-DCS | WA3963998 | unit 8 D wing showers no cold water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 07:43:30 | 2021-02-08 13:30:00 | Fail | Replaced seized isolation vakve
MSA-DCS | WA3964016 | Unit 17 - The Whole Unit No gas hot water to entire Unit | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 11:59:58 | 2021-02-05 14:30:00 | Fail | Nill
MSA-DCS | WA3964022 | Unit 6 A2 dripping tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-19 11:36:00 | Fail | Rewashed tap
MSA-DCS | WA3964033 | Unit 6 A23 toilet will not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 08:15:50 | 2021-02-09 11:10:00 | Fail | Replaced inlet valve and flexi
MSA-DCS | WA3964042 | kitchen bakers oven not heating up | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 08:22:44 | 2021-02-05 16:15:00 | Pass | completed 5/2/21
MSA-DCS | WA3964081 | Unit 6 B5 Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-19 12:40:00 | Fail | Replaced inlet valve and washers
MSA-DCS | WA3964187 | Unit 6 A11 toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-19 13:50:00 | Fail | Replaced button and button mechanism
MSA-DCS | WA3964262 | kitchen Cool room #7 display not showing temp coolroom remains cool at this stage | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 08:47:07 | 2021-02-05 12:23:09 | Pass | Arrived on site and signed in tools,checked over found controller siezed,picked up new controller return and replaced,tested controller all working ok.
MSA-DCS | WA3964263 | Unit 7 - A1 Self Care Cell --shower leaking overnight | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 16:30:00 | Pass | Nill
MSA-DCS | WA3964266 | Unit 14 - B16 tongue and spring of the personal lock has come free of door | Casuarina Prison | WSM-BR-SITE | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 05 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-16 12:00:00 | Fail | Unable to attend on time due to covid lockdownRequire parts.Replace mortise lock, install lock with rivnuts and m5 screws
MSA-DCS | WA3964325 | Unit 13, Cell D4- Toilet is leaking around the seals when flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-03-24 15:30:00 | Fail | Worked planned for 18/3 , unit has been vacated due to the new build so we cannot gain access without an escort, escort request sent on 17/3 waiting for date to be booked in by prison 24,3,19Replaced leaking pan and pipe work
MSA-DCS | WA3964332 | Unit 7, Cell H8- Tap leaking in cell | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 09:13:50 | 2021-02-09 12:15:00 | Fail | Replaced corroded and leaking tap
MSA-DCS | WA3964334 | Unit 7, G wing showers- Showers not turning off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 09:17:27 | 2021-02-08 14:40:00 | Fail | Replaced spindles and rewashed tap
MSA-DCS | WA3964515 | unit 1 D10 Cell call not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 13:26:51 | 2021-02-05 11:15:00 | Pass | Test full functions of cell call point D10, ok and operational. Job completed.
MSA-DCS | WA3964857 | SB2 (Between U17-U18)No Hot Water, the gas keeps shutting off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 09:41:53 | 2021-02-05 11:45:00 | Pass | Nill
MSA-DCS | WA3964868 | kitchen door lock on rational oven is broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-09 12:00:00 | Pass | Repairs to SCCWE door assy. Replaced door catch and door lock barrel assy. Ensure total door is adjusted down to doorseal properly. Test on cleanjet ok. Door lock smooth to operate & seals well. Tested by Tony - Chef.As advised due to previous issues with this No callout or Labour has been charged on this job.
MSA-DCS | WA3964897 | Jeelia, Rooms A1 & A3- shower drains blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-16 09:30:00 | Fail | Unblocked shower drain in cell A11 and A3
MSA-DCS | WA3964920 | education, class room 3 copper pipe leaking under sink | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-17 09:30:00 | Fail | Arrived on site and inspected found the cone tight leaking. Retighten the cone tight. Tested multiple times all working in order.
MSA-DCS | WA3964929 | jasper unit office water cooler leaking from nylon bolt | Banksia Hill Detention Centre | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 08:37:00 | Pass | Replaced 2 leaking fittings. All now working ok.
MSA-DCS | WA3964938 | Investigate ongoing issues with admin air con | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-05 14:00:00 | Pass | HVAC Technician (4/2/2021)Attended site, signed in and went through process of signing in toolingaccessed work area, and carried out an inspection & operational testing of the airconditioning system, took photos of areas of concernprovided report to Programmed FM
MSA-DCS | WA3964945 | Admin, Cleaning store- No hot water | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-16 09:47:00 | Fail | Rewashed hot tap
MSA-DCS | WA3964999 | Unit 2, Cell D4- Lighing is faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 13:00:00 | Fail | Repaired faulty lights in unit 2 d4
MSA-DCS | WA3965003 | Unit 6, C Wing Landing- First light is faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 08:30:00 | Fail | Investigate and repair unit 6 c wing landing light
MSA-DCS | WA3965320 | Gate House - Control Room Fire alarm faulty and continuing to sound in the POD,- see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 17:06:07 | 2021-02-22 10:21:00 | Fail | M1-16 odp flow switch causing intermittent alarm. Issue has been previously reported but no access due to construction site. Isolation has been removed. Construction now completed. Will required investigation with sprinkler fitter.Reattended site with fitter deisolated flow switch and there were no faults, waited for 20 mins still no fault so left online.
MSA-DCS | WA3965324 | Unit 14 - C2 shower drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-16 11:30:00 | Fail | Nill
MSA-DCS | WA3965332 | Number 6 washing machine is indicating low oil | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 13:17:20 | 2021-02-08 10:43:00 | Fail | Top up lubricating oil on WM#6
MSA-DCS | WA3965347 | control, internal perimiter MF zone 9 B constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 17:29:36 | 2021-02-05 16:00:00 | Pass | Rectified and fixed damaged connection, job completed.
MSA-DCS | WA3965348 | Boot shop - Workshop faulty power lead 3 phase to short - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 15:00:00 | Fail | Relocated 3 phase outlet in boot shop
MSA-DCS | WA3965350 | Bootshop- electrical fault back part of moulding machine keeps tripping out at beam when turned on | Casuarina Prison | WSM-BR-SITE | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 15:00:00 | Fail | Investigate and repair boot shop moulding machine tripping out
MSA-DCS | WA3965353 | Unit 10 C 8 Cell has water leaking into it possibly pipes in wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 13:31:02 | 2021-02-08 15:50:00 | Fail | Replaced faultyi inlet valve and flexi, adjusted pipe work to suit
MSA-DCS | WA3965360 | Unit 3, Cell A9- Drain in floor is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-11 12:30:00 | Pass | Nill
MSA-DCS | WA3965398 | Vegetable Prep - CL60 Machine is faulty, possible bearing issue | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-03-31 10:00:00 | Fail | Vegetable prep - CL60 Machine faulty. Check machine & controls. Remove for repairs. Dismantle, replace bearings & seal. Assemble & test. Return to store.
MSA-DCS | WA3965409 | Security office aircon not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 13:52:21 | Fail | Checked over system found filter blocked,picked up new one,returned to site and fitted.
MSA-DCS | WA3965449 | Unit 1 - B & D - Fire sprinkler has been damaged by a prisoner. - see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 18:50:35 | 2021-02-05 19:30:00 | Fail | 5/2/21BR & CW-attended site for broken sprinkler in unit 1 cell-investigated to find that sprinkler was live and had already been replaced overnight. Found out that maintenance person did not know about the leak and called us out without realising that it had already been fixed.-checked system and cleared fip alarm, normal
MSA-DCS | WA3965458 | Unit 13,cell B8- Key snapped in lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 19:01:35 | 2021-02-05 16:30:00 | Pass | Dismantle lock and remove broken key, reassemble lock.
MSA-DCS | WA3965516 | PDA System is not working. | Bandyup Prison-Entry Building-Ground Floor-Control Room | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 20:05:54 | 2021-02-05 21:00:00 | Fail | Attended site checked and found MDAS system not working properly. MDAS master computer is not running, slaver computer not accepting all user codes. Reboot both master and Slave computer. Tested all service back and running.
MSA-DFES | WA3965488 | Blinds in kitchen, SO Office and Training Room broken (see notes below) | CFRS Osborne Park | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 05 Feb 2021 | 2021-02-12 17:00:00 | 2021-05-19 11:16:00 | Fail | completed & Invoiced
MSA-DTAG | WA3964860 | Window in President’s Chamber above the driveway has a golf ball sized hole in the outer window | Perth Children's Court | GMP-BR-HO | Building | Windows (BU) | O'Brien Glass With Care | 1 | CLOSE | 05 Feb 2021 | 2021-02-06 09:45:15 | 2021-03-05 07:55:00 | Fail | job completed - Re-glaze single skin to double glazed unit with special high performance low e safety glass
MSA-DTAG | WA3965327 | Custody Faulty smoke detector in secure corridor leading to Court 3 stairs – Zone 9 | Supreme Court-Supreme Court Building-Basement | GMP-BR-HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Feb 2021 | 2021-02-05 17:13:54 | 2021-02-05 15:15:00 | Pass | Attended site and found device 1059 Az 9 disabled/alarm fitted new detector and reset okDe isolated Az 8,9,10 & 11 left panel normal.
MSA-DTWD | WA3964819 | K Block shed - Fluro lights faulty | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-09 10:30:00 | Pass | Located k block. Located faulty light fittings. Completed jsa. Isolated power and replaced light fittings. Tested all ok. Re energised, all ok. Completed paperwork. Signed out. Job complete.
MSA-DTWD | WA3965265 | Eco Playgroup external area to be sprayed for spiders | Joondalup Kendrew Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 05 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-10 06:30:00 | Pass | Sprayed external of playground, classroom, verandah's and fences
MSA-DCS | WA3965563 | Transit Cell 3.10-Cell call is not working | Roebourne Regional Prison-Prisoner Accommodation Unit 1 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Feb 2021 | 2021-02-07 09:53:11 | 2021-02-15 17:45:00 | Fail | Tested on site Unit 1 Cell 3.10 with officer and confirmed cell call point is working ok. Loud and clear both sides, call activated and reset correctly. Can’t see the problem.
MSA-DCS | WA3965676 | Unit 1- B Wing Close to cell 1-No Hot water to the shower | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-17 09:00:00 | Fail | Arrived on site and inspected hot water flowing. Tested multiple times all working in order.
MSA-DCS | WA3965682 | J ACCOMODATION- Broken pipe located in the communal toilet outside. | Banksia Hill Detention Centre-Block J Accommodation | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 06 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 15:05:00 | Pass | Replace a section of damaged pipe in the wall as well As the tap. Wall has been filled up withc concrete.
MSA-DFES | WA3965544 | Rear sliding gate is not working(not opening, slow to close) 15 MOore st | CFRS Perth | GMP-BR | Carpentry | Materials (CA) | Anvil Doors | 1 | CLOSE | 06 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-06 09:30:00 | Pass | Attended Perth Fire station call out for sliding gate. The gate was found to have one of the stops bent back that caused and issues with the closed limits. The stop has been repositioned The gate operation has been tested and is working as it should. Refer to the attached service reports.
MSA-DCA | WA3965753 | Gallery 14 high humidity alarm | Art Gallery of WA - James St | GMP-BR | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 14:07:25 | 2021-02-08 11:30:00 | Fail | After Hours Callout. Attended site. CG FCU 6 high humidity alarm. Reheat not controlling correctly via Dehum strategy. Inspected program. Made adjustments and monitored. Schneider to check out during next site visit. Alarms cleared.Checked conditions and logs since alarm on Sunday. Cleared. Closed job.
MSA-DCA | WA3965805 | leak from roof in spare parts, main theatre | Short Street Theatre-Main Building | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 07 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-23 13:57:00 | Fail | Replace section of box gutter on northern side of building. Seal all joins and outlets
MSA-DCS | WA3965740 | In control room no audio in the alarm | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 16:28:02 | 2021-02-07 14:00:00 | Pass | Attended site checked and found Gallagher workstation no audio alarm when alarm goes off. Also alarm lagging monitor of Indigovision not working properly when alarm goes off. Reboot Gallagher and Indigovision workstations and tested all working ok after work.
MSA-DCS | WA3965741 | Camera 161-is blury | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 12:31:37 | 2021-08-09 09:45:00 | Fail | Attended site, inspected camera 161 live view, image good.Inspected playback, image also good.
MSA-DCS | WA3965742 | Main control room Fire alarm fault -SUB FIP remand Zone 23 | Hakea Prison-Main Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 12:34:37 | 2021-02-22 10:17:00 | Fail | After hours call to Hakea Prison to panel faults. Found to be vesda low flow fault for units 6 & 7 adjusted setting to clear faults but many pipes flows getting low.Will require a return visit with two techs to check and clean all sample points in both units.Cleaning carried out
MSA-DCS | WA3965771 | In admin bldg mobile duress system is faulty sayo=ing receiver holding R4point 0 and Point 2 | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Feb 2021 | 2021-02-08 12:20:59 | 2021-02-16 11:30:00 | Fail | Checked and found MDAS receiver R.4.0.2 is water damaged. Replaced with new receiver and tested all ok after replacement. Bosch EA102A-304 X 1
MSA-DCS | WA3965785 | Unit 17 fire alarm is fault unable to clear | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Automatic Fire Protection (ARA) | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 17:32:40 | 2021-02-07 17:03:00 | Pass | Attended after hours to Casuarina for faults on MADS units in units 16 and 17 and found the following.Unit 16: found 15 MADS units disabled with 5 in flow fault. Enabled all detectors will require to re attend during normal hours to adjust units to try and clear fault.Unit 17: found two devices disabled one normal.Device in fault is a Wagner unit and will require interface module and 8 ft steps to access to find out fault.Possibly faulty detector.Site will be logging job to look at these faults on Monday during business hours
MSA-DCS | WA3965790 | Fire panel fault - alarm not resetting | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 2 | CLOSE | 07 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-09 11:00:00 | Pass | Contractors onsite repairing damaged fire hydrant
MSA-DCS | WA3965810 | Tamper alarm cannot be cleared which is taking out all prison cell call alarms | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Feb 2021 | 2021-02-08 00:55:58 | 2021-02-08 11:00:00 | Fail | delayed entry due to staff shortage, removed cell call from wall. noticed a lot of cockroaches in cell call. replaced cell call. cleaned out toothpaste from grill. reassembled. tested ok.
MSA-DCS | WA3969072 | Eyre Kitchen fan is running but no cooling | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 07 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-07 12:30:00 | Pass | Fixed ev b 01 and ev b 02
MSA-DFES | WA3965733 | water leaking through a light in the front fire fighters ensuite. Make safe light. | CFRS Osborne Park-Main Building | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 11:18:57 | 2021-02-16 16:15:00 | Fail | Returned to site and installed new light fitting. Site Rep Luke asked me to report that the replacement light does not completely cover the paintwork. He wanted this reported due to programmes inspection.
MSA-DFES | WA3965799 | under-croft carpark metal auto steel gate dislodged, hit by a car | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Materials (BU) | Go Doors | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 19:52:58 | 2021-02-08 12:35:00 | Fail | COMPLETED
MSA-DTWD | WA3965798 | Fire alarm going off in E-block | Joondalup Kendrew Campus | GMP-BR | Building | Materials (BU) | Critical Fire Protection & Training | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 19:39:17 | 2021-02-08 10:30:00 | Fail | Attended site - investigated FIP in alarm. Zone 2 and zone 3 were acknowledged. Alarm and strobe going off.Isolated code red and FIP.Investigated further by deisolating and checking every detector. No detector in alarm.No leaks to be found.Isolated zones and returned FIP to normal and code red. Further investigation needed by electrician.
MSA-MRWA | WA3965797 | Investigate and report, fire alarm activation. TECH TO CALL BRENDAN | Don Aitken Centre MRWA Head Office-Main Building | GMP-BR | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 07 Feb 2021 | 2021-02-07 19:39:01 | 2021-02-07 17:15:00 | Pass | Attended site after hours to Din Atkins Centre found two alarms on panelAz 3 Under ground car park found detector in alarm in bay 34 but car parked in bay. Was able to remove detector but unable to re fit newdetector as require clear accessMade good wiring reset and de isolated zone.As 4 Basement Centre in alarm since 31/10/19 as per tag on panel from Ara
MSA-DCA | WA3966087 | Main Building -No Phone line in the Lift -1is not working | Art Gallery of WA - James St | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 11:46:08 | 2021-02-08 15:34:00 | Fail | Lift 1 Art (large)-Geared :No incoming phone line possible sim fault, informed supervisor
MSA-DCA | WA3966127 | Main Building -Lift Motor room Door Lock broken Unable to access In L5 | Art Gallery of WA - James St | GMP-BR | Building | Materials (BU) | ADVANCED LOCK & KEY | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 11:52:58 | 2021-02-08 10:55:00 | Pass | Replace cylinder components & faulty mortice to plant room door lock
MSA-DCA | WA3966251 | Urban Orchard -Light pole to be repaired -Diffuser fallen off | Perth Cultural Centre Precinct-Urban Orchard-Ground Floor | GMP-BR | Electrical | Materials (EL) | Techworks Electrical | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 16:00:00 | Pass | Refix defused to light pole in urban orchard.
MSA-DCA | WA3966661 | Main entrance revolving doors - Door fault E20 please investigate | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 10:15:00 | Pass | Noted fault from staff as 26. Inspected and required to clean spider web from trailing leaf, belowsensor. Also adjusted sensors slightly. Checked water leaks with none found.
MSA-DCA | WA3966974 | Studio - water has penetrated light fitting, please make safe | Short Street Theatre-Main Building-Ground Floor-Cleaners Storage | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 14:08:56 | 2021-03-25 11:30:00 | Fail | Arrived on site at 1015. We didn’t get access to site until 1045. Located faulty light. Replaced faulty light with new. Advised staff of work completed.
MSA-DCA | WA3967203 | main Stage - Automatic fire door magnet will not hold | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Area | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 16:28:00 | Pass | King street fire door. Found relay controlling power supply to be 12volt relay on a 24volt supply. This relay was burnt out. Fitted new 24 volt relay. Tested ok.
MSA-DCA | WA3967241 | Plant Room- Smoke detector in fault (M2-82) | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 5-Roof Area | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 12:30:00 | Pass | Replaced base & detector M2-82Replaced detector M-120Replaced detector M3-61
MSA-DCA | WA3967283 | Ross Chadwick’s office Faulty light switch to be replaced. Please see notes. | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 10:30:00 | Pass | Replaced faulty light switch for a new switch
MSA-DCS | WA3965943 | LEVEL 4-One of the blinds has fallen down. Located near Annas work station. | East Perth-Main Building-Level 4 | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 08 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-08 10:00:00 | Pass | Attended site and carried out repairs to level 4 blind that had fallen down.
MSA-DCS | WA3965963 | Lenard, C Wing- Smashed window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 08 Feb 2021 | 2021-02-10 17:00:00 | 2021-03-03 12:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3965973 | Gatehouse - PTZ 3 and PTZ 7 cameras are not responding, unable to get any image on the camera. | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 11:36:05 | 2021-02-08 09:45:00 | Pass | PTZ 2 , PTZ 3 and PTZ 7 has been decommissioned and replaced with new AXIS PTZ IP cameras.
MSA-DCS | WA3966212 | Unit 1 - Main fire panel smoke alarm is coming up as a fault on main fire panel. | Karnet Prison Farm-Administration, Stores Dairy Office | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 07:57:37 | 2021-02-09 07:11:00 | Pass | 9/2/21 MBReplaced faulty detector in Unit 1 SO’s Office (L1 S32). De-isolated and returned system to normal working order.
MSA-DCS | WA3966404 | Bandyup Unit 3 Cell M5 bedside light in cell not working | Bandyup Prison-Unit 3 Crisis Care Unit-Ground Floor-Cell 5 - Crisis | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-22 12:30:00 | Fail | No Fault Found
MSA-DCS | WA3966443 | kitchen Dishwasher emmited a loud bang on filling and a noticable smell of electrical burning-notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 12:21:38 | 2021-02-08 16:00:00 | Fail | Repaired dishwasher
MSA-DCS | WA3966445 | Laundry- Roof Leaks over A/C 2 and 3 | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 08:27:23 | 2021-05-25 10:00:00 | Fail | TO RECTIFY LEAK - REMOVED FLASHINGS AND RUSTED METAL PAN FLASHINGS. REPLACD/INSTALL NEW MULTIPLE UNITS
MSA-DCS | WA3966483 | Unit 2, A wing day room vents leaking water onto tables. | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 08:29:06 | 2021-02-11 08:00:00 | Fail | Attended site twice and denied access, closing with cost to date. If it leaks again a new job will need to be raised.
MSA-DCS | WA3966484 | Video link Water filtration unit not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 08:29:04 | 2021-02-08 13:44:00 | Pass | Filter locked out. Changed filter, captured asset and allowed up to temp. All working ok.
MSA-DCS | WA3966564 | Unit 3, Cell A12 - Roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-03-04 10:15:00 | Fail | sealed roof penetration and checked roof area to see where getting in. lifted flashing and replaced. no other signs of water ingress
MSA-DCS | WA3966605 | Sallyport - flood light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-10 13:30:00 | Pass | Investigate and repair sally port lights
MSA-DCS | WA3966646 | Kitchen - bun machine leaking oil | Karnet Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-17 13:10:00 | Fail | COMPLETED 17/2/21
MSA-DCS | WA3966652 | Kitchen- large mixer not working correctly | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-17 12:10:00 | Fail | COMPLETEDC 17/2 NO TRAVEL COSTS AS ATTENDED SITE AT THE SAME TIME FOR ANOTHER JOB.
MSA-DCS | WA3966656 | Reception - front flood light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 08:30:00 | Pass | Investigate and repair reception flood light
MSA-DCS | WA3966667 | unit 6 N6 Light switch in cell needs repair | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 08:52:50 | 2021-02-08 13:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3966668 | Unit 6, Cell A4- Window in cell not operational, cant be open/lifted | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-03-03 10:30:00 | Fail | SPIRAL BALANCES RE NEWED
MSA-DCS | WA3966671 | Unit 1 C16 Main lock is not functioning correctly, some keys are unable to operate the mechanism | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 12:57:52 | 2021-02-08 10:30:00 | Pass | Onsite, replaced thrower due to wear.
MSA-DCS | WA3966672 | Karakin - Entry pedestrian gate- lock is jamming on occasions | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-15 09:30:00 | Fail | Attend site, replace faulty lock.
MSA-DCS | WA3966673 | Unit 2 - B Wing Cell 3 Toilet not flushing properly, not blocked just wont flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 08:58:30 | 2021-02-08 13:55:00 | Pass | Nill
MSA-DCS | WA3966675 | Bandyup Assessments Unit - light circuits keep tripping out | Bandyup Prison-Assessments | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 08:49:58 | 2021-02-08 15:00:00 | Pass | Investigate possible water leak on lighting circuit, unable to investigate fully due to poor ceiling access, suggest roof plumber investigate for leak before proceeding with cutting access holes in ceiling to investigate further.
MSA-DCS | WA3966677 | Unit 6 D9 Light in cell not working needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 09:02:20 | 2021-02-08 12:30:00 | Pass | Repaired light
MSA-DCS | WA3966682 | Laundry - No power to number 2 washing machine, can a check of main fuse be done | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 13:06:10 | 2021-02-08 11:30:00 | Pass | No washing machine power
MSA-DCS | WA3966723 | Unit 14, Cell B4- Tap leaking in sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-16 12:30:00 | Fail | Nill
MSA-DCS | WA3966731 | OBs Post 5 - Orange coloured switch board 2/3 up stair case Sound like trip switches try to go off | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 09:13:00 | 2021-02-08 15:00:00 | Pass | Checked switch board contractors function all operational with no noise, checked connections all ok.
MSA-DCS | WA3966732 | Unit 14- Tap in Dayroom constantly leaking on B/D side. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-16 13:30:00 | Fail | Nill
MSA-DCS | WA3966772 | Unit 14, Cell 5- shower is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-16 14:30:00 | Fail | Nill
MSA-DCS | WA3966776 | Unit 4 control room - Aircon has water leaking into control room - see notes | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 09:14:28 | 2021-02-09 09:00:00 | Pass | Found air leaking where pipes entered indoor unit in roof space causing condensation. . Sealed gap. Tested drain. All ok.
MSA-DCS | WA3966778 | light in the female toilet is not working in the admin area | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-09 12:00:00 | Pass | Repaired light
MSA-DCS | WA3966781 | Unit 2, Cell A2- Broken light switch for personal light top bunk | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-15 11:30:00 | Fail | Repaired damaged lights switch in unit 2 a2
MSA-DCS | WA3966829 | Unit 2, Broken window chain A/C dayroom. | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 12:30:00 | Pass | WINDOW WINDER REPLACED AND SECURED
MSA-DCS | WA3966872 | Unit 3, Cell A3- Window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-18 12:00:00 | Fail | NEW WINDOW BALANCERS FITTED
MSA-DCS | WA3966915 | Unit 2, Cell D2- Window does not hold up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 11:00:00 | Pass | SPIRAL BALANCES RE NEWED
MSA-DCS | WA3966919 | The B/D shower Ventilation - shower ventilation was damaged during the Incident | Casuarina Prison | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 09:29:04 | 2021-02-24 11:07:28 | Fail | Arrived on site and signed in tools,removed capping on open duct,fit new section and seal.
MSA-DCS | WA3966922 | Unit 13, Cell A4- No water from sink tap & shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 15:30:00 | Pass | Nill
MSA-DCS | WA3966925 | Unit 1, A wing shower head blocked (shower closest to entry) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-10 16:30:00 | Pass | Nill
MSA-DCS | WA3966929 | Cell A 08 in Unit 13 has a leaking tap in the sink, constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 16:30:00 | Pass | Nill
MSA-DCS | WA3966955 | PA handset faulty unit 2 officer station | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-19 12:00:00 | Fail | Unit 2 handset intermittently working and damaged mounting. Replaced as handset is faulty and mounting damaged.1x CG-OH Handset
MSA-DCS | WA3966978 | Zone 24 -Perimeter light pole has damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 09:06:42 | 2021-02-08 15:00:00 | Pass | Investigate and repair damaged perimeter light pole
MSA-DCS | WA3967000 | Leaking window in the main kitchen. | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-07-05 14:45:00 | Fail | roof repairs made
MSA-DCS | WA3967004 | Unit 3, Cell C1- Strike plate is damaged | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 10:36:56 | 2021-02-08 15:00:00 | Pass | Replace door plate, lock and weld on strike.
MSA-DCS | WA3967006 | Unit 14, Cell B4- Light blast faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-17 10:30:00 | Fail | Repaired damaged lights and switch in unit 14 b4
MSA-DCS | WA3967009 | Unit 4 - B4 - catch plate faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-16 11:00:00 | Fail | Unable to attend on time due to covid lockdown.Require parts.Weld plate to frame over existing damaged frame. Weld on strike plate.
MSA-DCS | WA3967012 | Laundry - water leak from roof near lunch room | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA3967015 | Repair Hot/coldKimberley Kitchen - Repair Hot/cold mixer t mixer tap in small kitchen as It's loose. | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 21:30:00 | Pass | Tightened up mixer tap
MSA-DCS | WA3967018 | Automatic security door located main gatehouse entry has issues with Electronic Strike | Roebourne Regional Prison | SPA-BR | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-11 17:00:00 | Pass | Attend site, rectify alignment issue with gatehouse front door. Replace electric strike on Senior officers door in gatehouse.
MSA-DCS | WA3967029 | Unit 6, B Wing grill not operating | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 10:59:39 | 2021-02-08 15:30:00 | Pass | Checked operation of control console buttons and confirmed operation of associated relay. Unlocked mechanical lock on grill and engaged drive motor. Tested operation of drive from motor location. Tested grill operation from unit control room. Grill functioning correctly.
MSA-DCS | WA3967030 | Level 4, Male showers - light not working | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 09:45:00 | Pass | Replaced failed lamp in level 4 male shower.
MSA-DCS | WA3967059 | Laundry - washing machine has gone down | Bandyup Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 11:21:54 | 2021-02-09 11:26:00 | Fail | No power on display. Checked machine all ok. Customer to call if needed again
MSA-DCS | WA3967063 | Unit 5, house 4 - WC flushing Mech faulty not the inlet valve | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-17 13:30:00 | Fail | Arrived on site and inspected found the the outlet valve broken. Collected parts from supplier and returned to the site. Removed the faulty outlet valve and replaced with new outlet valve. Tested multiple times all working in order.
MSA-DCS | WA3967066 | Unit 5, house 4 - Bath hot water tap faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-03-24 11:00:00 | Fail | Arrived on site and inspected found the hot spindle broken. Need parts. Installed the plug in the hot and cold taps. Will come back once we get the parts Collected parts from supplier and returned to the site. Replaced the hot and cold spindles Tested all working good
MSA-DCS | WA3967085 | unit 3 D5 Water leaking from ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 11:34:56 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA3967086 | Laundry - Number 2 washing machine blowing fuses | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 11:32:25 | 2021-02-11 09:45:00 | Fail | 09/02/21 - The drain valve is faulty causing the fuse to blow. Needs new drain valve.11/02/21 - Replaced WM2 drain valve and 3.15 Amp fuse. Test ok.
MSA-DCS | WA3967087 | Pedestrian gate is not closing correctly & buzzer not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 15:37:42 | 2021-02-09 08:30:00 | Fail | Replaced lock and 24v Buzzer.Parts Used.1 ES9000 Lockwood lock1 24 v Buzzer
MSA-DCS | WA3967090 | unit 2 A/B wing, Kitchen - Hot water Urn leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 11:43:39 | 2021-02-09 10:14:00 | Pass | Replaced tap
MSA-DCS | WA3967178 | unit 2 Cell 2B cell call prisoners cannot hear operater | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 13:08:03 | 2021-02-09 11:00:00 | Pass | Attended site and investigated the fault.Checked Input on CI-8 board and connections.Found that cell call intercom is faulty (end of life) and replaced with new CellGuard CI-CC and RJ45 Adapter( supplied by SEME).Used sundries.Conducted test.All back to normal and operational
MSA-DCS | WA3967184 | Unit 10 - Front entry door closure not closing properly | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 13:18:13 | 2021-02-09 14:30:00 | Fail | Advised to close off job cost to date, temp closer installed. SITE TOOK TO LONG TO DECIDE IF THEY WANTED A NEW PERMENANET ONE INSTALLED. SEEM HAPPY WITH TEMP ONE. THEY CAN ALWAYS RE ISSUE A NEW JOB IF THEY WANT A PROPER ONE
MSA-DCS | WA3967196 | Unit 15 - alarms are disabled on the fire panel, | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 13:31:19 | 2021-02-08 15:46:00 | Pass | 8/02/21 EI/JGAttended site cleared unit 15 sample points in cells A7 & B12.Reset MASD OK.System status displaying normal on departure.
MSA-DCS | WA3967200 | external to fence line ajacent to staff houses - has been run over and leaking water alot | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 17:35:41 | 2021-02-09 15:30:00 | Fail | Repair damaged fire hydrant, used excavator
MSA-DCS | WA3967204 | Kaartdijin Mia - C3 - classroom door faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-03-05 14:00:00 | Fail | Temp. repair barrel.Replace barrel and install offset strike and adjust to suit.
MSA-DCS | WA3967252 | Gate control , main prison - Wireless keyboard for security camera monitor not working. | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 11:30:00 | Pass | Attended site and investigated the fault.Found that wireless keyboard for CCTV monitors is faulty and requires replacement.Replaced with critical spare from site.Tested.All ok at departure.
MSA-DCS | WA3967261 | Unit 2 Cell B2 sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 10:38:00 | Fail | Replaces spindles to basin taps
MSA-DCS | WA3967265 | Unit 2 Cell B-8 Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 11:13:00 | Fail | Replaced spindles to basin taps
MSA-DCS | WA3967266 | Unit 2 Cell B9 sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 11:35:00 | Fail | Replaced spindles to basin taps
MSA-DCS | WA3967267 | Unit 2 Cell B5 sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 12:45:00 | Fail | Replaced spindles to basin taps
MSA-DCS | WA3967269 | Unit 2 Cell B5 shower taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 14:10:00 | Fail | Replaced spindles to shower taps
MSA-DCS | WA3967271 | Unit 2 Cell A14 shower taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 13:35:00 | Fail | Replaced spindles to shower taps
MSA-DCS | WA3967296 | Unit 7, control room - cell call alarm continuously alarming/network fault | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 16:28:02 | 2021-02-08 17:00:00 | Pass | Cell call Tamper alarm caused by damage to circuit board on Cell call unit in cell 13B10. Damage from cockroach excerpts. Many cockroaches observed when cell call removed. Replaced cell call PCBandcleaned tooth pasted from behind the speaker grill. Tested cell call to local control, good audio both ways. Note: delayed getting access to cell due to staff operational requirements.
MSA-DCS | WA3967303 | gas HWs is not working in the dairy section | Karnet Prison Farm | SPA-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-03-19 16:00:00 | Fail | Replaced hwu
MSA-DCS | WA3967304 | Battery back up for Camera #22 the expander is starting to fail. | Albany Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-03-03 18:30:00 | Fail | Attended Camera EC outside external perimeter, checked power supply voltage (13.8vdc) ok. Confirmed terminals on power supply and battery were secure. Returned to gate control, ran report on Gallagher activity. Only significant activity (Power Fail Alarms) occurred between 17:28 andu 18:46hrs on 08/02/2021. No further action taken.
MSA-DFES | WA3966917 | Workshop Amenities ground dinning room - Door latch mechanism is damaged | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-12 12:15:00 | Fail | Door handle hardware has been replaced
MSA-DFES | WA3966970 | Level 2 Soffit Leak in The wellness area | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 12:45:00 | Pass | Contacted Michelle from programmed regarding issue. recommend building contractor to investigate issue as believe water proofing issue with slab and windows onsite. Michelle raising work order for building contractor to attend.
MSA-DFES | WA3967003 | Outside of the building : Human excreta -Requires cleaning | DFES Education and Heritage Centre | GMP-BR | Cleaning | Hazardous Materials (CL) | Facilities First Australia Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 12:23:00 | Pass | Work completed as requested on 8th February 2021
MSA-DFES | WA3967021 | The kitchen door reader is not working can't get access | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Doors (BU) | SONTEC WA PTY LTD | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 15:00:00 | Pass | Ryan - 8/2/2021 - Checked kitchen reader, found reader only responding to receptionist access card. power cycled cardreader and tested, all cards workingtested all onsite card readers, all onsite readers working.
MSA-DFES | WA3967107 | 2nd floor, Mens toilet 4th cubicle in, Blocked toilet | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 13:45:00 | Pass | Investigate blocked toilet located level 2 men’s toilet Attempt to locate inspection or duct, investigate cause of blockage and remove issue Flush multiple times and plunge, once cleared paper test, blockage caused by paper hand towels Pack up and clean up worksite
MSA-DFES | WA3967229 | Fire fighters Ensuite Room #5 front bedroom has a roof leak | CFRS Osborne Park | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 08:30:00 | Pass | Investigated roof leak, found vent cause of leak. Cleaned back and re-sealed
MSA-DFES | WA3967248 | ground floor fire panel zone 1 showing fault ground sth carpark - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-12 07:20:00 | Fail | L1d96 zone 1 intermittent fault (f07)Cleaned detector head as no stock available.Recommend replace detector headRequires 1x FAPT-851AUSDetector located in car park adj bat 17
MSA-DFES | WA3967260 | Male FF shower and toilet both exhaust fans faulty | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 14:30:00 | Pass | Complete
MSA-DFES | WA3967263 | front yard Paving walkway at front of station has collapsed - see notes | CFRS Claremont | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 09:45:00 | Pass | Investigate sunken pavers / possible water leak ; after lifting pavers and excavating area found the edge of 1800 soakwell , believe water from the heavy rains on the weekend washed the sand away .Backfilled hole and reinstated pavers . If problem re occurs camera inspection of soakwell maybe required .
MSA-DFES | WA3967268 | ground FF study room 13 extractor fan squealing noise when operated | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 15:00:00 | Pass | Complete
MSA-DFES | WA3967286 | Level 1, RCR PAO outside - light attached to gym shed, facing crash rescue Pad | VFRS Falcon | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 11:15:00 | Pass | Located broken floodlight on shed. Light was beyond repair to we collected a replacement and installed As new.
MSA-DFES | WA3967288 | Engine Bay - Leak and ceiling damage in change room 2 | FESA RHQ - Forrestfield | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-03-05 17:00:00 | Fail | On attendance to site it was noted that the leak was coming from water pipes.Protek sent a plumber out to site to investigate and found two leaks in the pipe work requiring repairs. These repairs were completed to stop water leak.Once plumbing works were completed, then the ceiling required to be repaired due to finding the leaks and damage that had been caused by the water leaks.Ceiling were repaired and painted to match existing ceiling white.
MSA-DTAG | WA3965971 | Custody - Faulty smoke detector in secure corridor adjacent to interview rooms – Zone 9 | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 08 Feb 2021 | 2021-02-08 11:37:01 | 2021-02-08 09:12:00 | Pass | Problem was not caused by faulty detector.Two isolated detectors in Z9 activated on Friday night between 10 and 11pm due to works being out by other contractors in Custody area. Checked detectors @ L1 S50 and 51, all now showing normal analog values and area clean.De-isolated Z9 and left system in normal working order.
MSA-DTWD | WA3965934 | B Block, Male toilet- Urinal is blocked | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-08 16:15:00 | Pass | Arrived on site and inspected found the b block level 2 male urinal trout blocked and over flowing in the male toilet. Used plunger and sprites of salt to clear the blockage. Flushed water and cleaned up the site
MSA-DTWD | WA3965955 | D Block, Plant Room- Black Water Recycling Pump in Alarm | East Perth Campus | GMP-BR | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 08 Feb 2021 | 2021-02-08 17:00:00 | 2021-02-08 12:06:00 | Pass | Fault finding to find issue with pump skid not working. RDC's had tripped due to storm and solenoid had a rock inside preventing from opening.RCD - TrippedSolenoid - Failed to openWatercon employee attended site 08.02.2021
MSA-DTWD | WA3966658 | B block ground B04/B07 Damaged external window glass. | Midland Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-03-05 09:15:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSMADE SAFE 2 LARGE BROKEN PANELS6.38 CLEAR LAMINATED SAFETY GLASS1-915 X 466, 1-920 X 770SAFETY FILM USED 2-1000 X 1000PLUS SILICONERETURNED LATER DATE TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-1640 X 9601-1640 X 1000PLUS SILICONE2 MEN REQUIRED
MSA-DTWD | WA3966663 | C block ground C31 Corridor Damaged external glass in doors. | Midland Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 16:30:00 | Pass | ATTENDED SITEREGLAZED 2 BROKEN DOOR PANELS & HILITE PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-990 X 7441-703 X 7441-483 X 8739.1 L/M OF RUBBER REPLACED
MSA-DTWD | WA3966773 | Recall WA3950841: A block L1 A114 no power to all lights in the room | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 15:00:00 | Pass | Attended site and found hard active that I connected to previously no longer has power and suspected to be switch from a separate BMS system. Found new hard active that is not connected to old BMS system and re-designed switching operation.No charge applied - re-attended and rectified issue
MSA-DTWD | WA3966784 | Canteen - Pin hole leak in HW ceiling ring main | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 10:45:00 | Pass | Inspected, no plumbing fault found
MSA-DTWD | WA3966932 | roof leaking in room 8006 | Naval Base | GMP-BR | Roofing | Rooflights and Skylights (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-15 15:00:00 | Fail | Sealed around dektites on roof.Contacted client and agreed to close out the job due to no rain forecast for the near future.
MSA-DTWD | WA3966935 | Passage lights are not working | Mount Lawley Campus-Block A-North Wing-Level 1-N 116 - Corridor | GMP-BR | Electrical | Materials (EL) | AWB Co. | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 12:29:00 | Pass | Repalced faulty fluro,starter,ballasts and light switch to lights in passage.job completed
MSA-DTWD | WA3966936 | smoke alarm is keeps going off in room D003, D006 | Naval Base | GMP-BR | Building | Materials (BU) | AWB Co. | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 13:15:00 | Pass | Attended site and signed in. Located D block on site. Found smoke alarms in each room. Tested and checked smoke alarms and found all to be out of compliance. Some flat batteries also. Disconnect and removed faulty smoke alarms. Supply and replace with new smoke alarms throughout. Checked all interconnected to each other. Signed out. Job complete
MSA-DTWD | WA3966979 | A block ground ladies toilet west ladies toilet 1st cubicle burst water resirvoir, isolated in duct | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 15:15:00 | Pass | Arrived on site and inspected found the no 1 cubicle inlet valve broken and leaking from pan collar. Collected parts from supplier and returned to the site. Replaced the faulty inlet valve and flex hose. Removed the faulty rubber from the pan collar and closed the pan collar with pan seal wax. Tested multiple times all working in order.
MSA-DTWD | WA3966982 | Replace faulty batten flouro with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 08:30:00 | Pass | Attended site and signed in. Found facilites and asked about the problem. Investigated light fitting that has fallen down. Found fitting to decided it no longer wanted to be of the ceiling batten and fell down. Cable is safe and still terminated to outlet. Light in that corner not required as new hi bay has been installed. Advised that we will need to tidy up that cable. Site has advised to close job and over next school holidays we will get a ewp in and repair a couple of faulty lights and use ewp to access to cable over welding bay. Job complete
MSA-DTWD | WA3966991 | B Block (electrical) - Passageway roof leak between B15 & B14 | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 13:36:00 | Pass | Clear roof of debris around leak area.Works were on hold to see if this had resolved the roof leak. As we are not expecting rain in the near future, it has been decided this job be closed off at this time.
MSA-DTWD | WA3967039 | D Block, Classroom D20 - Roof Leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-18 11:30:00 | Fail | Replace rusted roof sheet to d block
MSA-DTWD | WA3967092 | T block T032 Staff amenities - Zippy Hot water not working/ flowing | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 13:16:00 | Pass | Replaced faulty pump which rectified issue. Alspmreplaced PLV as virtually completely blocked and not allowing much water through
MSA-DTWD | WA3967108 | building 10, 10F89/90/91 and 94 - no lights in 4 vlassrooms | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-03-11 08:00:00 | Fail | Attended site and signed in. Located switchboard with temporary main switch. Isolated switchboard. Disconnect and removed temporary main switch. Supply and replaced original main switch with new. Tested all okay. Reinstated power. Signed out. Job complete
MSA-DTWD | WA3967129 | E block ground E57 male toilet not flushing | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 13:15:00 | Pass | Arrived on site and inspected the male toilet working fine. Tested multiple times could mot find any blockage. Found the urinal blocked. Used plunger and sprites of salt to clear the blockage. Flushed with hot water. Tested multiple times all working in order. Material used - sprites of salt-2 lts
MSA-DTWD | WA3967187 | Lvl 1, Entrance of building on Newcastle street- Damage ceiling panel (potenial OSH issues) | Perth Campus B4 | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-03-18 13:00:00 | Fail | Replace Eave sheets in front of Entrance as per scope on BRAF
MSA-DTWD | WA3967190 | H block and surrounding sheds horticulture spiders to be sprayed- see notes | Mandurah Campus (formerly Peel) | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 07:15:00 | Pass | Indoor spider control
MSA-DTWD | WA3967193 | Billi hot and chilled water not working | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 10:25:00 | Pass | Unit operational on arrival. Complete check over. Also put unit into “locked on” at clients request. Client on site wouldn’t sign. Said needs to be maintenanace manager located 30mins drive away.
MSA-DTWD | WA3967220 | B block BG25 Broken 10A GPO - see notes | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 11:15:00 | Pass | Attended site, signed in,spoke to fm about job, completed jsa, went to wholesaler to pick up materials, returned to site, spoke with lecturers to let them know I was isolating power , isolated power, removed old gpo, installed new gpo, re energised the circuit , tested gpo , working as intended, cleaned up the work area, completed paperwork, signed out ***job completed ***
MSA-DTWD | WA3967230 | R block R021 air con not turning on | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-10 09:00:00 | Fail | Accessed unit and part fault rectified.Unit now operational to thermostat temp control. Evap fan, compressor and condensing fan tested and operating as desired. Facilities manager notified of repair and room now usable
MSA-DTWD | WA3967237 | block 10 L1 Isolating lock on disabled toilet door not working. | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-10 11:00:00 | Fail | Block 10 - L1 - disabled toilet locks are faulty.Locks repaired.
MSA-DTWD | WA3967245 | A Block, Room A314 - Air Con Burnt motor smell | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 13:30:00 | Pass | Investigated reported burning smell. Smell no longerpresent as was detected the day prior and since ceased.Checked ventilation and electrical. Ok. Informed labtechnician to report immediately if problem reoccurs.
MSA-DTWD | WA3967247 | Cafe L2, 25Ab Cafe oil fryer leaking oil | Perth Campus B1 | GMP-BR | Equipment | Catering Equipment (EQ) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-19 15:55:00 | Fail | Install new fryer
MSA-DTWD | WA3967249 | E block, E200 - repair blinds fallen down from fixing E200 | Mount Lawley Campus | GMP-BR | Building | Curtains & Blinds (BU) | AWB Co. | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-17 15:45:00 | Fail | Repair blind
MSA-DTWD | WA3967255 | T Block, Entrance- Drink fountain leaking | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-09 11:00:00 | Pass | Arrived on site and inspected found the elbow broken and leaking. Collected parts from supplier and returned to site. Replaced the faulty part. Reconnected water and tested all working good.
MSA-DTWD | WA3967259 | S4 - Gas tap in fume cupboard appears to be broken. Potential leak | Murdoch Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 08 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-09 14:51:00 | Pass | Re tighten and service gas tap
MSA-DTWD | WA3967289 | E block, Roof Leak – ET02 Water coming down wall & and water leaking to floor below inside EG02 | Carlisle Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 13:30:00 | Pass | Heavy leaf debris has clogged both downpipes. Cleaned out leaves from gutter.
MSA-DTWD | WA3967295 | E block - Water roof leak, E58 east end coming through exit light | Bentley Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 10:30:00 | Pass | Roof inspection to find leak in E58. Clean old silicone off and Silicone seal to flashing joins, screws and dektites
MSA-MRWA | WA3967027 | Laboratory/office - air-conditioned is not switching on | Materials Engineering Branch-Metrology-First Floor-Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 08 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-09 12:30:00 | Pass | Attended site. Signed in on promaps. Carried out site induction. Checked over asphalt lab as shown by site contact. Found main circuit breaker tripped. Compressor is down to earth. Will need to be replaced. Gathered information and will prepare quote. Upon leaving seen Craig from programmed was advised that it was the met lab that had the faulty air con. Found main circuit breaker to be trip. Investigated package unit and found a comp overload to be tripped on stage 1. Reset to test. Found compressor to be seized. Attached gauges to check pressures and confirm. Checked across the phases all ok. Amps will climb as comp ran causing it to trip. Isolated stage 1. Recorded details and will submit quote. Quote approved new job raised to carry out works.
MSA-MRWA | WA3967033 | male toilet cistern leaking | Jandakot Depot-Main Building-Ground Floor-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Feb 2021 | 2021-02-09 17:00:00 | 2021-02-08 14:56:00 | Pass | Replaced leaking outlet washer to cistern in male toilet.
MSA-DCA | WA3967720 | Ant infestation around the Makigawa statue | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-17 08:00:00 | Fail | Allpest completed works 17.02.2021
MSA-DCA | WA3967952 | Breezeway leading to staff car park - Hinge on Large wooden breezeway door has is off door frame | Shipwreck Galleries-Main Building | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-12 14:45:00 | Fail | Job to be closed off due to extensive remedial works required.Job to be quoted on replacement of both door frames.
MSA-DCA | WA3968070 | Half flush button in cubicle stuck in-photo to follow in email | State Library of WA-Main Building-Ground Floor-Female Toilets - Rear Entrance Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-11 15:00:00 | Pass | Replaced faulty bellows
MSA-DCA | WA3968074 | Tap broken at one of the sinks – handle came off - photo to follow in email | State Library of WA-Main Building-Ground Floor-Female Toilets | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-04 13:25:00 | Fail | Replaced sink mixer
MSA-DCA | WA3968080 | M11 Tap at sink has to be turned off really firmly and keeps dripping | State Library of WA-Main Building-Mezzanine | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-11 15:35:00 | Pass | replaced washers
MSA-DCA | WA3968085 | Staff men’s bathroom Blocked urinal | State Library of WA-Main Building-Level 4-4.10. - Male Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-11 14:20:00 | Pass | Unbocked urinal
MSA-DCS | WA3967407 | Zone 9 inner and Zone 11 outer fence alarm is constantly activating, unable to clear it. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 05:43:50 | 2021-03-16 11:30:00 | Fail | Replaced damaged cable and re calibrate,job completed.
MSA-DCS | WA3967511 | Unit 6, Strip light hanging down from ceiling on A wing landing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 07:21:25 | 2021-02-09 12:00:00 | Pass | Repaired damaged lights in unit 6. Waited access to wing
MSA-DCS | WA3967517 | Perimeter trax alarms SM17 & SM07 | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 07:49:46 | 2021-02-10 15:47:00 | Fail | Investigated fault, used recycled parts to fault find this old obsolete system as new parts are no longer available. Repaired multiple faults and tested OK.Job Complete
MSA-DCS | WA3967532 | Assessments- Roof leak causing power to trip, see notes | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Schlager Construction Group | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 07:52:59 | 2021-02-10 15:00:00 | Fail | Carried roof inspection and sealed all penetrations.
MSA-DCS | WA3967569 | Numerous perimeter lights are out | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-10 08:00:00 | Pass | Repairs to perimeter lights
MSA-DCS | WA3967577 | Gate Control Main Prison- no audio alarms on PRU computer | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 08:56:08 | 2021-02-09 13:00:00 | Pass | Attended site and investigated the fault.Checked audio ports on work station and monitor.Checked cable.Restarted Gallagher work station 3 and conducted test.All back to normal and operational
MSA-DCS | WA3967586 | Unit 15 - C12 Personal key for C12 Mallee snapped off.Half of the key is still inside the lock. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 09 Feb 2021 | 2021-02-09 13:03:41 | 2021-02-09 11:30:00 | Pass | Dismantle barrel, remove broken key, reassemble barrel.
MSA-DCS | WA3967696 | SB2 (Between U17-U18) - Toilet- toile roll has been pushed into toilet blocking it | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 10:43:46 | 2021-02-11 09:51:00 | Fail | Nill
MSA-DCS | WA3967889 | Unit 2, cell C36 - door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 11:00:00 | Pass | Attend site, service and repair faulty door lock for correct operation.Date on site: 12/02/2021Time on site:10:30am - 11:00am
MSA-DCS | WA3967899 | unit 4 cell D13 - bathroom door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 10:30:00 | Pass | Attend site, replace damaged / broken external handle to D 13 bathroom, and replace internal components to lock for correct operation.Date on site: 12/02/2021Time on site: 09:30am - 10:30am
MSA-DCS | WA3967903 | unit 2 lower landing - toilet cistern leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-09 13:00:00 | Pass | replaced flush cone from cistern to pan. And collect materials for various job for the day
MSA-DCS | WA3967994 | Main Kitchen - Data point D11 is having connectivity issues | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-25 13:00:00 | Fail | Attended site.Replaced faulty network modular socket with new - supplied by SEME.Tested.All ok at departure
MSA-DCS | WA3968016 | Investigate faulty light fixtures/poles in front of Unit 2 | Casuarina Prison | SPA-BR | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-31 15:00:00 | Fail | Replace poles, pole lights, redirect/replace base conduits etc.
MSA-DCS | WA3968031 | Boiler house Boiler feed water tank has a steam leak | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 13:46:32 | 2021-02-12 14:00:00 | Fail | Repair leak on tank fittings.
MSA-DCS | WA3968041 | Unit 7 H12 Light switch outside cell broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 13:58:37 | 2021-02-10 10:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3968061 | Assessments, rear kitchen - water dripping in leaking roof near corridor area | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 14:21:04 | 2021-06-29 11:00:00 | Fail | REPAIR BOX GUTTER AND ROOF PENETRATION, REPAIR FLASHINGS AND CLEAN ROOF DEBRIS
MSA-DCS | WA3968189 | Perimeter Fence - Lights 26, 28, 30 (A & B), 27B - not working | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 02:42:27 | 2021-02-10 00:00:00 | Pass | * Phone support *Contacted site and found that PDS and CCTV systems are operational.Required attendance by electrical contractor to rectify problem with perimeter lights.
MSA-DFES | WA3967603 | Excerise Development office next to main entrance A/C is not working correctly | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Ducted Split System (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-22 11:00:00 | Fail | Attend site. Access plantroom and check room temps. Found room temp to be 22.8 degrees. Check with staff and they say its better but still warm in the morning and cool in the afternoon. Adjust louvers on outlets to help with the air direction. Slightly adjust setpoint lower by .1 of a degree. Face bypass is working correctly. Unit is cooling correctly.
MSA-DFES | WA3967669 | ground Stair 4 External Door and other Stairwell external doors, 3, 2 and 5 - damaged see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 14:00:00 | Pass | D4 tighten screws to anti tamper plate over lock mechanism and to bottom seal. Adjust door closer speed. D2 adjust door closer speed and remove sand build up under threshold plate. D3 & D5 inspect only. No adjustments required.
MSA-DFES | WA3967673 | Many of the vertical blinds have sections missing & draw cords don't work (see notes) | CFRS Armadale | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-03-31 15:44:00 | Fail | completed & Invoiced
MSA-DFES | WA3967842 | Toilet Block Near Applied Training - exhaust fan not working | FESA RHQ - Forrestfield | GMP-BR | Equipment | Building Equipment (EQ) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 14:30:00 | Pass | Complete
MSA-DFES | WA3967865 | Dormitory - Air conditioning unit is releasing a constant drip of water inside the room on carpet | CFRS Canning Vale | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 16:31:00 | Pass | Fixed ac water leak
MSA-DFES | WA3968083 | Building 1, Room 10, FF Bedroom 3- Circular flourcent light not working | CFRS Murdoch | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 10:45:00 | Pass | Complete
MSA-DFES | WA3968106 | external station security gate needs timing- see notes | CFRS Maddington | GMP-BR | Security | Access Control (SE) | Go Doors | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-11 12:45:00 | Pass | COMPLETED
MSA-DFES | WA3968116 | external ground lights not working, please see notes | CFRS Osborne Park | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-04 11:15:00 | Fail | We repaired 3 x faulty exterior lights. We were unable to repair 2 lights down the side wall and have sent off an email to find suitable replacements in LED form. The 2 lights have had their seals broken and there was clear ingress of water and dirt. Will return to complete.Locate faulty lights. Replaced faulty lights with new
MSA-DTAG | WA3967872 | Custody, interview room - flickering light | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-11 08:00:00 | Pass | Attended site and signed in with security. Got shown the flickering light in interview room. Supply and replace 2 x tubes and starters. Clean diffuser and refit to fitting. Signed out. Job complete
MSA-DTAG | WA3968081 | Lift 9 is ‘shuddering’ and intermittently going out of service. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 10:45:00 | Pass | Lift ROA found when lift car is shaken skate knocks landing door lock rollers causing the lift to crash stop. Made minoradjustments to skate and re tested lift, working fineTo be closed out at $0
MSA-DTAG | WA3968091 | Ground floor, camera C012 - not connecting to server | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 17:00:00 | 2021-03-12 09:00:00 | Fail | Installed and programmed new Axis PTZ camera, all programmed and tested ok. Job complete
MSA-DTWD | WA3967558 | Ground Floor cafeteria commercial fridge is not working | Murdoch Campus-Block T-Ground Floor-T018 - Cafe and Cafe Servery Area | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 0 | CLOSE | 09 Feb 2021 | 2021-02-09 12:28:33 | 2021-02-09 11:15:00 | Pass | Arrived on site signed found cafe coolroom fridge turned off. no member of staff knows why. Have switched back on and watched while it has cycled to temperature.
MSA-DTWD | WA3967565 | Front - Eave lining to roof space is damaged & lifted | Armadale Campus - 40 Commerce Ave | GMP-BR-RC | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 17:00:00 | 2021-07-15 14:00:00 | Fail | BRAF declined - refer to note on BRAF for sign off. Claiming costs to date. Note this is covered by Riskcover
MSA-DTWD | WA3967568 | cafe all power has tripped | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 09 Feb 2021 | 2021-02-09 12:40:15 | 2021-02-09 10:47:00 | Pass | Reset tripped power to canteen.job completed
MSA-DTWD | WA3967602 | BLD 812, Garage - white ant infested | Muresk Institute | GMP-BR | Pest Control | General Pest (PC) | Morris Pest and Weed Control | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 16:30:00 | Pass | SPOT TREATMENT OF TERMITES TO GARAGEAREA. SUPPLY AND INSTALL 7 X TRELONA BAITSYSTEMS
MSA-DTWD | WA3967634 | Reception area male toilet bowl loose | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 11:45:00 | Pass | Arrived on site and inspected found the the rhs male toilet bowl loose. Refitted the bowl with sealant. Tested all good
MSA-DTWD | WA3967647 | BLD 822, outside front door - water drinking fountain faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | CDA Air & Solar | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-17 14:45:00 | Fail | Repairs to fountain
MSA-DTWD | WA3967670 | Lvl 1, Beauty Clinic - Faulty lights | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-09 15:33:00 | Pass | Attended site, signed in, completed jsa, spoke to fm about job , located lighting, removed a lamp to get sample like for like ,went to wholesaler to pick up materials, returned to site, changed lamps and turned off lights that needed changing so they could cool down , cleaned up work area, completed paperwork,signed out *** job completed ***
MSA-DTWD | WA3967699 | Retic Centrifual pump tripping overload and sounding rough | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-08-30 15:12:00 | Fail | Emailed BRAF with report and cost to replace irrigation storage tank on the 26-2-2021.Job cancelled, Western Irrigation to invoice cost to date only. Advised 16-8-2021 job being sent out for quotes, Western Irrigation closed off the job 16-8-2021.Any questions please contact Eric Reedman at PFM
MSA-DTWD | WA3967770 | S Block, Level 2 - AC 2 and AC 3 currently tagged out in S209 | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-30 12:30:00 | Fail | Picked up required parts, attended site and signed in and filled out roof permit, located systems and replaced faulty inverter boards with new, re instated systems and tested, left all systems operational
MSA-DTWD | WA3967980 | Building unit 3, ground - Cold well water pump not working Heavy Plant Test Cells. | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-10 16:00:00 | Pass | Attended site and signed in. Got keys from facilities. Ran conduit and new cabling from switchboard around outside our walls in compound around to the cold well pump. Replace isolator with new rated isolator. Disconnect faulty wiring and made safe. Connect new feed to terminal blocks in control board. Labelled and tested. Replaced blown fuses as required. Reset system and ran pump. All okay. Signed out. Clean and tidy site. Job complete
MSA-DTWD | WA3967988 | L1 Electrical room - Aroma meter giving different watt usage readings (see notes) | Perth Campus B2 | GMP-BR | Electrical | General Electrical (EL) | NILSEN (WA) PTY LTD | 3 | CLOSE | 09 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 09:30:00 | Pass | Replaced faulty meter
MSA-DTWD | WA3968023 | Block 8, Room 8G36- lights tripping | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 09 Feb 2021 | 2021-02-10 17:00:00 | 2021-02-15 15:25:00 | Fail | Replaced faulty control gear in faulty light. All working properly now
MSA-DTWD | WA3968069 | T block, Canteen - thermostat control knob on the front of this food heater missing | Murdoch Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 09 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-10 14:00:00 | Pass | COMPLETED 10/2/21
MSA-DCA | WA3968850 | Outside History offices-Faulty light switch,crackling when switched on & is jamming. Notes below | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Collection Area 09 - History | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 11:26:00 | Pass | Replaced faulty light switches
MSA-DCA | WA3969081 | plant room - no heating water flow through coil on VAV. (see notes) | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Precise Air Group | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 13:00:00 | Pass | Investigate issue with BAE controls technician and found the issue to be caused from the second boiler not operating due to controls lead/lag configuration. Issue now resolved and viewed the trendlogs all temperatures now within range.
MSA-DCA | WA3969119 | loading dock - large automatic door locking pin broken, on the bottom of door 3 | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Driveway To L2 Scene Dock | GMP-BR | Building | Automatic Doors (BU) | Barclay Engineering | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-26 12:30:00 | Fail | Repairs to door
MSA-DCA | WA3969139 | Lvl 1, public male toilet,disabled cubicle - Water leaking from pan. Water supply switched off. | State Library of WA-Main Building | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-11 16:00:00 | Pass | unblocked toilet
MSA-DCA | WA3969182 | 2 input smoke alarms zones L1554 and L1553 faults | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Entrance - Security | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 08:30:00 | Pass | L1S53 & 54 Craft store riser reporting a “missing” fault on the FIP.Investigation identified water damaged detector L1S53 replaced smoke detector & base for new however the cabling appears to be damagedelsewhere due to building works & is spur wire configured.The cable to smoke detector L1S54 is also spur wire Configured from L1S53.Advised staff, who have noted the current isolation fault list. No further action required until advised otherwise.Note there are 6 x other faults present on the FIP relating to on going building works & 70 isolations.
MSA-DCS | WA3968312 | Chiller # 7 not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Materials (EL) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 06:13:35 | 2021-02-10 12:00:00 | Pass | found water leaking into junction box on the evaporative coil. drain water and seal box , test and left system operational
MSA-DCS | WA3968414 | G02 mircowave constant alarm | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 07:05:01 | 2021-02-10 09:30:00 | Pass | Rectified and fixed the relay fault on MW G02, job completed.
MSA-DCS | WA3968423 | Person gate at Zone 1 coming from the gate house, lock issues- details below | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 07:12:22 | 2021-02-10 12:45:00 | Pass | Attend site. Replaced faulty lock and two MKH key cylinders.
MSA-DCS | WA3968427 | Unit 2 middle landing vinyl flooring torn and lifting trip hazard | Karnet Prison Farm | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 10 Feb 2021 | 2021-02-12 17:00:00 | 2021-06-17 11:30:00 | Fail | UPLIFTED DAMAGED VINYL, SUPPLY & INSTALL NEW VINYL
MSA-DCS | WA3968447 | Unit 6, Cell D7- Tap is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-10 12:30:00 | Pass | Nill
MSA-DCS | WA3968449 | Unit 6, D Wing- Tap is leaking in shower block | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-10 13:30:00 | Pass | Nill
MSA-DCS | WA3968568 | Unit 4D the circuit board is overloading and tripping switch | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 08:48:44 | 2021-03-05 16:00:00 | Fail | Replaced overhead sub-mains
MSA-DCS | WA3968569 | Unit 4A power cable for PA system had fallen down | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 08:53:56 | 2021-03-05 10:00:00 | Fail | Re-attached hanging speaker cable
MSA-DCS | WA3968593 | Recreation Office - Key broken in the lock to main entry door. | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 13:07:24 | 2021-02-10 12:50:00 | Pass | Replaced jammed lock on entry door to recreation
MSA-DCS | WA3968653 | Administration - Lobby Area-Lobby doors not self closing hard enough to action locking mechanism | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 13:28:47 | 2021-02-11 09:30:00 | Fail | Adjust door closer operation and lubricate lock.Check door closing operation.
MSA-DCS | WA3968656 | INF (10), Control Room, Observation cell monitor in infirmary control not working. (see notes) | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 13:31:10 | 2021-02-10 12:30:00 | Pass | Indigo time server fault, rectified and fixed. Job completed.
MSA-DCS | WA3968691 | Kitchen, Fridge 6 reportedly keeps dropping temperature | Banksia Hill Detention Centre | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-25 08:30:00 | Fail | Complete. Monitored fridge, cleared ice. Leaving over weekend. Will return to check.Returned to check on fridge, monitored. All running ok.
MSA-DCS | WA3968700 | woodwork tea prep Zip boiler has no power | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-10 12:00:00 | Fail | Replaced faulty urn.
MSA-DCS | WA3968706 | VideoLink- Power has gone and can not reset | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 13:04:16 | 2021-02-10 14:00:00 | Fail | Reset circuit and tested after circuit was overloaded again.
MSA-DCS | WA3968736 | Unit 2 - A1 Personal door latch is also broken | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 10:10:05 | 2021-02-12 11:00:00 | Fail | Unable to attend on time due to covid lockdownReplace hinges, door plate and adjust strike.Replace barrel.
MSA-DCS | WA3968737 | Education, Lunch room- Lock not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-19 13:30:00 | Fail | Require parts.Replace mortise lock and strike .
MSA-DCS | WA3968738 | B2 - internal perimeter showing red light (unsecured) | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 10:13:39 | 2021-12-09 16:30:00 | Fail | Checked cabling between beam sets and from the receiver stack to the alarm inputs in the EC. Found cabling issue between EC and the alarm stack. Repaired and tested ok back to the gatehouse.
MSA-DCS | WA3968743 | Farm egg processing room roof, gutters rusted out and leaking | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-07-05 09:00:00 | Fail | Replace roof sheeting and gutters
MSA-DCS | WA3968747 | Unit 2, lower landing office- TV decoder system making loud grinding noise | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-11 13:30:00 | Pass | Attended site, found faulty fan in MATV encoder modulator.Equipment is no longer in use, powered everything down.Job completed.
MSA-DCS | WA3968748 | Lenard, Cell A08- Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-10 12:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3968760 | CCTV system screens are blank and not showing | East Perth | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 14:40:59 | 2021-02-10 13:15:00 | Pass | Attended siteFound both monitors on levels 1 & 2 only displaying 11 cameras appears to have 4 missingFound 4 cameras operational on the server and re-added the cameras to both spot monitorsAll 15 cameras displaying on both spot monitors correctlyProvided staff training on this for future if it occurs againLeft site
MSA-DCS | WA3968767 | CCu (11), Cell C03- Main cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 11:30:00 | Pass | Investigate and repair ccu cell c03 main light
MSA-DCS | WA3968770 | Unit 3, porch lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-11 12:30:00 | Pass | Investigate and repair unit 3 external lights
MSA-DCS | WA3968780 | Chapel lights faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-12 10:00:00 | Pass | Investigate and repair/replace lights in chapel
MSA-DCS | WA3968813 | Outer perimeter fence, G01 no activation | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 15:33:06 | 2021-02-10 15:00:00 | Pass | Rectified and fixed the senstar fault to activate the G01 electric fence, job completed.
MSA-DCS | WA3968834 | Unit 2, Staff office's - Broken GPOs & Data Points & Exposed Cables at bottom of Walls | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 11:42:43 | 2021-03-10 11:00:00 | Fail | Repaired duct
MSA-DCS | WA3968921 | Unit 1, Staff office's - Broken GPOs & Data Points & Exposed Cables at bottom of Walls | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 12:35:31 | 2021-03-10 09:30:00 | Fail | Repairs to duct.
MSA-DCS | WA3968957 | Replace faulty light in office area, remove dead insects & clean diffusers | Midland (North East Metro) | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-11 15:00:00 | Pass | Replaced lamps and cleaned diffusers
MSA-DCS | WA3969104 | Unit 2 house 3 network switch failed. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 13:17:03 | 2021-02-11 14:00:00 | Fail | Removed network switch and repaired. Installed and tested ok. New switch programmed up as a straight swap but was not needed. Left on site as a spare. SMS, MDAS and cell call tested ok. Parts used:Planet network switch GS-4210-24PL4C
MSA-DCS | WA3969114 | Unit 2 house 3 SMS controller Offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 13:19:07 | 2021-02-11 15:00:00 | Fail | Once the network switch had been repaired the SMS controllerstarted communicating again. Door sensors tested ok
MSA-DCS | WA3969118 | Unit 2 house 3 Expander failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 13:25:05 | 2021-02-11 16:00:00 | Fail | Once the network switch had been repaired the SMS controllerstarted communicating again. Door sensors tested ok
MSA-DCS | WA3969128 | unit 2 control room no lights | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 10 Feb 2021 | 2021-02-10 17:28:41 | 2021-02-10 16:00:00 | Pass | Replaced burnt wiring and ballast
MSA-DCS | WA3969144 | SOG Mice sighted in our kitchen, and smells emitting from roof indicate significant | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 10:40:00 | Pass | Carried out a service for rodents at sog kitchen. There were reports of an odour coming from roof space, no odourcould be located at time of inspection, indicating that the odour has cleared. Inspected and replenished existingrodent stations, as well as installing two new rodent stations in the area. Monthly follow ups are recommended tomonitor and replenish the stations.
MSA-DCS | WA3969184 | Unit 1, B & D Day Room- Tap is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 11:54:00 | Pass | Nill
MSA-DCS | WA3969219 | Secuirty office - Programming issue, inability to extract data (PTZ footage) due to locked program o | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 12:30:00 | Pass | Following the recent generator test the computer appears to have accessed an incorrect database. Identified problem on Security Office PC after checking site database and finding no problem. Reprogrammed Security Workstation to access correct database and confirmed ability to download video.
MSA-DFES | WA3968468 | ground front external Internal globe/lamps flashing/Flickering. Believe Fluro Tubes on way out | CFRS Wangara | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 10 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 16:30:00 | Pass | Arrived on site at 15:00 to repair front sign. Found 4 blown 3ft Fluro tubes and starters. Picked up tubes from Joondalup. Tested fitting and signed out at 16:30
MSA-DFES | WA3969190 | Metro Office & Maintenance office - Lights have blown | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 16:30:00 | Pass | Located fault with Lights in 2 offices. We spoke to a worker who advised they had just turned off. We reset RCDs W2 and B2 which we’re off. We functionally tested the lights multiple times and all is working.
MSA-DTAG | WA3968728 | Ground floor, lobby area - keypad faulty as some staff had issues swipe card, unable to open door | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-15 13:00:00 | Fail | Work performed by Drake Van der Merwe (10/02/2021)Card reader number 8 button is faulty. Needs replacement keypad. HID RX40Work performed by Drake Van der Merwe (15/02/2021)Replaced keypad/reader and tested. All buttons working and swipe working. Changed schedule in programming back tocard and code.Job completed.APPROVED BRAF ATTACHED
MSA-DTAG | WA3968759 | Level 5, lift 1 - Door is closing but lift isn’t moving, technician ‘joel’ already onsite | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMPFIN | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-10 12:19:00 | Pass | Lift ROA errors in error log DCL under voltage 719, 35, 11. Reset VF drive and tested lift to every floor, all okayTo be closed out at $0
MSA-DTAG | WA3968897 | 1987 L1 sherrif's office Exit sign in basement plastic instruction sheet fallen out and held at desk | Supreme Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-11 09:15:00 | Pass | EXIT SIGN PLASTIC SHEET REFIXED
MSA-DTAG | WA3969187 | A/C 1A in security office is not linked to BMS | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 13:00:00 | Pass | Attend site with Icon Logic. Icon re-established coms to FCU1/CU6. Due to unit being isolated( fan motor failed)
MSA-DTAG | WA3969201 | ground everywhere Cockroach infestation | Armadale Courthouse | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 16:30:00 | Pass | .
MSA-DTAG | WA3969210 | L10 front counter Security door is accessable without access card | Westralia Square | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 09:15:00 | Pass | Found door lever/furniture loose and once someone will shake the door lever from the opposite side the lever inside will move causing the mortise lock to engage and open. Tightened the mortise lock and levers. Showed client Vicki and tested all ok
MSA-DTAG | WA3969256 | ground, Non contact room 2 duress alarm - The duress button is not activating when pressed. | Joondalup Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-11 13:30:00 | Pass | Attended site. Checked duress in Non Contact Booth 2 in Custody, found resistor broken off, rectified & tested duressbutton activation, all OK.Job completed
MSA-DTWD | WA3968419 | N Block, Passage N116 - Repair ceiling tiles loose | Mount Lawley Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 10 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-11 15:30:00 | Pass | Inspected loose eave sheet, set up exclusion zone with hazard tape. Cleaned around outside edges of sheet and pushed back into place, sealed around edges to secure. Job complete
MSA-DTWD | WA3968665 | D Block, D207 Staff Room – Faulty Lock on Comms Rack | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-22 12:30:00 | Fail | D207 - STAFFROOM COMMS RACK - FAULTY LOCK.Lock repaired, worn keys replaced.
MSA-DTWD | WA3968710 | L Block lift ground floor button is faulty, working intermittently | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-10 12:22:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3968734 | E block, Restaurant Kitchen - dishwasher leaking from main holding tank | Joondalup Kendrew Campus | GMP-BR | Equipment | Cleaning Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-10 13:55:00 | Pass | COMPLETED 10/2/21REFER TO SERVICE REPORT FOR PLUMBER TO ATTEND.
MSA-DTWD | WA3968740 | R Block, Room R023- middle row of lights are tipping the circuit | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-19 13:15:00 | Fail | Repaired lights in classroom.job completed
MSA-DTWD | WA3968750 | Repair the door lock on painting building opposite L Block. | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-11 09:15:00 | Pass | Repair to lock
MSA-DTWD | WA3968762 | A Block Community services area Replace faulty batten flouros with LEDs | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-11 11:30:00 | Pass | Attended site and signed in. Spoke with facilities about light fittings. 5 lights dead in office. Supply and replace old fluros with new led fittings. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3968763 | C Block, Room C003- condenser fan on APAC unit is faulty | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-05-28 16:00:00 | Fail | Access gained and new parts obtained from supplier. Unit isolated and condenser fan mtr and blade installed to package unit.Tested all ok.
MSA-DTWD | WA3968812 | A Block, level 1 - Cafe Gas Stove wont light up | Mount Lawley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-03-29 08:45:00 | Fail | NOTE, THIS WAS ACTUALLY AT EAST PERTH SITE, NOT MT LAWLEY CAMPUS.
MSA-DTWD | WA3968845 | Unit 8 - BSD isnt on | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-15 15:21:00 | Fail | replaced burnt out motor on AHU8 - works completed rectifying the fault
MSA-DTWD | WA3968864 | A block, Level 1 - Sensor on Cafe Door to Oxford Street is not working | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 10 Feb 2021 | 2021-02-11 17:00:00 | 2021-02-10 13:15:00 | Pass | Inspected door and found a loose connection on the controller causing the external sensor to fault, remade connections as necessary, checked over door and tested operation.
MSA-DTWD | WA3968903 | carpark 2, east end - 3 bollards damaged | Thornlie Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 11:15:00 | Pass | Reinstalled 3 bollards and installed an extra 3 bollards as directed by site.
MSA-DTWD | WA3968927 | Building 8, southern door off courtyard - door has dropped and is sticking on brick paving | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 09:30:00 | Pass | Adjust pivots and brackets to glass door
MSA-DTWD | WA3969238 | Level 3, room 3-12 - rooms to warm | Perth Campus B2 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 10 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-18 11:09:00 | Fail | Returned to site with new duct work for VAV. Confimed access time with site facilities. Gained access set up installed new flex duct and carried out operation test. All ok. Class room left tidy.
MSA-DCA | WA3973793 | Water leaking from pan | State Library of WA-Main Building-Ground Floor-Male Toilet - Rear Entrance Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-11 16:47:00 | Pass | Replaced faulty bellow on the 2nd cubicle. No leaks found
MSA-DCA | WA3974409 | Retic leak Zone 3 Franic St Museum End | Perth Cultural Centre Precinct - Museum Plaza (James Street) | GMP-BR | Plumbing & Drainage | Drainage (PD) | Earth & Water Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 12:45:00 | Fail | Retic zone 3 Francis St Museum end - debris stuck in vacuum breaker
MSA-DCS | WA3973763 | Fire panel in control room showing fault Unit1 dining room | Karnet Prison Farm-Administration, Stores Dairy Office | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 11 Feb 2021 | 2021-02-11 10:56:16 | 2021-02-11 10:48:00 | Pass | 11/2/21 JNMissing detector fault on FIP, L4 S78 unit 1 dining store room. Located sensor and replaced. Deisolated and panel normal.
MSA-DCS | WA3973779 | Unit 4, PA System not working, nothing heard in the unit | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 07:14:02 | 2021-02-18 09:03:00 | Fail | Rectified and fixed faulty bypass button, test PA all wing. Job completed.
MSA-DCS | WA3973785 | Reset Centre- Outside toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 07:17:16 | 2021-02-11 12:06:00 | Pass | Cleared partially blocked outside toilet.
MSA-DCS | WA3973794 | Unit 9, Cell A8- Windows & View hatch smashed by prisoner | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 07:25:47 | 2021-02-11 15:00:00 | Pass | WINDOW AND OBS RE GLAZED - FRAME REPAIR
MSA-DCS | WA3973806 | Unit 3, B & D Wing- Boiling water system casing has been damaged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 11 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 11:00:00 | Pass | Urn has dent in top right hand corner All working okayMaintenance advised no repairs are required
MSA-DCS | WA3973821 | Unit 1, Cell C2- Louver vent in window damaged | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 07:35:30 | 2021-02-11 11:45:00 | Pass | DAMAGED WINDOW VENT REPLACED
MSA-DCS | WA3973824 | Internal perimeter fence mircowave C03 & permitrax F13 is faulty keeps activating | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 07:38:01 | 2021-02-24 16:38:00 | Fail | Recalibrated multiple zones, repaired faulty MW PCB and tested OK.Job Complete
MSA-DCS | WA3973866 | Unit 14- D Wing- Chain winder on window has snapped off | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 11 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-26 14:30:00 | Fail | WINDER REPLACED WITH NEW - WINDOW FRAME REPAIRED
MSA-DCS | WA3973911 | Unit 4, SMS cabinet tamper has changed state to Open | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 16:30:00 | Pass | No Fault Found.job recalled, technician found loose , resecured & tested ok
MSA-DCS | WA3973949 | gate house keywatcher R/H Door not closing | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 08:34:09 | 2021-02-18 09:05:00 | Fail | Attend site. Latch on gatehouse door not closing correctly due to damaged latch. Part ordered. Re-attend site to fit new latch.
MSA-DCS | WA3973974 | control room, DVM memory server critical - SEME on site | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 08:54:46 | 2021-02-16 13:45:00 | Fail | Investigated fault, corrected memory fault and rebalanced/redistributed recordings between storage servers.Modified for increased storage efficiency.Tested OKJob Complete
MSA-DCS | WA3973981 | Assessments - light circuits keep tripping out | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 08:57:34 | 2021-02-11 15:00:00 | Pass | Disconnected faulty fan on roof, reset power and tested.
MSA-DCS | WA3974020 | Void -Tug Charging cable damaged, inmate drove off with the tug still plugged in. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-09 13:30:00 | Fail | Investigated damaged charge port on tug. Ordered replacement parts, picked up and installed
MSA-DCS | WA3974068 | Academy Accommodation Wing- 2x fluoros along main corridor not working. | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 12:00:00 | Pass | Repaired light
MSA-DCS | WA3974075 | Unit 5 - Back Yard-Retic Valve won't shut at the rear of unit 5 Urgent repair required. | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 10:17:36 | 2021-02-16 10:30:00 | Fail | FAULTY SECOND VALVE REQUIRED REPLACING, LOCATED AND REPLACED.
MSA-DCS | WA3974084 | Main Building, A Wing, Training Cell No 10- Toilet bowl cracked causing water leak | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 10:15:00 | Pass | Resealed pan collar
MSA-DCS | WA3974085 | SOG Academy Accommodation Wing, male bathroom, accommodation wing - hole in bathroom door (see notes | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 09:00:00 | Pass | door repaired
MSA-DCS | WA3974088 | Unit 1, B&D wing - side drainsin cleaning rooms both blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 10:25:55 | 2021-02-12 10:30:00 | Fail | Nill
MSA-DCS | WA3974097 | Unit 2, Cell 29 - Door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-12 11:45:00 | Pass | Attend site, service and repair faulty door lock to cell 29 for correct operation.Date on site: 12/02/2021Time on site: 11:00am - 11:45am
MSA-DCS | WA3974105 | Abattior - broken 3 phase switch small good cooker room | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-12 13:00:00 | Pass | Investigate and replace broken 3 phase switch in abattoir
MSA-DCS | WA3974106 | Gwynlea building, Male toilet near STS section - water leaking from Cistern, unable to shut off | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 08:30:00 | Pass | Replaced outlet washer
MSA-DCS | WA3974170 | Abattoir- No.6 fridge not holding temperature | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-22 12:00:00 | Fail | found compressor faulty, replace compressor commission and left operational.
MSA-DCS | WA3974200 | Gwynlea Building ground Repair fluoros not working in STS Manager's Office & male toilet in Pilbara | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 15:00:00 | Pass | Replaced faulty lamps and ballast
MSA-DCS | WA3974293 | Kitchen, Work Area- Repair Broken Mixer safety Guard | Melaleuca Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 12:39:46 | 2021-02-15 16:30:00 | Fail | 15/02/21Arrive at site to check mixer issues. Staff explain they have to j the micro switch up for it to run and is making a grinding noise and stopping/starting when under load. Found micro switch is faulty and requires replacing. Also investigated motor/gearbox as slight oil leak from gearbox area. Will need to gather more information from service manual and asses if viable to repair or replace. 19/02/21Investigate manuals for spare parts, recommend replacing micro switch parts and if gear box/ motor still having issues will need to investigate further as all spare parts come as seperate.*** Not worth repairing ***
MSA-DCS | WA3974360 | Unit 1 & 2 - Lower Hot Water Urn temperatures to a safe Level to hot | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 12:43:56 | 2021-02-12 09:55:00 | Pass | ADJUSTED TEMPARATURES ON MULTIPLE ZIP UNITS AS REQUESTED
MSA-DCS | WA3974414 | Mechanical w/s, lunch room - broken GPO | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-12 08:30:00 | Pass | Investigate and replace mechanical workshop lunchroom gpo
MSA-DCS | WA3974419 | WWTP digestor tank pump faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-24 10:00:00 | Fail | Picked up and put in for quote and repairs , repaired and reinstalled.
MSA-DCS | WA3974449 | The Gatehouse main entrence lock buzzer not working.- see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 13:43:49 | 2021-02-16 13:30:00 | Fail | Checked and found prison main entrance door lock buildin buzzer is not working. Door lock is ok. Modified and replaced with a external buzzer and tested all ok after work. 24VAC Buzzer X 1 stock from office store.
MSA-DCS | WA3974479 | reception area door to prison - faulty reed switch, door constantly alarming | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 13:00:00 | 2021-02-16 11:00:00 | Fail | Reed switch replaced fault remains. Fault appears with door lock tongue sensor not fully closing lock out of alignment. Lock Smith required to repair.
MSA-DCS | WA3974484 | Gate control - MDAS system, has a about 20 alerts "this point is not programmed in the data base" | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Feb 2021 | 2021-02-11 18:30:42 | 2021-02-11 17:30:00 | Pass | Attended site and investigated the fault.Cleared all Transponder troubles.Restarted Slave server and conducted test.All ok at departure
MSA-DCS | WA3974487 | Administration security area Aircon not working- see notes below | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 14:35:54 | 2021-02-15 11:43:40 | Fail | Picked up new fuseable link,fitted new link to damper.
MSA-DCS | WA3974489 | SOP toilet water keeps running HA 9 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 14:39:52 | 2021-02-12 14:24:00 | Pass | Nill
MSA-DCS | WA3974541 | Security office & visits center - camera monitor not connecting to network indigo control centre | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 16:58:00 | 2021-02-15 14:45:00 | Fail | Attended site checked and found Indigovision Control Center not starting up in Security and Visits workstations. Further check located the problem to be IndigositeDB folder sharing problem. Rectified the problem and tested all ok after work.
MSA-DFES | WA3974535 | Engine room/ appliance bay - bay door 1 is not working | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-15 16:30:00 | Fail | Attended Duncraig Fire Station bifold door # 1. There is a fault one of the PE beams that requires replacement. The door was left operational as the faulty PE Beam was left disconnected. Please see attached BRAF for the replacement of the PE Beams. This set of PE Beams should be replaced urgently.Please see attached service reports, BRAF and Quote.Works complete.Note -- the target finish date expired before the braf was approved. Upon approval of the target BRAF the target finish date was not increased.
MSA-DFES | WA3974556 | engine room door not closing and securing - door no.: 2 | CFRS Malaga | GMP-BR | Building | Doors (BU) | Anvil Doors | 0 | CLOSE | 11 Feb 2021 | 2021-02-11 22:46:38 | 2021-02-11 21:15:00 | Pass | Attended Malaga Fire Station for the issues reported as engine room door # 2 not closing. Took some time to diagnose the cause of the door not being able to fully close- it was eventually found that one of the remotes was faulty so the remote was removed and a new one supplied. After the faulty remotes was removed from the system and the new one programmed to the system, Door # 2 operated correctly. (Its is noted that the faulty remote was likely the cause of the issue with the rear door number 3 as-well.Please see attached BRAF, Service report and Quote
MSA-DTAG | WA3973972 | Front entry revolving door is making a loud squeaking noise | Central Law Courts | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-11 13:48:00 | Pass | Inspected door and found to be running all OK could not see any sine of damage or rubbing for door to be making a noise. All ok at time of test
MSA-DTAG | WA3974182 | Sewage Pump alarm is going off in the staff carpark | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 11 Feb 2021 | 2021-02-11 15:42:00 | 2021-02-11 13:50:00 | Pass | Attended site,Investigate sewer pumps alarming,Lift lids on pit too find levels ok in tank.System identified pump 2 as potential outage.Check pumps manually for operation and find all operating ok.Reset both pumps to automatic and system has returned to normal function.If system alarms again in the near future, recommend pumps be lifted for inspection and electrical checked for faults.
MSA-DTAG | WA3974460 | Registry/counter area - Flickering light in counter area | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 10:30:00 | Pass | Attended site and signed in. Located light out at reception. Supply and replace faulty fluro tubes and starters. Tested all okay. Signed out. Job complete
MSA-DTAG | WA3974480 | Lock on door to registry is stiff and is becoming harder to unlock. | Armadale Courthouse | GMP-BR-HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 15:45:00 | Pass | Attend site. Lock is working but the door was found to be out of alignment. Readjusted door alignment and check closing of door and lock. All working.
MSA-DTAG | WA3974530 | L23 reception - Reception Service cannot hear visitors through speakers - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-08 12:00:00 | Fail | 12/02/2021 - Moved microphone from table to glass temporarily to test for proper quality of sounds when peak time. Client will advise and tech to return and secure microphone properly if client is ratified with sound quality18/02/2021 - Fixed microphone to window, Job completeWorks completed under Warranty.
MSA-DTWD | WA3973778 | North Block, Room N111 - Repair metal strip to technicians office entry | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 11 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 13:30:00 | Pass | Met with security and located the damaged threshold strip on facilities management doors. I then filled out a jsa and asked staff to open the doors for me. After removing the strip I countersunk the holes in the strip and secured it back in place with screws. I filled out a signature slip to complete the job.
MSA-DTWD | WA3973941 | Lvl 1, Chalk and cheese- Broken drainage pip | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-11 10:00:00 | Pass | Fix drop tray for coffee machine
MSA-DTWD | WA3973973 | T, U & V Blocks Sewage pit controller in alarm | Rockingham Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 17:00:00 | Pass | located electrical fault, repaired
MSA-DTWD | WA3973990 | E Block, E8 Laundry- Blocked Trap | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 11 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-11 09:00:00 | Pass | Cleared blockage
MSA-DTWD | WA3973999 | Classroom B16 - Roof mounted Email A/C making bearing like squealing sound | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 09:00:00 | Pass | Arrived on site signed in. Assisted by Dave with working at height. Checked a/C found no fault. On start up there is a inner ceiling rattle, completed paperwork and informed Frank and Phil on findings. Signed out.
MSA-DTWD | WA3974007 | E Block, E58 - Entree fridge not working | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 11 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-11 16:30:00 | Pass | Found unit to be low on refrigerant and short cycling. Isolated unit. Reclaimed refrigerant. Pressure tested and located leak at TX valve flare. Repaired leak and pressure tested. No further leaks found and system held 300psi for 1 hour.Released nitrogen and vacced out system. Recharged with new R 404a refrigerant. Started unit and checked operation and that fridge cycling off and on at setpoints.
MSA-DTWD | WA3974049 | A Block, 2nd Floor, disabled toilet leaking from cistern when flushed | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-13 10:15:00 | Pass | Attended site,Service leaking toilet including supply and installation of new inlet valve, outlet washer and flush cone rubber. Works tested on completion
MSA-DTWD | WA3974055 | E block, restaurant kitchen - dishwasher wall outlet leaking water everywhere | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 07:30:00 | Pass | Attended site,Alter water service, supply and install new duo valve as existing had failed to restaurant kitchen dishwasher. Tested works on completion
MSA-DTWD | WA3974059 | E Block, E71 broken tap right hand side 3rd sink along | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 08:45:00 | Pass | Attended site,E block E71 RHS 3rd sink along. Supply and install new kitchen sink mixer as the old one had failed and was not repairable.Tested works on completion
MSA-DTWD | WA3974172 | K Block, Repair two GPO pendants in the tiling workshop | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-18 13:00:00 | Fail | Attended site and signed in. Located K block. Found gpos for workshop to be running off extension cords plugged in over work areas. Advised to replaced with proper pendant gpos to middle of workshop. Began running pendants. Need to return and complete. Signed out. Job not complete Attended site and signed in. Ran new cabling to location of pendant gpos. Connected to existing power. Fitted off outlets in middle of workshop. Tested all okay. Job complete
MSA-DTWD | WA3974173 | G Block, room G23a (Elizabeth Elzmans desk)-Replace faulty flouro batten with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 13:30:00 | Pass | Attended site and signed in. Located desk in admin block. Found faulty light over desk. Supply and replace with new led batten. Tested all okay. Job complete
MSA-DTWD | WA3974179 | W Block Workshop - red knob on emergency stop button is missing | Munster Campus (ACEPT) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-11 15:30:00 | Pass | Attended site and signed in. Located workshop W. Found broken button at exit door. Supply and replace with new E stop button. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3974194 | H Block HG01 Evap (closest to battery test area) not running -see notes | Carlisle Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-05-21 14:00:00 | Fail | Gained access to unit. Identified a failed blower fan that needs replacing. Found safety issue with a skylight directly where access to change motor is. Raised issue with service manager and awaiting instructions.Returned to site after roof made safe. Met with other tech.Gained access to unit to get details.Picked up new fan motor and pulley from suppliers. Returned to site and fitted new motor. Found water sump dump valve leaking. Discussed with maintenance and was informed to go ahead with further repairs. Replaced valve and checked operation. All ok.
MSA-DTWD | WA3974294 | J block, transportable, J003 - black ants infestation | Balga Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 12:15:00 | Pass | Sprayed external walls and subfloor for ants with 40 Litres Bifrenthrin
MSA-DTWD | WA3974463 | D Block, Room DG02- Ducted split unit is squeaking | Carlisle Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-22 13:43:00 | Fail | On inspection of system found squeezing noise was made by movement of ductwork on bracket. Applied armaflex tape to cushion connection, and tightened bracket to eliminate movement.
MSA-DTWD | WA3974471 | E block, restuarnt cool room - cool room not cooling | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Coolroom (RE) | Precise Air Group | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 13:26:00 | Pass | Attended site signed in and filled out jsa and roof permit, accessed roof top condensor and investigated, diagnosed system to have faulty start capacitor and compressor relay, cooled compressor down to remove open circuit. Picked up required parts from supplier. Returned to site and fitted new parts,tested system and pump down cycle. Left system all operational.
MSA-DTWD | WA3974507 | Block 3 ground Heavy Plant workshop High bay security lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 15:30:00 | Pass | Attended site and signed in. Located lights not working. Accessed with ewp. Supply and replaced with new tubes and starters. Tested all okay. Job complete
MSA-DTWD | WA3974510 | block 3, ground - Metal feb, Cropper in undercover area has no power. | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 15:30:00 | Pass | Attended site and signed in. Located cropper machine. Tested RCD all okay. Tested isolator all okay. Turned on and off. Reset all okay. Machine operating good. Signed out. Job complete
MSA-DTWD | WA3974524 | Block 10 L1 ladies toilet First 2 hand basins leaking underneath | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 11 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-22 13:00:00 | Fail | repaired 2 leaking traps
MSA-DTWD | WA3974525 | block 3, workshop - cabling to be remounted as fixings have broken on cabling to switchboard | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 11 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 10:30:00 | Pass | Attended site and signed in. Located block 3 switchboard.found cabling fallen off cable tray and hanging down on wall. Bottom of cable pit was full of water, used pump to get water out and dry out. Re cable tied all cables back into cable tray. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3974537 | Canteen exit roller shutter - faulty lock on roller cant be locked | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 11 Feb 2021 | 2021-02-12 17:00:00 | 2021-02-12 11:15:00 | Pass | Canteen - faulty lock on exit roller shutter.Lock re-aligned.
MSA-MRWA | WA3973992 | Toilet Lobby - Light switch pushed in/not working please replace switch/switch plate | Don Aitken Centre MRWA Head Office-Main Building-First Floor-E1.01-Electrical Equipment Riser | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 0 | CLOSE | 11 Feb 2021 | 2021-02-11 12:59:21 | 2021-02-11 11:00:00 | Pass | Arrived on site, signed in, spoke to fm about job, completed jsa, located switch, set up work area, isolated lighting circuit, removed old switch , switch and plate had to be replaced , fitted switch and plate, re energised circuit, tested lighting, lighting working as intended , cleaned up work area, completed paperwork,signed out *** job complete***
MSA-DCA | WA3980228 | Fault on device Z36, flame detector | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor-G.04 - Wet Processing Lab | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 15:12:00 | Pass | Attended WIPfault.Carried out checks.Tested and checked terminations.All cleared.Monitor.
MSA-DCA | WA3980470 | Broken lollypop light outside PICA front door | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-23 09:00:00 | Fail | Began to investigate fault, went into Pica tried to gain access to the switchboard in the rehearsal room to find out they had rehearsals going on and we could not gain access will have to come back when rehearsals are not on to access the switchboardClosed today as per David De Villiers instructions, as we are unable to gain access to perform works.
MSA-DCA | WA3980476 | Broken lollypop light outside rear of Library /Theatre | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 13:30:00 | Pass | 12/2/21Senna and Morgan 12pm-1:30pmArrived on site and began to investigate fault, found cause of fault to be a blown fuse back at the Substation switchboard. Replaced fuse, went back to lights to confirm they were still on, Circuit is on and holding. Cause of blown fuse unknown.
MSA-DCS | WA3980178 | ISU- Smashed window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 07:47:44 | 2021-02-12 12:00:00 | Pass | NEW GLASS INSTALLED TO DOOR IN ISU
MSA-DCS | WA3980184 | Wash down cabinet right side of cleaning towards unit 4 -Hose reel leaking water, seals gone | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 07:51:57 | 2021-03-03 09:20:00 | Fail | Replaced leaking hose reel with new one
MSA-DCS | WA3980195 | Wester courts unit 4 end, second door marked cleaning - Lock handle broken and door cannot be opened | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 07:57:44 | 2021-02-15 12:55:00 | Fail | Attend site, replace broken handle set with new temporary lock. Re-attend site to remove temporary lock and install new handle set.Time was spent with security to find key code for the lock. Could not be found, the lock at to be grinded open and the handle was broken to operate.
MSA-DCS | WA3980197 | Unit 4, Cell A12- Sink tap will not turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 08:00:04 | 2021-02-12 11:20:00 | Pass | Replaced washer
MSA-DCS | WA3980204 | Unit 3, Cell A11 - Tap faulty in sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 08:06:20 | 2021-02-12 13:00:00 | Pass | Rewashed tap
MSA-DCS | WA3980262 | Visits, Staff Lunch Room- Hydro Tap Runs Intermittently | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 09:57:00 | Pass | Replaced dual solenoidREPLACED SOLENOID TO BILLI QUADRA A40189255N
MSA-DCS | WA3980270 | Medical Centre - Broken tap in the consult room | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 08:50:39 | 2021-02-18 10:30:00 | Fail | Inspected amd found the cold water tap leaking. Need new spindle. Need to order parts with supplier Collected parts from supplier and returned to the site. Removed the faulty ceramic spindles for both hot and cold. Replaced with new hot and cold spindles. Reconnected water and tested all working in order.
MSA-DCS | WA3980271 | Gardens- meeting place- Tap Stand Pipe Leaking in the Ground | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-23 15:21:00 | Fail | Replaced section of leaking pipe and hose tap in garden.
MSA-DCS | WA3980274 | Unit 3 outside room 40 - HWS pilot light keeps going out | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 08:51:38 | 2021-02-12 12:45:00 | Pass | Inspected both hwu near room 40. Tested multiple times all working in order. The hydropower unit is working fine.
MSA-DCS | WA3980277 | Principle office - 2x light covers have fallen off | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 08:53:16 | 2021-02-13 08:52:00 | Pass | replaced 2 old light fittings with LED fittings
MSA-DCS | WA3980285 | Canteen- Circuit boards keep trying out | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 09:02:02 | 2021-02-13 07:00:00 | Pass | Reset power, regular issue with staff overloading circuit, have advised a solution a month ago. waiting for response.
MSA-DCS | WA3980286 | Abultion block, 2A - lights have blown | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 09:03:33 | 2021-02-12 15:00:00 | Pass | Replaced light fittings with LEDs in unit 2A ablutions block 2
MSA-DCS | WA3980340 | front gate house - hot water system not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 09:27:42 | 2021-02-15 09:15:00 | Fail | Inspected the hwu in the front office all working fine. The urn tap in the kitchen dripping need new tap. We will come back with parts. Collected parts from supplier and returned to site. Removed the faulty tap and installed new tap. Tested all working in order.
MSA-DCS | WA3980354 | control room - Zone 16 & 17 in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Feb 2021 | 2021-02-12 13:42:56 | 2021-02-12 13:30:00 | Pass | Attended site and investigated the fault.Checked Omnitrax cables and connections on node 8.Checked surge protectors.Reseted power to processor.Checked sensitivity and conducted test.All back to normal and operational
MSA-DCS | WA3980355 | control room - emergency tone alarm not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 09:45:15 | 2021-02-12 15:00:00 | Pass | Attended site and investigated the fault.Checked connections and wiring on officer station unit CI-3210 located in control room.Checked fibre link in equipment room.Conducted test.All ok at departure
MSA-DCS | WA3980357 | External perimeter - ext zone 13 permitrax in constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Feb 2021 | 2021-02-12 13:48:28 | 2021-02-12 16:14:00 | Fail | Recalibrate zone 13 external perimitrax due to constant alarming. Job completed.
MSA-DCS | WA3980403 | Unit 7, SCU A wing - faulty light located in day room near fire extinguisher door. 11ft Ladder req | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-23 11:30:00 | Fail | Repaired numerous faulty lights in unit 7 from 12 foot ladder
MSA-DCS | WA3980425 | INF - Light tubes have been changed but lights still not working in the storeroom | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-15 13:00:00 | Pass | Investigate and repair infirmary store room light
MSA-DCS | WA3980428 | Unit 6, B Wing - Cleaning tap has come off the wall | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 13:30:00 | Pass | Nill
MSA-DCS | WA3980430 | main kitchen- food grade castor wheels to fix benchs are damaged | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-11 11:00:00 | Fail | Replaced wheels on trolleys and benches
MSA-DCS | WA3980431 | Main kitchen- 3x stainless steel Tray locks to oven racks are faulty | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-11 13:00:00 | Fail | Replaced wheels on stainless steel tray racks
MSA-DCS | WA3980432 | Entry- state flag pole t is damaged | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 13:00:00 | Pass | Carry out repairs to the flag poles located at the entry to prison.
MSA-DCS | WA3980435 | Pedestrian Gate is not closing | Bandyup Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Schlager Construction Group | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 11:04:59 | 2021-02-15 10:30:00 | Fail | Supplied and installed new Lockwood Hydraulic door closer to pedestrian gate.
MSA-DCS | WA3980461 | Unit 7, Cell C11- Powerpoint coming away from the wall. Lefthand side wall. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 10:00:00 | Pass | Investigate and replace unit 7 cell c11 gpo
MSA-DCS | WA3980494 | Unit 13, Cell D1- Drain in the cell shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 09:30:00 | Pass | Noll
MSA-DCS | WA3980526 | External gardens - external zone 5, fix 6 broken sprinklers | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 12:09:18 | 2021-02-15 08:00:00 | Fail | LOCATED BROKEN SPRINKLER AND REPLACED
MSA-DCS | WA3980553 | Unit 9, A8 - Spout snapped off sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 12:39:35 | 2021-02-12 16:05:00 | Pass | Replaced ,spout, breech and spindle
MSA-DCS | WA3980572 | Gascoyne - Zone 1 fire alarm | Wandoo Rehabilitation Facility | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 12 Feb 2021 | 2021-02-12 16:57:06 | 2021-03-26 08:26:00 | Fail | Attended site Gascoyne block in alarm at main fip, checked Gascoyne sub fip and found zone 1 in alarm but no indication of location of zoneas no labelling or block plan at sip. Located detector in alarm via remote indicator as it is in the roof above the electrical switchboards adjacentthe fip. Tried accessing detector to replace but unable as there is lack of manholes and ducting in way, will require a manhole to be cutadjacent to electrical switchboard to access detector to replace. Left zone 1 isolated at sub fip and reset main fip, notified site on departure.24/2/21Attended site liaised with Harry from maintenance no manhole had been cut to access detector showed him from other manholes insideGascoyne there is no physical access to detector in alarm he advised he will need approval from head office to cut manhole.26/3/21Returned to site after access hatch was cut by site. Replaced 1x series 65 head and base. Reset alarm, did not return. System normal at timeof departur
MSA-DCS | WA3980596 | Gatehouse - Keywatcher unable to connect with gatehouse or security computer | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-24 11:00:00 | Fail | Work with mark form dcs it fix network and connection issues site keywatcher systems all working all ok
MSA-DCS | WA3980599 | Gatehouse - Camera are not operation on the 4th monitor | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 13:18:13 | 2021-02-16 09:30:00 | Fail | Checked and found Indigovision Control Center not starting up in Comtrol. Further check located the problem to be IndigositeDB folder sharing problem. Rectified the problem and tested all ok after work.
MSA-DCS | WA3980650 | Administration Tearoom - door to courtyard is slamming shut | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-05 15:00:00 | Fail | Unable to attend on time due to covid lockdownReplace door closer.Replace hinges.
MSA-DCS | WA3980659 | Administration controller off line- Unit 2 house 3 expander not responding | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 16:00:00 | Pass | Checked controller in Admin and found fuse blown. Drawing 0.7A so replaced fuse with 2A. Unit 2 House 3 GBUS 1 & 2 faulty even after power cycle.No L.E.D lights on comms line. Replaced 6000 Standard controller from site stock. Tested and all is ok.1 x 6000 controller delivered to site to replace stock
MSA-DCS | WA3980670 | SOG Base- Ladies showers are blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 14:41:08 | 2021-02-12 17:00:00 | Pass | Used drain machine to clear blockage caused by tree roots.
MSA-DCS | WA3980764 | Perimeter Fence Zone 5 camera 2 is blank | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Feb 2021 | 2021-02-13 01:19:26 | 2021-06-03 14:00:00 | Fail | Setup camera in gatehouse equipment room. Used EWP to access camera. Replaced the camera and lens. Replaced coax cable running from the camera to the EC with underground Cat6. Terminated cable into the network switch. Tested ok at the gatehouse. Parts used:Indigo BX630-HD-FC cameraCamera lens15m underground Cat6 cable
MSA-DCS | WA3980765 | External door for West link Sallyport jammed open. | Casuarina Prison | GMP-BR- HO | Building | Security Doors (BU) | AFD Contracting | 0 | CLOSE | 12 Feb 2021 | 2021-02-13 01:10:09 | 2021-02-13 01:00:00 | Pass | 12/02/21 to 13/02/21Troubleshoot West sallyport doors not closing.Issue found with PE Beams.Resolved and all tested okay.
MSA-DCS | WA3990119 | Unit 17, Day room - Air lock entry door locks & staff entry dayroom door locks fail to lock correct | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Feb 2021 | 2021-02-13 15:24:57 | 2021-02-15 12:00:00 | Fail | Investigated fault and found sensor suspected sensor fault. Advised staff the equipment is under warranty by another contractor and they need to contact Honeywell.
MSA-DFES | WA3980174 | Door alarm keeps activating over the last 3 nights, see further notes below | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 12 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-12 11:00:00 | Pass | 12/2/21 - Dylan ParslowFound alarm coming through on undercroft vehicle gate.Realigned magnet, if issue continues recommend replacement with a heavy duty reed switch.
MSA-DFES | WA3980189 | Next to the cooker on the north west corner of the kitchen - GPO switch has split | CFRS Midland | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 12 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-12 15:30:00 | Pass | Complete
MSA-DFES | WA3980213 | Back sliding gate has stopped working and need to be looked at | CFRS Midland | GMP-BR | Building | Steel Fencing & Gates (BU) | Go Doors | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-23 12:30:00 | Fail | Complete
MSA-DFES | WA3980281 | Hose on wall at front of building, copper piping coming out of wall | DFES Rescue Helicopter Base | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 14:45:00 | Pass | Reattach hose cock back on to wall
MSA-DFES | WA3980365 | Engine room/ appliance bay - bay door 2 manual door button | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 19:15:00 | Pass | Attended P1 Call out at Duncraig Fire Station - As reported the engine room appliance door Bay 2 manual button was not working. Our service technician removed the controller and found that the manual switch was loose. This was rectified and the operation of bifold door 2 works correctly there after.Please see attached service reports and Signature Slip.Thank you
MSA-DFES | WA3980512 | Engine room - The 12 V lead has breaks in it. See notes | CFRS Ellen Brook | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-02 14:00:00 | Fail | Sent in quote for rewire
MSA-DFES | WA3980514 | Front Verge- Light in signage is not working | CFRS Joondalup | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-24 10:20:00 | Fail | Will need to return with taller ladder
MSA-DFES | WA3980523 | front engine room door - not working correctly | CFRS Midland | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-13 13:15:00 | Pass | COMPLETED
MSA-DFES | WA3980567 | Potential rat issue in main building. Crew have identified rat faeces in kitchen | DFES Rescue Helicopter Base | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 13:30:00 | Pass | Checked existing bait stations and renewed bait, as required.High levels of mouse activity with 2x internal (Peti) stations having 50%+ bait taken since last general pest service.Added 4x baited Peti stations to internal areas.
MSA-DFES | WA3980625 | Bathroom 2- Fluro light & starter not working | CFRS Murdoch | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 10:00:00 | Pass | Locate faulty light. There was other electrician onsite earlier in the week they fixed all of the lights. Advised staff of work completed.
MSA-DFES | WA3980655 | Decking weathered between demountable buildings- see further notes below | DFES Rescue Helicopter Base | GMP-BR | Flooring | Timber (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-26 13:45:00 | Fail | Decking has been resealed with two coats of decking oil
MSA-DFES | WA3980665 | Cockroaches around station | CFRS Duncraig | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 12:45:00 | Pass | Carried out treatment for cockroaches around external perimeter areas of fire station, using a residual insecticide .
MSA-DFES | WA3980688 | Station entrance right hand side - Colour bond fence panels damaged x2 as have been driven into | CFRS Kiara | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-04-27 15:15:00 | Fail | Replace section of damaged fence
MSA-DFES | WA3980721 | Front door GF- Intercom button is not working - Cant hear any audio | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-18 14:40:00 | Fail | 12/2/21 - Dylan ParslowIntercom speaker faulty, requires replacement.BRAF submitted18/2/21 - Dylan ParslowIntercom Setup and connected to network.IT department to program and setup.
MSA-DFES | WA3980726 | 1 Set of Centre Row of Lights in Pump House have Stopped Working requiring repairs/replace | VFRS Kwinana | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 09:30:00 | Pass | Locate faulty lights. Replaced faulty tubes with new.
MSA-DTAG | WA3980439 | Multiple faulty lights - see notes for locations | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-24 09:45:00 | Fail | Replaced faulty lamps and fitting through court
MSA-DTAG | WA3980529 | Ground, Rear Kitchen door - lock on door doesn't not hold closed,When key locked you can push open | Perth Children's Court | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-16 17:00:00 | Fail | Attended site and viewed the broken lock on the kitchen door.We need to order the parts in and swap the lock out at a later date.Fixed escutcheon plate on boys toilet. Attended site, replaced mortice lock on kitchen door.Date on site: 16/3/2021Time on site: 3:00pm - 5:00pm
MSA-DTAG | WA3980602 | Person in Custody has VRE Disease and Bio clean is required on surfaces | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 22:00:00 | Pass | Job completed as per WO
MSA-DTAG | WA3980684 | Lvl 5, Room R5.4 - Rubber door seal is loose | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 08:30:00 | Pass | NEW RUBBER DOOR SEAL FITTED
MSA-DTAG | WA3980699 | Custody care - An alarm indicated on panel “Receiver 3 System Alarm has changed stat to: Open: | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 11:00:00 | Pass | Attended site. System alarm on Receiver 3. Found CA Office Duress 1 low battery. Replaced battery and restoredsystem alarm.Job completed.
MSA-DTAG | WA3980748 | Custody cell 1 - BIO clean required as person in cell had heath warning of staph | Supreme Court | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 12 Feb 2021 | 2021-02-12 20:41:41 | 2021-02-13 16:15:00 | Fail | Job done as per WO
MSA-DTWD | WA3980137 | West Block, Room W119 & W121- Water filters as flashing | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 12 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 14:25:00 | Pass | Replaced filter. Replaced hot pump.
MSA-DTWD | WA3980139 | Lvl 3, Room A310- External door handle to corridor is damaged | East Perth Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 12 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-15 15:30:00 | Pass | Signed in at security desk then inspected loose door handles. I filled out a jsa and then removed door handles. I fixed the handles back in place and filled out a signature slip to complete the job.
MSA-DTWD | WA3980145 | A Block, Room A301- 2x window hinges to be repaired | Leederville Campus | GMP-BR | Building | Windows (BU) | AWB Co. | 3 | CLOSE | 12 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-12 13:00:00 | Pass | Closed and shut windows as secured in place as requested by site Inspected windows with facilities management then filled out a JSA. I managed to get the loose windows closed and screwed them shut as advised by John the facilities manager. Filled out signature slip to complete the job.
MSA-DTWD | WA3980147 | Lvl 3, Ladies toilet - Basing leaking underneath | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 12 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-12 12:00:00 | Pass | Fix leaking basin and trap
MSA-DTWD | WA3980245 | R Block, Ladies toilets 4th cubicle from right continuously running, isolated in service duct | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-12 15:01:00 | Pass | Attended site,Investigate leaking cistern,Supply and install service kit to inlet valve and outlet washer. Tested works on completion
MSA-DTWD | WA3980306 | Level 1, W109 - repair aircon unit W109 error code E3 | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 10:00:00 | Pass | Investigate unit. Reset fault. Test operation and monitor for 2 hours. No faults found. Possible reason due to air blockage across condenser with flysceen panel. Remove fly screen.
MSA-DTWD | WA3980333 | F block, FG02 Male toilets - Exhaust fan is noisy. Sounds a bit clunky/wobbly. | Carlisle Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 13:45:00 | Pass | Found 2 x v belts falling apart. Picked up new belts. Returned to site. Fitted and adjusted 2 x v belts. Removed isolation and started unit. Checked operation. All okEntered wrong times. Should be 17/2 - 11.00 to 13.45.
MSA-DTWD | WA3980335 | D Block, 1st Floor, Library- 7x blown fluro lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 16:00:00 | Pass | Replace tubes and starters in library d block
MSA-DTWD | WA3980338 | Grounds grass area in central quad has two broken gear sprinklers | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 08:30:00 | Pass | Run through irrigation system and replace faulty sprinklers. Also capped of unwanted sprinklers as directed by Dave Blaber.
MSA-DTWD | WA3980380 | Rooms 17/18 - blinds faulty/damaged, inspect and repair/replace blinds | Jandakot Campus - Annex | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-09 13:28:00 | Fail | completed & Invoiced
MSA-DTWD | WA3980414 | D Block, Gym ladies toilet is blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-12 14:15:00 | Pass | Attended site,Clear blockage to pan by plunger,Knock out section of brickwork rear of pan in duct to expose failed flush pipe rubber. Supplied and installed new rubber and service kit to cistern inlet valve as required for repair. Tested works on completion
MSA-DTWD | WA3980416 | F Block male toilet south, RH cubicle- Toilet bowel inlet seal perished | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 18:00:00 | Pass | Replaced flush cone rubber
MSA-DTWD | WA3980444 | K Block, Repair security fence following break in | Rockingham Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-18 10:00:00 | Fail | Replace bay of chain mesh to rear of bricklaying yard
MSA-DTWD | WA3980450 | A block, Level 1 expo area - Auto door A Block Service IP 1077249 fault | East Perth Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 12:42:00 | Pass | Found that the internal sensor was only working intermittently, replaced faulty sensor and tested, all ok.
MSA-DTWD | WA3980490 | F & D Blocks - Repair faulty door locks to F48 classroom & D1 ladies toilet | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 13:15:00 | Pass | Repair to lock
MSA-DTWD | WA3980533 | student services toilet - both sinks block (see notes) | Jandakot Campus - Hangar | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 15:47:00 | Pass | Unblocked multiple fixtures
MSA-DTWD | WA3980538 | Chalk and cheese cafe - Re install fallen cabinet in Chalk and cheese cafe | Perth Campus B2 | GMP-BR | Furniture | Indoor Furniture (FU) | AWB Co. | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 12:45:00 | Pass | Work completed
MSA-DTWD | WA3980547 | C Blocked , level 1 C118 - FCU 13a/b not turning off at wall buttons | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 15:24:00 | Pass | Attended site and investigated the BMCS logic. Found that the BMCS had set to Time Clock Mode which disablesthe Local Room Push Buttons. Set the BMCS to Push Button mode and tested operation with Barry. Found all tonow be operating correctly. Demonstrated and explained settings and operation with Facilities.Noted the internal clock was out of sync by approximately 1 hour. Updated the controllers time on C Block.Suggest updating the rest of the site controllers internal clocks and carry out a BMCS controls maintenance toensure the rest of the is operating correctly and efficiently.
MSA-DTWD | WA3980622 | Level 3, B324 - Repair/replace lighting as required | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-10 15:22:00 | Fail | Replaced fluros and starters to areas as per list.job completed
MSA-DTWD | WA3980628 | B Block, B2303- Power regularly tripping on north wall | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 16:30:00 | Pass | Attended site and signed in. Met with facilities and checked out classroom. Found the gpos on walls to be running multiple power boards and tripping. Removed old gpos and relocated them to better suit sewing machines and installed extras where needed to elimate power boards everywhere. Tested all okay. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA3980671 | B block, Level 1, B107 - faulty lighting, repair/replace light tubes not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 09:47:00 | Pass | Repalced fualty fluros and starters to light , job completed
MSA-DTWD | WA3980685 | E block - Pressure clean of building work site, path, steps and hardstand between E and N Blocks | Mount Lawley Campus | GMP-BR | Cleaning | Cleaning (CL) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 12 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-10 08:30:00 | Fail | Pressure cleaning
MSA-DTWD | WA3980704 | Q block, Chiller compound - chiller not responding | Joondalup McLarty Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-15 14:25:00 | Pass | NRP attended - Pump was set to local off - turned back on chiller started back up and seems to be working fine
MSA-DTWD | WA3980711 | E Block, Room E58, Entree Bench- Hot water tap is leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 12 Feb 2021 | 2021-02-15 17:00:00 | 2021-02-12 17:30:00 | Pass | Fixed leaking taps
MSA-DTWD | WA3980728 | AMEP reception - description broken wiring issues | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 12 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-04 09:20:00 | Fail | Installed cable management and relocated data points
MSA-DCS | WA3983300 | Internal Perimeter Micro and Perimeter tracks not working | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Feb 2021 | 2021-02-13 10:10:01 | 2021-02-13 09:00:00 | Pass | Attend site, main network controller showing incorrect leds. reset network controller & software. all units are back online. tested all zones. job complete.
MSA-DCS | WA3983311 | unit 1 house 3 - SMS controler power high activating repetitly every 8 secs appears to be online | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 18:00:00 | Fail | Unit 1 House 3 power high. Checked PSU in Gallagher Panel & continuously ticking on the coil. After power cycle issue still persisted. Replaced Gallagher PSU C200440 8A from site stock. Tested and all is in working order.
MSA-DCS | WA3983332 | One of the pedestrian gate is not operating | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Feb 2021 | 2021-02-13 14:46:00 | 2021-02-13 14:30:00 | Pass | Attended site and investigated the fault.Checked power and connections to electric strike of perimeter pedestrian gate.Re-sync data on controller 2 and conducted test.All back to normal and operational.
MSA-DCS | WA3983424 | Boiler in Kitchen not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Materials (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 13 Feb 2021 | 2021-02-17 17:00:00 | 2021-05-02 13:30:00 | Fail | Date - 15/2/2021Make - Cleveland Model - KGL-80-TSerial - 181223057868Technician - Shannon Customer complaining LH unit not working at allFound power and gas going to unit and turned on full but not heating Fault find Upon removing covers unit started working.Fault find and found potentiometer intermittently faulty and causing ignition to go out Found front indicator lights not working Advise manager of intermittent issue but unit is working ok presently. Parts required:1 x Potentiometer x1 1 x Green Led1 x Amber Led1 x Red LED3 x O- rings02/05/21 WS. Found the job had already been completed by another contractor, left parts on site for stock.
MSA-DCS | WA3983428 | Unit 6 -Cell 4- toilet button is not flushing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Feb 2021 | 2021-02-17 17:00:00 | 2021-08-11 15:00:00 | Fail | Arrived on site and inspected found the flush button broken. Need parts. Will come back once the parts are available. Returned, removed old cistern drilled out for new connections installed new all good
MSA-DCS | WA3983429 | high temp reading in equipment room | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Feb 2021 | 2021-02-13 21:53:44 | 2021-02-13 20:15:00 | Pass | Attended site and investigated the fault.Found that temporally installed cooling system in equipment room is not working.Required attendance by air conditioning technician
MSA-DCS | WA3985482 | Perimeter zone 11 - fence alarm is not working. Not going off at all. | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Feb 2021 | 2021-02-14 10:11:19 | 2021-02-14 10:30:00 | Fail | Attended site and investigated the fault.Checked microphonics cable for any damage.Checked EOL resistor.Reseted power to processor.Adjusted sensitivity and conducted test.All back to normal and operational.
MSA-DCS | WA3985483 | In gatehouse equipment room temporary aircon not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 14 Feb 2021 | 2021-02-15 08:09:21 | 2021-02-16 07:45:00 | Fail | Temporary unit now operational
MSA-DCS | WA3990758 | RETROSPECTIVE WORK ORDER- System in alarm, cannot clear-Attended on the 14/2 | Maddington (South East Metro) | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 14 Feb 2021 | 2021-02-15 07:00:00 | 2021-02-17 13:00:00 | Fail | AFTER HOURS CALL OUTDirk Malan attended site AFTER HOURS (12/02/2021):Found Zones 1, 7 & 14 were alarming upon arming the system. Inspected programming and found zones were not set upas exit delay. Reconfigured as such. Tested system, issue still present. Unable to investigate further as Patrol had toleave site. Isolated inputs and armed system for weekend.Work performed by Nathan Groenewald (15/02/2021):Attended site and checked logs, found Zone 7 constantly activated on trying to arm building. Checked Zone 7 status andall tested ok. Removed Zones 7 and 14 from alarm zone delays. Will retest system and check logs on system after todayonce building has been armed.Work performed by Drake Van der Merwe 17/02/2021:Closed job as all working correctly.
MSA-DCA | WA3990107 | Plant room - fault on chiller 1. please investigate | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - In Front of Lift | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 10:30:00 | Pass | Attended site. Chiller 1 to be in fault. Applied tests and checks. Investigation found circuit A to have faulted on a HP lockout. Reset HP and swapped lead lag to monitor chiller operation. Tested operation. Chiller operating correctly.
MSA-DCA | WA3990171 | Level 4 plant room-Chiller 1 requires manual reset, unable to reset. Please check on BMS. | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 11:15:00 | Pass | Chiller 1 reset faults cleared on BMS Chiller 1 manually reset via chiller panel
MSA-DCA | WA3990651 | circuits off in PICA gallery fed from pica Bar distribution board. Please investigate | PICA-Main Building-External Area-PICA Bar Courtyard | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 14:30:00 | Pass | Arrived on site and spoke to Jeremy about fault, found fault to be main switch off, under investigation found a short between the phases tripping out the main switch, rectified phase issue and main switch is holding fine and all tests show perfect results.
MSA-DCA | WA3990656 | Wet Store Pump Room – FIP Sub-indicator panel-Fault on Fire Sub-Indicator panel-see notes | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 14:44:00 | Pass | Attend fault.WIP issue.Collect WIP.Replaced test ok.WIP 3w.
MSA-DCS | WA3989943 | Control room - bottom left hand screens are freezing. | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 09:37:23 | 2021-02-15 10:30:00 | Fail | Rectified and fixed the fault on video wall 4/5, job completed.
MSA-DCS | WA3990015 | unit 2 - PA system not working | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-15 14:30:00 | Pass | System tested no fault found, fault related to phone system not serviced by Seme.
MSA-DCS | WA3990027 | Eyre, B4 - shower head blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 15 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-16 10:29:00 | Pass | No issue with shower, cleared basin aerator
MSA-DCS | WA3990033 | Gascoyne, whole unit - insect infestation | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 15 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-22 11:30:00 | Fail | .
MSA-DCS | WA3990035 | Kitchen rear - bitumen has potholes and is uneven | Wandoo Rehabilitation Facility | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | AFD Contracting | 3 | CLOSE | 15 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-09 12:00:00 | Fail | 19/02/21Attended site to quote works.Extensive repairs required.BRAF to be submitted.Can not complete on first attendance.08/03/21 - 09/03/21Rip up and remove damaged asphalt at Kitchen.Recompact and lay asphalt
MSA-DCS | WA3990042 | wwtp chlorine plant not dosing chlorine | Karnet Prison Farm | GMP-BR- HO | Waste Management | Plant & Pumps (WM) | TRILITY Solutions Pty Ltd | 3 | CLOSE | 15 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 14:25:00 | Pass | Changed chlorine cylinders
MSA-DCS | WA3990062 | Kitchen cool room # 4 still has frozen motors & constantly drips water | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 12:01:08 | 2021-03-29 08:00:00 | Fail | Door switches installed by Danny Hellwigs are operating as intended. No ice build up and unit is at set point. All ok
MSA-DCS | WA3990073 | Coolroom #5: Temperature running high, ice formed at back of fans | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 12:10:02 | 2021-03-02 08:30:00 | Fail | Checked unit and found no ice and unit running correctly. Fault possibly cause by workers not closer door correctly but just enough the activate door switch
MSA-DCS | WA3990082 | Karakin A wing day room - broken lower sash window Approx. 600mm x 450mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-03-12 12:00:00 | Fail | WINDOW RE GLAZED & FILM APPLIED
MSA-DCS | WA3990083 | Karakin A wing laundry - broken window Approx. 450mm x 450mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-03-03 13:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3990085 | Gym - broken window at main entry door Approx. 600mm x 500mm | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-03-12 15:00:00 | Fail | WINDOW REPLACED & SEC FILM APPLIED
MSA-DCS | WA3990112 | Unit 13, Carpet tiles lifting & torn in control room. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-07-29 13:30:00 | Fail | CARPET TILES REPAIRED TO CONTROL POD ONLY AREA
MSA-DCS | WA3990115 | Unit 5, A Wing, Cell A13 - Toilet running continuously | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 14:37:00 | Pass | Nill
MSA-DCS | WA3990118 | Unit 4, Cell A11- toilet leaking from bottom (ground joint) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 11:30:00 | Pass | Nill
MSA-DCS | WA3990121 | CCU, Cell 4 - blocked toilet | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 08:39:56 | 2021-02-15 13:50:00 | Pass | Cleared blocked toilet
MSA-DCS | WA3990126 | Kitchen work area - Mice infestation | Melaleuca Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 08:42:51 | 2021-02-16 15:00:00 | Fail | Carried out a service for rodents at Melaleuca Prison. There were reports of rodents located in the kitchen. Inspected and replenished all existing rodent stations, as well as installing four new rodent stations. Monthly follow ups are highly recommended to monitor and replenish the stations.
MSA-DCS | WA3990129 | Unit 1, Cell B06- Sink & toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 08:44:47 | 2021-02-15 12:30:00 | Pass | Nill
MSA-DCS | WA3990169 | MPU (8), M18 - PVC pipe is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-24 10:30:00 | Fail | Nill
MSA-DCS | WA3990210 | Unit 1, Staff lunch room urn is not working, see notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-15 11:44:00 | Pass | Reset trip run and test all seems okay
MSA-DCS | WA3990263 | Unit 7, regi oven - not warming correctly | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 09:01:22 | 2021-03-23 14:25:00 | Fail | Returned 23/03 and replaced element. Test all elements heating ok.
MSA-DCS | WA3990288 | Cleaning - Workshop-button on polisher handle stuck | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-16 08:30:00 | Pass | Investigate and repair polisher at cleaning workshop
MSA-DCS | WA3990289 | Unit 7, S wing - faulty light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 09:05:11 | 2021-02-15 09:30:00 | Pass | Repaired light
MSA-DCS | WA3990296 | medical centre Faulty light Lamp holder needs repair - see notes | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 09:09:19 | 2021-02-15 12:00:00 | Pass | Repaired light
MSA-DCS | WA3990313 | Pedestrian entry gate is not engaged | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 13:09:18 | 2021-02-15 12:30:00 | Pass | 15/02/21Inspected Gate.Access control issue.SEME Required.
MSA-DCS | WA3990399 | Unit 6, Cell D9 - main light faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 09:51:08 | 2021-02-15 15:00:00 | Pass | Repaired light
MSA-DCS | WA3990404 | Unit 4 - office sink drain blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-15 15:00:00 | Pass | Inspected found thdd we unit 4 office sink blocked. Plunged multiple times to clear the blockage and tested multiple times all working in order.
MSA-DCS | WA3990453 | Dead rodent in the ceiling of the ablusion block of unit 1. | Wooroloo Prison Farm | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 09:32:22 | 2021-02-19 12:10:00 | Fail | .
MSA-DCS | WA3990456 | Unit 6 A23 Sink tap leaking faulty needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-19 14:55:00 | Fail | Rewashed tap
MSA-DCS | WA3990483 | Unit 7 S10 Toilet not flushing needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 10:18:22 | 2021-02-16 08:59:00 | Pass | Replaced inlet valve,Flexi,outlet washer and flushing button to toilet cistern
MSA-DCS | WA3990490 | Administration - 7 lights faulty front of staff toilets (lights requires 2 tubes) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-16 12:30:00 | Pass | Repaired numerous faulty lights in admin
MSA-DCS | WA3990495 | Unit 14, A & C - regi oven not working on AC side, water may of got into the eclectic or fuse gone | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 14:27:56 | 2021-03-10 09:50:00 | Fail | Returned 25/2 to replace on/off switch but now requires a contactor. Returned 10/03 and fitted contactor , fitted and tested ok.
MSA-DCS | WA3990500 | CCTV monitors are not working in Unit 2. | Melaleuca Prison | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 14:21:07 | 2021-02-15 13:00:00 | Pass | Trace KVM fault , rectified and fixed. Job completed.
MSA-DCS | WA3990506 | Unit 2, Cell D6 window not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 11:00:00 | Pass | NEW WINDOW BALANCERS FITTED
MSA-DCS | WA3990507 | SOG pod - perimeter sn1 fault on perimeter alarms | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-16 17:00:00 | Pass | Repaired multiple perimeter communication faults.Tested OKJob Complete
MSA-DCS | WA3990509 | Unit 2, Cell D12 window not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-17 13:30:00 | Pass | FRAME REPAIRED AND SPIRAL BALACES RE NEWED
MSA-DCS | WA3990511 | Unit 6 N1 Toilet continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-19 15:20:00 | Fail | Replced putlet washer and mechanism washer
MSA-DCS | WA3990513 | Unit 6, B5 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-16 14:30:00 | Pass | Nikl
MSA-DCS | WA3990521 | Unit 2, A13 - smashed mirror | Melaleuca Prison | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 10:41:44 | 2021-02-16 15:00:00 | Fail | NEW MIRROR INSTALLED
MSA-DCS | WA3990532 | Unit 2, A13 - smashed sink & broken toilet seat | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 10:46:58 | 2021-02-23 09:00:00 | Fail | Replaced smashed basin and toilet seat.
MSA-DCS | WA3990570 | Reception, interview rooms 3/4 - lights faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 11:06:52 | 2021-02-15 14:00:00 | Pass | Repaired lights
MSA-DCS | WA3990613 | unit 1, A11 - sink damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 11:36:07 | 2021-03-03 09:20:00 | Fail | Replaced leaking hose reel and adjusted pipework
MSA-DCS | WA3990646 | CCU (11)- Cleaning room tap is dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 10:30:00 | Pass | Nikl
MSA-DCS | WA3990678 | Education - Prisoners lunch room door handle has come off. Door can still be opened by a key. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-03-02 10:30:00 | Fail | Replace handles. Replace hinges
MSA-DCS | WA3990687 | Unit 4 - C10 sink broken/smashed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 12:19:10 | 2021-02-24 14:30:00 | Fail | Nill
MSA-DCS | WA3990707 | Unit 15, Cell C7- TV point mech on wall is damaged | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-17 10:30:00 | Pass | Attended site. Repaired TV point in Unit 15, Cell C7.Job completed.
MSA-DCS | WA3990767 | Gardens - retic not coming on around units 6,7. Staions 8,10,11. Suspect wiring fault | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 13:04:12 | 2021-03-04 11:30:00 | Fail | broken wire, couldn't fix so changed to spare wire running alongside.
MSA-DCS | WA3990777 | Roof leak to industries boot shop | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-06-15 08:00:00 | Fail | REPAIRS TO SKYLIGHTS THAT WERE LEAKING INTO THE INDUSTRIES. REMOVE AND REINSTALL AND SEAL, SCREW OFF SHEETING, SEAL JOINS
MSA-DCS | WA3990781 | Unit 2 SO's office air con faulty | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 13:10:18 | 2021-02-15 15:30:00 | Pass | Job duplicated, parts to arrive 16/02/21
MSA-DCS | WA3990809 | Unit 5, House 10- Kitchen mixer tap faulty/rusty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-17 16:15:00 | Pass | Arrived on site and inspected found the the kitchen mixer tap faulty. Collected parts from supplier and returned to the site. Removed the faulty tap and installed new tap. Tested multiple times all working in order
MSA-DCS | WA3990811 | Unit 5, House 10- Exhaust fan to bathroom not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 13:00:00 | Pass | Cleaned fan blades
MSA-DCS | WA3990814 | Unit 4, K Block- 2x round lights to day room not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 14:30:00 | Pass | Replaced 4x Large downlights
MSA-DCS | WA3990834 | Reset, disabled toilet - blocked toilet | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 13:43:49 | 2021-02-15 14:45:00 | Pass | Cleared blocked disabled toilet
MSA-DCS | WA3990925 | Perimeter- Zone 1 is not resetting & Zone 13 constant activation | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 18:56:43 | 2021-02-16 10:30:00 | Fail | Able to reset zones and test ok, spoke to gatehouse and both zones have been a constant fault. Ok now but follow up required ASAP.
MSA-DCS | WA3991017 | MPC 2 camera loss | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 20:06:35 | 2021-02-15 18:46:00 | Pass | Found loose BNC connector on rear on Panasonic vid selector, crimp and test, all ok.
MSA-DCS | WA3991096 | Unit 2 B7 - Key broken and stuck in lock. Please call prior | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-16 12:20:00 | Pass | Attend site to remove broken key from hatch lock in B7 unit 2. Broken part of key handed to Bree in Security as requested.
MSA-DCS | WA3993808 | ***Retrospective work order*** Tanks were over flowing | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-15 20:24:00 | Pass | Attended to overflowing tank, bermad valve passing, removed and lubricated. Reset all ok
MSA-DFES | WA3990449 | Ground and 1 - Mice seen (see notes) | CFRS Fremantle | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 14:00:00 | Pass | Carried out a service for mice to phillimore fire station. Reports of mice droppings around air con units reported byair con crew. Added new baited stations around here as well as rebaiting all current stations onsite.
MSA-DFES | WA3990474 | ground driveway - Antenna for electric gate to driveway has rusted and broken off | CFRS Duncraig | GMP-BR | Building | Steel Fencing & Gates (BU) | Anvil Doors | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 15:15:00 | Pass | Attended Duncraig Fire Station and replaced damaged auto gate Antenna as the old one had rusted through and broken off. Please see attached service report and signature slip for completed works.Thank you
MSA-DFES | WA3990522 | Entry security gate - damaged sensor gate is stuck open | CFRS Hope Valley | GMP-BR | Security | Access Control (SE) | Go Doors | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 14:39:35 | 2021-02-15 13:15:00 | Pass | Complete
MSA-DFES | WA3990630 | Front automatic doors - not opening on exiting | Armadale Regional Office | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 14:00:00 | Pass | Completed - Access Control required for rectifications
MSA-DFES | WA3990880 | front auto doors have to manually overide to get out of building | Armadale Regional Office | GMP-BR | Building | Automatic Doors (BU) | SONTEC WA PTY LTD | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 12:15:00 | Pass | 16/2/21 - Dean SimpsonChecked system and door all ok.Found stand alone timer in the door head out by 4 hours.
MSA-DFES | WA3990948 | Level 1 - Water cooler leaking | DFES Rescue Helicopter Base | GMP-BR | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 12:46:00 | Pass | Hot tank on cooler has completely corroded on arrival. They have used the wrong tools to isolate water and damaged tube and fittings. Replaced tube, plv and all John guest fittings. Replaced faulty cooler with a W2W rental unit. Approved over the phone to do so
MSA-DFES | WA3991048 | Network port p3/7 in office not functioning - see notes | DFES Regional Office - Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 09:15:00 | Pass | Locate faulty data point. The data point was labeled incorrectly out in the field. Test the data point and it is working correctly. Patch the port in. Staff tested the computer and phone and everything is working correctly.
MSA-DTAG | WA3990291 | Court 6 sensor damaged by contractor replacing panels. Needs re-fixing | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-15 11:00:00 | Pass | Attend site. Check court 6 FCU 8 AC warm. Access BMS and found temp sensor reading -59 degrees, fan coil unit is on full heating. Manual override controls so court has cooling.Access court 6 and check sensor. Unable to locate sensor. Further investigation found sensor to have been removed by others as new panelling had been installed over the weekend. Search for sensor and found to be laying on the table. Talk with contractors to find actual original location of sensor so as to find the wiring. Locate sensor wiring behind panel. Remove panel from wall and drill hole for sensor cable. Reinstall panel and pull through wiring. Connect sensor to wiring and mount on panel. Access BMS and check sensor temp, found temp now reading correctly. Clean up area
MSA-DTAG | WA3990298 | Multiple areas - Air conditioner not cooling properly | Mandurah Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-24 11:30:00 | Fail | Carried out gas leak repair on system 1. System working normally.
MSA-DTAG | WA3990549 | Lvl 1, DPP reception receiving s/air temp at 33.7. Cooling appears to be blowing warm air | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 14:00:00 | Pass | Attend site. Investigate AC 2 serving upstairs not cooling. Check BMS and found fan running with 2 stages of cooling required. Supply air temp of 27 degrees. Access roof and check operation of unit. Found indoor fan running but no compressor operation. Check faults and found both stages out on high pressure failure. Reset and check operation, found compressor stage 1 and 2 to start but condenser fans remained off. Isolate unit and isolate compressors. Turn unit on and and carry out testing of condenser fans. Found fan motors to have power, further testing found the neutral connection to be loose and when moved fell off. Isolate unit and reconnect fan motor neutral. Deisolate and check operation, found condenser fans to now start and operate as normal. Deisolate compressors and test unit operation. Both stages of cooling now on with supply air of 14 degrees and return air of 28 degrees. Monitor operation. Unit now working as normal.
MSA-DTAG | WA3990597 | 1987 L1 Sheriff's Office Front door is not opening properly or not opening at all - see notes | Supreme Court | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 15:00:00 | Pass | Sheriffs Office is was found to be under warrantly as access control was only recently installed. Checked access control operating as usual by using provided swipe card. Found auto not releasing due to mechanical issue. Auto door technician to attend site
MSA-DTAG | WA3990754 | Level 5, lift 9 - showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 11:00:00 | Pass | Car door Belt replaced Skates adjusted Lift runningTo be closed out at $0
MSA-DTWD | WA3990017 | classroom D5 - bad smell coming from floor waste | Murdoch Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 15 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-08 15:30:00 | Fail | Investigate and solve smells in d5
MSA-DTWD | WA3990023 | Glasshouse N01 NE side - 4 x faulty evap may required pads change and the belt is slipping | Murdoch Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 15 Feb 2021 | 2021-02-17 17:00:00 | 2021-04-19 13:33:00 | Fail | Checked over the glass house s.e corner evap, needs new filters and frames unit very rusted . Das to be submittedDAS submitted and approved, 4-5 weeks for parts to arrive.9/4/21: Removed the old filters, fitted the new ones and replaced the belt , disposed of the waste
MSA-DTWD | WA3990038 | B block, level 2,B209 - Swipe Lock doesn’t release B209 passage entry | East Perth Campus | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 15 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 12:00:00 | Pass | replaced lock
MSA-DTWD | WA3990133 | A block, Cafe, A120 - Door is sticking (very hard to close) | Leederville Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-06-04 15:30:00 | Fail | Work completed
MSA-DTWD | WA3990365 | AHU 9- Noisy bearing | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-24 15:03:00 | Fail | Specialist contractor attended and carried out isolation and replacement of AHU 9 motor bearings. Alignment carried out and confimed operation. Equipment operation restored.
MSA-DTWD | WA3990396 | E Block, Deli stand up fridge behind counter not cooling properly | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 12:00:00 | Pass | Investigate unit. Found drain blocked. And door not closing causing coil to ice up. Unblock drain. Pack door up 3mm. Door now stays closed. Note condensate drain has no floor wastes. Facility manager notified.
MSA-DTWD | WA3990397 | E Block, Deli under counter fridge not working | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-09-02 09:00:00 | Fail | Travel to workshop to collect materials for tomorrow morning.Remove all items from fridge. Dissassemble fridge to find pan heater placement. Unable to locate. Original QRF sent and noted that job requires 2 x people to complete works.Carry out repairs as per previous QRF. Job complete.
MSA-DTWD | WA3990454 | Room D016 A/C is not working | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | Precise Air Group | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-15 13:00:00 | Pass | Accessed site and tested unit ac not operational. Tested components and found operation wall switch position not locking in position. Rectified switch component seizing. Tested ok
MSA-DTWD | WA3990462 | H block, H1 – No Power to AC | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 09:15:00 | Pass | Located breaker board as no power at unit. Reset tripped breaker and restarted unit. Checked operation. All ok.
MSA-DTWD | WA3990476 | A blockm A131, 1st floor - FCU 22 not turning on | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-04-07 13:00:00 | Fail | Unable to complete works due to classroom being occupied. Also will need a scaffold as the unit is above desks and computers etc. Precise Air to liase with FM from Joondalup Campus to organise a time for access.
MSA-DTWD | WA3990484 | B & G blck - External light between B & G Block not working | Bentley Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-25 07:30:00 | Fail | Attended site early hours. Began investigating cabling to plant room and pe cell. Tested back through ducting and light fittings. Found circuit to be wired through the emergency lighting feed. Meaning that it never turns off. Altered wiring to be fed from the fuse in cabinet of the em controls. Plant room and pe cell can now be isolated. Put ducts and lights back together. Isolated pe cell and replaced with new. Tested all lights to be working. Labelled switchboard and em control to identify for future. All okay. Job completeAll notes on this job have been deleted, had to restart job. Job actual start by Xavier on the 16th
MSA-DTWD | WA3990524 | Block 6, TIG Welding room Metal Fab 2- No power to power point RWB15 | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 11:30:00 | Pass | Attended site and signed in. Located faulty outlet. Found all blown phases to welder. Tested welder and found it to be shorted. Tagged out welder and replaced fuses with site supplied. Tested all okay. Job complete
MSA-DTWD | WA3990533 | Block 3, 3B7 light engine test cell- Top door hinge torn out of frame | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-16 10:00:00 | Pass | Adjust hinges and rehang doors to test cell
MSA-DTWD | WA3990536 | Block 7, Ladies toilet - Water leaking from mixer tap on first basin | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-22 14:00:00 | Fail | replaced tap and installed mini stops
MSA-DTWD | WA3990557 | house 2 - gas hot water not working | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 13:30:00 | Pass | Repaired gas HWS to House 2
MSA-DTWD | WA3990563 | U Block, Keys are broken for B13, U, 5 & 239 | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-19 08:30:00 | Fail | job completed - replaced keys
MSA-DTWD | WA3990576 | A Block, Ladies cubicle button wont turn off | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-15 12:35:00 | Pass | COMPLETED
MSA-DTWD | WA3990578 | level 2, L2 Cafe - exhaust fan to cafe keeps tripping | Perth Campus B1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 11:54:00 | Pass | Parts collected from suppliers. Returned to site gained access and confimed isolation. Removed and replaced faulty contactors on equipment. Carried out operation test. During testing cable into isolator at fan was also found to be damaged. This has been repaired. Fan has been restored to normal operation. Work area left tidy. .
MSA-DTWD | WA3990582 | block E ground deli no airconditioning | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-16 10:00:00 | Pass | Investigate deli Evap cooler. Organise replacement parts from gamatos. Return to site. Organise roof works permit. Isolate water and electrics. Remove faulty components. Test unit operation. Set float level and water flow rate. Job complete.
MSA-DTWD | WA3990618 | A and C block chillers not working no air con - Precise please contact NRP | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 15:37:55 | 2021-02-15 14:00:00 | Pass | Investigate chillers. No faults present. Chiller not running and no run status. NRP to attend site to access BMS. Chiller water pump switched over and chiller now running. Chiller running to design with no faults present. Job complete.
MSA-DTWD | WA3990833 | D Block, Room D103- Air con not working | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-04-06 14:00:00 | Fail | Attended supplier and collected parts. Attended site and signed in. Accessed unit isolated and completed replacement of fan motor, fan blade, capacitor and pcb. Test ran system. Found unit to start and run with out fault.
MSA-DTWD | WA3990844 | A Block, Room A412- 4x floros are not working- see notes below | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 08:22:00 | Pass | Replace faulty lamps and starters
MSA-DTWD | WA3990890 | N block ground N05 Blue 13 RCD in DB3 cannot be reset as well as some of the Red 2 GPO's in the room | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 15:19:00 | Pass | Replaced faulty rcd to circuit B13 all working .
MSA-DTWD | WA3990905 | S block S107 air con not working | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-03-22 10:00:00 | Fail | Picked up part and attended site. Completed pre start paperwork and signed in. Accessed unit isolated and removed/replaced 1x electronic expansion valve.Reinstated power and test ran system. Observed system run and left unit in good working order.
MSA-DTWD | WA3990907 | block 1 ground floor - Customer Service Kitchen Mouse dropping found in kitchen and cupboards | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 10:30:00 | Pass | Carried out a service for rodents to Thornlie TAFE. Staff reported mouse droppings within the cupboards of the customer service kitchen. Inspected the area and determined the droppings were actually belonging to American cockroaches. There are a few gaps around the pipe penetration where cockroaches Could gain access. Gel baited all these potential harborage areas. Also rebaited all rodent stations within the vicinity.
MSA-DTWD | WA3990911 | Level 5, plant room - HWS leaking | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 15 Feb 2021 | 2021-02-22 17:00:00 | 2021-04-07 17:30:00 | Fail | Installed new hws as old tank was split
MSA-DTWD | WA3990916 | Admin, Level 1- kitchen wall mounted Zip auto boil - water not getting hot enough | West One Services | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-16 16:40:00 | Pass | Replaced element and calibrated. Unable to get programme slip signed as everyone had gone home.A40139091G Level 1 Training Room replaced element to Autoboil Zip unit tested calibrated
MSA-DTWD | WA3990963 | Stores area evap cooler continuously leaking water | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-09-08 16:00:00 | Fail | Accessed site , completed relevant sign in procedures and covid safe app wa requirements, filled out roof access permit , gained access to roof , continued investigation of 4x evaporative units , found unit components to ge old and near end of life with potential to fail before next maintenance, qrf submitted
MSA-DTWD | WA3990964 | E Block, EG08 Office - Split System leaking water down wall and on floor | Carlisle Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-04-20 11:39:00 | Fail | On inspection of system, found crack in back chassis. Condensation forming here and running down to front of unit, dripping in room.
MSA-DTWD | WA3990970 | J block ground J127 dropped a phase on the DB in room - see notes | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 15 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 15:20:00 | Pass | Inspected power loss to room found to be white phase dropped out due to cable screwed on insulation .repaired job completed
MSA-DTWD | WA3991050 | G block G20 External Door Closer is faulty | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-04 16:45:00 | Fail | New door closer installed with stainless steel cover plate installed over existing door closer mount to cover up existing holes. This prevented the door having to be painted. Existing door closer was not the same as this was an older model, and had to be replaced with a smaller model.
MSA-MRWA | WA3990362 | Level 1 - Please investigate meeting room AC. Not working | Don Aitken Centre MRWA Head Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 15 Feb 2021 | 2021-02-15 13:30:44 | 2021-02-16 11:00:00 | Fail | Fault reset
MSA-MRWA | WA3990547 | Asphalt and Bitumen Laboratories - air conditioners not workinf | Materials Engineering Branch-Asphalt Lab-Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-15 12:30:00 | Pass | Quote to be submitted
MSA-MRWA | WA3990599 | Soils office - The aircon unit in the soils 2 offices is not working correctly. (see notes) | Materials Engineering Branch-Asphalt Lab-Ground Floor-Office-Old Soil Lab | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Feb 2021 | 2021-02-16 17:00:00 | 2021-02-17 12:00:00 | Fail | Unit repaired
MSA-DCA | WA3993284 | New Museum Area- Fume hood is not working. It disconnects after a few seconds and goes into alarm. | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Equipment | Electrical Equipment (EQ) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-03-19 16:30:00 | Fail | Attended site. CRC extract fume hood not operating correctly. Applied tests and checks. Investigation found inline extract fan US. Requested safe access via boom lift. Raised BRA for boom lift and additional labour. Returned to site removed fan motor & replaced motor. Reconnected ductwork and tested operation. System operating correctly.
MSA-DCA | WA3993383 | Broken light fitting - suspected broken ballast | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Corridor - From Stairwell 1 to Laundry | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-17 11:00:00 | Pass | Replaced faulty ballast and rectified lighting fault
MSA-DCA | WA3993563 | dropped below floor level | PICA-Main Building-Level 1-Lift Foyer | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 13:45:00 | Pass | Completed non chargeable
MSA-DCA | WA3993805 | concourse, female toilets - toilets not flushing | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-AG.26 - Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 09:05:00 | Pass | Replaced faulty inlet valve and bellow
MSA-DCA | WA3993809 | ground floor Cafe - constantly running tap | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Cafeteria | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 10:00:00 | Pass | Rewashed taps
MSA-DCA | WA3993823 | Khuloud & David’s Office AC unit is dripping water.- see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 11:30:00 | Pass | Attended site. Ac system in staff office leaking water. Applied tests and checks. Investigation found condensate drain blocked. Cleaned and cleared condensate drain. Tested flow and operation. System operating correctly.
MSA-DCA | WA3993936 | Multiple alarms after power failure | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-18 12:09:00 | Fail | DLGSC representative informed me that the scheduled power shutdown works at AGWA had been completed. Monitored alarms off site. All active alarms cleared. After shirt period a few P1 hi humidity alarms popped up, 60%rh+. Set up phone for remote access but password expired. Requested password update from DLGSC IT. Job raised. Attended site to find AGWA in LOCAL. Both Chillers staged on. Water temps at setpoint. All alarms cleared. Building rotated back to ETS.
MSA-DCA | WA3993948 | Lift No1 out door damaged unable to open lift stuck on L4 | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Lift Storage | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | COMPFIN | 16 Feb 2021 | 2021-02-16 19:44:54 | 2021-02-16 17:08:00 | Pass | Found lift as reported with slow door landing panel dislodged. Accessed top of car for assessment and found door header hanger and top hat bracket that attaches to the door severely damaged. Removal of door and brackets required once second assistance is available. Left unit shutdown and informed duty supervisor.Note: level 4 is currently a construction siteto be closed out at $0 cost
MSA-DCS | WA3993171 | Internal alarm monitor INDIGOWS1 not working | Albany Regional Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Feb 2021 | 2021-02-16 14:32:06 | 2021-03-03 09:00:00 | Fail | 17/02/2021. Instructed control staff to swap HDMI extender connection to make the alarm screen visible on another working monitor. 03/03/2021 Remove existing failed monitor from wall bracket, mount wall bracket on replacement monitor and reinstall on wall. Configure monitor and reconnect to HDMI extender. Confirm alarm video displaying on alarm activation.
MSA-DCS | WA3993175 | Special operations bay - Gallagher system fault | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Sapio Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 06:33:04 | 2021-02-16 11:00:00 | Pass | Issue with Gallagher login , reset server and restarted services. All restarted and tested ok. Job complete
MSA-DCS | WA3993204 | Gardens, External Reticulation - Zones 3 & 4 mainline leak | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 07:14:31 | 2021-02-16 16:00:00 | Pass | REPAIRED CRACKED PIPE AND RESET CONCRETE
MSA-DCS | WA3993215 | Unit 3, C wing, dayroom - door handle broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 16 Feb 2021 | 2021-02-16 11:30:44 | 2021-02-16 11:10:00 | Pass | Attend site, dayroom door lock in Unit 3 C Wing requires new handle set and old thread requires to be tapped out. Re-attend site to refit handle set after re-tapping thread in handle set.
MSA-DCS | WA3993216 | Unit 4, D15 - Mesh damaged in sliding window | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 07:36:13 | 2021-02-16 14:30:00 | Pass | MESH REPAIRS CARRIED OUT
MSA-DCS | WA3993289 | Unit 2, Seniors officers office - Air Con is not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-16 14:18:03 | Pass | Checked over aircon,found main fuse blown,isolated power replaced fuse with spare one on site,turned on and tested all running ok.
MSA-DCS | WA3993294 | Unit 5, control room- Airconditining is functioning very poorly | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-16 14:19:17 | Pass | Checked over aircon,found someone had turn on via button on unit instead of remote,reset and tested all ok at present.
MSA-DCS | WA3993311 | Laundry - Number 2 washing machine, door hard to close | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 09:06:15 | 2021-04-13 14:36:00 | Fail | Unimac HF730 Washer adjusted switch and door latch - replace door microswitchSpeedqueen HF575 Door handle hinge assy worn - to replace
MSA-DCS | WA3993316 | Admissions, Senior office- light not working ( blown electronic Ballast) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 08:30:00 | Pass | Repaired light
MSA-DCS | WA3993317 | Unit 13, D8 - Cell D8 shower screen leaking onto bed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Midolo Building Services | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-03 11:30:00 | Fail | SHOWER SCREEN LEAK REPAIRED
MSA-DCS | WA3993376 | administration area - Aircon not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 09:38:18 | 2021-02-16 14:54:00 | Pass | Complete. replaced circuit breaker
MSA-DCS | WA3993487 | Entry building staff room- smell coming from both set of showers | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-24 13:40:00 | Fail | COMPLETED
MSA-DCS | WA3993510 | Visit prisoner toilets leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-23 09:30:00 | Pass | Repaired one toilet will require more parts for the second toilet, replaced inlet vave and flexi hose
MSA-DCS | WA3993512 | Unit 1, Day Room- water cooler tap leaking | Karnet Prison Farm | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-10 13:17:00 | Fail | Replaced both taps to cooler.REPLACED 2 X LS100 TAPS ON LS100 CHILLER UNIT TESTED ALL OK A40189308M
MSA-DCS | WA3993517 | unit 1 showers exhaust fan covers broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-10 16:00:00 | Fail | Investigate unit 1 shower exhaust.Source replacement parts.Replace unit 1 shower exhaust.
MSA-DCS | WA3993527 | Unit 2 top landing toilet exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-24 15:00:00 | Fail | Replace Unit 2 Top Landing Exhaust Fan
MSA-DCS | WA3993548 | Investigate PA system not operating correctly in Units 2 and 4. - see notes | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-04-23 14:15:00 | Fail | Report submitted to PFM - new work order to be provided if proposed works are to proceed.
MSA-DCS | WA3993601 | Medical Centre, Reception- Air Con not cooling | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 12:27:27 | 2021-03-02 08:37:27 | Fail | Arrived on site and signed in tools,isolated power,removed faulty option card and fitted new one,turn back on and tested all running ok at present.
MSA-DCS | WA3993605 | Jeelia, A&C - ceiling fans damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-23 14:00:00 | Pass | Investigated faulty fans Jeelia a and c wing
MSA-DCS | WA3993608 | Oval ant infestation | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-10 09:15:00 | Fail | .
MSA-DCS | WA3993667 | mechanic in industries office ceiling fan making loud noise | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 10:30:00 | Pass | replaced ceiling sweep fan in mechanics office
MSA-DCS | WA3993680 | mechanic in industries light switche falling off wall and broken | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 12:59:17 | 2021-02-17 08:30:00 | Pass | Replaced light switch in mechanics
MSA-DCS | WA3993682 | mechanic in industries over head lights faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-10 12:00:00 | Fail | Replaced 5x Hibays in mechanics area
MSA-DCS | WA3993695 | mechanic in industries electric HWS not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 11:30:00 | Pass | Reset thermostat on hot water unit
MSA-DCS | WA3993767 | Admin- hot water urn on wall not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-03 09:30:00 | Fail | Unit leaking and rusted. Will need replacement. INSTALLED NEW ZIP ECONBOIL REMOVED OLD TO TIP NEW SERIAL NO A40421574G ZIP SN 202101140504 CONNECTED TO EXISTING MAXIFLOW SCALE SYSTEMRemoved faulty wallmount and installed a new system.
MSA-DCS | WA3993842 | Unit 5 control room Fire alarm air flow fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 14:02:50 | 2021-02-16 17:10:00 | Pass | BG 16/2/21Unit 5 A wing Vesda pipe 4 urgent low airflow. Cleared out all pipe work. Airflow spiked to 250% after clean out. Normalised to clear highairflow fault now present. Raw air flow was 1200. Other pipe on Vesda showing raw flow of approx 300-400. Recommend return visit to cleanout remainder of pipes and sample points. Some sample point ends missing for capillary piping. Revisit scheduled under another task where tubing and sample points are being replaced.
MSA-DCS | WA3993850 | whole of education A/C not cooling | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 14:10:37 | 2021-02-26 14:45:00 | Fail | 3/4 of system is running correctly. 1 stage is being pressure tested for leak check. Will be back online and complete on next attendance.
MSA-DCS | WA3993855 | Kitchen, prisoner toilets - Right hand basin has no grate in sink waste | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 14:12:16 | 2021-02-17 13:17:00 | Pass | Replaced waste and adjusted pipework
MSA-DCS | WA3993918 | medical centre officer has key stuck in lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 16 Feb 2021 | 2021-02-16 19:26:13 | 2021-02-16 16:40:00 | Pass | Attend site, key stuck in lock. Mortice lock has broken. New lock installed.
MSA-DCS | WA3993946 | Zone 9 outer alarm keeps activating | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Feb 2021 | 2021-02-16 19:46:19 | 2021-02-17 15:21:00 | Fail | Tested zone 9 inner microwave, all tested ok. Zone 9 has been troubling for some time now, will need to follow up for possible cable issue? - Recalibrate the IR beam and test the zone, ok and working as normal.
MSA-DCS | WA3993977 | Unit 2A- Cell call fail in cells 3-7 | Bunbury Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Feb 2021 | 2021-02-17 01:23:57 | 2021-02-17 13:00:00 | Fail | Prison was contacted last night regarding this fault. We were advised that due to the time of day Prisoners in the affected cell would be relocated to vacant cells in Unit two as the site was locking down for the night and staff number was at minimum. Attendance this morning was approved.17/02/2021 0630. On site and investigating fault. Found fault to be with one CI-8 card. Replacement CI8a card was obtained and cards replaced. Connection wiring rearranged to suite change in controller card. Adaptor cables wired to existing cell call cables, controller powered up and cell calls tested. All cells found to be faulty last night tested to Local control. Good audio both ways.
MSA-DCS | WA3993980 | External Perimetre - 1A-MW3 is not holding/faulty | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 19:42:15 | 2021-02-17 11:00:00 | Pass | Rectified and fixed southwest mw, job completed.
MSA-DFES | WA3993267 | Engine Bay- Change room 4- Broken thread connecting the tap to the hand basin | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 09:00:00 | Pass | Investigate job on hand source part shut water off replace mixer install mini stops test job complete
MSA-DFES | WA3993361 | Administration Building, ladies toilet, opposite reception - water leaking & flush button jammed | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 12:15:00 | Pass | Investigate leaking toilet and sticky buttons located admin building detail toiletIsolate water supply to toilets, remove leaking mini stop and Flexi hose, supply and install new mini stop, Flexi hose and cover plate, turn water on and test operation/check for leaksLubricate cistern button sand test operationPack up and clean up worksite
MSA-DFES | WA3993378 | Bathroom No 3 - Flick Mixer has failed | CFRS Murdoch | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 15:29:00 | Pass | Replaced Mixer tap
MSA-DFES | WA3993856 | L1 patio lights not working - see notes | VFRS Mandurah | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 14:15:00 | Pass | Arrived onsite. Located lights. Replaced globe in one. Others needed new fitting. Left site to collect gear. Back on site. Replaced LED batten for new and old toilet light falling from ceiling for new oyster light. All working
MSA-DFES | WA3993900 | Operational Delivery - Carpet underneath Chris Hudson’s desk is torn and fraying | FESA RHQ - Forrestfield | GMP-BR | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 12:15:00 | Pass | REPAIRED CARPET UNDER CHRIS HUDSON'S DESK
MSA-DFES | WA3993910 | General Area- float/sensor for the water tank is not working | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 11:30:00 | Pass | Investigate job ,after multiple test found float arm and ball failing sourced part replaced for new test job complete
MSA-DFES | WA3993939 | Repair A/C as per quote # 32768 | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Ducted Split System (AC) | AWB Co. | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-12 08:00:00 | Fail | repairs to existing AC system
MSA-DFES | WA3993981 | Main admin building - Fire panel gone into error cannot reset | FESA RHQ - Forrestfield | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 16 Feb 2021 | 2021-02-17 00:21:01 | 2021-02-16 22:00:00 | Pass | Ows was in fault sounding. A loss of power caused the generator to activate putting the ows in fault. Hard reset rectified the fault.
MSA-DTAG | WA3993492 | Ground Registry - Flickering light in Registry above Counter 4 | Armadale Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 08:15:00 | Pass | Attended site and signed in. Awaited access from security. Found light flickering in registry. Supply and replace tubes and starters to lights. Used 12FT ladder to access lights. Signed out. Job complete
MSA-DTAG | WA3993509 | L5 Water Fountain near Court 57 (Hay Street end) low water flow | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-22 10:40:00 | Fail | COMPLETED
MSA-DTAG | WA3993531 | Level 5, Male public toilets near 57 (hay streeet end) - toilet blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 14:28:00 | Pass | COMPLETED
MSA-DTAG | WA3993712 | Roof - Air con unit that services Courts 2, 3 & 7 intermittently fails | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-17 15:30:00 | Pass | Attend site. Check courts 2,3 and 6. Found court 6 AC working. Check court 2 and 3 and found not running. Access plantrooms and check units. Found both unit to be locked out. Remove panels and check safety controls found units to be tripped on high discharge pressure. Reset and check operation, found court 3 unit to reset and start operating. Found court 2 to reset then trip out again. Further investigation found air in the condenser water pump causing cavitation. Access roof cooling tower abd found water level in tower to be too low. Found make up water from float valve just trickling out. Trace pipework down to ground level and found old water meter installed inline. Check pressure in front of meter and found to be good. Check pressure after meter and found to be restricted. Programmed organised plumber to attend site and replace old meter with straight section. Meter replaced, access cooling tower and found to be full. Check float valve operation and found to have plenty of water p
MSA-DTAG | WA3993886 | Roof - water pressure feed to cooling tower is low. attendance 17/02/21 see notes) | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 11:50:00 | Pass | Removed section of corroded pipe and replaced it with copper pipe
MSA-DTAG | WA3993909 | ground custody cell 1 Bodily fluid around the toilet | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 20:30:00 | Pass | Body fluid around toilet in Cell 1.
MSA-DTWD | WA3993195 | Level 1, C108 - Repair rack tp C block riser cabinet | Leederville Campus | GMP-BR | Equipment | Electrical Equipment (EQ) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 16 Feb 2021 | 2021-02-22 17:00:00 | 2021-03-30 12:45:00 | Fail | Complete
MSA-DTWD | WA3993246 | Processing Plant room - water not chilling for plant | Munster Campus (ACEPT) | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 16 Feb 2021 | 2021-02-16 17:00:00 | 2021-03-23 10:30:00 | Fail | Found the process chiller running ok at 40% compacity , after the students had finished we ramped it up to 88% compacity the head pressure increased and had trouble maintaining the water temp . Rang manufacturer and needs a new controller and had charge to be re weighed in.Quote submitted to remove the gas and reweigh in charge , waiting for approval.16/3/21 arranged to attend on the 23/3/21 through Rick at the tafe. 23/3/21: Carried out qouted works on the chiller. Removed the old gas charge and weighed in the correct charge. The tafe will test on the 25th , if it still doesn't cope with the heat load a bigger kw capacity chiller would be required to cope. We will forward a quote
MSA-DTWD | WA3993260 | B Block Male toilets - Left side W.C blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-16 15:44:00 | Pass | Unblocked toilets
MSA-DTWD | WA3993261 | Glasshouse No1 Southwest side Evap No4- Water pump jammed not working | Murdoch Campus | GMP-BR | Mechanical Services | Pumps (MS) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-23 10:30:00 | Fail | Checked the evap over found the pump siezed, picked up a new one from the suppliers.ATTENDED SITE AND SIGNED IN. LOCATED UNIT AND INSTALLED NEW WATER PUMP. TEST RAN UNIT ON COOLING AND FRESH AIR SETTINGS. UNIT NOW WORKING WELL. JOB COMPLETE
MSA-DTWD | WA3993264 | P Block, Compressor - not working | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-31 15:31:00 | Fail | Attended site and signed in. Located compressor room. Found new box installed. Replace fuses with new. Tested machine and had to rewire new control box to run as an auto restart after getting to pressure. Tested all okay. Showed site running and ready. Signed out. Job complete
MSA-DTWD | WA3993266 | Exterior Carpark - Recoat Crossover markings due to Graffiti near Skip Enclosure, Driveway | East Perth Campus | GMP-BR | Cleaning | Graffiti (CL) | AWB Co. | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-20 12:30:00 | Fail | Work completed
MSA-DTWD | WA3993272 | Ground floor, Canteen - Pie warmer The glass sliding doors intermittently keep jamming. | Murdoch Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-22 11:45:00 | Fail | COMPLETED
MSA-DTWD | WA3993276 | House 16- Faulty water meter | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-16 13:00:00 | Pass | job completed - Dig up and repair pipe work near meter House 16
MSA-DTWD | WA3993373 | Foyer faulty alarm sensor | Kwinana Automotive Centre | GMP-BR | Security | Security Management System (SE) | BJ SYSTEMS | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 16:15:00 | Pass | Area 2 ATLA, replaced input 15 south west PIR, all tested ok
MSA-DTWD | WA3993392 | Entry Foyer - Intermittent fault on Fire Panel | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 11:30:00 | Pass | Inspected panel. Replace 6x AA batteries - fault cleared.
MSA-DTWD | WA3993422 | BLD 822 Level C fire Alarm going off Faulty | Muresk Institute | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 10:40:00 | Pass | Zone 5 detector base - back room faulty - hidden corrosion on terminal.Replaced base conventional base - all ok. Fault cleared,
MSA-DTWD | WA3993428 | UO15 - Evaporative aircon constantly dumping water | Balga Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Precise Air Group | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-12-06 11:28:00 | Fail | Completed quoted works
MSA-DTWD | WA3993432 | B block B2305 – 2x faulty ceiling GPO’s | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 12:15:00 | Pass | Attended site and signed in. Completed jsa. Found pendant points in room been isolated. Found pendants on site. Reinstated and connected them to either end of the room near the desks. Tested all ok. Job complete.
MSA-DTWD | WA3993436 | Removal of fallen trees and prunning of unsafe branches | Mandurah Campus (formerly Peel) | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-05 08:15:00 | Fail | WORKS COMPLETED6 STAFF @$100 PER HOURS X 1.5 HOURS = 9 HOURS = $9002 VEHICLES; CHIPPER TRUCK AND CHERRY PICKER @ $100 PER UNIT X 1.5 HOURS = $300TOTAL ACTUALS $1,200BUDGET BRA $2,450CLAIM $1,200 PLUS GST
MSA-DTWD | WA3993507 | P Block, Play Area- Store roller door is damaged | Midland Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-29 13:00:00 | Fail | WO-02622482 - Door has been vandalised I have made building secure and measured up for new door?Braf approvedWO-02647642 - Remove old door ,fit new door , door tested working well
MSA-DTWD | WA3993526 | E Block, SK3 left hand side ceiling light is faulty | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 14:30:00 | Pass | Replace 4x 28w tubes and 2x electronic ballasts in E block SK3.
MSA-DTWD | WA3993560 | Rooms AF1 & AF2- Air Con unit AC2 appears to be working but not cooling | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-05-25 09:02:00 | Fail | Attended site and signed in and booked out keys. Found air-conditioning system number two in block not cooling properly, stage one and stage two short of gas. No obvious signs of leaks , as units are on R22 and 25yesrs old a Braf has been submitted to upgrade.26/3/21: Quote to remove the old unit and install splits in the class rooms has been submitted.
MSA-DTWD | WA3993603 | E Block hallway between Kitchens entrance the vinyl floor is lifting at the join again, trip hazard | Joondalup Kendrew Campus | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 07:30:00 | Pass | Vinyl repairs completed in E Block corridor. Note start/completion date was 3/2/21 not 17/2/21
MSA-DTWD | WA3993610 | E Block - Exit light not working in LSK east end exit | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 14:45:00 | Pass | Attended site and signed in. Located large scale kitchen and found exit sign and light fitting near exit door not working. Looked into light fitting and found to be disconnected. Reconnected and fitted to roof panel. Supply and replace exit sign as water ingress caused failure. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3993611 | • B Block - No power to A/C in B2421A - please investigate | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 12:00:00 | Pass | Attended site and signed in. Located room b2421. Could not find air con faulty. Checked out rooms near by and found room 2425a had a air con not switching on. Tested remote to be calling to turn on. Went on the roof and located condenser unit. No power to unit. Opened isolator and found juice coming in and out. Retest condenser and had power. Turned isolator on and off a few times and retested all okay. Went back to aircon and switched on and ran up. All okay. Signed out. Job complete
MSA-DTWD | WA3993612 | E Block - Walk in fridge LSK Room E38 - water in light fitting | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 14:00:00 | Pass | Attended site and signed in. Located large scale kitchen coolroom and found light fitting holding water and leak from roof. Supply and replaced with new led weatherproof fitting. Installed junction box and sealed over water ingress point. Tested all okay. Signed out. Job complete
MSA-DTWD | WA3993635 | L1 carpark Refill/ replace Fire extinguishers due to incident - see notes | Perth Campus B5 | GMP-BR | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Critical Fire Protection & Training | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 11:30:00 | Pass | Replaced the below extinguishers:1X 2Kg Carbon Dioxide - new barcode A40275740I (A151 B5 Outside Art Studio)1X 9Kg ABE Power Type - new barcode A40275739Q (A113 Print Room near Chem Store)3X 4.5Kg ABE Power Type - new barcode A40275742K (Tool Room Workshop), A40275323F (Workshop) and A40275738P (B4 Ground Level)1X 5Kg Carbon Dioxide - new barcode A40275741J (A110 outside)
MSA-DTWD | WA3993710 | E block, ground level E40 - the swipe access does not always unlock door when swiped | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-16 15:15:00 | Pass | Replaced faulty strike E Block E40 door. All ok
MSA-DTWD | WA3993792 | Block 3, Mezzanine Floor- A/C not working | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-25 16:30:00 | Fail | Checked out the high wall split in 3F , needs parts for the condenser, ordered partsAccessed the roof , working at heights. Replaced the condenser fan motor, blade and board on the split.
MSA-DTWD | WA3993830 | Wood Workshop- booth extractor faulty | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-25 11:00:00 | Fail | Returned to site with roof kit. Located faulty exhaust fan and discovered the fan belt to be damaged. Replaced fan belt and tested. All in working order.Complete
MSA-DTWD | WA3993853 | Training on fire panel settings T block , B Block & S Block.- see notes below | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 11:30:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochWork Order Number: WA3993853 Priority #: 2Call out Date: 16/02/2021Target finish: 19/02/2021WO# Value: $1,000Original information:Training on fire panel settings T block , B Block & S Block.We require Firesafe to attend Murdoch site Facilities Office on Thursday 18-2-21 at 11 amAttended site:Date: 18/2/21Start Time: 1045hrsFinish Time: 1130hrsTechs on Site: 1Works Carried:Evacuation drill instructions given to staff for all panels on siteSystem Status on Departure:Normal.
MSA-DTWD | WA3993860 | L2 Cafe - Oven self ignition wont work | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-19 16:08:00 | Pass | Ignitor no longer working
MSA-DTWD | WA3993876 | A block A232 air con not working | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-04-22 08:00:00 | Fail | Attended site regarding AC in room A232 not functioning.Signed in and completed pre-start paperwork and promap.Accessed room and turned on unit, test ran and checkedoperating pressures and temp TDs, coils and filters andoperation of compressor and fans. Running all ok with nofault present, may have been an intermittent fault butcouldn't find any issue while onsite. Informed site FMand said if issue reoccurs we will re attend.
MSA-DTWD | WA3993889 | A Block, Foyer - Fire panel intermittently beeping, no fault showing | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-22 13:22:00 | Fail | A Block panel intermittent, reset fire panel 3/3/21 Panel normal, Monitor for two weeks for fault, Panel all clear working well.completed
MSA-DTWD | WA3993903 | Damaged electrical cord Training room fridge | West One Services | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 16 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 15:00:00 | Pass | Checked leads and tagged as shown by site.job completed
MSA-DTWD | WA3993933 | G Block, Room G113- Air conditioner is not cooling | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 09:30:00 | Pass | Attended office and signed in and obtained keys, upon inspection found unit to be blowing room air and unit out on a coms fault, found switchboard and located breaker and.reset, checked operation of unit and air on air off All ok unit cooling. Suspect power fault / surge with power supply caused unit to fault
MSA-DTWD | WA3993952 | A Block External west end - AC condensation running through eave sheeting - see notes | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-04 16:04:00 | Fail | Job complete
MSA-DTWD | WA3993974 | L1 B110 room to hot no air flowing in | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-04 15:57:00 | Fail | Returned to site gained access and spoke with facilities. Provided with the as built drawings to assist with locating vav 2-7. Set work area up and located vav. On inspection actuator found to be lose on damper drive shaft. Restored and tested operation. All ok. Checked BMS read out and confimed setting had returned to normal. Work area left tidy. Equipment returned to auto operation.
MSA-MRWA | WA3993863 | Freestanding toilet cistern flush is intermittently not working, please replace. | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor-Toilet-Male-AG.01 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-17 08:00:00 | Pass | Replaced faulty inlet valve and broken/damaged outlet valve
MSA-MRWA | WA3993864 | GPO’s in room trip without RCD fully tripping at switchboard, please replace RCD | Don Aitken Centre MRWA Head Office-Main Building-Second Floor-232-Meeting Room | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 16 Feb 2021 | 2021-02-17 17:00:00 | 2021-02-17 06:30:00 | Pass | Repalced faulty rcd.job complete
MSA-DCA | WA4009830 | Winch room above lift - Leaking air con unit | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 6-Winch Room - West | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 10:00:00 | Pass | Leak repaired
MSA-DCA | WA4009836 | north east corner, large graffiti artwork to be removed | State Library of WA-Main Building-External Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 09:00:00 | Pass | Removed graffiti
MSA-DCA | WA4009842 | Disable lift making grinding sound and not moving | Maritime Museum Victoria Quay-Main Building-Ground Floor-Entry Foyer and Caf? | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | FLDCOMP | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 16:18:00 | Pass | No completion notes
MSA-DCA | WA4009978 | leaking air con - this is the second time this unit has had to be looked at recently | His Majesty's Theatre-Theatre Building-Ground Floor-G22 - Dressing Room 3 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 16:00:00 | Pass | Investigate water leak. Found drip trays drains blocked on dressing room 2 ground floor due to no fall on main line. Reason blocked is there is no fall on main line. 3 x FCUs are plumbed into the 3/4 -19mm copper line. Line is undersized. QRF to be submitted for rectification works. Approx length of drain is 20 to 25m to laundry trough. Unblocked drain and raised FCU to get more fall for unit. Precise Air to liase with FM to organise access to work area.15/3/2021 - carry out quoted works. Run new drain line for 3 x dressing rooms over to chemical storage room on work order WA4049233.
MSA-DCA | WA4010165 | Graffiti to be removed | State Library of WA-Main Building-Ground Floor-High Voltage Electrical Room - Near Francis Street | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-18 10:30:00 | Pass | Removed graffiti
MSA-DCS | WA4009662 | Jeelia B wing front door not able to open | Wandoo Rehabilitation Facility | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 10:35:53 | 2021-02-17 13:40:00 | Fail | Attend site, made external door safe as temporary fix as parts are required. Re-attend site to replace lock cylinder
MSA-DCS | WA4009665 | Perimeter response gate unable to open and the pin won't come up. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 10:37:56 | 2021-02-17 08:59:00 | Pass | Motorised vehicle gate not responding inform GH control room officer to check the issue with other contractor.
MSA-DCS | WA4009666 | Zone #3 - Fence alarm is going off from last night | Wooroloo Prison Farm | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 06:42:47 | 2021-02-17 11:00:00 | Pass | Tested extensively sensitivity adjusted tested ok.
MSA-DCS | WA4009682 | Kitchen - combi oven not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 07:02:30 | 2021-02-17 11:00:00 | Pass | 17/02/21Arrive at site to check oven error, staff explained this morning when turned on had come up with service error, they didn't recall the number. Checked over all functions and everything working well at this time. Ran on steam to see if any moisture entering electrical cabinet and all looks ok. Some signs of cockroach debris around electronic parts but nothing too bad, cleaned and checked all connections. Asked staff if happens again to record which service error number appears.
MSA-DCS | WA4009725 | Unit 2, cell D10 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 14:30:00 | Pass | Nill
MSA-DCS | WA4009753 | Control Room - Camera 157 & screen not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 12:15:51 | 2021-02-17 15:00:00 | Fail | Devices found offline after RCD tripped by electrical contractor testing. Devices reset tested ok.
MSA-DCS | WA4009759 | end reception area, Building alarm - faulty alarm, showing as not set when staff are setting alarm | Maddington (South East Metro) | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 12:16:40 | 2021-02-17 12:30:00 | Fail | Work performed by Drake Van der Merwe & Nathan Groenewald 17/02/2021:Attended site. Reprogrammed entry / exit zones on alarm due to alarming when arming system.Job completed.
MSA-DCS | WA4009761 | 50 new proximity cards, requiring activation/programming | Maddington (South East Metro) | WSM-BR-SITE | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 08:20:52 | 2021-03-12 13:27:00 | Fail | Not for Sapio as another contractor is working on Access control
MSA-DCS | WA4009774 | Perimeter response gate - gate/door wont open | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 12:32:46 | 2021-02-17 11:30:00 | Pass | 17/02/21Modify gate so it can be operated manually until WA3957240 is completed.
MSA-DCS | WA4009786 | Abattior office wall sheets broken and crumbling | Karnet Prison Farm | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-04-08 13:52:00 | Fail | New LVM job issued WA4122129. Invoicing costs to date.
MSA-DCS | WA4009795 | Abattoir boning room green line water pipes leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 15:00:00 | Pass | Redirected pipework to inside of building
MSA-DCS | WA4009811 | Unit 14 - B & D Blocked shower in D Wing, cell # 7. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 10:30:00 | Pass | Nill
MSA-DCS | WA4009823 | Unit 13, C Wing, Cell C02 - Drain is blocked (plunger not working) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-02 10:30:00 | Fail | Nill
MSA-DCS | WA4009825 | Unit 13, Cell C02 - Tap is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-02 11:30:00 | Fail | Nill
MSA-DCS | WA4009827 | internal perimeter fence - internal zone 25 MX2 constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 09:38:29 | 2021-02-17 12:30:00 | Pass | Recalibrate microphonics zone 25 mx2 and tested ok. Job completed.
MSA-DCS | WA4009889 | Unit 7, F Wing yard- Line break under new fence, see notes below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 11:05:05 | 2021-03-04 09:30:00 | Fail | broken pipe under fence not used but still live so capped off
MSA-DCS | WA4009909 | Case planning- C/P kitchen - Broken double power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 07:30:00 | Pass | Replaced broken gpo
MSA-DCS | WA4009911 | ISU (harding), Senior office - light loud humming noise | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 09:30:00 | Pass | Repaired light
MSA-DCS | WA4009912 | ISU B wing - shower not resetting, works once a day | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-03-02 08:50:00 | Fail | Replaced faulty control box
MSA-DCS | WA4009915 | Unit 6, B wing, leaning cupboard cup tap off again | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-26 13:18:00 | Fail | Nill
MSA-DCS | WA4009917 | Unit 4, Cell D3- burst pipe in plumbing duct. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 12:30:00 | Pass | Nill
MSA-DCS | WA4009920 | MPU (8) - Internal cell door viewing window smashed | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-25 10:45:00 | Fail | NO DAMAGE DETECTED - POSSIBLE DOUBLE UP OR WRONG LOCATION UPLOADED TO PROMAP
MSA-DCS | WA4009979 | Unit 13, D Wing, Cell D12- On exit from cell floor vinyl has lifted creating a trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-07-30 10:00:00 | Fail | new rubber flooring installed
MSA-DCS | WA4010011 | House 4, Kitchen- Fluro light not working (twin 36W tubes) | Boronia Pre-release | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-17 15:00:00 | Pass | Replaced faulty light fitting in house 4 with new led batten
MSA-DCS | WA4010018 | Unit 7 tearoom Powerpoint in Staff Kitchenette needs checking. Tripping the RCD behind small fridge. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-18 15:00:00 | Pass | Investigated power circuits in scu kitchen, found and replaced damaged gpo. Split overloaded circuits and tested
MSA-DCS | WA4010103 | Unit 2, B Wing, Cell B4- Power point ( one outlet only) not working. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-18 11:30:00 | Pass | Replaced damaged gpo in unit 2 b4
MSA-DCS | WA4010160 | unit 2 A15 and B17 cell call not working - SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 14:08:09 | 2021-02-18 16:00:00 | Fail | Fault was resolved with assistance of Cell Guard Tech Support team. Server Services were restarted and all nodes restarted to clear corrupt data. All cells in Unit two were tested to ensure correct operation and intelligible studio between cell call unit and control. Prison management informed throughout fault investigation and when repaired.
MSA-DCS | WA4010185 | SITE COST Monitor 1 is faulty and losing colour | Albany Regional Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 22:34:22 | 2021-03-03 11:30:00 | Fail | 03/03/2021 Attended site, removed faulty monitor from the wall mount bracket. Transferred the mounting bracket from old monitor to new monitor and returned monitor to wall, reconnected HDMI connection and configured monitor. Monitor on-line and operational.
MSA-DCS | WA4010187 | Kitchen wire going into kitchen tug recharging unit has pulled away from plug has wires exposed | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-18 08:30:00 | Pass | Repaired faulty tug charger lead in kitchen
MSA-DCS | WA4010240 | Unit 1 - monitors have gone down | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 10:33:00 | Pass | Change power settings on pc for cctv monitors, job completed.
MSA-DFES | WA4009914 | Fire panel is constantly activating at least once a wekk | Butler Career Fire Station | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 13:20:00 | Pass | Attended site - investigated fault. No fault on panel.Searched logs and found smoke detector in room 9.Confirmed by station.Changed faulty detector (L255624). Performed loop test. Passed.
MSA-DFES | WA4010216 | FF Dorm, Room 6- Air Con is leaking | CFRS Murdoch | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 11:30:00 | Pass | Dorm 6 Ac was leaking. Unblocked ac drain and confirmed correct operation
MSA-DFES | WA4010230 | Workshp Amenities, Northern Office, Air Con unit #21 is faulty- see notes below | Fleet Management Services - O'Connor Workshop | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 10:00:00 | Pass | Service call on Ac
MSA-DTAG | WA4009817 | Air Con is currently not working throughout the entire buidling . | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 17 Feb 2021 | 2021-02-17 13:26:54 | 2021-03-10 14:30:00 | Fail | Andrija Skender (17/02/2021) - Work NoteChecked BMS and found building fire status on fire mode from Fire Panel. BMS network down also called Thomas from Icon logic to attend site. Network controller 15 off line for FCU 2 through to 9. In MSSb 3 which controls heater contactors. Investigated found problem with controller 15. Disconnect power to controller to be replaced. Icon to supply quote.Investigated HP problem with Chiller 2 and found control fuse blown. Control fuse seems to related with HP fault reset.Replaced slow blow control fuse checked operation of chiller all working ok.Seems to be power fluctuation or spuke that has caused the problem.Chiller 2 operating ok will monitor control fuse and power supply to chiller.Andrija Skender (10/03/2021) - Work NoteTravelled to site to.meet Brenton from Icon to fit new network controller15 and re program parameters.Checked operation of new controller all working ok.
MSA-DTAG | WA4010151 | ground Lift 9 is out of service. Doors opening and closing on their own when at ground floor. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-17 17:56:00 | Pass | Doors closing than reopening cause of lock not dropping. Adjusted stops so make contact same time. Further investigationrequired. Notified AS.
MSA-DTAG | WA4010270 | Bio clean required inCell 1 & 2 as accused in custody has caused blood on the floor . | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 22:00:00 | Pass | Job completed as per WO
MSA-DTAG | WA4010271 | L10 front counter lights flickering one in marriage service area. One above mail opening desk. | Westralia Square | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 08:43:00 | Pass | Replaced faulty fluros around site as shown.all complete
MSA-DTWD | WA4009720 | Ground, Jewelry - room is too hot | Perth Campus B4 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 17 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-24 14:14:00 | Fail | Attended site gained access and carried out inspection of HVAC plant equipment. The main control contactor for AHU1 VAV zones had failed. FCU 1 contractor was found to have also become faulty. Pricing sourced for replacement. Parts were collected brought to site and fitted. Plant has been restored to operation
MSA-DTWD | WA4009777 | Campus computer labs - Keys are broken for B13, U, 5 & 239 | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 08:30:00 | Pass | repairs to locks
MSA-DTWD | WA4009852 | J Block, Room J128- No power in Construction Workshop | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 15:18:00 | Pass | Rectified power loss to room.job completed
MSA-DTWD | WA4009854 | A block Hole in mainline near Fire Pump Station | Rockingham Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | LD TOTAL | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-17 13:30:00 | Pass | DAMAGED 50MM PIPE NEAR FIRE SHED REPAIRED
MSA-DTWD | WA4009868 | Hairdressing, Store C43- Leaking tap | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-18 13:08:00 | Pass | Repaired leaking hot tap
MSA-DTWD | WA4009886 | Canteen - Repair damaged ceiling manway | Rockingham Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-03-17 10:15:00 | Fail | Ceiling replaced and manhole installed. Ceiling painted white to match existing.
MSA-DTWD | WA4009899 | Courtyard near E Block and pathway- lighting not working | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-24 12:00:00 | Fail | Attended site and signed in. Checked out and investigated grounds lighting and poles. Found light on at A block to be hard wired. No switch or pe cell. Site aware. Pole lights in court yard have fault incoming. Tested back to switchboard and have been isolated and tagged out previously. Made safe cables in pole and tagged other end. Notified site and said to leave poles redundant. Signed out. Job complete
MSA-DTWD | WA4009959 | Ground foyer 19Ab Security pad showing RAS Fail code | Perth Campus B6 | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-19 10:00:00 | Fail | 17/02/2021, 1330-1415Ras 1 and 5 offline, checked all dgp and ps fuses all ok so power cycled panel and all came back up ok. Power failurescaused drop out18/02/2021, 1145-1230Not the same issue, problems arming apparently. System is actually no comms. Found phone numbers removed fromprogramming, all other info still there. Reprogrammed phone numbers and tested comms confirmed all signals received.Unknown as to who or why the programming had changed.18/02/2021, 1430-1545 and 1500-1545Opens and closing for 2.3.4 wasn't set. No test signals programmed . Multi breaks and restores not programmed. Testedareas 2.3.4 got opens and closing for all areas.19/02/2021, 830-1000Found issue is part of the schneider electric access control fixed zone 4 as the panel wasn't locked properly . Zone 1dotl is being tripped by there panel . Need to get schneider out to fix as there's nothing to indicate which door is at faultto check and have swted zone 4 sothey can arm in mean time
MSA-DTWD | WA4010017 | Workshops, compressor room - water in air line, compressor not filtering water | Clarkson Campus | GMP-BR | Equipment | Compressors, Generators (EQ) | CAPS AUSTRALIA PTY LTD | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-03-03 11:45:00 | Fail | Replaced auto drain
MSA-DTWD | WA4010091 | Roof mounted Email A/C not cooling properly | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-03-02 11:00:00 | Fail | Checked the air conditioning system , found the wall sensor needs replacing. Will pick up parts and replace.Tech attended site 02/03/21 and replaced faulty wall sensor. job is complete
MSA-DTWD | WA4010115 | Level 1, N117 - Treat Cockroach infestation | Mount Lawley Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-18 11:10:00 | Pass | Gelled and inspected N117. Found cockroach eggs. Treated with Amdro gel and installed 1 Cockroach Detector
MSA-DTWD | WA4010133 | Workshop RCD keeps tripping | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 14:30:00 | Pass | Attended site and signed in. Located fault on RCD. Reset and found water fan in workshop. Tested fan and pump and all okay. Plugged back in to wall and reset and ran up fan and water pump. No fault found. Advised site that if does it again fan it not serviceable and needs to be replaced. All okay. Job complete
MSA-DTWD | WA4010147 | Cafeteria cool room - Coil is icing up needs to be de-iced and cleaned | Carlisle Campus | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-18 17:15:00 | Pass | Attended site meet with second tech gained access and completed requered safty paperwork. Gained access to roof and carried out inspection of cool room unit. Time clock found to have failed. Left site to collect new parts. Returned and installed confimed operation and temps drop. All ok. Work area left tidy.
MSA-DTWD | WA4010202 | D Block, Room D108- Air Con not working | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 17 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 10:00:00 | Pass | Accessed site completed relevant sign in procedures and covid safe app wa requirements, gained access to d block room 108 ac unit , found fault code C1 (indoor - outdoor communication fault) to be present, carried out testing to ac unit with no defect identified , cleared fault , and tested unit operation , all ok
MSA-DTWD | WA4010251 | G Block, Room G22- No hot water in dog wash sink | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 17 Feb 2021 | 2021-02-24 17:00:00 | 2021-07-01 17:43:00 | Fail | install 15mm rpzd, tmv etc
MSA-MRWA | WA4010020 | Lift 1 and 2 investate doors closing to fast | Don Aitken Centre MRWA Head Office-Main Building | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 17 Feb 2021 | 2021-02-18 17:00:00 | 2021-02-18 16:30:00 | Pass | Completed non chargeable
MSA-DCA | WA4011459 | Disabled Access Lift not working - see notes | Maritime Museum Victoria Quay-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | FLDCOMP | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 11:26:00 | Pass | DOOR PROTECTION - PHOTOCELL - COMPONENT DUSTY, CLEANED
MSA-DCA | WA4011565 | 240/24v relay transformer faulty-Sena is aware | State Library of WA-Main Building-Ground Floor-Library Foyer- Distribution Board Room | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 06:30:00 | Pass | Faulty transformer swapped with new
MSA-DCA | WA4011568 | poster box, light flashing new ballast required | State Theatre Centre (Heath Ledger Theatre)-External Area | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 15:22:00 | Pass | Investigated flickering lights to find a faulty electronic drivers. Tested all sources of power and all was ok but the output of driver. Sourced drivers from wholesaler, picked up new parts, isolated and replaced 2x drivers to fix the fault. Tested lights for correct operation and in working order.
MSA-DCA | WA4011592 | Foyer – eastern side pillar GPO is loose and coming away from wall. Please replace | Swan Bell Tower-Main Building-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 15:30:00 | Pass | Rectified loose gpo from wall, fixings came out of wall and had to be replaced.
MSA-DCS | WA4011281 | Level 2 Female Shower - The drain appears to be blocked and water is flooding the floor | East Perth | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 13:30:00 | Pass | Arrived on site and inspected found the the female shower floor drain blocked. Plunged multiple times to clear the blockage. Tested multiple times all working in order.
MSA-DCS | WA4011284 | SITE COST Gate house - perimeter Zone 9 inner, in constant alarm. | Wandoo Rehabilitation Facility | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Feb 2021 | 2021-02-18 11:22:15 | 2021-02-18 13:00:00 | Fail | MW unit realigned possible animal (bird contamination found on top of unit)the cause. Retested now working ok Job left open until tomorrow for further testing purposes as per office. 19/02/21 Call placed to site no further alarm activations on Zone 9 MW job completed. 12:30pm
MSA-DCS | WA4011287 | Unit 2, top landing - double door fridge leaking water onto floor | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 15:00:00 | Pass | check leaking fridge , found block drain clear drain test and left operational
MSA-DCS | WA4011291 | Unit 1, B13 - viewing glass broken & silde (may require new glass & slide) | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 07:28:20 | 2021-02-18 11:30:00 | Pass | NEW GLASS & PRIVACY SLIDER FITTED
MSA-DCS | WA4011298 | Unit 2, B wing - light faulty, hanging form ceiling | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 07:34:44 | 2021-02-18 10:00:00 | Pass | Repaired damaged lights in unit 2
MSA-DCS | WA4011306 | Unit 14 - Fire alarm vesdas multiple activation/faults, see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 07:40:33 | 2021-02-19 08:57:00 | Fail | Attended unit 14 & investigated faults.Found VESDA BD Cell 5/6 VESDA sample point blocked with tooth paste & VESDA isolated by staff.Advised unit OIC, cleaned sample point, reset VESDA & de-isolated VESDA.Whilst onsite investigation of fault AC Cell 9/10 found VESDA isolated.De-isolated VESDA OK.System status displaying normal on departure.
MSA-DCS | WA4011314 | UNIT 3, A&C - regi oven leaking - may require a new seal | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-19 09:00:00 | Pass | Replaced Doorseal on oven, fitted and tested ok
MSA-DCS | WA4011324 | Unit 4, Control room - Carpet tile lifting and needs re-glueing | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-04-06 12:00:00 | Fail | DAMAGED CARPET TILES LIFTED & REPLACED WITH NEW
MSA-DCS | WA4011348 | Broken sewer lid requires replacing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-04-28 15:20:00 | Fail | Job completed
MSA-DCS | WA4011358 | Industry market gardens- Broken solenoid structure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 11:30:00 | Pass | Replaced faulty valve
MSA-DCS | WA4011359 | Unit 9, C/D wing - D wing L/H window frame needs repair (see motes) | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 08:18:17 | 2021-03-19 12:00:00 | Fail | FRAME REPAIRED AND RE FITTED
MSA-DCS | WA4011361 | Unit 9, C/D wing - , C wing Flashing has come off around window needs re-fixing (see motes) | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 08:38:32 | 2021-03-17 13:30:00 | Fail | RE INSTALLED FLASHING TO WINDOW
MSA-DCS | WA4011364 | Unit 10, first entry door - Entry door doesn’t self close on its own | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 08:41:11 | 2021-03-17 09:30:00 | Fail | DOOR CLOSER ADJUSTED AND NOW CLOSES
MSA-DCS | WA4011365 | Stores - Lights not working near Coolroom & Freezer Stores area | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 08:42:10 | 2021-02-18 12:30:00 | Pass | Repaired lights
MSA-DCS | WA4011369 | Visits - Fire panel keeps alarming toilet | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 08:43:47 | 2021-02-19 09:00:00 | Fail | BG 19/2/21Visits toilet L4S5 causing intermittent missing fault. Replaced detector with new xp95 smoke detector.
MSA-DCS | WA4011378 | House 12- toilet, laundry & shower drains are blocked | Boronia Pre-release-AP21 - Prisoner Accommodation House 12 and 13 | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 09:01:16 | 2021-03-25 13:00:00 | Fail | replaced sections of drainage behind toilet/shower block
MSA-DCS | WA4011402 | Unit 4 D wing, pantry & roof - mouse infestation | Wooroloo Prison Farm | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-19 12:40:00 | Pass | .
MSA-DCS | WA4011437 | SITE COST INF(10), Obs Cell 1 - Infirmary OBS cell cameras/monitor views not functioning. | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Feb 2021 | 2021-02-18 13:57:23 | 2021-02-18 12:30:00 | Pass | Rectified and fixed the cctv view for infermary, job completed.
MSA-DCS | WA4011478 | Unit 2, B Wing- First Shower is not working, no water comes out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 11:30:00 | Pass | Nill
MSA-DCS | WA4011482 | Unit 2, Cell D1- Window is not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-04 10:30:00 | Fail | spiral balances renewed and frame repaired
MSA-DCS | WA4011484 | Unit 2, D wing - Light hanging from the ceiling in cleaning store | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 10:49:36 | 2021-02-18 13:00:00 | Pass | Repaired damaged lights in unit 2 d wing
MSA-DCS | WA4011491 | Microwave E2 &F4 in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 10:55:34 | 2021-02-18 15:54:00 | Pass | Rectified and fixed faulty mw E2 and F4 outer defence, job completed.
MSA-DCS | WA4011495 | INF (10), Cell C1- Toilet is partially blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-18 15:30:00 | Pass | Knifes and forks in toilet
MSA-DCS | WA4011500 | MPU (8) - camera 143 not operational | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 11:00:15 | 2021-02-19 09:45:00 | Pass | Rectified and fixed the fault on decoder, job completed.
MSA-DCS | WA4011502 | zone 10 MW constant alarm - SEME on site | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 10:37:21 | 2021-04-30 10:30:00 | Fail | Replaced defective Z10 MW with set of UW, configured and tested. Job completed.
MSA-DCS | WA4011551 | front gate entrance - x-ray machine not working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Feb 2021 | 2021-02-18 15:43:43 | 2021-02-22 11:15:00 | Fail | Attended by Leidos (L3). On arrival on site, guards advised me that a local technician had been "pressurized" to open up the X-ray machineover the weekend and had bypassed the faulty UPS to enable the machine to run. NB *Unless local technicians have a cabinetX-ray licence from the WA government, this is against the law and can pose a risk to Leidos engineers health and safety.Re-wired replacement UPS into system and tested OK. Ran system verification - passed OK. Ran test bags. System fullyfunctional.
MSA-DCS | WA4011555 | Demountable Transition Drains blocked badly | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 11:53:00 | Pass | Repared perished seal no blockages found
MSA-DCS | WA4011580 | Offical Visits, PO's Office - Emergency GPOs R-2 have No Power | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 12:27:24 | 2021-02-22 08:30:00 | Fail | 18.02.21 Found cables disconnected at DB for R2. Tested cables & GPO, reconnected and tested.22.02.21 Returned as requested to find all GPO's in office working fine.
MSA-DCS | WA4011612 | ISU A wing smashed window 450x300 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 13:11:57 | 2021-04-21 14:30:00 | Fail | 2X DOOR GLASS RE GLAZED AND SEC FILMED
MSA-DCS | WA4011631 | Uni 1, Control room -Black handset (Cell call to C&D wing) talk button VERY temperamental. (see note | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 13:33:08 | 2021-02-19 10:45:00 | Pass | Attended site checked and found Unit 1 Control cell call handset push to talk button faulty. Replaced the handset and tested all ok after replacement. CG-OH X 1
MSA-DCS | WA4011632 | Outer Sallport doors have been reported as having to be reset several times during open and close | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 18 Feb 2021 | 2021-02-18 17:36:41 | 2021-02-18 14:45:00 | Pass | 18/02/21Inspect and checked opening and closing at external sally port doors and anti ram.No fault found.16 movements at doors since fault report.All good.
MSA-DCS | WA4011651 | Unit 3, Cell D2- Window out of window track | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-03 13:30:00 | Fail | RE NEW SPIRAL BALANCES AND REPAIR FRAME
MSA-DCS | WA4011654 | Unit 3, Cell D13- Window out of window track | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-03 14:15:00 | Fail | RE NEW SPIRAL BALANCES AND REPAIR FRAME
MSA-DCS | WA4011681 | Unit 4, Cell C14- Toilet cistern faulty (part of outlet valve broken) | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 14:04:24 | 2021-02-19 08:10:00 | Pass | Replaced broken flushing part and washers
MSA-DCS | WA4011707 | North wing outside tap continuously running can’t turn of needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 14:01:12 | 2021-02-19 07:35:00 | Pass | Replaced outdoor tap
MSA-DCS | WA4011709 | Unit 2, Cell D1- Door split by bottom hinge | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 14:13:08 | 2021-02-19 10:00:00 | Pass | CRACK FILLED WITH ADHESIVE FILLER
MSA-DCS | WA4011713 | Official Visits,Interview room 4 & main officer station- Roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 14:14:46 | 2021-05-04 08:00:00 | Fail | TRACE LEAK IN OFFICAL VISITS, REPAIR OVER FLASHINGS, DRY BOX GUTTER AND SEAL JOINS AS REQUIRED, FLUSH DOWN PIPE AND CLEAN DEBRIS OFF ROOF
MSA-DCS | WA4011764 | Unit 7 H2 Damaged toilet leaking needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 14:44:22 | 2021-02-19 09:45:00 | Pass | Reinstalled loosen pan, replaced broken button and flushing part
MSA-DCS | WA4011811 | gate house fire alarm is not setting of alarm when hydrent is activated | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 15:46:19 | 2021-02-19 11:18:00 | Pass | Complete
MSA-DFES | WA4011470 | Mens toilets- Exhaust fan switch is tripping RCD | Jandakot Airport Hanger | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-09 10:00:00 | Fail | Complete
MSA-DFES | WA4011595 | kitchen boiling water unit has no hot water | VFRS Mandurah | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 15:40:00 | Pass | Replaced level sensors all seems okay
MSA-DTAG | WA4011270 | Check unknown fibre in the security rack | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-04-13 15:00:00 | Fail | Work performed by Lee Kiok 19/02/2021:Attended site. Checked fibre connections in Security Room.- 8-4-21- Separate / replace Lockdown button and door release button in Reception. Tested ok- Rearrange custody comms room rack equipment as per Instruction.- Install UPS for CCTV encoder in Reception.-13-4-21- Replaced lock down button face plate with metal plate. Tested operation ok.
MSA-DTAG | WA4011272 | Sallyport camera not working | Perth Children's Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-18 16:00:00 | Fail | Work performed by Lee Kiok 19/02/2021:Attended site. Checked Sallyport camera, no signal, tested power OK.Deemed faulty, requires replacement.Work performed by Drake Van der Merwe & Ryan Craven (17/03/2021 & 18/03/2021):Attended site and installed new conduit from communications room to Sallyport, install, program and commission twoBX420 4MP cameras onto existing Indigo CCTV system. Unforeseen complication with cable run and court scheduleTechnicians to find alternative cable route to communications room.APPROVED BRAF ATTACHED
MSA-DTAG | WA4011273 | No video signal from cameras in custody to court hallway | Perth Children's Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-16 16:00:00 | Fail | Work performed by Lee Kiok 19/02/2021:Attended site. Temporarily installed new power supply for Cameras 5 & 9.Confirmed both cameras restored.Work performed by Lee Kiok 16/03/2021:Removed temporary power supply for Cameras 5 & 9, installed new rack mount 24 VAC PS. Tidied up cabling.Confirmed Cameras 5 & 9 are online.Job completed.APPROVED BRAF ATTACHED.
MSA-DTAG | WA4011274 | Level 29 check foyer auto door, failed to close on several occasions | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 18 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 13:45:00 | Pass | Auto door working ok
MSA-DTAG | WA4011454 | Lvl 2, Airconditioning in court 3 not working | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 12:00:00 | Pass | Attend site. Access BMS and check operation of court 3 Airconditioning. Found courtroom to be 21.3 degrees and supply air temp to be 12 degrees. Check time schedule and found to be ok. Access AC 3 and check operation, working ok. No faults found at present. Check cooling tower and found to be operating as normal. Monitor operation and found compressors to cycle on and off as normal. Courts have there own setpoint adjustment so there is a possibility different staff members have been adjusting this. Possibly install data loggers if issues arises again.
MSA-DTAG | WA4011455 | Level 10 - CCTV camera flickering in reception | Westralia Square | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 10:30:00 | Pass | Attended site and checked camera system. Found Camera 3 flickering and lagging. Checked recordings and recordingsshowing ok. Possibly interference, reset camera and dropped video frame rate, changed frequency on camera video viewto avoid any interference from lighting. Retested with heath and all tested ok.Job completed.
MSA-DTWD | WA4011296 | metal storage shed - 50 amp 3 phase outlet burnt out | Naval Base | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 18 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 10:45:00 | Pass | Attended site and signed in. Located faulty outlet in workshop shed. Found faulty light switch also. Supply and replace with new outlet and switch. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4011342 | G block, ladies staff toilet - Leak at join in pipe where bowl penetrates the wall (see notes) | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 14:45:00 | Pass | Removed old seal and cover, filled adaptor with silicone
MSA-DTWD | WA4011351 | Carpark 2 - Carpark light at north west end has broken lamp | Thornlie Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-11 11:30:00 | Fail | Attended site and signed in. Located ewp on site. Took to job area. Ran Pre start checks. Used ewp to access light fitting. Disconnect and removed old light fitting. Supply and replace with new led street light. Dispose of old light fitting. Clean and tidy site. Signed out. Job complete
MSA-DTWD | WA4011353 | Q007 - vertical blinds not operating correctly and some are broken | Balga Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-29 10:22:00 | Fail | completed & Invoiced
MSA-DTWD | WA4011362 | G Block, Woodwork, metals & auto workshops- Lighting is faulty, see notes below | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-10 09:45:00 | Fail | Attended site and signed in. Located ewp on site. Carried out pre start checks. Used ewp to access faulty lights. Supply and replace with new led hi bay lights. Clean and tidy site. Dispose rubbish on site. Signed out. Job complete
MSA-DTWD | WA4011397 | B201 lighting not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 0 | CLOSE | 18 Feb 2021 | 2021-02-18 13:19:00 | 2021-02-18 11:15:00 | Pass | Checked lights to b201.all working fine. Job complete
MSA-DTWD | WA4011412 | existing bollards barrier Brocken need replacing., three locations. | Murdoch Campus | GMP-BR | Building | External Walls (BU) | AWB Co. | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-11 15:00:00 | Fail | COMPLETED
MSA-DTWD | WA4011432 | Roof mounted A/C not operating | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 11:00:00 | Pass | Checked the air conditioning system, found it running on fan only compressor not required as temperature was 20degbin the class room.
MSA-DTWD | WA4011442 | Block 6E, Cabinet Making workshop- Lights in main workshop not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-12 14:30:00 | Fail | Attended site and signed in. Located ewp on site. Ran Prestart checks. Took into workshop. Advised staff and students of works being carried out. Set up safety zones. Access lights row on back wall. Removed tubes and covers to lights. Supply and Installed 3 x hi bays along back row. Located 2 x suspended fluros. Supply and replaced with new led battens. Tested all okay. Clean and tidy site. Dispose rubbish. Job complete
MSA-DTWD | WA4011444 | B Block,Plant Room-Blue 13 RCD in DB3 cannot be reset as well as some of the Red 2 GPO's not working | Midland Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Precise Air Group | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-19 11:00:00 | Pass | Isolated unit, obtained parts required for repairs travelled to supplier picked up parts and returned to site carried out repairs, replaced pulley pulley hub and belts, aligned and re fitted guards removed isolation and tested all ok.
MSA-DTWD | WA4011516 | Main entrance to car parks - Light pole damaged and bent | Murdoch Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-03-29 16:30:00 | Fail | Attended site. Located damaged pole. Soaked rag bolts in lube to loosen up. Unbolted pole base. Removed pole base. Disconnected light fitting and installed to new pole. Stood up new pole. Wired up in base. Tested all okay. Need trailer and grinder ro cut pole and take away in trailer. 6m pole too heavy for roof and is bent. Job not complete
MSA-DTWD | WA4011524 | E Block E21 Male Staff Toilet – Faulty Flush Button | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-18 14:39:00 | Pass | Replaced outlet rubber in changerooms Fixed stuck cistern button in staff toilet
MSA-DTWD | WA4011578 | T block L2 T201 two tubes keep having to be replaced. Please investigate possible underlying issue. | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-19 16:30:00 | Pass | Attended site and signed in. Located main T block admin area. Found faulty lights out. Supply and replaced tubes and blew tubes instantly. Supply and replaced ballasts to light fittings. Replaced tubes. Re fitted all covers and diffusers to ceiling, tested all okay. Job complete
MSA-DTWD | WA4011616 | T Block level 2 Staff canteen- The colt tap on the North side does not work | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 15:20:00 | Pass | Replaced cold pump. All working ok
MSA-DTWD | WA4011712 | A block, Mens toilet, ground floor, east end - Urinal blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-18 15:38:00 | Pass | Unblocked urinal
MSA-DTWD | WA4011718 | E Bock, Room E200 - Lights faulty | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 14:20:00 | Pass | Repalced fualty flueos
MSA-DTWD | WA4011720 | External car parks - Multiple car park light globes not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 3 | CLOSE | 18 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 17:00:00 | Pass | Attended site to carry out site walk around and Mark up / identify total replacements required, access types, light types , hours of work with campus manager as SEVERAL lights were out.
MSA-DTWD | WA4011731 | E block, Skills kitchen 3 - Lecturers oven, pilot light will not stay on. | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-17 15:45:00 | Fail | COMPLETED AS ON SITE ATTENDING OTHERJOBS.
MSA-DTWD | WA4011783 | Q Block, A/C not functioning | Joondalup McLarty Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 11:30:00 | Pass | Attended site signed in and recieved site keys, investigated issue with q block chiller, found system to be set to local off, when it should be on ccn seting, tested system and checked bms logs ,left all system operational
MSA-DTWD | WA4011790 | L1 27mus broken window | Perth Campus B7 | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 08:50:00 | Pass | ATTENDED SITEREGLAZED 2 BROKEN WINDOW PANELS5.38 CLEAR LAMINATED SAFETY GLASS1-758 X 7631-765 X 763PLUS SILICONE AND 5.4 L/M OF PUTTY USED
MSA-DTWD | WA4011800 | Level 1 comms cupboard door replace damaged door filter | Clarkson Campus | GMP-BR | Carpentry | Timber (all types) (CA) | AWB Co. | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-08 14:00:00 | Fail | Supply and install new door vent with filter
MSA-DTWD | WA4011802 | Library study room 5- repair lights as required | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-11 13:51:00 | Fail | Repalced lamps to multiple areas B2.job completed
MSA-MRWA | WA4011780 | Lvl 4, South Bicycle Entrance- Female toilet full flush not working / lost, please remediate | Don Aitken Centre MRWA Head Office-Main Building-Fourth Floor-A4.02-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Feb 2021 | 2021-02-19 17:00:00 | 2021-02-19 09:46:00 | Pass | Replaced flushing buttons and bellow to toilet cistern in level 4 female last cubicle.
MSA-DCA | WA4014814 | ground floor, male toilet - extremally blocked and over flowing toilet | His Majesty's Theatre-Theatre Building-Ground Floor-Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 14:45:00 | Pass | Cleared blocked male toiletground floor stalls last cubicleReplaced push button seal kit,outlet sealing kit and bellows to 3rd cubicle male toilet stalls
MSA-DCA | WA4014995 | ground level - vesda zone 38 in fault | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 09:45:00 | Pass | Vacuumed the VESDA sample pipe clean & normalised the VESDA
MSA-DCA | WA4015102 | plantroom Fault on Chiller 2 – please investigate | Maritime Museum Victoria Quay-Main Building-Ground Floor | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 19 Feb 2021 | 2021-02-19 19:38:39 | 2021-02-19 18:00:00 | Pass | Attended site. Chiller 2 in fault. Applied tests and checks to find BP1 to have also tripped. Investigation found BP1 electrically down to earth. Disconnected and isolated BP1 and made safe. To return Monday to remove defective BP1 motor. Job to be closed with new LVM to be raised.
MSA-DCS | WA4014251 | Domain 2B, 3A, 4A & 4B UPS Mains Fail Alarms | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-20 09:00:00 | Pass | CHecked all UPS listed. Unit 1 House 5, Unit 2 House 1, Unit 2 House 4 & Unit 2 House 5. Tested UPS and all is working & reset all HLI Alarms.
MSA-DCS | WA4014254 | Unit 1 House 5 Controller Offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-20 10:30:00 | Pass | Unit 1 House 5 Controller offline. Checked controller and found no network activity. Found that switch was frozen due to intermittent mains fail. Power cycled switch and all is working.
MSA-DCS | WA4014257 | Unit 1 House 4 Locks faulting | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-20 13:30:00 | Pass | Unit 1 House 4 Entry Door not looking after power issues on site. Simulated operation for Entry Door to go fail secure after power fail, and all is working with no issue. Fault from previous night was due to intermittent power fails reverting the controller software to Version 6. Downloaded latest version back to controller and tested, all is in working order.
MSA-DCS | WA4014258 | Unit 1 House 6 Camera full of water | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-25 17:00:00 | 2021-07-18 11:00:00 | Fail | Cabled and installed new IP camera. Positioned to suit best FOV.
MSA-DCS | WA4014279 | Gatehouse pod - Air conditioning not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-19 10:58:40 | Pass | Checked over unit foun d to be running ok and down to temp,did find 1 belt cracked, replaced.
MSA-DCS | WA4014287 | Unit 5, C2 - Water build up under lino may be from shower | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 07:44:23 | 2021-03-29 22:00:00 | Fail | ONCE TILING INVOICE RECEIVED - WE WILL CLOSE OFF JOB - DEAN SCOTHERN ADVISED, PRISON WILL ISSUE NEW JOB FOR PLUMBING AND ONCE THAT IS FIXED - RE ISSUE US A JOB FOR VINYL REPAIR.
MSA-DCS | WA4014301 | Unit 16, Cell B5 - water not draining properly in shower. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-16 13:30:00 | Fail | Nill
MSA-DCS | WA4014303 | Reception, Office Area- Light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-23 15:00:00 | Pass | Repaired light in reception office
MSA-DCS | WA4014306 | Unit 14, D4 - leaking shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 10:30:00 | Pass | Nill
MSA-DCS | WA4014313 | Programs officer office- vanity tap is leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-31 06:30:00 | Fail | Found the tap leaking. Could not find the isolation for this tap. Returned to site isolated water. Serviced the spindle, reseated the tap and changed the tap washer.
MSA-DCS | WA4014342 | unit 5 control room Rat smell coming from under control room floor - see notes | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 08:59:18 | 2021-02-19 11:00:00 | Pass | 19/2- attended site but no available escorts - was advised that there was no real smell evident anyway - probably from another job - water pooling under Lino
MSA-DCS | WA4014370 | Unit 2B, toilet has broken window | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-04 12:30:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA4014618 | control room cell calls directed from ISU to control I crackling | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-19 15:00:00 | Pass | Attended and investigated the fault, replaced the cell call handset with new GH control room. Job completed.
MSA-DCS | WA4014764 | 4A day room - Hot water urn is not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 12:15:00 | Pass | Element had tripped due to water being turned off. Reset and tested.
MSA-DCS | WA4014769 | Recreation Hall - power point is faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 11:00:00 | Pass | Reset power supply
MSA-DCS | WA4014785 | Unit 6, C wing dayroom - Faulty stopcock (faucet) in C wing dayroom | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 11:05:56 | 2021-02-19 16:00:00 | Pass | Replaced broken spout
MSA-DCS | WA4014834 | Gardens - sprinkler damaged near social clib and car park. | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 11:36:33 | 2021-02-19 14:15:00 | Pass | REPLACED BROKEN SPRINKLER
MSA-DCS | WA4014838 | Gardens, Eastern Oval - stop cock valve split, solenoid box flooded, possible damage to solenoid | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 11:39:32 | 2021-03-04 13:15:00 | Fail | replaced valve
MSA-DCS | WA4014871 | Unit 10, First Entry door electric lock not latching | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 12:09:35 | 2021-02-23 11:45:00 | Fail | Replaced defective electric strike with new, tested ok. Job completed.
MSA-DCS | WA4014874 | Gascoyne- Zone 1 fire alarm constantly activating | Wandoo Rehabilitation Facility | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 19 Feb 2021 | 2021-02-19 16:14:14 | 2021-02-19 14:05:00 | Pass | BG 19/2/21Attended site for callout in Gascoyne unit. Ongoing alarm causing buzzing sound from FIP. Manhole to be cut next week for alarm rectification.Isolated zone one to prevent buzzing until issue is resolved. Notified gate staff and assistant superintendent of isolate in zone one. Unsure ofentirety of area cupboard. This task to be closed out as previous attendance to be used.
MSA-DCS | WA4014875 | Reception- Sliding door in shower area has come off runners | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 12:16:46 | 2021-02-26 09:30:00 | Fail | DOOR REPAIRED AND NOW ON ITS RUNNERS
MSA-DCS | WA4014930 | SITE COST MPU, M14 - Viewing Hatch Smashed on the door | Casuarina Prison | WSM-BR-SITE | Glazing | Window Glass (GL) | Midolo Building Services | 0 | CLOSE | 19 Feb 2021 | 2021-02-19 17:08:07 | 2021-02-19 18:00:00 | Fail | VIEWING HATCH GLASS REPLACED
MSA-DCS | WA4014936 | Boiler house, number 2 - out on fault (see notes) | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 13:13:17 | 2021-02-24 13:30:00 | Fail | Investigated the pilot fault checking the flame rod and found it dirty so I cleaned it. If the fault continues I recommend theflame rod be replaced with either a QRA2 or a new flame rod.Completed paperwork as required.
MSA-DCS | WA4014942 | Unit 1, Cell B11- Damaged door frame | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 15:30:00 | Pass | carried out repairs to cell door that was jamminig.
MSA-DCS | WA4014946 | Unit 2, d wing dayroom - replacement urn requires connection to water & over flow | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 13:20:30 | 2021-02-19 17:50:00 | Pass | Plumbed up bouling unit
MSA-DCS | WA4014949 | Unit 2,Outside C-D Wing Perimeter Wall End- Camera 155 Lens Cover is Dirty obstructing vision | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-26 12:00:00 | Fail | EWP required to clean camera can only occur during Friday Lockdown period due to camera location. Must be booked with site approval and escort required. Approximately 10 other cameras require cleaning recommend this occurs at sametime. 1 x day 2 x technicians preferably familiar with site camera access. Awaiting Access. Work completed along with WA4086536 work.
MSA-DCS | WA4014996 | Unit 1, B & D - day room oven seals are damaged | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-04-07 10:20:00 | Fail | Returned 7/04 to fit new oven door window seals. Replaced ok & test oven operation ok.
MSA-DCS | WA4015063 | Unit 1, CCTV screens have gone down | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 14:55:40 | 2021-02-19 16:15:00 | Pass | No live view from indigo ws, restart the ws pc and set the view to normal. Job completed.
MSA-DCS | WA4015070 | L4 near lift wall card reader has become loose. | East Perth | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-22 14:30:00 | Pass | Attended siteLocated swipe card on level 4 - found cover was half offInspected closer and found broken screw on the main back plateDiagnosed swipe card covering requires replacement due to the screw broken off the back plateReplaced swipe card housing, required to re-soldering the connections due to the way the wall plate for the swipe card is designed, re-soldered wiring as requiredTested swipe access - all okAdvised site of the outcomeLeft siteSupplied Part:1x Gallagher Cardax Prox Reader Cool Grey Housing Only
MSA-DCS | WA4015089 | Social Visits, Spine Entrance Door- Door Lock Cartridge Intermittently, Jamming Open | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 11:30:00 | Pass | Attend site. Checked doors to social visits. Unable to locate any faults. Also had DOJ representative confirm. Perhaps the job was raised on incorrect site?
MSA-DCS | WA4015110 | Unit 14 - B & D fire alarm system wont clear at panel and vespa | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 Feb 2021 | 2021-02-20 15:55:12 | 2021-02-19 21:03:00 | Pass | BG 19/2/21Attended site and found wing AC 9/10 intermittently causing fault condition. Pipe 1 low air flow. Cleaned out sample point. Other pipesshowing high airflow due to maintenance works. Normalised vesda flows. Fault cleared. BD 5/6 in alarm on arrival reset panel and alarm didnot return.
MSA-DFES | WA4014304 | Flouro light not working NE hallway and NE SES / RURAL offices | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 11:00:00 | Pass | Arrived on site at 10:30 to repair light in main office block. Replaced tube and starter, tested and continued on site at 11:00.
MSA-DFES | WA4014727 | engine bay door | VFRS Falcon | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 19 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 12:30:00 | Pass | COMPLETED
MSA-DFES | WA4014755 | dorm 2 night light turn out light not working | CFRS Joondalup | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 13:15:00 | Pass | Complete
MSA-DFES | WA4014783 | Workshop Amenities Southern Male Toilet Block damaged door - see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-03 14:00:00 | Fail | New door installed and painted to match existing colours
MSA-DFES | WA4014966 | Dorm 11/12 - 3x door lock unservicable | CFRS Ellen Brook | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-03 12:30:00 | Fail | Supply and install x 3 locks
MSA-DFES | WA4015054 | dam pumps relocate pumps as per Sharon instructions | FESA RHQ - Forrestfield | GMP-BR | Mechanical Services | Pumps (MS) | MALCOLM THOMPSON PUMPS PTY LTD | 1 | CLOSE | 19 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-26 07:00:00 | Fail | Repairs to pump
MSA-DFES | WA4015055 | Air con in the watchroom is leaking, water dripping onto the desk below | CFRS Maddington | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 09:00:00 | Pass | Aircon in watchroom was leaking. Proceeded to unblock drain and tested drain.
MSA-DTAG | WA4014333 | External - Several ceramic tiles are broken on main entrance steps/walkway ramp – OSH issue | Perth Children's Court | GMP-BR-HO | Flooring | Tiling (FL) | Midolo Building Services | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-29 22:43:00 | Fail | NEW CERAMIC TILES INSTALLED
MSA-DTAG | WA4014813 | in session buttons on few courts (35, 36 , 907 and few other ) being faulty - not operational . | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 19 Feb 2021 | 2021-02-19 15:27:46 | 2021-02-19 14:30:00 | Pass | Attended site and reset system, cleared all open alarms and tested relevant doors. All tested and working ok. Jobcomplete
MSA-DTAG | WA4014818 | L10 Banksia Marriage room doors not closing correctly manual opening | Westralia Square | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-02 15:28:00 | Fail | 19/2/21 - Inspected door and found that the door closed latch has failed, spoke with site and explained that a hydraulic door closer would be more suitable for use of door etc. please quote for 1x ts83 en3-62/3/21 - Banksia room- supplied and fitted TS72 closeR, adjusted and tested operation.
MSA-DTAG | WA4014828 | ground “In Session” Button not working in Room 5.06, 2.01 and 2.06 and 3.08 | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 19 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-19 15:00:00 | Pass | Attended site and reset system. Cleared all alarms and tested doors. All tested and working ok.Job completed.
MSA-DTAG | WA4014845 | Information center PA system has ceased working - see notes | Joondalup Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-19 13:30:00 | Pass | Attended site. Court had a power outage and PA system lost all settings.Reload settings from head unit and tested.Job completed.
MSA-DTAG | WA4014890 | Side wall of Courthouse has graffiti & poster stuck on the wall, please remove | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 17:00:00 | Pass | Removed Graffiti/Poster
MSA-DTAG | WA4014895 | ground Electronic button to open the public door from inside Room 4.06 isn’t working - see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-05 14:00:00 | Fail | Re-attended site and retested door push button, all tested and working correctly, checked programming and all sealing and unsealing ok. Found issue with door lock, replaced with new site lock, site stock usedAll tested and working correctly. Job complete
MSA-DTAG | WA4014910 | Drinking water fountain in Cell 1 has overflowed and caused cell 1 to be taken out of use | Joondalup Courthouse | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 0 | CLOSE | 19 Feb 2021 | 2021-02-19 16:46:44 | 2021-02-19 21:59:00 | Fail | Tech attended, solenoid valve requires replacement. Drain requires major plumber to attend - Blockage down further in the drain. ADVISED WORK ORDER TO BE CLOSED OUT AS PLUMBER TO ATTEND FIRST TO REPAIR DRAINS THEN WILL RETURNTO REPLACE PARTS FINISHED 2.30PM
MSA-DTAG | WA4014964 | Ground - Lift 1 doors weren’t closing on level 13 and it was making a noise | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-19 15:23:00 | Pass | Level 13 landing door twisted, realigned and tested. All ok and back in serviceTo be closed out at $0
MSA-DTAG | WA4014968 | Ground - Lift 5 or 6 was also described as making a new noise as if a bearing was failing. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-19 15:03:00 | Pass | Travelled in both lifts, can hear counterweight pass but no unusual noises.
MSA-DTAG | WA4015037 | custody Smell of dead animal from custody ceiling. | Mandurah Courthouse | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 11:35:00 | Pass | .
MSA-DTWD | WA4014734 | B block L1 Gate Rear Courtyard Lock to rear B Block gate barrel faulty2 | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 09:55:00 | Pass | Service lock & tighten cam screws
MSA-DTWD | WA4014754 | C Block, Room CF3- Air con not working, shuts down after 1 hour | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 10:41:00 | Pass | On inspection of system found 02 fault present. PSH protection enabled. Up pressure switch activated. Tested switch found to be faulty always in fault. Will source replacement and return to fit.Returned 23/02/21 removed and replaced faulty up. Switch. With new, tested system, working ok.
MSA-DTWD | WA4014804 | F Block, Heavy Fabrication workshop - Power point is damaged | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 14:18:00 | Pass | Repalced 7x faulty /damaged gpos in F blood as shown by site. Job completed
MSA-DTWD | WA4014848 | F block, workshop - Replace fluoro lights not working in the Heavy Fabrication workshop | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-25 14:45:00 | Fail | Retrofitted faulty light to led. Parts supplied by site.job completed
MSA-DTWD | WA4014859 | Workshop access area- multiple student lockers are faulty | Clarkson Campus | GMP-BR | Carpentry | Joinery (CA) | M Construction (WA) | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-08-02 10:00:00 | Fail | Assessed broken lockers. 66 are damaged and need doors replaced. Will return with a contractor to quote replacement. Asked by Eric Reedman to close job.
MSA-DTWD | WA4014933 | J block K-1 Restaurant- Kitchen blown lights | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 15:27:00 | Pass | Repalced faulty fluro starters and controls gear to lights kitchen.job completed
MSA-DTWD | WA4014937 | S Block, Room S104- Male toilet door broken off hinge | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-23 15:30:00 | Pass | Inspected damaged toilet door. Filled out jsa then found spare dome headed both. I then fixed the door hinge back in place and adjusted latch plate.
MSA-DTWD | WA4014939 | West Block - Arming Panel W101 has system faults | Mount Lawley Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-22 10:00:00 | Pass | 22/02/2021, 930-1000System showing low battery, replaced and cleared alarms
MSA-DTWD | WA4014959 | Room B41 prayer room air con fault - It stops when mode switched to cool or hot | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 11:30:00 | Pass | Sub contractor has attended site and installed new air con - job is complete
MSA-DTWD | WA4015023 | Rear Carpark off Lipfert St No bollard locks working. | Perth Campus B2 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-05 14:00:00 | Fail | Attended site 22/2/2021 to check bollards Bollard specialist required.Ram Guard Bollards attend site 5/3/2021 Service bollards
MSA-DTWD | WA4015027 | A Block, Lvl 3, Opposite A350- Male urinal is blocked | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 08:15:00 | Pass | Arrived on site and inspected found the urinal blocked. Used plunger and sprites of salt to clear the blockage. Tested multiple times all working in order.
MSA-DTWD | WA4015032 | A Block, There is an audible “beep” coming from the lift at a regular interval (estimate every min) | Carlisle Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 2 | FLDCOMP | 19 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 13:41:00 | Pass | CONTROLLER - MICROPROCESSOR UNIT - HIGH RESISTANCE CORRECTED
MSA-DTWD | WA4015059 | A Block, Level 2, A218 - latch faulty to door A218 | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 19 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-22 09:55:00 | Pass | Replace broken spring to handle
MSA-DTWD | WA4015090 | B block fire panel, analog faut room S2 | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 1 | CLOSE | 19 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-23 13:45:00 | Fail | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Brian Blechynden 0419900980Work Order Number: WA4015090Priority #: 2Call out Date: 19/02/2021Target finish: 22-2-21Work order contact: Brian Blechynden 0419900980Original information: B block fire panel, analog fault room S2. Attended site:Date:22/2/21Start Time:14:00Finish Time:16:15Techs on Site: 1Works Carried Out: Open circuit fault on zone 2 admin block at B block.Inspected and found break in circuit on cable from board room to in ceiling detector as no voltage on next detector at entrance to office .Follow up to either re-wire and replace in ceiling detector, discuss with facilities as no direct access to the in ceiling detector.Eol put in zone monitor and zone 2 isolated.Returned to site:Date:23/2/21Start Time:10:00Finish Time:13:45Techs on Site: 1Works Carried Out: Rewired detection cabling in admin block as open circuit fault, open circuit loca
MSA-DCA | WA4019919 | Vesda Faults, job to be attended on first thing on Monday 22/2/21 | Collection and Research Centre Welshpool | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 20 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 15:00:00 | Pass | Attend fault on systemFault find discovered vesda 6 faultDiagnose with program found filter near capacity?Req new / investigate may require pipework cleanCollect vesda filter , replaced reprog all okMATERIALS/CONSUMABLES USED:Vesda filter
MSA-DCA | WA4020059 | Lift is not working and has stopped -No one is stuck in the lift | PICA-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 20 Feb 2021 | 2021-02-20 20:40:42 | 2021-02-20 18:00:00 | Pass | completed non chargable
MSA-DCS | WA4019947 | leaking toilet in Unit 8, Cell A3 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-03 10:40:00 | Fail | Replaced inlet valve and replaced one of the bellows
MSA-DCS | WA4020046 | faulty lock on search room door | Banksia Hill Detention Centre | GMP-BR- HO | Building | Internal Walls (BU) | AAA Ability Locksmiths | 0 | CLOSE | 20 Feb 2021 | 2021-02-20 17:15:34 | 2021-02-20 14:30:00 | Pass | Attend site after hours. Search room door lock required replacement batteries. New AA batteries installed.
MSA-DCS | WA4020069 | Blocked toilet cell H23 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-03 10:00:00 | Fail | unblocked toilet
MSA-DCA | WA4020150 | Fire exit door is jammed can't open it | State Theatre Centre (Heath Ledger Theatre) | GMP-BR | Carpentry | Materials (CA) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 21 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-23 10:30:00 | Fail | Remove old mortice lock and replace with new and put a new keep on door frame.
MSA-DCS | WA4020080 | monitoring 228 in the control room is not working properly | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Feb 2021 | 2021-02-21 11:11:11 | 2021-02-23 10:00:00 | Fail | Follow up required, indigo vision passwords and further programming required. 23/02/21 Passwords obtained alarms cleared from system and restored. System test ok.
MSA-DCS | WA4020141 | M-das not working in 2 locations - unit 1 and unit 5 | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Feb 2021 | 2021-02-22 12:02:49 | 2021-04-12 09:30:00 | Fail | Transponder 13 replaced and reprogrammed Moxa. Rewired Transponder 13 in server room to have own Moxa port. Tested operation and all is now working.
MSA-DCS | WA4020156 | Blank camera in cell A3 in the Shu | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Feb 2021 | 2021-02-21 18:25:22 | 2021-02-21 17:45:00 | Pass | Refresh view on control room screens, test, all ok
MSA-DCS | WA4020157 | Hot water urn faulty ANC bay room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 21 Feb 2021 | 2021-02-22 14:28:01 | 2021-03-02 11:00:00 | Fail | No power on arrival, gpo blown. Switched gpo back on. Unit started filling (25L) long time, waited for element to turn on, after filling the unit completely the element blew the power again. Will check re warranty. Not common spares, need to organise parts from manufacturer - ordered special parts in returned and installed parts and checked unit A40183055 Billi Ultra System
MSA-DCS | WA4020158 | Casuarina Prison - Unit 14 - Cell 1A - Cell call is not working. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Feb 2021 | 2021-02-21 18:44:07 | 2021-02-25 11:00:00 | Fail | Code red in unit 14 at time of visit, advised to return Monday. No access 24/02/21 Intercom in lower bunk tested working ok.Cell guard standard size button only unit required for top bunk button does not activate system. ***Part required***25/02/21 Fault related to bug infestation causing damage to bottom intercom unit. Replaced with new unit retested ok.
MSA-DFES | WA4020155 | security gate failure, still receiving power, not responding to pressure pad and not secure | CFRS Vincent | GMP-BR | Building | Materials (BU) | Anvil Doors | 1 | CLOSE | 21 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 22:15:00 | Fail | Attend Vincent Fire Station on P1 call out to report of issue with security gate. The attending technician checked the gate and found that the rear limit stop was not in the correct position. The attending technician adjusted the limit stop, reset the logic and tested all inputs. The gate was tested to be functioning correctly.Please see attached service report and signature slip.Thank youAttended Recall on the 2.3.21. -- Technician was informed that gate closed on a vehicle. The gate capacitor was identified as defective and was subsequently replaced. Please see attached service reports and signature slip and quote
MSA-DCA | WA4023023 | garden bed by cleaners room broken sprinklers | Perth Cultural Centre Precinct-Cultural Centre Square-Ground Floor | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-23 11:30:00 | Pass | Repairs to sprinklers
MSA-DCA | WA4032435 | In car key barrel to restricted Lvl 4 area is loose & spinning | State Library of WA-Main Building-Level 5-Lift Lobby | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-10-07 15:55:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DCA | WA4032487 | florescent lights have gone out and making cracking noise, circuit breaker has tripped and unable to | Short Street Theatre-Main Building-Ground Floor-Cleaners Storage | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-23 10:15:00 | Pass | Complete
MSA-DCS | WA4020371 | control, internal MX1 not working - SEME on site | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-22 09:00:00 | Pass | Zone in unknown state. Reset controller. Checked calibration. Tested ok locally and to control.
MSA-DCS | WA4020377 | Unit 1 Cell B07 & B6 power points have no power. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 07:42:56 | 2021-02-23 15:00:00 | Fail | Investigated power loss to unit 1 b6-7 found power feed had been drilled into by maintenance team. Replaced damaged feed + gpos and tested
MSA-DCS | WA4020541 | Unit 16 - Control Room flow fault alarm/cannot be reset | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 07:50:36 | 2021-02-23 07:09:00 | Pass | Attended site found flow faults on cells c5,c6 and whilst on site cell b7 came into fault checked grills and found no blockages wasinvestigating but got moved out due to lunch and low staff, advised site we will be back tomorrow morning to continue investigation.23/2/20GA/JGAttended site and started rectifying the above faults from yesterday whilst onsite fire protection services attended and they have received a jobto clean out all air sense Vesda’s and replace any that were not operating correctly.ARA to close out this task as FPS have been engaged.
MSA-DCS | WA4020712 | control internal MX25 A/B not activationg- SEME on site | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 07:56:16 | 2021-02-23 09:00:00 | Fail | Shut down and restarted Network Manager 4 program on the Senstar PC. Shut down and restarted the network controller and the Intelliflex fence power. Cleared errors on EBI. Both zones tested ok.
MSA-DCS | WA4020824 | Unit 14 - D6 cell door will not open from the inside - see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 07:59:32 | 2021-02-22 10:30:00 | Pass | Replace mortise lock.
MSA-DCS | WA4020907 | air con not cooling and oil leaking from part of the outside | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Corridor (Next to Visits Waiting Area) | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 08:02:47 | 2021-03-19 11:00:00 | Fail | Repairs complete. Replaced compressor and contactor/overload. Unit fully operational
MSA-DCS | WA4020920 | CCU (11) - Hot water unit in CCU "appears to be too hot". | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-15 12:30:00 | Fail | Nill
MSA-DCS | WA4020969 | Unit 5 - The sound of running water between cell A9/A10 believed to be the toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 08:30:00 | Pass | Nill
MSA-DCS | WA4021359 | unit 14 - C3 hot water tap wont turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 14:30:00 | Pass | Noll
MSA-DCS | WA4021439 | unit 14 C3 - shower and sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 13:30:00 | Pass | Nill
MSA-DCS | WA4021492 | Unit 1, C wing - No hot water in the c wing bathroom includes showers and sinks | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 08:18:03 | 2021-02-22 13:58:00 | Pass | Nill
MSA-DCS | WA4021520 | plant room vesda fire fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 10:33:00 | Pass | 24/2/21 MBUnit 1 Vesda in Plant Room in ‘Zone fault’ due to too many scans in a week. Alert threshold still at factory setting, raised threshold by approx10% and reset Vesda. No further faults occurred whilst on site.
MSA-DCS | WA4021626 | unit 5 control door lock faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 12:20:30 | 2021-02-22 10:15:00 | Pass | COMPLETED
MSA-DCS | WA4021812 | conrol access audio and visual not alarms activating correctly | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 12:26:13 | 2021-02-22 12:41:00 | Fail | Attended siteReplicated issue reportedChecked all alarm settings and was unable to find any odd settings to cause the issuesRestarted both work stationsRe-tested all perimeters, confirmed working correctly as the highest priorityDiagnosed the software logs needed to be refreshed via restarting the PCs Advised site of the outcomeLeft site
MSA-DCS | WA4021933 | Unit 1 cell B02 sink is blocked/slowly draining. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 09:30:00 | Pass | Nill
MSA-DCS | WA4022102 | Unit 3, A9 - floor drain is flooding the cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-12 13:30:00 | Fail | Nill
MSA-DCS | WA4023186 | Shower drain in Cell A11 is blocked, plunger has not been working to rectify problem | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-05 15:30:00 | Fail | Nill
MSA-DCS | WA4023391 | External Gardens Knoll pump not switching on either in auto or manual mode | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 08:36:02 | 2021-02-22 15:00:00 | Pass | FOUND NO FAULT WITH SYSTEM BUT NOTED THAT THE PUMP IS NOT OPERATIONAL. PUMP IS BEING WORKED ON BY OTHER CONTRACTORS.
MSA-DCS | WA4023575 | Unit 7, B wing - main tap faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 15:30:00 | Pass | Nill
MSA-DCS | WA4023759 | Unit 2 cell B2 - toilet cistern keeps running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-22 15:30:00 | Pass | Nill
MSA-DCS | WA4023867 | Unit 1 - Office PA system in unit 1 not working | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 08:52:07 | 2021-02-22 15:55:00 | Pass | Investigated PA fault. Checked PA in gatehouse, checked audio communication equipment.Checked equipment at unit and traced to suspected intermittent fault with analog telephone in Unit 1 Control Pod. Advised staff they need NEC technicians to investigate PABX phone.Job Complete
MSA-DCS | WA4024016 | Unit 13, D14 - sink leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 12:30:00 | Pass | Nill
MSA-DCS | WA4024334 | Unit 7 - A Wing faulty light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-23 08:30:00 | Pass | Repaired faulty lights in unit 7 a wing
MSA-DCS | WA4024357 | UNIT 5, C WING - The sink of the cleaning cupboard is blocked. Its very slowly draining | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-12 15:30:00 | Fail | Nill
MSA-DCS | WA4024648 | unit 1 C1 Cell call has been damaged and keeps showing up as tamper on the control panel. | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 09:02:17 | 2021-02-24 16:05:00 | Fail | Replaced damaged cell call with new, tested working ok. Job completed.
MSA-DCS | WA4024736 | Reception S/O, Operations a/c unit leaking water | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 08:30:00 | Pass | Arrived on site and signed in tools,cleared blocked draain and cleaaned and flushed,all flowwing ok.
MSA-DCS | WA4024773 | Unit 13, D9 - constant trickle of water down the side of the sink basin & cell wall creating puddles | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-03 08:30:00 | Fail | Nill
MSA-DCS | WA4024927 | Unit 4, Cell H31 - shower taps leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 10:30:00 | Pass | Replaced Tapware
MSA-DCS | WA4024974 | Unit 5, C wing - Leaking pipe in food storage room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-17 13:30:00 | Fail | Nill
MSA-DCS | WA4025108 | Unit 5, B10 cell alarm working, just very quiet when talking to the pod. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 08:00:00 | Pass | Debris cleaned from unit retested ok.
MSA-DCS | WA4025137 | Unit 14, cell A9 - hot water from tap still running, split pin shorn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 09:10:42 | 2021-02-22 13:55:00 | Pass | Nill
MSA-DCS | WA4025189 | Unit 5, Cell C7- Cell alarm is very quiet when talking with the pod. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 09:00:00 | Pass | Debris cleaned from unit retested ok.
MSA-DCS | WA4025382 | Unit 2 - all wings shower cubicles missing tiles | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-04 13:30:00 | Fail | 06/09/21 - closing job cost to date as site not given us response on access - cost for labour only/inspection
MSA-DCS | WA4025383 | Unit 6 - Low water pressure in c wing shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 13:17:00 | Pass | Nill
MSA-DCS | WA4025542 | Unit 13, Cell B13- Water leaking under the bed from shower screen | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-03 12:30:00 | Fail | SHOWER LEAK REPAIRED
MSA-DCS | WA4025640 | Bakery, workshop - fault light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-18 15:00:00 | Fail | Repaired faulty lights in bakery on scissor lift. Replaced faulty switch panel
MSA-DCS | WA4025832 | SHU, A4 - Fluro tube globe in cell A4 light is flashing on and off and needs to be replaced | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 09:17:40 | 2021-02-22 12:30:00 | Pass | Repaired faulty lights in SHU. Waited access for cell
MSA-DCS | WA4025833 | Unit 3, Cell B12- viewing hatch window broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 12:30:00 | Pass | VIEWING GLASS RE GLAZED
MSA-DCS | WA4025926 | Unit 5, Cell C11- Window will not stay open. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 15:00:00 | Pass | REPAIRS MADE TO SLIDING WINDOW/FRAME
MSA-DCS | WA4026156 | Unit 5, Cell A13 - Cell window will not stay open. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 13:30:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA4026351 | unit 4 zone 6 in constant alarm cannot be cleared - SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 17:23:59 | 2021-02-22 17:30:00 | Fail | Attended Unit 4 (PRU) EC3 and connected Intelliflex tested/programmer to Controller card. Monitored Fence noise level for indication of activation. Zone came nowhere near preset threshold. At PRU control interrogated Gallagher system and found Lock block associated with the zone latched on.rsset zone and monitored zone from PRU control. Zone now stable.
MSA-DCS | WA4026842 | Unit 3, Cell C3- window runners missing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-03 15:00:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA4026881 | Unit 3, Cell A2- window runners missing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-04 12:30:00 | Fail | SPIRAL BALANCES RE NEWED AND FRAME REPAIRS
MSA-DCS | WA4028202 | Unit 13, Cell D03- Sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-03 09:30:00 | Fail | Nill
MSA-DCS | WA4028280 | SOG base demountable office air con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-18 13:53:00 | Fail | New wall mounted split system installed, commissioned & set to work.
MSA-DCS | WA4028337 | Unit 14, Cell D11- Personal lock will not work | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-22 12:00:00 | Pass | Replace mortise lock and remove broken key.
MSA-DCS | WA4028719 | unit 4, CL5 - bunk lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-22 15:00:00 | Pass | Replaced bunk light tube
MSA-DCS | WA4029027 | Please extract CCTV footage as per request | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 10:24:22 | 2021-02-22 14:30:00 | Pass | Retrieved footage as requested. Footage given to GAVIN KERR. Tested ok on his PC.
MSA-DCS | WA4031688 | Unit 1, Cell D4- Lock not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 11:45:00 | Pass | Attempt repair - require parts.Replace Barrel.
MSA-DCS | WA4031904 | Unit 2 - C6 Personal lock not working, Barrel requires replacing. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-17 11:00:00 | Fail | Require parts.Replace barrel, door plate, lock and hinges.
MSA-DCS | WA4032310 | Unit 2- Smelly brown waste coming up through drainage pipe in water cupboard & cell basin B9-B10 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 16:18:40 | 2021-02-22 14:00:00 | Pass | Nill
MSA-DCS | WA4032333 | Kitchen, Work Area- 2 x Sinks tap washers leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 09:30:00 | Pass | Rewasher kitchen taps
MSA-DCS | WA4032335 | Unit 1, A & B Wing kitchen sink- Tap is broken | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 10:00:00 | Pass | Reseat and rewasher kitchen taps
MSA-DCS | WA4032348 | Unit 2, Cell A9- Prisoners Lock Door Cartridge Broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 10:30:00 | Pass | Attend site. Inspected lock, no damage found. Multiple keys used to test lock. No faults found.
MSA-DCS | WA4032361 | Unit 2A, Cell 11- Cell window runners are damaged | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-04-08 14:00:00 | Fail | new sash rollers fitted
MSA-DCS | WA4032366 | Unit 2B, Ablutions north end broken window | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-04 15:00:00 | Fail | NEW WINDOW FITTED
MSA-DCS | WA4032394 | unit 4, Control room - Bottom latch on control room door has come unsecured. Door doesn’t self close | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 17:37:24 | 2021-02-22 16:30:00 | Pass | HINGE RE SECURED TO DOOR FRAME - DOOR NOW OPERATIONAL
MSA-DCS | WA4032396 | Control - cell call fault, | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 13:42:14 | 2021-03-17 15:30:00 | Fail | After replacing the CI8 for a CI8a the intercom in U10C8 was removed and replaced. Tested loud and clear in the cell and the n control. Parts used:Austco CI-CC intercom taken from site stockRJ45 wiring adapter taken from SEME stockSite stock was replaced with new CI-CC
MSA-DCS | WA4032399 | external Gardens - west side pumps tripping out mid cycle showing low flow | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 13:47:00 | 2021-02-24 10:15:00 | Fail | 23-2-2021 - Liaise with Larry regarding faulty, diagnosis the fault to station #2 solenoid valve, irrigation time removed from station 2.Larry has arranged access to inside the prison for 7:30am 24-2-2021.24-2-2021 - Located faulty solenoid valve and repair, check for correct operation.
MSA-DCS | WA4032419 | kitchen No2 combi oven showing faults | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 14:14:09 | 2021-02-26 12:05:00 | Fail | Replaced faulty ignition module & blower , left in working condition.
MSA-DCS | WA4032454 | Unit 7, E19, E20 - Water leaking from duct between E19 & E20 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 14:57:05 | 2021-02-23 14:45:00 | Pass | Replace corroded pipe with flexi to suit new pipework
MSA-DCS | WA4032459 | Unit 10, A/B dayroom door electric lock faulty needs repair | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 15:03:46 | 2021-02-23 12:30:00 | Pass | Replaced defective electric strike and tested ok, job completed.
MSA-DCS | WA4032478 | Amenities building- Camera 1 is not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-04-09 17:00:00 | Fail | Accessed camera using Boom Lift. Checked for voltage at camera, no 12v. Using tone source traced cable into equipment room and located damaged cable connection under floor ( possibly caused when new cable installed). Repaired cable joint and reconnected camera. Camera now viewable on Indigo CCTV.
MSA-DCS | WA4032479 | Temp sally port- external vehicle gate camera not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-26 18:00:00 | Fail | Identified fault as Intermittent fault in CoAxial cable patch lead between OSD fibre modem and Indigo Encoder in Gatehouse Equipment room Rack 06. Disconnected and reconnected patch cable to restore video.
MSA-DCS | WA4032482 | Vegetable prep- constant alarms, see notes below | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 11:30:00 | Pass | Three doors in perm alarm: 1. Inwards goods Ped door- new door missing magnet - drilled door installed magnet. 2. Outwards goods roller door. HD roller door reed switch damaged (? Forklift) - removed damaged reed switch, rebated concrete floor, installed new reed switch, rebated cable entry and supplies and installed aluminium checker plate protection cover. 3. Outwards goods Ped door - new door , drilled door installed magnet, damaged cable at reed switch. Repaired and covered with flexible conduit.
MSA-DCS | WA4032483 | Cabinet shop room in constant alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 14:30:00 | Pass | Passive Infrared Detector in SW corner of Cabinet shop building (old Upholstery room) constant alarms. Removed PIR and extended cable to allow installation of new unit. Installed new PIR and tested operation to control.
MSA-DCS | WA4032486 | Pump alarm showing fault on security circuit | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-05-06 11:00:00 | Fail | Checked history of alarms from pump, none since 2008. Checked nearby Bore pump, no alarm output. Cable from alarm point travels via ceiling space to ???. Discussed fault with Tony Vavier (ASSIEM) who advised to disable alarm and sign off.
MSA-DCS | WA4032490 | Visits Area - admin male toilet urinal blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 14:30:00 | Pass | Nill
MSA-DFES | WA4032245 | Kitchen Sink Flick Mixer failing rigid & sticking handle | CFRS Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 13:15:00 | Pass | Replaced kitchen sink mixer tap
MSA-DFES | WA4032263 | Door Pelmet to PPC storage room Broken | CFRS Belmont | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 08:30:00 | Pass | Signed in and shown the job, removed the pelmets and screws and glued the ends back in, reinstalled cleaned up and signed out
MSA-DFES | WA4032331 | door leading from duty room to engine room - door lock faulty, can not lock | CFRS Joondalup | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 12:40:00 | Pass | REPLACE CODE LOCK.STRIKE & ADJUST CLOSER
MSA-DFES | WA4032332 | Gym sliding door - faulty door lock | CFRS Joondalup | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 11:30:00 | Pass | Supply & Install Lockwood Onyx to gym sliding door
MSA-DFES | WA4032463 | Engine Room Door (front pump door) will not close/wont respond | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 19:05:35 | 2021-02-22 17:30:00 | Pass | Attended Claremont Fire station on P0 call out regarding issue reported as "engine room door front pump door will not close/wont respond". Service electrical technician attended and found the issue was with the control button ,number 1 up. the button was removed and checked and reinstalled. The button requires replacement. The door was left operating. The following morning we received a call back as the door is not operating again. as button number 1 up needs top be replaced, it is our recomentdation that all 8 buttons are replaced at the same time to prevent any future issues. Please see attached service report, site photos, signature slip, DAS and QuoteThank you
MSA-DFES | WA4032470 | Perimeter fence damage - Holes appear in the fence links, due to vandalism | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-15 14:00:00 | Fail | Front perimeter fence has been replaced with new cyclone fencing , strainer and barb wire. All existing posts were reused.
MSA-DFES | WA4032475 | Front lawn - broken retic head. (between the entry keypad & tree) | CFRS Claremont | GMP-BR | Plumbing & Drainage | Water (PD) | Dom's Total Grounds Maintenance | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-23 15:35:00 | Pass | Call out & Labour & Supply 1 x Nozzle
MSA-DFES | WA4032499 | Light at eastern end of the Vintage Fleet Workshop is hanging down from the ceiling. | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 10:15:00 | Pass | Complete
MSA-DFES | WA4032500 | Female Dorm - Air conditioning unit is making loud noise | CFRS Daglish | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 15:00:00 | Pass | Fixed rattle in ac
MSA-DFES | WA4032777 | Kitchen- flick mixer tap is unservicable due to corrosion | CFRS Vincent | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 12:15:00 | Pass | Replaced sink mixer tap.
MSA-DTAG | WA4025704 | control room don't have visuals of BB lift A , BB lift B , BB lift C, Ground Public entry C012 PTZ | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-12 06:30:00 | Fail | Work performed by Michael Tomlinson (22/02/2021)Found switch on Level 10 SAT with no network traffic to POE Cisco Edge switch. All reset and checked working again. Allokay.Work performed by Nathan Groenewald (12/03/2021)No visuals on certain cameras, reset all camera power and reconnected to servers. Re-tested and all tested and workingcorrectly.Job completed
MSA-DTAG | WA4028879 | Level 29 auto foyer door opposite F lift is stuck in open state after access granted | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 14:15:15 | 2021-03-08 11:30:00 | Fail | Attended site with Dorma door technician, re-checked programming and all programming side checked ok, went through history logs from December to most recent and all logs seem ok with no irregular faults present.Tested all inputs/Press to exit buttons and Emergency break glass, all inputs tested and activating ok. Checked voltage levels and all extra low voltage side is all ok.Had Dorma test the auto door, found no issues on the auto door motor. Had motor factory reset/defaulted and re-programmed again. Checked door logs, found 1 error code but does not appear to relate to any security equipment triggers as is not being used or is programmed into our equipment. All door functions tested and working correctly, no other issues found. Issue may possibly be related to an irregular mains voltage going through the motor/controllers on the auto door, unable to confirm without licensed electrician, and also may need to test when the fault occurs, which would make it hard to do. Dorma will
MSA-DTAG | WA4030825 | L10 duress alarms remote witness room faulty - not activating when pressed. | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-03-05 10:15:00 | Fail | Reattended site and retested duress buttons with updated software in system, all tested and reset correctly. Job complete
MSA-DTAG | WA4032303 | Custody - Staff Toilet door handle screw has come loose & looks as though it will fall off | Armadale Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-05 10:15:00 | Fail | NEW DOOR HANDLE RE SECURED
MSA-DTAG | WA4032336 | Reception Still unable to hear visitors through microphones - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-24 11:15:00 | Fail | Tested system and is working correctly but when the ambient noise is too loud it makes it hard to hear
MSA-DTAG | WA4032345 | 1903 ground Kitchen near custody centre door Strong smell like dead animal matter | Supreme Court | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-23 07:40:00 | Pass | .
MSA-DTAG | WA4032436 | room 1.06 no notification recieved when alarm activated - see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-23 12:30:00 | Pass | Cleared alarms and reinitialized controller associated with duress and retested system. All tested and working ok. Job complete
MSA-DTAG | WA4032451 | Kitchen - Filtered water/zip tap on Lvl 10 isn’t working for either the hot or cold water. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 15:10:00 | Pass | Replaced element due to tripping power. Unit under warranty. CHARGED WARRANTY WORKS TO BILLI REPLACED ELEMENT
MSA-DTAG | WA4032469 | The fire panle is reflecting a fault " 1st Floor Magistrates Office" and is sounding an alarm | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 19:12:08 | 2021-02-22 16:15:00 | Pass | Investigated fault to find zone 3 intermittent fault.panel reset and detectors to be changed 27/02/21 System normal on departure.
MSA-DTWD | WA4020279 | A block East End Level 3 blocke urinal | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Feb 2021 | 2021-02-22 17:00:00 | 2021-02-22 09:00:00 | Pass | Arrived on site and inspected found the blocked urinal. Used plunger and sprites of salt to clear the blockage and tested multiple times all working in order.
MSA-DTWD | WA4020372 | Main front reception counter top, front edge is damaged | Jandakot Campus - Hangar | GMP-BR | Carpentry | Timber (all types) (CA) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-24 17:00:00 | 2021-04-09 12:21:00 | Fail | Works carried out - benchtop install
MSA-DTWD | WA4020375 | G block ground male studet toilet Cubicle wont flush - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 2 | CLOSE | 22 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 09:30:00 | Pass | Investigate faulty toilet. Faulty flush valve . Source new valve. Refitted tested and commissioned toilet.
MSA-DTWD | WA4020382 | internal balcony above reception roof leaks | Jandakot Campus - Hangar | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-18 13:00:00 | Fail | work completed as per signature slip
MSA-DTWD | WA4021203 | Presentation Room B201 - downlight faulty | East Perth Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 12:09:30 | 2021-02-22 13:00:00 | Fail | Repalced cable and switch.job completed
MSA-DTWD | WA4021932 | S106 alarm activated E block and locking out air con | Mount Lawley Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 22 Feb 2021 | 2021-02-22 12:28:42 | 2021-02-22 10:00:00 | Pass | Investigated alarm zone 7 to find detector in plant room in alarm. Alarm values on detector back at 0% so reset and all okay.Alarm possibly caused by smoke or dust entering plant room through outdoor louvres
MSA-DTWD | WA4027125 | A block L1 passage way West 1st Floor the water fountain does not chill the water anymore | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-09 12:00:00 | Fail | Reinstalled chiller unit after repair. Time 10.30 to 12.00pmsee 3rd party invoice for repairs completed on Undersink Chiller unit off site - reinstalled on 9.3.21 working well
MSA-DTWD | WA4027700 | E Block, E26 Corridor external door dragging & hard to close | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 12:15:00 | Pass | Refix ali frame back to wall and adjust hinges
MSA-DTWD | WA4027818 | F Block, F30 – Several faulty light fittings | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-22 15:30:00 | Pass | Attended site and signed in. Located f block lights. Checked out classroom and found multiple lights out and one broken and hanging. Dismantle and repair end of light fitting and refit parts. Supply and replace tubes and starters. Lights at front of class have been isolated due to projector installed on those rows. Supply and replace ballast where needed. Signed out. Job complete
MSA-DTWD | WA4027931 | B Block, Room B246- Air Con is leaking | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-22 14:00:00 | Pass | Blew out drain. Found some resistance in drain but unsure if completely blocked. Sealed around ends of pipe insulation at condenser unit as issue was found on another unit that condensation water was running down loose insulation. Checked operation. No further leaks found.
MSA-DTWD | WA4028570 | level 1, pump room - Pump running constantly | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Critical Fire Protection & Training | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 11:00:00 | Pass | On arrival electric pump running, suspect pressure fluctuation activated electric pump.Electric pump run is not monitored and no external alarms.Pump run continuously until noticed by tafe staff.Stopped electric pump with manual stop button (on controller)Water below sprinkler stop valves extremely hot (pipework very hot to the touch)Dropped pressure on sprinkler to allow jacking pump to push fresh cool water through pipework.Pressures all sitting normal, pumps sitting normal, pipework at normal temperature.
MSA-DTWD | WA4029188 | A Block, Room A004.1- Air Con air direction flaps not working. | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-07-15 10:00:00 | Fail | Parts obtained and access to unit gained and isolated. Indoor louvre mtrs replaced and tested.all ok
MSA-DTWD | WA4029853 | Refix sign that has fallen over at the cnr of Mirrabooka Ave & Reid Hwy | Balga Campus | GMP-BR | Signage | General Signage (SI) | AWB Co. | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-23 12:30:00 | Pass | Arrived on site and call site contact Gefri he guided me to the signs location after finding a hole in the fence to access I took the attached photo. I suggest that we hand this job to a contractorSubmitted BRAF, declined.
MSA-DTWD | WA4032241 | Block G G9 Kitchenette Wall Urn mixer has fallen off | Bentley Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 19:30:00 | Pass | replaced autoboil tap, repiped vent, resecured unit to wall
MSA-DTWD | WA4032330 | Block E, Room E1- combination fan/light switch is faulty | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 13:15:00 | Pass | Attended site and signed in. Located E block and found switch in classroom to be non compliant and broken. Supply and replace with new 4 gang switch with fan controller. Looked at switchboard and found to be an old type switchboard and parts are not available. It did have a door once but now doesn’t. Advised site to get a carpenter to knock up a frame and door for it and have it covered that way. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4032357 | rooms E1 and E2 two doors have trouble being opened. Need to be re-hung and locks checked. | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 13:15:00 | Pass | Inspected both external doors that were rubbing. I filled out a jsa then removed one of the doors that was rubbing on the floor. I moved the hinges down allowing the door to clear the floor then filed down the strike plate. I asked Peter to check the door locked. I tightened up all the screws on the other door and also noticed the decking was rubbing the bottom of the door. The decking is to be fixed on another work order. Filled out signature slip to complete the job
MSA-DTWD | WA4032381 | decking outside room E3 needs repairs safety issue - photo's to follow in email | Murdoch Campus | GMP-BR | Carpentry | Timber (all types) (CA) | AWB Co. | 3 | CLOSE | 22 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 15:30:00 | Pass | Inspected damaged decking then filled out a jsa. I removed the damaged decking then cut new ones from timbers provided by facilities manager. I had to form a rebated to allow timbers to sit level onto of the metal sub structure. I removed another piece of decking and turned it end for end and screwed it back into place. I then screwed down the decking that needed additional fixings to keep them secure. I filled out a signature slip and cleaned the work area to complete the job.
MSA-DTWD | WA4032385 | Tower block level 4 east office requires damaged walls to be repaired and painted | West One Services | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-03 14:00:00 | Fail | Tower block level 4 east officerequires damaged walls to be repaired and paintedPaint and patch walls
MSA-DTWD | WA4032403 | A Block, Room A01/A17- 2x Light fittings not working | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 15:00:00 | Pass | Repalced faulty control gear to lights.job completed
MSA-DTWD | WA4032406 | D-Block - 1st Floor ( Library ) disabled toilet has come loose | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-24 12:30:00 | Fail | Arrived on site and inspected found the disabled toilet seat is broken and the pan having a crack. Need parts. Ordered parts and will come back once we have the parts. Collected parts from supplier and returned to the site. Removed the faulty pan and installed new pan. Tested multiple times all working in order. Cleaned up the site.
MSA-DTWD | WA4032418 | B Block, Room B2111- Ceiling bulk head has dropped | Bentley Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-04-23 11:00:00 | Fail | Work done over two days___ scope site, jsa, plastic floor hallway to stop spread of mess, re staple case bead, corner trim, re cut out vent holes, base, base again, scrape, top, sand, undercoat, tried to make flashings fit but finish not suitable, need to be removed and something new put in place, bulk head still needs small pin holes filled and painting, large site clean so that room can be used, clean hall way.Pick up gear from Bunnings and sign safety documents sand and paint bulkhead clean up get job signed off
MSA-DTWD | WA4032424 | G Block, Dog kennel area- 2x door locks faulty | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 08:30:00 | Pass | G Block - kennel area - 2 x door locks faulty.Locks repaired.
MSA-DTWD | WA4032431 | B block, level 1 - Lift B Block Stopped working | East Perth Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 16:00:00 | Pass | Completed non chargeable
MSA-DTWD | WA4032441 | C Block, 1st Floor glass auto sliding door not opening from inside at all times | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 11:16:00 | Pass | Inspected door and found that the internal activation sensors was faulty,spoke with site and they asked me to replace both activation sensors. Replaced 2x activation sensors with Microhead type sensors, checked over door and tested operation upon completion.
MSA-DTWD | WA4032443 | Carpark lighting adjust timers and replace blown globes - see notes | West One Services | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-26 10:30:00 | Fail | Attended site and signed in. Supply and replace lamps to rear carpark walls. Cleaned out diffusers. Sealed up lights. Supply and replaced timer to building lighting and timer was faulty out of box. Got replacement timer. Changed over and set times as required. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4032488 | U022.5 - air con blowing hot air | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 10:30:00 | Pass | Complete roof works permits. Access roof with harness and fall restraints. Locate unit and found to have faulty wiring to water solenoid. Check operation.
MSA-MRWA | WA4028981 | Domestic hot water circulation pump is leaking, please attend and remediate | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Boiler Room | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Feb 2021 | 2021-02-23 17:00:00 | 2021-02-22 15:32:00 | Pass | Inspected faulty pumps and cleared blocked floor drain.
MSA-MRWA | WA4032437 | Lift 2 - Lift in lift not working | Don Aitken Centre MRWA Head Office-Main Building-Basement-Lift Car 2 | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-22 17:00:00 | Pass | Completed non chargeable
MSA-MRWA | WA4032439 | Blocked condensate drain on aircon | Don Aitken Centre MRWA Head Office-Main Building-Basement-PABX Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 22 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 16:30:00 | Pass | Quote to be submitted
MSA-DCA | WA4032906 | front of house, cracked toilet bowl leaking when flushed | His Majesty's Theatre-Theatre Building-Ground Floor-Female Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-19 13:30:00 | Fail | Replaced toilet pan , seat and pan collar
MSA-DCA | WA4032911 | large floor to ceiling mirror coming away from the wall needs to be looked at and fixed if poss | His Majesty's Theatre-Theatre Building-Level 2-Studio 1 - WAB Studio | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-16 09:30:00 | Fail | ATTENDED SITE TO ASSESS MIRRORRETURNED LATER DATESEALED AROUND MIRROR1 TUBE OF CLEAR SILICONE AND 2 TUBES OF WHITE USED2 MEN & LARGE PLATFORM LADDER REQUIRED
MSA-DCA | WA4032912 | Domestic hot water circulation pump noisy | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - In Front of Lift | GMP-BR | Refrigeration | Materials (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-04-13 16:30:00 | Fail | Attended site. Domestic Hwp noisey and leaking water. Applied tests and checks to find main gland/seal defective & bearings u/s. Submitted a Brag to remove and repair pump. Braf approved. Removed pump for applicable repair works. Reinstalled pump and tested operation. System operating correctly.
MSA-DCA | WA4032918 | plant room chiller system in fault | Perth Concert Hall-Main Building-Ground Floor | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 13:27:09 | 2021-04-12 14:00:00 | Fail | Spoke to Bruce and signed into SiteWe noted the Cooling Towers 1 tripped on Low Level alarm. We tested the probes which are havebeen found defective.Recommend replacement as per Bruce's instructions.Collect parts from workshop and supplier. Return to site. Isolate cooling tower. Install hi/lo water float sensor as per work orders. Schneider to electrically connect and complete commissioning. Job complete.
MSA-DCA | WA4032927 | Chiller 1 in fault | Collection and Research Centre Welshpool-Administration and Library Building-Roof Level-Rooftop Plant - Above Administration | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 14:00:00 | Pass | Attended site. Chiller 1 in fault. Applied tests and checks. Investigation found chiller 1 to have faulted on a HP error. Reset HP and tested operation. Investigation found condenser fan VSD to have tripped. Reset VSD and carried out electrical tests and checks to fan motor and electrical switching gear (ok). Tested chiller operation. System operating correctly.
MSA-DCA | WA4032943 | cracked window 1689 wide by 1986 high - please contact Bruce prior to attendance | Perth Concert Hall-Main Building-Ground Floor | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-11 10:00:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSRETURNED LATER DATE TO REGLAZE8.38 CLEAR LAMINATED SAFETY GLASS1-1700 X 200115 L/M OF RUBBER AND 2 TUBES OF SILICONE USED5 MEN REQUIRED
MSA-DCA | WA4033263 | exteria door unable to lock with key | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Multi Purpose Room | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 18:07:42 | 2021-02-23 15:15:00 | Pass | Not a lock problem - Access Control Company required
MSA-DCS | WA4032535 | Front Gate alarm and door opening monitor faulty | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 06:37:58 | 2021-03-16 13:30:00 | Fail | Installed new monitor and extended 12v power supply to new monitor. All is up and running as per normal functionality
MSA-DCS | WA4032762 | Hotham B1 drains clogged solid | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-11 09:50:00 | Fail | Cleared blocked sink.
MSA-DCS | WA4032764 | Unit 3 - D Wing shower leaking hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-10 15:30:00 | Fail | Nill
MSA-DCS | WA4032767 | unit 3 A Wing showers build up of calcium so water not coming out very well. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-10 14:30:00 | Fail | Nill
MSA-DCS | WA4032776 | Outpatients Area gate to the right hand side of S8 can not double lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 23 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-23 13:00:00 | Pass | Service lock and remove debris from bottom locking bolt.
MSA-DCS | WA4032784 | E wing cleaning cupboard light switch faulty needs repair | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:05:28 | 2021-02-23 12:15:00 | Pass | Replaced faulty light switch with a new one . Test ran ok.
MSA-DCS | WA4032786 | Unit 7, Cell E20 intercom lot of static on line hard to hear needs repair | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:10:13 | 2021-02-23 15:43:00 | Pass | Replaced damaged cell call with new, tested ok. Job completed.
MSA-DCS | WA4032792 | Property store - Property store light not turning on | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:13:56 | 2021-02-23 11:00:00 | Pass | Replaced lamps and starters. Traced out control and there multiple switches in series that prevent the lights coming on if all switches are not on. Staff are aware of the switches required to be on.
MSA-DCS | WA4032793 | cleaning office evap air water contiunes to run after switched off | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:14:07 | 2021-03-08 13:30:00 | Fail | COMPLETED
MSA-DCS | WA4032802 | Kitchen - bakers oven not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:28:22 | 2021-02-23 16:30:00 | Pass | COMPLETED
MSA-DCS | WA4032806 | ISU medication/interview room, smashed winding 1400x600 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 12:29:51 | 2021-02-24 11:00:00 | Fail | SMASHED WINDOW RE GLAZED
MSA-DCS | WA4032810 | MPU (8), lobby area - SPU unit washing machine intermittently working | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-15 12:00:00 | Fail | MPU (8) lobby area - SPU unit washing machine intermittently working. Check machine, remove for repairs. Agent repaired as required. Assemble & test. Return to Store.
MSA-DCS | WA4032815 | Central Admin - Air con issues, system not holding temperature | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:37:33 | 2021-02-25 14:28:00 | Fail | Luke Crisp (25/02/2021) - Material NotePicked up parts Attended site Began checks on the system with single stage running, made a few modifications to temperatures and noted further issues that need to be fixed for system operation.Gained roof access to change the condenser fan motor on stage 1. Replaced fan motor and 2x fan capacitors on stage 1 and stage 2.Conducted tests on system stage 1 pressures 410kpa and 1550 kpa amps 10a per phase both stages running well and sweating back nicely. Returned to plant room and unblocked drain, conducted further measurements and tests on system, further works to be submitted for approval.Packed up reported findings left site.
MSA-DCS | WA4032817 | unit 7 F5 leaking toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-03 15:21:00 | Fail | Replace outlet washer 2 plastic parts and red washer
MSA-DCS | WA4032821 | Jasper - A02, light switch smashed off wall & light smashed cover | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 10:00:00 | Pass | Replaced light and light switch
MSA-DCS | WA4032823 | unit 7 H23 Toilet continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-03 14:30:00 | Fail | Replaced outlet washer and 2 plastic parts from outlet valve and red washer
MSA-DCS | WA4032827 | Jasper - A01,Light switch smashed off wall | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:45:46 | 2021-02-25 11:00:00 | Fail | Replaced light and light switch
MSA-DCS | WA4032829 | Unit 7 H24 faulty sink tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-03 13:25:00 | Fail | Replace tap and handle
MSA-DCS | WA4032831 | Unit 7 G1 toilet will not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-25 08:32:00 | Fail | Replaced tpilet, toilet seat, and adjusted pipe work to suit
MSA-DCS | WA4032835 | Jasper, A01 & A02 - Mirror smashed | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:51:15 | 2021-02-25 12:00:00 | Fail | 2 X MIRRORS & 4 X WALL TILES REPLACED
MSA-DCS | WA4032836 | Unit 7 H7 Toilet continuously running needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-03 13:07:00 | Fail | Replaced outlet washer 2 plastic parts from outlet and red washer
MSA-DCS | WA4032838 | Jasper, B04 - x2 cell window x1 mirror x1 obs window damaged | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 08:53:39 | 2021-02-24 15:00:00 | Fail | WINDOWS RE GLAZED AND MIRROR REPLACED
MSA-DCS | WA4032890 | Jasper, A wing living room - small window cracked approx 450x300 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo Building Services | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 13:00:00 | Pass | WINDOW PANEL REPLACED
MSA-DCS | WA4032891 | Jasper, C Wing Living- Bottom sash window cracked | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-12 13:00:00 | Fail | WINDOW REGLAZED & SEC FILM APPLIED
MSA-DCS | WA4032895 | Jasper, C Wing Living- Large glass panel cracked approx 1200x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 15:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA4032915 | Kitchen- Left hand prover not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 09:27:17 | 2021-02-27 10:00:00 | Fail | Kitchen -left hand prover not working. Check prover & controls. Found water supply turned off. Ball float had been melted by element, no water. Replace ball float. All working.
MSA-DCS | WA4032919 | Kitchen- Bin room hose is damaged | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 09:00:00 | Pass | Kitchen bin room hose is damaged. Check hose, order new gun. Return new gun to site.
MSA-DCS | WA4032930 | Printing Area - Light broken (light planel might have blown) | Walcott Centre (Central West Metro ) | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-24 11:15:00 | Pass | Replaced failed lamps in printing area after sourcing parts.
MSA-DCS | WA4032971 | center wide cell call go through cannot but cannot hear audio | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 13:55:36 | 2021-02-23 13:22:00 | Pass | Attended site and repaired faults with central cell call system.Tested ok
MSA-DCS | WA4032985 | 100mm gate valve on mainline. Handle sheaered off- unable to be opened | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-16 10:00:00 | Fail | REPLACED BROKEN BRASS GATE VALVE
MSA-DCS | WA4032987 | Case Planning- Air Con not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-17 16:03:00 | Fail | Complete
MSA-DCS | WA4033005 | Equipment room 1 - air con leaking | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 09:18:00 | Pass | Cleared blocked drain,cleaned and flushed with water,all flowing ok.
MSA-DCS | WA4033008 | NVR2 RAD fail | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 13:15:00 | Pass | Attended siteLogged into NVR2 ServerInvestigated raid failure issuesFound multiple errors in event viewer reporting hardware diagnosis report assumes raid failure as well as fan failure, Checked services and found 5 services stoppedRestarted services and logged into server administrator to check raid controllerConfirmed all raid controllers operational no failures reportedChecked event viewer logs, both raid failure and fan failure reporting returned to normalDiagnosed server administrator services crashed causing false alerts with raid failure and fan failure reportingAll services are now working, advised site of the outcomeLeft site
MSA-DCS | WA4033018 | Sterile Zone - weed pulling | Bandyup Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | AFD Contracting | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 11:30:00 | Pass | 24/02/21Remove weeds and trees from sterile zone (area 1 and 2)25/02/21Inspect finished works. Remove waste to tip.
MSA-DCS | WA4033034 | Reset Building (outside prison) - staff toilet blocked and overflowing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 14:52:27 | 2021-02-23 14:00:00 | Pass | Cleared blockage
MSA-DCS | WA4033049 | control room all monitors all lagging | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 15:07:23 | 2021-02-23 15:00:00 | Pass | Fault investigated uncleared alarms found on system cleared test of CCTV system including camera playback/live tested ok.
MSA-DCS | WA4033057 | EC8 Powerfence C2 not responding. Controller has failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 08:00:00 | Pass | Replaced PowerFence Controller C2 in EC8. Parts Used: F32 Controller.
MSA-DCS | WA4033069 | PA speakers in recreation basketball courts not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 09:00:00 | Pass | Reset Austco Network Controller. PA system in Basketball Courts resumed normal functionality
MSA-DCS | WA4033077 | Reed switch missing unit 2 house 4 | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 10:00:00 | Pass | Glued in magnet in door in unit 2 House 4
MSA-DCS | WA4033080 | PA speakers unit 4 textiles area not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 12:00:00 | Pass | Had to reset All nodes from main server. Cleared all faults. Textiles area PA back online
MSA-DCS | WA4033114 | Various lights out, one bulb to be removed, see list below | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 14:00:00 | Pass | Replaced be repaired lights across site
MSA-DCS | WA4033181 | Unit 1, office rear door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 11:00:00 | Pass | Attended site, serviced lock and adjusted strike so door shuts properly.Date on site: 25/2/2021Time on site: 10:45am - 11:00am
MSA-DCS | WA4033206 | Unit 8, Cell D2- Toilet low pressure not flushing properly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-08 10:30:00 | Fail | Rerun flush pipe replaced bellow and inlet valve
MSA-DCS | WA4033224 | Unit 8 A3 Toilet cistern faulty needs Urgent attention | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 13:11:08 | 2021-02-24 09:09:00 | Pass | Replace inlet valve and bellows
MSA-DCS | WA4033249 | Unit 2, Cell B8- Toilet Pan Flush Pipe Seal Leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-11 14:59:00 | Fail | Remove pan, replace leaking kee seal and reinstall toilet
MSA-DCS | WA4033261 | electrical room - Fire Panel Alarm Fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 14:01:07 | 2021-02-24 08:52:00 | Pass | 24/2/21 MBUnit 1 Vesda in Plant Room in Zone fault due to too many scans in a week. Alert threshold still at factory setting, raised threshold by approx 10% and reset Vesda. No further faults occurred whilst on site.Unit 2 Vesda fault on Wing C/D cells 11/12. Found low airflow on pipes 2, 3 and 4 due to build up of dust on sampling point grills. Cleaned sampling points and vacuumed out pipework and returned airflow to normal levels. Reset Vesda and left in normal working order.
MSA-DCS | WA4033294 | Unit 1, Cell B1- Repaired damaged door frame | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 15:30:00 | Pass | carried out repairs to cell doors that are jamming, welded hinges to frame to stop doors dropping.
MSA-DCS | WA4033330 | Unit 2, Cell B14- Rubber Flooring Lifting & Jamming Cell Door | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-08 08:00:00 | Fail | DAMAGED FLOORING SECTION REMOVED , FLOOR PREPARED & NEW FLOORING LAID
MSA-DCS | WA4033338 | perimiter top and bottom pins are taking multiple attemps on not at all to engage | Albany Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-24 13:30:00 | Fail | 24/03/21Repair.Note - no accommodation, travel, meals, vehicles, plant & equipment charged as already on site for other works.
MSA-DFES | WA4032981 | Unable to activate the alarm, showing fault 02 roller door | VFRS Mundaring | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 14:50:00 | Pass | 23/02/2021, 1420-1450Replaced roller reed it had gotten squished
MSA-DFES | WA4033233 | entrance gate - faulty not working | CFRS Murdoch | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 18:00:00 | Pass | Complete
MSA-DFES | WA4033349 | Bunker Excon Room (AHIIMS Room) - Exit Sign is too big and and preventing door from being closed | DFES Regional Office - Belmont | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 14:00:00 | Pass | Continued on site at 11:00 to fix emergency exit light in bunker as door is hitting it. Left site at 11:30 to pick up blade fitting to replace eco light.Returned to site at 12:04 replaced fitting tested and signed out at 14:05.
MSA-DTAG | WA4032790 | Plant room 8 circuit keeps tripping when lights are turned on | Supreme Court | WSM-BR-SITE | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 13:30:00 | Pass | Inspected lighting and found faulty ballasts tripping lights - replaced and tested working
MSA-DTAG | WA4032796 | L3 court 35 Hole in floorboard beneath the JSO bench | Central Law Courts | GMP-BR-HO | Flooring | Timber (FL) | Midolo Building Services | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-08 08:15:00 | Fail | HOLE COVERED AND SECURED TO PREVENT MOVEMENT WHEN CHAIR ROLLING OVER TOP
MSA-DTAG | WA4032964 | Ground, Staff Entry - Door to the registry’s entrance not closing freely | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-05 09:30:00 | Fail | HINGES & CLOSER ADJUSTED - NOW OPERATIONAL
MSA-DTAG | WA4032972 | Court 2 door from Magistrates Chambers cannot open or close freely.- see below notes | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-04-07 09:00:00 | Fail | adjusted door closer and latch
MSA-DTAG | WA4032978 | L31 Director Generals Office swipe access does not lock the door when closed | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-05 13:00:00 | Fail | Director General door issue, changed programming shunt timing on door properties, re-tested multiple times. All re-configured and tested ok. Job complete
MSA-DTAG | WA4032983 | desks in hearing and mediation rooms duress alarm buttons not working - see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 14:05:44 | 2021-03-05 11:30:00 | Fail | Reattended site and retested all duress alarms related to previous issue, all has been tested and confirmed correct operation. Job complete
MSA-DTAG | WA4032994 | Court 35 judicial door in session button not working | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-03-05 15:01:00 | Fail | Attended site and checked court 35, reset macros and tested in session buttons, all In session buttons activating and resetting ok. Job complete.
MSA-DTAG | WA4033000 | Lvl 22- OPA Kitchen Door- Swipe Access Control consistently locked. No card working | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-08 10:30:00 | Fail | Work performed by Ken Moore 08/03/2021:Attended site, investigated issue. Work to be completed under Work Order WA4033643.Please note: There is no charge for this as work has been completed under another work order.
MSA-DTAG | WA4033090 | Custody, Cell 1 waste drain is blocked (attend at 07.30am Wed 24th Feb) | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-24 08:46:00 | Pass | COMPLETED
MSA-DTAG | WA4033094 | Custody, Cell 1 water fountain is not dispensing any water (attend at 07.30am Wed 24th Feb) | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-24 08:15:00 | Pass | Replaced solenoid and Ball valve conetite tested . All working as should.
MSA-DTAG | WA4033244 | level 4, GCIP - A/C temperature above work stations is very cold | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-23 16:00:00 | Pass | Attend site. Investigate air conditioning too cold on level 4. Access level 4 and check temps. Found room temp to be 23 degrees. Check calibration of temps sensors, ok. Access level 6 BMS and check operation of vav boxes serving area, found to be ok. Return to level 4 and talk with staff effected and found issue to be possible draft from oulets. Access outlets and deflector blades to be fully open causing air to exit straight down. Adjust blades to change direction. Relocate one outlet to opposite side of light to stop air drafting down wall. Found drafts to now stop and staff are happy with temperature.
MSA-DTAG | WA4033270 | Lvl 5, Toilet opposite Court 55 is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 09:30:00 | Pass | COMPLETED
MSA-DTAG | WA4033278 | Staff Kitchen - Pump under sink is blocked/leaking – foul smell emanating | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 17:32:00 | Pass | Jet washed saniflo. Unit not working properly due to built up grease in the unit. Cupboard has water damage. Kitchen must be professionally cleaned asap.
MSA-DTAG | WA4033307 | Side rear of court house wall - graffiti. Graffitti located near emergency exit door off cycle path | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 18:00:00 | Pass | Remove Graffiti
MSA-DTWD | WA4032769 | T block right hand side lift not working indicating out of order | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 23 Feb 2021 | 2021-02-23 11:45:27 | 2021-02-23 14:49:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA4032799 | tower block, Level 2 - blocked kitchen & toilet sink | West One Services | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-25 10:15:00 | Fail | Arrived on site and inspected found the kitchen sink, male, female and cleaners sink blocked. Used mini drain machine to clear the blockage and also found the boss junction is rusted blocking the line and leaking. Cleared the blockage at the boss junction. Applied sealant around box junction. We will come back tomorrow to check. Checked the boss junction still leaking. Need to change the boss junction. Discussed with facilities to plan the job on 25/2/21. Collected parts from supplier and returned to the site. Removed the faulty boss junction and replaced with new boss junction. Applied sealant around boss junction.
MSA-DTWD | WA4032800 | Foyer entry fire panel reporting fault to security monitoring | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-03 15:00:00 | Pass | Attended site - investigated fault. Works to rectify have been approved through another DAS. No further action required for this call out.
MSA-DTWD | WA4032903 | A Block, 2nd floor, Room A237 - Faulty aircon switch | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 11:30:00 | Pass | Attended site signed in and imvestigated room a237 wall sensor/switch found to have broken push botton request, picked up new part reattended site and replaced, tsted and left operational
MSA-DTWD | WA4032936 | D Block, Plant Room- Repair dosing line to Block Water Treatment | East Perth Campus | GMP-BR | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-04-28 10:56:00 | Fail | Watercon employee attended site 28.04.2021 - Fixed blockage on dosing pump system.
MSA-DTWD | WA4033028 | L2 B200 Blinds fallen down repair as required | Perth Campus B6 | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-04-21 10:50:00 | Fail | completed & Invoiced
MSA-DTWD | WA4033091 | Level 1, Chalk and cheese cafe - Replace/repair broken tap water | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 12:45:00 | Pass | Broken tap replaced
MSA-DTWD | WA4033093 | D Block, D001.2 - Male staff cistern faulty | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-02 15:15:00 | Fail | Repaired leaking cistern
MSA-DTWD | WA4033097 | Q block, Q0101 & Q012 - door frames coming away from wall | Joondalup McLarty Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-23 15:30:00 | Pass | Works provisionally complete pending upload of trade notes, CSS, JSA, to be updated with such information ASAP.
MSA-DTWD | WA4033105 | Kendrew- E-Block restaurant ice machine not producing ice | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Ice machine (RE) | Precise Air Group | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-24 14:00:00 | Fail | Collect parts from office. Attend site. Sign in and complete permits etc. Locate ice machine. Isolate and remove faulty components and replace with new. Fill system and clean/flush. Job complete.
MSA-DTWD | WA4033132 | Lvl 3, Male Toilet- Toilet not flushing properly | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 13:00:00 | Pass | Fix toilet issues
MSA-DTWD | WA4033153 | B block, B2308 - several cabinet doors are dropping due to faulty hinges | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-23 16:00:00 | Pass | Remove six worn out cabinet door hinges and replace with new. And repair broken rubbish bin door by removing old piano hinges and replacing with door hinges , to allow door to open sideways rather than in a downward motion
MSA-DTWD | WA4033201 | U Block, U022 - Multiple Air cons not working | Balga Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Precise Air Group | 1 | COMPFIN | 23 Feb 2021 | 2021-02-24 17:00:00 | 2022-09-09 13:30:00 | Fail | Met subcontractor on site set up all safety gear to get onto roof assisted changing both bearings on evap cooler fan replaced and checked operation all running efficiently
MSA-DTWD | WA4033235 | Level 3 vinyl next to male toilets - broken vinyl flooring | Perth Campus B6 | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-03 11:15:00 | Pass | Repairs to vinyl flooring on level 3 next to male toilets.
MSA-DTWD | WA4033237 | T Block, Western, end adjacent to roller door - Workshop wall mounted fan not operating; | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-24 14:30:00 | Pass | Attended site and signed in. Located fan on wall not working. Disconnect and removed old fan. Supply and replace with new fan. Connected and tested all okay. Signed out. Job complete
MSA-DTWD | WA4033246 | A-Block 1st Floor Ladies toilets A122 tap running | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 10:15:00 | Pass | COMPLETED
MSA-DTWD | WA4033252 | E Block, SK2- 3rd sink on right hand side blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-24 10:54:00 | Pass | COMPLETED
MSA-DTWD | WA4033254 | L block lift Doors on lift not opening - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-24 13:14:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA4033260 | T Block, G Floor- external keys are broken | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 08:15:00 | Pass | job completed - keys replaced
MSA-DTWD | WA4033273 | C block caferia ants nest on the lawn area outside | Bentley Campus | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 06:45:00 | Pass | Ant activity to C block lawn sections, application of chemical residual spray to external perimeter of lawn , all hardsurfaces live activity and around trees , Granules used to lawn sections, around visible nests.
MSA-DTWD | WA4033288 | Staff Room Kitchen- Tap leaking | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 23 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 14:30:00 | Pass | Fix tap
MSA-DTWD | WA4033302 | Front auto door will not open | Kwinana Automotive Centre | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 08:15:00 | Pass | Front auto door not working, has no power. Found wires had been pulled out by sliding door, connected wires but still not working. Need Dorma techs to look at door
MSA-DTWD | WA4033337 | T block stores - Replace/repair 3 faulty batten fluro fittings with LED; | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-24 15:30:00 | Pass | Attended site and signed in. Located faulty lights in store room. Supply and replace with new led battens. Tested all okay. Signed out job complete
MSA-DTWD | WA4033354 | B Block, Room B162- Lighting not working, repair as required | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 11:50:00 | Pass | Repalced faulty fluros and control gear to various areas block 6
MSA-MRWA | WA4032761 | Fluorescent light fitting nor working, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 12:32:00 | Pass | Repalced faulty ballast, cable and tubes starters.job complete
MSA-MRWA | WA4033283 | air con not running, no power at switch | Materials Engineering Branch-Concrete Workshop-Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Feb 2021 | 2021-02-24 17:00:00 | 2021-02-24 08:30:00 | Pass | Ac operational
MSA-DCA | WA4033841 | AHU2 leaking water | Shipwreck Galleries-Main Building-Level 1-Dutch Wreck Gallery | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-24 17:30:00 | Pass | Attended site. FCU2A leaking water. Applied tests and checks to find ondensate pump to have failed. Investigation found electrical pump safety connection broken. Removed and replaced broken connection. Cleaned up spill water inside FCU with wet dry vacuum. Reinstated system and tested condensate pump operation. System operating correctly.
MSA-DCA | WA4034313 | toilet seal on system leaking | State Library of WA-Main Building-Level 1-Disable and Male Toilet - In Open Study Area | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 24 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-04 12:45:00 | Fail | Replaced pan and toilet washer, keyseal replaced and reinstalled toilet.Recommend toilet to be professionally cleaned,Bathroom can not be used for 24 hours
MSA-DCS | WA4033536 | Unit 3 - C7 Officer's lock (Key 1) is hard to lock and unlock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 07:19:18 | 2021-02-25 12:00:00 | Fail | Replace hinges, personal lock and adjust strike.Replace weld on strike plate.
MSA-DCS | WA4033564 | admin office air con inbalanced | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 08:04:36 | 2021-03-03 11:00:00 | Fail | COMPLETED
MSA-DCS | WA4033565 | Turner A06 shower & basin not working (flowmatic PB-2) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-04 08:35:00 | Fail | Requires a new control box
MSA-DCS | WA4033568 | Unit 2, Cell 41 (obs) Cell call system not working | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 08:20:10 | 2021-03-25 10:20:00 | Fail | Reset node tested cell call tested all ok
MSA-DCS | WA4033571 | Door in gate house, lobby to entry door - when secured showing green not red | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-05-14 12:30:00 | Fail | Investigated issue reportedUnable to fault issue reportedAdvised the site and the site has confirmed the issue appears to now be resolvedNo further work required
MSA-DCS | WA4033579 | Social Visits, Spine Entrance Door- Door Lock Cartridge Intermittently, Jamming Open | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-24 11:50:00 | Pass | Attend site. Adjusted alignment of lock and strike plate. Lock body was also serviced.
MSA-DCS | WA4033627 | Kitchen, fridge - Sliding Door Stops Broken | Melaleuca Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 09:22:04 | 2021-03-17 09:00:00 | Fail | Completed , tested and is now working good
MSA-DCS | WA4033656 | unit 16 D10 shower drain blocked pooling and slow to drain away | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-08 14:30:00 | Fail | Nill
MSA-DCS | WA4033657 | Unit 14, Cell A12- shower leaking and basin has low pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-09 13:30:00 | Fail | Nill
MSA-DCS | WA4033671 | unit 2 exhaust system EF2 failed - WAMS on site | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-24 16:00:00 | Pass | Whilst conducting maintenance in unit 2 found EF 2 not running.Raised job through Maintenance department as this is an essential fan.Checked over controls and began fault finding procedures.VSD flashing fault with no active faults.Checked through out mechanical controls system and found fused contactor for EF 2A start up.Rewired for temporary fix to force other fan to start.This job and other in same mech board will have a DAS repair submitted for all contactors to be updated and tested.
MSA-DCS | WA4033708 | Farm- Water Chiller not working | Wooroloo Prison Farm | WSM-BR-SITE | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 10:34:44 | 2021-02-24 16:30:00 | Pass | COMPLETED
MSA-DCS | WA4033736 | Karakin, Cell A08- Shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 11:30:00 | Pass | Replaced control box
MSA-DCS | WA4033743 | Abattior 3 phase power cable perished | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-02-25 10:00:00 | Pass | Investigate and replace damaged 3 Phase cable at abattoir.
MSA-DCS | WA4033745 | Gardens lettuce shed fan power cable broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-02-25 13:00:00 | Pass | Investigate and repair gardens lettuce shed faulty cable
MSA-DCS | WA4033749 | Unit 2 lower landing exhaust fans timers not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 13:00:00 | Pass | Investigate and repair Unit 2 Lower landing exhaust fan timers
MSA-DCS | WA4033753 | Unit 1 tap at rear door to office broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-02-25 13:30:00 | Pass | Replaced wall socket and hosetap to repair
MSA-DCS | WA4033821 | Unit 2 top landing showers roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-04-08 11:00:00 | Fail | RIDGE CAPPING REPAIRS MADE & EXCESS LEAVES CLEANED OFF ROOF
MSA-DCS | WA4033833 | Waterproof power point over in external transport has been badly damage & tripped circuit | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 09:00:00 | Pass | Picked up replacement parts and replaced and tested in external transport
MSA-DCS | WA4033879 | Unit 5 B5 Cell B05 Lock is inoperative Main lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 24 Feb 2021 | 2021-02-24 17:12:28 | 2021-02-25 12:35:00 | Fail | Attend site. Bolt had to be cut for door to open. Return to workshop to refurbish lock. Return back to site to instal.
MSA-DCS | WA4033899 | reception Toilet between Cell 1 and staff kitchen not flushing needs repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 13:41:21 | 2021-02-25 09:25:00 | Pass | Replaced water wafer flushing buttons and bellows to toilet system
MSA-DCS | WA4033902 | Stores - The External Stores stationery roller door is malfunctioning again. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | UNIVERSAL DOORS | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 14:10:00 | Pass | Job completed - Repairs to two roller doors
MSA-DCS | WA4033911 | Reception, Induction area- Light above Induction desk, faulty needs repair. (WILL NEED 12ft LADDER) | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-05 13:30:00 | Fail | Repaired lights
MSA-DCS | WA4033912 | Canteen - air conditioner cant adjust the speed on the cont | Casuarina Prison | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 12:43:19 | Pass | Arrived on site and signed in tools,checked over aircon,found thermostat hanging off wall,checked to make sure sensor cables secure and refitted sensor,checked over operation all amp draws and pressures ok,coils clear.
MSA-DCS | WA4033938 | INF (10) - Node 11 showing many open circuits, system isolated | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 24 Feb 2021 | 2021-02-24 18:13:33 | 2021-04-20 08:17:00 | Fail | 25/2/20 GAChecked status of detectors whilst onsite found total of 5 x missing detectors in new medical centre and 1 x dirty detector will require investigation with 2 x techs injunction with other missing faults on other nodes8/3/21 MB CSFaults appear to be mainly within the temporary med centre demountable. Unable to gain access as building is currently unused. VSO/escort officer to arrange key access for tomorrow morning.9/3/21 MB CSReplaced faulty detector in Med centre prisoner waiting room 2 M-16-176Checked and re-enabled pressure switch in sprinkler valve room, all ok.5 x Detectors at addresses M1-139, 139, 117, 118 and 124 have removed from system by others and require deleting from config, will need to engage Johnson Controls (Sean Scudds) to carry out.13.04.2021 - nothing further heard from client - close out works and invoice for time on site
MSA-DCS | WA4033942 | Industries Admin- Node 3 showing open circuits | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-04-13 09:18:00 | Fail | Attended site no escort available checked graphics found multiple missing detector faults in generator room x 11 l. Recovery area has 4 xmissing faults on relays for mcp, fsw and monitor valve + recovery maint bell relay missing aswell. Will require 2 x techs for 2 days injunctionwith other missing faults on other nodes to rectify.5/3/21 MB CSInvestigate open circuit and missing sensor faults.Cabling fault appears to be underground between recreation block and recovery/generator blocks.6/3/21 MB CSAttempted to trace underground cabling and snake new cables through existing conduits. Unable to install cables due length of runs and lackof access pits and lack of information about in ground cable runs.More information and drawings will be required from Prisons/Programmed about in ground services to be able to rectify.13.04.2021 - nothing further heard from client - close out works and invoice for time on site
MSA-DCS | WA4033944 | Recreation Area- Node 12 showing open circuits | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-08 09:07:00 | Fail | Attended site unable to investigate as would of required a escort to take me to multiple areas which prison could not provide. Checkedgraphics and found the following missing faults - visits area has 4 x detectors missing will require further investigation.8/3/21 MB CSNo faults showing on system for recreation area at present, but faults may have been due to damaged underground cable between recreationand recovery/generator building.
MSA-DCS | WA4033953 | Unit 1 A11 sink loose on the wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 14:23:45 | 2021-02-25 10:15:00 | Pass | job completed on another work order
MSA-DCS | WA4033954 | A4- Microwave outer constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 16:16:00 | Pass | Attended site and repaired multiple perimeter faults.
MSA-DCS | WA4033955 | E1- mircowave outer constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 10:34:00 | Pass | Attended site and repaired multiple perimeter faults.
MSA-DCS | WA4033956 | unit 5 upstairs kitchen Double door fridge not cooling | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 14:30:01 | 2021-04-12 14:00:00 | Fail | Repaired by sub contractor.
MSA-DCS | WA4033958 | Unit 1, Cell B11- Main lock faulty | Hakea Prison | SPA-BR | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 14:25:18 | 2021-03-17 16:30:00 | Fail | On site, inspect faulty main lock on door. Like requires to be refurbished. Re-attend site to install refurbished lock. Tested, all operational. Suggested that the door be replaced due to poor condition. Job quoted and placed on hold. Quote was approved and new door manufactured. Re-attend site to install new door.
MSA-DCS | WA4033968 | Unit 13 - Day Room - The tumbler in the door lock has come loose | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 14:41:49 | 2021-02-25 09:45:00 | Pass | tighten cam screws and lubricate lock
MSA-DCS | WA4033972 | Unit 13, A4 - Cold tap in cell A4 does not operate due to being seized up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-03 10:30:00 | Pass | Nill
MSA-DCS | WA4033975 | Unit 13 - Wooden entry door inside the A/C laundry has got broken hinges and is hanging off | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 14:59:10 | 2021-02-25 10:00:00 | Pass | DOOR RE HUNG
MSA-DCS | WA4033978 | Kitchen and Manager Office- Lights & Light Switch not working, see notes below | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-10 15:00:00 | Fail | Relocated managers office lights to kitchen and installed dimible lights and dimmer in managers office
MSA-DCS | WA4034036 | Perimeter Zones 18- 21 are offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 16:38:15 | 2021-07-16 19:30:00 | Fail | Confirmed system is operational and parts replenished.
MSA-DFES | WA4033592 | SO dorm, office 7/14 black ants in office and front ensuite | CFRS Joondalup | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 13:30:00 | Pass | Carried out requested treatment for ants to SO dorm, ensuite and office area. Applied ant gel bait internally and also sprayed abutting external perimeter areas, using a residual insecticide.
MSA-DFES | WA4033623 | Hydrant in Back yard - Station Hydrant isn’t working in back yard now | VFRS Kwinana | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 15:45:00 | Pass | Main water valve at the boundary had been turned off hence no water. Turned back on and water flowing checked all correct.
MSA-DFES | WA4033681 | in the kitchen north wall tap fault- contractor on site | CFRS Vincent | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 12:46:00 | Pass | Replacing sink mixer tap
MSA-DFES | WA4033737 | Main front door- lock is fauly | O'Connor Fleet Storage | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 15:45:00 | Pass | Service, repair & test lock
MSA-DFES | WA4033785 | fluro lights in the evacuation passageway between the admin block & the main workshop is faulty | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 11:15:00 | Pass | Located light. Replaced fluorescent tube and starter. All working
MSA-DFES | WA4033909 | Downstairs - toilet/shower, bad smell coming from room. | CFRS Fremantle | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 09:15:00 | Pass | Clearing smelly drains, unblocked the toilet
MSA-DFES | WA4033933 | Front house - lighting circuit breaker switching to off position = no light in container | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-02-25 11:00:00 | Pass | Attended site and signed in. Investigated lighting fault. Found electronic ballast to faulty as well as the tubes, replaced and tested. All ok.
MSA-DFES | WA4033969 | Fire Station Building and surrounds- Pest Control spraying required as the below | CFRS Hope Valley | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 15:00:00 | Pass | Carried out treatments to control spiders, ants, mosquitos and flies - ULV application of repellant residual spray to engine room and all external walls, roofing, under furniture, bins etc. To all vegetation in surrounding garden beds, around drains and soak wells. Non- repellant residual spray to high level ant activity (coastal brown) and entries to nests in paved areas and granular bait targeting same in lawns.
MSA-DFES | WA4033997 | Soakwell immediately behind the engine room is full of sand and overflows easily | CFRS Hope Valley | GMP-BR | Waste Management | Waste Removal (WM) | Western Resource Recovery Pty Ltd | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-04-14 12:27:00 | Fail | Completed 14/04/2021
MSA-DTAG | WA4033612 | all floors - in session button faulty . | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-05 11:00:00 | Fail | In session buttons fault identified to controller firmware server, SQL, and resource limitations, adjusted and mitigated issue for future operations. Job complete
MSA-DTAG | WA4033629 | Lvl 3 - Green door light for staff exit/entry in room 3.08 is not working | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-09 13:30:00 | Fail | Checked and reset door controller, rechecked and retested and all tested ok. Job complete
MSA-DTAG | WA4033635 | Basement - Due to a leak in pump under sink, staff kitchen requires full clean/deodrise | Supreme Court | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 20:00:00 | Fail | Job completed as per PO
MSA-DTAG | WA4033643 | L22 room 22.01 & 22.18 door not working staff getting stuck in kitchen after swiping - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-16 11:00:00 | Fail | both doors working correctly
MSA-DTAG | WA4033675 | C lift camera not working - see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-03-09 14:00:00 | Fail | Reset camera settings and reprogrammed recording schedules and and retested. All functions and recordings working ok. Job complete
MSA-DTAG | WA4033989 | Lvl 8, Meeting rooms 1, 2 & 3- No power to GPO's | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-25 10:30:00 | Pass | Job complete
MSA-DTWD | WA4033527 | West block L1 W100 air con faulty | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 24 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 14:00:00 | Pass | Accessed site completed relevant sign in procedures and covid safe app wa requirements, gained access to room W101 , unit showing indoor - outdoor comms fault , rectified fault , checked over electrical components, all ok , test ran unit , supply air @ 9dgr , all ok
MSA-DTWD | WA4033550 | B6 door access ramp faulty High usage area. Contractor sign in area. | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 24 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 11:30:00 | Pass | Arrived on site and signed I on ipad. Spoke with Peter who showed me around the jobs that where on on run sheet. I inspected the double doors that were hitting against the metal ramp and the door. I placed some bollards outside the work area and removed the ramp. Most of the screws snapped when trying to remove them. I chipped away the high bricks allowing the ramp to site lower then drilled and screwed the ramp back into place. I then cleaned the work area and filled out the signature slip to get signed to complete the job.
MSA-DTWD | WA4033566 | F Block wash trough & floor drain is backing up. | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-03 16:30:00 | Fail | Used small drain machine to clear blockage
MSA-DTWD | WA4033567 | front auto door motor faulty | Kwinana Automotive Centre | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 12:39:00 | Pass | On arrival found motor loom was disconnected from the controller, connected back motor loom to the controller, inspected door and found after push buttons was not working and PIB board was heavily corroded, found push button connection was loose, reconnected push buttons to the mode board and replaced 1x PIB board, checked all fixings, tested door operation a number of times, all working fine.
MSA-DTWD | WA4033586 | A block L3 A309-A331 lights faulty Lab Operations | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 15:00:00 | Pass | Inspected lights in classroom, need to return to complete
MSA-DTWD | WA4033608 | F-Shed - Yellagonga - the Rheem hot water unit does not dispense water | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-24 11:00:00 | Pass | Cleared internal calcium blockage. Removed twin filteration system and installed a maxiflow scale system.
MSA-DTWD | WA4033631 | A Block, Room A232 - Set up tempoary air cons | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-04-05 10:32:00 | Fail | Attended site to carry out the replacement of existing under ceiling split systemwith new9.5 kw fujitsu reverse cycle wall split system
MSA-DTWD | WA4033640 | E Block, E300 Automotive- evap air conditioner is running but not cooling and was dumping water yest | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 08:58:00 | Pass | Found sump dump faulty requires replacement. 24.2.2125.2.21 purchased and replaced sump dump valve and solenoid. Test. Ok.
MSA-DTWD | WA4033703 | Block 1, Male toilet- Button on wall sticking - water running continuously | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 19:30:00 | Pass | replaced cistern and button
MSA-DTWD | WA4033712 | House 4 laundry Faulty washing machine taps | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 13:00:00 | Pass | Repairs to washing machine
MSA-DTWD | WA4033786 | Outside B1 office Brick paving has subsided adjacent to walk way creating a trip hazard | Murdoch Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-04 11:00:00 | Pass | Work completed
MSA-DTWD | WA4033814 | L3 East Exhaust fan male toilets fan faulty | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-09 17:13:00 | Fail | Returned to site with new drive belts for TEAF system. Completed required paperwork and gained access to fan on roof. Replaced and tensioned belts. Confimed operation. Simon assisted as second tech for working at hight.
MSA-DTWD | WA4033830 | S Block, Exterior Door near S109- Door closer faulty as door slamming | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 11:15:00 | Pass | Attend site sign in , locate door in question and need door close was required, left site to collect materials and return to install . Set up safety barriers as area is well used by staff and students. Install closer and test all working as should . Fill out all forms and sign out
MSA-DTWD | WA4033896 | West Block, Level 1, W119 - Rehang Blind fallen down W119 | Mount Lawley Campus | GMP-BR | Building | Curtains & Blinds (BU) | AWB Co. | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-04 12:00:00 | Pass | repair blind to W121 and W119
MSA-DTWD | WA4033906 | F block passageway near room F12 Replace 2 x 2’ faulty batten flouro fittings with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 08:45:00 | Pass | Attended site and signed in. Located hallway at F12. 2 x lights broken. Supply and replace with new led fittings. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4033935 | Block J & K Faulty / Damaged Lids & surrounds - see notes | Murdoch Campus | GMP-BR | Building | Foundations (BU) | AWB Co. | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-04-01 15:45:00 | Fail | Got parts delivered. Installed last pit. Job complete
MSA-DTWD | WA4033939 | outside of building, retic cover box rusted - please Brian with any queries | Jandakot Campus - Annex | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 24 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-19 14:15:00 | Fail | Attended site and signed in. Spoke with staff regarding replacing box. All good to do so. Disconnected and removed gpo and retic controller in cabinet. Controller is very brittle and fallen to pieces as we unscrewed it. Advised facilities to replace. Installed new cabinet. Installed gpo in box. Temporary mounted retic controller in cabinet. Left isolated due to controller stuck on. Box is all okay. Signed out. Job complete
MSA-DTWD | WA4033976 | Jan Rose - Faulty Fluro light Tombstones | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 16:00:00 | Pass | job completed - replace tombstones
MSA-DTWD | WA4033984 | A Block, AT10- Multiple fluro’s in same room not working | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-04 14:00:00 | Fail | Job complete
MSA-DTWD | WA4033993 | B Block, Room B154- Split system not working | Perth Campus B6 | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 24 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-25 10:00:00 | Pass | ATTENDED SITE GAINED ACCESS AND LOCATED ROOM. CARRIED OUT INSPECTION OF A/C. NOTE A/C HAS REACHED THE END OF LIFE CYCLE AND CAN NO LONGER BE REPAIRED. R22 UNIT QUOTED FOR UPGRADE. QUOTE SENT TONPFM FACILITIE MANAGER ERIC. NOTEROOM IS B112
MSA-DTWD | WA4034035 | E Block, E74 & E75- Blowen phase on VSD units. | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-26 14:00:00 | Fail | Sub contractor attended site and fitted new vsd on 26/02/21. job is complete
MSA-MRWA | WA4033700 | VAV11 not maintaining set point circa 6 deg above. Please investigate | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-820-Meeting Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 13:00:00 | Pass | Quote to be submitted for replacing water cooled package unit.
MSA-MRWA | WA4033752 | Cistern constantly running , please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor-A7.0-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Feb 2021 | 2021-02-25 17:00:00 | 2021-02-24 17:30:00 | Pass | Replaced outlet valve, if the issue occurs again please let us know.
MSA-DCA | WA4034306 | Ground floor, ladies toilet - broken hand dryer | His Majesty's Theatre-Theatre Building-Ground Floor-Female Toilet | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-19 09:30:00 | Fail | Replaced hand dryer in ground floor female toilet
MSA-DCA | WA4034308 | Female & male toilets - hand dyers will not turn off | His Majesty's Theatre-Theatre Building-Level 1-Dress Circle | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-19 14:00:00 | Fail | Replaced 4x hand dryers in level 1 male and female toilets.
MSA-DCA | WA4034548 | boiler 2 is in fault | Maritime Museum Victoria Quay-Robert Steele Marine Engineers Display-Ground Floor-Boiler Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 09:30:00 | Pass | Attended site. Boiler 2 in fault. Raised PO for Boilertronics to attend. Investigation found boiler to be faulting due to a low gas error. Please refer to Boilertronics attached service report for in depth repair works and reporting. Works completed.
MSA-DCA | WA4034551 | Chilled water pump 2 vibrating please investigate | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Mechanical Services | Pumps (MS) | Precise Air Group | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 15:00:00 | Pass | Attended site and accessed plantroom. Found CHW pump 2 to be running at 100% and bypass valve open at 52% due to system DP pressure. Due to pump running too fast it was causing the vibration and noise. Have notified BMS technician about problem. Packed up and left site.
MSA-DCA | WA4034589 | Air Con unit is rattling | His Majesty's Theatre-Theatre Building-Ground Floor-G24 - Dressing Room 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 15:08:00 | Pass | Notes AC is rattling from loose mounts and drain leaking fromspout on pan. Re mounting re mount fan and installedfitting to suit pan. All ok.
MSA-DCA | WA4034665 | chilled water pump 2 - running %100 causing vibration (BMS control issue) | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Refrigeration | Chiller (RE) | Building Automation & Electrical Services Pty Ltd | 0 | CLOSE | 25 Feb 2021 | 2021-02-25 17:50:00 | 2021-02-26 11:30:00 | Fail | 25-02-2021 — Arrived on site, Investigated CHWP2 reported speed control and water pressure issues. Carried out system testing on the water flow through the chiller. This testing identified noise in the VAV AHU valve when pumps were running at 100%speed. BMS was controlling pumps to run at that speed due to flow not being maintained through the chiller evap. The chiller EVAP setpoint was set to 45kPa.26-02-2021 — Requested by David De Villers (Programmed) to attend site as the noise in the pipes had returned. Met David and Precise onsite. Carried out water flow test and pump speed control testing. BMS was controlling the system correctly and fault lay within the mechanical system. Further investigation found that Chilled water pump-2 was shaking quite significantly on it mounts compared with chilled waterpump-1 when running at the same speed. The 'shaking' of the chwp-2 was causing cavitation in the pipe work that magnified down the pipe work.
MSA-DCS | WA4034160 | Library flyscreen door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 25 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-25 11:45:00 | Fail | Attended site, serviced fly screen door on library.Date on site: 25/2/2021Time on site: 11:15am - 11:45am
MSA-DCS | WA4034164 | Kitchen light fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 10:30:00 | Pass | Investigate and repair kitchen light
MSA-DCS | WA4034187 | entrance into gate house sliding door not working has to be open manually | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 0 | COMPFIN | 25 Feb 2021 | 2021-02-25 11:42:20 | 2021-02-25 11:00:00 | Pass | Attended site, viewed door and it requires an electrician to do.Work order to be closed out at $0 cost
MSA-DCS | WA4034190 | york tower cooling system - system 1 fault | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 07:30:59 | 2021-02-25 13:30:00 | Pass | Attended site inspected chiller and fond fault, Further investigation found breaker for system 1 compressor had tripped, reset and carried out test and adjusted accordingly. System running fine.
MSA-DCS | WA4034197 | class 4 smashed window approx 650x650 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 25 Feb 2021 | 2021-03-02 17:00:00 | 2021-04-06 11:30:00 | Fail | CLASS 4 WINDOW REGLAZED
MSA-DCS | WA4034201 | Education 1 art & craft smashed window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 25 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-03 16:00:00 | Fail | windows re glazed
MSA-DCS | WA4034206 | CCU 11 Cell D5. Has an apparent leak coming from the wall. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 08:01:12 | 2021-02-26 13:04:00 | Fail | Nill
MSA-DCS | WA4034209 | Unit 6, Regi oven on left - not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 08:05:14 | 2021-03-23 13:50:00 | Fail | Fan Noisy as reported, Found fan working ok. Noted some fat buildup in fan baffle. Likely the cause of the noise. Better cleaning required to prevent this. and replaced lower hinge which was bent , check door alignment ok.
MSA-DCS | WA4034211 | Health Administration - Office Fire Alarm is going off. Urgent | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 08:05:15 | 2021-02-25 09:49:00 | Pass | Attended site due to fire alarm beeping in health office found beeping was not due to fire system but due to a defib unit - advised client.
MSA-DCS | WA4034222 | unit 1 cell B31 taps leaking reseat and repace washers | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-25 09:00:00 | Fail | Pillar tap leaking. Reseated the tap, serviced the spindle and changed the tap washer. Still leaking. Need to replace the pillar tap Collected parts from supplier and returned to the site. Could not reMove the old tap from basin. Installed the new tap next to the old tap. Reconnected water and tested all working good.
MSA-DCS | WA4034224 | Unit 13, B5 - The light switch has come away from the wall and there are exposed wires. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 08:18:15 | 2021-02-25 11:30:00 | Pass | Replaced damaged lights switch in unit 13 b5
MSA-DCS | WA4034226 | unit 2 D10 vanity spindles leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-05-11 14:15:00 | Fail | Found the tap leaking. Need to order ceramic spindles. Ordered the spindle with supplier.
MSA-DCS | WA4034227 | unit 6 cell 12 shower spindles leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-09 15:30:00 | Fail | COMPLETED
MSA-DCS | WA4034233 | Unit 5, A20 - basin failing off wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 08:22:21 | 2021-02-25 11:45:00 | Pass | Secure and reseal basin to wall
MSA-DCS | WA4034234 | Unit 13 - B4 toilet is leaking around the base and there is a bad odour coming from the area. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-24 11:30:00 | Fail | Replaced broken/leaking toilet
MSA-DCS | WA4034237 | Unit 1, C wing shower - shower floor lifting | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 08:25:43 | 2021-03-20 17:31:00 | Fail | DAMAGED FLOORING UPLIFTED AND NEW VINYL LAID
MSA-DCS | WA4034238 | Gate house visits air con noisey | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-26 14:06:00 | Pass | Complete
MSA-DCS | WA4034244 | B wing yard door near kitchen - fly wire door handle broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 13:05:00 | Pass | Onsite. Replace broken lock on with new security door lock.
MSA-DCS | WA4034249 | INF (10) - Toilet cistern not filling. Obs cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 25 Feb 2021 | 2021-02-25 12:31:51 | 2021-02-25 08:39:00 | Pass | Nill
MSA-DCS | WA4034264 | Unit 5, C14 - Cold tap spindle damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-03 16:40:00 | Pass | Replaced anti vandle tap handle
MSA-DCS | WA4034312 | ** Job already attended too ** Unit 2A kitchen fridge not cooling | Wooroloo Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 10:03:00 | Pass | ARRIVED AT SITE LOCATED UNIT FOUND UNIT IN POOR CONDITION FURTHER INSPECTION FOUND THERMOSTAT FAULTY PICKED UP NEW THERMOSTAT INSTALLED RECOMMEND UNIT BE REPLACED DUE TO AGE AND CONDITION. BRAF REJECTED, CLOSE JOB
MSA-DCS | WA4034378 | Health, Corridor- Power point sparking | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 09:43:36 | 2021-02-25 12:00:00 | Pass | Replaced faulty power point and tested new one ok.
MSA-DCS | WA4034381 | Jeelia, Cell C1- personal lock from inside of cell damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 09:45:23 | 2021-02-25 10:55:00 | Pass | Attend site. Replaced broken spindle and spring. Check operation on lock and door.
MSA-DCS | WA4034382 | Recreation, Resident toilet- power point sparking | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-02-25 12:30:00 | Pass | Checked Staff and Resident toilets for gpos , none found . Consulted with staff and believe that fault may be at another site. Closed job off.
MSA-DCS | WA4034386 | Cabinet Shop-hot water urn not working - see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-16 08:45:00 | Fail | Unit not dispensing water. Unit had been replace by another unit. Client requested to take off site and repair. Drop back when next on site and they will use as spare. diagnosed and tested in workshop replaced solenoid reinstalled at site A40189438Q rheem bwu 16.3.21 - Unit redelivered to Casuarina. All Okay.
MSA-DCS | WA4034445 | Vesda system for B/D wing cells 13 & 14 Really noisy (falure imminnent) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-08 09:05:00 | Fail | 8/3/21 MB CSChecked Vesda in unit 13 B/D cells 13/14. All airflows are showing between 80 and 100% but fan speed is set at maximum and is starting tomake a whining noise. Unable to make any further adjustments as parameters and fan speed have been pushed out as far as they can go. Iffurther faults occur this unit will need to be replaced.Vesda in A/C cells 15/16 found to be in Fire 1 condition and had been isolated. Reset and check vesda, all now showing normal.
MSA-DCS | WA4034447 | Unit 17 Cell door C7 is not opening several keys have been tried in the door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 25 Feb 2021 | 2021-02-25 14:34:38 | 2021-02-25 11:45:00 | Pass | Open jammed cell, remove lock and service.
MSA-DCS | WA4034489 | Crisis Care unit - Air conditioner control not working SAFE CELLS are cold | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 10:59:41 | 2021-02-26 12:00:00 | Fail | Units operating correctly. Adjusted set point and monitored room. Guards confirmed room temp is ok.
MSA-DCS | WA4034492 | Visits - Camera No.18 not working needs repair | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 11:03:04 | 2021-02-26 11:00:00 | Pass | Cable and network switch port tested ok. Traced fault to the camera. Removed camera and bracket. Modified bracket for new camera. Installed and tested ok. Parts used:Indigo BX-420 from site critical spares
MSA-DCS | WA4034495 | Unit 5, computer room - aircon is leaking quite rapidly. Only been in use for 2 hours | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 14:28:29 | Pass | Checked over found drain blocked,cleared obstuction and flushed drip tray and drain.
MSA-DCS | WA4034507 | Controller is tripping out system when you manually run the system. | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 11:18:27 | 2021-05-26 10:45:00 | Fail | Attended site 26-2-2021 to check controller.Received approval of the BRAF 12-4-2021, replacement controller has been ordered.26-56-2021 Install new controller, reprogram and test for correct operation.
MSA-DCS | WA4034541 | Manual trades extraction fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-02 15:00:00 | Pass | Investigate and repair manual trades extraction fam
MSA-DCS | WA4034568 | Unit 14, Cell A2 - Shower screen leaking onto mattress | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-08 14:30:00 | Fail | SHOWER SCREEN RE SEALED
MSA-DCS | WA4034587 | control, internal zones 23 and 24 PX is constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 12:39:14 | 2021-02-26 08:30:00 | Pass | Recalibrate and fixed the fault on internal zones perimitrax, job completed.
MSA-DCS | WA4034611 | unit 3 CCU 1 hatch lock sticking key working in one direction not both | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-03 09:35:00 | Pass | Replaced Lock on Meal Hatch - Unit 3 (CCU) cell 1
MSA-DCS | WA4034616 | interview room 3 Door lock does not operate in the correct way. - see notes | Midland (North East Metro) | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-15 14:45:00 | Fail | Attended site, changed locking functions on all interview rooms, modified cams to suit. Handles are now locked at all times on outside and free on the inside at all times.Date on site: 15/03/2021Time on site: 12:00pm - 2:45pm
MSA-DCS | WA4034671 | Unit 4, Cell D12- Tap leaking & water coming into hallway | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-05 08:30:00 | Fail | Nill
MSA-DCS | WA4034675 | Unit 2, office- Air Con not working, contactor will not stay in | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 15:17:36 | Pass | Checked over found fire alarm tripped,reset and tested all ok.
MSA-DCS | WA4034686 | Assessments - Water dripping through ceiling onto kitchen floor small rear kitchen area | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 14:11:02 | 2021-02-26 10:00:00 | Pass | Found breach in drain connection. Fixed connection and tested flow. All ok
MSA-DCS | WA4034688 | Unit 4, A Wing- light at the end of corridor has come away from the ceiling with wires exposed. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 14:09:21 | 2021-02-26 12:00:00 | Pass | Investigate, repair and refit unit 4 a wing light. Emergency muster in effect through job.
MSA-DCS | WA4034691 | Laundry - Water leak from pipe work (ladder required) | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 14:14:01 | 2021-03-04 20:33:00 | Fail | Unable to find isolation valve and map drawings, unable to get approval to turn off water to facility. Returned at night the next day to turn off water main and repair corroded pipework
MSA-DCS | WA4034692 | Yeeda C wing unit has no hot water | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 14:15:55 | 2021-03-18 12:35:00 | Fail | Replaced faulty gas valve and flame rod
MSA-DCS | WA4034696 | Unit 2 b pod 3 - extraction fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-10 14:30:00 | Fail | Replaced rangehood
MSA-DCS | WA4034732 | Unit 3, Cell A7 does not have power most of the morning | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 15:03:17 | 2021-02-26 15:00:00 | Pass | Investigated and repaired power to unit 3 a7
MSA-DFES | WA4034181 | tunic room no lights in all 4 rooms - see notes | CFRS Hope Valley | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 13:00:00 | Pass | Completed Attended site and investigated faulty lights in the ba room. Found faulty ballast and rcd. Replaced and all in working order
MSA-DFES | WA4034348 | L1 urinals are blocked | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 12:00:00 | Pass | Unblocking the urinals
MSA-DFES | WA4034361 | L1 comunication center kitchen Hot/cold water tap not water | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 14:26:00 | Pass | Refitted filter pressure test all seems okay NO CHARGE TO CLIENT
MSA-DFES | WA4034410 | First floor, Disable toilet - toilet, shower, and sink all blocked | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-25 13:30:00 | Pass | Unblocking the drains
MSA-DFES | WA4034502 | Parts washer - Entry Card readers taking 3 to 4 swipes before opening | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-26 13:45:00 | Pass | 26/2/21 - Ryan VestyClient advised 3 doors having issues.Tested reception entry door, found lock releasing 1 second after card swipe. Found handle loose, advised client.Tested reception to workshop, and washroom entry doors, found both operating correctly.
MSA-DFES | WA4034556 | Gutters - Water is leaking into them from aircon and then the gutter is leaking - check for holes or | VFRS - Armadale | GMP-BR | Roofing | Roof Safety Systems (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-26 10:45:00 | Pass | Inspect roof above eave for signs of leaks , siliconed various cracked roof tiles below air conditioning unit and in surrounding areas
MSA-DFES | WA4034577 | workshop office light circuit has failed/faulted. No lights in offices | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 14:45:00 | Pass | Arrived on site at 14:00 to inspect office and kitchen lights. Found RCD tripped out but couldn’t fined any faulty fittings. Informed manager to try reset RCD before we are called out so then we know there will be a bad light on circuits. Signed out at 14:45.
MSA-DFES | WA4034581 | roof Evap aircon is leaking directly onto the roof and into the gutters | VFRS - Armadale | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-08 09:30:00 | Fail | Investigated water leak. Repaired leak
MSA-DFES | WA4034654 | Groud floor, Change room, Male toilets - toilet is broken, top half hanging | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 14:18:00 | Pass | Replacing toilet seat
MSA-DFES | WA4034719 | Sliding door to Tunic room (off engine room) has broken from its mount/ track. | CFRS Armadale | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-04-19 10:30:00 | Fail | Existing sliding door track has been replaced with a new Fitzroy door sliding track. Door is now operational again.
MSA-DFES | WA4034747 | A number of spiders and webs in station. We require spider termination treatment for station | CFRS Wangara | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-03 13:15:00 | Pass | Carried out a service for spiders to the wangara fire station. Spiders were reported in various locations around thestation. Residually sprayed the full external perimeter as well as within the sheds, tunic room and spot treatinginternally where safe to do so. Have advised staff that if problems persist internally we would need to attend on aquiet day to mist inside. Do not brush off spider webbing for at least 2 weeks after treatment.
MSA-DFES | WA4034768 | check all light globes at site | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-05-29 11:00:00 | Fail | COMPLETED
MSA-DTAG | WA4034377 | Female public tiolets latch/ lock is no longer working and not locking | Joondalup Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-05 08:15:00 | Pass | NEW LATCH INSTALLED - ALL OPERATIONAL
MSA-DTAG | WA4034380 | Female toilets custody toilet seat is loose requires securing | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-02 08:00:00 | Pass | COMPLETED
MSA-DTAG | WA4034385 | Lvl 1, Court 2 waiting room- A skirting board has come off the wall | Midland Courthouse | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo Building Services | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-05 10:30:00 | Pass | skirting re attached
MSA-DTAG | WA4034509 | Level 29 auto foyer door opposite F lift is stuck in open state after access granted - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-04-08 14:09:00 | Fail | Inspected door and found to have a relay fault as previously found on previous visits. Check access with access company confirmed to be ok at time of test. Recommend a ups be fitted to regulate mains voltage to door to see if this will rectify fault I have reset the door and left in running condition all OK at time of test. Braf has been raised and approvedReturned 8/4/21 - Supplied and fitted ups set up and tested all ok
MSA-DTAG | WA4034639 | Staff kitchen tap has become loose and is leaking - see notes | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-02 10:30:00 | Pass | COMPLETED
MSA-DTAG | WA4034644 | female public toilet stall 2 missing roll holder, stall 1 holder loose | Joondalup Courthouse | GMP-BR-HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-05 08:30:00 | Pass | Waiting on parts. Completed
MSA-DTAG | WA4034689 | Case managers Desk in room 1.03,2.03 , 3.05,4.05 are not programmed | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-09 13:00:00 | Fail | Checked all programming on all duress points. Activated all Duress and checked with level 10 Security on DMJC. All tested and activated correctly. Job complete
MSA-DTWD | WA4034258 | Pump shed - fire service jacking pump in fault | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-08 09:53:00 | Fail | Jacking pump investigation found that pump tripping out to power surge readjust amps from 12 amps to 13 ampsRESET JACKING PUMP-CALIBRATE SWITCH TO PUMP-COMPLETED
MSA-DTWD | WA4034293 | Exterior wall, G block - Remove two broken 3phase isolators. | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-02 12:02:00 | Pass | Removed isolates and filled holes g block
MSA-DTWD | WA4034303 | A Block Lift is not working | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 25 Feb 2021 | 2021-02-25 13:11:32 | 2021-02-25 14:59:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA4034316 | A Block staff toilet (A13) - Replace/repair faulty single flush toilet cistern in female toilet | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-05 16:00:00 | Fail | replaced cistern female staff toilet
MSA-DTWD | WA4034368 | L2 front door - Fix faulty electronic locks as required | Perth Campus B6 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 15:30:00 | Pass | Repair to lock
MSA-DTWD | WA4034387 | Level 5, E528 - Repair locks as required | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-03 11:00:00 | Pass | Repair/replace 3 x locks
MSA-DTWD | WA4034393 | Block 10, Pathways - Paving sunk and lifting | Thornlie Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-02 14:00:00 | Pass | Lift and relay paving in various areas
MSA-DTWD | WA4034413 | A Block, A02 -North auto door is emitting a beeping alarm intermittently. It is resetting by itself. | Midland Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 11:52:00 | Pass | Inspected door and found that the battery backup was low and causing the door to alarm, replaced battery backup as necessary, checked over and tested operation.
MSA-DTWD | WA4034417 | Foyer, fire panel showing fault System 1 FLT | Perth Campus B2 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-09 09:30:00 | Fail | Attended site - investigated fault. Zone 54 in plant room. Ordered detector - Petronic FIP. Replace faulty detector - zone 54.
MSA-DTWD | WA4034461 | Block 6, Painting & Decorating - Faulty power point next to eye wash | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-05 13:30:00 | Pass | Attended site and signed in. Located block 6 painting. Found gpo on wall in wet area and not weatherproof. Disconnect and removed outlet. Installed plate over hole and mounted new weatherproof double gpo in its place. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4034497 | B block L3 female toilet last cubicle toilet leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 16:30:00 | Pass | Leaking toilet
MSA-DTWD | WA4034598 | G block GG03 workshop evap leaking water out the bottom/side of louvres/pads. | Carlisle Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-02 12:00:00 | Pass | Found water float valve and bleed valve leaking.Picked up parts from suppliers. Returned to site. Fitted new parts. Found flexible hose and elbow at solinoid valve worn. Picked up new parts from another supplier and returned to site. Fitted parts. Adjusted water float valve and flow valve. Started unit and checked for water leaks. Non found. All appears ok.
MSA-DTWD | WA4034645 | E-Block restaurant Kitchen water leaking through light fitting | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 10:00:00 | Pass | Investigated water leak in ceiling of kitchen.No leak evident and plumbing pipework is 4m away from where leak was sighted. I suspect the leak is from the evaporative airconditioning.
MSA-DTWD | WA4034657 | D block D012 very smelly air con | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-03-19 15:30:00 | Fail | Travelled to collect parts , accessed site completed relevant sign in procedures and covid safe app wa requirements, gained access to d block room D012 , electrically loto ac unit , removed covers , carried out chemical clean of ac unit, tested drain operation, reassembled covers and tested unit , all ok- filters have reached end of life , replacements are unavailable, Sylvio has been informed and agreed to leave old filters in unit.
MSA-DTWD | WA4034729 | Murdoch Campus, Science Block, Fume cupboard #3 keeps tripping despite re-sets | Murdoch Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | SW HART & CO | 3 | COMPFIN | 25 Feb 2021 | 2021-03-05 17:00:00 | 2021-05-10 09:05:00 | Fail | Flow Sensor Calibrated & Retested
MSA-DTWD | WA4034731 | J Block, J003- Faulty air con, not cold | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-02 10:00:00 | Pass | Investigate unit. Test operation. Unit works to design. Unit set to dehumidification setting. Advised client on correct operation. Job complete.
MSA-MRWA | WA4034334 | ground reception Front entrance auto doors sensor overly sensitive - see notes | Materials Engineering Branch | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 25 Feb 2021 | 2021-03-03 17:00:00 | 2021-02-25 10:15:00 | Pass | Inspected door and found internal activation sensor required adjusting. Set up sensor and tested. All ok at time of test.
MSA-MRWA | WA4034761 | Toilet continues to flush please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor-A5.01-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Feb 2021 | 2021-02-26 17:00:00 | 2021-02-26 16:03:00 | Pass | Replaced inlet valve,outlet washer and bellows to 3rd floor male toilet cistern LHS
MSA-DCA | WA4035044 | chilled water pipe vibrating making loud noise | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-12-24 10:20:00 | Fail | Complete laser alignment of mechanical services pumps. Investigate chilled water valve/bypass serving AHU VAV. Steve Kinslow controls contractor to investigate as unable to initiate original noise reported.13/7/2021 - Precise Air to engage Mechanical Engineer for to inspect Chilled Water Valve/bypass for correct operation and design due to irregular noise and vibration.
MSA-DCA | WA4035245 | External roller shutter has jammed open and failed | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Building | Awnings (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | COMPFIN | 26 Feb 2021 | 2021-02-26 17:08:12 | 2021-02-26 16:45:00 | Pass | found door jammed in guides ang bagged out.Tech unjammed curtain and took bag out. Closed door and mase safe/secure. Tagged out.Quoted extra works on 04/03/2021.
MSA-DCS | WA4034890 | L1 duty room 1 door will not close properly | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | COMPFIN | 26 Feb 2021 | 2021-02-27 07:11:02 | 2021-03-05 11:00:00 | Fail | Attended site and repaired faulty mortice lock.sourced and picked up new mortice lock.
MSA-DCS | WA4034891 | front door handle is loose | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 26 Feb 2021 | 2021-03-05 17:00:00 | 2021-02-26 11:00:00 | Pass | carried out repairs to the loose handles on front doors.
MSA-DCS | WA4034902 | Corridor to health light damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-10 09:00:00 | Fail | Repairs to lights in hallway to health
MSA-DCS | WA4034915 | industries prisoner toilet block toilets blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Feb 2021 | 2021-03-05 17:00:00 | 2021-02-26 14:00:00 | Pass | Advised to have septic pumped out
MSA-DCS | WA4034920 | Unit 5 - Cell B12 Hatch won't open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 07:45:39 | 2021-03-02 10:15:00 | Fail | Open jammed hatch, remove build up of paint on hatch and hinge, adjust hatch hinge and lubricate lock.
MSA-DCS | WA4034932 | Unit 4 - D2 cell window springs not working. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 26 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-04 11:30:00 | Pass | SPIRAL BALANCES RE NEWED AND FRAME REPAIRED
MSA-DCS | WA4034957 | Unit 1, B5 - Toilet Pan Seals Leaking into the shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-25 11:00:00 | Fail | Replaced smashed toilet pan and seat.Job delayed due to escort
MSA-DCS | WA4034961 | Unit 1 C1 toilet and sink smashed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 08:25:40 | 2021-03-08 15:28:00 | Fail | No issues with toilet and basin
MSA-DCS | WA4034963 | Unit 1, B2 - Toilet Pan Seals Leaking into the shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-11 11:00:00 | Fail | Remove pan, replace leaking keep seal and pan collar rubber with new. Silicone back down pan.
MSA-DCS | WA4034975 | Unit 2, D12 - Water leak from D wing, D12 or D11 into utilities cupboard down on B wing corridor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-09 15:30:00 | Fail | Nill
MSA-DCS | WA4034978 | Unit 1 C1 viewing hatch smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 08:45:06 | 2021-02-27 08:30:00 | Pass | NO EVIDENT DAMAGE TO VIEWING HATCH - PERHAPS JOB WAS UPLOADED WITH WORNG LOCATION - LABOUR ONLY TO INSPECT
MSA-DCS | WA4034983 | gate house 2 electronic doors 5 and 6 will not operate correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Feb 2021 | 2021-02-26 16:51:07 | 2021-02-26 16:00:00 | Pass | Two doors insecure from inside. Door 5 (SO to Control corridor) Door not closing correctly. New door closer installed by others. Referred to Tony Vavier to get contractor to return & adjust. Door 6 (Control corridor to Sally Port) latch tongue exposed, able to be manipulated to open. Referred to Tony Vavier to get on-site Metal shop to manufacture "latch cover plate" for this and door 5. Custom manufacturer required as both door have Electric strike locks.
MSA-DCS | WA4034995 | CCU, Common Area Entrance Door - Door Jamming in the Door Frame jamming Lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 08:59:12 | 2021-02-26 11:00:00 | Pass | Attend site. Rectify and adjust hinges to secure door with new bolts. Reattach strike to frame.
MSA-DCS | WA4035031 | Unit 4 - B & D Exposed electrical wire under the B/D Dayroom kitchen overhead cabinet. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 26 Feb 2021 | 2021-02-26 13:39:23 | 2021-02-26 13:30:00 | Pass | Investigate and make safe unit 4 b & d kitchen pelmet light circuit
MSA-DCS | WA4035040 | stair case leading to level 1 - banister is loose | East Perth | GMP-BR- HO | Building | General Building (BU) | Schlager Construction Group | 3 | CLOSE | 26 Feb 2021 | 2021-03-08 17:00:00 | 2021-02-26 12:00:00 | Pass | carried out repairs to handrail located above stairs
MSA-DCS | WA4035075 | unit 4 B stove not working ignition and burners fault | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-16 09:30:00 | Fail | Unit 4B Stove not working, ignition and burners fault. Check stove & controls. Clean up ignition on burners, reset oven door & panel. Assemble & test. Report to staff.
MSA-DCS | WA4035088 | unit 1 cell 45 fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-04 10:00:00 | Pass | Replaced ceiling fan
MSA-DCS | WA4035093 | Metal shop office - aircon not working | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 10:52:06 | 2021-03-08 01:30:00 | Fail | COMPLETED
MSA-DCS | WA4035095 | Metal shop, stores room - air con faulty | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-08 14:30:00 | Fail | COMPLETED
MSA-DCS | WA4035228 | Maintenance workshop - air compressor switch faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 12:53:35 | 2021-02-26 14:00:00 | Pass | Maintenance Workshop, air compressor switch faulty. Check compressor, main pressure switch faulty. Dismantle & replace with new overload/contactor. Assemble & test.
MSA-DCS | WA4035266 | kitchen right hand prover GPO broken | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 26 Feb 2021 | 2021-02-27 13:45:06 | 2021-02-27 12:00:00 | Pass | Replaced damaged power outlet and 24hr timer
MSA-DCS | WA4035281 | gate house lower floor, monitors are blank no picture | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Feb 2021 | 2021-02-26 17:55:19 | 2021-02-26 16:30:00 | Pass | Restarted the INDIGO software and all went fine as normal. NOTE: took some time to get the correct user name and password since it was changed just recently as per Ian
MSA-DCS | WA4035307 | Market Gardens - Office door lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-09 10:55:00 | Fail | Requires new lock due to corrosion.Replace mortise lock, adjust strike and lubricate.
MSA-DFES | WA4035008 | Applied trainin grounds, near intermediate pad - pipe has burst in ground, water rising and bubbling | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-17 13:08:00 | Fail | Repaired burst pipe
MSA-DFES | WA4035073 | ground floor, door entering into corridor from lobby - Door handle has come off, completely snapped. | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-08 12:00:00 | Fail | Replaced door handle to north side of lobby
MSA-DFES | WA4035217 | Dorm 2(FF Middle) -Air Conditioner Leaking water onto the floor when operating. | CFRS Duncraig | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 15:30:00 | Pass | Unblocked drain, cleaned evaporator coil and fan barrel.
MSA-DFES | WA4035229 | L1 kitchen cold water system leaking - see notes | DFES Rescue Helicopter Base | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-02-26 16:23:00 | Pass | Replaced cooler, flushed new system and checked under pressure NO CHARGE FOR THIS PART OF WORKSRETURNED AS REQUESTED AND REMOVED OLD LEAKING UNIT FROM SITE AND DISPOSED OF AT TIP
MSA-DFES | WA4035236 | Office – at North End of building next to kitchenette - light flickering - see notes | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-03 09:00:00 | Pass | Fixed light and tested for function
MSA-DFES | WA4035270 | metro and maintenance office lights keep tripping | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 16:45:00 | Pass | Located tripping circuit. We isolated the fault to 4 lights in an office. This internals of the lights seem old and worn, I have halved the load and by doing so the tubes and starters broke in my hands. Halving the load has reduced the stress on the internals which is causing the trip, we will seek approval to replace the older lights for 4 new LEDs which will hopefully fix the issue.Closing job out at cost to date, ceilings in room are being replaced under LVM and new fittings will be installed then.
MSA-DFES | WA4035283 | bathroom all glazing and grout has worn away from daily use | CFRS Joondalup | GMP-BR | Flooring | Tiling (FL) | AWB Co. | 3 | CLOSE | 26 Feb 2021 | 2021-03-08 17:00:00 | 2021-06-02 15:30:00 | Fail | bathroom all glazing and grout has worn away from daily useRetile and re grout as per BRAF/Quote submitted
MSA-DFES | WA4035312 | ground floor issue with ants - see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-04 13:00:00 | Pass | Carried out initial gel bait treatment for ants to Emergency Services Intelligence Dept. office area. Applied ant gelbaits throughout this area, unless obstructed or unsafe. Treated eg. Around skirtings, window sills, power points,cable ducts, desks, bins etc. Due to higher level of infestation, at least one follow up is strongly recommended.
MSA-DFES | WA4035357 | Kitchen / dining area - Air conditioner in kitchen / dining area leaking water onto floor | CFRS Murdoch | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-03 11:13:00 | Pass | Attended site and signed in. Inspected aircon in dorm 1. Found no leak visible. Flowed water through unit and found no leaks or blockages present. Checked aircon in kitchen and found drain is blocked. Could not access drain exit as it runs through wall cavity. Cleared blockage from inside the unit. Poured hot water through drain line and found flowing well. Poured some drain treatment into drain to prevent future leaks. Cleared debris from site and completed paperwork.
MSA-DFES | WA4035376 | BMS fault alarm - remotely login and asses, attend if required to restart | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 26 Feb 2021 | 2021-02-26 20:22:02 | 2021-03-16 12:22:42 | Fail | Repair works were carried out under a second work order. The bms had a fault which was causing the crac unit to alarm. This has been rectified.
MSA-DTAG | WA4034998 | L8 staff toilet has become detached from the wall | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Feb 2021 | 2021-03-08 17:00:00 | 2021-03-10 14:06:00 | Fail | COMPLETED
MSA-DTAG | WA4035009 | 1987 L1 FIP Sensor fault in FIP – Zone 19 | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-26 12:30:00 | Pass | Attended site and found device 1075 Z3 Ground floor room RM20 in analog fault.Located detector and fitted newReset and left system normal.
MSA-DTAG | WA4035117 | L1 Links Office Bathroom loose tap | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-04 14:55:00 | Pass | Replaced corroded threaded bar and nut on the loose basin mixer
MSA-DTAG | WA4035197 | Cell 4 - security camera lens damaged and scratched, few screws missing (see notes) | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-07-07 08:30:00 | Fail | Replaced corner mount camera cover in Pod 4.
MSA-DTAG | WA4035206 | Cell 4 - intercom has been urinated on and now short circuiting and cease working | Joondalup Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-17 11:30:00 | Fail | Replaced Intercom unit in custody cell4. Tested ok
MSA-DTAG | WA4035209 | Custody Staff And Persons In Custody - Bio clean required - see notes | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-02-27 15:00:00 | Pass | Job completed as per WO
MSA-DTAG | WA4035329 | Control room - Printer not connected to monitor in control room | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | ICT/Audiovisual | Software / Licences (AV) | Sapio Pty Ltd | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-08 16:00:00 | Fail | Installed printer software and setup network settings. All setup and tested correctly. Job complete
MSA-DTWD | WA4034909 | A block ground A032 Repair water damaged sink cupboard | Joondalup Kendrew Campus | GMP-BR | Carpentry | Timber (all types) (CA) | AWB Co. | 2 | CLOSE | 26 Feb 2021 | 2021-03-03 17:00:00 | 2021-03-09 08:50:00 | Fail | A block ground A032 Repair water damaged sink cupboardFit new shelf and trims
MSA-DTWD | WA4034912 | E block pavillion Backing plate to stainless steel bench pulling away from welds - see notes | Joondalup Kendrew Campus | GMP-BR | Building | Steel Work (BU) | AWB Co. | 3 | CLOSE | 26 Feb 2021 | 2021-03-05 17:00:00 | 2021-03-05 09:45:00 | Pass | Work completed
MSA-DTWD | WA4034954 | D block ground floor walkway - Security lights not operating in walkway behind D Block. | Midland Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-03 13:06:00 | Pass | Retro fitted 6x vandalites to led to walkway behind D block. Parts supplied by site.job completed
MSA-DTWD | WA4035002 | E100 Electrical Workshop - 15 double fluoro lights that are not working in the Electrical Workshop | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-04-08 10:15:00 | Fail | replaced faulty fluros and startres, all materials supplied by site
MSA-DTWD | WA4035024 | A block, A02 Admin - Metal halide / mercury lights not operating in Admin at high level. | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-04-14 16:30:00 | Fail | Attended site, signed in , completed jsa , used 12ft ladder to grab lamp for sample , went to wholesaler to pick up 2x lamps , returned to site , changed lamps , lights now working , cleaned up work area, put ladder away , completed paperwork , signed out *** job completed ***
MSA-DTWD | WA4035027 | A block AG01 & Corridor RCD for lighting keeps tripping. | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-10 08:30:00 | Fail | Attended site and signed in. Got access to AG01. Investigated fault within light fittings. Located to middle light cabling breakdown and shorting out. Repaired cabling and re fitted covered to light fittings. Reinstated power and tested light to operate okay. Signed out. Job complete
MSA-DTWD | WA4035035 | Block 6 Carpetry and Joinery Corridor lock on door between 6E53 and 6E54 faulty. | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 26 Feb 2021 | 2021-03-08 17:00:00 | 2021-03-02 11:45:00 | Pass | Block 6 - between 6E53 and 6E54 lock faulty.Lock repaired.
MSA-DTWD | WA4035048 | block 4/5 ground toilets Exhaust fans not working | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 26 Feb 2021 | 2021-03-08 17:00:00 | 2021-05-31 10:05:00 | Fail | Found both motors seized. Awaiting approval to carry out repairs or replace unit.
MSA-DTWD | WA4035051 | block 1 ground 1G27 Air conditioner making an noise | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 26 Feb 2021 | 2021-03-08 17:00:00 | 2021-03-05 15:00:00 | Pass | OnsiteInvestigated issue with noise coming from ducting under AC head unit. Found noise to be water condensate pump operating. Moved pump but very low noise can still be heard due to pump operation. Unable to make pump silent unless pump is disconnected, which cannot be done as water won't run out drain.
MSA-DTWD | WA4035064 | Various areas, grounds - brick paving uneven/lifted, causing trip/fall hazards | Thornlie Campus | GMP-BR | Flooring | Concrete (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 14:00:00 | Pass | Lift and relay paving in various areas
MSA-DTWD | WA4035068 | Block 8 ground main entrance Automatic sliding door banging on stopper when opened. | Thornlie Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-02-26 12:37:00 | Pass | On inspection, found door slamming open.Adjusted opening settings and end stops as required. Unit showing heavy signs of wear and due to age.Track wheels showing heavy signs of wear and tear.If problem occurs again, highly recommend to upgrade unit due to obsolete equipment to replace and safety.Please provide quote to supply and install the following.1x non locking ES200 kit (SL200)1x IXIO 1x M42x Track wheelsBraf has been raised on 26/2/2021, but not approved, so first call out has been invoiced
MSA-DTWD | WA4035145 | T block T009 broken foot pedal on bed | Joondalup McLarty Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-03 08:30:00 | Pass | After arriving on site and walking through the job with Dave, we checked every bed to ensure correct operation, we found 2 beds to be unplugged from their GPO and after plugging them both back in they’re working correctly. We checked every bed in T009 to ensure it would go completely up and down, all working, we checked the other rooms with the same beds and found them all to work as well. After finding nothing wrong with any beds we have put it down to operator error, with the motors just not being plugged in.
MSA-DTWD | WA4035154 | T block ground T009 has two faulty/ loose tap handles | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-02 12:30:00 | Pass | COMPLETED
MSA-DTWD | WA4035250 | A block, AG01 - AC1 not cooling, unit is running but heating instead | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-04 15:15:00 | Pass | Attended site and monitored unit. Unit found to be achieving set point of 22.5 Celsius. monitored unit and found no faults. job completed
MSA-DTWD | WA4035285 | D block ground admin student services broken blind. | Joondalup Kendrew Campus | GMP-BR | Building | Windows (BU) | NEYLOR | 2 | CLOSE | 26 Feb 2021 | 2021-03-04 17:00:00 | 2021-03-05 13:12:00 | Fail | completed & Invoiced
MSA-DTWD | WA4035318 | Outside rom W213 - replace burnt out electrical switch | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 26 Feb 2021 | 2021-03-02 17:00:00 | 2021-03-02 09:21:00 | Pass | Replaced melted 2 gang light switch in lvl 2 west hallway
MSA-DTWD | WA4044310 | Provide spot coolers for AF 1 & 2 - Job already completed | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 26 Feb 2021 | 2021-03-05 17:00:00 | 2021-04-01 11:54:00 | Fail | job raised to cover the cost of spot cooler hire. job is complete and spot coolers have been picked up by supplier. job can be invoiced
MSA-DCS | WA4035467 | Gatehouse - Sally port personal door keeps opening randomly - Currently closed | Albany Regional Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Feb 2021 | 2021-03-08 17:00:00 | 2021-02-28 14:30:00 | Pass | Rectified and fixed the interlocking issue on sally port doors, tested all doors from control room and reception, systems back to normal operations.
MSA-DCS | WA4035491 | unit 1 04afd Dwing roll not operating loose motor mounting suspected | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 0 | CLOSE | 27 Feb 2021 | 2021-02-27 14:58:24 | 2021-02-27 14:00:00 | Pass | Saturday 27/02/21Adjust strike plates for limit switches.Install missing bolt to mounting plate for motor.
MSA-DCS | WA4035524 | unit 1 CD wing - air lock door not locking correctly | Melaleuca Prison | GMP-BR- HO | Building | General Building (BU) | AAA Ability Locksmiths | 1 | CLOSE | 27 Feb 2021 | 2021-02-28 12:04:57 | 2021-02-27 15:45:00 | Pass | Attend site after hours. Air lock door C/D wing not locking. Lock serviced and hinges tightened. Tested and working correctly.
MSA-DCS | WA4035649 | Gate house - Door control system is faulty and showing Buffering | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Feb 2021 | 2021-02-28 14:19:56 | 2021-03-04 08:45:00 | Fail | phone support ccompleted
MSA-DCS | WA4035689 | Casuarina Prison - Monitors down at the front gate and infirmary. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Feb 2021 | 2021-02-28 20:41:10 | 2021-02-28 19:45:00 | Pass | Attended Gate Control, all monitors in control room operating correctly. Attended Infirmary, on arrival noted that the screen display was 16 pane (4x4). Checked monitors in CCU section, all operating correctly. Returned to Infirmary where I found staff wanted a 4 pane (2x2) display so they could monitor the Safe Cells. Showed staff how to change display setup using mouse and keyboard. Confirmed outpatients monitor was operating prior to leaving Health precinct. Advised Night SO and departed prison.
MSA-DCA | WA4038321 | Fire alarm fault in work shop-to be attended tomorrow morning | Maritime Museum Victoria Quay | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 01 Mar 2021 | 2021-03-02 17:00:00 | 2021-03-03 10:50:00 | Fail | Attended site investigated alarm and faultsub FIP had no power. Building contractors resolved power issue. Zone 40 had been in alarmon 1-3-21 and 2-3-21Fault may have happened due to supply and battery fails- replace 2 x 7ah batteriesRoof has been replaced but not the cap at this time Detectors are exposed to elementsDisabled zone 39 and 40 on sub panelZone 39 on main FIP in fault
MSA-DCS | WA4038297 | Cell call system Unit 10 Cell D12 not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Mar 2021 | 2021-03-01 14:31:32 | 2021-03-01 13:45:00 | Pass | Unit found unresponsive reset restested ok.
MSA-DCS | WA4038394 | Multi fire panel fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 01 Mar 2021 | 2021-03-02 13:09:08 | 2021-03-02 15:32:00 | Fail | BG JG 3/3/21Attended site due to 2x module faults on node 7. NP7 health centre showing loss of comma with network. Rebooted site site work. Comms regained. Monitored. Fault did not reoccur
MSA-DCS | WA4038427 | ISU Wing Cell B -6 camera scartched | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Mar 2021 | 2021-03-02 14:18:13 | 2021-03-01 16:30:00 | Pass | Replaced damaged Bosch corner mount camera window glass with new.Used parts : 1 X Bosch bubble type camera window NCN - 90022F1(site spare).
MSA-DCS | WA4038462 | Hakea Prison - Unit 3 - porcelain sink has been ripped off the wall. prisoners unable to use showers | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Mar 2021 | 2021-03-02 15:48:15 | 2021-03-08 09:20:00 | Fail | Replace basin, basin set and waste
MSA-DCS | WA4038500 | internal microwave and PTX system is not working properly | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Mar 2021 | 2021-03-01 21:47:10 | 2021-03-01 21:15:00 | Pass | Attended site checked and found all perimeter MW&PX are showing purple ( no comms ) on Control panel. Checked in EC carbinet 8&9 are not working properly. Reboot Fiber modems and tested all ok after.
MSA-DCS | WA4038501 | fire panel earth faulty and alarm | Karnet Prison Farm | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 01 Mar 2021 | 2021-03-02 18:45:29 | 2021-03-02 13:29:00 | Pass | Attended site and found network in fault with nodes 2 & 3 off line and others not communicating correctly.Replaced all 4 Nic cards and got system back on line and left system normal.
MSA-DCS | WA4038502 | External Zones in tamper (all down) on security system - Internal working | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Mar 2021 | 2021-03-01 23:16:18 | 2021-03-11 16:14:00 | Fail | Investigated network fault on external perimitrax system. Found when zone 11 is connected the system becomes unstable and the entire external perimeter crashes after about 1-2 hours. This system became obsolete years ago and new parts are no longer available. This makes fault finding very difficult and time consuming. Checked modules, found data cable in OBS tower 5 located inside a cable duct had rodent damage causing intermittent data faults. Also found evidence of dead rats and rat feces inside OBS tower. Replaced data cable with industrial instrumentation cable and housed it in a new corrugated conduit run directly between SM7 enclosure and data module enclosure to better protect it in such an infested environment.Found sennet module 7 also faulty from possible shorting out of conductors in data cable or lightning damage. Located several unknown old second hand modules and managed to restore function. External perimeter network is now fully functional. Tested dual redund
MSA-DFES | WA4038480 | Crack unit in alarm | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Materials (BU) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 01 Mar 2021 | 2021-03-01 21:03:52 | 2021-03-16 11:59:33 | Fail | Attended site and signed in. Met tech from mizco onsite. Inspected crac unit 1.1a alarm. Mizco confirmed the crac unit does not appear to be sending a alarm signal. Found some settings on the alarm input for crac unit controller were incorrect. Mizco adjusted alarm input settings. Will monitor if alarms return.
MSA-DCA | WA4038661 | Alerton building management system offline | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Mar 2021 | 2021-03-02 17:00:00 | 2021-03-02 12:00:00 | Pass | Attended site. BMS control remote access not operating correctly. Contacted Alerton to log in remote via TeamViewer to investigate issue. Investigation found issue with IP address for remote access via optergy. Completed reset of IP and tested remote access. System operating correctly.
MSA-DCA | WA4038665 | Both Chillers in fault - Please attend Tuesday 2nd March | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Mar 2021 | 2021-03-02 17:00:00 | 2021-03-12 16:30:00 | Fail | Attended site. Chillers 1 and 2 to be in fault due to recent power interuption. Reset chillers and raised a PO for Airvison to attend to investigate fault with chiller 2 circuit 1 compressor 1. Please refer to attached Airvison service report for findings and in depth analysis.
MSA-DCA | WA4038894 | Currently sitting at around 12 degrees and should be a 10 degree | State Library of WA-Main Building-Level 3-10 Degree Stacks Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-02 16:30:00 | Pass | Calibrated monitoring temperature sensor. Unit controlling to setpoint. Logs to confirm also.Will request Honeywell calibrate their temperature sensor during next PM visit.
MSA-DCA | WA4038976 | Zones 2 and 10 high water usage leaks | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-02 15:00:00 | Pass | Full body and nozzle replacement
MSA-DCA | WA4039070 | Chiller room - Chiller 1 in fault | Shipwreck Galleries | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-02 16:30:00 | Pass | Attended site. Chiller system in fault. Applied tests and checks. Investigation found circuit A to have tripped on HP lockout. Reset HP reset and checked circuit pressures and entering and leaving water temps. Set chiller to lead and monitored on off cycle. System operating correctly.
MSA-DCA | WA4039342 | Leaking air con unit | Subiaco Arts Centre-Main Building-Ground Floor-Caf? Area | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-11 14:55:00 | Fail | Carry out investigation of unit. Found drain to be blocked. Unable to complete works due to no access. Re schedule works for tomorrow at 2.30pm.
MSA-DCS | WA4038641 | Western courts, Unit 2 end - Water cooler tripping the power | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-04-06 13:15:00 | Fail | Restarted work at 11.30am 6/4/21. Replaced faulty unit. Fixed unit to wall. All ok. removed old to tip
MSA-DCS | WA4038645 | Unit 2, Cell C10- Cell Call faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 06:46:34 | 2021-03-02 10:30:00 | Pass | Unit found with unknown substance removed and restested ok.
MSA-DCS | WA4038647 | Unit 4, Cell C9- Cell call indicator light does not go out | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-02 15:00:00 | Pass | Rectified and fixed the fault on the cell call point, tested working ok. Job completed.
MSA-DCS | WA4038690 | SITE COST PTZ camera 36 - no video input | Boronia Pre-release-AH19 - Administration, Education Senior Officers and Programs-Ground Floor | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 11:15:26 | 2021-03-02 11:11:00 | Pass | Attended siteInvestigated no video input from camera 36Upon investigation found faulty power supply for the reciever unit for cam 36 due to power cycle the reciever unit did not power on, diagnosed blown capacitor inside the power supplyReplacement power supply installedReset camera 36 power supply down at the EC unitConfirmed cam 36 now all working with siteLeft siteSupplied Part:1x PBOX 1040 13.8VDC 8A Power Supply
MSA-DCS | WA4038704 | Unit 4, A & C Dayroom- Sky Light is leaking | Casuarina Prison | SPA-BR | Roofing | Rooflights and Skylights (RF) | Midolo Building Services | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-04-08 17:00:00 | Fail | new skylights installed and roof repaired
MSA-DCS | WA4038707 | Unit 4, B Wing Cleaning room- Power point is hanging out of the wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 07:26:16 | 2021-03-02 13:30:00 | Pass | Replaced damaged gpo in unit 4 store
MSA-DCS | WA4038712 | Unit 4, Cell B6- pipe under sink is cracked & leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-05 09:30:00 | Fail | Nill
MSA-DCS | WA4038713 | Unit 13, Cell D12- shower water pressure is just dripping out. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-03 12:30:00 | Pass | Nill
MSA-DCS | WA4038715 | Unit 13, B & D- Door seal on Regi oven door has perished in places & is leaking heat while | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 10:00:00 | Pass | Oven door seal is ok, some minor damage to window seal but is ok not leaking.Left oven operational after adjusting door catch.
MSA-DCS | WA4038717 | Unit 14, Cell B1- Shower drain is blocked, water leaking from cell whenever shower is on | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-11 12:32:00 | Fail | Nill
MSA-DCS | WA4038721 | Unit 14, Cell C13- Shower tap & wash basin taps won't shut completely off. Toilet cistern running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-11 14:30:00 | Fail | Nill
MSA-DCS | WA4038723 | Unit 14, Cell B1- Prisoner lightswitch is not switching on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-02 15:00:00 | Pass | Repaired faulty lights and switch in unit 14 b1
MSA-DCS | WA4038726 | Gate House- Light is flickering above the Keywatcher in the western corridor | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-02 12:00:00 | Pass | Repaired faulty lights in western corridor
MSA-DCS | WA4038728 | Unit 3 - Fire Alarms activating but not showing in control | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 11:39:54 | 2021-03-11 09:02:00 | Fail | 2/03/21 EIAttended site to investigate reported faults at unit 3.On arrival main fire panel POD FIP reporting network break outside NP15 inside NP1. FIP also reporting unit 4 VESDA fault.Attended unit 3 and checked unit 3 FIP OK.Attended unit 1 and checked unit 1 FIP NP14 & the mimic NP15 OK.Attended security FIP NP1 and checked system status OK.Attended unit 4 VESDA and checked J block VESDA.J block VESDA reporting filter clogged.Also checked VESDA history log.The log identifies that the J block VESDA is reporting a “Low power laser” fault on a daily basis. Replaced clogged filter OK.Recommend this VESDA be replaced.Return to site required to further fault find on suspect lightning damaged NIC network interface card in FIP or damaged cabling between PODFIP & Security FIP.3/3/21 EIRe-attended site & recommenced network fault finding.Network break outside 15 inside 1.Fault finding concluded that the fibre optic network portion of the fire alarm system from the gatehouse
MSA-DCS | WA4038734 | Gascoyne, Cell A4- toilet flush button loose/damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-11 09:05:00 | Fail | Replaced flushing buttons to the toilet cistern.
MSA-DCS | WA4038737 | Hotham, Cell A6- Cell Call faint/muffled | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-03 09:15:00 | Pass | Check cell call point for any vandalism, test cell call function working as normal. Job completed.
MSA-DCS | WA4038740 | Jeelia, Cell B7- Light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-10 11:00:00 | Fail | Repairs to light in jeelia
MSA-DCS | WA4038741 | Jeelia, Cell B1- light switch cracked | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-10 10:00:00 | Fail | Repairs to light switch
MSA-DCS | WA4038745 | Serpentine, bathroom - MDAS identified a fault with transponder | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-08 08:45:00 | Fail | Replaced housing on reciever. Tested and working
MSA-DCS | WA4038746 | Unit 14, Cell B15- Toilet leaking in cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-09 12:30:00 | Fail | Nill
MSA-DCS | WA4038790 | Void - Toilet Prisoner toilet has a terrible smell after it has been used and flushed. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-19 12:39:00 | Fail | Nill
MSA-DCS | WA4038798 | Unit 2 - A Wing cleaning cupboard vent, has a massive hole in it, - see notes | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-02 13:26:35 | Pass | Arrived on site and signed in tools,patch up hole in duct.
MSA-DCS | WA4038802 | 2x fire system faults | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:11:24 | 2021-03-03 08:02:00 | Pass | BG JG 3/3/21Attended site due to 2x module faults on node 7. NP7 health centre showing loss of comms with network. Rebooted site site work. Comms regained. Monitored. Fault did not reoccur
MSA-DCS | WA4038805 | ISU A wing x2 smashed windows (approx 1400x750 top door window's) | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-21 13:15:00 | Fail | 2 X WINDOWS RE GLAZED AND SEC FILMED
MSA-DCS | WA4038816 | Unit 3, Cell D4- Water leaking from ceiling | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:23:46 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA4038817 | Unit 5 - C2 tap head has come loose and requires to the locking screw to be tighten. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-15 11:30:00 | Fail | Nill
MSA-DCS | WA4038818 | Unit 5, A Wing showers- Tiles lifting & coming away from wall | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:25:01 | 2021-06-09 10:47:00 | Fail | NEW WALL TILES INSTALLED, GROUTED AND WATERPROOFED MEMBRANE
MSA-DCS | WA4038852 | Unit 1 camera 24 No picture on monitor | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:39:54 | 2021-03-02 13:00:00 | Pass | Rectified the view from the monitor, job completed.
MSA-DCS | WA4038861 | ISU, A Wing common area- Roof leak (near end of table betweeb the camera and light) | Banksia Hill Detention Centre | SPA-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-09-13 14:30:00 | Fail | rectified leaks, installed new roof sheets, installed new air con units
MSA-DCS | WA4038876 | Unit 4, D Wing yard door- Door jammed on door frame | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-19 15:00:00 | Fail | door reset, re aligned
MSA-DCS | WA4038883 | Unit 1, Control Room- Water leak from ceiling over control desk | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:53:42 | 2021-06-15 14:00:00 | Fail | located leak and rectified
MSA-DCS | WA4038887 | Unit 5 A wing kitchen Regi oven faulty fan making a loud noise | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:51:06 | 2021-03-02 11:55:00 | Pass | Ensure fan was free of debris & rotating properly. Check Thermostat ok, left unit operational.
MSA-DCS | WA4038898 | Laundry Washing machine number 5 Low oil warning | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 08:59:38 | 2021-03-03 08:40:00 | Pass | Hakea - AMS781599 WA4038898 - WM #5 Low Oil WarningAttend Site - supply 20 litres of Oil for WM #5Test machine - OK
MSA-DCS | WA4038906 | Kimberley Wing, Female Toilet- Fluoro light not working | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-03 10:30:00 | Pass | Repaired faulty lights in Kimberly wing toilets
MSA-DCS | WA4038913 | control multiple fire fault through out facility | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 09:12:19 | 2021-04-07 09:00:00 | Fail | BG JG 3/3/21Attended site and performed the following;Node 1- removed and cleaned contact terminals for both card 2 and 3. Faults cleared and did not return. Recorded part numbers for both cards In cause of fault return.8 point relay card and motherboard- ASSY 565 045 RevF and ASSY 562 727 RevAMonitor card and motherboard- ASSY 562 731 RevD and ASSY 562 799 Rev DNode 4- Power cycled PSU and fault cleared. Completed replacement as this is a reoccurring issue with board. Part# ASSY 565 247 RevHNode 19- Yeeda faults caused by leak after hot water system failure. Faults cleared upon reset and did not return. Leak has been rectified and area drying out.Ravensthorpe- detector and cables found hanging. Reinstalled detector and reset alarm. Removed isolation.Computer and library- found detector in constant alarm. Required 10ft steps and tyco/simplex conventional thermal detector and base. Detector in inside library, first detector as you head through staff area. LED active.Gym
MSA-DCS | WA4038932 | unit 4A night light near cells 60, 59 and 9 near verandah not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 09:27:59 | 2021-03-03 09:00:00 | Pass | Replaced internal parts on 2 lights.
MSA-DCS | WA4038954 | 4A day room - Hot water urn is not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 09:44:16 | 2021-03-02 12:40:00 | Pass | Exchange thermal overload and re calibration
MSA-DCS | WA4038958 | Farm super shed (chemical storage sghed) - damage roof | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 09:45:35 | 2021-10-15 07:30:00 | Fail | REPAIRS CARRIED OUT TO SHED ROOF
MSA-DCS | WA4038969 | gatehouse, control room - external zone 1a - constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 13:50:37 | 2021-03-02 13:30:00 | Pass | Alarm input on panel in constant alarm reset retested ok.
MSA-DCS | WA4038972 | gatehouse, control room - external zone 15 px not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 13:53:52 | 2021-03-02 12:30:00 | Pass | Reset. Retested ok.
MSA-DCS | WA4038993 | SOG Base alarm not responding | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 10:06:33 | 2021-03-02 13:30:00 | Pass | Found pin that client was using had no arming or disarming privilege. Added privileges and tested code all good.
MSA-DCS | WA4039017 | Turner, Cell B02- Smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-08 11:45:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA4039019 | Unit 6, D13 - Key broken in lock D13 | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 10:22:10 | 2021-03-05 10:00:00 | Fail | Remove foreign object jammed in barrel, require parts.Replace barrel and weld on strike.
MSA-DCS | WA4039020 | Turner, Loose window near C wing entry door | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-08 11:45:00 | Fail | REPAIRS MADE TO WINDOW
MSA-DCS | WA4039029 | Temporary sally port - no video camera feed from area | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 10:29:23 | 2021-03-04 13:30:00 | Fail | Faults with BNC plugs on Coaxial cable patch leads between fibre modem and Indigo Encoder. Cut off and replaced 2 X BNC plugs on two cables.
MSA-DCS | WA4039032 | Unit 4, camera PTZ 37 - not working unable to move | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 10:31:12 | 2021-03-04 11:00:00 | Fail | On arrival tested operation of PTZ camera. Camera Pan Tilt Zoom functions all worked correctly. Was advised that there was a site-wide power outage this morning prior to my arrival. This may have reset the fault condition.
MSA-DCS | WA4039037 | Turner, B02 - door split near lock | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-08 11:10:00 | Fail | REPAIRS TO DOOR CARRIED OUT, RE HUNG & PAINTED
MSA-DCS | WA4039051 | Grounds - Office Brickwork falling apart | Casuarina Prison | GMP-BR- HO | Building | External Walls (BU) | Midolo Building Services | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-04-07 10:32:00 | Fail | NEW SCILL BLOCKS INSTALLED
MSA-DCS | WA4039126 | Ground floor, Billi is not working. Lights are all completely down - nothing flashing. (see notes) | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-03 11:57:00 | Pass | Billi unit tripping the power. Replaced element, level sensor and loom. Replaced filter as due. A40189280L
MSA-DCS | WA4039148 | yeeda C wing roof leak in the laundry end from water pipe | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 11:34:40 | 2021-03-04 13:05:00 | Fail | Job commenced on the 2/3/2021 at 11:31 and completed on the 2/3/2021 at 13:05 Replaced temp relief valve upstairs
MSA-DCS | WA4039157 | Unit 3, Cell B6- Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-09 16:30:00 | Fail | Nill
MSA-DCS | WA4039185 | Unit 1 D15 Leaking Sink Taps | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 12:06:58 | 2021-03-02 16:06:00 | Pass | Replaced spindles in the basin adn adjusted pressure
MSA-DCS | WA4039243 | Dairy packing room - Roof Leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA4039249 | SOG Base- TV aerial faulty (appears to have fallen from roof) | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 10:30:00 | Pass | Resecured antenna to roof.Antenna had previously been repaired with foil tape, recommend replacing.
MSA-DCS | WA4039313 | Unit 8, Entire unit- PA System not working correctly. Keeps cutting in and out. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-03 15:36:00 | Pass | Attended site and repaired speaker fault.Tested OKJob Complete
MSA-DCS | WA4039316 | Unit 10, Cell C8- Cell Call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 13:31:01 | 2021-03-17 14:00:00 | Fail | Removed and replaced CI8#5 with a CI8a. Added 8 x RJ45 wiring adapters. Replaced cabling for Comms, audio and power between CI8s 4, 5 and 6. Cleared NODE errors from other units 3210 officer stations. Parts used:Cell Guard CI8a8 x RJ45 wiring adapters 4m figure 8 cable6m 4core shielded cable
MSA-DCS | WA4039318 | Unit 10, Cell D12- Cell Call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 13:31:42 | 2021-03-03 15:49:00 | Fail | Attended site and repaired cell call system fault.Tested OKJob Complete
MSA-DCS | WA4039322 | Unit 10, Cell C8- Toilet bowl broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 13:32:43 | 2021-03-03 08:15:00 | Pass | Replaced cracked toilet and adjusted pipework
MSA-DCS | WA4039329 | Unit 7, Cell E9- Main Cell Door Lock Faulty. Tongue not sliding into recess | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 13:34:34 | 2021-03-02 14:45:00 | Pass | Attend site, main lock not working. Bolt thrower replaced on lock. Tested and working.
MSA-DCS | WA4039345 | L3 kitchen Cold water tap not working in the large Kitchen | East Perth | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-02 15:30:00 | Pass | Arrived on site and inspected found the the zip cold tap not working. They have another contractor to service zip units.
MSA-DCS | WA4039374 | SITE COST Unit 1, Plumbing duct between 14 & 15 sewer blocked, see notes below | Bandyup Prison | WSM-BR-SITE | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 18:16:44 | 2021-03-02 16:10:00 | Pass | COMPLETED
MSA-DCS | WA4039379 | unit 6 D10 Water leaking from copper pipe underneath sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 12:49:00 | Pass | Nill
MSA-DCS | WA4039392 | Unit 14, Cell B07 - toilet is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-11 09:30:00 | Fail | Nill
MSA-DCS | WA4039408 | Health care room 1 Vinyl Flooring ripped and lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-11 08:30:00 | Fail | damaged sections of rubber flooring lifted & replaced with new flooring
MSA-DCS | WA4039417 | stores The Purchasing windows have been pushed in and need to be fixed. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 15:00:00 | Pass | BENT FRAMEWORK REPAIRED & SECURED
MSA-DCS | WA4039430 | Unit 14 cell B10 toilet leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-11 10:30:00 | Fail | Nill
MSA-DCS | WA4039434 | MPU, office - Senior Officers office has no aircon | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 15:07:31 | 2021-03-11 14:51:20 | Fail | Checked operation of a/c after seme rectified control panel issue,all running ok.
MSA-DCS | WA4039435 | Outside Industries Stores Air Con Faulty. Not starting | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-09 15:00:00 | Fail | Checked unit after reset. Unit fully operational. Power surge possibly cause of fault. All ok
MSA-DCS | WA4039444 | L3 kitchen Cold water tap not working in the large Kitchen | East Perth | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-03 15:35:00 | Pass | Replaced cold pump
MSA-DCS | WA4039474 | Visits room, air conditioning - not operating (error code E5) | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 16:06:43 | 2021-03-03 15:30:00 | Pass | Ac wall controller replaced control phases swapped, all working well now
MSA-DCS | WA4039503 | GATE HOUSE-PERIMETER FENCE- Alarms not showing on system is stuffed. | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 21:50:52 | 2021-03-02 21:15:00 | Pass | Attended site checked and found whole perimeter Microphonics alarms showing purple on Senstar system and can’t be activated after lightning strike. Further check located the problem to be the power supply to all the Senstar controller tripped after lightning strike. Rectified the problem and tested all ok after.
MSA-DCS | WA4039505 | Multiple area fire alarm is faulty -constantly beeping | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 22:15:48 | 2021-04-13 09:07:00 | Fail | WA40395052/03/21 EIAttended after hours callout Banksia hill site.On arrival 3 x fire alarms 9 x faults & 4 x isolations present.Node 1 - Main fire panel reporting 2 x faultsCard 2 relay card missingCard 3 monitor card missingRebooted node 1 OK & faults cleared for awhile but returned.Replacement parts needed.Node 4 - Kitchen reporting 1 x faultPSU 24V B output fault.Node 19 - Yeeda reporting 4 x faultsCard 1 PSU negative earth faultM1-10 smoke detector in corridor o/S meeting room AZF112 disabled/fault.M1-25 duct detector cell A-03 AZF 113 disabled/fault.M1-19 smoke detector laundry store AZF112 disable/fault.Node 20 - Urqhart block reporting 1 x faultCard 2 class A abnormal faultM1-104 AZF 117wing A plantroom detector no answer fault.3 x Fire alarms present on Gymnasium AZF 79 & isolated by othersRavensthorpe AZF 64 & isolated by othersComputer & library AZF 11 & isolated by othersAZF 31 isolated by others.Advised staff attendance during business hours is
MSA-DCS | WA4039507 | SITE COST Visit centre cannot be alarmed and re entry house as well | Wooroloo Prison Farm-Gatehouse | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Mar 2021 | 2021-03-03 00:58:59 | 2021-03-03 13:45:00 | Fail | Found visits area PIR is wireless type and no power. Checked battery and found dead. Need to source out battery. Replaced battery and PIR will not power up anymore. PIR needs replacement (1x FA206I, INOVONICS). Deprogrammed PIR as required. NOTE: sourced out battery from Mundaring. Very difficult to cross between buildings because of heavy rains
MSA-DFES | WA4038841 | engine room 5x lights need to be change - insight on sight | CFRS Ellen Brook | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-02 15:45:00 | Pass | Replaced faulty tubes and ballast in engine room. All working.
MSA-DFES | WA4039060 | ground Critical Fire to attend to isolate the server room | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-08 14:45:00 | Fail | Attended site and isolated FIP and appropriate zones 24 & 30.De isolated zones 24 & 30 & FIP.
MSA-DFES | WA4039181 | L1 room 24 Shower rose holder broken | CFRS Ellen Brook | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 15:30:00 | Pass | REPLACED DAMAGED TILES AND REPLACED SHOWER HEAD.
MSA-DFES | WA4039215 | L1 rooms Room 20 (SO Dorm) - Reading light U/S Room 7 (duty room) – side light U/S | CFRS Ellen Brook | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-02 16:00:00 | Pass | Replaced faulty tubes
MSA-DFES | WA4039281 | station yard, hydrant stand pipe the thread on the valve is loose and coming off | CFRS Canning Vale | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-16 12:47:00 | Fail | Repairing the hydrant
MSA-DFES | WA4039298 | engine room door back not going all the way up | CFRS Osborne Park | GMP-BR | Building | Doors (BU) | Anvil Doors | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-02 15:00:00 | Pass | Attended Osborne Park Fire Station on P1 Service call out (Rear Door number 4 not going all the way up). Service technician found that the clutch was slipping to the motor so removed clutch pin, tightened up clutch and reinstalled clutch pin. Door 4 now working correctly. Please refer to the attached service reports and signature slip.Thank you
MSA-DFES | WA4039314 | ground storeroom room 26 ceiling light damaged - see notes | CFRS Fremantle | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 09:00:00 | Pass | CompleteAttended site and replaced faulty light fitting in store room 26. Tested and all in working order
MSA-DFES | WA4039336 | Security system is offline | DFES Education and Heritage Centre | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 17:38:57 | 2021-03-04 09:30:00 | Fail | 2/3/21 - Ryan Vesty, Dean SimpsonFound entry reader not responding, advised by monitoring that issue since lightning storm.Gained entry with key.Powered whole system down. Tested all hardware separately, found 2 Input boards dragging system down.Boards to be replaced, BRAF submitted. 4/3/21 - Ryan Vesty, Dylan ParslowReplaced input boards and tested, all ok.
MSA-DFES | WA4039454 | Engine room 55, 1st bay - charging cable from ceiling pulled down threw plaster. (see notes) | CFRS Perth | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 17:15:00 | Fail | Complete Attended site and located damaged charger cable, fixed back to ceiling and all in working order. Notified staff and signed out. Returned scissor lift
MSA-DFES | WA4039457 | external 25cm hole in rear yard asphalt.- photo's to follow in email | CFRS Wangara | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 12:00:00 | Pass | Repairs to pot holes
MSA-DTAG | WA4039008 | Lvl 4, Kitchen in Centra Breach Unit - Billi Quadra Water 2 Water Unit faulty, see notes below | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-10 13:25:00 | Fail | Replaced faulty dual solenoid and also replaced leaking tube kits. Work shop labour 8/03/21 10.15am to 12.27pm. RETURNED AND REINSTALLED UNIT AT SITE
MSA-DTAG | WA4039442 | Registry area - aircon has not worked all day | Rockingham Justice Complex | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-03 09:28:41 | Pass | Attended site and signed in.Staff reported that ahu 1 serving office was offline all day and after hours button did not operate the aircon. Inspected ahu 1 and found system operating correctly. Checked bms and time schedules. Found time schedule are correct and no holiday times were present that would affect operation. Turned time schedule off and confirmed operation of after hours button. Carried out operational checks and found unit is operating correctly. Suspect bms or power fault occered which stopped the unit from running
MSA-DTWD | WA4038828 | C Block, Room C112- Sift Shaker attached to wall cord ripped off machine | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-02 14:45:00 | Pass | Replaced broken cord and faulty 56 series GPO to C112Job complete
MSA-DTWD | WA4038910 | J Block, Eastern Auto door not operating/locking properly | Rockingham Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-02 15:17:00 | Pass | Found LM91 lock module faulty causing door to not lock and key switch has come loose, re fixed key switch and replaced LM91 locking module, reset and tested door all ok
MSA-DTWD | WA4038916 | A Block, foyer - Water fountain gooseneck leaking from base | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 13:38:00 | Pass | A40190158H Waterware Fountain Leakng from base of Tapware replacedGoosenext Chrome Faucet replacedtubing and JG Fittings TeeA Block Main Entrance
MSA-DTWD | WA4038973 | Block 5, Courtyard- Broken soak well east end of block 5 | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-09 16:30:00 | Fail | Rectify stormwater issues and brickwork
MSA-DTWD | WA4038980 | Main foyer entry doors west- Doors not locking | Perth Campus B6 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-09 14:58:00 | Fail | Found that the lock is not engaging when in lock mode, suspected faulty lock motor or controller. Quotation required to replace faulty el301 lock motor.Braf approved, returned to site and replaced 301 controller and tested ok. On arrival found the controller was faulty, not the lock motor. Tested lock and performed several walk through tests.
MSA-DTWD | WA4038989 | Remove fallen tree from carpark | West One Services | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-03 08:20:00 | Pass | TREE REMOVED AND PRUNING TO TWO OTHER TREES.2 HOURS ON SITE. 5 STAFF @ $100 PER HOURS = $1,000.CHIPPER TRUCK AND CHERRY PICKER 2 HOURS @ $100 PER HOUR = $400ACTUALS $1,400.BUDGET $1,000.CLAIM $,1000.
MSA-DTWD | WA4039015 | Classroom F60 - Unable to reset lighting circuit breaker in sub board | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-03 12:45:00 | Pass | Attended site and signed in. Located faults in switchboard. 2 x breakers tripping. Found 1 to be outside lighting. Traced back to junction box sitting in water. Drilled holes and drained out pit. Moved junction to sit upright. Reset and tested all okay. 2nd fault found to be store room light with weather ingress. Isolated and made safe till roof fixed. Job complete
MSA-DTWD | WA4039207 | A block male toilets, urinal is blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-02 14:00:00 | Pass | Unblocked urinal
MSA-DTWD | WA4039328 | L7 Water fountain in wall near lifts leaking | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 14:45:00 | Pass | Note: ProMAP down replaced Arcus TapTimes 12.30 to 13.00 tried to locate water isolation to fountain. Facilities not available. Returned 14.15 to 14.45 to isolate supply and replace faulty tap.
MSA-DTWD | WA4039363 | E Block, SK3 has 3 ovens not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-13 17:45:00 | Fail | COMPLETED 13/4/21
MSA-DTWD | WA4039371 | G Block, Male toilet is leaking | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-03 14:30:00 | Pass | Attend siteFaulty inlet valve.Replaced with new inlet valve, test and commission. Clean up site.
MSA-DTWD | WA4039375 | E Block, SK2 and SK3 - blown ceiling lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 08:00:00 | Pass | Replaced faulty tubes in kitchen lights
MSA-DTWD | WA4039396 | L1 west block W11 repair vertical blinds | Mount Lawley Campus | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-04-21 10:29:00 | Fail | completed & Invoiced
MSA-DTWD | WA4039412 | C Block Hairdressing, C47 green salon, external door glass craccked | Midland Campus | GMP-BR | Glazing | Door Glass (GL) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 02 Mar 2021 | 2021-03-02 18:34:34 | 2021-03-02 18:00:00 | Pass | ATTENDED SITE AFTER HOURSREGLAZED 2 BROKEN DOOR PANELS6.38 CLEAR LAMINATED SAFETY GLASS1-995 X 7451-710 X 745
MSA-DTWD | WA4039421 | I Block - Air conditioner in the front reception area is not working | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-12 14:25:00 | Fail | Investigate unit and found faulty condenser fan capacitors. Organise replacements return to site tomorrow to replace.12/3/2021 - Organise parts. Return to site. Sign in complete permits etc. Isolate unit. Remove faulty capacitors. Install new capacitors. Replace active and neutral wiring connections. Test operation. Unit working to design.
MSA-DTWD | WA4039424 | O Block, Plumbing Workshop- Roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 12:25:00 | Pass | COMPLETED
MSA-DTWD | WA4039426 | L1 west block Replace faulty filters on units in W109..W121..W119 | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 14:10:00 | Pass | Carried out routine filter changes in the zip water units and recorded any defects found. Note: ProMAP down earlier.
MSA-DTWD | WA4039431 | O block water cooler on the eastern side of O block (Balga)is not working - see notes | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 02 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-16 14:30:00 | Fail | Replaced blocked pressure limiting valve
MSA-DTWD | WA4039443 | Block 9 ground Library Computer room Water leak on to desks | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 02 Mar 2021 | 2021-03-03 17:00:00 | 2021-03-19 13:30:00 | Fail | Completed safety docs, removed old box gutter and dispose of, removed flashing to re use later. Fitted new box gutter with new pop, refitted flashing.
MSA-DTWD | WA4039448 | A block L3 A317 and A318 Repair roller on White Board | East Perth Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 08:30:00 | Pass | Work completed
MSA-MRWA | WA4039155 | MDB warehouse - Light timer external floods not operating (probable timer setting issue), See notes | Neerabup Depot | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 02 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 09:24:00 | Pass | Replaced faulty time clock
MSA-DCA | WA4040107 | auto door open intermittently key barrel lock key moving around in the barrel | The Blue Room-Main Building-Ground Floor | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-03 11:40:00 | Pass | Found key switch barrel had come loose and was spinning around causing door to go into no mode and not operate correctly, re fixed loose key switch barrel and checked over door, tested all ok
MSA-DCA | WA4040211 | fire panel isolate fire panel due to hot works-as per David De Villiers | Swan Bell Tower-Main Building-Ground Floor - Stairs | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 15:30:00 | Pass | Attend site - inspect area to be worked in - isolated zones 3-7 on fire panel.Client to advise on reinstatementReturn to site and reinstate fire system back to normal
MSA-DCA | WA4040509 | Urinal blocked. Cleaner’s attempted to unblock yet failed. | State Library of WA-Main Building-Level 1-Male Toilets - Near Lift Foyer - East | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 14:15:00 | Pass | Unblocked blocked urinal
MSA-DCS | WA4039812 | Various alarms on fencing cowling will not clear | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Mar 2021 | 2021-03-03 11:01:29 | 2021-04-15 15:00:00 | Fail | Replaced 7meters of intelliflex cable on front gate.Tested and working. Parts Used. 7 m of Intelliflex cable and 2 splice kits
MSA-DCS | WA4039873 | Unit 16 Cell C11 shower blocked and pooling | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-16 14:30:00 | Fail | Nill
MSA-DCS | WA4039875 | Karakin, Cell A06- top lock is sticking causing door to malfunction when opening | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 03 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 10:00:00 | Pass | Attend site, replace screws to hinges and adjust top lock at Cell A6. Tested, all functional.
MSA-DCS | WA4039877 | MPU (8) - M3 SPU cell 3 light switch is broken needs replacing. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:01:51 | 2021-03-03 15:00:00 | Pass | Investigate and repair spu cell 3 light switch
MSA-DCS | WA4039879 | Karakin, A Wing- broken double power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-09 10:30:00 | Fail | GPO Broken Karakin A Wing - pick up new one and replaced
MSA-DCS | WA4039880 | Karakin, Room B04- Shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 09:00:00 | Pass | No issues with shower
MSA-DCS | WA4039882 | Unit 2, Control- Fire alarm constantly alarming | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:06:42 | 2021-03-03 10:46:00 | Pass | Attended site to investigate N8 education in fault - fault found to be a dirty detector, removed and reinstated and fault reset and no longerthere
MSA-DCS | WA4039884 | Education, Control- Fire alarm constantly alarming | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:08:09 | 2021-03-03 10:39:00 | Pass | Attended site to investigate N8 education in fault - fault found to be a dirty detector, removed and reinstated and fault reset and no longerthere
MSA-DCS | WA4039886 | Unit 1, Cell B14- cell call speaker not clear | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:08:36 | 2021-03-03 10:20:00 | Pass | Attended siteAwaited for an escort to unit 1Escorted to unit 1Awaited for unit 1 to be secureTested Cell B14, found to be ok however the call was sent over to the other unit, due to the cell guard head unit being set to unattended inside Unit 1 security officeSet Unit 1 to attended and retested, voice drops half way throughRetested within another cell B3 Cell call is all okPower cycled the main head unit within a Unit 1Retested Cell B14 all okAdvised site of the outcome, all okLeft site
MSA-DCS | WA4039889 | Cell call 4.11 is working intermittedly. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:08:30 | 2021-03-05 14:49:00 | Fail | Technician attended site - investigated fault - traced to faulty CI-8 Card.Replaced CI-8, tested and confirmed correct operation - works completeParts used from SEME Stock:1 x CI-8A 10 x RJ45 Adaptors
MSA-DCS | WA4039894 | Unit 6 C6 faulty cistern - see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:15:19 | 2021-03-03 11:50:00 | Pass | Replaced outlet washer and inlet valve
MSA-DCS | WA4039903 | unit 3 B8 Floor waste blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:21:15 | 2021-03-03 12:10:00 | Pass | Unblocked floor gully
MSA-DCS | WA4039920 | laundry No washer trips out when power is turned on not washing | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 08:43:16 | 2021-06-03 13:45:00 | Fail | New soap board required, blowing fuses, replaced board found rotation sensor faulty. Replaced and test OK
MSA-DCS | WA4039933 | Vesda 4 alarm and apollo loop on fire panel | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 03 Mar 2021 | 2021-03-03 12:50:26 | 2021-03-03 11:58:00 | Pass | BG JG 3/3/21Vesda in unit 4 alarmed at 0500. Alarm was reset and cleared on arrival to site. Suspect smoking in cells. Unit 4 system normal at time of departure
MSA-DCS | WA4039977 | Bakery - safety guard on the Hobart mixer damaged/missing | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-04 15:45:00 | Pass | NO RESPONSE TO BRAF SO INVOICE WORK TO DATE.
MSA-DCS | WA4039983 | Boot shop - roof leaking badly over the electrical outlets | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 09:30:42 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA4039990 | Administration building - starnet & computers down | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Mar 2021 | 2021-03-03 13:34:09 | 2021-03-03 14:30:00 | Fail | Found NEC technicians working on the Starnet and computer networks because it was hit by lightning. NEC technician confirmed that it is not related to security at all and no physical connection to alarms/security. NOTE: very difficult to cross between buildings due to heavy rains
MSA-DCS | WA4040004 | Bakery - We keep having a pool of water coming from the proover that needs attending. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-18 15:15:00 | Fail | COMPLETED
MSA-DCS | WA4040005 | Unit 1, B Wing showers- check lock and striker (temp repair has been made) | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 12:00:00 | Pass | Repair mortise lock and remove deadlatch to allow correct function.
MSA-DCS | WA4040077 | Unit 4, A Block- chef hot plate knob shaft broken | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-05-12 15:00:00 | Fail | Replaced cook top
MSA-DCS | WA4040088 | Unit 6, D wing - urn faulty, constantly overflowing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 10:21:08 | 2021-03-03 13:02:00 | Pass | Replaced inlet solenoid and level sensors
MSA-DCS | WA4040151 | Kitchen- roof in pot wash area leaking | Wooroloo Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 10:57:08 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA4040154 | re entry house - power fault no router | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-03 13:00:00 | Pass | Investigate no power to router box, power present, possible surge caused damage to router.
MSA-DCS | WA4040173 | Sallyport intercom is not working | Albany Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-03 14:30:00 | Pass | Plugpack power supply failed. Noted 12vdc power supply in adjacent cabinet with available capacity. Installed new cable under floor from intercom to control cabinet. Terminated cable and tested operation of intercom.
MSA-DCS | WA4040200 | Unit 4, D Wing cleaning room- Door damaged around lock area | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 11:19:54 | 2021-03-03 15:00:00 | Pass | door repaired
MSA-DCS | WA4040226 | Demountable Classroom 7- Roof Leak | Nyandi Training Academy | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 11:34:13 | 2021-03-15 09:00:00 | Fail | Repaired roof leak
MSA-DCS | WA4040245 | Unit 1 Office - roof leak over computer desk | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-04-08 17:00:00 | Fail | REPAIRED SHEETS, RIDGE AND VALLEYS
MSA-DCS | WA4040252 | CCTV system in alarm, cameras not matching time and date with server | Maddington (South East Metro) | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-23 14:00:00 | Fail | - Completed cabling, install and setup of Time server device.- Set all camera and server to sync with time server.
MSA-DCS | WA4040260 | unit 6 D 13 toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-08 15:30:00 | Pass | Nill
MSA-DCS | WA4040419 | Jeelia, Cell B7- Aerial point damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-08 10:00:00 | Pass | Replaced faulty TV Point in Jeelia Cell B7. Tested ok
MSA-DCS | WA4040420 | Unit 5 - A & C AC regi oven fan is making a banging noise when switched on. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 09:35:00 | Pass | Reattached cable & test all elements ok.
MSA-DCS | WA4040423 | Unit 13, Cell A10- tap has a bad leak | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-08 11:30:00 | Pass | Nill
MSA-DCS | WA4040424 | kitchen robot coupe machine power cable broken at base of machine | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 12:00:00 | Pass | Investigate and repair kitchen robot coupe machine
MSA-DCS | WA4040433 | Administration lock faulty lock change Prisoner Release Coordinators office. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-18 10:00:00 | Fail | Require parts.Change barrel from GMK to POK to prevent unauthorised access.
MSA-DCS | WA4040454 | Lenard, B Wing- HWU wont ignite | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 10:35:00 | Pass | Inspected Hwu - electrician required
MSA-DCS | WA4040457 | Yeeda, A Wing- HWU wont ignite | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 11:20:00 | Pass | No issues with hot water unit
MSA-DCS | WA4040464 | Unit 4,Cell K3- door lock jamming | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 03 Mar 2021 | 2021-03-03 18:50:13 | 2021-03-03 16:15:00 | Pass | Adjusted door frame strike to enable positive cell locking
MSA-DCS | WA4040495 | SOG base, external walk way to TSU - clear plastic patio like roof has come off | Hakea Prison | GMP-BR- HO | Roofing | Polycarbonate (RF) | Midolo Building Services | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-06-10 15:00:00 | Fail | replace damaged roof sheeting from recent storm winds. Replaced with polycarbonate sheets - like for like
MSA-DCS | WA4040552 | Security computer system Cardax not responding - restarting taking too long | Roebourne Regional Prison-Gatehouse | SPA-BR | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Mar 2021 | 2021-03-04 06:35:12 | 2021-03-05 14:43:00 | Fail | Technician attended site on earliest available flight-Investigated fault - found SMS PC had failed - Supplied and installed new Custom Mini PC workstation - Reconfigured system and confirmed correct operation.SEME recommend installation of a secondary MCR workstation due to its critical function - recommendations to be included in BRAFReturn travel to Perth
MSA-DFES | WA4039906 | Change room- Leak & hole in the roof | CFRS Joondalup | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 14:25:00 | Pass | Work completed
MSA-DFES | WA4039972 | Workshop Offices Dining Room and adjacent Toilet water leaking from pipe - see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-25 14:45:00 | Fail | Remove rusted box gutter x 2 and fit new box gutter x2. Re fit existing stainless steel sumps and reconnect.
MSA-DFES | WA4039984 | dorm carpet needs to be cleaned after incident | CFRS Joondalup | GMP-BR | Cleaning | Emergency Cleans (CL) | Facilities First Australia Pty Ltd | 1 | FLDCOMP | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-05 16:34:00 | Fail | completed on the same day when request received
MSA-DFES | WA4040012 | L1 Fire Extinguisher bracket in Critical Care Paramedic (CCP) room has come off wall - see notes | DFES Rescue Helicopter Base | GMP-BR | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Critical Fire Protection & Training | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 07:50:00 | Pass | Installed fire extinguisher.
MSA-DTAG | WA4040123 | When the doors are unlocked, they are glowing red - see notes below | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-08 13:30:00 | Fail | Attended site, updated firmware to corresponding controller and forced/refreshed all alarms and config. Re-tested readers and made sure all is changing state according to reader color reference. All tested and working ok. Job complete
MSA-DTAG | WA4040160 | Hay street entry door intercom is flashing red and not operational | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-08 12:30:00 | Fail | Hay street Intercom not working, Checked Cable, re-terminated cable and connected to correct network port on F17. All tested and working correctly. Job complete
MSA-DTAG | WA4040456 | L11 staff corridor Movement in door frame/door not locking - see notes | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 11:00:00 | Pass | BRACE APPLIED TO DOOR FRAME
MSA-DTWD | WA4039872 | Various security lights on buildings not working or stuck on during day, pathway lights not working | Rockingham Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 03 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-13 16:15:00 | Fail | Attended site and signed in. Located scissor lift. Energised carpark lights to make clarify which lights are out. Placed cones around all lights out. Went or wholesaler and brought 5 x 250w mv lamps and 1 x 100w led flood. Replaced lamps and flood. 2 X lamps did not work and flood did not work. One lamps holder was bent. Bent it back and it worked. One lamps ballast was faulty. No volatge at flood cable. Could not find where cable was joined. Isolated and ran new feed to base. All lights work.
MSA-DTWD | WA4039897 | Lift 1 not responding to call button doors not opening | Perth Campus B2 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMP | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-03 10:00:00 | Pass | T4 bottom lock snagging Fixed and lift running- To be closed out at $0
MSA-DTWD | WA4039899 | E block LSK no power to combotherm | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 0 | CLOSE | 03 Mar 2021 | 2021-03-03 12:22:03 | 2021-03-03 13:45:00 | Fail | NO RESPONSE FROM BRAF SUBMITTED 6/3/21. THEREFORE INVOICE FOR WORKS TO DATE.
MSA-DTWD | WA4039953 | D block student toilet blocked drains | Balga Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-10 15:40:00 | Fail | Cleared blockage using jetter
MSA-DTWD | WA4039960 | BLD 833, Servery - Water leak above Servery | Muresk Institute | GMP-BR | Building | Ceiling (BU) | Lee Carpentry | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 15:00:00 | Pass | Repairs to leak
MSA-DTWD | WA4039967 | BLD 812, various rooms - leaks through house | Muresk Institute | GMP-BR | Building | Ceiling (BU) | Lee Carpentry | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 16:00:00 | Pass | sealed vent
MSA-DTWD | WA4039973 | Building 8, ground, 8G36 -Sparking light switch | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-16 08:30:00 | Fail | Attended site and signed in. Got access to 8g36. Checked out lights in room. Reinstated power, tested circuit, tested lights. No faults. Can not locate a fault. Everything working okay. Signed out job complete
MSA-DTWD | WA4040015 | D Block, D19 Baking Lab- Moffat Bun Divider/Rounder is jammed closed – Can’t be cleaned | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-10 12:45:00 | Fail | COMPLETED
MSA-DTWD | WA4040027 | E Block, SK1 tap on left hand side 3rd sink has little to no water pressure | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-03 15:00:00 | Pass | The FM advised to complete the job, and if reoccurs they will resubmitt job as the kitchen areas will need to be shutdown to isolate
MSA-DTWD | WA4040032 | Workshops, Mech board - no power to compressor dryer and drains, rcd keeps tripping | Clarkson Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 15:31:00 | Pass | Investigated no power to dryer and compressor. Was shown db where the main CB had tripped on the protected power chassis. Turned off all CB’s and rcds and still tripped. Inspected db and found a twin active attached to the circuit breaker. So i walked around checking for EM stop buttons. Found one in a classroom which was no longer needed as the room is now just a classroom so i blank plated it off to prevent students pressing it and killing the power. I then found one in tiling which was pressed, unlocked it with key and CB no longer trips. Checked dryer and compressor and found no power still. Investigated and found a switch on wall, turned on and water shot out so i turned back off. Storeman said other workers were working on it previously and never finished the job so pipes were no reconnected. Placed out of service tag on switch and notified facilities
MSA-DTWD | WA4040085 | U024.7 - power tripping all the time (finishing room power isolation panel) | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 08:18:00 | Pass | Inspected power issue in u24.7;.:re terminated terminals and tested power , all seems to be woekimg fine
MSA-DTWD | WA4040114 | E Block, Passage way - Ice machine in hallway not producing ice | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Ice machine (RE) | Precise Air Group | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-19 12:00:00 | Fail | Found ice maker with led indicators showing cleanrequired. Initiated cleaning mode and Ran ice machine cleaning solution through system for 90 mins. Dumpedwater and flushed 3 x as per manufacturers recommendations...Disposed of first two ice harvest asper instructions. Reassembled the system and put intonormal ice production. Harvesting full ice sheet per 25 mins. All seems ok. Suspect that duty load for such a small machine in this mess kitchen too high. Recommend installing a second machine to cope with the demand.
MSA-DTWD | WA4040137 | Faulty batteries on wireless detectors | Perth Campus B7 | GMP-BR | Equipment | Electrical Equipment (EQ) | Securex Security Systems & Services | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 12:15:00 | Pass | Replaced batteries in all PIRs as requested by the facilities staff
MSA-DTWD | WA4040166 | S Block room S009, exterior wall light is broken | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 15:31:00 | Pass | Replaced faulty external light for new LED light
MSA-DTWD | WA4040235 | G Block, Male toilet - Wall mount exhaust fan not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-05 10:45:00 | Pass | Attended site and signed in. Spoke with facilities regarding fan. Tested to find seized and not working. Disconnect and removed faulty fan. Supply and replace with new wall exhaust fan. Tested all okay. Job complete
MSA-DTWD | WA4040243 | Block 3, Fitting and Machining- Sink flow from wash up area coming up floor drain | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-03 15:00:00 | Pass | Unblocked drain full of sand
MSA-DTWD | WA4040244 | T block cafe remove the drain covers and unblock the kitchen drains. | Murdoch Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-03 16:30:00 | Pass | Unblocked bucket traps
MSA-DTWD | WA4040258 | G Block, G200 Plantroom - 6 x minor roof leaks throughout plantroom | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-18 14:00:00 | Fail | Roof inspection revealed numerous potential leaks, cleaned and re sealed with silicone. Replaced missing screws on ridge capping.
MSA-DTWD | WA4040273 | Blocked drains around Campus | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-04-12 14:00:00 | Fail | work completed CLEAR BLOCKED STORMWATERDRAINS AROUND CAMPUS
MSA-DTWD | WA4040324 | Lecture theatre - Door closers not working properly | Perth Campus B6 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-05-18 15:35:00 | Fail | Door number 605188 & L20143594S. internal lecture theatre opener. Door showing encoder & motor fault. Performed learning cycle and door re faulted. opener required replacement and Braf has been raisedBraf approved to replace failed auto swing door operator with 1 x ED100 operator with slide arm and coverReturned to site. Removed old swing operator and replaced with an Ed 100.
MSA-DTWD | WA4040326 | G Block, G230- Replace broken twin flouro with LED | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 15:06:00 | Pass | Replaced broken light fitting with new
MSA-DTWD | WA4040328 | A Block, Room A357 - Leaking roof two spots | Perth Campus B5 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 03 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-04 09:25:00 | Pass | COMPLETED
MSA-DTWD | WA4040351 | A Block, room A 216 has faulty network ports PP9-P4-1 and PP9-P4-2 | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 09:30:00 | Pass | Replaced faulty data jacks and reterminated patch panel end to rectify issue
MSA-DTWD | WA4040372 | B block BG24 RH side AC not working. Flashing Light. | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-25 16:30:00 | Fail | Found AC condenser unit PCB and rectifier have failed.Ordered parts. Picked up parts from workshop. Returned to site. Replaced failed PCB and rectifier. Removed isolation and started unit. Checked operation. All ok.
MSA-DTWD | WA4040409 | G Block, Operating theatre- Air Con not working | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-25 14:32:00 | Fail | Picked up parts from workshop. Travelled to site. Gained access to site. Replaced evaporator fan motor in AC 2 in G block rear plantroom as per BRAF. Checked operation. All ok. Cleaned up work area and disposed of rubbish.
MSA-DTWD | WA4040411 | C Block, Kitchen- roof leak | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-18 12:30:00 | Fail | Repair PVC pipe to Aircon 2 x 40mm sockets and install new dry pan to length of roofing
MSA-DTWD | WA4040418 | A Block, room A118 - broken wall ports need re locating | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 11:03:00 | Pass | Relocated and replced data points above location to prevent chair from damaging points in the future
MSA-DTWD | WA4040437 | F60 store room - Roof leak flooding light fitting | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-15 14:00:00 | Fail | Look for leak find exhaust fan and flashings needed to be re-siliconed, also small hole in roof sheet where text screw had been removed and had been poorly siliconed. Replace with new text screw in the hole and clean around the area.
MSA-DTWD | WA4040514 | B block, B2423 - air con leaking water | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 03 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-12 12:55:00 | Fail | COMPLTED JOB
MSA-DTWD | WA4040535 | Power keeps tripping in the staff room. | Bentley Campus-Block H-Ground Floor-H10 - Staff Office | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 09:00:00 | Pass | Attended site and met with cleaner. Got access to H block. Found circuit B1 tripped. Conducted testing to circuit and RCD. All okay no fault found. Reset and tested offices . All gpos working. Ran at full load and tested okay. No faults on site. Spoke with facilities and advised to replace rcd with new. Supply and replace 20amp RCD to circuit B1. Tested and ran all working. Job complete
MSA-MRWA | WA4039949 | Stairs Light fitting transformer not working, please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 03 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 06:41:00 | Pass | Replaced faulty Fluro to lvl8 staircase light
MSA-DCA | WA4040738 | Chiller 2 in fault | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 04 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 12:00:00 | Pass | Attended site. Chiller system in fault. Applied tests and checks. Investigation found circuit A to have tripped on HP lockout. Reset HP and applied tests and checks to refrigerant pressures and applicable entering and leaving condenser temps (ok). Set chiller to lead and monitored on off cycle. System operating correctly.
MSA-DCA | WA4040779 | Multiple BMS alarms | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 04 Mar 2021 | 2021-03-04 17:00:00 | 2021-03-04 11:30:00 | Pass | All alarms related to power outages over last few days. Reset Controller # 130 for AC 3, Atrium SEF 104. Reset AC 9 VSD's. Hi temperature alarms remain for AC 9 Stack. Screeb shots saved for Honeywell to investigate during RM. Found cracked pneumatic line and sealed temporarily until correct repairs can be carried out.
MSA-DCA | WA4040817 | workshop blocked workshop sink water currently overfowing into carpark | PICA-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-05 14:30:00 | Pass | Unblocked drain. Sewer line requires a rerun.
MSA-DCA | WA4041195 | BMS un responsive unable to change set point in studio under ground - see notes | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Stage Door | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 18:23:47 | 2021-03-04 16:00:00 | Pass | System back in auto operating correctly
MSA-DCA | WA4041272 | fire door thats been damaged (housing electrical unit) | Perth Cultural Centre Precinct-Cultural Centre Car Park | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Property Fire Maintenance | 1 | COMP | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 15:45:00 | Pass | Site visit to detail items for Quote to be sent for approval.
MSA-DCS | WA4040720 | Carey training house - auto boil faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 04 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 12:40:00 | Pass | Replaced inlet solenoid and element. Tested and working fine
MSA-DCS | WA4040722 | Unit 2 top landing shower taps handles broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-11 10:30:00 | Fail | Replaced tap handles
MSA-DCS | WA4040723 | Canteen - security flood light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 12:30:00 | Pass | Investigate and repair canteen security flood light
MSA-DCS | WA4040725 | Kitchen - bread slicer faulty | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 04 Mar 2021 | 2021-03-10 17:00:00 | 2021-04-28 14:30:00 | Fail | COMPLETED
MSA-DCS | WA4040726 | Unit 10 - Front door is locked, not able to unlock | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 10:38:00 | 2021-03-04 09:45:00 | Pass | Attend site and replaced lock on Unit 10 main door. Door closer also adjusted.
MSA-DCS | WA4040741 | Cleaning- Water not clearing in urinal | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-17 10:41:00 | Fail | Nill
MSA-DCS | WA4040745 | Water leak on water main. Under foot path where it branches off to Unit 6 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 11:15:44 | 2021-03-04 17:00:00 | Fail | We spoke to Joel from maintenance and head of security about possibly doing the job on a Tuesday lockdown day as it wasn’t causing any hazard and we had another outstanding job booked in for the day and so there were no prisoners walking back and forth because it was on the main pathway and to concrete when it wasnt raining , but they said they wanted it done today , so we got it all done but after we left it started raining just after we concreted
MSA-DCS | WA4040748 | Security Office - PAD 146 not operational, need to program replacement | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-04 11:47:00 | Pass | spare unit programmed, back online.
MSA-DCS | WA4040752 | Admin/Visits, Monitor Room (Control Room)- Billi Quadra filter faulty | Boronia Pre-release | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 04 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 09:10:00 | Pass | Replaced locked out filter. Checked over whole system. All ok
MSA-DCS | WA4040772 | Zone 7 & 8 external not activating | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 07:45:34 | 2021-03-04 12:00:00 | Pass | Recalibrate the perimitrax zone and fixed MW Z7 and PX Z8, job completed.
MSA-DCS | WA4040783 | Unit 3, Cell B8- Floor drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 07:50:38 | 2021-03-04 14:40:00 | Pass | Checked and inspected drain in unit 3 cell B8. floor drain was repaired yesterday .Tested drain - working fine.
MSA-DCS | WA4040795 | Unit 4 - Lunch Room Air con unit leaking water near an electrical socket. | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-04 11:58:29 | Pass | Checked over aircon,found condensate pump had failed,picked up new pump returned to site,isolated power replace pump,turned power back on and tested,all flowing ok.
MSA-DCS | WA4040806 | Unit 2 - D2 Toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 10:30:00 | Pass | Nill
MSA-DCS | WA4040818 | Unit 13, Cell A6- Taps leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-12 14:30:00 | Fail | Nill
MSA-DCS | WA4040856 | Admin stores roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-09-08 09:00:00 | Fail | Locate leak and rectify
MSA-DCS | WA4040864 | Unit 1 inside showers light fittings faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 14:30:00 | Pass | Investigate and repair unit 1 shower block lights
MSA-DCS | WA4040867 | Unable to reset fire alarm | Maddington (South East Metro) | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 13:23:27 | 2021-03-04 11:36:00 | Pass | Attended site, checked keypad to find duress zone disarmed and unable to re arm due to zone 48 active.Checked Gallagher software, zone 48 is duress reception.Found 4 duress buttons in reception and one still active. Reset and armed System working normally
MSA-DCS | WA4040873 | Bakery, Rotel fuse - Rotel oven had smoke coming from fuse box. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 13:28:32 | 2021-03-10 13:45:00 | Fail | COMPLETED
MSA-DCS | WA4040912 | Unit 3, C Wing left side- Toilets blocked main line | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 13:55:24 | 2021-03-04 13:10:00 | Pass | Cleared blocked main drain in Unit 3 C wing LHS.
MSA-DCS | WA4040913 | Vegetable Preparation - Powerpoints across prep areas are not working. - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 13:55:09 | 2021-03-04 15:00:00 | Fail | Investigate and repair gpo’s not working in vege prep
MSA-DCS | WA4040935 | Unit 14 - Control Room Air conditioner keeps cutting out and light flashes, - see notes | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-08 10:13:08 | Pass | Arrived on site and signed in tools,checked over unit still no current fault codes present and unit still running ok.
MSA-DCS | WA4040944 | Lenard, B07 - smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 15:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA4040946 | Turner, C wing, plant - Pump 1 constantly trips RCD | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 09:30:00 | Pass | Circulation pump OOO - picked up new and replaced
MSA-DCS | WA4040951 | Lenard, B07 - light switch broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 12:00:00 | Pass | Replace broken light switch Lenard B07
MSA-DCS | WA4040959 | Yeeda, C wing - RCD faulty (wont trip) GF essential W1 | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 13:00:00 | Pass | Light full of water - Disconnect , return and replace light
MSA-DCS | WA4040973 | Unit 15, Ventilation systems - Mech Fault, AHU-15-01 Motor Failure | Casuarina Prison | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 10:44:31 | 2021-03-05 10:37:45 | Pass | Job closed off as instructed by Graham Murphy.
MSA-DCS | WA4040985 | Security office & video links office - security camera feed not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 15:37:00 | Pass | Job complete
MSA-DCS | WA4040997 | Unit 2, Cell C2- Push tap not mounted flush on wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 13:30:00 | Pass | Installed button flush, flush against the wall
MSA-DCS | WA4041024 | Unit 4, D wing cleaning closet - Tap over the sink is leaking a substantial amount | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 11:30:00 | Pass | Nill
MSA-DCS | WA4041034 | Unit 13 - D12 shower glass leak | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-08 11:30:00 | Pass | SHOWER SCREEN RE SEALED
MSA-DCS | WA4041056 | Bakery Bread mixer Sotorvia has stopped working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 12:02:18 | 2021-03-04 13:45:00 | Pass | COMPLETED
MSA-DCS | WA4041061 | kitchen exhaust fans keeps showing faults - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 12:08:54 | 2021-03-08 15:43:31 | Fail | Checked over exhaust,still running and amp draw ok,spoke with staff who informed me that they had no problems with it over the weekend.
MSA-DCS | WA4041136 | Comms room server and maintenance terminal monitor failed, keyboard and mouse intermittently working | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-05-14 16:00:00 | Fail | Modified sliding rack in workshop to make it suitable for 612mm depth rack. Back to site to install the sliding rack and two RAPOO K2600 wireless keyboard for the new sliding racks. Tested all ok after work.
MSA-DCS | WA4041165 | swimming pool, flat valve in pool sump faulty | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 13:50:48 | 2021-03-05 13:00:00 | Pass | Swimming pool, foot valve in pool sump faulty. Check pump, remove faulty foot valve & source replacement. Return to pool install new parts. Prime pumps & reset flow. Report to staff.
MSA-DCS | WA4041192 | SOP, A12 - Toilet keeps leaking into bowl. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-12 12:30:00 | Fail | nil
MSA-DCS | WA4041193 | Unit 14, Cell B13- shower & sink not draining | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-12 12:36:00 | Fail | Nilll
MSA-DCS | WA4041194 | Unit 2, court yard - outside tap missing handle | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 11:04:00 | Pass | Nill
MSA-DCS | WA4041197 | Unit 2, Entry door stiff to open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-05 12:00:00 | Pass | Remove jammed hinges, repair and lubricate, re install hinges with locking washers.
MSA-DCS | WA4041201 | Unit 7, Cell H7- Main lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 14:28:39 | 2021-03-04 16:15:00 | Pass | Attend site to look at Cell H7 main lock. Lock was removed and disassembled to inspect. Lock serviced and replaced worn out bolt throw. Lock was reassembled and installed. Checked, all functional.
MSA-DCS | WA4041213 | Security Area - Office Security Indigo system unable to show Camera (443) U7-SC-Bwing -262 | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 18:37:33 | 2021-03-04 16:30:00 | Pass | Reset network encoder in self care office unit. Camera came back online
MSA-DCS | WA4041222 | Official visits Next to the Control Pod in the Hallway roof leak | Melaleuca Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Schlager Construction Group | 1 | COMPFIN | 04 Mar 2021 | 2021-03-05 14:50:38 | 2021-03-05 11:30:00 | Pass | Carried out inspection to ceiling space to identity where water leak was coming from.Roof leak was due to leaking air conditioning unit pipe work.Advised client to contact air conditioning contractor to carry out repairs.
MSA-DCS | WA4041223 | U2 A6 Door dragging on the floor & has broken the tiles in the Doorway | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | COMPFIN | 04 Mar 2021 | 2021-03-05 14:54:47 | 2021-03-05 10:00:00 | Pass | Replaced all the bolts on the cell door hinges, re hung door to stop it jamming.
MSA-DCS | WA4041228 | Stores, Staff toilet - Basin is leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 10:40:00 | Pass | Replaced basin taps and mini stops to toilet basin.
MSA-DCS | WA4041229 | Unit 2, Cell B1- Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-11 13:20:00 | Fail | Replace leaking basin spindles
MSA-DCS | WA4041233 | Unit 1, D16 - GPO tripping power | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 10:30:00 | Pass | Replaced shorted out power points with new ones and tested ok.
MSA-DCS | WA4041234 | Unit 2 B11 Prisoners Door Lock Latch Mech Broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 11:30:00 | Pass | Attend site. Door lock latch mechanism is broken. Replace faulty parts, service lock and key barrel.
MSA-DCS | WA4041288 | MDAS alarm system has communication fail | Wooroloo Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 21:02:18 | 2021-04-13 15:58:00 | Fail | 90242321Job Complete
MSA-DCS | WA4041312 | Melaleuca Prison - Unit 1 - Wing A & B - Cameras are out in the pod. | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 22:24:01 | 2021-03-04 21:30:00 | Pass | Cameras found to be online though monitor display off. Password obtained and reset. Tested ok.
MSA-DCS | WA4041315 | Gate control room - monitors won't reset and won't turn back on again. | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 15:53:00 | Pass | Called site resolved issue site will recall if issue persists
MSA-DFES | WA4040847 | workshop office light circuit has failed/faulted - No lights in maintenance offices. (see notes) | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 13:00:00 | Pass | Arrived on siteInvestigated issue with Supervisor. We narrowed down the issue to the circuit tripping when the sensor is activated. The sensor was bypassed and everything is holding. We are leaving this solution until renovations in the area have been completed.
MSA-DFES | WA4040994 | main workshop ground Loose dyna-bolts securing an air hose reel to the wall in Bay 1 requires repair | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Steel Work (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 13:45:00 | Pass | Refixed hose reel back to wall again
MSA-DFES | WA4041091 | Main entry gate - will not shut, goes across then retracts back to open | O'Connor Fleet Storage | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 16:00:00 | Pass | Complete
MSA-DFES | WA4041155 | Dorm 1 and dorm 2 bathrooms 2 x light globes need replaced in the bathrooms of dorm 1 and 2-notes | CFRS Malaga | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 14:15:00 | Pass | COMPLETED
MSA-DFES | WA4041196 | ground cylinder room Found aircon cover was up and no filter - see notes | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 08:30:00 | Pass | Investigated AC in cylinder room. Filters are fitted.
MSA-DFES | WA4041221 | 1st floor, communications centre- door striker has fallen off | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 18:49:59 | 2021-03-04 16:30:00 | Pass | Door striker was resecured back on to door frame.
MSA-DFES | WA4041248 | Foyer, security swipe - Swipe entry in foyer that leads into meeting rooms not working | Armadale Regional Office | GMP-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 11:30:00 | Pass | Reset retested ok.
MSA-DFES | WA4041261 | Frint roller door - one of the rollers has come off | CFRS Joondalup | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 15:30:00 | Pass | Attended Joondalup Fire Station checked sectional door # 2 and found hinge broken. Made temporary repair to the hinge. The hinge requires replacement. Please see attached service reports, BRAF and quotation.10.3.21-- Please see attached completion photos and service report of new roller installation.Please note station crew were not available to sign off signature slipThank you
MSA-DTAG | WA4040828 | Lvl 4, Plant Room - Water leaking from cooling tower | Supreme Court | GMP-BR-HO | Air Conditioning | Cooling Tower (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 10:00:00 | Pass | Return to site and check cooling tower. Found floor dry and no leaks from tower. Will check again next maintenance.
MSA-DTAG | WA4040839 | Lift 3 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 14:22:00 | Pass | Lift on JRVP tested operation, unable to fault. Will let run and return to check.To be closed out at $0
MSA-DTAG | WA4040950 | L3 court 33 air con not working | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 14:30:00 | Pass | Attend site. Court 33 AC not cooling. Access BMS on level 6 and check AC operation. Found level 3 and 5 to be offline. Access level 3 and carry out power cycle of controller. Allow time for controller to reboot. Found level 3 and 5 to come back online. Access level 5 and check temps accross floor, found to be normal. Access level 3 and check temps accross floor, found to be normal. Wait for access into court 33 and check operation and temps of court. Court temp 22.5 degrees and working as normal. No other faults found.
MSA-DTAG | WA4041069 | ground front Revolving door makes a screeching sounds when in use. | Central Law Courts | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 16:24:00 | Pass | Inspected door and found bottom bearing noisy lubricated bottom bearing and tested all OK at time of test
MSA-DTAG | WA4041199 | Basement, Custody cell 02 - The water fountain in cell 2 is not stopping, constantly running | Perth Children's Court | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-22 08:45:00 | Fail | Replaced bubbler insert and tested. All working fine. A40184199P
MSA-DTAG | WA4041205 | Court 6 gate from Bench to Courtroom needs re-fixing as hinge dropped and does not close without lif | Perth Children's Court | GMP-BR-HO | Building | General Building (BU) | Midolo Building Services | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 14:15:00 | Pass | NEW HINGE FITTED TO GATE
MSA-DTAG | WA4041210 | Electrical cupboard outside Court 4 (secure passage) does not open/close without force or screwdrive | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 12:25:00 | Pass | Work completed
MSA-DTWD | WA4040801 | North East perimeter fence Jennalup Street, adjacent to double gates is damaged/cut | Murdoch Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 15:45:00 | Pass | Panel of fencing was removed and replaced with new panel of black vinyl chainmesh fencing.
MSA-DTWD | WA4040805 | Science Block, Corridor between rooms S6.2 & S6.3 - Fridge 1 not running at correct temperature | Murdoch Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-19 13:50:00 | Fail | Found the compressor siezed, unit on R22 quote to replace sent off.26/3/21: New units ordered to replace , awaiting on parts.19/4/21: New fridge installed.
MSA-DTWD | WA4040807 | Science Block, Corridor between rooms S6.2 & S6.3 - Fridge 2 not running at correct temperature | Murdoch Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-19 13:47:00 | Fail | Found the system only getting down to 6deg C . Checked the operation and the gas charge is low, put R22 in the temperature came down to 4 deg , this a old Arcus two door glass fridge , the vaccum seal in the doors had gone so a lot of cold air transfers through the glass . Recommend replacing the fridges as they are on R22 and no leak could be found .26/3/21: New fridge been ordered to replace the old one.19/4/21: New fridge installed.
MSA-DTWD | WA4040827 | G block ladies staff toilet not flushing correctly. Ladies staff toilet G block - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 16:30:00 | Pass | repaired cistern and pan adaptor
MSA-DTWD | WA4040831 | L1 no chillers running in the plant room | Perth Campus B1 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-09 15:17:00 | Fail | Travelled to site, signed in as required and accessed chiller plant. downloaded faulty history and found multiple Axial Over current faults. Carried out bearing calibration and found values to be outside on manufacturer recommendations. tested bearing sensor feed throughs and found values to be also reading higher than manufacturer recommendations. Swapped out bearing sensor cables and carried out bearing calibrations. Found readings to be within the correct range. Returned to chiller service and monitored operation. Found compressor to stage up and run normally. Tidied up workspace and removed rubbish from site.
MSA-DTWD | WA4040843 | Plant room No1 chiller has stopped working | Leederville Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 13:00:00 | Pass | Accessed site completed relevant sign in procedures and covid safe wa requirements, accessed chiller 1 found low evaporator flow fault to be present , and a12 overcurrent fault present on vsd ,isolated and removed chiller water pump 1 guards covers and checked shafter operation , all ok , tested components all ok , rectified fault at chiller and vsd , chiller 1 running , all ok
MSA-DTWD | WA4040850 | Chiller 1 has faulted and will not start | East Perth Campus | GMP-BR | Refrigeration | Chiller (RE) | CARRIER AUSTRALIA PTY LTD | 0 | CLOSE | 04 Mar 2021 | 2021-03-04 13:09:34 | 2021-03-04 13:00:00 | Pass | Repairs to chiller
MSA-DTWD | WA4040865 | G Block room G27 - Roof leak along gutter/window line | Rockingham Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-24 14:00:00 | Fail | Sign into job check ACM register ,Set up work area with exclusion zones and extension ladder tied off. Remove rusty section of box gutter, replace with new, reseal around all joins resecure capping down with new screws, perform site cleanup removal barricades and ladders. And get the job signed off. Return to yard with rubbish.
MSA-DTWD | WA4040870 | Both entry locks broken | Perth Campus B3 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-05 11:40:00 | Pass | Repair 2 x locks
MSA-DTWD | WA4040878 | L block Lift not working | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-04 12:42:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA4040884 | L3 Female toilet next to drinking fountain damage vinyl | Perth Campus B6 | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-12 12:30:00 | Fail | Section of flooring was removed and replaced
MSA-DTWD | WA4040907 | block 7 ground cafeteria Exhaust fan switch for dishwasher loose in housing | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 16:15:00 | Pass | Attended site and signed in. Located cafeteria fan switch next to dishwasher. Supply and replace cracked switch with new. Found main exhaust fan switch broken also. Supply and replace with new switch. Tested all okay. Job complete
MSA-DTWD | WA4040919 | Tower, ground floor, east - Split system air conditioner not working | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-05-07 07:46:00 | Fail | Installed 5kw Wall Split
MSA-DTWD | WA4040932 | Plant, nitrogen generator - not running | Munster Campus (ACEPT) | GMP-BR | Equipment | Compressors, Generators (EQ) | Nessco Pressure Systems | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-05-14 10:50:00 | Fail | Prepare and install control valves to nitrogen generator
MSA-DTWD | WA4040971 | S block science S1 4.5 KG ABE Powder Type extinguisher has been partially discharged. - see notes | Murdoch Campus | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 13:30:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochWork Order Number: WA4040971 Priority #: 2Call out Date: 04/03/2021Target finish: 09/03/2021WO# Value: $1000.00Original information: S block science S1 4.5 KG ABE Powder Type extinguisher has been partially discharged. - see notes --> Replace or re-tag if considered fit for continued service. (05/03/2021) - Work NoteWorks Carried Out:Replaced 1x4.5kg ABE ext inside room s1
MSA-DTWD | WA4041014 | Outside BLD 832 - Faulty Storm water Drain | Muresk Institute | GMP-BR | Plumbing & Drainage | Drainage (PD) | Lane's Plumbing | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-04 15:30:00 | Pass | Repairs to storm drain
MSA-DTWD | WA4041055 | D Block, classroom D26 - Light switch broken | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-15 10:00:00 | Fail | Attended site and signed in. Located class D26. Got access to room. Isolated power. Disconnect and removed faulty light switch. Supply and replace with new switch. Tested all okay. Signed out. Job complete
MSA-DTWD | WA4041134 | U Block, Room U013- Repair damaged brick wall of U013 Storeroom | Balga Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-04-21 15:30:00 | Fail | work completed as per signature slip
MSA-DTWD | WA4041146 | Centre courtyard - Pavers ruptured in courtyard outside Student Services | Mount Lawley Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 04 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-19 09:30:00 | Fail | completed as per signature slip
MSA-DTWD | WA4041243 | Block 7 ground cafeteria Roof mounted evaporative air conditioner not working in kitchen. | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 11:00:00 | Pass | Found factory wiring from motor to isolator burnt out. Picked up new cable. Rewired motor to isolator. Removed isolation and started unit. Checked amp draws and full operation and condition of unit. All ok. Cleaned up work area and completed paperwork.
MSA-DTWD | WA4041280 | G block - possible BMS fault | Bentley Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 1 | COMPFIN | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 14:00:00 | Pass | Repairs
MSA-MRWA | WA4041219 | Server room, crack unit comunications fault | Don Aitken Centre MRWA Head Office-Main Building-Basement | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 04 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 11:30:00 | Pass | Fault cleared
MSA-DCA | WA4041581 | Function Venue lobby door - handles are loose and rattles and door closer faulty | Maritime Museum Victoria Quay-Main Building-First Floor-Foyer | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-08 15:45:00 | Pass | Resecured glass door handles.
MSA-DCA | WA4041893 | urinal system not flushing | PICA-Main Building-Level 2-Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 15:08:00 | Pass | No issues with the urinal
MSA-DCA | WA4041897 | male urinal constantly running | The Blue Room-Main Building-Ground Floor-Male Toilet - Access off Kitchen | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 16:30:00 | Pass | Replaced leaking outlet washer and asjusted water flow
MSA-DCA | WA4041930 | office RAC unit is not working at all. Please inspect | Shipwreck Galleries-Main Building-Level 1-Maritime Archaeology | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 16:30:00 | Pass | Attended site. RAC system not operating correctly. Applied tests and checks. Investigation found job title incorrect (split system smelly and not working properly in SWG main building.). Defective RAC located in admin building upstairs (DAS to be submitted for defective RAC). Applied tests and checks to split system not working in archive office. Investigation found batteries in remote controller defective. Removed and replaced batteries. Service and sanitized system and tested operation. System operating correctly.
MSA-DCA | WA4041968 | admin office space RAC unit is working intermittently. Please inspect | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-15 10:30:00 | Fail | Attended site RAC system not operating correctly. Applied tests and checks to find control settings not set correctly. Set controller to 22c cooling hi fan. Tested operation and checked TDs. System operating correctly.
MSA-DCS | WA4041404 | Unit 4, B Wing showers- Shower door damaged | Hakea Prison | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 3 | CLOSE | 05 Mar 2021 | 2021-03-11 17:00:00 | 2021-04-14 14:00:00 | Fail | SHOWER DOOR RE HUNG - NEW HINGES
MSA-DCS | WA4041406 | Unit 3, C Wing shower- Shower door damaged | Hakea Prison | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo Building Services | 3 | CLOSE | 05 Mar 2021 | 2021-03-11 17:00:00 | 2021-04-14 12:15:00 | Fail | DUPLICATE WORK ORDER -WORK COMPLETED ON WA4112481
MSA-DCS | WA4041409 | Assist ARA fire in eliminating cause of fibre issue in Unit 3 | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-11 09:15:00 | Pass | System was restored upon arrival. Gave ARA a better understanding on how the fire is fibered around site so fault finding is easier in the future
MSA-DCS | WA4041418 | CCTV Monitors are down in gate control room - cannot reset | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 10:48:43 | 2021-03-05 09:15:00 | Pass | Centre CCTV monitor images reset check of logs no cause evident. System test ok.
MSA-DCS | WA4041445 | Reset Centre- light in toilet not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-05 15:00:00 | Pass | Investigate and repair light in reset centre toilet
MSA-DCS | WA4041447 | Unit 2, Cell A4- Prisoner main light switch hanging out wall. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 07:29:41 | 2021-03-05 13:30:00 | Pass | Investigate and repair unit 2 cell A4 light switch
MSA-DCS | WA4041448 | Unit 2, Cell D12- Connection from basin to trap leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 12:30:00 | Pass | Nill
MSA-DCS | WA4041452 | Investigate 4 hot water units that are too hot and cannot be adjusted as per Karl Fowler | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 05 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-11 13:15:00 | Pass | Asset capture, site visit completed.
MSA-DCS | WA4041457 | 2x module faults on the fire panel | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 11:41:16 | 2021-03-05 11:36:00 | Pass | 5/3/21Upon arrival only 1 fault present.Module fault on node 7 (medical centre), sourced new card from office and directly replaced, panel back to normal.
MSA-DCS | WA4041458 | INF (10), Treatment Room- Air Con not blowing cold air | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 05 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 11:14:11 | Pass | Checked over unit gas pressures ok,unit was set on cooling and running ok,someone may have set on heat.
MSA-DCS | WA4041459 | Front Gate- Door between frontgate and key control is not unlocking electronically | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 11:46:00 | 2021-03-05 09:00:00 | Pass | No power to door strike. Power supply and fuses tested ok. Traced fault to relay in the access control rack. Repaired and tested ok.
MSA-DCS | WA4041464 | Cleaning, workshop- 5x ceiling fans not working (EWP required) | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-31 15:00:00 | Fail | Replaced fans
MSA-DCS | WA4041497 | Unit 14, Cell A9- Hot water tap will not turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 08:21:32 | 2021-03-05 13:30:00 | Pass | Nill
MSA-DCS | WA4041514 | P35 tamper alarm - SEME on site | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 08:35:56 | 2021-03-05 10:45:00 | Pass | Broken resistor discovered replaced retested ok.
MSA-DCS | WA4041522 | Lvl 2- Door is not closing correctly and making noise | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | COMPFIN | 05 Mar 2021 | 2021-03-06 08:44:42 | 2021-03-05 15:00:00 | Pass | Removed emergency escape door and planed the bottom to stop it jamming on rubber carpet strip.
MSA-DCS | WA4041523 | Unit 2, Cell D7 toilet/sink system is leaking out on to the floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 08:42:12 | 2021-03-05 23:42:00 | Pass | Nill
MSA-DCS | WA4041533 | Kitchen - Fridge door broken off track | Wandoo Rehabilitation Facility | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 12:51:45 | 2021-03-05 14:30:00 | Fail | New top rollers and 1 x new roller bolt installed. Adjusted limit switch and door angles, checked door seals.
MSA-DCS | WA4041543 | kitchen slicer damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 08:57:05 | 2021-03-05 12:00:00 | Pass | 05/03/21Sign in Check slicer Found prisoners have been putting cooking oil on slide and has solidified. Clean slide and lubricate Test unit ok.
MSA-DCS | WA4041568 | SB1 (Between U15-U16) - Room 3 Lock on Health Consult Room 3 Faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 14:00:00 | Pass | Keys are pulling out in incorrect position, require parts.Obtain barrel and install with 90 degree X cam.
MSA-DCS | WA4041586 | Retic, Sprinkler top is missing | Warminda Hostel | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 09:37:15 | 2021-03-12 07:30:00 | Fail | Isolated problem and returned with parts to fix correctly
MSA-DCS | WA4041587 | Driveway has a pothole | Warminda Hostel | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 09:39:00 | 2021-03-05 15:00:00 | Pass | 05/03/21Repair and fill potholes on driveway
MSA-DCS | WA4041595 | Kitchen - sink has split pipe | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-05 12:06:00 | Pass | Replaced kitchen sink taps and installed mini stops .
MSA-DCS | WA4041597 | Unit 5 - Control Room air con leaking and blowing cold air | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-04-07 14:35:00 | Fail | New 5Kw Daikin system installed & commissioned
MSA-DCS | WA4041601 | Visits center - strip search room - roof leaking, ceiling water damaged | Wooroloo Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 09:55:25 | 2021-03-26 10:00:00 | Fail | CEILING DAMAGE REPAIRED & PAINTED
MSA-DCS | WA4041604 | Admin building, next to phone box - gutters have come down and rusted out | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Guttering (RF) | Midolo Building Services | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 09:57:13 | 2021-09-24 12:00:00 | Fail | Re-secured gutters
MSA-DCS | WA4041617 | Unit 6, D wing, shower pressure is reduced by about 50% | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-15 13:20:00 | Fail | Nill
MSA-DCS | WA4041678 | Unit 4, A Wing Cleaning closet & laundry - lights are not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 08:30:00 | Pass | Investigate and repair unit 4 A wing cleaning closet light
MSA-DCS | WA4041735 | Education Office, Deputy principle office- Light switch faulty | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 08:30:00 | Pass | Replace broken light switch EDU Office
MSA-DCS | WA4041736 | Security - multiple lights out & buzzing | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 09:00:00 | Pass | Repaired security lights
MSA-DCS | WA4041738 | Unit 2, Control Room - Carpet tiles damaged and dangerous in control room | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-04-20 11:15:00 | Fail | DAMAGED CARPET TILES LIFTED & REPLACED WITH NEW
MSA-DCS | WA4041743 | Unit 13, Cell C07- Shower glass leaks (bed side getting wet) | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-08 13:00:00 | Pass | SHOWER SCREEN RE SEALED
MSA-DCS | WA4041764 | Kitchen - all the floor drains are blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 15:59:40 | 2021-03-05 13:25:00 | Pass | On arrival the blockage has already cleared itself.Test all drains working fine
MSA-DCS | WA4041786 | Unit 9, C8 - lock broken, door not opening | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 12:10:31 | 2021-03-08 14:00:00 | Fail | Onsite. Lock on door to had to be drilled off due to broken/jammed latch. There was a wait time of 1 hour due to med's being done at time of repair. Re-attend site on 08/03 to install new lock.
MSA-DCS | WA4041790 | Unit 9, C2 0 tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 12:15:30 | 2021-03-05 15:10:00 | Pass | Replaced spindles to basin taps and cleaned blocked aerator.
MSA-DCS | WA4041797 | Unit 9, A/B wing - lino lifting in wing by office | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-08 11:30:00 | Pass | damaged sections of vinyl replaced - job started 18-02-2021- completed 19-02-2021
MSA-DCS | WA4041798 | Visits / Non Contact Room Alarm malfunctioning, constantly going off. | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 12:20:04 | 2021-03-05 14:25:00 | Pass | Tested system found no fault no fault on arrival
MSA-DCS | WA4041813 | Unit 9 staff room Boiling Water Unit not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 12:26:15 | 2021-03-05 17:55:00 | Pass | Replaced faulty hot pump. Unit not in very good condition. If further issues occur highly recommend replacement.
MSA-DCS | WA4041815 | Official visits Outside Control Pod Passage - Air Con Leaking Water in Ceiling | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 12:32:52 | 2021-04-06 08:30:00 | Fail | Completed quoted work , insulated duct work
MSA-DCS | WA4041827 | Kitchen - Bakers oven rack not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 12:49:13 | 2021-03-05 16:30:00 | Pass | COMPLETED
MSA-DCS | WA4041847 | video link - holding cell roof hatch locks - inspected and check integrity | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 17:15:33 | 2021-03-12 07:30:00 | Fail | Attend site. Inspect roof hatch lock. Tested latch and lock, could not fault. No issue found. Reported findings to Chris in Security. Recommend Survey to be conducted on hatch. Re-attend site, conducted surveys on all hatches with findings submitted through to DOJ. Delay in completing job as access could only be granted during specific times.
MSA-DCS | WA4041848 | PE beams 3 and 4 in the perimeter activated cannot process alarm | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-06 13:16:14 | 2021-03-05 17:00:00 | Pass | Traced and tested 3 x PE BEAMS and found the bottom PE beam is faulty and once connected it will unseal the circuit. Bypassed as required and tested all ok confirmed by control room operator. NOTE: PULNIX PB-IN- 100HF is needed for replacement24/3/21 Replaced IR bEAM, Calibrate & align, tested ok . job complete.
MSA-DCS | WA4042002 | unit 1 B30 and 31 no power | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 19:26:08 | 2021-03-05 18:00:00 | Pass | Unable to reconnect power as the circuit is feed from the construction site in nearby pod and has been isolated by another contractor
MSA-DCS | WA4042039 | Control room-EBI system for the screen has disappeared | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 21:02:35 | 2021-03-05 19:30:00 | Pass | Attended site checked and found Gallagher/Indigovision workstation in Control room is frozen and showing blue screen. Located the computer in equipment room. Reboot computer and bring all services back online.
MSA-DFES | WA4041420 | Engine Room- rear engine room door for light tanker will not close | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 05 Mar 2021 | 2021-03-05 17:00:00 | 2021-03-05 17:30:00 | Fail | Attended Claremont Fire Statin on p1 Call out from report of rear engine room door not closing. The attending technician found that the door was jamming due to inertia . the motor was free and door was operating correctly. All motors have been previously recommended to be replaced.Thank you
MSA-DFES | WA4041579 | BMS lost comms to MSSB1-1 | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-06-24 14:40:00 | Fail | Installed new nce controller and split comms bus to prevent bms controller from faulting due to running at limit.
MSA-DFES | WA4041964 | Server room air con leaking quite badly into room with computers | CFRS Wangara | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 05 Mar 2021 | 2021-03-05 18:46:17 | 2021-03-06 08:00:00 | Fail | Replaced condensate pump
MSA-DTAG | WA4041535 | Ant and Cockroach problem throughout the building | Rockingham Justice Complex | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-09 11:45:00 | Pass | .
MSA-DTAG | WA4041559 | Duress alarm in Court 1 is going off from about 3pm. No one in the Courtroom | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 14:45:00 | Pass | Inspected termination of both duress buttons in courtroom 1, visually in good condition. Replaced both duress buttons with dual-press duress buttons, tested and working correctly. Had to wait for Stuart to return from lunch break. Left phone number with Stuart if issue has not been rectified with the replacements.
MSA-DTAG | WA4041657 | PA system issues - please see notes | Joondalup Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-09 09:45:00 | Pass | - Reboot Main PA unit due to " waiting area no signal". - Replaced Cat6 lead of console to wall. Check all connection ok. Tested PA signal in waiting area ok.
MSA-DTAG | WA4041685 | Door to L10.13 on the right hand side when entering is unlocking but the left hand side isn't | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-08 14:00:00 | Pass | Removed power to lock and reset drop bolt, retested and all tested and working correctly. Job complete
MSA-DTAG | WA4041833 | Lvl 6- A/C temperature indicator fault in BMS system | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-23 12:00:00 | Fail | Attend site with icon logicAssist in installation of static pressure sensor AHU DD level 6. Commission operation, working ok.
MSA-DTWD | WA4041472 | F Block, FG23 Workshop- 2x Broken E stops | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 05 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 15:15:00 | Pass | Attended site and signed in. Got keys from facilities. Located faulty e stop buttons. Disconnect and removed faulty buttons and enclosures. Supply and replace with new emergency buttons, installed protection shroud to e stops. Tested all okay. Job complete
MSA-DTWD | WA4041512 | L4 Plant Room- multiple leaks in plant room roof | Perth Campus B6 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-09 15:00:00 | Pass | COMPLETED
MSA-DTWD | WA4041515 | L2 ladies staff toilet- hot water taps running very slowly. | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 12:30:00 | Pass | Fixed hot water issues
MSA-DTWD | WA4041596 | C Block, Room C116- broken air con switch | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-08 14:00:00 | Pass | Attended site signed in and investigated issue with wall sensor inside room c116, found sensor switch to be faulty, picked up new switch from supplier,reattended site and fitted, tested and left all operational
MSA-DTWD | WA4041611 | Grounds numerous walkway lights not working between all buildings | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 15:06:00 | Pass | Replaced all faulty walkway lights and some faulty bunker lights. Found issue with 3 selector switch in board, replaced for new
MSA-DTWD | WA4041627 | Woodworking area - Replace 4 off faulty Hi Bay lights | Clarkson Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 10:30:00 | Pass | Replace 4x old high Bay lights with new led high Bay lights.Replace 1x led high Bay with new led high Bay - no charge for this
MSA-DTWD | WA4041632 | Ground, building 1, main entrance - right hand side auto door not working | Thornlie Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 15:21:00 | Pass | Door IP number is 1007545Programmed number is A403131067LH door belt bracket clip came loose and fell off.Door leaf disconnected from belt.Refitted the belt with the door and secured properly.Door is back into operational. Cleaned track, sensors are all working properly.
MSA-DTWD | WA4041638 | tower block main office area fill holes and paint | West One Services | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 13:00:00 | Pass | Attend site fill and paint holes as requested
MSA-DTWD | WA4041642 | Block 11, Component store - 9 LED lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-24 15:30:00 | Fail | Attended site , signed in, located block 11 storage shed , completed jsa, se5 up work area, isolated lighting circuit, replaced 11 remaining drivers as per list received from Dan , re energised circuit, all lighting working as intended, cleaned up work area, completed paperwork, signed out *** job complete***
MSA-DTWD | WA4041672 | block 3 ground Fitting and Machining Water leaking into washroom from ceiling | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-04-16 12:30:00 | Fail | Cleaned and re sealed join with silicone and tested floor drain all goodConfirmation leak reseal has worked
MSA-DTWD | WA4041740 | E block E4 locker faulty light switch | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 13:46:00 | Pass | Replaced light switch and tubes E4
MSA-DTWD | WA4041748 | E block E74 kitchen Damaged tapware at stations 8 and 20 | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 14:26:00 | Pass | Repaired one tap outletReplaced one tap outlet Installed a new locking nut on tap handle Replaced an outlet washer in cistern Replaced jumper valves on lecturers tap in E74
MSA-DTWD | WA4041762 | M Block Carpark, Jarrah Road boundary Hanging tree branch over car bays | Bentley Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 07:15:00 | Pass | tree removed
MSA-DTWD | WA4041871 | A block Sink in Café Kitchen blocked. | Carlisle Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 05 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-05 16:00:00 | Pass | Unblocked Sink
MSA-DTWD | WA4041874 | kitchen - tap leaks outside sink when turned on | Perth Campus B3 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 05 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 12:30:00 | Pass | Fix tap
MSA-DTWD | WA4041910 | H Block Electronics workshop Replace five broken Electronic w/s keys, (B13, F30, 5, 239, RED/RED | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 15:15:00 | Pass | repairs to lock
MSA-DTWD | WA4041981 | B block, B2428 - Air con leaking condensation | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 13:15:00 | Pass | Found condensate water running down refrigerant pipe from condenser unit on roof. Found insulation loose on pipes and water able to run down pipe, soaking the insulation and leaking at joint at indoor unit. Sealed insulation at condenser unit and tightened insulation at indoor unit. Leak appears to have ceased. Cleaned up work area and disposed of rubbish. Completed paperwork and logged off job.
MSA-DTWD | WA4041986 | E block external valve pit - Faulty water valve. | Carlisle Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 11:30:00 | Pass | Fix leak and install new valve on branch to fire hose reel
MSA-DCS | WA4042060 | Gate 4 and 5 alarm is not activated, when being opened | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Mar 2021 | 2021-03-06 10:11:36 | 2021-03-08 14:00:00 | Fail | Replaced reed in pit 23 and tested all ok confirmed by control room operator. Took some time locate the correct pit with escort guard
MSA-DCS | WA4042063 | Water drainage in cleaners room C wing -Blocked | Casuarina Prison-Prisoner Accommodation Unit 5 | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Mar 2021 | 2021-03-06 11:06:56 | 2021-03-06 11:00:00 | Pass | Used drain machine to clear silt in line
MSA-DCS | WA4042099 | Banksia Hill control room camera has no pic 25,30,37,45,65,66,67,115 & 141 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-15 15:30:00 | Fail | Camera 65, 66, 67:still visible and recording on DVM. PTZs 25, 30, 115: cameras are being upgraded by SEMECamera 141: ok after restarting and reconfiguring monitor setup on Indigo workstation in ISUCamera 37: ok after restarting TX fiber modem Camera 145: ok after restarting camera PSU
MSA-DCS | WA4042100 | Cell MA & MB- CCU 1 ,2 and two other cameras are not working | Bandyup Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Mar 2021 | 2021-03-06 16:17:10 | 2021-03-10 10:15:00 | Fail | Get new power supply and modified to compatible with the VIDEOART COLOR QUAD. Tested it ok in workshop. Attended site to replace the faulty power supply and tested all ok after replacement.
MSA-DCS | WA4042109 | UNIT 4-J BLOCK-Fluro light is very bright, smell of a burning smell coming from light. | Bandyup Prison-Entry Building | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 06 Mar 2021 | 2021-03-06 17:00:00 | 2021-03-06 17:00:00 | Pass | Removed faulty light fitting
MSA-DCS | WA4042113 | West Kimberley Regional Prison - Front main gate - Sallyport is not moving up and down. | West Kimberley Regional Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 1 | CLOSE | 06 Mar 2021 | 2021-03-07 15:24:29 | 2021-03-07 10:00:00 | Pass | 07/03/21Clean anti-ram barrier.Apply grease.Check hydraulic pressures.Ram is operating again, however will require extra work at the next routine maintenenance.Note - no failure reporting section availabe to complete in promap
MSA-DCS | WA4042120 | Perimeter alarm B2 not activating and G2 constantly activating, won't reset | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Mar 2021 | 2021-03-06 22:19:12 | 2021-03-06 22:15:00 | Pass | Zone G2 MW. Attended zone tested MW at external test point. No voltage showing. Removed cover, when test Meter probe touched input power terminal, voltage on at test point. Checked termination and pcd connections all appeared in order. Replaced cover and walk-tedted zone. MW alarmed correctly. Zone B2 PTX. Set log running on maintenance terminal and attended zone. Walk-tested in zig-zag pattern with 4 passes over zone. Returned to equip room to check log. Noted on log, first pass did not activated alarm threshold, where subsequent passes did. Adjusted threshold to accommodate difference.
MSA-MRWA | WA4042128 | 5th Floor Don Aitken - near office 546 - Water leaking from ceiling, could be A/C | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor-Open Office Area-South East-Station 5 546 to 5 549 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 06 Mar 2021 | 2021-03-06 23:44:46 | 2021-03-07 11:00:00 | Fail | Called out to site Saturday night. Accessed building. Found fcu feeding computer room on level 5 to be leaking from drain. Ceiling tile had collapsed. Accessed unit and found glue to be deteriorated and pipe wrapped. Had no 15mm pvc available will have to source tomorrow and return to fit. Vacuumed remaining water out of unit and bunged drainage point. Isolated unit and will return tomorrow. Sourced parts. Removed bung. Cut drain back and ran new. Restored power and tested operation. All ok. Couldn't locate a ceiling tile to replace the broken one. Vacuumed up mess from the ceiling tile and removed rubbish. A40483536M
MSA-DCS | WA4042154 | Roller door is broken in bakery section, needs new tracks for the roller doors. | Casuarina Prison | GMP-BR- HO | Carpentry | Materials (CA) | UNIVERSAL DOORS | 2 | CLOSE | 07 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-23 10:45:00 | Fail | 23.03.21 - ATTENDED SITE, SUPPLY & INSTALLED ONE (1) L/H GUIDE, REMOVED,STRAIGHTENED & REFIT R/H GUIDE, CHECKED OPERATION, ALL OK.
MSA-DCS | WA4042170 | In Block H , telephone in the yard not working | Banksia Hill Detention Centre-Block H Accommodation | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-15 10:00:00 | Fail | Not an intercom or cell call. Fault is with the prisoner telephone system and will need to be referred to another contractor to repair.
MSA-DCS | WA4042173 | unit 5 control, leaking air-con, dripping water inside office, close to a PowerPoint | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 07 Mar 2021 | 2021-03-08 11:07:20 | 2021-05-13 10:47:00 | Fail | COMPLETED
MSA-DCS | WA4042186 | kitchen - bain marie - element has blown | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 07 Mar 2021 | 2021-03-08 14:09:47 | 2021-03-08 16:00:00 | Fail | Kitchen bain marie element blown. Check unit, found thermostat faulty, has been eaten by rats. Pick up new parts. Return & install. Test all working correctly.
MSA-DCS | WA4042190 | Control room fire panel fault, battery fault | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Assistant Superintendent - Prisoner and Security Management | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 07 Mar 2021 | 2021-03-07 19:19:09 | 2021-03-08 08:55:00 | Fail | 7/03/21 EIAfter hours callout to Boronia Prison.Attended site & liaised with onsite staff.Inspected MFIP at gate house & FIP status displaying normal.Checked MFIP history log which records intermittent panel 1 battery fault. Old batteries dated 18/08/18.Replaced MFIP batteries for new.2 x 12VDC 40ah batteries.Placed battery fitted date on each battery.System status displaying normal on departure.8/3/21 JN JGAttended site for battery fault P01 C01 D0615. As above batteries replaced yesterday. Measured voltage from charger card output howevercard won’t voltage unless under load. Batteries measured at 26.8v disconnected from charger card, and 27.5v once connected. Ran a manualbattery test through FIP no faults appeared. Checked that main FIP was definitely P01 as fault indicated and confirmed that it was.Recommend monitoring fault, may need to look at replacement charger card if fault re appears.
MSA-DTWD | WA4042147 | Midland Campus Block B Main Entry Door - Board up and make safe. | Midland Campus-Block B-Ground Floor | GMP-BR | Building | Materials (BU) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 07 Mar 2021 | 2021-03-07 06:45:35 | 2021-03-07 05:05:00 | Pass | ATTENDED SITE AFTER HOURSREGLAZED 2 BROKEN DOOR PANELS6.38 CLEAR LAMINATED SAFETY GLASS2-1035 X 745PLUS 2 L/M OF RUBBER REPLACED
MSA-DCA | WA4042523 | ground main public lift fingers caught in lift - see notes | Maritime Museum Victoria Quay-Main Building | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | SSP | 08 Mar 2021 | 2021-03-09 17:00:00 |  | Overdue
MSA-DCA | WA4042733 | Molecular Science/Student office area, near lunch room- Air Con quite high in temp | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Molecular Laboratory | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 12:30:00 | Pass | Attended site. Ac system not cooling reading 28c. Applied tests and checks. Investigation found timeclock settings to have been activated to switch off at 1400 ? Reset controller and Programmed applicable settings. Tested operation. System operating correctly.
MSA-DCS | WA4042231 | Push button for the pedestrian gate at the entry building is not working. | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 05:24:26 | 2021-03-08 08:45:00 | Pass | Tested both entry and exit side button and found working confirmed by staff. Tested 6 other buttons on other location and found all ok
MSA-DCS | WA4042289 | Unit 10, A wing outside A1 - floor lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 08 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-12 11:30:00 | Fail | DAMAGED SECTIONS (2) REMOVED & REPLACED WITH NEW VINYL FLOORING & COVING
MSA-DCS | WA4042300 | unit 1, Lobby Area - Water is leaking into the unit lobby area from the roof space.( see notes ) | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-08 13:44:20 | Pass | Checked for water leak,all condensate pump hoses ok,there is no a/c near where water was leaking through and no water present when investigated.
MSA-DCS | WA4042303 | Reception -Floor under and around Seniors Officer's desk is lifting up.1 piece has lifted up | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-04-08 14:00:00 | Fail | DAMAGED SECTION OF VINYL FLOORING LIFTED & REPLACED WITH NEW
MSA-DCS | WA4042305 | Unit 4, Cell A11- Toilet leaking from the bottom & sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-12 08:30:00 | Pass | Nill
MSA-DCS | WA4042306 | Unit 2, B Wing- cleaning cupboard pipes leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 08:07:28 | 2021-03-08 13:00:00 | Pass | Nill
MSA-DCS | WA4042307 | Unit 14, C wing utility room tap leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-16 13:30:00 | Fail | Nill
MSA-DCS | WA4042308 | Unit 14 - Tap in the west side of unit 14 yard constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-19 13:00:00 | Fail | Replaced 20mm hose tap and secured hose tap back to wall.
MSA-DCS | WA4042309 | Unit 14, Cell D1- Hot water tap at basin not working (broken pin) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-11 11:31:00 | Pass | Nill
MSA-DCS | WA4042312 | Unit 5, Cell D12- Cell call system is very faint & difficult to hear | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-08 14:00:00 | Pass | Unit replaced tested ok.
MSA-DCS | WA4042316 | Unit 7, A wing - Vinyl is bubbling up in the kitchen area of A wing and B wing | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-04-09 09:30:00 | Fail | rubber flooring repairs
MSA-DCS | WA4042317 | Unit 13, Cell A14- Main light switch not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 10:00:00 | Pass | Repaired faulty lights in unit 13 a14
MSA-DCS | WA4042318 | SHU, B8 - Obs light cell B8 not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 08:21:35 | 2021-03-09 11:30:00 | Fail | Attend and organise access.Investigate and repair SHU B8 obs light
MSA-DCS | WA4042322 | Unit 2, D12 - lock jamming with officers number 1 key. can't double lock or unlock properly | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 08:23:37 | 2021-03-17 12:30:00 | Fail | Remove edge capping and main lock, service, re install lock and edge capping with new fixings, require parts.Replace barrel, door plate lock and strike.
MSA-DCS | WA4042325 | SITE COST ISU, exercise yard- Camera has fault | Banksia Hill Detention Centre | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 12:25:48 | 2021-03-08 11:15:00 | Pass | Reset workstation and adjusted time to match cameras. All cameras working on workstation
MSA-DCS | WA4042326 | During cell call checks in Unit 6, D11 is un audible | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-08 16:30:00 | Pass | Unit cleaned and tested ok
MSA-DCS | WA4042328 | Unit 13 - Hot water tap in B & D Dayroom sink has a constant stream of water, not able to turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 08:30:02 | 2021-03-09 07:30:00 | Pass | Nill
MSA-DCS | WA4042331 | Unit 5, A wing, Cell 10 -Cell window will not stay open, metal rod has been removed (see notes) | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-11 12:00:00 | Pass | SPIRAL BALANCES RENEWED & PULL HADLES RE FIXED TO WINDOW
MSA-DCS | WA4042336 | Unit 6, Main glass front door- lock is faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 12:35:26 | 2021-03-08 12:30:00 | Pass | Attend site. Refit strike plate to door and refit bottom hinges. Re-aligned door. Repaired and working but suggest new doors and frames due to amount of wear. Discussed with Robert pool Coordinating Locksmith, on site.
MSA-DCS | WA4042337 | Control room - perimeter zone, internal zones - mutiple faults (see notes) | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 12:34:55 | 2021-04-14 16:00:00 | Fail | Repaired all zone faults and tested OK.Job Complete
MSA-DCS | WA4042339 | Control room - duress alarm slave computer has only 112 hours of operation left | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 12:38:36 | 2021-03-10 16:43:00 | Fail | Repaired duress computer faults and tested OK.Job Complete
MSA-DCS | WA4042342 | SITE COST Unit 4, C wing - C wing stores cupboard door lock is bent needs replacing. | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 12:41:38 | 2021-03-08 10:00:00 | Pass | Check lock, No lock fault, Lock is new, Officers have worn keys (advised officers to attend security to have worn service keys replaced)
MSA-DCS | WA4042351 | Unit 6, B & D - Water liking from the basin in the showers room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-15 13:30:00 | Pass | Nill
MSA-DCS | WA4042355 | Amenities - leaking pipe or aircon something in the roof in the hall outside male toilets | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 08:45:56 | 2021-03-10 10:31:00 | Fail | Job was raised as ‘leaking aircon or something’ At time of investigation, we asked casuarina maintenance head officers for some further information regarding the leak, we were told it wasn’t their job to investigate the job first prior to allocating it to us , so upon our investigation we could not find any plumbing related issues/leaks
MSA-DCS | WA4042372 | Flood lights on main laundry not working at night | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 08:52:40 | 2021-03-08 16:30:00 | Pass | Replaced PE cell and reset power
MSA-DCS | WA4042375 | Unit 13, B & D- Instanst hot water system is faulty, see notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-16 09:45:00 | Fail | Unit not filling correctly. Dirty level sensors causing unit to think it is full. Cleaned and now working ok.
MSA-DCS | WA4042381 | Unit 7, Regi Area Yard Grille - Bottom Hinge has seized | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 09:01:58 | 2021-03-08 13:15:00 | Pass | Onsite. Bottom hinge on grille has seized. Repair hinge. Tested and working correctly.
MSA-DCS | WA4042384 | Unit 3, control room door - the barrel on the control room door is rotating | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 09:05:58 | 2021-03-08 15:00:00 | Pass | Onsite to look at Unit 3 control room door lock. The lock body was broken. Repaired lock and re-installed. Tested, working correctly.
MSA-DCS | WA4042386 | Unit 1 B wing - Camera has stopped working and is failing to re-connect | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 09:08:19 | 2021-03-11 16:17:00 | Fail | 8/2/21 Provided phone support and officer told me the camera came back.11/3/21 Checked over system and found fault had not reoccured.Tested OK.Job Complete
MSA-DCS | WA4042388 | Medical center, medical center cage internal lock, faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 13:08:28 | 2021-03-08 10:30:00 | Pass | Attend site. Lock faulty at medical centre gate. Lock removed and serviced.
MSA-DCS | WA4042393 | unit 8, water room/paint shop - water hater leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-04-29 16:39:00 | Fail | Replaced hwu. Electrician wired up unit as well.
MSA-DCS | WA4042394 | Reception, 4th Shower- Tap is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-17 09:05:00 | Fail | Replaced missing handle
MSA-DCS | WA4042398 | Unit 7, S Wing showers - Middle shower leaking and sink tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-17 09:55:00 | Fail | Rewashed shower taps
MSA-DCS | WA4042400 | Unit 9, A10 - drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 09:13:53 | 2021-03-08 14:55:00 | Pass | Unblocked drain
MSA-DCS | WA4042405 | Unit 5, B & C Wing - Washing machine not spin drying | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 11:00:00 | Pass | Fisher & Paykel machine was tested without load and had no issues. Recommend monitoring and check load. May need balance sensor.
MSA-DCS | WA4042413 | SHU (9), B2 - Night light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 09:28:21 | 2021-03-09 11:30:00 | Fail | Organised access. Attended and repaired faulty light in b2
MSA-DCS | WA4042418 | SHU (9) east - Sink tap not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 13:40:51 | 2021-03-09 08:55:00 | Fail | 8/3 : no access, booked in for 8:30am 9/3
MSA-DCS | WA4042420 | Unit 4, Cameras in perimeter zones 1,3,4,5,6 & PTZ 38 are not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 17:40:16 | 2021-03-08 16:00:00 | Pass | On arrival we found the power suppies for the Indig CCTV encoder Cage had failed. Replaced one power supply with a site critical spare. Two power supplies ordered, one to replace the second supply for that cage the second to replace the Critical spare used. Service was restore once the Encoder Cage was back on-line.
MSA-DCS | WA4042422 | HR corridor- Walkway light outsoide of corridor not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-31 10:00:00 | Fail | Repaired and replaced lights
MSA-DCS | WA4042423 | Unit 2, Cell B01- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-08 13:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA4042424 | Unit 1, Cell C01- No power in cell due to possible burn out of power point | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 09:48:35 | 2021-03-08 11:30:00 | Pass | Replaced Broken GPO due to full of water
MSA-DCS | WA4042433 | Stop and start of boilers for the rest of the week | Hakea Prison | WSM-BR-SITE | Mechanical Services | Boilers (MS) | Boilertronics | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-19 08:47:00 | Fail | 9/03/2021 - 12/03/2021 - Start up & Shutdown Boilers15/03/2021 - 19/03/2021 - Start up & Shutdown Boilers
MSA-DCS | WA4042472 | Unit 6 Toaster requires a new plug | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 10:00:00 | Pass | Investigate and repair unit 6 toaster
MSA-DCS | WA4042492 | Unit 3, Cell B10- Window wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-11 10:45:00 | Pass | NEW SPIRAL BALANCES INSTALLED TO WINDOW
MSA-DCS | WA4042495 | Industries gardens- Solenoid 5,Requires a 2-core data coil. | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-16 13:30:00 | Fail | REPLACE DATA COIL AND REPROGRAM
MSA-DCS | WA4042567 | rear of the laundry water leak coming out of the ground | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 11:39:01 | 2021-03-09 12:30:00 | Fail | Found old unsed electrical conduit sleaved in pvc ground water running through
MSA-DCS | WA4042575 | Public toilet near reception Vacant Occupied door lock for public toilet is not working - cant lock | Mandurah | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 09:30:00 | Pass | Carried out repairs to the lock on toilet door.
MSA-DCS | WA4042588 | Unit 1 A13 Viewing hatch glass scratched and burnt needs replacing | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-18 13:30:00 | Fail | replaced obs panel
MSA-DCS | WA4042597 | Unit 6, N Wing Dayroom- Urn overflowing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-24 10:04:00 | Fail | Replaced level probes and solenoid. Rectified issue. Was already in prison and couldn’t re start w/o. Started again at 9.30am 24/03/21
MSA-DCS | WA4042604 | Unit 2, A5 - Officers 1 key is getting stuck in the lock and not turning | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 13:30:00 | Pass | Remove edge capping and main lock, service lock. Requires rebuild in workshop.Rebuild and repair lock in workshop.Re install rebuilt lock and edge capping with new fixings.
MSA-DCS | WA4042647 | Administration, office - Air Con no working in Admin, it is getting very uncomfortable/sticky | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-08 14:43:13 | Pass | Checked over a/c found no faults present,checked airflow switch found found probe slightly blocked,cleaned out and turned back on unit started back up and running ok.
MSA-DCS | WA4042649 | Administration, lunchroom - Bain-marie is faulty and not getting hot enough | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 13:16:20 | 2021-03-08 16:25:00 | Pass | Replaced simmerstat control & test ok.
MSA-DCS | WA4042653 | Garments - Skylights in Garments are leaking badly | Casuarina Prison | GMP-BR- HO | Roofing | Rooflights and Skylights (RF) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-04-08 17:00:00 | Fail | new skylights installed and roof repaired
MSA-DCS | WA4042657 | Yeeda, Obs - camera 109 has no picture from control | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 13:25:19 | 2021-03-09 09:30:00 | Pass | Found dead power supply for the fibre modem in QUE block. Replaced 24 vdc 3 amp powersupply. Tested and working back to gatehouse
MSA-DCS | WA4042672 | Unit 2, A&C - Vinyl outside A/C door bubbling causing a trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-04-09 13:30:00 | Fail | rubber flooring repairs
MSA-DCS | WA4042692 | SITE COST ISU monitors have no picture | Banksia Hill Detention Centre | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 18:09:09 | 2021-03-08 18:00:00 | Pass | Found all 3 monitors for the indigo system is down. Played with the display settings and checked and tested configurations, all ok. 1 PACOM DVR # 3 is also on alarm, rebooted and went back to normal
MSA-DCS | WA4042705 | D2 IDF/microwave - constant alarm. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 14:23:30 | 2021-05-11 12:00:00 | Fail | Lighting protection device found to be causing alarms. Removed and tested working ok.
MSA-DCS | WA4042709 | Main Kitchen - Dishwasher is not working | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 14:27:21 | 2021-03-08 15:30:00 | Pass | Reset dishwasher
MSA-DCS | WA4042712 | E1 - perimeter trax - constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 14:30:22 | 2021-03-09 12:15:00 | Pass | Investigated fault, recalibrated, walk tested and monitored for correct operation.Tested OKJob Complete
MSA-DCS | WA4042790 | human resources main door, key is not un locking door properly | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 16:15:54 | 2021-03-09 09:15:00 | Pass | Adjusted lock and cylinder on Door to Human Resources( water ingress into lock and cylinder causing main issue )
MSA-DFES | WA4042272 | Room10 (Station TV room) - Air conditioning unit making a ticking/humming noise whilst operating. | CFRS Welshpool | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 08 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-18 13:00:00 | Fail | Replaced Condensate pump. Works good.
MSA-DFES | WA4042282 | Engine room, bay 2 rear door (door 6) - cable has cable has come off (out of service) | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Go Doors | 1 | COMP | 08 Mar 2021 | 2021-03-08 17:00:00 | 2021-03-08 13:30:00 | Pass | Complete
MSA-DFES | WA4042314 | North East SES/ RURAL Office - Flouro light not working | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-23 13:45:00 | Fail | Complete
MSA-DFES | WA4042333 | Water entering Engine Room from Ceiling above Store 3 | CFRS Wangara | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-05-25 16:00:00 | Fail | Work completed
MSA-DFES | WA4042380 | 3 bed dorm at end - Leaking shower and noisy leaking cistern in toilet | CFRS Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-10 11:15:00 | Pass | Replaced inlet valve,outlet valve rubber to cistern and replaced shower mixer for new tested job complete
MSA-DFES | WA4042430 | ground study room ceiling is sagging and has water marks- see notes | CFRS Joondalup | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-04-19 15:30:00 | Fail | To remove damaged section of ceiling and install new gyprock, flushed sanded and painted
MSA-DFES | WA4042585 | Kitchen - Instant hot water/cold water ZIP tap not working | CFRS Belmont | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 11:05:00 | Pass | DIAGNOSED AND REPLACED ZIP SAFETY SOLENOID KIT HTAP AND ZIP ACETAL NUT KIT ON ZIP HYDROTAP A40190379M
MSA-DFES | WA4042587 | L1 room 7 Duty room door to engine room difficult to open/doesn’t open fully | CFRS Ellen Brook | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 11:30:00 | Pass | Attend site and ease and adjust door
MSA-DFES | WA4042687 | Admin building ground lecture room 6 flashing light - see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-15 14:00:00 | Pass | CompletedAttended site and located multiple fluros out. Replaced and tested all in working order. Notified staff and signed out
MSA-DFES | WA4042760 | Simulation Centre- Numerous fluoro lights that are not working- locations listed below | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-31 13:00:00 | Fail | Arrived onsite and signed in. Started works and located Excon room where we need to put in new LED tubes. Put the tubes in. Tested and all working
MSA-DFES | WA4042770 | BA service room HWS cupboard not hot water DO office, kitchen and BA service room | CFRS Perth | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-10 15:28:00 | Fail | Attended site and located faulty hot water unit Found dead short on element ,Replaced thermostat and element Tested and all workingAttended site and located faulty hot water unitFound dead short on element ,Replaced thermostat and elementTested and all working
MSA-DTAG | WA4042378 | Lvl 3, male toilets- Tap outside court 32 is faulty | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-10 10:30:00 | Pass | COMPLETED
MSA-DTAG | WA4042406 | Desk top of JSO Bench needs repairing | Rockingham Justice Complex | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo Building Services | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-09 09:00:00 | Pass | BENCH TOP RE SECURED
MSA-DTAG | WA4042499 | Custody Control Room - Bad smell coming from air vent in custody - Could be from a dead animal | Midland Courthouse | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 07:45:00 | Pass | .
MSA-DTAG | WA4042528 | Registry, Waiting room hallway - Round ceiling lights are dim and gone out | Mandurah Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-24 08:15:00 | Fail | Replaced new donwlights in waiting area hallway. Tested and are in workibg condition
MSA-DTAG | WA4042576 | Registry - Security Monitor in registry is not working (Possibly from power outage) | Mandurah Courthouse | GMP-BR-HO | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 15:30:00 | Pass | 8/3/21 - Ryan VestyFound screens with no picture.Checked connected hardware.Re-booted NUC, setup cameras on screen.All tested ok.
MSA-DTAG | WA4042583 | Parliamentary Counsel’s Office - Level 29 - swipe access control issues - see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 15:00:00 | Pass | Attended site. Assigned Card Profile to User Group in Unison. Tested, all OK.Job completed.
MSA-DTAG | WA4042637 | 1987 L1 Sheriff's Office Front door is not opening properly or not opening at all | Supreme Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 15:20:00 | Pass | Inspected door and found lock wiring fault corrected it wiring fault and tested all OK at time of test
MSA-DTAG | WA4042648 | Ground, stairwell into court 1 Judicial entrance - lights not wokring | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-20 12:30:00 | Fail | Ran in new cable for light in stariqell to court 1 and tested. All in working order
MSA-DTAG | WA4042691 | Level 3 - The CCTV Monitoring system in the Building Managers Office is giving out and constant ala | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-10 08:00:00 | Fail | Reprogrammed/Reconfigured managers office workstation to disable unused audio alarms from workstation, all programmed and tested ok. Job complete
MSA-DTWD | WA4042286 | Remove graffiti all around the building | Perth Campus B1 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 08 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 14:45:00 | Pass | REMOVAL OF GRAFFITI FROM AROUND THE BUILDING
MSA-DTWD | WA4042455 | D Block - AHUD2 is showing a Fan Status Fault | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-09 11:30:00 | Pass | Picked up belts from supplier, went to site, signed in checked in with Sharyn. Gathered tools and equipment replaced New for Old belts tested all ok. Cleaned up and completed paperwork and swiped out.
MSA-DTWD | WA4042467 | campus Ants posing a problem | Muresk Institute | GMP-BR | Pest Control | General Pest (PC) | Morris Pest and Weed Control | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-08 16:30:00 | Pass | Treatment of large ant nest
MSA-DTWD | WA4042471 | E Block Skills Kitchen 1 has tagged out ovens that are not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-04-01 10:00:00 | Fail | WAS ASKED TO ATTEND REPAIRS ON OTHER EQUIPMENT AFTER QUOTED WORKS COMPLETED. PARTS ONLY EXTRA CHARGE.
MSA-DTWD | WA4042505 | B Block, B35 male toilets- light fittings are faulty (replace with LED dome lights) | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 15:30:00 | Pass | Attended site and signed in. Investigated lights in b35 male toilet. Found 1 x faulty and 2 x very dim oyster lights. Disconnect and removed old lights. Supply and replace with new led oyster lights. Tested all ok. Reenergised, all ok. Cleaned site and completed paperwork. Informed staff of completion of job.
MSA-DTWD | WA4042548 | Security Gatehouse External - Entry to campus from Hayman road Sinkhole in exit driveway lane | Bentley Campus | GMP-BR | Paving & Roadworks | Asphalt (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-19 08:30:00 | Fail | Investigation was completed by the client and Protek returned to site to backfill the pothole and install bitumen to the area.
MSA-DTWD | WA4042582 | L3 outside deck area- blocked drains | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-04-20 08:51:00 | Fail | Inspect drains and clean out where requiredBlocked damaged line
MSA-DTWD | WA4042616 | A block, Level 1, A105 - replace fualty/damaged lights in cafe | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 12:53:00 | Pass | Repalced faulty fluro and starters to light .job completed
MSA-DTWD | WA4042617 | A block, Level 1, A105 cafe- Flexi Hose in cafe Leaking in sink | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 10:30:00 | Pass | Replaced mixer and spray handle
MSA-DTWD | WA4042644 | Beauty Clinic- Rectify lighting (C-bus system) | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-26 15:45:00 | Fail | Complete
MSA-DTWD | WA4042650 | Block 6, Bricklaying - Emergency Stop button for Pug Mill loose on control panel | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 08 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 13:45:00 | Pass | Found loose stop button in bricklaying. Investigated and isolated. Tightened stop button so it could not be loosened easily. Tested and reenergised. Job complete
MSA-DTWD | WA4042669 | ground student toilet cistern constantly running | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 10:15:00 | Pass | Repalced toilet and pan one rubber and seat
MSA-DTWD | WA4042706 | BLD 832, level 1, Hallway - Faulty overflow chillers | Muresk Institute | GMP-BR | Refrigeration | Chiller (RE) | CDA Air & Solar | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 15:00:00 | Pass | Cleared drain
MSA-DTWD | WA4042761 | House 13 laundry roof leaks | Muresk Institute | GMP-BR | Roofing | Metal Roofing (RF) | Lee Carpentry | 1 | CLOSE | 08 Mar 2021 | 2021-03-09 17:00:00 | 2021-03-09 11:45:00 | Pass | vents sealed with silicon
MSA-DTWD | WA4042763 | A block admin panel under stairs indication comms failure and cannot be armed up. | Midland Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 0 | CLOSE | 08 Mar 2021 | 2021-03-08 19:45:00 | 2021-03-26 12:30:00 | Fail | The job was finished 26/03/2021
MSA-MRWA | WA4042456 | Outside 1st floor meeting room - Emergency exit light not illuminating. Please repair or replace | Materials Engineering Branch-Asphalt Lab | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 08 Mar 2021 | 2021-03-15 17:00:00 | 2021-04-13 16:00:00 | Fail | Attended site, signed in, completed JSA, spoke with office ladies, inspected switchboard and RCD, left site to pick up parts, returned, waited until we got the approval to shut off power, replaced faulty rcd with new one like for like , tested, all working. **job complete**Assets wouldn’t let me scan.
MSA-DCA | WA4043223 | High water usage alarm zone 10 - low water usage in zone 6 | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Earth & Water Pty Ltd | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-11 11:45:00 | Fail | Repairs to sprinkler
MSA-DCA | WA4043588 | Education Room - leaking tap | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-ABG0.2 - Margaret Preston Room | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 14:10:00 | Pass | Replaced corroded taps and leaking washers
MSA-DCA | WA4043592 | waste pipe seal under the sink needs repaired as fault/damaged | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1-Storage Room - Behind Foyer Bar | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 11:35:00 | Pass | Uninstalled waste and resealed it. Cleaned trap and unblocked drain
MSA-DCA | WA4043607 | ground male toilet sink waste pipe disconnected please replace damaged | State Theatre Centre (Heath Ledger Theatre)-Main Building-External Area-Courtyard - Entry and External Corridor | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 13:20:00 | Pass | Replaced lhs trap and rerun waste pipe to existing copper pipe. Relaced leaking fittings on the rhs basin and adjusted pipework to suit
MSA-DCA | WA4043638 | Leaking air con unit - see further notes below | King Street Arts Centre-Main Building-Ground Floor-Shop 5 - One Off (shoe shop) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 11:26:00 | Pass | Investigate water leak and foundcdrain blocked with dirt. Unlock drain and test. Unit now fixed.
MSA-DCA | WA4043745 | BMS control room Building management system offline | Shipwreck Galleries-Main Building-Level 1 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-13 16:30:00 | Fail | Attended site. BMS control system not operating correctly. Applied tests and checks to find remote access ok but unable to establish connection and log in to ecostruxure BMS front end. Raised PO for Schnieder to attend. Schnieder to have attended and updated applicable licencing for BMS software. Reset router and tested operation and remote access. System operating correctly.
MSA-DCS | WA4043181 | Yeeda, Class 2- 2x lights constantly trip (approx 6m high) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-24 15:30:00 | Fail | Repaired fans and lights
MSA-DCS | WA4043183 | Karakin, Cell B03- Smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 11:30:00 | Pass | CELL WINDOW REGLAZED & WELDED
MSA-DCS | WA4043191 | Canteen - Faulty wall port | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-11 08:00:00 | Pass | Repairs to data port in canteen
MSA-DCS | WA4043210 | SITE COST uni 1, A wing - blocked drains & toilets to entire left side of wing | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 09 Mar 2021 | 2021-03-09 12:44:07 | 2021-03-09 14:40:00 | Fail | Cleared blocked drain to Unit 1 A wing and part of Unit 2.Job took long to complete within the time.
MSA-DCS | WA4043218 | Laundry, Number 3 washing machine - showing fault ‘ no motor com’ | Hakea Prison | SPA-BR | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 08:54:10 | 2021-04-07 22:20:00 | Fail | 15/03 - Attend site - check machine. Trace fault to a blown motor drive due to water accumulating inside electrical cabinet from a leaking steam pipe. Remove motor to workshop and prepare repair quote.07/04 - Return to site - supply and fit new motor drive - reassemble and test - tests O.K.
MSA-DCS | WA4043255 | unit 2 cell call not working to gate control | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Mar 2021 | 2021-03-09 17:29:34 | 2021-03-09 15:01:00 | Pass | Unit 2 cellcall not working properly back to gatehouse. After resetting equipment and checking programming was still not working. Took apart the node in unit 2 and found a loose ribbon cable on circuitry. Plugged back in and tested. All working as per normal.
MSA-DCS | WA4043294 | Kitchen- right hand prover not steaming plus water is leaking | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 09:51:21 | 2021-03-10 14:00:00 | Fail | Kitchen - right hand prover not steaming plus water is leaking. Check prover, found float valve ball melted & shaft broken. Pick up new parts. Clean scale from steam tank, install new ball & valve. Fit isolating valve. Test all.
MSA-DCS | WA4043327 | GRound floor, kitchen - Bill and tap leaking | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-18 16:30:00 | Fail | Calibrated hot and dropped temperature by 0.5 degrees, this stopped the issue regarding hot water dispensing from Billi dispenser. Mixer poor flow and dripping. Had to wait for Billi technical support to get back to me. Advised to change/adjust cartridge, replace dual solenoid and Venturi. Waiting for parts. 11.00 to 11.15NOT COMMON SPARE - DONT NORMALL CARRY THE CARTRIDGE MIXER PART - ORDERED THIS PART IN FOR THIS JOB CALIBRATED HOT DROPPED TEMP TO 98 REMOVED KINK IN PIPE REMOVED AND CELANED VENTURI VALVE UNIT STILL SPLUTTERINGHAD TO SPEAK TO BILLI SUPPORT - ORDERED IN CARTRIDGE FOR MIXER - RETURNED AND INSTALLED NEW CARTRIDGE AND VENTURIE VALVE ASSEMBLY
MSA-DCS | WA4043328 | Public Toilet / Staff Shower Terrible smells - sewerage blockage | Rockingham Justice Complex | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-09 14:15:00 | Pass | Advised to have ventilation looked at as drains good and no sign if smell
MSA-DCS | WA4043350 | Unit 1, C15 - Sink is backed up has been plunged but still blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-17 10:30:00 | Fail | Unblocked basin
MSA-DCS | WA4043351 | Unit 3, C wing day room - Day room GPO next to toaster needs replacing as its broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 09:30:00 | Pass | Replaced gpo
MSA-DCS | WA4043354 | Unit 3, C wing day room - Window has been cracked in the day room | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-18 11:30:00 | Fail | reglazed window
MSA-DCS | WA4043356 | Unit 2, B15 - tap will not turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-17 11:40:00 | Fail | Rewashed tap
MSA-DCS | WA4043360 | Unit 3, B15 - Cell light switch has been burnt/melted | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 08:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA4043365 | C-D 7-8 & C-D 3-4 Vesda Fault on Fire Panel | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 10:55:52 | 2021-03-10 08:34:00 | Pass | 10/3/21 JNAttended site for the following:Unit 2:C/D 3+4 low airflow on pipe 4. Cleaned out sampling point and vacuumed pipework, levels returned to normal.Checked C/D 7+8, no history of recent faults on this vesda and levels appear normal.C/D 15+ 16 low airflow on pipe 1. Cleaned out sampling point and vacuumed pipework. Levels returned to normal.Unit 1:Plant room vesda in fault on arrival. Vesda showing zone fault ‘too many scans in one week’, reset scan count and vesda returned to normal.
MSA-DCS | WA4043398 | MPU - air con controller faulty | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-09 16:30:00 | Pass | 26/7/21 - No further works under this BR - Quoted works/Project planning underway (SHU Sec OBS Works package by DOJ/SCG)**************Liaised with aircon contractor, determined fault with Maxpro Control Equipment. Parts are no longer available for this obsolete technology.Temporarily enabled airconditioner manually via laptop.Will attempt to find old reused parts but recommend upgrading to Gallagher.Note: Lighting control is also out of order related to same fault.Parts:CablesBattery
MSA-DCS | WA4043410 | Unit 6, A3 - toilet pulled away from the floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 11:37:29 | 2021-03-10 11:38:00 | Fail | Replaced toilet pan,seat and adjusted flush pipe.
MSA-DCS | WA4043418 | Unit 1, D2 -broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-17 10:00:00 | Fail | Replaced broken shower tiles.
MSA-DCS | WA4043422 | Unit 1, D1 -broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-17 08:30:00 | Fail | Replaced broken shower tiles.
MSA-DCS | WA4043423 | Unit 1, D3 -broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-17 11:30:00 | Fail | Replaced broken shower tiles.
MSA-DCS | WA4043425 | Unit 1 D4 Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-17 13:00:00 | Fail | Replaced broken shower tiles.
MSA-DCS | WA4043473 | medical 4 air cons not powering up | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:26:38 | 2021-03-09 18:00:00 | Pass | Tested power supply, Aircon tech required to repair faulty aircon.
MSA-DCS | WA4043482 | Laundry - ceiling power fuse to #3 washing machine faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:33:38 | 2021-03-12 15:00:00 | Fail | No power washing machine.
MSA-DCS | WA4043488 | Reception Cell 3 vinyl flooring lifting in front of cell | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-04-10 09:15:00 | Fail | vinyl floor repairs
MSA-DCS | WA4043504 | admin reseat and replace washers to hand basin tap in toilet | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-24 12:30:00 | Fail | Reseated the tap, serviced the spindle and replaced the tap washer all working good
MSA-DCS | WA4043507 | reseption reseat washing machine taps | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-31 07:30:00 | Fail | Could not find isolation to the reception block. Isolated water and serviced the spindle, reseated the tap and changed the tap washer.
MSA-DCS | WA4043508 | Unit 1 B wing cell 13 vinyl floor damaged | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:41:58 | 2021-04-28 07:30:00 | Fail | VINYL REPLACED WITH NEW TO CELL
MSA-DCS | WA4043511 | Unit 1 B wing cell 14 vinyl floor damaged | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:48:20 | 2021-05-18 15:00:00 | Fail | OLD VINYL LIFTED, SUB FLOORS PREPPED & READIED, NEW VINYL & SKIRTING LAID
MSA-DCS | WA4043514 | Unit 1 B wing cell 20 vinyl floor damaged | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:48:59 | 2021-05-18 15:00:00 | Fail | OLD VINYL REMOVED , FLOORS PREPPED & NEW VINYL FLOORING & SKIRTING INSTALLED
MSA-DCS | WA4043517 | Unit 1 B wing cell 23 vinyl floor damaged | Bandyup Prison | SPA-BR | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:49:40 | 2021-04-16 11:15:00 | Fail | vinyl flooring replaced
MSA-DCS | WA4043524 | Kitchen - hot pipes over gas heater corroded | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:56:29 | 2021-03-22 16:00:00 | Fail | Collected parts from supplier and returned to site. Isolated and drained water from the system. Removed the faulty pipe work. Fabricated new pipe work and fitted the new pipe work. Reconnected water and power. Tested all working good.
MSA-DCS | WA4043525 | unit 1 B wing cell 19 vinyl skirting needs repair | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:55:38 | 2021-05-13 20:15:00 | Fail | NEW VINYL LAYED
MSA-DCS | WA4043528 | unit 1 B wing cell 27 vinyl skirting needs repair | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 12:58:03 | 2021-05-19 15:00:00 | Fail | damaged flooring lifted up, sub floor prepped, new vinyl floor & skirting installed
MSA-DCS | WA4043539 | Murchison, garden shed - lock is sticking and hard to unlock | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 09:30:00 | Pass | On site. Lock is sticking and difficult to unlock. Lock removed and serviced. Tested, working correctly.
MSA-DCS | WA4043541 | Jasper, Pedestrian gate - lock is sticking | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 09:00:00 | Pass | Attend site. Lock is sticking. Lock replaced with new 3572SC mortice lock.
MSA-DCS | WA4043604 | Kitchen - brust water pipe in ceiling | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 09 Mar 2021 | 2021-03-09 18:06:59 | 2021-04-20 09:17:00 | Fail | Replaced cororded air vent
MSA-DCS | WA4043640 | Health Centre, kitchen - Urn leaking under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 15:07:00 | 2021-03-10 11:05:00 | Pass | Replaced cracked filter housing -installed new capex asset maxiflow scale filter system connected to feed bwu new asset code A40189458S
MSA-DCS | WA4043664 | Unit 2, Art & Programmes Rooms- Air Con Controls not working | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-05-06 10:00:00 | Fail | Leak check complete. Unit operational
MSA-DCS | WA4043691 | unit 4 shop/gym MDAS transponder low battery | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 09:30:00 | Pass | Attended Main prison control room. Confirmed alarm still in and equipment location. Attended PRU House K removed failed battery and installed replacement. Confirmed battery was trickle charging.
MSA-DCS | WA4043732 | Public toilet, staff toilets - male and female Ventilation units not drawing air out - see notes | Rockingham Justice Complex | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 11:22:00 | Pass | All fans running. Increased speed for public exhaust within current rating. All okCleared blockages in duct work and outside grill increasing airflow. All ok.
MSA-DCS | WA4043735 | unit 9 PA system not working cannot make announcments | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 15:30:00 | Pass | Attended site checked and found customer complaints that some error messages were showing up in Unit 9 cell call console last night and PA announcements not working. Staff tried to cancel the error messages. Error messages not present when technician on site. Tested cell call function and PA are all working ok. Can’t see the problem. Checked in Site Management in cell call server in equipment can’t see system error as well.
MSA-DCS | WA4043753 | Black inner gate has frozen wont close | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Mar 2021 | 2021-03-09 22:03:26 | 2021-03-09 20:01:00 | Pass | Found RHS gate motor slipping on belt tightened and gate works if issue happens again gate techs to attend
MSA-DCS | WA4043755 | Unit 2 - Cell call system failure | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 22:22:13 | 2021-03-10 00:00:00 | Pass | Attended Bunbury Prison. Accessed cell call power supply and disconnected, then reconnected. Returned to Gatehouse and sent computer instruction to restart all Nodes on site. In Control room we answered qued calls on console. Returned to Unit 2, tested a selection of cell calls in Unit 2. All calls connected to Master Control with two-way audio. Test calls were established from multiple cell in other units on-site.
MSA-DFES | WA4043192 | (front doors) Doors to engine room - doors will not operate correctly (automatic doors) | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Anvil Doors | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 17:00:00 | Pass | Attended Claremont Fire Station on P1 call out, Checked door #1 and #2. Technician found that there was a fault in the logic board that prevented the doors operating correctly. The technician reset the logic board and tested the doors operation to be OK. Please see attached service reports and signature slip
MSA-DFES | WA4043204 | Main workshop, stores office - issue with card reader | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-09 13:45:00 | Pass | 9/3/21 - Ryan VestyAdvised by staff that reader on stores door not opening this morning.Tested door, in full access.Contacted head office to overide timezone.Tested with contractor card and Rick's card, all ok.Disabled timezone overide, all ok.
MSA-DFES | WA4043432 | sink outside engine tap leaking constantly | CFRS Maddington | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 14:15:00 | Pass | Investigate leaking sink tap located outside engine room Isolate water supply to sink and remove old faulty tapware, once removed reseat tap seatSupply and install new basin set tapware, turn water back on and flush brass shavings, test operation and check for leaksPack up and clean up worksite
MSA-DFES | WA4043538 | External Relief valve on hot water system is leaking | CFRS Claremont | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-12 12:15:00 | Pass | Supply and install 2xnew hot relief valves on solar HWU Use working at heights harness and ropes to gain access to roof with ladder pointIsolate water to HWU and drain pressure, remove existing valves and install new valves, adjust pipe work on drain due to leak on roofTurn water back on and test operation/check for leaksPack up and clean up worksite
MSA-DFES | WA4043619 | Simulation Centre, Basement, Bunker Excon Room (AHIIMS Room) - unsupported floor tiles fallen threw | DFES Regional Office - Belmont | GMP-BR | Flooring | Carpet (FL) | AWB Co. | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-15 13:45:00 | Pass | Re-supported subframe structure as there was none present in that particular spot underneath doorway also re-glued carpet tiles as and he should haveworn
MSA-DTAG | WA4043171 | Lift 3 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMPFIN | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 11:00:00 | Pass | Lift on JVRP on ground floor with last error from Friday night a 148 T4 fault and 11 FC fault. Found ground floor doors had loose components and out of alignment, Made adjustments and returned lift to service.To be closed out at $0
MSA-DTAG | WA4043174 | Travel in lift 9 is erratic – sudden shudder and delayed carriage response | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-09 14:24:00 | Pass | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA4043390 | control room level 10 door - faulty , unable to open with swipe card | State Administrative Tribunal (SAT) | WSM-BR-SITE | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 09 Mar 2021 | 2021-03-09 15:24:30 | 2021-03-09 12:30:00 | Pass | Sapio on siteChecked and found faulty Mortice lock on level 10 security door, replaced lock and re-tested. All tested and working correctly. Job complete
MSA-DTAG | WA4043395 | Lvl 1, Sheriff’s Office- End Ladies toilet when flushed continues to run. | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 12:20:00 | Pass | Inspected induct cistern. Flushed toilet multiple times -everything in good working order.
MSA-DTAG | WA4043645 | 1st Floor, Room 220, Gents Toilets (staff)- toilet not functioning correctly- see notes below | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 13:40:00 | Pass | Replaced faulty inlet vakve
MSA-DTAG | WA4043695 | ground custody female toilet occasionally gets blocked | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 09:45:00 | Pass | Arrived on site and inspected found the toilet partially blocked. Plunged multiple times to clear the blockage. While testing found the inlet valve filling very slowly. Collected parts from supplier and returned to the site. Removed the faulty inlet valve and installed new inlet valve and hose. Tested multiple times all working in order.
MSA-DTWD | WA4043202 | Exterior- Remove Graffiti from Hose Box and Hydrant Booster at Entrance | Leederville Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-10 09:00:00 | Pass | REMOVAL OF GRAFFITI FROM HOSE BOX AND HYDRANT BOOSTER AT ENTRANCE
MSA-DTWD | WA4043239 | K block grund K02 canteen kitchen Tap constantly running in Cafe Kitchen, North wall | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 09:45:00 | Pass | Serviced leaking tap
MSA-DTWD | WA4043296 | - A-Block G/Floor East end Kitchen, the sink is leaking from the drain waste pipe | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 14:00:00 | Pass | Arrived on site and inspected found the the east end tea preparation room trap is leaking under the sink. Collected parts from supplier and returned to the site. Refitted the trap and tested all working good.
MSA-DTWD | WA4043301 | Building 6, Vehicle body building - Water leak from pipe in wall behind guillotine. | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-09 12:30:00 | Pass | Capped leaking pipe
MSA-DTWD | WA4043343 | BLD 820- B & D kitchen - leaking roof | Muresk Institute | GMP-BR | Building | Ceiling (BU) | Lee Carpentry | 1 | CLOSE | 09 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 14:30:00 | Pass | Job completed - replaced broken titles
MSA-DTWD | WA4043358 | C block L1 male toilets has a basin tap continuously dripping | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 12:15:00 | Pass | Arrived on site and inspected the lhs hand basin tap running. Serviced the tap and replaced the tap washer. Tested multiple times all working in order. The aerator filter was missing. Installed the aerator.
MSA-DTWD | WA4043379 | Cooling Towers - Unusual noise coming from Cooling Tower 2 | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-10-19 09:00:00 | Fail | Carried out checks on the number one cooling tower fan after wiring was completed, put the chiller back on line.
MSA-DTWD | WA4043394 | L2 Cafe courtyard lock jammed | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-16 10:31:00 | Pass | Service/repair lock & 2 x replacement keys
MSA-DTWD | WA4043503 | B block, female toilet - cubicle has leak from the bottom, when flushed leaks | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 11:00:00 | Pass | Called out to have a look at a leaking toilet from under the pan. Once arrived on site and tested for leak there was no leak any more.
MSA-DTWD | WA4043510 | A block, level 2 & 3 east end - urinals blocked | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 09 Mar 2021 | 2021-03-09 16:45:57 | 2021-03-09 15:45:00 | Pass | cleared block urinals with drain machine
MSA-DTWD | WA4043532 | L1 S100 female door faulty | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-11 14:30:00 | Pass | Work completed
MSA-DTWD | WA4043561 | Circuit R42 located in “E” block automotive. RCD cannot be reset | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-12 14:21:00 | Pass | Reset power cleaned water out of fueling rose. Advised site that must be roof leak
MSA-DTWD | WA4043596 | block 9 library Faulty GPO in staff work area | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-16 15:45:00 | Pass | Attended site and signed in. Located library staff room. Found gpo on pillar broken. Replaced with new and installed 2 x extra double gpos to help with load of constant use. Tested all okay. Job complete
MSA-DTWD | WA4043597 | F block F112 door into shower block broken lock | Leederville Campus | GMP-BR | Building | Doors (BU) | ADVANCED LOCK & KEY | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 14:00:00 | Pass | Replace faulty lock
MSA-DTWD | WA4043639 | Exit near D224 - door handle on the inside of the external door next D224 has fallen off | Perth Campus B4 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-15 12:10:00 | Pass | Replaced damaged handle and test.
MSA-DTWD | WA4043663 | J Block, Room J004.1- AIr Con wont turn on | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-08-11 14:43:00 | Fail | attended site, decommissioned and removed old LG split.installed and commissioned new Fujitsu 09 HWS.new pipes, interconnecting cables, feed from isolator and isolator used. system operating well when departing site commissioned as per commissioning sheet
MSA-DTWD | WA4043724 | A block Outside AG11 roof leak - see notes | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-11 11:15:00 | Pass | Relocated air con condensation pipe with bracket. Silicone seal to roof sheet and flashing.Issue relating to original cause of work order has been resolved but there are still concerns that this area may still leak due to poor design of flashings.A full dry pan flashing was suggested but declined at the time the job was signed off
MSA-DTWD | WA4043729 | Block 7 ladies toilet faulty inlet valve | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 09 Mar 2021 | 2021-03-12 17:00:00 | 2021-03-10 15:00:00 | Pass | Specific inlet valve for invisi toilet required
MSA-MRWA | WA4043236 | Level 10, external water tank - Float valves not shutting pumps off when full, investigate/remediate | Don Aitken Centre MRWA Head Office-External Area | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Mar 2021 | 2021-03-16 17:00:00 | 2021-03-10 14:09:00 | Pass | Investigate high level float switch.Faulty switch to be replaced.
MSA-DCS | WA4043866 | Entry security, vehicle access gate - unable to open eletricaonally , has to be manual opened | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Mar 2021 | 2021-03-10 11:15:14 | 2021-03-10 09:15:00 | Pass | Relay in Motor control box in a constant state of open and close. Power cycled Motor Controls. Everything back to normal functionality
MSA-DCS | WA4043897 | Unit 2, B3 - Electrical fault in cell keeps tripping out | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 07:34:47 | 2021-03-10 10:30:00 | Pass | Investigate and repair unit 2 cell b3 power
MSA-DCS | WA4043900 | Unit 1, B07 - viewing window and slide smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 07:47:04 | 2021-03-11 10:00:00 | Fail | VIEWING WINDOW RE GLAZED
MSA-DCS | WA4043949 | Reset building, outside prison - replace/repair kitchen mixer faulty/damaged | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-31 09:00:00 | Fail | Inspected for the sprout having pin holes. Need to replace the spout. Could not find the isolation for this tap. Collected parts for the job from supplier on 29/3/21Returned site. Installed mini stop to hot and cold connection. Removed the faulty breech mixer tap. Installed flick kitchen mixer tap.
MSA-DCS | WA4043954 | Unit 6, Cell D3- Lock is jammed | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-11 11:00:00 | Pass | Replace hinges, door plate and lock, require parts.Weld on strike plate.
MSA-DCS | WA4043955 | Unit 7, retic pipe main line broken | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 08:42:15 | 2021-03-10 11:20:00 | Pass | cracked pipe added joiner to break location
MSA-DCS | WA4043963 | Transponder to Unit 1 A wing has gone down | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Mar 2021 | 2021-03-10 12:53:50 | 2021-03-10 11:45:00 | Pass | Moved a reciever in Unit 1A due to some demolition works. Tested after moving. Everything working as per normal
MSA-DCS | WA4043969 | SOG Base, Departmental vehicle car park - fence post is loose | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-10 11:45:00 | Pass | 10/03/21Move fence and replace fixings at SOG fence line
MSA-DCS | WA4043981 | Unit 2, B - last ablution block - urinal sensor light not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-12 11:15:00 | Pass | Arrived on site and inspected found the 1st and 3 Ed urinal blocked. Plunged multiple times to clear the blockage and tested multiple times all working in order. Tested the auto flush all working good.
MSA-DCS | WA4044011 | PTZ 7 gate control has been hit by lightning no video input | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 10:02:53 | 2021-03-16 10:15:00 | Fail | Attended site confirmed no video in Gatehouse equipment rack. Attended perimeter Equipment Cabinet (EC/E2). No less illuminated on fibre modem, power supply intact. Replaced failed fibre modem with second hand spare. Confirmed video restored to Gate Control and PTZ function available. Reset camera preset settings.
MSA-DCS | WA4044037 | Unit 14 - D Wing cleaning cupboard sink tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 12:30:00 | Pass | Nill
MSA-DCS | WA4044045 | Unit 14, D16 - shower drain in floor blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 09:30:00 | Pass | Nill
MSA-DCS | WA4044046 | Unit 14 - B & D dayroom sink leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 09:30:00 | Pass | Nill
MSA-DCS | WA4044054 | Unit 14, B10 - leaking toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 10:30:00 | Pass | Nill
MSA-DCS | WA4044056 | Unit 4 - B Wing shower head clogged up and not flowing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 08:30:00 | Pass | Nill
MSA-DCS | WA4044062 | Education, Toilet - The staff toilet, situated in the back demountable toilet cubicle (right side) i | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 12:16:00 | Pass | Nill
MSA-DCS | WA4044077 | Unit 14, D13 - shower floor drain clogged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-12 12:39:00 | Pass | Nill
MSA-DCS | WA4044080 | Unit 14, D5 - shower head leaking in cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 10:30:00 | Pass | Nill
MSA-DCS | WA4044086 | Unit 4, B7 - sink leaking in pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 15:30:00 | Pass | Nill
MSA-DCS | WA4044098 | Unit 14, B2 - light switch in cell B2 damaged, wires exposed | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 11:16:39 | 2021-03-10 15:00:00 | Pass | Replaced damaged switch in unit 14 b2
MSA-DCS | WA4044110 | Unit 4, C wing - 3 x lights broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-12 11:30:00 | Pass | Investigate and repair 3 broken lights in unit 4 c wing
MSA-DCS | WA4044121 | Education, Day Room- hot water tap on boiler (on wall) is not working in education tea room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 12:17:00 | Pass | Nill
MSA-DCS | WA4044126 | Vegetable Preparation - Indoor unit frosting up in cool room | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-04-12 15:30:00 | Fail | Leak check completed successfully.Unit operational.
MSA-DCS | WA4044147 | Attend MCR and ensure all security services return post testing and tagging | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-10 14:15:00 | Pass | Reviewed all security systems. No faults on security systems except for a tamper on Mdas system in admin comms room. Got escort to admin and closed mdas tamper on cabinet. All systems working as per normal
MSA-DCS | WA4044162 | Level 2, opposite male toilets - light globe has blown | East Perth | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 16:30:00 | Pass | Repaired lighting on level 2
MSA-DCS | WA4044224 | Unit 1. Cell D7- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-26 12:30:00 | Fail | Replaced broken shower tiles.
MSA-DCS | WA4044225 | Unit 1, Cell D6- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-18 08:30:00 | Fail | Replaced broken shower tiles.
MSA-DCS | WA4044226 | control room - main control room door not closing by itself (hinge) | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-23 11:30:00 | Fail | Onsite, inspect door. Part requires to be ordered. Re-attend site to install new door closer. Tested, all functional.
MSA-DCS | WA4044228 | Unit 1, Cell D5- Broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | COMPFIN | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 15:30:00 | Pass | Replaced broken shower tiles.
MSA-DCS | WA4044230 | Unit 1, Cell D10- Repair Damaged Door Frame | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-23 15:30:00 | Fail | welded hinges to door frames cells 9-16
MSA-DCS | WA4044233 | Unit 1, Cell D8- Repair Damaged Door Frame | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-24 15:30:00 | Fail | Welded hinges to door frames cells 1-8
MSA-DCS | WA4044239 | Gate house control room - PTZ 20 stopped working | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Mar 2021 | 2021-03-10 21:34:46 | 2021-03-24 14:30:00 | Fail | Adjusted stream settings camera all ok now
MSA-DCS | WA4044255 | Kitchen - water pipe behind bell damaged | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-12 14:30:00 | Pass | Kitchen, water pipe behind bell damaged. Kettle water supply line burst. New line needs to be machined for thread to fit. Return to site. Install repaired line. Test for leaks. Report to staff.
MSA-DCS | WA4044264 | Unit 2, D wing - Shower privacy door broken off | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-15 15:00:00 | Pass | NEW HINGES INSTALLED/DOOR REPAIRED
MSA-DCS | WA4044281 | Kitchen- 2 air curtain fans not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-25 13:30:00 | Fail | Replaced 2x air curtains
MSA-DCS | WA4044299 | Unit 2B pod 1 fly screen door locked from the outside cannot manually unlock from inside | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-12 12:30:00 | Pass | Unit 2b - flyscreen doors (security screen )modified both doors to be non -lockable after discussion with Security .
MSA-DCS | WA4044367 | MDAS System has tamper alarms on system that cannot be cleared | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 22:08:45 | 2021-03-16 16:00:00 | Fail | Found MDAS MASTER computer is dead. Tried to reboot a few times but it will not even fire up. Pulled out the PC for repair. NOTE: client needs to be updated on the status of repairReturned to site and reinstalled the MDAS MASTER computer, tested with head guard and staff on site all ok. Need to observe if the master computer will crash again. If so then (quote to replace)26/3/21 work order to be invoiced at cost to date.
MSA-DFES | WA4043932 | Lvl 1, Men's toilet- Second door closer is not working, futher notes below | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Mar 2021 | 2021-03-15 17:00:00 | 2021-03-10 14:45:00 | Pass | Made adjustments to door closer speed then tested to confirm in working order.
MSA-DFES | WA4044025 | Relieving Bathroom 2 -Light in Second relieving bathroom, not working | CFRS Maddington | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 12:30:00 | Pass | Changed 2 no. 4 pin 18 watt lamps in shower room light fitting
MSA-DFES | WA4044078 | ground change room 2 & 4 broken GPO's both next to sink | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-15 15:30:00 | Pass | CompleteReplaced gpo
MSA-DFES | WA4044104 | Kitchen flywire door rollers broken | CFRS Malaga | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-15 10:45:00 | Pass | Work completed
MSA-DFES | WA4044112 | admin ground large amount of Millipedes mainly in change room - see notes | FESA RHQ - Forrestfield | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-17 11:15:00 | Pass | Attended on site and carried out a treatment for millipedes. Applied a residual insectice around safely accessible areas of external perimeter around all change rooms, incl. paths, walls and garden beds, in order t kill approaching millipedes. Re-spraying of affected areas may be necessary after heavy rain falls.
MSA-DFES | WA4044185 | Engine Bay, applied training grounds - loose lighting fitting | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 10 Mar 2021 | 2021-03-11 17:00:00 | 2021-03-10 16:00:00 | Pass | Arrived onsite located light. Defuser had moved out of position. Re positioned to correct position. All done and working
MSA-DTAG | WA4043885 | Ground, court 6 - Duress alarm has been going off about 8 times, no one in court room | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Mar 2021 | 2021-03-10 17:00:00 | 2021-03-10 11:09:00 | Pass | Found loose connection repaired
MSA-DTAG | WA4043945 | Courtyard- Electrical junction boxes are corroded – central inner courtyard | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-16 08:00:00 | Pass | Replaced new junction box
MSA-DTAG | WA4043947 | Courtyard- Blocked drains in west inner courtyard – access via custody | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 10 Mar 2021 | 2021-03-17 17:00:00 | 2021-03-13 12:00:00 | Pass | Unblocked stormawater drains in various locations